## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:June 2020
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | June 2020 |  | May 2020 |  | June 2019
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 12070 | 24/06/20 | 11977 | 18/05/20 | 12780 | 24/06/19 | 12893 | 29/05/19
|  |  | 22:00 |  | 22:00 |  | 21:00 |  | 21:00
2 | Minimum Generation (MW) | 6656.5 | 05/06/20 | 2679.2 | 21/05/20 | 5341 | 06/06/19 | - | -
|  |  | 7:00 |  | 6:00 |  | 7:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 12070 | 24/06/20 | 11941 | 18/05/20 | 12780 | 24/06/19 | 12893 | 29/05/19
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 10183.6 | 24/06/20 | 9490.1 | 18/05/20 | 10554 | 24/06/19 | 10636.2 | 01/09/19
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 12070 | 24/06/20 | 11941 | 18/05/20 | 12780 | 24/06/19 | 12893 | 29/05/19
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 10925.7667 |  | 9477.5161 |  | 11184.6333 |  | 11679.07 | 2019-09-19
7 | Average Generation (MW) at Day Peak | 9156.325 |  | 7427.4674 |  | 8726.5667 |  | 9378.1933 | 2019-09-19
8 | Maximum Power Import from India, HVDC (MW) | 950 | 04/06/2020 | 949 | 10/05/2020 | 949 | 09/06/19 | 956 | 27/3/2019
|  |  | 2:30 |  | 1:00 |  | 2:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 182 | 09/06/2020 | 190 | 17/05/2020 | 194 | 12'/06/19 | 194 | 12/06/19
|  |  | 21:00 |  | 21:00 |  | 19:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 2010-05-04
20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 3707.5 | 05/04/10
20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 3156.9465 |  | 3143.7123 |  | 3440.1955 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 79.8302 |  | 60.14 |  | 104.8438
22 | Net Generation of BPDB (MKWH) | 3077.1163 |  | 3083.5723 |  | 3335.3516
23 | Net Generation of IPP & RPCL (MKWH) | 2233.4592 |  | 1715.9925 |  | 2092.3389
24 | Net Generation of REB (MKWH) | 148.3631 |  | 118.008 |  | 134.161
24 | Net Generation of Rental Power Plant (MKWH) | 560.7517 |  | 375.5825 |  | 497.087
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 6019.6903 |  | 5283.4564 |  | 6058.9385 |  | 6553.86 | Sep-19
26 | Energy Generation by Gas (MKWH) | 4101.8172 |  | 4152.6276 |  | 4367.2451 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 302.7603 |  | 175.8613 |  | 300.7306 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1221.1035 |  | 644.461 |  | 1284.7373 |  | 1524.02 | July-19
29 | Energy Generation by Hydro (MKWH) | 62.4299 |  | 38.7155 |  | 26.8955 |  | 151.4 | August-19
30 | Energy Generation by Solar (MKWH) | 4.9313 |  | 15.7592 |  | 5.1029 |  | 22.56 | 2019-09-16
31 | Energy Generation by Coal (MKWH) | 406.4783 |  | 325.8707 |  | 180.8932 |  | 416.1569 | 2020-04-17
32 | Enegry Import from India (HVDC & AC) (MKWH) | 736.3907 |  | 568.5998 |  | 695.7256 |  | 762.62 | August-19
33 | Monthly Load Factor (%) | 78.6605 |  | 66.4568 |  | 74.5667 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:June' 2020
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 12070 | 24/06/20 | 22:00
Generation Period
| Dhaka | MW | 3791
| Chattogram | MW | 1090
| Cumilla | MW | 1182
| Mymensingh | MW | 925
| Sylhet | MW | 365
a) | Total supply in East zone | MW | 7353
| Khulna | MW | 1535
| Barisal | MW | 359
| Rajshahi | MW | 1282
| Rangpur | MW | 742
b) | Total supply in West zone | MW | 3918
c) | Total supply in both zone ( a+b) | MW | 11271
Ref: | 27.21.0000.603.16.087.20.296 | Date: 20/07/2020
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:June' 2020
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 650 | 13/06/20 | 15:00
| b) Ishurdi end | MW | 228 | 10/06/20 | 18:30
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 660 | 10/06/20 | 18:30
| b) Ishurdi end | MW | 245 | 13/06/20 | 15:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | 1.8975 | 22/06/20
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | 1.8484 | 22/06/20
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 9.998
| b) Ishurdi end | MKWH | 51.4063
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 49.8641
| b) Ishurdi end | MKWH | 9.7068
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 450 | 03/06/20 | 20:00
| b)Serajganj end | MW | 440 | 26/06/20 | 10:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 420 | 26/06/20 | 10:00
| b)Sirajganj end | MW | 420 | 03/06/20 | 20:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 4.352 | 23/06/20
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 4.246 | 23/06/20
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 29.304
| b)Sirajganj end | MKWH | 89.054
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 86.064
| b)Sirajganj end | MKWH | 29.04
30 | Transmission loss of EWI /NO-2 | % | 2.308
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishwardi.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: June 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kabirpur | 132 kV main Bus | 2020-06-06 21:21 | 2020-06-06 22:35 | 1:14 | E/O | Due to red-hot maintenance | 172 | 212.1333 | Power interruption
Satmosjid | 132/33 kV Transformer-T2 | 2020-06-13 19:44 | 2020-06-13 22:45 | 3:01 | T | Tripped showing PRV relay | 0 | 0 | No interruption
Tongi | 132/33 kV Transformer-T3 | 2020-06-14 22:12 | 2020-06-15 02:17 | 4:05 | E/O | Due to bursting of CT | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T3 | 2020-06-17 06:24 | 2020-06-17 07:49 | 1:25 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-06-22 10:50 | 2020-06-22 10:58 | 0:08 | T | Tripped showing O/C & E/F relay | 50 | 6.6667 | Power interruption
| 132/33 kV Transformer-T2 | 2020-06-22 10:50 | 2020-06-22 11:02 | 0:12 | T
Mymensingh | 132/33 kV Transformers-T1 & T2 | 2020-06-24 19:30 | 2020-06-24 19:37 | 0:07 | T | Tripped showing SPS relay | 146 | 17.0333 | Power interruption
Savar | 132/33 kV Transformer-T1 & 33 kV Bus | 2020-06-26 11:28 | 2020-06-26 11:37 | 0:09 | T | Tripped showing O/C & E/F relay | 110 | 16.5 | Power interruption
Dhamrai | 132/33 kV Transformer-T2 | 2020-06-26 14:07 | 2020-06-26 18:16 | 4:09 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T2 | 2020-06-26 22:58 | 2020-06-27 00:50 | 1:52 | E/O | Due to red-hot maintenance | 45 | 84 | Power interruption
|  |  | Total : | 16:22 |  | Unserved Energy: |  | 336.3333
Dhaka (South) Grid Circle :
Munshiganj | 132/33 kV both Transformer-T1 | 2020-06-02 07:24 | 2020-06-02 08:06 | 0:42 | T | Due to 33 kV auxiliary Transformer fault | 104 | 72.8 | Power interruption
Bhulta | 132/33 kV Transformer-T1 | 2020-06-07 21:10 | 2020-06-07 21:10 | 0:00 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Madanganj | 132/33 kV Transformer-T2 | 2020-06-13 19:58 | 2020-06-13 20:15 | 0:17 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Hasnabad | 230/132 kV Transformers-T1 | 2020-06-18 11:40 | 2020-06-18 23:58 | 12:18 | E/O | Due to flashing at DS Y-phase HT side | 375 | 112.5 | Power interruption 11:40 to 11:58
| 230/132 kV Transformers-T2 | 2020-06-18 11:40 | 2020-06-18 16:02 | 4:22 | E/O
| 230/132 kV Transformers-T3 | 2020-06-18 11:40 | 2020-06-18 12:27 | 0:47 | E/O
Siddhirganj | 132/33 kV Transformer-T1 | 2020-06-30 06:32 | 2020-06-30 09:18 | 2:46 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 21:12 |  | Unserved Energy: |  | 185.3
Chattogram Grid Circle :
Rangamati | 132/33 kV Transformers-T1 | 2020-06-01 06:11 | 2020-06-01 07:15 | 1:04 | T | Tripped showing differential relay | 6 | 6.4 | Power interruption
| 132/33 kV Transformers-T2 | 2020-06-01 06:11 | 2020-06-01 07:13 | 1:02 | T
Halishahar | 132/33 kV Transformers-T2 & T3 | 2020-06-04 01:30 | 2020-06-04 02:03 | 0:33 | T | Due to 33 kV feeder fault | 42 | 23.1 | Power interruption
| 132/33 kV Transformer-T2 | 2020-06-04 10:58 | 2020-06-04 11:12 | 0:14 | T | Tripped showing O/C & E/F relay at 33 kV side | 0 | 0 | No interruption
Madunaghat | 132/33 kV Transformers-T1 & T2 | 2020-06-08 15:34 | 2020-06-08 15:47 | 0:13 | T | Tripped showing O/C relay | 47 | 10.1833 | Power interruption
Halishahar | 132/33 kV Transformer-T2 | 2020-06-13 07:42 | 2020-06-13 10:10 | 2:28 | E/O | Due to red-hot maintenance at 33 kV side | 35 | 86.3333 | Power interruption
| 132/33 kV Transformer-T3 | 2020-06-16 14:43 | 2020-06-16 16:02 | 1:19 | E/O | Due to red-hot maintenance | 25 | 32.9167 | Power interruption
| 132/33 kV Transformer-T1 | 2020-06-21 20:45 | 2020-06-21 21:59 | 1:14 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Madunaghat | 132/33 kV Transformer-T1 | 2020-06-22 05:37 | 2020-06-22 07:56 | 2:19 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
| 132/33 kV Transformers-T1 & T2 | 2020-06-28 09:52 | 2020-06-28 10:15 | 0:23 | T | Tripped showing O/C & Dir.relay at 33 kV feeder fault | 41 | 15.7167 | Power interruption
|  |  | Total : | 10:49 |  | Unserved Energy: |  | 174.65
Cumilla Grid Circle :
Bibiyana | 400/230 kV Transformer-T02 | 2020-06-04 07:21 | 2020-06-04 09:07 | 1:46 | T | Tripped showing BFP start | 0 | 0 | No interruption
Cumilla (N) | 132/33 kV Transformer-T4 | 2020-06-05 05:25 | 2020-06-05 11:47 | 6:22 | T | Tripped showing winding temperature high | 0 | 0 | No interruption
Shahjibazar | 132/33 kV Transformer-T2 | 2020-06-06 13:23 | 2020-06-06 13:31 | 0:08 | T | Tripped showing 33 kV feeder fault | 30 | 4 | Power interruption
Bibiyana | 400/230 kV Transformer-T02 | 2020-06-07 00:06 | 2020-06-07 02:53 | 2:47 | T | Tripped showing Gen.trip & fire fight trip | 0 | 0 | No interruption
Cumilla (N) | 132/33 kV Transformer-T3 | 2020-06-08 14:12 | 2020-06-08 18:08 | 3:56 | T | Tripped showing REF relay | 24 | 94.4 | Power interruption
Baroierhat | 132/33 kV Transformer-T2 | 2020-06-12 09:41 | 2020-06-12 12:20 | 2:39 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Cumilla (N) | 132/33 kV Transformer-T3 | 2020-06-14 20:58 | 2020-06-14 21:18 | 0:20 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Sunamganj | 132/33 kV Transformer-T1 | 2020-06-17 09:01 | 2020-06-17 11:08 | 2:07 | E/O | Due to red-hot maintenance 33 kV side | 0 | 0 | No interruption
Fenchuganj | 230/132 kV Transformer-Tr1 | 2020-06-19 11:50 | 2020-06-19 12:16 | 0:26 | T | Tripped showing E/F relay | 0 | 0 | No interruption
B.Baria | 132/33 kV Transformer-T2 | 2020-06-19 21:15 | 2020-06-19 22:00 | 0:45 | E/O | Due to red-hot maintenance | 7 | 5.25 | Power interruption
Sreemongal | 132/33 kV Transformers-T2 | 2020-06-21 18:22 | 2020-06-22 11:13 | 16:51 | T | Tripped showing PRD relay | 0 | 0 | No interruption
| 132/33 kV Transformers-T3 | 2020-06-21 18:22 | 2020-06-21 19:35 | 1:13 | T |  | 0 | 0 | No interruption
Biyanibazar | 132/33 kV Transformer-T1 | 2020-06-24 11:27 | 2020-06-24 13:18 | 1:51 | E/O | Due to gas pressure low | 0 | 0 | No interruption
Sunamganj | 132/33 kV Transformer-T1 | 2020-06-29 12:05 | 2020-06-29 14:05 | 2:00 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
|  |  | Total : | 43:11 |  | Unserved Energy: |  | 103.65
Khulna Grid Circle :
Mongla | 132/33 kV Transformer-T2 | 2020-06-02 01:02 | 2020-06-02 02:44 | 1:42 | E/O | Due to red-hot maintenance 33 kV side | 14 | 23.8 | Power interruption
Gallamari | 132/33 kV Transformers-T1 | 2020-06-02 07:20 | 2020-06-02 08:46 | 1:26 | E/O | Due to red-hot maintenance at 33 kV side | 30 | 43 | Power interruption
| 132/33 kV Transformer-T2 | 2020-06-02 07:20 | 2020-06-02 08:47 | 1:27 | E/O |  | 0 | 0
Khulna© | 132/33 kV Transformers-T1 ,T2 & T3 | 2020-06-02 18:10 | 2020-06-02 18:16 | 0:06 | T | Tripped showing E/F relay | 15 | 1.5 | Power interruption
Faridpur | 132/33 kV Transformer-T1 | 2020-06-03 16:23 | 2020-06-03 17:16 | 0:53 | E/O | Due to red-hot maintenance | 50 | 44.1667 | Power interruption
Page: 2/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: June 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Gopalganj | 132/33 kV Transformers-T1 & T2 | 2020-06-03 16:57 | 2020-06-03 17:33 | 0:36 | T | Tripped showing 33 kV feeder fault | 76 | 45.6 | Power interruption
Bagerhat | 132/33 kV Transformers-T1 & T3 | 2020-06-07 23:02 | 2020-06-07 23:44 | 0:42 | E/O | Due to red-hot maintenance 33 kV side | 73 | 51.1 | Power interruption
Madaripur | 132/33 kV Transformer-T1 | 2020-06-12 07:09 | 2020-06-12 09:12 | 2:03 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Faridpur | 33 kV Bus section -1 | 2020-06-13 09:51 | 2020-06-13 10:30 | 0:39 | E/O | Due to red-hot maintenance 33 kV side | 25 | 16.25 | Power interruption
Chuadanga | 132/33 kV Transformers-T1 | 2020-06-15 03:12 | 2020-06-15 03:17 | 0:05 | T | Tripped showing O/C relay | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 | 2020-06-15 03:12 | 2020-06-15 07:40 | 4:28 | T |  | 0 | 0 | No interruption
Noapara | 132/33 kV Transformer-T2 | 2020-06-17 05:57 | 2020-06-17 09:46 | 3:49 | T | Tripped showing differential relay | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformers-T1 | 2020-06-19 14:22 | 2020-06-19 14:29 | 0:07 | T | Tripped showing E/F relay at 33 kV side | 40 | 4.6667 | Power interruption
| 132/33 kV Transformers-T2 | 2020-06-19 14:22 | 2020-06-19 14:33 | 0:11 | T |  | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T1 | 2020-06-24 23:10 | 2020-06-25 23:03 | 23:53 | T | Tripped showing 33 kV feeder fault | 0 | 0 | No interruption
Gallamari | 132/33 kV Transformer-T2 & 33 kV Bus | 2020-06-28 07:50 | 2020-06-28 09:10 | 1:20 | E/O | Due to red-hot maintenance | 30 | 40 | Power interruption
Bagerhat | 132/33 kV Transformer-T3 | 2020-06-29 22:38 | 2020-06-30 01:08 | 2:30 | E/O | Due to red-hot maintenance 33 kV side | 24 | 60 | Power interruption
|  |  | Total : | 45:57 |  | Unserved Energy: |  | 330.0833
HVDC Grid Circle :
Bottail | 132/33 kV Transformer-T2 | 2020-06-03 15:07 | 2020-06-03 16:17 | 1:10 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Benapole | 132/33 kV Transformers-T1 & T2 | 2020-06-08 19:10 | 2020-06-08 19:20 | 0:10 | T | Tripped showing O/C & E/F relay | 30 | 5 | Power interruption
Bheramara HVDC | 230/132 kV auxiliary Transformer | 2020-06-10 14:17 | 2020-06-10 17:53 | 3:36 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Bottail | 132/33 kV Transformer-T2 | 2020-06-10 23:05 | 2020-06-11 00:31 | 1:26 | E/O | Due to red-hot maintenance 33 kV side | 48 | 68.8 | Power interruption
Jhenidah | 132/33 kV Transformers-T1 | 2020-06-17 11:39 | 2020-06-17 11:52 | 0:13 | T | Tripped showing O/C & E/F relay | 60 | 13 | Power interruption
| 132/33 kV Transformers-T2 | 2020-06-17 11:39 | 2020-06-17 11:53 | 0:14 | T
Shahjadpur | 132/33 kV Transformers-T4 | 2020-06-20 21:13 | 2020-06-20 21:49 | 0:36 | E/O | Due to red-hot maintenance 33 kV side | 20 | 12 | Power interruption
Bheramara HVDC | Bheramara HVDC 230 kV 20DF22 filter | 2020-06-26 22:27 | 2020-06-26 22:27 | 0:00 | T | Tripped showing Diff. relay | 0 | 0 | No interruption
| Bheramara HVDC 230 kV 20DF12 filter | 2020-06-27 06:43 | 2020-06-27 10:12 | 3:29 | T | Due to capacitor unbalance | 0 | 0 | No interruption
Pabna | 132/33 kV Transformer-T3 | 2020-06-30 15:59 | 2020-07-01 12:03 | 20:04 | E/O | Due to 33 kV Y-phase cable burst | 0 | 0 | No interruption
|  |  | Total : | 30:58 |  |  |  | 98.8
Bogura Grid Circle:
Thakurgaon | 132/33 kV Transformers-T1 & T2 | 2020-06-01 07:45 | 2020-06-01 07:53 | 0:08 | T | Due to crow on 33 kV Bus | 40 | 5.3333 | Power interruption
Barapukuria | 132/33 kV Transformer-T5 | 2020-06-01 21:01 | 2020-06-01 21:23 | 0:22 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Bogura | 132/33 kV Transformer-T1 | 2020-06-02 07:45 | 2020-06-02 09:40 | 1:55 | E/O |  | 45 | 86.25 | Power interruption
| 132/33 kV Transformer-T1 | 2020-06-02 08:20 | 2020-06-02 09:40 | 1:20 | E/O | Due to red-hot maintenance | 40 | 53.3333 | Power interruption
Barapukuria | 132/33 kV Transformer-T4 | 2020-06-03 22:22 | 2020-06-03 23:26 | 1:04 | E/O | Due to red-hot maintenance | 25 | 26.6667 | Power interruption
Rangpur | 132/33 kV Transformers-T1 & T2 & 33 kV bus | 2020-06-04 07:45 | 2020-06-04 09:50 | 2:05 | E/O | Due to red-hot maintenance | 60 | 125 | Power interruption
Bogura | 132/33 kV Transformers-T1 & T2 | 2020-06-09 11:56 | 2020-06-09 12:14 | 0:18 | T | Due to 33 kV feeder fault | 72 | 21.6 | Power interruption
Rangpur | 132/33 kV Transformers-T1 & T2 & 33 kV bus | 2020-06-10 07:30 | 2020-06-10 08:12 | 0:42 | E/O | Due to red-hot maintenance | 100 | 70 | Power interruption
Palashbari | 132/33 kV Transformer-T2 | 2020-06-12 07:34 | 2020-06-12 08:39 | 1:05 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2020-06-12 09:07 | 2020-06-12 10:15 | 1:08 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Purbasadipur | 132/33 kV Transformer-T1 & 33 KV bus | 2020-06-15 23:23 | 2020-06-16 01:02 | 1:39 | E/O | Due to red-hot maintenance at 33 kV side | 48 | 79.2 | Power interruption
Rangpur | 33 kV Bus | 2020-06-17 07:10 | 2020-06-17 08:40 | 1:30 | E/O | Due to red-hot maintenance at 33 kV side | 45 | 67.5 | Power interruption
Mohasthangar | 132/33 kV Transformer-T2 | 2020-06-25 12:46 | 2020-06-27 12:37 | 47:51 | E/O | Due to Oil leakge | 0 | 0 | No interruption
Purbasadipur | 132/33 kV Transformer-T1 | 2020-06-28 12:35 | 2020-06-28 15:40 | 3:05 | E/O | Due to 33 kV feeder fault | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-06-29 18:48 | 2020-06-29 19:36 | 0:48 | E/O | Due to red-hot maintenance at 33 kV side | 30 | 24 | Power interruption
|  |  | Total : | 65:00 |  |  |  | 558.8833
Others :
Ashuganj | 230/132 kV Transformer-OAT12 | 2020-06-05 00:05 | 2020-06-05 06:39 | 6:34 | T | Tripped showing master pro. relay | 0 | 0 | No interruption
| 230/132 kV Transformer-OAT12 | 2020-06-08 05:22 | 2020-06-08 08:03 | 2:41 |  |  | 0 | 0 | No interruption
| 230/132 kV Transformer-OAT12 | 2020-06-10 04:27 | 2020-06-10 13:04 | 8:37 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
| 230/132 kV Transformer-OAT12 | 2020-06-10 19:05 | 2020-06-10 20:57 | 1:52 | T | Tripped showing O/C relay | 0 | 0 | No interruption
|  |  | Total : | 19:44 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 253:13 | Hours
T = Tripping | [7 empty] | Executive Engineer
E/O = Emergency Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/3 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: June 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tangail | Tangail-RPCL 132 kV line-1 | 2020-06-01 05:35 | 2020-06-01 05:56 | 0:21 | T | Tripped showing dist.(Z1) relay | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-1 | 2020-06-03 07:08 | 2020-06-03 07:31 | 0:23 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2020-06-04 09:52 | 2020-06-04 10:09 | 0:17 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Tangail | Tangail-Mymensingh RPCL 132 kV line-1 | 2020-06-04 13:00 | 2020-06-04 13:10 | 0:10 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-2 | 2020-06-04 18:45 | 2020-06-04 18:57 | 0:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV line-2 | 2020-06-06 15:21 | 2020-06-06 16:02 | 0:41 | T | Tripped showing dist.& O/C relay | 172 | 117.5333 | Power interruption
Kaliakoir | Kaliakoir-Kabirpur 132 kV line-1 | 2020-06-06 15:21 | 2020-06-06 15:21 | 0:00 | E/O | Due to B-phase Jumper flashing | 0 | 0 | No interruption
Tangail | Tangail-Mymensingh RPCL 132 kV line-1 | 2020-06-10 04:27 | 2020-06-10 04:39 | 0:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Mymensingh RPCL | Mymensingh RPCL-Mymensingh S/S 132 kV line-1 & 2 | 2020-06-10 19:05 | 2020-06-10 19:46 | 0:41 | T | Tripped showing O/C relay | 700 | 478.3333 | Power interruption
Gazipur Summit | Gazipur Summit-Toni-Kaliakoir 230 kV line | 2020-06-12 11:10 | 2020-06-12 14:30 | 3:20 | E/O | Due to bursting of PT | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-1 | 2020-06-15 09:15 | 2020-06-15 09:33 | 0:18 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-2 | 2020-06-15 14:43 | 2020-06-15 14:59 | 0:16 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Lalbagh | Lalbagh-Kallyanpur 132 kV line-2 | 2020-06-16 22:27 | 2020-06-17 12:43 | 14:16 | T | Tripped showing 86B 67 N signal | 0 | 0 | No interruption
Tongi | Tongi-Uttara 3rd phase 132 kV line | 2020-06-25 16:40 | 2020-06-25 18:50 | 2:10 | T | Tripped showing Diff. relay | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh United 132 kV line-1 & 2 | 2020-06-25 19:04 | 2020-06-25 19:13 | 0:09 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Dhamrai | Dhamrai-Kaliakoir 132 kV line-2 | 2020-06-28 13:47 | 2020-06-28 14:43 | 0:56 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kallyapur | Kallyapur-Tongi 132 kV line-1 | 2020-06-30 12:17 | 2020-06-30 12:29 | 0:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 24:34 |  | Unserved Energy: |  | 595.8667
Dhaka (South) Grid Circle :
Madanganj | Madanganj S/S -Madanganj P/S 132 kV line | 2020-06-02 13:02 | 2020-06-02 15:00 | 1:58 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj(S) 230 kV line-1 | 2020-06-03 15:10 | 2020-06-03 21:30 | 6:20 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ghorashal-Ashuganj(S) 230 kV line-1 | 2020-06-03 21:58 | 2020-06-03 21:58 | 0:00 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Lalbagh | Lalbagh-Hasnabad 132 kV line | 2020-06-04 15:45 | 2020-06-04 16:02 | 0:17 | T | Tripped showing dist. relay | 75 | 21.25 | Power interruption
Sitalakhya | Sitalakhya-Madanganj 132 kV line | 2020-06-04 19:38 | 2020-06-04 21:52 | 2:14 | T | Tripped showing main protection relay | 76 | 169.7333 | Power interruption
| Sitalakhya-Hasnabad 132 kV line | 2020-06-04 19:38 | 2020-06-04 19:50 | 0:12 | T | Tripped showing O/C & E/F. relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-1 | 2020-06-04 21:57 | 2020-06-04 22:58 | 1:01 | T | Tripped showing dist. relay
Sonargaon | Sonargaon-Daudkandi 132 kV line-2 | 2020-06-10 03:40 | 2020-06-10 03:47 | 0:07 | T | Tripped showing dist.(Z3) relay | 0 | 0 | No interruption
Haripur | Haripur-Haripur HPL 230 kV line-1 | 2020-06-11 08:28 | 2020-06-11 10:56 | 2:28 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Madanganj | Madanganj-Munshiganj 132 kV line-2 | 2020-06-11 17:30 | 2020-06-11 18:16 | 0:46 | T | Tripped showing Differential relay | 0 | 0 | No interruption
| Madanganj-Munshiganj 132 kV line-1 | 2020-06-13 03:46 | 2020-06-13 04:23 | 0:37 | T |  | 80 | 49.3333 | Power interruption
| Madanganj-Munshiganj 132 kV line-2 | 2020-06-13 03:46 | 2020-06-13 05:16 | 1:30 | T
Meghnaghat | Meghnaghat-Cumilla(N) 132 kV line-1 | 2020-06-14 11:29 | 2020-06-14 12:00 | 0:31 | T | Tripped showing dist.(Z3) relay | 0 | 0 | No interruption
Sonargaon | Sonargaon-Daudkandi 132 kV line-2 | 2020-06-14 23:15 | 2020-06-15 10:50 | 11:35 | T | Tripped showing dist.(Z3) relay | 0 | 0 | No interruption
Hasnabad | Hasnabad-Lalbagh 132 kV line | 2020-06-16 18:14 | 2020-06-16 18:27 | 0:13 | T |  | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 230 kV line | 2020-06-20 20:52 | 2020-06-21 09:40 | 12:48 | T | Tripped showing O/C & E/F. relay | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 132 kV line-2 | 2020-06-26 00:16 | 2020-06-26 01:35 | 1:19 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Sonargaon | Sonargaon-Daudkandi 132 kV line-1 | 2020-06-28 16:22 | 2020-06-28 16:33 | 0:11 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 44:07 |  | Unserved Energy: |  | 240.3167
Chittagong Grid Circle :
Dohazari | Dohazari-Cox'xbazar 132 kV line-1 | 2020-06-03 20:03 | 2020-06-03 20:12 | 0:09 | T | Tripped showing dist. relay | 24 | 3.6 | Power interruption
| Dohazari-Cox'xbazar 132 kV line-2 | 2020-06-09 14:03 | 2020-06-09 14:32 | 0:29 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Halishahar | Halishahar-Julda 132 kV line | 2020-06-20 08:39 | 2020-06-20 08:54 | 0:15 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'xbazar 132 kV line-2 | 2020-06-24 11:34 | 2020-06-24 11:54 | 0:20 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Dohazari-Cox'xbazar 132 kV line-2 | 2020-06-25 11:02 | 2020-06-25 11:06 | 0:04 | T | Tripped showing dist. relay | 80 | 5.3333 | Power interruption
| Dohazari-Cox'xbazar 132 kV line-1 | 2020-06-25 15:28 | 2020-06-25 15:42 | 0:14 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hathazari | Hathazari-AKSML 230 kV line | 2020-06-27 15:45 | 2020-06-27 18:32 | 2:47 | T | Tripped showing TCSR & SF6. relay | 0 | 0 | No interruption
|  |  | Total : | 4:18 |  | Unserved Energy: |  | 8.9333
Page: 2/3 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: June 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Cumilla(N) | Cumilla(N)-Meghnaghat 230 kV line-1 | 2020-06-03 18:00 | 2020-06-03 18:42 | 0:42 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Cumilla(N)-Meghnaghat 230 kV line-1 | 2020-06-03 18:00 | 2020-06-03 18:47 | 0:47 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Tripura 132 kV line-2 | 2020-06-04 03:49 | 2020-06-04 04:12 | 0:23 | T | Tripped showing auto reclose relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-B.baria 132 kV line-2 | 2020-06-05 00:05 | 2020-06-05 01:03 | 0:58 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Chandpur | Chandpur-Cumillla(N) 132 kV line-2 | 2020-06-05 01:17 | 2020-06-05 01:36 | 0:19 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Daudkandi 132 kV line-1 | 2020-06-05 17:22 | 2020-06-05 17:47 | 0:25 | T | Tripped showing dist. & O/C relay | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Tripura 132 kV line-2 | 2020-06-07 13:40 | 2020-06-07 14:11 | 0:31 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorashal 132 kV line-1 | 2020-06-08 05:22 | 2020-06-08 05:22 | 0:00 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-B.baria 132 kV line-2 | 2020-06-08 06:53 | 2020-06-08 07:26 | 0:33 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-Ghorashal 132 kV line-2 | 2020-06-08 04:55 | 2020-06-08 05:24 | 0:29 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Tripura 132 kV line-2 | 2020-06-08 11:38 | 2020-06-08 11:56 | 0:18 | T | Tripped showing pole discrepancy | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Daudkandi 132 kV line-2 | 2020-06-08 14:05 | 2020-06-08 14:13 | 0:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Cumilla(N)-Daudkandi 132 kV line-1 | 2020-06-09 11:17 | 2020-06-09 12:56 | 1:39 | T | Tripped showing directional & O/C relay | 0 | 0 | No interruption
B.Baria | B.Baria-Shahjibazar 132 kV line-2 | 2020-06-10 04:27 | 2020-06-10 04:52 | 0:25 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Shahjibazar 132 kV line-3 | 2020-06-10 04:27 | 2020-06-10 06:08 | 1:41 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-Ghorashal 132 kV line-1 & 2 | 2020-06-10 04:27 | 2020-06-11 21:10 | 40:43 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-B.Baria 132 kV line-1,& 2 | 2020-06-10 04:22 | 2020-06-10 06:52 | 2:30 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 kV line-1 | 2020-06-10 04:27 | 2020-06-10 07:46 | 3:19 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 kV line-2 | 2020-06-10 04:27 | 2020-06-10 09:20 | 4:53 | T | Tripped showing dist. RST SOTF relay | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV line-1 | 2020-06-10 07:13 | 2020-06-10 07:13 | 0:00 | T |  | 0 | 0 | No interruption
| Ashuganj-Ashuganj(S) 230 kV line-2 | 2020-06-10 17:34 | 2020-06-11 17:31 | 23:57 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Srimongal | Srimongal-Fenchuganj 132 kV line-1 & 2 | 2020-06-10 19:05 | 2020-06-10 19:48 | 0:43 | T | Tripped showing O/C relay | 247 | 177.0167 | Power interruption
Cumilla(N) | Cumilla(N)-Daudkandi 132 kV line-1 | 2020-06-11 10:58 | 2020-06-11 11:16 | 0:18 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Bhulta 400 kV line-2 | 2020-06-12 15:04 | 2020-06-12 22:02 | 6:58 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV line-2 | 2020-06-13 14:56 | 2020-06-13 15:44 | 0:48 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Surjimoninagar 132 kV line-1 | 2020-06-14 11:47 | 2020-06-14 12:05 | 0:18 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-2 | 2020-06-16 19:06 | 2020-06-16 19:57 | 0:51 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV line-2 | 2020-06-16 21:03 | 2020-06-16 21:42 | 0:39 | T | Tripped showing General trip & dist. relay | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV line-2 | 2020-06-18 04:08 | 2020-06-18 04:36 | 0:28 | T | Tripped showing dist.R-phase relay | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV line-2 | 2020-06-18 04:36 | 2020-06-18 18:01 | 13:25 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Choddagram 132 kV line-2 | 2020-06-18 16:34 | 2020-06-18 16:53 | 0:19 | T | Tripped showing dist.Dir.& O/C relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-2 | 2020-06-19 09:25 | 2020-06-19 11:55 | 2:30 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
B.Baria | B.Baria-Shahjibazar 132 kV line-2 | 2020-06-20 11:36 | 2020-06-20 12:36 | 1:00 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
| B.Baria-Shahjibazar 132 kV line-1 | 2020-06-20 12:44 | 2020-06-20 13:30 | 0:46 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Tripura | Tripura-Cumilla(S) 132 kV line-1 | 2020-06-21 12:05 | 2020-06-21 12:35 | 0:30 | T | Tripped showing dist. relay | 100 | 50 | Power interruption
Ashuganj | Ashuganj-Ghorashal 230 kV line-1 | 2020-06-21 12:21 | 2020-06-21 13:00 | 0:39 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Choddagram 132 kV line-1 | 2020-06-21 16:32 | 2020-06-21 16:44 | 0:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Cumilla(N)-Choddagram 132 kV line-1 | 2020-06-21 16:49 | 2020-06-21 21:11 | 4:22 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Cumilla(N)-Daudkandi 132 kV line-1 | 2020-06-22 04:20 | 2020-06-22 05:18 | 0:58 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-S,M.Nagar 132 kV line-1 | 2020-06-22 10:52 | 2020-06-22 12:08 | 1:16 | T | Due to Palatona Ckt trip | 104 | 131.7333 | Power interruption
Cumilla(N) | Cumilla(N)-Choddagram 132 kV line-2 | 2020-06-23 15:01 | 2020-06-23 15:28 | 0:27 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sylhet | Sylhet-Chattak 132 kV line-1 | 2020-06-28 00:51 | 2020-06-28 07:03 | 6:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Tripura 132 kV line-1 | 2020-06-28 19:11 | 2020-06-28 19:47 | 0:36 | T | Tripped showing dist. relay | 132 | 79.2 | Power interruption
| Cumilla(S)-Tripura 132 kV line-2 | 2020-06-28 19:11 | 2020-06-28 19:55 | 0:44 | T | Tripped showing dist. relay
|  |  | Total : | 129:39 |  | Unserved Energy: |  | 437.95
Page: 3/3 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: June 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Gopalganj(New) | Gopalganj(New)-Payra 400 kV line-2 | 2020-06-04 09:23 | 2020-06-04 09:29 | 0:06 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Gopalganj(New)-Payra 400 kV line-2 | 2020-06-04 22:52 | 2020-06-05 00:04 | 1:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Goalpara | Goalpara-Bagerhat 132 kV line-1 | 2020-06-13 05:11 | 2020-06-13 05:43 | 0:32 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Gallamari 132 kV line-1 | 2020-06-15 11:27 | 2020-06-15 11:57 | 0:30 | T | Tripped showing O/C & E/F. relay | 38 | 15 | Power interruption
| Khulna(S)-Gallamari 132 kV line-2 | 2020-06-15 11:27 | 2020-06-15 12:03 | 0:36 | T
Payra | Payra-Gopalganj 400 kV line | 2020-06-21 10:35 | 2020-06-21 10:53 | 0:18 | T | Tripped showing dist.R-phase relay | 0 | 0 | No interruption
| Payra-Gopalganj 400 kV line | 2020-06-21 12:51 | 2020-06-21 14:41 | 1:50 | T | Due to unbalanced voltage | 0 | 0 | No interruption
|  |  | Total : | 5:04 |  | Unserved Energy: |  | 15
HVDC Grid Circle :
Bharamara | Bharamara-Bottail 132 kV line-1 & 2 | 2020-06-01 09:10 | 2020-06-01 09:25 | 0:15 | T | Tripped showing dist. relay | 217 | 54.25 | Power interruption
Jashore | Jashore-Jhenidah 132 kV line-1 | 2020-06-01 09:10 | 2020-06-01 09:55 | 0:45 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Jashore-Jhenidah 132 kV line-2 | 2020-06-01 09:10 | 2020-06-01 10:03 | 0:53 | T |  | 0 | 0 | No interruption
Bottail | Bottail-Jhenidah 132 kV line-1 | 2020-06-01 09:10 | 2020-06-01 10:11 | 1:01 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ishurdi | Ishurdi-Bheramara 132 kV line-1 | 2020-06-03 13:12 | 2020-06-03 13:26 | 0:14 | T | Tripped showing CSW,CAT ,CD signal | 0 | 0 | No interruption
| Ishurdi-Bheramara 132 kV line-2 | 2020-06-03 13:12 | 2020-06-03 15:25 | 2:13 | T |  | 0 | 0 | No interruption
Bharamara | Bharamara HVDC-Khulna(S) 132 kV line-1 | 2020-06-04 12:27 | 2020-06-04 13:01 | 0:34 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ishurdi | Ishurdi-Natore 132 kV line-1 | 2020-06-04 16:53 | 2020-06-04 17:07 | 0:14 | T | Tripped showing CSW,CAT ,CD signal | 0 | 0 | No interruption
| Ishurdi-Natore 132 kV line-2 | 2020-06-04 20:08 | 2020-06-04 20:40 | 0:32 | T |  | 0 | 0 | No interruption
Jashore | Jashore-Noapara 132 kV line-1 | 2020-06-05 11:33 | 2020-06-05 12:59 | 1:26 | T | Tripped showing dist. relay | 253 | 362.6333 | Power interruption
| Jashore-Noapara 132 kV line-2 | 2020-06-05 11:33 | 2020-06-05 13:00 | 1:27 | T
Baghabari | Baghabari-Ishurdi 132 kV line | 2020-06-06 03:00 | 2020-06-06 03:35 | 0:35 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
Ishurdi | Ishurdi-Bheramara 132 kV line-1 | 2020-06-10 04:31 | 2020-06-10 04:46 | 0:15 | T |  | 0 | 0 | No interruption
Baghabari | Baghabari-Shahjadpur 132 kV line-1 | 2020-06-11 20:23 | 2020-06-11 21:03 | 0:40 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
| Baghabari-Shahjadpur 132 kV line-2 | 2020-06-11 20:23 | 2020-06-11 20:23 | 0:00 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Bharamara | Bharamara HVDC pole 1 | 2020-06-11 21:36 | 2020-06-12 04:39 | 7:03 | T | Tripped showing external protection trip | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ghorashal 230 kV line-2 | 2020-06-14 09:00 | 2020-06-14 12:14 | 3:14 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Pabna | Pabna-Ishurdi 132 kV line | 2020-06-23 10:19 | 2020-06-23 10:51 | 0:32 | T | Tripped showing E/F. relay | 90 | 48 | Power interruption
| Pabna-Shahjadpur 132 kV line | 2020-06-23 10:19 | 2020-06-23 11:51 | 1:32 | T | Tripped showing dist. relay
Ishurdi | Ishurdi-Bheramara 132 kV line-1 | 2020-06-26 16:16 | 2020-06-27 13:20 | 21:04 | T | Tripped showing dist.Y.CAT.CASCD signal | 0 | 0 | No interruption
|  |  | Total : | 44:29 |  | Unserved Energy: |  | 464.8833
Bogura Grid Circle:
Barapukuria S/S | Barapukuria S/S-Barapukuria P/S 230 kV line-2 | 2020-06-03 15:16 | 2020-06-03 16:10 | 0:54 | T | Tripped showing differential. relay | 0 | 0 | No interruption
Sherpur | Sherpur-Sirajganj 132 kV line-2 | 2020-06-20 13:16 | 2020-06-20 14:12 | 0:56 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Palashbari | Palashbari-Mohasthangarth 132 kV line-1 | 2020-06-24 10:18 | 2020-06-24 10:26 | 0:08 | T | Tripped showing dist relay | 0 | 0 | No interruption
Purbasadipur | Purbasadipur-Thakurgaon 132 kV line-1 &2 | 2020-06-25 02:32 | 2020-06-25 02:59 | 0:27 | T | Tripped showing dist relay | 26 | 11.7 | Power interruption
Palashbari | Palashbari-Mohasthangarth 132 kV line-1 | 2020-06-27 22:12 | 2020-06-27 22:38 | 0:26 | T | Due to CB problem | 0 | 0 | No interruption
|  |  | Total : | 2:51 |  | Unserved Energy: |  | 11.7
Others :
Matuail | Matuail-Siddhirganj 132 kV line | 2020-06-02 13:58 | 2020-06-02 15:21 | 1:23 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Ullon | Ullon-Dhanmondi 132 kV line-2 | 2020-06-16 14:43 | 2020-06-16 15:07 | 0:24 | T | Tripped showing dist relay | 0 | 0 | No interruption
Haripur | Haripur-Ullon 132 kV line | 2020-06-17 04:19 |  |  | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
| Haripur-Ullon 132 kV line | 2020-06-17 08:10 | 2020-06-17 16:20 | 8:10 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Matuail | Matuail-Siddhirganj 132 kV line | 2020-06-23 10:29 | 2020-06-23 10:40 | 0:11 | T | Tripped showing O/C relay | 78 | 14.3 | Power interruption
|  |  | Total : | 10:08 |  |  |  | 14.3
Total outage period of Sub-station Equipment : |  |  |  | 309:39 | Hours |  |  | Executive Engineer
T = Tripping | [7 empty] | Information Management Division
E/O = Emergency Outage | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/3 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:June 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Uttara | 132/33 kV Transformer-GT2 | 2020-06-02 11:32 | 2020-06-02 16:03 | 4:31 | S/O | Due to C/M work | 7 | 31.6167 | Power interruption
Jamalpur | 132/33 kV Transformer-T4 | 2020-06-06 07:01 | 2020-06-06 10:32 | 3:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | 132/33 kV Transformer-T1 | 2020-06-06 08:29 | 2020-06-06 08:56 | 0:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformers-T1,T2 & T3 |  | 2020-06-06 22:37 |  | S/O | After maintenance work | 0 | 0 | No interruption
Jamalpur | 132 kV Bus-A | 2020-06-07 08:35 | 2020-06-07 15:20 | 6:45 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-06-08 07:40 | 2020-06-08 10:03 | 2:23 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-06-08 10:30 | 2020-06-08 11:48 | 1:18 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2020-06-08 11:54 | 2020-06-08 12:42 | 0:48 | S/O | Due to D/W work | 0 | 0 | No interruption
Uttara | 132/33 kV Transformer-T3 | 2020-06-09 09:52 | 2020-06-09 09:52 | 0:00 | S/O | Due to fire protcetion work | 0 | 0 | No interruption
Kaliakoir | 400/132 kV Transformer-T2 | 2020-06-09 05:41 | 2020-06-09 06:48 | 1:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132 kV Bus-2 | 2020-06-09 06:27 | 2020-06-09 18:56 | 12:29 | S/O | Due to bus reconductoring work | 0 | 0 | No interruption
| 132 kV main Bus | 2020-06-12 05:27 | 2020-06-12 09:25 | 3:58 | S/O | Due to D/W work | 20 | 79.3333 | Power interruption
| 132/33 kV Transformers-T1,& T2 | 2020-06-12 08:11 | 2020-06-12 10:00 | 1:49 | S/O | Due to D/W work | 0 | 0 | No interruption
Kaliakoir | 230 kV Bus | 2020-06-12 17:56 | 2020-06-12 18:26 | 0:30 | S/O | Due to removing kite | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformers-T1& T3 | 2020-06-13 06:03 | 2020-06-13 08:20 | 2:17 | S/O | Due to D/W work | 25 | 57.0833 | Power interruption
| 132 kV Bus-2 | 2020-06-13 06:03 | 2020-06-13 08:09 | 2:06 | S/O | Due to changing work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T1 | 2020-06-13 16:05 | 2020-06-13 16:35 | 0:30 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2020-06-14 09:05 | 2020-06-14 13:52 | 4:47 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2020-06-14 13:58 | 2020-06-14 19:20 | 5:22 | S/O | Due to bus upgradation work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-06-15 09:32 | 2020-06-15 10:14 | 0:42 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-06-15 13:11 | 2020-06-15 15:15 | 2:04 | S/O | Due to D/W work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T2 | 2020-06-16 05:10 | 2020-06-16 16:35 | 11:25 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV Bus-2 | 2020-06-16 07:20 | 2020-06-16 07:26 | 0:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | 132 kV(New) Bus-2 |  | 2020-06-17 11:32 |  |  | New connection
Agargaon | 132/33 kV Transformer-T1 | 2020-06-20 07:45 | 2020-06-20 07:45 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Uttara | 132/33 kV Transformer-T3 |  | 2020-06-24 13:44 |  |  | After maintenance work | 0 | 0 | No interruption
Saver | 132/33 kV Transformer-T1 | 2020-06-25 06:37 | 2020-06-25 08:18 | 1:41 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 |  | 2020-06-25 08:18 |  |  | After maintenance work | 0 | 0 | No interruption
Kabirpur | 132 kV reserve Bus | 2020-06-26 05:40 | 2020-06-26 07:46 | 2:06 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2020-06-26 05:29 | 2020-06-26 08:17 | 2:48 | S/O | Due to D/W work | 0 | 0 | No interruption
Saver | 132/33 kV Transformer-T1 | 2020-06-26 06:01 | 2020-06-26 08:33 | 2:32 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-06-26 10:41 | 2020-06-26 12:01 | 1:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Dhamrai | 132/33 kV Transformer-T1 & 33 kV Bus | 2020-06-26 08:35 | 2020-06-26 12:08 | 3:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Saver | 132/33 kV Transformer-T1 | 2020-06-27 06:07 | 2020-06-27 08:03 | 1:56 | S/O | Due to B-phase HT bushing problem | 0 | 0 | No interruption
Kabirpur | 132 kV reserve Bus | 2020-06-28 09:41 | 2020-06-28 16:16 | 6:35 | S/O | Due to replacement work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-06-28 06:24 | 2020-06-28 09:40 | 3:16 | S/O |  | 0 | 0 | No interruption
|  |  | Total : | 94:42 |  | Unserved Energy: |  | 168.0333
Dhaka (South) Grid Circle :
Munshiganj | 33 kV Bus-1 | 2020-06-06 08:22 | 2020-06-06 10:42 | 2:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | 132/33 kV Transformer-T1 | 2020-06-16 07:17 | 2020-06-16 11:04 | 3:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur 230 kV Bus-1 | 2020-06-17 07:39 | 2020-06-20 17:34 |  | S/O | Due to D/W work | 0 | 0 | No interruption
Rampura | 230/132 kV Transformer-ATR01 |  | 2020-06-17 15:17 |  |  | New connection | 0 | 0 | No interruption
Hasnabad | 132/33 kV Transformer-T1 |  | 2020-06-18 18:24 |  | S/O | After maintenance work | 0 | 0 | No interruption
Haripur | Haripur 230 kV Bus-1 |  | 2020-06-20 17:34 |  | S/O | After maintenance work | 0 | 0 | No interruption
| Haripur 230 kV Bus-1 | 2020-06-21 07:48 | 2020-06-26 19:32 |  | S/O | Due to D/W work | 0 | 0 | No interruption
Madanganj | 132/33 kV Transformer-T1 | 2020-06-21 11:27 | 2020-06-21 14:51 | 3:24 | S/O | Due to replacement work | 0 | 0 | No interruption
Munshiganj | 132/33 kV Transformer-T1 | 2020-06-22 14:17 | 2020-06-22 18:01 | 3:44 | S/O | Due to Tan-Delta Test | 0 | 0 | No interruption
Siddhirganj | 132/33 kV Transformer-T2 | 2020-06-23 07:11 | 2020-06-23 07:40 | 0:29 | S/O | Due to C/M work | 15 | 7.25 | Power interruption
Hasnabad | 230/132 kV Transformer-T03 | 2020-06-25 09:30 | 2020-06-25 21:36 | 12:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Sonargaon | 132/33 kV Transformer-T1 | 2020-06-27 07:05 | 2020-06-27 07:45 | 0:40 | S/O | Due to CB maintenance work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-06-27 07:46 | 2020-06-27 08:13 | 0:27 | S/O | Due to CB maintenance work | 0 | 0 | No interruption
Haripur | Haripur 230 kV Bus-2 | 2020-06-28 07:21 | 2020-07-01 10:43 | 75:22 | S/O | Due to D/W work | 0 | 0 | No interruption
Siddhirganj | 230/132 kV Transformer-T02 | 2020-06-29 12:34 | 2020-06-29 15:09 | 2:35 | S/O | Due to high temperature | 0 | 0 | No interruption
|  |  | Total : | 104:54 |  | Unserved Energy: |  | 7.25
Page: 2/3 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:June 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Chattogram Grid Circle :
Rangamati | 132/33 kV Transformer-T1 | 2020-06-01 09:17 | 2020-06-01 17:03 | 7:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Kulshi | 132/33 kV Transformer-T1 | 2020-06-03 10:30 | 2020-06-03 11:50 | 1:20 | S/O | Due to 33 kV loop maintenance | 30 | 40 | Power interruption
Halishahar | 33 kV Bus | 2020-06-04 10:13 | 2020-06-04 12:09 | 1:56 | S/O | Due to 33 kV cable fault | 60 | 116 | Power interruption
Madunaghat | 132/33 kV Transformer-T2 | 2020-06-22 08:32 | 2020-06-22 11:38 | 3:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Chanraghona | 132/33 kV Transformer-T2 | 2020-06-28 07:05 | 2020-06-28 08:36 | 1:31 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 15:39 |  | Unserved Energy : |  | 156
Cumilla Grid Circle :
Chowmuhani | 132/33 kV Transformer-T2 | 2020-06-05 06:40 | 2020-06-05 10:18 | 3:38 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 & 33 kV Bus | 2020-06-09 23:30 | 2020-06-10 00:30 | 1:00 | S/O | Due to maintenance work | 40 | 40 | Power interruption
Sreemongal | 132/33 kV Transformers-T2 | 2020-06-22 10:50 | 2020-06-22 11:13 | 0:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Chowmuhani | 132/33 kV Transformer-T1 | 2020-06-24 06:30 | 2020-06-24 11:35 | 5:05 | S/O | Due to C/M work | 25 | 127.0833 | Power interruption
Cumilla(S) | 132/33 kV Transformer-T3 |  | 2020-06-29 10:12 |  |  | After maintenance work | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2020-06-29 11:06 | 2020-06-29 12:54 | 1:48 | S/O | Due to protection test | 0 | 0 | No interruption
|  |  | Total : | 11:54 |  | Unserved Energy : |  | 167.0833
Khulna Grid Circle :
Khulna© | 132/33 kV Transformer-T1 | 2020-06-03 15:51 | 2020-06-03 16:54 | 1:03 | S/O | Due to CT replacement work at 33 kV side | 8 | 8.4 | Power interruption
Barishal | 132/33 kV Transformer-T2 | 2020-06-05 06:03 | 2020-06-05 07:03 | 1:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna © | 132 kV Bus-B | 2020-06-06 07:24 | 2020-06-08 18:44 | 59:20 | S/O | Due to conductor chanege | 0 | 0 | No interruption
Barishal | 132 kV main Bus | 2020-06-12 16:57 | 2020-06-12 17:03 | 0:06 | S/O | Due to replacement work | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T2 | 2020-06-12 10:07 | 2020-06-12 10:45 | 0:38 | S/O | Due to 33 kV CB problem | 0 | 0 | No interruption
Bhandaria | 132/33 kV Transformer-T2 | 2020-06-14 15:02 | 2020-06-14 15:16 | 0:14 | S/O | Due to maintenance work | 0 | 0 | No interruption
Barishal | 132/33 kV Transformer-T1 | 2020-06-18 10:18 | 2020-06-18 11:49 | 1:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T3 | 2020-06-18 13:10 | 2020-06-18 15:14 | 2:04 | S/O | Due to 33 kV feeder maintenance | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 |  | 2020-06-23 16:19 |  |  | After maintenance work | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T1 |  | 2020-06-25 11:45 |  |  | After maintenance work | 0 | 0 | No interruption
Bhandaria | 132/33 kV Transformer-T1 | 2020-06-27 07:11 | 2020-06-27 18:03 | 10:52 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-06-30 08:08 | 2020-06-30 13:06 | 4:58 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 81:46 |  | Unserved Energy : |  | 8.4
HVDC Grid Circle :
Bottail | 132/33 kV Transformer-T2 | 2020-06-04 22:21 | 2020-06-04 22:51 | 0:30 | S/O | Due to abnormal sound | 0 | 0 | No interruption
Baghabari | 230/132 kV Transformer-T01 | 2020-06-04 08:35 | 2020-06-04 14:55 | 6:20 | S/O | Due to temperature high at R-phase CT | 0 | 0 | No interruption
Baghabari | 132 kV Bus-1 | 2020-06-05 08:25 | 2020-06-05 12:10 | 3:45 | S/O | Due to replacement work | 0 | 0 | No interruption
Bottail | 132/33 kV Transformer-T1 | 2020-06-06 16:22 | 2020-06-06 22:03 | 5:41 | S/O | Due to D/W work | 0 | 0 | No interruption
Baghabari | 230/132 kV Transformer-T01 |  | 2020-06-10 16:35 |  | S/O | After maintenance work | 0 | 0 | No interruption
| 230/132 kV Transformer-T02 | 2020-06-10 17:18 | 2020-06-10 21:27 | 4:09 | S/O | Due to charging at Y-phase spare bank | 0 | 0 | No interruption
Bheramara HVDC | Bheramara HVDC-Block -1 | 2020-06-19 06:16 | 2020-06-19 11:20 | 5:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Kustia | 132 kV Bus-A & B | 2020-06-19 06:35 | 2020-06-19 14:36 | 8:01 | S/O | Due to D/W work | 120 | 30 | Power interruption 06:35 to 6:50
Bottail | 132 kV Bus | 2020-06-20 06:39 | 2020-06-20 15:38 | 8:59 | S/O | Due to D/W work | 160 | 42.6667 | Power interruption 06:39 to 6:55
Baghabari | 132 kV Bus-A | 2020-06-24 13:50 | 2020-06-24 17:30 | 3:40 | S/O | Due to D/W work | 0 | 0 | No interruption
Bottail | 132 kV Bus | 2020-06-26 06:17 | 2020-06-26 12:49 | 6:32 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132 kV Bus | 2020-06-27 06:52 | 2020-06-27 14:16 | 7:24 | S/O | Due to conductor change | 232 | 30.9333 | Power interruption 06:52 to 7:00
|  |  | Total : | 60:05 |  | Unserved Energy : |  | 103.6
Bogura Grid Circle:
Barapukuria | 132/33 kV Transformer-T3 | 2020-06-03 20:50 | 2020-06-03 22:08 | 1:18 | S/O | Due to C/M work | 10 | 13 | Power interruption
Palashbari | 132/33 kV Transformer-T4 | 2020-06-04 14:55 | 2020-06-04 16:50 | 1:55 | S/O | Due to 33 kV Bus maintenance | 11 | 21.0833 | Power interruption
Rajshahi | 132/33 kV Transformer-T3 | 2020-06-07 07:02 | 2020-06-07 11:24 | 4:22 | S/O | Due to replacement work | 25 | 109.1667 | Power interruption
| 230/132 kV Transformer-T01 | 2020-06-07 10:40 | 2020-06-07 11:18 | 0:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Ruppur | 132/33 kV Transformer-T2 | 2020-06-07 13:44 | 2020-06-07 14:24 | 0:40 | S/O | Due to measuring Earth resistance | 0 | 0 | No interruption
Shariatpur | 132/33 kV Transformer-T2 | 2020-06-10 07:22 | 2020-06-10 09:35 | 2:13 | S/O | Due to 33 kV feeder maintenance | 24 | 53.2 | Power interruption
Rangpur | 33 kV full Bus | 2020-06-12 06:10 | 2020-06-12 16:30 | 10:20 | S/O | Due to D/W work | 100 | 1033.3333 | Power interruption
Page: 3/3 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:June 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle:
Rangpur | 33 kV bus section -1,2 | 2020-06-13 06:10 | 2020-06-13 16:10 | 10:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| 33 kV Bus-1& 2 | 2020-06-14 06:20 | 2020-06-14 12:02 | 5:42 | S/O | Due to D/W work | 90 | 513 | Power interruption
C.nawabganj | 132/33 kV Transformer-T2 | 2020-06-14 10:23 | 2020-06-14 12:02 | 1:39 | S/O | Due to C/M work | 0 | 0 | No interruption
Natore | 132/33 kV Transformers-T1 & T2 & Bus33 kV | 2020-06-19 06:08 | 2020-06-19 09:14 | 3:06 | S/O | Due to D/W work | 45 | 139.5 | Power interruption
Rajshahi | 132 kV main Bus | 2020-06-19 05:04 | 2020-06-19 08:41 | 3:37 | S/O | Due to C/M work | 90 | 325.5 | Power interruption
Natore | 132/33 kV Transformer-T4 | 2020-06-19 10:37 | 2020-06-19 16:58 | 6:21 | S/O | Due to D/W work | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformer-T3 & 33 kV Bus | 2020-06-26 08:50 | 2020-06-26 10:40 | 1:50 | S/O | Due to C/M work | 22 | 40.3333 | Power interruption
Natore | 132/33 kV Transformer-T4 | 2020-06-29 11:01 | 2020-07-14 16:38 | 365:37 | S/O | Due to Oil centrifuging | 0 | 0 | No interruption
|  |  | Total : | 419:18 |  | Unserved Energy : |  | 2248.1167
Others :
Bashundhara | 132/33 kV Transformer-GT1 | 2020-06-17 10:40 | 2020-06-24 17:54 | 175:14 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total | 175:14 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 963:32 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/3 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:June 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Jamalpur | Jamalpur-Mymensingh 132 kV line-1 | 2020-06-06 06:31 | 2020-06-06 17:59 | 11:28 | S/O | Due to C/M work | 0 | 0 | No interruption
| Jamalpur-Jamalpur 95 P/S 132 kV line | 2020-06-06 06:35 | 2020-06-06 18:05 | 11:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-1 | 2020-06-07 08:09 | 2020-06-07 14:30 | 6:21 | S/O | Due to Bus up gradation work | 0 | 0 | No interruption
Jamalpur | Jamalpur-UMPL 132 line-1 | 2020-06-08 07:33 | 2020-06-08 10:02 | 2:29 | S/O | Due to D/W work | 0 | 0 | No interruption
| Jamalpur-UMPL 132 line-2 | 2020-06-08 10:35 | 2020-06-08 12:24 | 1:49 |  |  | 0 | 0 | No interruption
Dhamrai | Dhamrai-Kaliakoir 132 kV line-2 | 2020-06-08 07:12 | 2020-06-08 17:57 | 10:45 | S/O | Due to E/W work | 0 | 0 | No interruption
Jamalpur S/S | Jamalpur S/S-Jamalpur United 132 kV line-2 | 2020-06-08 10:35 | 2020-06-10 12:24 | 49:49 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-2 | 2020-06-08 12:39 | 2020-06-08 15:17 | 2:38 | S/O | Due to D/W work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Jamalpur 95 P/S 132 kV line | 2020-06-08 14:43 | 2020-06-08 16:16 | 1:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-1 | 2020-06-08 15:20 | 2020-06-08 16:26 | 1:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | Tangail-RPCL 132 kV line-2 |  | 2020-06-08 18:42 |  | S/O | After maintenance work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV line-2 | 2020-06-08 07:15 | 2020-06-08 07:15 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV line-1 & 2 | 2020-06-09 11:11 | 2020-06-09 14:01 | 2:50 | S/O | Due to D/W work | 50 | 141.6667 | Power interruption
Aminbazar | Aminbazar-Basila P/S 132 kV line | 2020-06-10 09:04 | 2020-06-10 19:54 | 10:50 | S/O | Due to OPGW work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-1 |  | 2020-06-11 02:20 |  | S/O | After maintenance work | 0 | 0 | No interruption
| Mymensingh-Kishoreganj 132 kV line-2 |  | 2020-06-11 02:23 |  | S/O |  | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV line-2 | 2020-06-11 07:53 | 2020-06-11 18:40 | 10:47 | S/O | Due to OPGW work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-2 | 2020-06-11 14:40 | 2020-06-11 15:10 | 0:30 | S/O | Due to removing kite | 0 | 0 | No interruption
Kabirpur | Kabirpur-Tongi 132 kV line-1 | 2020-06-12 08:15 | 2020-06-12 11:52 | 3:37 | S/O | Due to D/W work | 0 | 0 | No interruption
| Kabirpur-Manikganj 132 kV line-1 & 2 | 2020-06-12 10:10 | 2020-06-12 11:52 | 1:42 | S/O | Due to D/W work | 0 | 0 | No interruption
Jamalpur | Jamalpur-UMPL 132 line-1 | 2020-06-13 15:39 | 2020-06-13 16:59 | 1:20 | S/O | Due to loop changing | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-1 | 2020-06-14 08:05 | 2020-06-14 12:20 | 4:15 | S/O | Due to D/W work | 0 | 0 | No interruption
| Mymensingh-Jamalpur 132 kV line-2 | 2020-06-14 12:22 | 2020-06-14 14:35 | 2:13 | S/O | Due to D/W work | 0 | 0 | No interruption
| Mymensingh-Jamalpur 95 MW P/S 132 kV line | 2020-06-14 15:05 | 2020-06-14 16:35 | 1:30 | S/O | Due to D/W work | 0 | 0 | No interruption
| Mymensingh-Netrakona 132 kV line-1 | 2020-06-14 16:35 | 2020-06-14 17:52 | 1:17 | S/O | Due to SPS work | 0 | 0 | No interruption
| Mymensingh-Netrakona 132 kV line-2 | 2020-06-14 15:59 | 2020-06-14 17:50 | 1:51 | S/O |  | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 200 MW line-2 | 2020-06-15 11:52 | 2020-06-15 13:08 | 1:16 | S/O | Due to D/W work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Dhamrai 132 kV line-1 | 2020-06-15 11:00 | 2020-06-15 11:41 | 0:41 | S/O | Due to removing kite | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV line-1 | 2020-06-17 08:25 | 2020-06-17 16:46 | 8:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | Savar-Manikganj (160 MW) 132 kV line-2 | 2020-06-18 12:15 | 2020-06-18 13:07 | 0:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-1 | 2020-06-19 08:11 | 2020-06-19 12:19 | 4:08 | S/O | Due to D/W work | 0 | 0 | No interruption
Bhaluka | Bhaluka-Mymensingh 132 kV line-1 | 2020-06-19 10:43 | 2020-06-19 12:14 | 1:31 | S/O | Due to C/M work | 0 | 0 | No interruption
| Mymensingh-Jamalpur 132 kV line-2 | 2020-06-19 12:51 | 2020-06-19 17:14 | 4:23 | S/O | Due to D/W work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Tongi 132 kV line-1 | 2020-06-26 06:24 | 2020-06-26 07:45 | 1:21 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-1 | 2020-06-28 11:24 | 2020-06-28 12:20 | 0:56 | S/O | Due to D/W work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Dhamrai 132 kV line-2 | 2020-06-30 19:22 | 2020-06-30 21:15 | 1:53 | S/O | Due to removing kite | 0 | 0 | No interruption
|  |  | Total : | 167:32 |  | Unserved Energy: |  | 141.6667
Dhaka (South) Grid Circle :
Hasnabad | Hasnabad-Lalbagh 132 kV line | 2020-06-06 11:03 | 2020-06-06 12:53 | 1:50 | S/O | Due to replacement work | 0 | 0 | No interruption
Haripur | Haripur-Narsinghd 132 kV line | 2020-06-16 10:58 | 2020-06-16 17:16 | 6:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Shyampur | Shyampur-Meghnaghat 230 kV line-2 | 2020-06-19 23:56 | 2020-06-20 00:39 | 0:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Madanganj | Madanganj-Haripur 132 kV line | 2020-06-19 09:05 | 2020-06-19 20:43 | 11:38 | S/O | Due to replacement work | 0 | 0 | No interruption
Sonargaon | Sonargaon-Haripur 132 kV ine-1 | 2020-06-21 10:05 | 2020-06-21 11:00 | 0:55 | S/O | Due to C/M work | 0 | 0 | No interruption
| Sonargaon-Haripur 132 kV ine-2 | 2020-06-21 11:12 | 2020-06-21 12:10 | 0:58 | S/O | Due to C/M work | 0 | 0 | No interruption
| Sonargaon-Daudkandi 132 kV line-1 | 2020-06-21 12:13 | 2020-06-21 12:50 | 0:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV line-1 |  | 2020-06-21 09:50 |  | S/O | After maintenance work | 0 | 0 | No interruption
Haripur | Haripur-EGCB 132 kV Ckt & 132 kV Bus | 2020-06-21 10:37 | 2020-06-21 18:37 | 8:00 | S/O | Due to C/M work | 0 | 0 | No interruption
[7 empty] | 0 | 0 | No interruption
Page: 2/3 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:June 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (South) Grid Circle :
Haripur | Haripur-Bhulta 230 kV line-1 | 2020-06-21 08:37 | 2020-06-21 21:43 | 13:06 | S/O | Due to D/W work | 0 | 0 | No interruption
| Haripur-Bhulta 230 kV line-2 | 2020-06-22 07:34 | 2020-06-22 21:47 | 14:13 | S/O | Due to D/W work | 0 | 0 | No interruption
Sonargaon | Sonargaon-Meghna IEL 132 kV line | 2020-06-23 07:38 | 2020-06-23 11:36 | 3:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Meghaghat | Meghaghat-Haripur 132 kV line-2 | 2020-06-23 07:25 | 2020-06-23 23:02 | 15:37 | S/O | Due to D/W work | 0 | 0 | No interruption
Sonargaon | Sonargaon-Daudkandi 132 kV line-2 | 2020-06-23 11:40 | 2020-06-23 14:03 | 2:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Meghaghat | Meghaghat-Haripur 230 kV line-1 | 2020-06-24 08:07 | 2020-06-24 21:48 | 13:41 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | Haripur-HPL 360 MW 132 kV line-1 | 2020-06-25 08:12 | 2020-06-25 21:01 | 12:49 | S/O | Due to C/M work | 0 | 0 | No interruption
| Haripur-HPL 230 kV line | 2020-06-26 08:29 | 2020-06-26 21:18 | 12:49 | S/O | Due to D/W work | 0 | 0 | No interruption
Meghaghat | Meghaghat-Cumilla(N) 230 kV line-2 | 2020-06-28 08:51 | 2020-06-28 12:14 | 3:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Dutch bangla 132 kV bay | 2020-06-29 07:05 | 2020-06-29 07:05 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 122:58 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Hathazari | Hathazari-Kaptai 132 kV line-1 | 2020-06-01 08:40 | 2020-06-01 15:36 | 6:56 | S/O | Due to C/M work | 0 | 0 | No interruption
| Hathazari-Kaptai 132 kV line-2 | 2020-06-01 08:41 | 2020-06-01 15:36 | 6:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikalbaha(O) | Sikalbaha(O)-Sikalbaha(N) 132 KV line-2 | 2020-06-01 09:30 | 2020-06-01 10:48 | 1:18 | S/O | Due to C/M work | 0 | 0 | No interruption
| Sikalbaha-Shahmirpur 132 kV line-2 | 2020-06-03 10:12 | 2020-06-03 11:28 | 1:16 | S/O | Due to Oil leavel low at R-phase PT | 0 | 0 | No interruption
Rangamati | Rangamati-Khagrachari 132 kV line-2 | 2020-06-06 10:12 | 2020-06-06 12:11 | 1:59 | S/O | Due to tree trimming | 0 | 0 | No interruption
Sikalbaha(O) | Sikalbaha(O)-Sikalbaha(N) 132 KV line-1 | 2020-06-06 10:19 | 2020-06-06 13:28 | 3:09 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'xbazar 132 kV line-1 | 2020-06-12 07:14 | 2020-06-12 09:28 | 2:14 | S/O | Due to D/W work | 5 | 11.1667 | Power interruption
Kulshi | Kulshi-Halishahar 132 kV line-1 & 2 | 2020-06-13 07:30 | 2020-06-13 07:30 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'xbazar 132 kV line-1 | 2020-06-14 06:42 | 2020-06-14 08:45 | 2:03 | S/O | Due to C/M work | 20 | 41 | Power interruption
| Dohazari-Cox'xbazar 132 kV line-2 | 2020-06-16 06:33 | 2020-06-18 16:22 | 57:49 | S/O | Due to D/W work | 0 | 0 | No interruption
Madanganj | Madanganj-Sitalakyha 132 kV line | 2020-06-16 11:33 | 2020-06-16 22:43 | 11:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Halishahar | Halishahar-Rampura 132 kV line |  | 2020-06-16 11:48 |  |  | New connection | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'xbazar 132 kV line-2 | 2020-06-21 06:26 | 2020-06-23 19:51 | 61:25 | S/O | Due to D/W work | 0 | 0 | No interruption
AKSML | AKSML-Hathazari 230 kV line | 2020-06-22 08:38 | 2020-06-22 10:50 | 2:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Kulshi | Kulshi-Rampur 132 kV line | 2020-06-23 17:56 | 2020-06-23 17:58 | 0:02 | S/O | Due to relay test | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-1 | 2020-06-25 06:32 | 2020-06-27 15:02 | 56:30 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-AKSML 230 kV line | 2020-06-27 08:36 | 2020-06-27 12:14 | 3:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'xbazar 132 kV line-1 |  | 2020-06-27 15:02 |  |  | After maintenance work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV line-2 | 2020-06-27 23:21 | 2020-06-28 12:55 | 13:34 | S/O | Due to CB problem | 0 | 0 | No interruption
|  |  | Total : | 232:10 |  | Unserved Energy: |  | 52.1667
Cumilla Grid Circle :
Chandpur | Chandpur-Desh Energy 132 kV line-2 | 2020-06-07 12:25 | 2020-06-07 13:40 | 1:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2020-06-07 12:52 | 2020-06-07 13:25 | 0:33 | S/O | Due to tree trimming | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Chauddagram 132 kV line-1 | 2020-06-11 11:20 | 2020-06-11 12:22 | 1:02 | S/O | Due to removing kite | 0 | 0 | No interruption
| Cumilla(N)-Chauddagram 132 kV line-2 | 2020-06-11 12:24 | 2020-06-11 13:12 | 0:48 | S/O | Due to removing kite | 0 | 0 | No interruption
| Cumilla(N)-Daudkandi 132 kV line-2 | 2020-06-11 13:15 | 2020-06-11 14:36 | 1:21 | S/O |  | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorashal 132 kV line-2 |  | 2020-06-11 13:41 |  |  | After maintenance work | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV line-2 | 2020-06-12 10:52 | 2020-06-12 13:35 | 2:43 | S/O | Due to relay testing | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj 132 kV line | 2020-06-13 09:20 | 2020-06-13 11:28 | 2:08 | S/O | Due to C/M work | 20 | 42.6667 | Power interruption
Daudkandi | Daudkandi-Sonargaon 132 kV line-1 | 2020-06-15 11:08 | 2020-06-15 12:37 | 1:29 | S/O | Due to removing kite | 0 | 0 | No interruption
Feni | Feni-Chaddagaram 132 kV line-2 | 2020-06-15 08:43 | 2020-06-15 16:23 | 7:40 | S/O | Due to replacement work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2020-06-17 10:47 | 2020-06-17 12:09 | 1:22 | S/O | Due to removing kite | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV line-2 | 2020-06-17 10:48 | 2020-06-17 12:11 | 1:23 | S/O |  | 0 | 0 | No interruption
Ashuganj | Ashuganj-Shahjibazar 132 kV line-3 | 2020-06-17 08:24 | 2020-06-17 12:58 | 4:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Daudkandi | Daudkandi-Cumilla(N) 132 kV line-1 | 2020-06-18 10:06 | 2020-06-18 13:15 |  | S/O | Due to D/W work | 0 | 0 | No interruption
Tripura | Tripura-Cumilla(S) 132 kV line-2 | 2020-06-21 08:58 | 2020-06-21 16:31 | 7:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-S.M.NagarTripura 132 kV line | 2020-06-22 09:15 | 2020-06-22 12:48 | 3:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorashal 132 kV line-1 & 2 | 2020-06-26 09:49 | 2020-06-26 17:40 | 7:51 | S/O | Due to D/W work | 0 | 0 | No interruption
Feni | Feni-PHP-Baroierhat 132 kV line | 2020-06-30 08:46 | 2020-06-30 16:52 | 8:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorashal 132 kV line-1 | 2020-06-30 09:01 | 2020-06-30 18:59 | 9:58 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 63:19 |  | Unserved Energy: |  | 42.6667
Page: 3/3 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:June 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Khulna © | Khulna ©-Khulna(S) 132 kV line-2 | 2020-06-06 07:26 | 2020-06-06 18:28 | 11:02 | S/O | Due to C/M work | 0 | 0 | No interruption
| Khulna ©-Noapara 132 kV line-1 | 2020-06-06 07:31 | 2020-06-06 18:22 | 10:51 | S/O | Due to C/M work | 0 | 0 | No interruption
| Khulna ©-Noapara 132 kV line-2 | 2020-06-06 07:31 | 2020-06-06 18:23 | 10:52
| Khulna ©-KPCL-2 132 kV line | 2020-06-06 07:56 | 2020-06-06 18:28 | 10:32 | S/O | Due to C/M work | 0 | 0 | No interruption
Goalpara | Goalpara-Khulna© 132 kV line-1 | 2020-06-06 07:24 | 2020-06-06 18:31 | 11:07 | S/O | Due to C/M work | 0 | 0 | No interruption
| Goalpara-Khulna© 132 kV line-2 | 2020-06-06 07:24 | 2020-06-06 18:32 | 11:08 | S/O | Due to reconductoring work | 0 | 0 | No interruption
| Goalpara-Khulna© 132 kV line-1 | 2020-06-07 06:06 | 2020-06-07 17:22 | 11:16 | S/O |  | 0 | 0 | No interruption
| Goalpara-Khulna© 132 kV line-2 | 2020-06-07 06:07 | 2020-06-07 17:24 | 11:17 | S/O |  | 0 | 0 | No interruption
| Goalpara-Khulna© 132 kV line-1 | 2020-06-08 06:02 | 2020-06-08 18:48 | 12:46 | S/O |  | 0 | 0 | No interruption
| Goalpara-Khulna© 132 kV line-2 | 2020-06-08 06:03 | 2020-06-08 06:46 | 0:43 | S/O |  | 0 | 0 | No interruption
| Goalpara-Khulna© 132 kV line-1 | 2020-06-09 10:57 | 2020-06-09 14:31 | 3:34 | S/O |  | 0 | 0 | No interruption
| Goalpara-Khulna© 132 kV line-1 | 2020-06-09 14:33 | 2020-06-10 12:14 | 21:41 | S/O | Due to maintenance work | 0 | 0 | No interruption
| 132 kV Bus & associates lines | 2020-06-07 06:45 |  |  | S/O | Due to reconductoring transfer Bus | 0 | 0 | No interruption
Barishal | Barishal-Patuakhali 132 kV line | 2020-06-07 07:05 | 2020-06-07 07:06 | 0:01 | S/O | Due to D/W work | 35 | 0.58333 | Power interruption
| Barishal-Patuakhali 132 kV line | 2020-06-08 07:01 | 2020-06-08 07:12 | 0:11 | S/O | Due to D/W work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-HVDC Bheramara 230 kV line-1 |  | 2020-06-08 09:39 |  |  | After maintenance work | 0 | 0 | No interruption
Patuakhali | Patuakhali-Barishal 132 kV line | 2020-06-12 07:09 | 2020-06-12 17:03 | 9:54 | S/O | Due to D/W work | 25 | 13.75 | Power interruption 07:01 to 7:42
Barishal | Barishal-Patuakhali 132 kV line | 2020-06-13 07:01 | 2020-06-13 18:12 | 11:11 | S/O | Due to D/W work | 40 | 3.75 | Power interruption 07:01 to 7:10
Madaripur | Madaripur-Barisahal (N) 132 kV line-2 | 2020-06-13 09:17 | 2020-06-13 17:34 | 8:17 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 156:23 |  | Unserved Energy: |  | 18.0833
HVDC Grid Circle :
Bottail | Bottail-Jhenidah 132 kV line-1 | 2020-06-01 12:24 | 2020-06-01 13:22 | 0:58 | S/O | Due to remove the kite | 0 | 0 | No interruption
| Bottail-Jhenidah 132 kV line-2 | 2020-06-01 12:24 | 2020-06-01 13:23 | 0:59 | S/O |  | 0 | 0 | No interruption
Jhenidah | Jhenidah-Bottail 132 kV line-2 | 2020-06-02 11:20 | 2020-06-02 18:41 | 7:21 | S/O | Due to relay testing | 0 | 0 | No interruption
Bheramara HVDC | Bheramara HVDC-Khulna(S) 230 kV line-1 | 2020-06-05 07:08 | 2020-06-05 07:08 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Jhenidah | Jhenidah-Bottail 132 kV line-2 | 2020-06-05 11:26 | 2020-06-05 17:55 | 6:29 | S/O | Due to relay testing | 0 | 0 | No interruption
Jessore | Jessore-Noapara 132 kV line-2 | 2020-06-07 06:15 | 2020-06-07 06:52 | 0:37 | S/O | Due to replacement work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Baghabari 132 kV line P.P 132 KV ine | 2020-06-07 10:22 | 2020-06-07 11:14 | 0:52 | S/O | Due to project work | 0 | 0 | No interruption
Jashore | Jashore-Jhenidah 132 kV both line | 2020-06-08 14:14 | 2020-06-08 15:51 | 1:37 | S/O | Due to removing kite | 0 | 0 | No interruption
Baghabari | Baghabari-Ishurdi 230 kV line-1 | 2020-06-10 10:46 | 2020-06-10 21:15 | 10:29 | S/O | Due to relay testing | 0 | 0 | No interruption
| Baghabari-Shahjadpur 132 kV line-2 | 2020-06-12 09:37 | 2020-06-12 12:07 | 2:30 | S/O | Due to connect of jumper at tower#119 | 0 | 0 | No interruption
Ishurdi | Ishurdi-Bheramara 132 kV line-1 & 2 |  | 2020-06-26 13:30 |  | S/O | After maintenance work | 0 | 0 | No interruption
|  |  | Total : | 31:52 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Barapukuria | Barapukuria-Rangpur 132 kV line-2 & Bus-1 | 2020-06-07 07:39 | 2020-06-07 07:39 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangpur | Rangpur-Confidenance P.S. 132 kV line-2 | 2020-06-07 11:06 | 2020-06-07 17:20 | 6:14 | S/O | Due to relay testing | 0 | 0 | No interruption
| Rangpur-Saidpur 132 kV line-2 | 2020-06-07 13:02 | 2020-06-07 19:41 | 6:39 | S/O | Due to relay testing | 0 | 0 | No interruption
Sirajganj | Sirajganj-Shahjadpur 132 kV line | 2020-06-12 09:15 | 2020-06-12 12:10 | 2:55 | S/O | Due to jumper connect | 0 | 0 | No interruption
Bogura | Bogura-Mohasthangarth 132 kV line-2 | 2020-06-16 12:03 | 2020-06-16 12:53 | 0:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Bogura 230 kV line-2 | 2020-06-26 08:18 | 2020-06-26 11:30 | 3:12 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 19:50 |  | Unserved Energy: |  | 0
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 794:04 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:June' 2020
| Area | Previous Month (May 2020) |  |  |  | Current Month (June 2020)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 27 | 10 | 33 | 70 | 20 | 7 | 66 | 93
2 | Dhaka (South) Grid Circle. | 22 | 1 | 9 | 32 | 17 | 8 | 31 | 56
3 | Chattogram Grid Circle. | 19 | 5 | 6 | 30 | 13 | 4 | 22 | 39
4 | Cumilla Grid Circle. | 24 | 7 | 9 | 40 | 50 | 9 | 23 | 82
5 | Khulna Grid Circle. | 23 | 14 | 9 | 46 | 15 | 9 | 27 | 51
6 | Bheramara HVDC Grid Circle | 12 | 5 | 11 | 28 | 26 | 4 | 21 | 51
7 | Bogura Grid Circle. | 31 | 24 | 11 | 66 | 5 | 15 | 21 | 41
8 | Others | 6 |  |  | 6 | 6 | 3 | 1 | 10
9 | Total | 164 | 66 | 88 | 318 | 152 | 59 | 212 | 423
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:June' 2020
| Area | Previous Month (May 2020) |  |  |  | Current Month (June 2020)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 14 | 57.6 | 319.8 | 391.4 | 636.07 | 296.13 | 309.7 | 1241.9
2 | Dhaka (South) Grid Circle. | 327.93 | 0 | 0 | 327.93 | 313.12 | 112.5 | 7.25 | 432.87
3 | Chattogram Grid Circle. | 492.96 | 0 | 221.7 | 714.66 | 64.33 | 119.25 | 208.17 | 391.75
4 | Cumilla Grid Circle. | 250.4 | 12.5 | 0 | 262.9 | 541.6 |  | 209.75 | 751.35
5 | Khulna Grid Circle. | 275.6 | 72.5 | 56.67 | 404.77 | 21.17 | 323.92 | 26.48 | 371.57
6 | Bheramara HVDC Grid Circle | 39.47 | 163.33 | 182.5 | 385.3 | 482.88 | 80.8 | 103.6 | 667.28
7 | Bogura Grid Circle. | 23.75 | 529.75 | 124.58 | 678.08 | 38.63 | 531.95 | 2248.12 | 2818.7
8 | Others | Energy unserved ( MWH ) due to T: 30; Energy unserved ( MWH ) due to Total: 30; Energy unserved ( MWH ) due to T: 14.3; Energy unserved ( MWH ) due to Total: 14.3
9 | Total | 1454.11 | 835.68 | 905.25 | 3195.04 | 2112.1 | 1464.55 | 3113.07 | 6689.72
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:June' 2020
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 5 | 3 | 8 | 3 |  | 5 | 504.36
2 | Dhaka (South) | 5031.6 | 2 | 1 | 3 | 2 | 1 |  | 192.55
3 | Chattogram | 2042 | 6 | 2 | 8 | 2 | 1 | 5 | 330.65
4 | Khulna | 2434 | 10 | 1 | 11 | 2 | 4 | 5 | 338.48
5 | Bheramara (HVDC) | 2423.3 | 4 | 3 | 7 | 5 | 1 | 1 | 202.4
6 | Bogura | 3145.6 | 10 | 9 | 19 | 2 | 2 | 15 | 2807
7 | Cumilla | 2981 | 3 | 2 | 5 | 1 | 2 | 2 | 270.73
8 | Others | -
| Total | 26859.1 | [6 empty] | 4646.17
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.96%
2 | Dhaka (South) | 99.88%
3 | Chattogram | 99.95%
4 | Khulna | 99.87%
5 | Bheramara (HVDC) | 99.93% | [6 empty] | Executive Engineer
6 | Bogura | 99.67% | [6 empty] | Information Management Division
7 | Cumilla | 99.81% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:June' 2020
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | 54+15(Partial) | 2 | 1 | 3 |  | 2 | 1 | 737.54
2 | Dhaka (South) | 990.29 |  | 3 |  | 3 | 1 | 1 | 1 | 240.32
3 | Chattogram | 917 | 20+9(Partial) | 2 | 2 | 4 | 2 |  | 2 | 61.1
4 | Khulna | 1238.4 | 21 | 1 | 3 | 4 | 2 |  | 2 | 33.08
5 | Bheramara (HVDC) | 598.7 |  | 3 |  | 3 | 2 | - | 1 | 464.88
6 | Bogura | 1803.3 | 38 | 1 | - | 1 | 1 | - | - | 11.7
7 | Cumilla | 1648.16 | 17 | 4 | 1 | 5 | 1 | 2 | 2 | 480.62
7 | Others | - |  | 1 | - | 1 | 1 | - | - | 14.3
| Total | 9450.3215 | 174 | [6 empty] | 2043.54
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 99.85%
3 | Chattogram | 99.98%
4 | Khulna | 99.71%
5 | Bheramara (HVDC) | 99.73% | [7 empty] | Executive Engineer
6 | Bogura | 100% | [7 empty] | Information Management Division
7 | Cumilla | 99.62% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:June' 2020
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2020-06-18 | 13 | - | 5 | 6hour 28 min | - | - | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/2 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:June' 2020
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Kabirpur | 3 | 1:14 | 172 | 212.1333 | Due to red-hot maintenance of 132 kV bus
|  | 0:08 | 50 | 6.6667 | Due to tripping of 132/33 kV Transformers-T1 & T2
Mymensingh | 1 | 0:07 | 146 | 17.0333 | Due to tripping of 132/33 kV Transformers-T1 & T2
Savar | 1 | 0:09 | 110 | 16.5 | Due to tripping of 132/33 kV Transformer-T1
Mymensingh | 1 | 1:52 | 45 | 84 | Due to red-hot maintenance of 132/33 kV Transformer T2
Kabirpur | 1 | 0:41 | 172 | 117.5333 | Due to tripping of Kabirpur-Kaliakoir 132 kv line
Mymensingh RPCL | 1 | 0:41 | 700 | 478.3333 | Due to tripping of RPCL -Mymensingh S/S 132 kV line-1 & 2
Uttara | 1 | 4:31 | 7 | 31.6167 | Due to S/D of132/33 kV Transformer-GT2
Kabirpur |  | 3:58 | 20 | 79.3333 | Due to S/D of 132 kV main Bus
| 3 | 2:17 | 25 | 57.0833 | Due to S/D of132/33 kV Transformers-T1 & T3
|  | 2:50 | 50 | 141.6667 | Due to S/D of Kabirpur-Manikganj 132 kV line-1 & 2
Munshiganj | 1 | 0:42 | 104 | 72.8 | Due to tripping of 33 kV auxiliary Transformer-T1
Hasnabad | 1 | 0:18 | 375 | 112.5 | Due to tripping of 230/132 kV Transformers-T1, T 2 & T3
Lalbagh | 1 | 0:17 | 75 | 21.25 | Due to tripping of Lalbagh-Hasnabad 132 kV line
Sitalakhya | 2 | 2:14 | 76 | 169.7333 | Due to tripping of Sitalakhya-Madanganj 132 kV line
Madanganj |  | 0:37 | 80 | 49.3333 | Due to tripping of Madanganj-Munshiganj 132 kV line-1
Siddhirganj |  | 0:29 | 15 | 7.25 | Due to S/D of 132/33 kV Transformer-T2
Matuail | 1 | 0:11 | 78 | 14.3 | Due to tripping of Siddhirganj-Matuail132 kV line
Rangamati | 1 | 1:04 | 6 | 6.4 | Due to tripping of 132/33 kV Transformers-T1 & T2
Halishahar | 1 | 0:33 | 42 | 23.1 | Due to tripping of 132/33 kV Transformer-T1 & T3
Madunaghat |  | 0:13 | 47 | 10.1833 | Due to tripping of 132/33 kV Transformers-T1 & T2
Halishahar | 2 | 2:28 | 35 | 86.3333 | Due to red-hot maintenance of 132/33 kV Transformer T2
|  | 1:19 | 25 | 32.9167 | Due to red-hot maintenance of 132/33 kV Transformer T3
Madunaghat | 1 | 0:23 | 41 | 15.7167 | Due to tripping of 132/33 kV Transformers-T1 & T2
Dohazari | 1 | 0:09 | 24 | 3.6 | Due to tripping of Dohazari-Cox'sbazar 132 kV line-1
Ramganj | 1 | 0:04 | 80 | 5.3333 | Due to tripping of Dohazari-Cox'sbazar 132 kV line-2
Kulshi | 1 | 1:20 | 30 | 40 | Due to S/D of 132/33 kV Transformer-T1
Halishahar | 1 | 1:56 | 60 | 116 | Due to S/D of 33 kV bus
Dohazari | 2 | 2:14 | 5 | 11.1667 | Due to S/D of Dohazari-Cox'sbazar 32 kV line-1
|  | 2:03 | 20 | 41
Shahjibazar |  | 0:08 | 30 | 4 | Due to tripping of 132/33 kV Transformer-T2
Cumilla (N) | 1 | 3:56 | 24 | 94.4 | Due to tripping of 132/33 kV Transformer-T3
B.Baria | 1 | 0:45 | 7 | 5.25 | Due to red-hot maintenance of 132/33 kV Transformer T2
Srimongal | 1 | 0:43 | 247 | 177.0167 | Due to tripping of Sreemongal-fenchuganj 132 k line-1 & 2
Tripura | ! | 0:30 | 100 | 50 | Due to tripping of Tripura-Cumilla(S) 132 kV line-1
Cumilla(S) |  | 1:16 | 104 | 131.7333 | Due to tripping of Cumilla(S)-S.M nagar 132 kV line-1
| 1 | 0:36 | 132 | 79.2 | Due to tripping of Cumilla(S)-Tripura132 kV line-1
Chowmuhani | 2 | 1:00 | 40 | 40 | Due to S/D of 132/33 kV Transformer T1
|  | 5:05 | 25 | 127.0833 | Due to S/D of 132/33 kV Transformer T1
Sylhet | 1 | 2:08 | 20 | 42.6667 | Due to S/D of Sylhet-Fenchiuganj 132 kV line
Mongla | 1 | 1:42 | 14 | 23.8 | Due to red-hot maintenance of 132/33 kV Transformer T2
Gallamari | 1 | 1:26 | 30 | 43 | Due to red-hot maintenance of 132/33 kV Transformers T1 & T2
Khulna© | 1 | 0:06 | 15 | 1.5 | Due to tripping of 132/33 kV Transformer-T1,T2 & T3
Faridpur | 1 | 0:53 | 50 | 44.1667 | Due to red-hot maintenance of 132/33 kV Transformer T1
Gopalganj |  | 0:36 | 76 | 45.6 | Due to tripping of 132/33 kV Transformers-T1 & T2
Bagerhat | 1 | 0:42 | 73 | 51.1 | Due to red-hot maintenance of 132/33 kV Transformer T1& T3
Faridpur | 1 | 0:39 | 25 | 16.25 | Due to red-hot maintenance of 33 kV Bus
Madaripur | 1 | 0:07 | 40 | 4.6667 | Due to tripping of 132/33 kV Transformers-T1 & T2
Gallamari | 1 | 1:20 | 30 | 40 | Due to red-hot maintenance of 132/33 kV Transformer T2
Bagerhat | 1 | 2:30 | 24 | 60 | Due to red-hot maintenance of 132/33 kV Transformer T3
Khulna(S) | 1 | 0:30 | 38 | 15 | Due to tripping of Khulna(S)-Gallamari 132 kV line-1 & 2
Khulna© | 1 | 1:03 | 8 | 8.4 | Due to S/D of 132/33 kV Transformer T1
Barishal | 1 | 0:01 | 35 | 0.58333 | Due to S/D of Barisal-Patuakhali 132 kV line
Patuakhali | 1 | 9:54 | 25 | 13.75 | Due to S/D of Patuakhali-Barisal 132 kV line
Barishal | 1 | 11:11 | 40 | 3.75 | Due to S/D of Barisal-Patuakhali 132 kV line
Benapole | 1 | 0:10 | 30 | 5 | Due to tripping of 132/33 kV Transformers-T1 & T2
Bottail | 1 | 1:26 | 48 | 68.8 | Due to red-hot maintenance of 132/33 kV Transformer T2
Jhenidah | 1 | 0:13 | 60 | 13 | Due to tripping of 132/33 kV Transformers-T1 & T2
Shahjadpur | 1 | 0:36 | 20 | 12 | Due to red-hot maintenance of 132/33 kV Transformer T4
Bharamara | 1 | 0:15 | 217 | 54.25 | Due to tripping of Bheramara-Bottail 132 kV line-1 & 2
Jashore | 1 | 1:26 | 253 | 362.6333 | Due to tripping of Jashore-Noapara 132 kV line-1 & 2
Pabna | 1 | 0:32 | 90 | 48 | Due to tripping of Pabna-Ishurdi 132 kV line
Kustia | 1 | 0:15 | 120 | 30 | Due to S/D of 132 kV Bus-A & B
Bottail | 1 | 0:16 | 160 | 42.6667 | Due to S/D of 132 kV Bus
| 1 | 0:08 | 232 | 30.9333
Thakurgaon |  | 0:08 | 40 | 5.3333 | Due to tripping of 132/33 kV Transformers-T1 & T2
Bogura | 1 | 1:55 | 45 | 86.25 | Due to red-hot maintenance of 132/33 kV Transformer T1
| 1 | 1:20 | 40 | 53.3333
Barapukuria | 1 | 1:04 | 25 | 26.6667 | Due to red-hot maintenance of 132/33 kV Transformer T4
Rangpur | 1 | 2:05 | 60 | 125 | Due to red-hot maintenance of 132/33 kV Transformers T1 & T2
Bogura | 1 | 0:18 | 72 | 21.6 | Due to tripping of 132/33 kV Transformers-T1 & T2
Page: 2/2 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:June' 2020
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Rangpur | 1 | 0:42 | 100 | 70 | Due to red-hot maintenance of 132/33 kV Transformers T1 & T2
Purbasadipur | 1 | 1:39 | 48 | 79.2 | Due to red-hot maintenance of 132/33 kV Transformer T1
Rangpur | 1 | 1:30 | 45 | 67.5 | Due to red-hot maintenance of 33 kV bus
Purbasadipur | 2 | 0:48 | 30 | 24 | Due to red-hot maintenance of 132/33 kV Transformer T1
|  | 0:27 | 26 | 11.7 | Due to tripping of Purbasadipur-Thakurgaon132 kV line-1 & 2
Barapukuria | 1 | 1:18 | 10 | 13 | Due to S/D of 132/33 kV Transformer T3
Palashbari | 1 | 1:55 | 11 | 21.0833 | Due to S/D of 132/33 kV Transformer T4
Rajshahi |  | 4:22 | 25 | 109.1667 | Due to S/D of 132/33 kV Transformer T3
Shariatpur | 1 | 2:13 | 24 | 53.2 | Due to S/D of 132/33 kV Transformer T2
Rangpur | 2 | 10:20 | 100 | 1033.3333 | Due to S/D of 33 kV full Bus
|  | 5:42 | 90 | 513 | Due to S/D of 33 kV Bus-1 & 2
Natore | 1 | 3:06 | 45 | 139.5 | Due to S/D of 132/33 kV Transformers T1 & T2
Rajshahi | 1 | 3:37 | 90 | 325.5 | 132 kV main Bus
Rajshahi | 1 | 1:50 | 22 | 40.3333 | Due to S/D of 132/33 kV Transformer T3
| Total Unserved energy : |  |  | 6689.7167 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:June'2020
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 130 | 16 | 2020-06-01 | 12:00
2 | Munsiganj | 128 | 9 | 2020-06-01 | 21:00
3 | Sonargaon | 79 | 10 | 2020-06-01 | 1:00
4 | Shyampur | 210 | 20 | 2020-06-01 | 10:00
5 | Bhulta | 195 | 24 | 2020-06-01 | 23:00
6 | Madanganj | 60 | 27 | 2020-06-01 | 22:00
7 | Shitalakhya | 115 | 16 | 2020-06-01 | 10:00
8 | Rahim steel | 28 | 3 | 2020-06-01 | 16:00
9 | Matuail | 90 | 8 | 2020-06-01 | 10:00
10 | Ghorasal | 79 | 9 | 2020-06-01 | 21:00
11 | Narsingdi | 168 | 25 | 2020-06-01 | 22:00
12 | Haripur (SBU) | 109 | 30 | 2020-06-01 | 14:00
13 | Ullon | 63 | 2 | 2020-06-01 | 19:00
14 | Hasnabad | 205 | 24 | 2020-06-01 | 21:00
15 | Magbazar | 110 | 9 | 2020-06-01 | 14:00
16 | Maniknagar | 116 | 9 | 2020-06-01 | 12:00
17 | Bangabhaban | 32 | 2 | 2020-06-01 | 12:00
18 | Narinda | 104 | 15 | 2020-06-01 | 11:00
19 | Dhanmondi | 163 | 28 | 2020-06-01 | 13:00
20 | Lalbag | 91 | 16 | 2020-06-01 | 15:00
21 | Madartek | 73 | 25 | 2020-06-01 | 23:00
22 | Dhaka University | - | - | 2020-06-01 | -
23 | Mirpur | 101 | 24 | 2020-06-01 | 14:00
24 | Kalyanpur | 90 | 24 | 2020-06-01 | 19:00
25 | Gulshan | 130 | 25 | 2020-06-01 | 15:00
26 | Uttara | 86 | 25 | 2020-06-01 | 14:00
27 | Uttara(new) | 36 | 15 | 2020-06-01 | 14:00
28 | Kamrangirchar | 88 | 23 | 2020-06-01 | 12:00
29 | Savar | 143 | 22 | 2020-06-01 | 16:00
30 | Bhasantec | 149 | 25 | 2020-06-01 | 13:00
31 | Agargaon | 66 | 25 | 2020-06-01 | 13:00
32 | Satmosjid | 125 | 9 | 2020-06-01 | 15:00
33 | Tongi | 147 | 25 | 2020-06-01 | 11:00
34 | Kabirpur | 235 | 15 | 2020-06-01 | 15:00
35 | Basundhara | 137 | 16 | 2020-06-01 | 13:00
36 | Manikganj | 76 | 9 | 2020-06-01 | 22:00
37 | Joydevpur | 178 | 13 | 2020-06-01 | 21:00
38 | New Tongi | 107 | 24 | 2020-06-01 | 15:00
39 | Kodda | 236 | 23 | 2020-06-01 | 14:00
40 | Dhamrai | 98 | 10 | 2020-06-01 | 20:00
41 | Rajendrapur | 96 | 14 | 2020-06-01 | 21:00
42 | Valuka | 102 | 30 | 2020-06-01 | 21:00
43 | Tangail | 202 | 7 | 2020-06-01 | 21:00
44 | Mymensing | 235 | 9 | 2020-06-01 | 23:00
45 | Kishorganj | 149 | 9 | 2020-06-01 | 23:00
46 | Netrokona | 138 | 8 | 2020-06-01 | 22:00
47 | Jamalpur | 143 | 9 | 2020-06-01 | 22:00
48 | Sherpur | 120 | 8 | 2020-06-01 | 20:00
49 | Srimongal | 54 | 25 | 2020-06-01 | 21:00
50 | Shahjibazar | 115 | 9 | 2020-06-01 | 21:00
51 | Fenchuganj | 50 | 9 | 2020-06-01 | 21:00
52 | Kulawara | 49 | 25 | 2020-06-01 | 19:00
53 | Sylhet | 123 | 9 | 2020-06-01 | 22:00
54 | Chatak | 32 | 16 | 2020-06-01 | 19:30
55 | Sunamganj | 47 | 25 | 2020-06-01 | 21:00
56 | Bianibazar | 63 | 9 | 2020-06-01 | 22:00
57 | Cumilla (S) | 182 | 9 | 2020-06-01 | 21:00
58 | Cumilla(N) | 129 | 28 | 2020-06-01 | 19:30
59 | Chandpur | 108 | 9 | 2020-06-01 | 21:00
60 | Feni | 124 | 9 | 2020-06-01 | 19:30
61 | Chowmuhani | 176 | 10 | 2020-06-01 | 22:00
62 | Ashuganj | 66 | 25 | 2020-06-01 | 23:00
63 | Daudkandi | 147 | 24 | 2020-06-01 | 22:00
64 | B.Baria | 158 | 24 | 2020-06-01 | 21:00
65 | Ramganj | 116 | 9 | 2020-06-01 | 23:00
66 | Chaddagram | 43 | 29 | 2020-06-01 | 16:00
67 | PHP | 11 | 21 | 2020-06-01 | 18:30
68 | Madanhat | 58 | 8 | 2020-06-01 | 11:00
69 | Hathazari | 102 | 24 | 2020-06-01 | 19:30
70 | Khulshi | 195 | 30 | 2020-06-01 | 15:00
71 | Halishahar | 144 | 13 | 2020-06-01 | 10:00
Page: 2/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:June'2020
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
72 | Baraulia | 152 | 28 | 2020-06-01 | 1:00
73 | Sikalbaha | 28 | 8 | 2020-06-01 | 10:00
74 | Dohazari | 100 | 25 | 2020-06-01 | 20:00
75 | Cox'sbazar | 98 | 10 | 2020-06-01 | 20:00
76 | Chandraghona | 32 | 15 | 2020-06-01 | 14:00
77 | Kaptai | 4.5 | 9 | 2020-06-01 | 19:00
78 | A. Khaer Stl. | 23 | 11 | 2020-06-01 | 11:00
79 | Bakulia | 104 | 23 | 2020-06-01 | 11:00
80 | Julda | 22 | 21 | 2020-06-01 | 9:00
81 | TK chemical | 25.2 | 20 | 2020-06-01 | 21:00
82 | Modern Steel | 18 | 16 | 2020-06-01 | 12:00
83 | Shahmirpur | 29 | 24 | 2020-06-01 | 23:00
84 | Khagrachhari | 24 | 8 | 2020-06-01 | 19:00
85 | Matarbari | 35 | 6 | 2020-06-01 | 21:00
86 | Baroiar Hat | 38 | 9 | 2020-06-01 | 19:30
87 | Rangamati | 12 | 10 | 2020-06-01 | 19:30
88 | Abul Khair 230 | 190 | 10 | 2020-06-01 | 15:00
89 | BSRM | 159 | 16 | 2020-06-01 | 13:00
90 | GPH Ispat | 71 | 4 | 2020-06-01 | 17:00
91 | Goalpara | 33 | 25 | 2020-06-01 | 23:00
92 | Central s/s | 93 | 9 | 2020-06-01 | 20:00
93 | Noapara | 68 | 21 | 2020-06-01 | 20:00
94 | Jashore | 124 | 3 | 2020-06-01 | 22:00
95 | Benapol | 50 | 24 | 2020-06-01 | 22:00
96 | Jhenidah | 111 | 30 | 2020-06-01 | 21:00
97 | Bottail | 137 | 24 | 2020-06-01 | 21:00
98 | G.K Project | 61 | 3 | 2020-06-01 | 21:00
99 | Faridpur | 197 | 24 | 2020-06-01 | 22:00
100 | Madaripur | 105 | 25 | 2020-06-01 | 22:00
101 | Sariatpur | 70 | 24 | 2020-06-01 | 21:00
102 | Gopalganj | 103 | 9 | 2020-06-01 | 21:00
103 | Bagerhat | 98 | 9 | 2020-06-01 | 20:00
104 | Mongla | 48 | 2 | 2020-06-01 | 13:00
105 | Satkhira | 113 | 10 | 2020-06-01 | 22:00
106 | Gallamari | 56 | 25 | 2020-06-01 | 20:00
107 | Magura | 56 | 24 | 2020-06-01 | 21:00
108 | Norail | 42 | 24 | 2020-06-01 | 21:00
109 | Chuadanga | 97 | 6 | 2020-06-01 | 20:00
110 | Barsal(N) | 47 | 9 | 2020-06-01 | 22:00
111 | Barsal(S) | 108 | 24 | 2020-06-01 | 21:00
112 | Patuakhali | 135 | 17 | 2020-06-01 | 17:00
113 | Bhandaria | 58 | 9 | 2020-06-01 | 22:00
114 | Borhan Uddin | 44 | 9 | 2020-06-01 | 21:00
115 | Ishurdi | 70 | 30 | 2020-06-01 | 21:00
116 | Ruppur Paromanobik | 2 | 1 | 2020-06-01 | 21:00
117 | Natore | 142 | 6 | 2020-06-01 | 21:00
118 | Bogura | 172 | 9 | 2020-06-01 | 21:00
119 | Naogaon | 136 | 23 | 2020-06-01 | 21:00
120 | Rajshahi | 155 | 9 | 2020-06-01 | 21:00
121 | Rajshahi New | 12 | 3 | 2020-06-01 | 20:00
122 | C.Nawabganj | 84 | 10 | 2020-06-01 | 21:00
123 | Amnura | 48 | 8 | 2020-06-01 | 22:00
124 | Pabna | 137 | 24 | 2020-06-01 | 21:00
125 | Shahjadpur | 104 | 14 | 2020-06-01 | 19:30
126 | Serajganj | 110 | 24 | 2020-06-01 | 21:00
127 | Niyamatpur | 60 | 8 | 2020-06-01 | 21:00
128 | Joypurhat | 52 | 7 | 2020-06-01 | 20:00
129 | Sherpur(Bogura) | 52 | 24 | 2020-06-01 | 24:00
130 | Mohastangar | 62 | 24 | 2020-06-01 | 21:00
131 | Rangpur | 151 | 30 | 2020-06-01 | 20:00
132 | Lalmonirhat | 62 | 10 | 2020-06-01 | 20:00
133 | Saidpur | 111 | 9 | 2020-06-01 | 20:00
134 | Purbasadipur | 119 | 16 | 2020-06-01 | 20:00
135 | Thakurgaon | 88 | 3 | 2020-06-01 | 21:00
136 | Palshbari | 125 | 8 | 2020-06-01 | 21:00
137 | Barapukuria | 52 | 9 | 2020-06-01 | 22:00
138 | Panchugar | 51 | 11 | 2020-06-01 | 20:00
139 | Joldhaka | 36 | 29 | 2020-06-01 | 19:30
140 | Kurigram | 61 | 16 | 2020-06-01 | 20:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:June' 2020
Area | MW | Date | Hour | Remarks
Dhaka | 4195 | 29.06.2020 | 16:00
Chattogram | 1241 | 26.06.2020 | 01:00
Khulna | 1535 | 24.06.2020 | 22:00
Rajshahi | 1316 | 24.06.2020 | 21:00
Cumilla | 1182 | 24.06.2020 | 22:00
Mymensingh | 1005 | 07.06.2020 | 21:00
Sylhet | 524 | 23.06.2020 | 23:00
Barisal | 371 | 09.06.2020 | 22:00
Rangpur | 793 | 10.06.2020 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: June'2020
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 409 | 4 | 2020-06-01 | 17:00 | 380 | 29 | 2020-06-01 | 12:00
2 | Bheramara | 400 | 409 | 23 | 2020-06-01 | 11:00 | 383 | 9 | 2020-06-01 | 23:00
3 | Ashuganj(N) | 400 | 406 | 1 | 2020-06-01 | 19:30 | 375 | 15 | 2020-06-01 | 17:00
4 | Payra | 400 | 429 | 2 | 2020-06-01 | 5:00 | 371 | 23 | 2020-06-01 | 19:00
5 | Kaliakoir | 400 | 391 | 4 | 2020-06-01 | 16:00 | 331 | 15 | 2020-06-01 | 21:00
6 | Bhulta | 400 | 405 | 1 | 2020-06-01 | 18:30 | 372 | 12 | 2020-06-01 | 16:00
7 | Gopalganj | 400 | 422 | 4 | 2020-06-01 | 4:00 | 323 | 21 | 2020-06-01 | 13:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 240 | 1 | 2020-06-01 | 1:00 | 220 | 28 | 2020-06-01 | 8:00
2 | Ishurdi | 230 | 238 | 1 | 2020-06-01 | 18:00 | 219 | 28 | 2020-06-01 | 10:00
3 | Ashuganj | 230 | 244 | 1 | 2020-06-01 | 18:30 | 217 | 28 | 2020-06-01 | 9:00
4 | Serajganj | 230 | 235 | 3 | 2020-06-01 | 18:00 | 221 | 10 | 2020-06-01 | 12:00
5 | Baghabari | 230 | 245 | 1 | 2020-06-01 | 16:00 | 217 | 28 | 2020-06-01 | 8:00
6 | Barapukuria | 230 | 241 | 1 | 2020-06-01 | 16:00 | 220 | 10 | 2020-06-01 | 21:00
7 | Bogura | 230 | 238 | 1 | 2020-06-01 | 18:30 | 213 | 30 | 2020-06-01 | 21:00
8 | Rajshahi | 230 | 238 | 1 | 2020-06-01 | 18:30 | 216 | 3 | 2020-06-01 | 20:00
9 | Khulna South | 230 | 236 | 1 | 2020-06-01 | 18:30 | 198 | 1 | 2020-06-01 | 10:00
10 | Rampura | 230 | 232 | 1 | 2020-06-01 | 20:00 | 218 | 17 | 2020-06-01 | 9:00
11 | Haripur | 230 | 235 | 3 | 2020-06-01 | 4:00 | 219 | 29 | 2020-06-01 | 12:00
12 | Hasnabad | 230 | 235 | 4 | 2020-06-01 | 19:30 | 216 | 17 | 2020-06-01 | 9:00
13 | Shyampur | 230 | 236 | 4 | 2020-06-01 | 10:00 | 212 | 29 | 2020-06-01 | 10:00
14 | Aminbazar | 230 | 237 | 1 | 2020-06-01 | 19:30 | 215 | 17 | 2020-06-01 | 9:00
15 | Tongi | 230 | 236 | 1 | 2020-06-01 | 19:30 | 210 | 17 | 2020-06-01 | 9:00
16 | Comilla (N) | 230 | 241 | 4 | 2020-06-01 | 16:00 | 224 | 29 | 2020-06-01 | 9:00
17 | Hathazari | 230 | 231 | 24 | 2020-06-01 | 20:00 | 214 | 13 | 2020-06-01 | 16:00
18 | Megnaghat | 230 | 240 | 1 | 2020-06-01 | 19:30 | 222 | 29 | 2020-06-01 | 11:00
19 | Fenchuganj | 230 | 246 | 4 | 2020-06-01 | 17:00 | 232 | 29 | 2020-06-01 | 9:00
20 | Siddhirganj | 230 | 239 | 12 | 2020-06-01 | 23:00 | 219 | 29 | 2020-06-01 | 9:00
21 | Maniknagar | 230 | 237 | 1 | 2020-06-01 | 18:30 | 217 | 29 | 2020-06-01 | 9:00
22 | Old Airport | 230 | 237 | 4 | 2020-06-01 | 16:00 | 213 | 29 | 2020-06-01 | 10:00
23 | Barisal | 230 | 251 | 23 | 2020-06-01 | 11:00 | 180 | 21 | 2020-06-01 | 13:00
24 | AKSML | 230 | 230 | 24 | 2020-06-01 | 17:00 | 208 | 13 | 2020-06-01 | 16:00
25 | BSRM | 230 | 230 | 1 | 2020-06-01 | 19:30 | 212 | 13 | 2020-06-01 | 16:00
26 | Bibiyana | 230 | 243 | 4 | 2020-06-01 | 16:00 | 228 | 29 | 2020-06-01 | 11:00
27 | Bhulta | 230 | 240 | 1 | 2020-06-01 | 18:30 | 219 | 29 | 2020-06-01 | 9:00
28 | Ashuganj (S) | 230 | 242 | 1 | 2020-06-01 | 18:30 | 226 | 29 | 2020-06-01 | 9:00
29 | Kaliakoir | 230 | 239 | 1 | 2020-06-01 | 19:30 | 217 | 29 | 2020-06-01 | 14:00
30 | GPH | 230 | 228 | 24 | 2020-06-01 | 2:00 | 209 | 13 | 2020-06-01 | 16:00
132 kV Substation
1 | Siddhirganj | 132 | 137 | 1 | 2020-06-01 | 0.77083 | 124 | 15 | 2020-06-01 | 0.41667
2 | Munsiganj | 132 | 140 | 1 | 2020-06-01 | 0.77083 | 121 | 29 | 2020-06-01 | 0.375
3 | Sonargaon | 132 | 136 | 20 | 2020-06-01 | 0.20833 | 122 | 18 | 2020-06-01 | 0.54167
4 | Shyampur | 132 | 138 | 21 | 2020-06-01 | 0.8125 | 124 | 7 | 2020-06-01 | 0.375
5 | Bhulta | 132 | 130 | 1 | 2020-06-01 | 0.75 | 118 | 15 | 2020-06-01 | 0.41667
6 | Madanganj | 132 | 136 | 13 | 2020-06-01 | 0.16667 | 128 | 1 | 2020-06-01 | 0.77083
7 | Shitalakhya | 132 | 143 | 24 | 2020-06-01 | 0.83333 | 125 | 8 | 2020-06-01 | 0.41667
8 | Rahim Steal | 132 | 136 | 1 | 2020-06-01 | 0.77083 | 124 | 15 | 2020-06-01 | 0.375
9 | Matuail | 132 | 137 | 1 | 2020-06-01 | 0.77083 | 124 | 15 | 2020-06-01 | 0.41667
10 | Ghorasal | 132 | 142 | 1 | 2020-06-01 | 0.83333 | 133 | 23 | 2020-06-01 | 0.29167
11 | Narsinghdi | 132 | 135 | 1 | 2020-06-01 | 0.91667 | 116 | 10 | 2020-06-01 | 0.91667
12 | Haripur (SBU) | 132 | 136 | 1 | 2020-06-01 | 0.79167 | 123 | 29 | 2020-06-01 | 0.375
13 | Ullon | 132 | 139 | 17 | 2020-06-01 | 0.29167 | 123 | 7 | 2020-06-01 | 0.45833
14 | Hasnabad | 132 | 139 | 23 | 2020-06-01 | 0.041667 | 125 | 29 | 2020-06-01 | 0.41667
15 | Magbazar | 132 | 137 | 21 | 2020-06-01 | 0.83333 | 123 | 7 | 2020-06-01 | 0.45833
16 | Maniknagar | 132 | 138 | 1 | 2020-06-01 | 0.77083 | 125 | 29 | 2020-06-01 | 0.41667
17 | Bangabhaban | 132 | 138 | 1 | 2020-06-01 | 0.77083 | 125 | 29 | 2020-06-01 | 0.41667
18 | Narinda | 132 | 138 | 1 | 2020-06-01 | 0.77083 | 125 | 29 | 2020-06-01 | 0.41667
19 | Dhanmondi | 132 | 139 | 17 | 2020-06-01 | 0.29167 | 123 | 7 | 2020-06-01 | 0.45833
20 | Lalbag | 132 | 138 | 1 | 2020-06-01 | 0.77083 | 121 | 18 | 2020-06-01 | 0.54167
21 | Madartek | 132 | 137 | 20 | 2020-06-01 | 0.16667 | 123 | 7 | 2020-06-01 | 0.45833
22 | Dhaka University | 132 | - | - | 2020-06-01 | - | - | - | 2020-06-01 | -
23 | Mirpur | 132 | 136 | 4 | 2020-06-01 | 0.083333 | 122 | 27 | 2020-06-01 | 0.45833
24 | Kalyanpur | 132 | 136 | 1 | 2020-06-01 | 0.875 | 124 | 27 | 2020-06-01 | 0.45833
25 | Gulshan | 132 | 136 | 18 | 2020-06-01 | 0.25 | 122 | 7 | 2020-06-01 | 11;00
26 | Uttara | 132 | 138 | 1 | 2020-06-01 | 0.8125 | 122 | 7 | 2020-06-01 | 11;00
27 | Uttara(New) | 132 | 135 | 1 | 2020-06-01 | 0.8125 | 121 | 18 | 2020-06-01 | 0.58333
28 | Kamrangirchar | 132 | 139 | 24 | 2020-06-01 | 0.91667 | 121 | 18 | 2020-06-01 | 0.58333
29 | Savar | 132 | 135 | 1 | 2020-06-01 | 0.8125 | 122 | 27 | 2020-06-01 | 0.45833
30 | Bhasantec | 132 | 138 | 16 | 2020-06-01 | 0.625 | 121 | 17 | 2020-06-01 | 0.41667
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: June'2020
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
31 | Agargaon | 132 | 135 | 1 | 2020-06-01 | 0.8125 | 116 | 12 | 2020-06-01 | 0.75
32 | Satmosjid | 132 | 134 | 1 | 2020-06-01 | 0.875 | 122 | 25 | 2020-06-01 | 0.625
33 | Tongi | 132 | 140 | 1 | 2020-06-01 | 0.875 | 119 | 16 | 2020-06-01 | 0.625
34 | Kabirpur | 132 | 140 | 4 | 2020-06-01 | 0.70833 | 120 | 7 | 2020-06-01 | 0.41667
35 | Basundhara | 132 | 137 | 24 | 2020-06-01 | 0.041667 | 122 | 7 | 2020-06-01 | 0.45833
36 | Manikganj | 132 | 144 | 4 | 2020-06-01 | 0.66667 | 124 | 16 | 2020-06-01 | 0.45833
37 | Joydevpur | 132 | 143 | 4 | 2020-06-01 | 0.875 | 129 | 28 | 2020-06-01 | 0.54167
38 | New Tongi | 132 | 139 | 1 | 2020-06-01 | 0.91667 | 124 | 7 | 2020-06-01 | 0.45833
39 | Kodda | 132 | 143 | 10 | 2020-06-01 | 0.25 | 116 | 17 | 2020-06-01 | 0.375
40 | Dhamrai | 132 | 139 | 4 | 2020-06-01 | 0.70833 | 122 | 1 | 2020-06-01 | 0.41667
41 | Rajendrapur | 132 | 140 | 5 | 2020-06-01 | 0.33333 | 116 | 17 | 2020-06-01 | 0.375
42 | Valuka | 132 | 134 | 1 | 2020-06-01 | 0.77083 | 111 | 23 | 2020-06-01 | 0.95833
43 | Tangail | 132 | 142 | 4 | 2020-06-01 | 0.70833 | 123 | 10 | 2020-06-01 | 0.79167
44 | Mymensing | 132 | 135 | 4 | 2020-06-01 | 0.625 | 114 | 23 | 2020-06-01 | 0.95833
45 | Kishorganj | 132 | 137 | 1 | 2020-06-01 | 0.83333 | 111 | 10 | 2020-06-01 | 0.79167
46 | Netrokona | 132 | 140 | 8 | 2020-06-01 | 0.16667 | 109 | 23 | 2020-06-01 | 0.95833
47 | Jamalpur | 132 | 141 | 3 | 2020-06-01 | 0.8125 | 115 | 8 | 2020-06-01 | 0.95833
48 | Sherpur | 132 | 140 | 21 | 2020-06-01 | 0.45833 | 115 | 25 | 2020-06-01 | 0.8125
49 | Srimongal | 132 | 140 | 4 | 2020-06-01 | 0.33333 | 128 | 10 | 2020-06-01 | 0.70833
50 | Shahjibazar | 132 | 139 | 8 | 2020-06-01 | 0.25 | 119 | 10 | 2020-06-01 | 0.79167
51 | Fenchuganj | 132 | 138 | 4 | 2020-06-01 | 0.20833 | 131 | 15 | 2020-06-01 | 0.8125
52 | Khulawara | 132 | 138 | 4 | 2020-06-01 | 0.29167 | 127 | 10 | 2020-06-01 | 0.79167
53 | Sylhet | 132 | 136 | 2 | 2020-06-01 | 0.125 | 129 | 15 | 2020-06-01 | 0.79167
54 | Chattak | 132 | 136 | 4 | 2020-06-01 | 0.29167 | 126 | 15 | 2020-06-01 | 0.91667
55 | Sunamganj | 132 | 135 | 1 | 2020-06-01 | 0.29167 | 125 | 15 | 2020-06-01 | 0.79167
56 | Biani Bazar | 132 | 137 | 2 | 2020-06-01 | 0.25 | 125 | 15 | 2020-06-01 | 0.79167
57 | Comilla(South) | 132 | 129 | 29 | 2020-06-01 | 0.29167 | 112 | 7 | 2020-06-01 | 0.58333
58 | Comilla (North) | 132 | 140 | 24 | 2020-06-01 | 0.8125 | 130 | 17 | 2020-06-01 | 0.375
59 | Chandpur | 132 | 140 | 24 | 2020-06-01 | 0.91667 | 120 | 14 | 2020-06-01 | 0.91667
60 | Feni | 132 | 139 | 24 | 2020-06-01 | 0.83333 | 123 | 29 | 2020-06-01 | 0.625
61 | Chowmuhani | 132 | 138 | 24 | 2020-06-01 | 0.83333 | 120 | 7 | 2020-06-01 | 0.79167
62 | Ashuganj | 132 | 140 | 4 | 2020-06-01 | 0.8125 | 122 | 10 | 2020-06-01 | 0.70833
63 | Daudkandi | 132 | 139 | 11 | 2020-06-01 | 0.45833 | 123 | 29 | 2020-06-01 | 0.375
64 | Brahminbaria | 132 | 138 | 10 | 2020-06-01 | 0.83333 | 119 | 10 | 2020-06-01 | 0.45833
65 | Ramganj | 132 | 132 | 24 | 2020-06-01 | 0.91667 | 116 | 13 | 2020-06-01 | 0.70833
66 | Chaddagram | 132 | 139 | 24 | 2020-06-01 | 0.77083 | 124 | 9 | 2020-06-01 | 0.79167
67 | PHP | 132 | 138 | 24 | 2020-06-01 | 0.5 | 122 | 29 | 2020-06-01 | 0.58333
68 | Madanhat | 132 | 140 | 24 | 2020-06-01 | 0.83333 | 128 | 1 | 2020-06-01 | 0.375
69 | Hathazari | 132 | 137 | 24 | 2020-06-01 | 0.83333 | 128 | 1 | 2020-06-01 | 0.375
70 | Khulshi | 132 | 137 | 24 | 2020-06-01 | 0.83333 | 123 | 1 | 2020-06-01 | 0.29167
71 | Halishahar | 132 | 140 | 16 | 2020-06-01 | 0.8125 | 126 | 1 | 2020-06-01 | 0.375
72 | Baraulia | 132 | 139 | 24 | 2020-06-01 | 0.875 | 126 | 1 | 2020-06-01 | 0.33333
73 | Sikalbaha | 132 | 139 | 15 | 2020-06-01 | 0.83333 | 127 | 1 | 2020-06-01 | 0.33333
74 | Dohazari | 132 | 138 | 24 | 2020-06-01 | 0.75 | 123 | 1 | 2020-06-01 | 0.45833
75 | Cox'sbazar | 132 | 131 | 24 | 2020-06-01 | 0.70833 | 107 | 25 | 2020-06-01 | 0.5
76 | Chandraghona | 132 | 138 | 24 | 2020-06-01 | 0.83333 | 124 | 4 | 2020-06-01 | 0.5
77 | Kaptai | 132 | 137 | 24 | 2020-06-01 | 0.79167 | 127 | 1 | 2020-06-01 | 0.41667
78 | A. Khaer Stl. | 132 | 135 | 15 | 2020-06-01 | 0.8125 | 126 | 1 | 2020-06-01 | 0.29167
79 | Bakulia | 132 | 138 | 24 | 2020-06-01 | 0.77083 | 125 | 1 | 2020-06-01 | 0.375
80 | Julda | 132 | 139 | 24 | 2020-06-01 | 0.77083 | 125 | 1 | 2020-06-01 | 0.33333
81 | TK Chemical | 132 | 139 | 24 | 2020-06-01 | 0.75 | 126 | 1 | 2020-06-01 | 0.375
82 | Modern Steel | 132 | 138 | 24 | 2020-06-01 | 0.8125 | 126 | 1 | 2020-06-01 | 0.33333
83 | Shahmirpur | 132 | 139 | 24 | 2020-06-01 | 0.8125 | 124 | 25 | 2020-06-01 | 0.125
84 | Khagrachhari | 132 | 137 | 9 | 2020-06-01 | 0.83333 | 126 | 1 | 2020-06-01 | 0.375
85 | Matarbari | 132 | 134 | 24 | 2020-06-01 | 0.75 | 103 | 25 | 2020-06-01 | 0.95833
86 | Baroiar Hat | 132 | 138 | 11 | 2020-06-01 | 0.875 | 123 | 29 | 2020-06-01 | 0.625
87 | Rangamati | 132 | 137 | 24 | 2020-06-01 | 0.875 | 126 | 1 | 2020-06-01 | 0.375
88 | Goalpara | 132 | 142 | 1 | 2020-06-01 | 0.77083 | 121 | 13 | 2020-06-01 | 0.5
89 | Khulna Central | 132 | 142 | 10 | 2020-06-01 | 0.79167 | 120 | 30 | 2020-06-01 | 0.5
90 | Noapara | 132 | 138 | 1 | 2020-06-01 | 0.77083 | 116 | 6 | 2020-06-01 | 0.58333
91 | Jessore | 132 | 138 | 26 | 2020-06-01 | 0.79167 | 112 | 8 | 2020-06-01 | 0.54167
92 | Benapol | 132 | 136 | 2 | 2020-06-01 | 0.75 | 113 | 6 | 2020-06-01 | 0.625
93 | Jhenida | 132 | 136 | 4 | 2020-06-01 | 0.91667 | 106 | 20 | 2020-06-01 | 0.5
94 | Bottail | 132 | 137 | 26 | 2020-06-01 | 0.25 | 116 | 21 | 2020-06-01 | 0.125
95 | G.K Project | 132 | 140 | 1 | 2020-06-01 | 0.75 | 124 | 26 | 2020-06-01 | 0.16667
96 | Faridpur | 132 | 137 | 3 | 2020-06-01 | 0.77083 | 115 | 21 | 2020-06-01 | 0.54167
97 | Madaripur | 132 | 140 | 2 | 2020-06-01 | 0.625 | 105 | 21 | 2020-06-01 | 0.54167
98 | Sariatpur | 132 | 140 | 1 | 2020-06-01 | 0.75 | 109 | 21 | 2020-06-01 | 0.54167
99 | Gopalganj | 132 | 146 | 2 | 2020-06-01 | 0.8125 | 110 | 21 | 2020-06-01 | 0.54167
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: June'2020
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
100 | Bagerhat | 132 | 139 | 2 | 2020-06-01 | 0.75 | 116 | 5 | 2020-06-01 | 0.79167
101 | Mongla | 132 | 137 | 1 | 2020-06-01 | 0.77083 | 114 | 30 | 2020-06-01 | 0.5
102 | Satkhira | 132 | 141 | 6 | 2020-06-01 | 0.375 | 118 | 5 | 2020-06-01 | 0.79167
103 | Gallamari | 132 | 142 | 1 | 2020-06-01 | 0.77083 | 122 | 5 | 2020-06-01 | 0.8125
104 | Magura | 132 | 139 | 4 | 2020-06-01 | 0.91667 | 105 | 27 | 2020-06-01 | 0.5
105 | Norail | 132 | 135 | 4 | 2020-06-01 | 0.91667 | 102 | 3 | 2020-06-01 | 0.83333
106 | Chuadanga | 132 | 136 | 4 | 2020-06-01 | 0.91667 | 96 | 3 | 2020-06-01 | 0.83333
107 | Barisal(N) | 132 | 143 | 1 | 2020-06-01 | 0.75 | 107 | 21 | 2020-06-01 | 0.54167
108 | Barisal(S) | 132 | 143 | 1 | 2020-06-01 | 0.75 | 104 | 21 | 2020-06-01 | 0.54167
109 | Patuakhali | 132 | 139 | 3 | 2020-06-01 | 0.75 | 102 | 21 | 2020-06-01 | 0.54167
110 | Bhandaria | 132 | 140 | 12 | 2020-06-01 | 0.375 | 100 | 21 | 2020-06-01 | 0.54167
111 | Ishurdi | 132 | 139 | 1 | 2020-06-01 | 0.75 | 127 | 21 | 2020-06-01 | 0.16667
112 | Ruppur paromanobik | 132 | 140 | 1 | 2020-06-01 | 0.77083 | 125 | 19 | 2020-06-01 | 0.875
113 | Natore | 132 | 139 | 1 | 2020-06-01 | 0.77083 | 123 | 6 | 2020-06-01 | 0.875
114 | Bogra | 132 | 140 | 4 | 2020-06-01 | 0.75 | 122 | 20 | 2020-06-01 | 0.875
115 | Noagaon | 132 | 136 | 1 | 2020-06-01 | 0.77083 | 114 | 20 | 2020-06-01 | 0.875
116 | Rajshahi | 132 | 137 | 4 | 2020-06-01 | 0.75 | 122 | 17 | 2020-06-01 | 0.041667
117 | Rajshahi New | 132 | 137 | 4 | 2020-06-01 | 0.75 | 120 | 7 | 2020-06-01 | 0.45833
118 | C.Nawabganj | 132 | 136 | 1 | 2020-06-01 | 0.77083 | 119 | 18 | 2020-06-01 | 0.875
119 | Amnura | 132 | 137 | 4 | 2020-06-01 | 0.75 | 119 | 17 | 2020-06-01 | 0.16667
120 | Pabna | 132 | 136 | 1 | 2020-06-01 | 0.77083 | 124 | 6 | 2020-06-01 | 0.875
121 | Shahjadpur | 132 | 144 | 1 | 2020-06-01 | 0.77083 | 128 | 11 | 2020-06-01 | 0.875
122 | Serajganj | 132 | 140 | 1 | 2020-06-01 | 0.77083 | 125 | 7 | 2020-06-01 | 0.875
123 | Niyamatpur | 132 | 136 | 2 | 2020-06-01 | 0.75 | 110 | 30 | 2020-06-01 | 0.875
124 | Joypurhat | 132 | 138 | 1 | 2020-06-01 | 0.77083 | 113 | 30 | 2020-06-01 | 0.875
125 | Sherpur(Bogura) | 132 | 140 | 1 | 2020-06-01 | 0.77083 | 123 | 30 | 2020-06-01 | 0.875
126 | Mohastangor | 132 | 137 | 1 | 2020-06-01 | 0.75 | 120 | 9 | 2020-06-01 | 0.875
127 | Rangpur | 132 | 138 | 1 | 2020-06-01 | 0.66667 | 114 | 10 | 2020-06-01 | 0.875
128 | Lalmonirhat | 132 | 135 | 1 | 2020-06-01 | 0.70833 | 108 | 9 | 2020-06-01 | 0.875
129 | Saidpur | 132 | 139 | 1 | 2020-06-01 | 0.66667 | 106 | 10 | 2020-06-01 | 0.875
130 | Purbasadipur | 132 | 137 | 1 | 2020-06-01 | 0.66667 | 103 | 10 | 2020-06-01 | 0.875
131 | Thakurgaon | 132 | 137 | 1 | 2020-06-01 | 0.625 | 102 | 9 | 2020-06-01 | 0.875
132 | Palashbari | 132 | 136 | 1 | 2020-06-01 | 0.77083 | 113 | 11 | 2020-06-01 | 0.875
133 | Barapukuria | 132 | 141 | 1 | 2020-06-01 | 0.77083 | 120 | 10 | 2020-06-01 | 0.875
134 | Panchagar | 132 | 136 | 1 | 2020-06-01 | 0.66667 | 94 | 11 | 2020-06-01 | 0.91667
135 | Joldhaka | 132 | 139 | 1 | 2020-06-01 | 0.625 | 106 | 10 | 2020-06-01 | 0.875
136 | Kurigram | 132 | 138 | 1 | 2020-06-01 | 0.66667 | 105 | 10 | 2020-06-01 | 0.875
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:June' 2020
Name of the | Auto transofrmer |  | Recorded maximum load
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kV side ) | Date | Time | Remarks
| TR1 | 225 | 160 | 350
Hasnabad | TR2 | 225 | 110 | 350 | 19.06.2020 | 16:00
| TR3 | 225 | 110 | 350
| TR1 | 225 | 170 | 500
Tongi | TR2 | 225 | 170 | 500 | 18.06.2020 | 09:00
| TR3 | 225 | 170 | 500
Haripur | TR1 | 225 | 141 | 385 | 28.06.2020 | 06:00
| TR3 | 225 | 141 | 385
| TR1 | 225 | 165 | 445
Rampura | TR2 | 225 | 165 | 445 | 17.06.2020 | 12:00
| TR3 | 225 | 165 | 445
| TR1 | 225 | 127 | 362
Aminbazar | TR2 | 225 | 127 | 362 | 27.06.2020 | 14:00
| TR3 | 225 | 132 | 372
Maniknagar | TR1 | 300 | 93 | 270 | 31.05.2020 | 13:00
| TR2 | 300 | 93 | 270
Cumilla (N) | TR1 | 225 | 200 | 577 | 07.06.2020 | 19:30
| TR2 | 225 | 199 | 557
Fenchuganj | AT2 | 300 | 146 | 373 | 10.06.2020 | 18:30
| MT1 | 150 | 90 | 260
Hathazari | MT2 | 150 | 90 | 260 | 05.06.2020 | 17:00
| MT3 | 150 | 90 | 260
| MT4 | 150 | 90 | 260
| TR1 | 225 | 145 | 360
Ishurdi | TR2 | 225 | 145 | 360 | 03.06.2020 | 21:00
| TR3 | 225 | 145 | 360
Khulna(S) | TR1 | 225 | 131 | 362
| TR2 | 225 | 131 | 362 | 20.06.2020 | 07:00
| TR3 | 300 | 168 | 444
Bogra | TR1 | 225 | 123 | 343 | 03.06.2020 | 21:00
| TR2 | 225 | 123 | 343
| TR3 | 225 | 164 | 446
Baghabari | TR1 | 300 | 165 | 460 | 30.06.2020 | 22:00
| TR2 | 225 | 150 | 420 | 04.06.20 | 11:00
Barapukuria | TR1 | 225 | 150 | 770 | 09.06.2020 | 19:30 | Due to unavailability of 230 kV side meters
| TR2 | 225 | 150 | 780 |  |  | 132 kV current is being provided
| TR6 | 300 | 194 | 104
Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:June' 2020
Name of the | Transofrmer |  | Recorded maximum load |  |  |  | Remarks
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 400 kV side ) | Date | Time
Kaliakoir | TR1(400/230 kV) | 520 | 126.5 | 233 | 04.06.2020 | 17:15
| TR2(400/230 kV) | 520 | 128.3 | 240
| TR1(400/132 kV) | 325 | 248.1 | 418 | 16.06.2020 | 19:45
| TR2(400/132 kV) | 325 | 247.4 | 414
Bibiyana | ICT1(400/230 kV) | 520 | 156 | 269 | 24.06.2020 | 15:00
| ICT2(400/230kV) | 520 | 156 | 269
Bhulta | ATR1(400/230 kV) | 520 | 200 | 357 | 14.06.2020 | 14:30
| ATR2(400/230kV) | 520 | 200 | 357
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:June' 2020 | [6 empty] | (For Evening Peak) | [7 empty] | Month:June' 2020 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-06-20 | 9834 | 9834 | - | - | - | - | - | - | - | - | - | - | - | - | 01-06-20 | 8859.9 | 8859.9 | - | - | - | - | - | - | - | - | - | - | - | -
02-06-20 | 10228 | 10228 | - | - | - | - | - | - | - | - | - | - | - | - | 02-06-20 | 9165.1 | 9165.1 | - | - | - | - | - | - | - | - | - | - | - | -
03-06-20 | 10238 | 10238 | - | - | - | - | - | - | - | - | - | - | - | - | 03-06-20 | 9280.3 | 9280.3 | - | - | - | - | - | - | - | - | - | - | - | -
04-06-20 | 9376 | 9376 | - | - | - | - | - | - | - | - | - | - | - | - | 04-06-20 | 9052.5 | 9052.5 | - | - | - | - | - | - | - | - | - | - | - | -
05-06-20 | 10098 | 10098 | - | - | - | - | - | - | - | - | - | - | - | - | 05-06-20 | 7720.9 | 7720.9 | - | - | - | - | - | - | - | - | - | - | - | -
06-06-20 | 10677 | 10677 | - | - | - | - | - | - | - | - | - | - | - | - | 06-06-20 | 8998.5 | 8998.5 | - | - | - | - | - | - | - | - | - | - | - | -
07-06-20 | 11441 | 11441 | - | - | - | - | - | - | - | - | - | - | - | - | 07-06-20 | 9670.9 | 9670.9 | - | - | - | - | - | - | - | - | - | - | - | -
08-06-20 | 11464 | 11464 | - | - | - | - | - | - | - | - | - | - | - | - | 08-06-20 | 9623.2 | 9623.2 | - | - | - | - | - | - | - | - | - | - | - | -
09-06-20 | 11934 | 11934 | - | - | - | - | - | - | - | - | - | - | - | - | 09-06-20 | 10166.5 | 10166.5 | - | - | - | - | - | - | - | - | - | - | - | -
10-06-20 | 10804 | 10804 | - | - | - | - | - | - | - | - | - | - | - | - | 10-06-20 | 9909.81 | 9909.81 | - | - | - | - | - | - | - | - | - | - | - | -
11-06-20 | 11211 | 11211 | - | - | - | - | - | - | - | - | - | - | - | - | 11-06-20 | 9492 | 9492 | - | - | - | - | - | - | - | - | - | - | - | -
12-06-20 | 10167 | 10167 | - | - | - | - | - | - | - | - | - | - | - | - | 12-06-20 | 7773.9 | 7773.9 | - | - | - | - | - | - | - | - | - | - | - | -
13-06-20 | 10714 | 10714 | - | - | - | - | - | - | - | - | - | - | - | - | 13-06-20 | 8525.7 | 8525.7 | - | - | - | - | - | - | - | - | - | - | - | -
14-06-20 | 11410 | 11410 | - | - | - | - | - | - | - | - | - | - | - | - | 14-06-20 | 9617.1 | 9617.1 | - | - | - | - | - | - | - | - | - | - | - | -
15-06-20 | 11634 | 11634 | - | - | - | - | - | - | - | - | - | - | - | - | 15-06-20 | 9834 | 9834 | - | - | - | - | - | - | - | - | - | - | - | -
16-06-20 | 11389 | 11389 | - | - | - | - | - | - | - | - | - | - | - | - | 16-06-20 | 9786.2 | 9786.2 | - | - | - | - | - | - | - | - | - | - | - | -
17-06-20 | 10355 | 10355 | - | - | - | - | - | - | - | - | - | - | - | - | 17-06-20 | 9118.2 | 9118.2 | - | - | - | - | - | - | - | - | - | - | - | -
18-06-20 | 10510 | 10510 | - | - | - | - | - | - | - | - | - | - | - | - | 18-06-20 | 8398.5 | 8398.5 | - | - | - | - | - | - | - | - | - | - | - | -
19-06-20 | 10548 | 10548 | - | - | - | - | - | - | - | - | - | - | - | - | 19-06-20 | 7642.6 | 7642.6 | - | - | - | - | - | - | - | - | - | - | - | -
20-06-20 | 11332 | 11332 | - | - | - | - | - | - | - | - | - | - | - | - | 20-06-20 | 8765 | 8765 | - | - | - | - | - | - | - | - | - | - | - | -
21-06-20 | 11090 | 11090 | - | - | - | - | - | - | - | - | - | - | - | - | 21-06-20 | 8868.7 | 8868.7 | - | - | - | - | - | - | - | - | - | - | - | -
22-06-20 | 11476 | 11476 | - | - | - | - | - | - | - | - | - | - | - | - | 22-06-20 | 9276.9 | 9276.9 | - | - | - | - | - | - | - | - | - | - | - | -
23-06-20 | 11673 | 11673 | - | - | - | - | - | - | - | - | - | - | - | - | 23-06-20 | 9747.46 | 9747.46 | - | - | - | - | - | - | - | - | - | - | - | -
24-06-20 | 12070 | 12070 | - | - | - | - | - | - | - | - | - | - | - | - | 24-06-20 | 10183.6 | 10183.6 | - | - | - | - | - | - | - | - | - | - | - | -
25-06-20 | 11285 | 11285 | - | - | - | - | - | - | - | - | - | - | - | - | 25-06-20 | 9692 | 9692 | - | - | - | - | - | - | - | - | - | - | - | -
26-06-20 | 10790 | 10790 | - | - | - | - | - | - | - | - | - | - | - | - | 26-06-20 | 8089.8 | 8089.8 | - | - | - | - | - | - | - | - | - | - | - | -
27-06-20 | 10753 | 10753 | - | - | - | - | - | - | - | - | - | - | - | - | 27-06-20 | 8659.7 | 8659.7 | - | - | - | - | - | - | - | - | - | - | - | -
28-06-20 | 10619 | 10619 | - | - | - | - | - | - | - | - | - | - | - | - | 28-06-20 | 9429.28 | 9429.28 | - | - | - | - | - | - | - | - | - | - | - | -
29-06-20 | 11286 | 11286 | - | - | - | - | - | - | - | - | - | - | - | - | 29-06-20 | 9449.7 | 9449.7 | - | - | - | - | - | - | - | - | - | - | - | -
30-06-20 | 11367 | 11367 | - | - | - | - | - | - | - | - | - | - | - | - | 30-06-20 | 9891.8 | 9891.8

## QF-LDC-38
page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:June' 2020
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 12070 | 24/06/20 | 22:00
2 | Maximum Day Peak Genaration | MW | 10183.6 | 24/06/20 | 12:00
3 | Maximum Evening Peak Demand | MW | 12070 | 24/06/20 | 21:00
4 | Minimum Generation | MW | 6656.5 | 05/06/20 | 7:00
5 | Average of the daily evening peak Genaration | MW | 10925.7667
6 | Average of the daily day peak Genaration | MW | 9156.325
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW | -
11 | Total Generation | MKWH | 6835.9112
12 | Total Generation by BPDB | MKWH | 3156.9465 | % of total Gen. | 46.18%
13 | Total Generation by IPP | MKWH | 2115.2966 | '' | 30.94%
14 | A) Total Generation by RPCL | MKWH | 118.1627 | '' | 1.729%
| B) Total Generation by REB | MKWH | 148.3631 | " | 2.17%
| C) Total Generation by RENTAL | MKWH | 560.7517 | " | 8.203%
| D) Total Imported from India (HVDC) | MKWH | 646.6262 | " | 9.459%
| E) Total Imported from Tripura, India (A.C) | MKWH | 89.7645 | " | 1.313%
15 | Fuel wise Generation.
| A) Gas | MKWH | 4101.8172 | % of total Gen. | 60%
| B) Oil | MKWH | 1523.8638 | '' | 22.29%
| C) Hydro | MKWH | 62.4299 | '' | 0.9133%
| D) Solar | MKWH | 4.9313 | '' | 0.07214%
| E) Coal | MKWH | 406.4783 | '' | 5.946%
| F) HVDC (Import from India) | MKWH | 646.6262 | '' | 9.459%
| G) A.C (Import from Tripura, India) | MKWH | 89.7645 | '' | 1.313%
16 | Maximun of the daily total Generation . | MKWH | 252.2599 | 24-06-2020
17 | Monthly Load factor | % | 78.6605
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 18302.8623
| A) Gas | M.Taka | 4742.7767
| B) Liquid fuel | M.Taka | 11662.4343
| C) Coal | M.Taka | 1897.6513
| D) HVDC (Import from India) | M.Taka | 3297.7935
| E) Tripura(Import from India) | M.Taka | 673.2336
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 927.2172 | 24/06/2020
| A) Gas | M.Taka | 180.3171 | 28/06/2020
| B) Liquid fuel | M.Taka | 752.2156 | 24/06/2020
| C) Coal | M.Taka | 84.721 | 10/06/2020
| D) HVDC (Import from India) | M.Taka | 116.0092 | 21-06-2020
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 3.586
| B) Excluding Hydro & Solar | Taka/KWHR | 3.621
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 83.73 | 30/06/2020 | 06:00
b) | Actual | FT (MSL) | 83.24 | 30/06/2020 | 06:00
22 | Peak Genaration of June 2019 | MW | 12780 | 24/06/19 | 21:00
23 | Peak Demand of June 2019 | MW | 12780 | 24/06/19 | 21:00
24 | Maximum peak Generation recorded upto 30/06/2020 | MW | 12893 | 29/05/19 | 21:00
25 | Maximum peak Demand recorded upto 30/06/2020 | MW | 12893 | 29/05/19 | 21:00
26 | Maximum load shed recorded upto 30/06/2020 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.