## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-07-21 | Tuesday
|  | Date (day): | 2020-07-21 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13602.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14832 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-07-21 | 2020-07-21 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 33 | 33 | 35 | 35 |  | 50 | Unit-2 Under maint
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 0 | 0
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 120 | 120 | 120 | 120
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 70 | 70
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 90 | 93 | 93 | 93
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 326 | 342 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 351 | 350 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 420 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel Shortage.
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 140 | 145 | 150 | 150 | 155 |  | GT-1 S/D for gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 79 | 79 | 81 | 81 |  |  | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 47 | 47 | 47 | 47 |  | 10 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 100 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 100 | 100 | 100 | 100
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Fuel Shortage.
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 217 | 217 |  |  | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 102 | 102 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 | 0 | Fuel Shortage.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 53 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 48 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 43 | 55 | 55 | 55 |  | 25 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 35 | 50
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 264 | 270 | 300 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 80 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 119 | 132 | 133 | 133
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 35 | 52 | 100 | 100
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 90 | 90 | 90 | 90
| Dhaka area Total |  |  |  |  | 6119 | 5895 | 2712 | 2954 | 3679 | 3964 | 519 | 570
38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 95 | 95 | 95 | 95 | 85 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 6.1 | 0 | 20 | 0
41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 32 | 50 | 50
42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 145 | 146 | 147 | 147 | 83 |  | Low water level
43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint.
44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 145 | 145 | 150 | 150
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  |  | Under maint.
47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 100 | 102
48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 100 | 100 | 100
50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 20 | 20 | 20
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 30 | 10 | 20
51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 97 | 100 | 100 |  |  | Engine problem
52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 1.4 | 0 | 5 | 0
53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 305 | 195 | 300 | 300
54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 54 | 50 | 54
55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| Chattogram area Total |  |  |  |  | 2326 | 2266 | 909.5 | 1048 | 1522 | 1573 | 348 | 225
57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 100 | 135 | 100 | 100
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas Shortage
58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 206 | 191 | 216 | 216 | 5 |  | Gas shortage
59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 305 | 360 | 360 |  |  | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 270 | 360 | 360 |  |  | FGMO
61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 38 | 42 | 46 | 46 |  |  | Engine problem
62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 51 | 55
63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 123 | 148 | 150 | 150
66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 42
67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 87 | 96 | 95 | 95 |  | 68 | ST under shut down
68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 200 | 200
69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 94 | 148 | 154 | 173
71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 43 | 43
73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 6 | 21 | 21 | 21
74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 113 | 113 | 113 | 113
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1456 | 1591 | 2140 | 2405 | 461 | 76
77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 140 | 144 | 160 | 160 | 42 |  | Gas shortage
78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 90 | 95 | 95 | 95
80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0.7 | 0 | 1.6 | 0
81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 50 | 170 | 200
82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 365.7 | 424 | 563.6 | 592 | 42 | 0
83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 89 | 90 | 90 | 90
84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 32 | 30 | 30
85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 130 | 163 | 163
86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 161 | 161 | 163 | 163 |  |  | GT-2 under maint.
87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 51 | 51
88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 46 | 46 | 44 | 44
89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 61 | 61 | 66
91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 77 | 80 | 80 | 80 |  | 6 | Engine problem
92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 150 | 151 | 151 |  | 225
93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 24 | 25
96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 315 | 341 | 341 |  |  | FGMO
97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
| Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
| Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1028 | 1181 | 1237 | 1243 | 0 | 631
99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 935 | 935 | 946 | 946
100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 115 | 115 | 115 |  |  | .
101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 20 | 30
102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 10 | 225
103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 48 | 60
104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 405 | 365 | 410 | 410
105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 16 | 40 | 40 | 40
106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 60 | 100
107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105
108 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Khulna Area Total |  |  |  |  | 2288 | 2284 | 1356 | 1455 | 1854 | 2147 | 0 | 0
109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 96 | 110 | 110
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 26 | 40 | 33 | 33
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 89 | 89 | 89 | 89 |  | 105 | GT-2 & ST Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 77 | 78 | 78 | 79 |  | 16 | Engine problem
113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 410 | 545 | 600 | 600
| Barisal Area Total |  |  |  |  | 1054 | 1054 | 602 | 848 | 910 | 911 | 0 | 121
114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 60
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 43 | 45
120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | S/D for ST Under maint.
121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 152 | 186 | 200 | 200 |  |  | FGMO
122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 165 | 182 | 210 | 210 |  |  | FGMO
123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 376 | 418 | 410 | 410 |  |  | FGMO
124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 35
125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 10 | 10 | 11 | 11
127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 99 | 100 | 100
130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 89 | 70 | 113
132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 70 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 732 | 1017 | 1449 | 1722 | 360 | 0
133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 149 | 150 | 150 |  |  | Coal Shortage.
135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 10 | 0 | 12 |  | 8 | Engine problem
137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 110 | 90 | 113
138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 0.4 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 150.4 | 269 | 248 | 275 | 170 | 28
| Total |  |  |  |  | 20383 | 19892 | 9311.6 | 10787 | 13602.6 | 14832 | 1900 | 1651
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8853.2279 | 10256 | 12932.9995 | 14101.8812
A. |  | 2020-07-21 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 10753 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 8114.9 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10787 | MW
3 | Day peak Generation : |  |  | 9311.6 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10256 | MW
4 | Evening peak Generation : |  |  | 10787 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 229.0521 | MKWHr | By Solar | 0.079289 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 136.9234 | MKWHr |  | By Oil: | 47.0473 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 16.0556 | MKWHr |  | By Hydro: | 3.3859 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1900 | MW | Dhaka | 3620 | 3620 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1651 | MW | Chittagong | 1086 | 1086 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3551 | MW | Khulna | 1307 | 1307 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1136.44 | MMCFD |  |  | Rajshahi | 1031 | 1031 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 159503364.296 | ii) Oil : | Taka | 355780423.06 | Comilla | 1043 | 1043 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 74265523 | Total | Taka | 589549310.356 | Mymensingh | 712 | 712 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.0395 | MKWHr. | Sylhet | 421 | 421 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -10 | MW (E to W) at | 21:00 | hrs | Barisal | 326 | 326 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -10 | MW at | 21:00 | hrs | Rangpur | 710 | 710 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 30.3° C |  |  | Total | 10256 | 10256 |  | 0
B. |  | 2020-07-21 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 32.9° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14832 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9200 | MW
4 | Reserve(Generation end) |  |  |  | 3832 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 234.3135 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8093.53 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.4771 | MKWHr. | ii) HVDC Flow at Peak Time |  | 935 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.0835 | MKWHr. | iii) Maximum HVDC Flow : |  | 941 | MW at | 5:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 88.39 |  | (b) Today: | 88.64 |  | (c) Rule Curve: |  | 87.2
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-07-21
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 33 | 0 | 0 | 180 | 120 | 22 | 0 | 322 | 355 |  | 0 | 390 | 145 | 0 | 96 | 47 | 296 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 17 | 0 | 25 | 29 | 33 | 33 | 0 | 0 | 82 | 65 | 95 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 45 | 0 | 20 | 40 | 0 | 100 | 0 | 315 | 290 | 191 | 8 | 95 | 42 | 5 | 0 | 43 | 0 | 0 | 24 | 22 | 11 | 33 | 21 | 152 | 159 | 72 | 20 | 0 | 89 | 30 | 53 | 46 | 163 | 161 | 61 | 79 | 0 | 0 | 18 | 0 | 10 | 295 | 23 | 11 | 0 | 195 | 0 | 0 | 100 | 0 | 132 | 0 | 100 | 0 | 100 | 0 | 115 | 0 | 0 | 0 | 234 | 35 | 0 | 0 | 113 | 100 | 0 | 0 |  | 940 | 0 | 380 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 32 | 88 | 35 | 80 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 183 | 0 | 78 | 20 | 165 | 0 | 420 | 35 | 0 | 111 | 0 | 98 | 0 | 0 | 0 | 555 |  | 6696 | 3585 | 10281 | 3841 | 940 | 2074 | 2362 | 705 | 147 | 60 | 152 | 0 | 0 | 88.37
2:00 | 33 | 0 | 0 | 180 | 120 | 22 | 0 | 323 | 359 |  | 0 | 390 | 140 | 0 | 96 | 47 | 296 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 17 | 0 | 25 | 29 | 33 | 33 | 0 | 0 | 80 | 65 | 95 | 0 | 0 | 0 | 0 | 146 | 0 |  | 0 | 0 | 0 | 0 | 60 | 0 | 20 | 40 | 0 | 100 | 0 | 310 | 290 | 183 | 8 | 96 | 42 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 150 | 158 | 72 | 20 | 0 | 89 | 30 | 53 | 46 | 163 | 162 | 61 | 79 | 0 | 0 | 18 | 0 | 10 | 280 | 23 | 11 | 0 | 150 | 0 | 0 | 100 | 0 | 132 | 0 | 100 | 0 | 50 | 0 | 109 | 0 | 0 | 0 | 234 | 35 | 0 | 0 | 113 | 100 | 0 | 0 |  | 940 | 0 | 386 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 32 | 88 | 35 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 184 | 0 | 80 | 10 | 167 | 0 | 416 | 17 | 0 | 35 | 0 | 90 | 0 | 0 | 0 | 555 |  | 6562 | 3420 | 9982 | 3846 | 940 | 2061 | 2135 | 705 | 145 | 0 | 150 | 0 | 0 | 88.37
3:00 | 33 | 0 | 0 | 180 | 120 | 23 | 0 | 323 | 356 |  | 0 | 390 | 140 | 0 | 96 | 47 | 295 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 17 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 79 | 65 | 95 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 40 | 0 | 20 | 40 | 0 | 100 | 0 | 315 | 290 | 182 | 8 | 92 | 42 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 146 | 158 | 72 | 20 | 0 | 89 | 30 | 53 | 46 | 163 | 163 | 61 | 79 | 0 | 0 | 18 | 0 | 10 | 295 | 23 | 11 | 0 | 95 | 0 | 0 | 100 | 0 | 132 | 0 | 100 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 234 | 35 | 0 | 0 | 113 | 100 | 0 | 0 |  | 940 | 0 | 390 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 32 | 88 | 34 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 183 | 0 | 78 | 0 | 171 | 0 | 411 | 17 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 555 |  | 6465 | 3304 | 9769 | 3867 | 940 | 2066 | 1901 | 705 | 144 | 0 | 146 | 0 | 0 | 88.38
4:00 | 33 | 0 | 0 | 180 | 120 | 23 | 0 | 329 | 353 |  | 0 | 420 | 145 | 0 | 82 | 47 | 296 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 17 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 79 | 65 | 95 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 41 | 0 | 100 | 0 | 340 | 315 | 198 | 8 | 96 | 42 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 142 | 157 | 72 | 20 | 0 | 89 | 30 | 53 | 46 | 163 | 162 | 62 | 79 | 0 | 0 | 18 | 0 | 10 | 300 | 23 | 11 | 0 | 0 | 0 | 0 | 70 | 0 | 105 | 0 | 100 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 234 | 17 | 0 | 0 | 55 | 100 | 0 | 0 |  | 940 | 0 | 390 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 32 | 89 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 188 | 0 | 78 | 0 | 185 | 0 | 417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 |  | 6243 | 3198 | 9441 | 3968 | 940 | 2105 | 1436 | 706 | 144 | 0 | 142 | 0 | 0 | 88.38
5:00 | 33 | 0 | 0 | 180 | 120 | 23 | 0 | 330 | 352 |  | 0 | 420 | 145 | 0 | 79 | 47 | 298 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 17 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 79 | 65 | 95 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0 | 100 | 0 | 320 | 295 | 190 | 8 | 96 | 41 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 138 | 157 | 72 | 20 | 0 | 89 | 30 | 53 | 46 | 163 | 162 | 62 | 79 | 0 | 0 | 18 | 0 | 10 | 300 | 23 | 11 | 0 | 0 | 0 | 0 | 24 | 0 | 84 | 0 | 100 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 55 | 100 | 0 | 0 |  | 941 | 0 | 395 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 32 | 89 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 190 | 0 | 78 | 0 | 187 | 0 | 417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 |  | 6098 | 3207 | 9305 | 3925 | 941 | 2103 | 1349 | 705 | 144 | 0 | 138 | 0 | 0 | 88.39
6:00 | 33 | 0 | 0 | 180 | 120 | 23 | 0 | 324 | 309 |  | 0 | 380 | 140 | 0 | 79 | 47 | 230 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 6 | 33 | 0 | 0 | 0 | 79 | 65 | 95 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 41 | 0 | 100 | 0 | 310 | 260 | 183 | 8 | 90 | 41 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 130 | 159 | 16 | 20 | 0.1 | 89 | 30 | 52 | 46 | 130 | 162 | 62 | 79 | 0 | 0 | 18 | 0 | 10 | 280 | 23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 0.8 | 100 | 0 | 0 | 0 | 115 | 0 | 0 | 0.3 | 178 | 0 | 0 | 0 | 26 | 100 | 0 | 0 |  | 940 | 0 | 395 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 32 | 89 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 159 | 0 | 77 | 0 | 182 | 0 | 389 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 508 |  | 5534.2 | 3021.1 | 8555.3 | 3702 | 940 | 1932 | 1048 | 658 | 144 | 0 | 130 | 1.3 | 0 | 88.39
7:00 | 33 | 0 | 0 | 180 | 120 | 23 | 0 | 322 | 303 |  | 0 | 350 | 140 | 0 | 79 | 47 | 230 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 30 | 33 | 0 | 0 | 0 | 79 | 65 | 95 | 0 | 0 | 0 | 0 | 142 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 35 | 0 | 100 | 0 | 270 | 260 | 183 | 8 | 88 | 38 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 120 | 159 | 8 | 20 | 0.3 | 89 | 30 | 53 | 46 | 130 | 160 | 62 | 77 | 0 | 0 | 18 | 0 | 10 | 295 | 23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 5.3 | 100 | 0 | 0 | 0 | 115 | 0 | 0 | 0.6 | 178 | 0 | 0 | 0 | 26 | 100 | 0 | 0 |  | 940 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 89 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 146 | 0 | 78 | 0 | 161 | 0 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 451 |  | 5453.2 | 2828.2 | 8281.4 | 3634 | 940 | 1840 | 996 | 601 | 144 | 0 | 120 | 6.4 | 0 | 88.4
8:00 | 33 | 0 | 0 | 180 | 120 | 23 | 0 | 322 | 289 |  | 0 | 320 | 140 | 0 | 79 | 47 | 54 | 0 | 40 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 24 | 33 | 16 | 0 | 0 | 80 | 65 | 95 | 0 | 0 | 0 | 0 | 142 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 7 | 0 | 100 | 0 | 275 | 260 | 192 | 8 | 96 | 38 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 116 | 158 | 8 | 20 | 0.3 | 89 | 30 | 53 | 46 | 130 | 162 | 63 | 77 | 0 | 0 | 18 | 0 | 10 | 290 | 23 | 11 | 0 | 21 | 0 | 0 | 0 | 0 | 76 | 0 | 100 | 0 | 0 | 0 | 115 | 0 | 0 | 1.4 | 180 | 0 | 0 | 0 | 0 | 100 | 0 | 0 |  | 936 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 89 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 147 | 0 | 77 | 0 | 158 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 450 |  | 5266.7 | 2848.2 | 8114.9 | 3535 | 936 | 1785 | 996 | 600 | 145 | 0 | 116 | 1.9 | 0 | 88.4
9:00 | 33 | 0 | 0 | 180 | 120 | 23 | 0 | 341 | 354 |  | 0 | 350 | 150 | 0 | 79 | 47 | 0 | 0 | 99 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 20 | 33 | 33 | 0 | 0 | 81 | 65 | 95 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 3 | 0 | 100 | 0 | 300 | 295 | 203 | 8 | 96 | 38 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 118 | 157 | 8 | 20 | 0.2 | 89 | 30 | 53 | 46 | 130 | 161 | 61 | 77 | 0 | 0 | 18 | 0 | 10 | 310 | 23 | 8 | 0 | 56 | 0 | 0 | 0 | 0 | 89 | 6.1 | 90 | 0 | 0 | 0 | 115 | 0 | 0 | 0.8 | 300 | 0 | 0 | 0 | 0 | 100 | 0 | 0 |  | 936 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 89 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 151 | 0 | 77 | 0 | 172 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 435 |  | 5658.1 | 2861.4 | 8519.5 | 3657 | 936 | 1906 | 1164 | 585 | 146 | 0 | 118 | 7.5 | 0 | 88.41
10:00 | 33 | 0 | 0 | 180 | 120 | 58 | 0 | 349 | 356 |  | 0 | 380 | 145 | 0 | 79 | 47 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 53 | 35 | 0 | 0 | 25 | 20 | 33 | 33 | 0 | 0 | 81 | 65 | 95 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 4 | 0 | 100 | 0 | 325 | 270 | 197 | 8 | 95 | 41 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 11 | 118 | 157 | 35 | 20 | 0.9 | 89 | 30 | 50 | 46 | 163 | 160 | 61 | 77 | 0 | 0 | 18 | 0 | 8 | 310 | 23 | 8 | 0 | 147 | 0 | 0 | 0 | 0 | 103 | 2.2 | 90 | 0 | 3 | 0 | 115 | 35 | 0 | 2.1 | 306 | 0 | 0 | 0 | 26 | 100 | 0 | 0 |  | 935 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 89 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 155 | 0 | 77 | 0 | 175 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 410 |  | 6016.2 | 2889.6 | 8905.8 | 3654 | 935 | 2052 | 1435 | 560 | 146 | 0 | 118 | 5.8 | 0 | 88.41
11:00 | 33 | 0 | 0 | 180 | 120 | 76 | 0 | 322 | 300 |  | 0 | 380 | 135 | 0 | 79 | 47 | 0 | 0 | 94 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 53 | 35 | 0 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 82 | 65 | 95 | 0 | 0 | 0 | 0 | 146 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 2 | 0 | 100 | 0 | 310 | 260 | 183 | 8 | 90 | 41 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 6 | 96 | 157 | 71 | 20 | 0.5 | 89 | 30 | 50 | 46 | 130 | 160 | 63 | 77 | 0 | 0 | 18 | 0 | 9 | 290 | 23 | 8 | 0 | 237 | 0 | 0 | 0 | 0 | 108 | 5.8 | 90 | 0 | 83 | 0 | 115 | 35 | 0 | 1.2 | 305 | 0 | 0 | 0 | 113 | 100 | 0 | 50 |  | 935 | 0 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 89 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 148 | 0 | 77 | 0 | 159 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 410 |  | 6188.5 | 2878.1 | 9066.6 | 3578 | 935 | 1971 | 1772 | 560 | 147 | 0 | 96 | 7.6 | 0 | 88.42
12:00 | 33 | 0 | 0 | 180 | 120 | 90 | 0 | 326 | 351 |  | 0 | 400 | 140 | 0 | 79 | 47 | 0 | 0 | 100 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 0 | 19 | 25 | 18 | 33 | 33 | 0 | 0 | 80 | 65 | 95 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 5 | 0 | 100 | 0 | 310 | 260 | 206 | 8 | 87 | 38 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 6 | 94 | 140 | 90 | 20 | 0.7 | 89 | 30 | 50 | 46 | 163 | 161 | 61 | 77 | 0 | 0 | 18 | 0 | 9 | 300 | 16 | 8 | 0 | 264 | 0 | 0 | 0 | 0 | 119 | 6.1 | 90 | 0 | 123 | 0 | 115 | 35 | 0 | 1.4 | 305 | 0 | 0 | 0 | 113 | 100 | 0 | 90 |  | 935 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 89 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 77 | 0 | 165 | 0 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 410 |  | 6471.2 | 2840.4 | 9311.6 | 3576 | 935 | 2057 | 1936 | 560 | 145 | 0 | 94 | 8.6 | 0 | 88.42
13:00 | 33 | 0 | 0 | 180 | 120 | 93 | 0 | 333 | 351 |  | 0 | 400 | 135 | 0 | 79 | 47 | 0 | 0 | 100 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 35 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 79 | 65 | 95 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 7 | 0 | 135 | 0 | 360 | 265 | 189 | 8 | 87 | 41 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 5 | 33 | 8 | 98 | 123 | 90 | 20 | 0.6 | 89 | 30 | 47 | 43 | 163 | 161 | 61 | 77 | 0 | 0 | 18 | 0 | 9 | 300 | 23 | 8 | 0 | 267 | 0 | 0 | 0 | 0 | 125 | 3.9 | 90 | 0 | 142 | 0 | 115 | 35 | 0 | 1.9 | 305 | 0 | 0 | 0 | 113 | 100 | 0 | 90 |  | 935 | 0 | 345 | 0 | 16 | 10 | 0 | 0 | 0 | 0 | 24 | 89 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 10 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 156 | 0 | 75 | 0 | 195 | 0 | 406 | 0 | 0 | 0 | 0 | 14 | 0 | 1.1 | 0 | 410 |  | 6611.4 | 2894.1 | 9505.5 | 3634 | 935 | 2085 | 2032 | 560 | 144 | 10 | 98 | 7.5 | 0 | 88.43
14:00 | 33 | 0 | 0 | 180 | 120 | 93 | 0 | 324 | 300 |  | 0 | 370 | 140 | 0 | 79 | 47 | 0 | 0 | 100 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 75 | 65 | 95 | 0 | 0 | 0 | 0 | 143 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 4 | 0 | 135 | 0 | 280 | 260 | 189 | 8 | 97 | 41 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 5 | 33 | 8 | 102 | 125 | 90 | 20 | 1.4 | 89 | 20 | 50 | 46 | 110 | 160 | 61 | 77 | 0 | 0 | 18 | 0 | 10 | 290 | 23 | 8 | 0 | 267 | 0 | 0 | 0 | 0 | 126 | 4 | 90 | 0 | 142 | 0 | 115 | 35 | 0 | 2 | 307 | 0 | 0 | 0 | 113 | 100 | 0 | 90 |  | 935 | 0 | 345 | 0 | 16 | 10 | 0 | 0 | 0 | 0 | 24 | 89 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 180 | 0 | 76 | 0 | 172 | 0 | 360 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 410 |  | 6408.4 | 2872 | 9280.4 | 3541 | 935 | 1900 | 2085 | 560 | 140 | 10 | 102 | 7.4 | 0 | 88.43
15:00 | 33 | 0 | 0 | 180 | 120 | 90 | 0 | 337 | 300 |  | 0 | 370 | 145 | 0 | 79 | 44 | 0 | 0 | 100 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 74 | 65 | 95 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 4 | 0 | 135 | 0 | 280 | 340 | 196 | 8 | 94 | 36 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 8 | 104 | 124 | 89 | 0 | 0.4 | 90 | 20 | 47 | 43 | 110 | 161 | 61 | 77 | 0 | 30 | 18 | 0 | 10 | 310 | 23 | 8 | 0 | 267 | 0 | 0 | 0 | 0 | 130 | 0 | 90 | 0 | 148 | 0 | 115 | 35 | 0 | 2 | 307 | 0 | 0 | 0 | 113 | 100 | 0 | 90 |  | 936 | 0 | 395 | 0 | 16 | 15 | 0 | 0 | 0 | 0 | 24 | 89 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 158 | 0 | 77 | 0 | 171 | 0 | 365 | 0 | 0 | 0 | 0 | 40 | 0 | 0.6 | 0 | 407 |  | 6528.4 | 2902.6 | 9431 | 3670 | 936 | 1911 | 2097 | 556 | 139 | 15 | 104 | 3 | 0 | 84.43
16:00 | 33 | 0 | 0 | 180 | 120 | 91 | 0 | 324 | 300 |  | 0 | 340 | 140 | 0 | 79 | 32 | 0 | 0 | 99 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 74 | 65 | 95 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 4 | 0 | 135 | 0 | 260 | 270 | 189 | 8 | 93 | 40 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 8 | 120 | 125 | 80 | 17 | 0.5 | 90 | 20 | 52 | 43 | 110 | 161 | 61 | 77 | 0 | 100 | 18 | 0 | 10 | 290 | 23 | 8 | 0 | 195 | 0 | 0 | 0 | 0 | 133 | 2 | 90 | 0 | 50 | 0 | 115 | 17 | 0 | 1 | 200 | 0 | 0 | 0 | 105 | 100 | 0 | 90 |  | 934 | 0 | 395 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 8 | 89 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 10 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 148 | 0 | 77 | 0 | 160 | 0 | 362 | 0 | 0 | 0 | 0 | 35 | 0 | 1.1 | 0 | 407 |  | 6146.5 | 2844.1 | 8990.6 | 3631 | 934 | 1866 | 1725 | 556 | 139 | 15 | 120 | 4.6 | 0 | 88.44
17:00 | 33 | 0 | 0 | 180 | 120 | 91 | 0 | 322 | 270 |  | 0 | 320 | 138 | 0 | 79 | 47 | 0 | 0 | 100 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 29 | 33 | 33 | 0 | 0 | 75 | 65 | 95 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 0 | 135 | 0 | 265 | 270 | 191 | 8 | 90 | 42 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 8 | 116 | 140 | 40 | 20 | 0.1 | 90 | 22 | 53 | 43 | 110 | 160 | 61 | 77 | 0 | 100 | 18 | 0 | 10 | 300 | 23 | 8 | 0 | 195 | 0 | 0 | 0 | 0 | 132 | 0.7 | 90 | 0 | 50 | 0 | 115 | 17 | 0 | 1.1 | 104 | 0 | 0 | 0 | 36 | 100 | 0 | 52 |  | 935 | 0 | 400 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 89 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 10 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 147 | 0 | 77 | 0 | 159 | 0 | 364 | 0 | 0 | 0 | 0 | 34 | 0 | 1.1 | 0 | 407 |  | 5912.9 | 2843.1 | 8756 | 3659 | 935 | 1838 | 1494 | 556 | 140 | 15 | 116 | 3 | 0 | 88.45
18:00 | 33 | 0 | 0 | 180 | 120 | 90 | 0 | 325 | 250 |  | 0 | 300 | 147 | 0 | 79 | 47 | 0 | 0 | 100 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 29 | 17 | 33 | 0 | 0 | 77 | 65 | 95 | 0 | 0 | 0 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 0 | 135 | 0 | 270 | 270 | 196 | 8 | 96 | 42 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 15 | 116 | 140 | 40 | 20 | 0 | 90 | 22 | 53 | 40 | 110 | 160 | 52 | 20 | 0 | 50 | 18 | 0 | 10 | 300 | 16 | 11 | 0 | 195 | 0 | 0 | 0 | 0 | 133 | 0.2 | 90 | 0 | 50 | 0 | 115 | 17 | 0 | 0.1 | 106 | 0 | 0 | 0 | 36 | 100 | 0 | 52 |  | 935 | 0 | 345 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 89 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 10 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 152 | 0 | 77 | 0 | 164 | 0 | 363 | 0 | 0 | 0 | 0 | 34 | 0 | 0.7 | 0 | 408 |  | 5735.3 | 2798.7 | 8534 | 3526 | 935 | 1736 | 1506 | 557 | 142 | 15 | 116 | 1 | 0 | 88.46
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 33 | 0 | 0 | 180 | 120 | 93 | 0 | 347 | 300 |  | 0 | 300 | 150 | 0 | 79 | 47 | 0 | 0 | 100 | 0 | 0 | 102 | 133 | 35 | 0 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 20 | 17 | 33 | 8 | 0 | 79 | 65 | 95 | 0 | 1 | 0 | 0 | 104 | 0 |  | 0 | 0 | 85 | 10 | 20 | 2 | 20 | 22 | 0 | 135 | 0 | 285 | 290 | 204 | 8 | 96 | 42 | 5 | 0 | 43 | 0 | 0 | 2 | 22 | 8 | 33 | 18 | 144 | 140 | 46 | 20 | 0 | 90 | 32 | 53 | 46 | 110 | 161 | 61 | 20 | 0 | 150 | 18 | 0 | 10 | 315 | 16 | 11 | 0 | 212 | 0 | 0 | 17 | 0 | 133 | 0 | 90 | 0 | 70 | 0 | 115 | 45 | 0 | 0 | 160 | 5 | 0 | 51 | 57 | 100 | 0 | 52 |  | 934 | 0 | 345 | 0 | 49 | 15 | 0 | 0 | 0 | 0 | 16 | 89 | 35 | 49 | 0 | 0 | 0 | 10 | 0 | 50 | 0 | 0 | 13 | 19 | 4 | 21 | 10 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 162 | 0 | 75 | 0 | 174 | 0 | 417 | 0 | 0 | 8 | 0 | 46 | 0 | 0 | 0 | 453 |  | 6463 | 3154 | 9617 | 3726 | 934 | 1883 | 1959 | 602 | 144 | 225 | 144 | 0 | 0 | 88.47
19:30 | 33 | 0 | 0 | 180 | 120 | 93 | 0 | 321 | 300 |  | 0 | 300 | 130 | 0 | 79 | 47 | 0 | 0 | 91 | 0 | 0 | 102 | 116 | 86 | 0 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 22 | 17 | 33 | 32 | 0 | 81 | 65 | 95 | 0 | 16 | 0 | 0 | 139 | 0 |  | 0 | 0 | 85 | 10 | 80 | 40 | 20 | 22 | 0 | 135 | 0 | 260 | 265 | 183 | 8 | 85 | 42 | 5 | 0 | 43 | 0 | 0 | 43 | 22 | 11 | 33 | 21 | 142 | 146 | 56 | 20 | 0 | 90 | 32 | 53 | 46 | 110 | 162 | 62 | 80 | 0 | 150 | 18 | 0 | 10 | 280 | 16 | 11 | 0 | 250 | 0 | 0 | 50 | 0 | 133 | 0 | 100 | 0 | 90 | 0 | 115 | 88 | 0 | 0 | 251 | 54 | 0 | 114 | 113 | 100 | 0 | 90 |  | 934 | 0 | 345 | 0 | 115 | 15 | 0 | 0 | 0 | 0 | 33 | 89 | 38 | 85 | 0 | 0 | 0 | 38 | 0 | 90 | 0 | 0 | 46 | 43 | 20 | 21 | 10 | 11 | 0 | 0 | 149 | 0 | 10 | 0 | 0 | 166 | 0 | 75 | 0 | 170 | 0 | 410 | 0 | 0 | 50 | 0 | 100 | 0 | 0 | 0 | 542 |  | 7065 | 3605 | 10670 | 3660 | 934 | 1904 | 2858 | 691 | 146 | 335 | 142 | 0 | 0 | 0
20:00 | 33 | 0 | 0 | 180 | 120 | 93 | 0 | 325 | 300 |  | 0 | 300 | 130 | 0 | 79 | 47 | 0 | 0 | 92 | 0 | 0 | 102 | 82 | 90 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 22 | 17 | 33 | 0 | 0 | 81 | 65 | 95 | 0 | 25 | 0 | 0 | 139 | 0 |  | 0 | 0 | 85 | 0 | 89 | 48 | 20 | 25 | 0 | 135 | 0 | 260 | 260 | 183 | 8 | 85 | 42 | 5 | 0 | 43 | 0 | 0 | 37 | 22 | 11 | 33 | 21 | 144 | 146 | 56 | 20 | 0 | 90 | 32 | 53 | 43 | 110 | 162 | 63 | 80 | 0 | 150 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 260 | 0 | 0 | 50 | 0 | 133 | 0 | 100 | 0 | 140 | 0 | 115 | 80 | 0 | 0 | 185 | 41 | 0 | 9 | 113 | 100 | 0 | 72 |  | 935 | 0 | 345 | 0 | 115 | 15 | 0 | 0 | 0 | 0 | 33 | 89 | 38 | 110 | 0 | 0 | 0 | 50 | 0 | 100 | 0 | 0 | 47 | 52 | 34 | 21 | 10 | 11 | 0 | 0 | 149 | 0 | 10 | 0 | 0 | 168 | 0 | 76 | 0 | 168 | 0 | 380 | 0 | 0 | 51 | 0 | 96 | 0 | 0 | 0 | 546 |  | 6877 | 3649 | 10526 | 3672 | 935 | 1875 | 2721 | 695 | 146 | 338 | 144 | 0 | 0 | 88.48
21:00 | 33 | 0 | 0 | 180 | 120 | 93 | 0 | 342 | 350 |  | 0 | 420 | 145 | 0 | 79 | 47 | 0 | 0 | 100 | 0 | 0 | 102 | 48 | 100 | 0 | 0 | 0 | 53 | 55 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 81 | 65 | 95 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 34 | 0 | 97 | 32 | 20 | 30 | 0 | 135 | 0 | 305 | 270 | 191 | 8 | 96 | 42 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 148 | 144 | 95 | 20 | 0 | 90 | 32 | 53 | 46 | 130 | 161 | 61 | 80 | 0 | 150 | 18 | 0 | 10 | 315 | 24 | 11 | 0 | 270 | 0 | 0 | 50 | 0 | 132 | 0 | 100 | 0 | 148 | 0 | 115 | 52 | 0 | 0 | 195 | 54 | 0 | 0 | 113 | 100 | 0 | 90 |  | 935 | 0 | 365 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 89 | 40 | 96 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 149 | 0 | 10 | 0 | 0 | 186 | 0 | 78 | 0 | 182 | 0 | 418 | 0 | 0 | 89 | 0 | 110 | 0 | 0 | 0 | 545 |  | 7164 | 3589 | 10753 | 3848 | 935 | 2151 | 2674 | 694 | 146 | 157 | 148 | 0 | 0 | 88.49
22:00 | 33 | 0 | 0 | 180 | 120 | 93 | 0 | 323 | 357 |  | 0 | 420 | 130 | 0 | 79 | 47 | 0 | 0 | 97 | 0 | 0 | 102 | 48 | 63 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 82 | 65 | 95 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 34 | 0 | 97 | 10 | 20 | 38 | 0 | 135 | 0 | 320 | 265 | 183 | 8 | 86 | 42 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 146 | 143 | 95 | 20 | 0 | 90 | 32 | 53 | 43 | 110 | 162 | 61 | 80 | 0 | 150 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 267 | 0 | 0 | 50 | 0 | 133 | 0 | 100 | 0 | 148 | 0 | 115 | 35 | 0 | 0 | 198 | 54 | 0 | 0 | 113 | 100 | 0 | 90 |  | 935 | 0 | 355 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 33 | 89 | 41 | 96 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 0 | 0 | 0 | 150 | 0 | 10 | 0 | 0 | 176 | 0 | 78 | 1 | 172 | 0 | 386 | 0 | 0 | 70 | 0 | 112 | 0 | 0 | 0 | 527 |  | 7073 | 3478 | 10551 | 3775 | 935 | 2097 | 2616 | 677 | 147 | 158 | 146 | 0 | 0 | 88.5
23:00 | 33 | 0 | 0 | 180 | 120 | 93 | 0 | 329 | 356 |  | 0 | 400 | 145 | 0 | 79 | 47 | 10 | 0 | 97 | 0 | 0 | 102 | 48 | 0 | 0 | 0 | 0 | 53 | 45 | 55 | 22 | 25 | 26 | 33 | 33 | 0 | 0 | 82 | 65 | 95 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 34 | 0 | 91 | 0 | 20 | 32 | 0 | 100 | 0 | 335 | 285 | 188 | 8 | 95 | 42 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 146 | 142 | 90 | 20 | 0 | 90 | 32 | 53 | 43 | 110 | 0 | 61 | 80 | 0 | 150 | 18 | 0 | 10 | 295 | 24 | 11 | 0 | 270 | 0 | 0 | 50 | 0 | 133 | 0 | 100 | 0 | 50 | 0 | 115 | 0 | 0 | 0 | 198 | 54 | 0 | 0 | 113 | 100 | 0 | 90 |  | 936 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 33 | 88 | 39 | 96 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 0 | 0 | 0 | 150 | 0 | 12 | 0 | 0 | 180 | 0 | 78 | 50 | 178 | 0 | 420 | 0 | 0 | 35 | 0 | 112 | 0 | 0 | 0 | 527 |  | 6691 | 3526 | 10217 | 3633 | 936 | 2097 | 2421 | 677 | 147 | 160 | 146 | 0 | 0 | 88.51
24:00 | 33 | 0 | 0 | 180 | 120 | 93 | 0 | 342 | 356 |  | 0 | 400 | 135 | 0 | 79 | 47 | 23 | 0 | 40 | 0 | 0 | 102 | 48 | 0 | 0 | 0 | 0 | 53 | 45 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 83 | 65 | 95 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 34 | 0 | 90 | 0 | 20 | 32 | 0 | 100 | 0 | 320 | 260 | 154 | 8 | 91 | 30 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 15 | 120 | 157 | 95 | 20 | 0 | 90 | 32 | 53 | 46 | 110 | 0 | 61 | 80 | 0 | 150 | 0 | 0 | 10 | 315 | 24 | 11 | 0 | 268 | 0 | 0 | 50 | 0 | 133 | 0 | 100 | 0 | 50 | 0 | 115 | 0 | 0 | 0 | 198 | 54 | 0 | 0 | 113 | 100 | 0 | 90 |  | 935 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 33 | 89 | 39 | 96 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 0 | 0 | 0 | 150 | 0 | 12 | 0 | 0 | 188 | 0 | 77 | 50 | 186 | 0 | 423 | 0 | 0 | 35 | 0 | 112 | 0 | 0 | 0 | 527 |  | 6555 | 3544 | 10099 | 3524 | 935 | 2122 | 2413 | 677 | 148 | 160 | 120 | 0 | 0 | 88.52
KWH | 643000 | 0 | 0 | 4268250 | 2876200 | 1486636 | 0 | 8078276 | 7810000 |  | 0 | 8914250 | 3407680 | 0 | 1970592 | 1121885 | 2156983 | 0 | 1603000 | 0 | 0 | 2367360 | 348000 | 381270 | 0 | 0 | 0 | 1153440 | 898722 | 717783 | 314064 | 600000 | 630900 | 774300 | 754400 | 46656 | 0 | 1833905 | 1552000 | 2200000 | 0 | 34585 | 0 | 0 | 3289526 | 0 |  | 0 | 0 | 274478 | 11160 | 654720 | 99840 | 461232 | 528960 | 0 | 2750810 | 0 | 7516900 | 6754000 | 4614000 | 217454 | 2224290 | 934272 | 138240 | 0 | 1023820 | 0 | 0 | 114187 | 507384 | 213660 | 819500 | 391390 | 3083520 | 3432280 | 1562880 | 414648 | 5550 | 2111000 | 657410 | 1245000 | 1068552 | 3283773 | 3435000 | 1452768 | 1752960 | 0 | 1054720 | 421000 | 0 | 237780 | 7362500 | 544255 | 237024 | 0 | 4315634 | 0 | 0 | 772800 | 0 | 2820960 | 46980 | 2278080 | 0 | 1771418 | 0 | 2806800 | 548796 | 13381 | 18720 | 5427163 | 432870 | 0 | 106020 | 2001720 | 2414400 | 0 | 1104000 |  | 22477090 | 0 | 9148032 | 0 | 1235520 | 89843 | 0 | 0 | 0 | 0 | 548250 | 2149342 | 714338 | 795840 | 0 | 0 | 0 | 41494 | 0 | 589416 | 0 | 0 | 55565 | 72480 | 31884 | 494160 | 245160 | 182268 | 0 | 0 | 3671300 | 0 | 51000 | 0 | 0 | 4222500 | 0 | 1864313 | 148800 | 4365218 | 0 | 9331727 | 100320 | 0 | 540480 | 0 | 1041600 | 0 | 8039 | 0 | 12384300 |  | 152451844 | 76600279 | 229052123 | 89203802 | 22477090 | 47719623 | 45840092 | 16055600 | 3385905 | 1207202 | 3083520 | 79289 | 0
Fuel Cost | 1054520 | 0 | 0 | 6274327.5 | 3192582 | 1962359.52 | 0 | 8159058.76 | 8044300 |  | 0 | 9716532.5 | 3782524.8 | 0 | 13577378.88 | 9491147.1 | 2243262.32 | 0 | 2773190 | 0 | 0 | 21590323.2 | 3424320 | 3515309.4 | 0 | 0 | 0 | 8420112 | 6947121.06 | 7077340.38 | 235548 | 450000 | 0 | 0 | 0 | 451163.52 | 0 | 495154.35 | 419040 | 3982000 | 0 | 321294.65 | 0 | 0 | 5592194.2 | 0 |  | 0 | 0 | 0 | 106578 | 5696064 | 790732.8 | 581152.32 | 1571011.2 | 0 | 4071198.8 | 0 | 5562506 | 6754000 | 4244880 | 280515.66 | 2557933.5 | 1055727.36 | 193536 | 0 | 1750732.2 | 0 | 0 | 1090485.85 | 644377.68 | 160245 | 1434125 | 293542.5 | 23126400 | 3638216.8 | 14190950.4 | 526602.96 | 88467 | 3462040 | 1051856 | 2216100 | 1666941.12 | 3743501.22 | 3572400 | 2861952.96 | 3348153.6 | 0 | 1824665.6 | 921990 | 0 | 485071.2 | 7436125 | 408191.25 | 180138.24 | 0 | 32626193.04 | 0 | 0 | 4018560 | 0 | 27758246.4 | 549196.2 | 18566352 | 0 | 12488496.9 | 0 | 25598016 | 5186122.2 | 116548.51 | 0 | 41029352.28 | 3770297.7 | 0 | 1058079.6 | 17154740.4 | 16079904 | 0 | 0 |  | 129468038.4 | 0 | 9605433.6 | 0 | 9711187.2 | 1245223.98 | 0 | 0 | 0 | 0 | 5712765 | 2428756.46 | 1107223.9 | 7767398.4 | 0 | 0 | 0 | 408300.96 | 0 | 5216331.6 | 0 | 0 | 538424.85 | 702331.2 | 309274.8 | 948787.2 | 379998 | 137976.876 | 0 | 0 | 19898446 | 0 | 1455030 | 0 | 0 | 5573700 | 0 | 2796469.5 | 2531088 | 5107305.06 | 0 | 9238409.73 | 1047340.8 | 0 | 5129155.2 | 0 | 8082816 | 0 | 88830.95 | 0 | 54367077 |  | 452781316.59 | 291003120.666 | 743784437.256 | 102617596.746 | 129468038.4 | 56885767.55 | 343183516.87 | 74265523 | 914194.35 | 12596906.19 | 23126400 | 726494.15 | 0
Yesterday Day Peak | 33 | 0 | 0 | 180 | 120 | 90 | 0 | 326 | 351 |  | 0 | 400 | 140 | 0 | 79 | 47 | 0 | 0 | 100 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 0 | 19 | 25 | 18 | 33 | 33 | 0 | 0 | 80 | 65 | 95 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 5 | 0 | 100 | 0 | 310 | 260 | 206 | 8 | 87 | 38 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 6 | 94 | 140 | 90 | 20 | 0.7 | 89 | 30 | 50 | 46 | 163 | 161 | 61 | 77 | 0 | 0 | 18 | 0 | 9 | 300 | 16 | 8 | 0 | 264 | 0 | 0 | 0 | 0 | 119 | 6.1 | 90 | 0 | 123 | 0 | 115 | 35 | 0 | 1.4 | 305 | 0 | 0 | 0 | 113 | 100 | 0 | 90 |  | 935 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 89 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 77 | 0 | 165 | 0 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 410 |  | 9311.6 | DayPeak
Yesterday Evening Peak | 33 | 0 | 0 | 180 | 120 | 93 | 0 | 342 | 350 | 0 | 0 | 420 | 145 | 0 | 79 | 47 | 0 | 0 | 100 | 0 | 0 | 102 | 48 | 100 | 0 | 0 | 0 | 53 | 55 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 81 | 65 | 95 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 34 | 0 | 97 | 32 | 20 | 30 | 0 | 135 | 0 | 305 | 270 | 191 | 8 | 96 | 42 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 148 | 144 | 95 | 20 | 0 | 90 | 32 | 53 | 46 | 130 | 161 | 61 | 80 | 0 | 150 | 18 | 0 | 10 | 315 | 24 | 11 | 0 | 270 | 0 | 0 | 50 | 0 | 132 | 0 | 100 | 0 | 148 | 0 | 115 | 52 | 0 | 0 | 195 | 54 | 0 | 0 | 113 | 100 | 0 | 90 |  | 935 | 0 | 365 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 89 | 40 | 96 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 149 | 0 | 10 | 0 | 0 | 186 | 0 | 78 | 0 | 182 | 0 | 418 | 0 | 0 | 89 | 0 | 110 | 0 | 0 | 0 | 545 |  | 10787 | EvPeak
Forecast for Evening | 35 | 0 | 0 | 0 | 120 | 93 | 70 | 412 | 360 | 0 | 0 | 450 | 150 | 0 | 81 | 47 | 217 | 0 | 100 | 0 | 0 | 100 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 50 | 0 | 82 | 65 | 95 | 0 | 25 | 0 | 0 | 150 | 0 | 0 | 0 |  | 102 | 100 | 100 | 50 | 20 | 20 | 0 | 100 | 0 | 360 | 360 | 216 | 8 | 95 | 46 | 55 | 0 | 43 | 0 | 42 | 43 | 22 | 11 | 33 | 21 | 173 | 160 | 95 | 22 | 0 | 90 | 30 | 51 | 44 | 163 | 163 | 66 | 80 | 0 | 151 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 133 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 90 |  | 946 | 16 | 410 | 0 | 115 | 225 | 0 | 0 | 30 | 60 | 40 | 89 | 33 | 110 | 0 | 0 | 60 | 50 | 40 | 100 | 0 | 50 | 45 | 52 | 35 | 22 | 11 | 11 | 0 | 0 | 150 | 0 | 12 | 0 | 0 | 200 | 0 | 79 | 100 | 210 | 0 | 410 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 600
Forecast for Day | 35 | 0 | 0 | 0 | 120 | 93 | 70 | 412 | 360 | 0 | 0 | 450 | 150 | 0 | 81 | 47 | 217 | 0 | 100 | 0 | 0 | 100 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 35 | 0 | 82 | 65 | 95 | 0 | 25 | 0 | 0 | 150 | 0 | 0 | 0 |  | 100 | 100 | 100 | 50 | 20 | 10 | 0 | 100 | 0 | 360 | 360 | 216 | 8 | 95 | 46 | 51 | 0 | 43 | 0 | 0 | 43 | 22 | 11 | 33 | 21 | 154 | 160 | 95 | 22 | 1.6 | 90 | 30 | 51 | 44 | 163 | 163 | 61 | 80 | 0 | 151 | 18 | 0 | 10 | 341 | 24 | 11 | 0 | 300 | 100 | 50 | 170 | 80 | 133 | 20 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 5 | 300 | 50 | 50 | 114 | 113 | 100 | 0 | 90 |  | 946 | 0 | 410 | 0 | 115 | 10 | 0 | 0 | 20 | 48 | 40 | 89 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 50 | 43 | 52 | 0 | 22 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 200 |  | 78 | 60 | 210 | 0 | 410 | 105 | 0 | 70 | 100 | 90 | 0 | 8 | 70 | 600
Generation at 08:00(Today) | 33 | 0 | 0 | 110 | 120 | 93 | 0 | 327 | 289 | 0 | 0 | 370 | 150 | 0 | 30 | 15 | 180 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 30 | 33 | 32 | 0 | 0 | 80 | 65 | 95 | 0 | 0 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 2 | 0 | 80 | 0 | 290 | 275 | 190 | 8 | 97 | 20 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 33 | 0 | 100 | 159 | 16 | 20 | 0.1 | 90 | 32 | 50 | 46 | 110 | 101 | 59 | 20 | 0 | 151 | 0 | 0 | 10 | 305 | 0 | 11 | 0 | 14 | 0 | 0 | 7 | 0 | 113 | 5.6 | 70 | 0 | 0 | 0 | 45 | 17 | 0 | 1 | 70 | 0 | 0 | 0 | 17 | 100 | 0 | 54 | 0 | 936 | 0 | 405 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 16 | 89 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 153 | 0 | 76 | 0 | 164 | 0 | 375 | 0 | 0 | 0 | 0 | 34 | 0 | 0.5 | 0 | 470 | 0
199
| Minimum Generation |  | 8114.9 | 8:00
| Highest Generation |  | 10753 | 21:00
| Day Peak Generation |  | 9311.6 | 12:00
| Evening Peak Generation |  | 10787 | 21:00
| HVDC Max Flow |  | 941 | 5:00
| HVDC EvPeak Flow |  | 935 | 21:00
| Load factor L.F |  | 88.76%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-07-21
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-07-20 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9311.6 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 8093.53 | MW
Evening Peak Generation : |  | 10787 | MW Hour : | 21:00 | Available Max Generation : |  | 14832 | MW
E.P. Demand (at gen end) : |  | 10787 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 11000 | MW
Maximum Generation : |  | 10753 | MW Hour : | 21:00 | Reserve(Generation end) |  | 3832 | MW
Total Gen. (MKWH) : |  | 229.0521 | System Load Factor : | 88.76% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -10 | MW at | 21:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-07-21
Actual : | 88.64 | Ft.(MSL) , | Rule curve : | 87.2 | Ft.( MSL )
Gas Consumed : | Total = | 1136.44 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 159503364.296
: |  | Coal : | 74265523 | Oil : | 355780423.06 | Total : | 589549310.356
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3895.1298 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1324.1768 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1186.3503 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1071.9433 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 968.713 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 781.7162 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 437.59 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 201.2839 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 602.896 |  |  | 0 | 0%
Total | 0 |  | 10469.7993 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Bibiyana #3
3) Ghorasal Unit-2,3,4,5
4) Ashuganj unit-3,5
5) Bhola-225 MW GT-2 & ST
6) Kaptai-2
7) Raozan # 2
8) Sirajganj #1
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Goalpara-Khulna 225 MW 132 kV Ckt was under shut down from 08:47 to 14:41 due to red hot maintenance
at Goalpara end.
b) Siddhirganj 335 MW GT was shut down from 08:38 to 22:55 for air filter changing.
c) Hasnabad 230/132 kV T2 transformer was shut down from 12:32 to 16:42 for C/M.
d) Hathazari-Raozan 230 kV Ckt-1 was under shut down from 09:10 to 12:27 for C/M.
e) Ishurdi 230/132 kV T2 transformer was shut down from 10:11 to 13:42 for C/M.
f) Purbasadipur-Thakurgaon 132 kV Ckt-1 was under shut down from 10:20 to 14:02 for C/M.
g) Purbasadipur 132 kV T2 transformer was shut down from 11:25 to 17:04 for C/M.
h) Kishoreganj 132/33 kV T1 & T2 transformer tripped at 12:03 due to fire at 33 kV PDB feeder under 11 kV |  |  |  |  | About 55 MW power interruption was occurred under Kishoreganj S/S
control panel board and were switched on at 12:53,12:57 respectively. |  |  |  |  | areas from 12:03 to 12:53.
i) After maintenance Hathazari-Baroierhat kV Ckt-2 was switched on at 15:04.
j) After maintenance Sylhet 150 MW was synchronized at 14:48.
k) Khulna 225 MW CCPP GT tripped at 20:59 due to tripping of fuel pump and was synchronized at 00:21.
l) Shajibazar 330 MW CCPP GT-1 tripped at 22:20 due to tripping of gas buster and was synchronized at 00:56.
m) Kulshi 132/33 kV T1 transformer was shut down from 01:40 to 02:46 for red hot maintenance at 33 kV bus |  |  |  |  | About 25 MW power interruption was occurred under Kulshi S/S
isolator. |  |  |  |  | areas from 01:40 to 02:46.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-07-21 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 33 | 643000 | Unit-2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4268250
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 120 | 2876200
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 93 | 1486636
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 342 | 8078276 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 350 | 7810000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 8914250 | frequency control.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Fuel Shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 145 | 3407680 | FGMO & GT-1 Under maint.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 79 | 1970592 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 47 | 1121885
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 100 | 381270
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 314064
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 100 | 1603000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Fuel Shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 2156983 | Machine problem.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 2367360
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel Shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 1153440
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 48 | 348000 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 898722
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 717783 | tripped at 20:55.
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1230900 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 774300 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 754400
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 46656 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 270 | 4315634 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 132 | 2820960 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 52 | 548796 | Low demand
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 1104000 | Engine problem
| Dhaka area Total |  |  |  | 5895 | 2954 | 62113037
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 95 | 2200000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 34585 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 46980
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 32 | 99840 | Low demand
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 146 | 3385905 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under S/D.
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 145 | 3289526 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 13381 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 274478 | Reserve
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 11160 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2278080
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 461232
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 30 | 528960
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 97 | 654720
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 18720
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 195 | 5427163 | Low demand
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 432870
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2414400
| Chattogram area Total |  |  |  | 2266 | 1048 | 21572000
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 135 | 2750810 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 191 | 4614000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 305 | 7516900 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 6754000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 42 | 934272
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 138240 | Gas Shortage
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 1023820 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 148 | 1771418
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 96 | 2224290 | ST under maint.
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 507384
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 213660
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 148 | 3083520 | Low demand
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 819500
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 114187 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 391390
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 106020 | Reserve
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 2001720
| Cumilla Area Total |  |  |  | 2980 | 1591 | 35182585
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 144 | 3432280 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 414648
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 95 | 1562880
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 5550
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 50 | 772800
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2806800 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 424 | 8994958
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 90 | 2111000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 32 | 657410 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3283773 | frequency control.
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 161 | 3435000
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1245000
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 46 | 1068552
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 237024
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 61 | 1452768 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1752960
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 150 | 1054720 | Synchronized at 14:48.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 421000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 544255
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7362500 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 237780
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1181 | 24863742
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 935 | 22477090
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 1235520
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 89843 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 365 | 9148032 | Gas shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 548250
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 148800 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 100320 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Reserve
| Khulna Area Total |  |  |  | 2284 | 1455 | 33747855
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 96 | 795840 | Low demand
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 40 | 714338
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 89 | 2149342 | GT-2 Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 78 | 1864313 | Engine problem
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 545 | 12384300
| Barisal Area Total |  |  |  | 1054 | 848 | 17908133
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 41494
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 55565 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage.
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 186 | 4222500 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 182 | 4365218 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 418 | 9331727 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 31884 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 494160
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 10 | 245160 | Engine problem
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 182268
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 72480 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 99 | 589416
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 89 | 540480 | Low demand
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | Reserve
| Rajshahi Area Total |  |  |  | 2183 | 1017 | 20172352
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 149 | 3671300 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 10 | 51000
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 110 | 1041600
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 8039
| Rangpur Area Total |  |  |  | 605 | 269 | 4771939
| Total |  |  |  | 19892 | 10787 | 229326601
| Eastern Grid Total |  |  |  | 13766 | 7198 | 152726322
| Western Grid Total |  |  |  | 6126 | 3589 | 76600279
| National Grid Total |  |  |  | 19892 | 10787 | 229326601
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-07-21
(a) ENTIRE EASTERN GRID : |  | 6882 | MW | (b) ENTIRE WESTERN GRID : |  | 3374 | MW
i) Dhaka area |  | 3620 | MW | i) Khulna area |  | 1307 | MW
ii) Chittagong area |  | 1086 | MW | ii) Rajshahi area |  | 1031 | MW
iii) Comilla area |  | 1043 | MW | iii) Barisal area |  | 326 | MW
iv) Mymensingh area |  | 712 | MW | iv) Rangpur area |  | 710 | MW
v) Sylhet area |  | 421 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 10256 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 134 | 15:00 | Sherpur | 80 | 1:00 | Jhenida | 90 | 19:30
Munsiganj | 116 | 21:00 | Srimongal | 43 | 19:30 | Bottail | 114 | 19:30
Sonargaon | 78 | 21:00 | Shahjibazar | 107 | 22:00 | G.K Project | 51 | 20:00
Shyampur | 188 | 10:00 | Fenchuganj | 42 | 19:30 | Faridpur | 162 | 0.8125
Bhulta | 200 | 1:00 | Kulawara | 46 | 19:30 | Madaripur | 90 | 0.041667
Madanganj | 67 | 15:00 | Sylhet | 108 | 19:30 | Sariatpur | 60 | 1:00
Shitalakhya | 114 | 15:00 | Chatak | 25 | 19:00 | Gopalganj | 87 | 19:30
Rahim steel | 27 | 19:00 | Sunamganj | 35 | 19:00 | Bagerhat | 92 | 19:30
Matuail | 83 | 16:00 | Biani Bazar | 48 | 19:00 | Mongla | 34 | 1:00
Ghorasal | 76 | 21:00 | Comilla (S) | 148 | 21:00 | Satkhira | 103 | 0.875
Narsingdi | 144 | 21:00 | Comilla(N) | 89 | 19:00 | Gallamari | 48 | 14:00
Haripur (SBU) | 95 | 17:00 | Chandpur | 102 | 21:00 | Magura | 40 | 0.041667
Ullon | 53 | 13:00 | Feni | 108 | 19:30 | Norail | 36 | 1:00
Hasnabad | 190 | 19:00 | Chowmuhani | 164 | 21:00 | Chuadanga | 84 | 20:00
Magbazar | 91 | 14:00 | Ashuganj | 54 | 19:00 | Barisal(N) | 44 | 0.91667
Maniknagar | 90 | 13:00 | Daudkandi | 120 | 21:00 | Barisal (S) | 90 | 0.041667
Bangabhaban | 28 | 11:00 | B.Baria | 135 | 22:00 | Patuakhali | 115 | 0.91667
Narinda | 90 | 13:00 | Ramganj | 104 | 22:00 | Bhandaria | 50 | 0.8125
Dhanmondi | 165 | 13:00 | Chaddagram | 34 | 19:30 | Borhan Uddin | 42 | 20:00
Lalbag | 83 | 12:00 | PHP | 8 | 17:00 | Ishurdi | 56 | 20:00
Madartek | 64 | 19:30 | Madunaghat | 48 | 20:00 | Ruppur Paromanobik | 2 | 20:00
Dhaka University |  |  | Hathazari | 91 | 0.79167 | Natore | 103 | 20:00
Fatullah | 28 | 0.5 | Khulshi | 176 | 0.5 | Bogra | 134 | 1:00
Mirpur | 97 | 15:00 | Halishahar | 126 | 0.58333 | Noagaon | 100 | 1:00
Kalyanpur | 84 | 15:00 | Baraulia | 124 | 0.041667 | Rajshahi | 122 | 21:00
Gulshan | 118 | 13:00 | Sikalbaha | 22 | 0.79167 | Rajshahi New | 8 | 21:00
Uttara | 75 | 15:00 | Dohazari | 176 | 0.375 | C.Nawabganj | 60 | 21:00
Uttara New | 28 | 15:00 | Cox'sbazar | 83 | 0.875 | Amnura | 42 | 21:00
Kamrangirchar | 83 | 12:00 | Chandraghona | 28 | 0.79167 | Pabna | 111 | 19:30
Savar | 123 | 19:00 | Kaptai | 4.2 | 0.83333 | Shahjadpur | 93 | 20:00
Bhasantec | 142 | 14:00 | A. Khaer Stl. | 0 | 0.041667 | Serajganj | 79 | 12:00
Agargaon | 64 | 15:00 | Bakulia | 93 | 0.5 | Niyamatpur | 51 | 21:00
Satmosjid | 97 | 14:00 | Julda | 19 | 0.041667 | Joypurhat | 51 | 20:00
Tongi | 128 | 0.5 | TK chemical | 23 | 0.79167 | Sherpur(Bogura) | 40 | 19:00
Kabirpur | 198 | 10:00 | Modern Steel | 15 | 0.95833 | Mohastangor | 42 | 21:00
Basundhara | 125 | 14:00 | Shahmirpur | 26 | 0 | Rangpur | 140 | 20:00
Manikganj | 62 | 21:00 | Khagrachhari | 22 | 0.83333 | Lalmonirhat | 56 | 20:00
Joydevpur | 172 | 11:00 | Matarbari | 28.5 | 0.8125 | Saidpur | 103 | 20:00
New Tongi | 99 | 11:00 | Baroiar Hat | 34 | 0.79167 | Purbasadipur | 108 | 19:30
Korda | 202 | 9:00 | Rangamati | 10 | 0.79167 | Thakurgaon | 78 | 21:00
Dhamrai | 94 | 19:30 | Abul Khair 230 | 161 | 0.375 | Palashbari | 110 | 21:00
Rajendrapur | 88 | 22:00 | BSRM | 110 | 0.041667 | Barapukuria | 49 | 19:30
Valuka | 110 | 20:00 | GPH Ispat | 69 | 0.041667 | Panchagar | 44 | 20:00
Tangail | 152 | 19:30 | Goalpara | 28 | 0.041667 | Joldhaka | 28 | 20:00
Mymensing | 188 | 22:00 | Central s/s | 87 | 20:00 | Kurigram | 46 | 19:30
Kishorganj | 108 | 1:00 | Noapara | 57 | 1:00
Netrokona | 96 | 19:00 | Jessore | 96 | 1:00
Jamalpur | 102 | 1:00 | Benapol | 44 | 1:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-07-21 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 396 | 20:00 | 388 | 9:00 | Kaliakoir | 377 | 0.8125 | 369 | 0.375
| Bheramara | 399 | 6:00 | 394 | 20:00 | Bhulta | 389 | 0.91667 | 379 | 0.375
| Ashuganj(N) | 395 | 22:00 | 386 | 17:00 | Gopalganj | 412 | 0.29167 | 394 | 0.8125
| Payra | 416 | 7:00 | 405 | 20:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 230 | 1:00 | Comilla (N) | 235 | 20:00 | 229 | 4:00
| Ishurdi | 236 | 18:00 | 226 | 21:00 | Hathazari | 230 | 20:00 | 221 | 18:00
| Ashuganj | 239 | 20:00 | 233 | 9:00 | Megnaghat | 230 | 1:00 | 223 | 11:00
| Serajganj | 231 | 7:00 | 226 | 22:00 | Fenchuganj | 235 | 4:00 | 234 | 1:00
| Baghabari | 240 | 18:30 | 236 | 8:00 | Siddhirganj | 228 | 1:00 | 224 | 10:00
| Barapukuria | 234 | 7:00 | 226 | 21:00 | Maniknagar | 227 | 7:00 | 221 | 16:00
| Bogra | 227 | 5:00 | 218 | 22:00 | Agargaon | 226 | 19:30 | 220 | 9:00
| Rajshahi | 231 | 18:00 | 219 | 12:00 | Barisal | 244 | 6:00 | 234 | 4:00
| Khulna South | 225 | 18:00 | 206 | 22:00 | AKSML | 227 | 20:00 | 217 | 6:00
| Rampura | 225 | 20:00 | 221 | 10:00 | BSRM | 227 | 19:30 | 219 | 6:00
| Haripur | 228 | 21:00 | 222 | 10:00 | Bibiyana | 235 | 14:00 | 231 | 8:00
| Hasnabad | 227 | 21:00 | 218 | 12:00 | Bhulta | 229 | 23:00 | 223 | 15:00
| Shyampur | 225 | 20:00 | 218 | 12:00 | Ashuganj (S) | 236 | 22:00 | 231 | 8:00
| Aminbazar | 228 | 24:00 | 221 | 15:00 | Kaliakoir | 230 | 19:00 | 224 | 4:00
| Tongi | 227 | 23:00 | 219 | 9:00 | GPH | 225 | 19:00 | 218 | 10:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 131 | 8:00 | 127 | 16:00 | Hathazari | 137 | 0.83333 | 131 | 0.25
| Munsiganj | 133 | 18:30 | 130 | 1:00 | Khulshi | 134 | 0.8125 | 128 | 0.77083
| Sonargaon | 130 | 18:30 | 125 | 1:00 | Halishahar | 138 | 0.8125 | 130 | 0.70833
| Shyampur | 136 | 19:30 | 131 | 10:00 | Baraulia | 138 | 0.83333 | 129 | 0.75
| Bhulta | 124 | 18:30 | 120 | 1:00 | Sikalbaha | 139 | 19:30 | 130 | 0.70833
| Madanganj | 132 | 4:00 | 130 | 10:00 | Dohazari | 137 | 20:00 | 127 | 0.70833
| Shitalakhya | 141 | 22:00 | 132 | 12:00 | Cox'sbazar | 130 | 0.8125 | 120 | 0.75
| Rahim steal | 131 | 7:00 | 128 | 10:00 | Chandraghona | 137 | 0.83333 | 132 | 0.41667
| Matuail | 131 | 8:00 | 127 | 16:00 | Kaptai | 135 | 1:00 | 132 | 0.29167
| Ghorasal | 138 | 20:00 | 134 | 1:00 | A. Khaer Stl. | 135 | 0.83333 | 129 | 15:00
| Narsinghdi | 129 | 8:00 | 124 | 13:00 | Bakulia | 137 | 0.8125 | 129 | 0.70833
| Haripur (SBU) | 131 | 13:00 | 128 | 10:00 | Julda | 139 | 0.79167 | 130 | 0.66667
| Ullon | 133 | 7:00 | 128 | 11:00 | TK Chemical | 138 | 0.8125 | 130 | 18:00
| Hasnabad | 136 | 7:00 | 130 | 10:00 | Modern Steel | 137 | 0.8125 | 131 | 0.25
| Magbazar | 132 | 2:00 | 126 | 15:00 | Shahmirpur | 138 | 0.8125 | 130 | 0.70833
| Maniknagar | 131 | 22:00 | 126 | 10:00 | Khagrachhari | 136 | 0.8125 | 131 | 0.41667
| Bangabhaban | 131 | 22:00 | 126 | 10:00 | Matarbari | 131 | 0.83333 | 123 | 0.041667
| Narinda | 131 | 22:00 | 126 | 10:00 | Baroiar Hat | 133 | 0.66667 | 128 | 0.29167
| Dhanmondi | 133 | 7:00 | 128 | 11:00 | Rangamati | 137 | 0.8125 | 131 | 18:00
| Lalbag | 136 | 19:30 | 125 | 13:00 | Goalpara S/S | 137 | 18:00 | 124 | 12:00
| Madartek | 132 | 2:00 | 127 | 12:00 | Khulna Central S/S | 135 | 0.70833 | 123 | 22:00
| Dhaka University |  |  |  |  | Noapara | 133 | 18:00 | 121 | 22:00
| Fatuiiah | 136 | 0.91667 | 131 | 9:00 | Jessore | 129 | 18:00 | 115 | 22:00
| Mirpur | 133 | 3:00 | 128 | 13:00 | Benapol | 130 | 18:00 | 116 | 22:00
| Kalyanpur | 132 | 2:00 | 129 | 15:00 | Jhenida | 127 | 0.70833 | 112 | 22:00
| Gulshan | 131 | 2:00 | 127 | 15:00 | Bottail | 132 | 17:00 | 124 | 22:00
| Uttara | 134 | 19:00 | 127 | 12:00 | G.K Project | 138 | 0.75 | 133 | 1:00
| Uttara New | 133 | 19:00 | 128 | 12:00 | Faridpur | 132 | 6:00 | 126 | 3:00
| Kamrangirchar | 133 | 5:00 | 126 | 12:00 | Madaripur | 140 | 0.29167 | 130 | 19:00
| Savar | 131 | 2:00 | 127 | 12:00 | Shariyatpur S/S | 138 | 0.29167 | 128 | 19:00
| Bhasantec | 132 | 19:00 | 126 | 12:00 | Gopalganj | 136 | 8:00 | 126 | 19:00
| Agargaon | 131 | 2:00 | 128 | 12:00 | Bagerhat | 135 | 17:00 | 121 | 4:00
| Satmosjid | 132 | 7:00 | 126 | 12:00 | Mongla | 132 | 0.75 | 116 | 22:00
| Tongi | 136 | 0.79167 | 130 | 11:00 | Satkhira | 136 | 0.75 | 124 | 22:00
| Kabirpur | 138 | 7:00 | 133 | 18:00 | Gallamari | 136 | 17:00 | 125 | 22:00
| Basundhara | 132 | 22:00 | 127 | 14:00 | Magura | 125 | 16:00 | 112 | 21:00
| Manikganj | 137 | 19:00 | 130 | 8:00 | Norail | 123 | 0.70833 | 108 | 22:00
| Joydevpur | 142 | 19:00 | 134 | 9:00 | Chuadanga | 124 | 17:00 | 103 | 22:00
| New Tongi | 135 | 0.79167 | 127 | 8:00 | Barisal(N) | 138 | 8:00 | 131 | 4:00
| Kodda | 136 | 19:00 | 121 | 0.33333 | Barisal (S) | 136 | 0.041667 | 130 | 22:00
| Dhamrai | 138 | 7:00 | 131 | 15:00 | Patuakhali(S) | 132 | 0.29167 | 124 | 22:00
| Rajendrapur | 138 | 19:00 | 119 | 8:00 | Bhandaria | 135 | 9:00 | 125 | 19:30
| Valuka | 129 | 11:00 | 123 | 20:00 | Ishurdi | 136 | 18:00 | 130 | 19:00
| Tangail | 139 | 14:00 | 133 | 21:00 | Ruppur Paromanobik | 135 | 18:00 | 130 | 12:00
| Mymensing | 131 | 4:00 | 128 | 20:00 | Natore | 133 | 20:00 | 127 | 13:00
| Kishorganj | 133 | 13:00 | 125 | 1:00 | Bogra | 133 | 18:00 | 127 | 21:00
| Netrokona | 130 | 11:00 | 124 | 23:00 | Noagaon | 129 | 18:00 | 121 | 21:00
| Jamalpur | 139 | 19:00 | 131 | 9:00 | Rajshahi | 133 | 19:30 | 125 | 12:00
| Sherpur | 137 | 12:00 | 131 | 17:00 | Rajshahi New | 133 | 20:00 | 125 | 3:00
| Srimongal | 136 | 5:00 | 134 | 0.041667 | C.Nawabganj | 133 | 19:30 | 123 | 12:00
| Shahjibazar | 135 | 10:00 | 130 | 0.041667 | Amnura | 134 | 19:30 | 120 | 2:00
| Fenchuganj | 134 | 7:00 | 131 | 0.041667 | Pabna | 134 | 18:00 | 129 | 3:00
| Khulawara | 134 | 14:00 | 130 | 0.041667 | Shahjadpur | 138 | 20:00 | 134 | 12:00
| Sylhet | 132 | 9:00 | 127 | 0.041667 | Serajganj | 132 | 17:00 | 128 | 12:00
| Chatak | 131 | 23:00 | 127 | 1:00 | Niyamatpur | 129 | 7:00 | 120 | 21:00
| Sunamganj | 130 | 7:00 | 124 | 0.041667 | Joypurhat | 130 | 6:00 | 120 | 21:00
| Biani Bazar | 130 | 7:00 | 125 | 0.041667 | Sherpur(Bogura) | 133 | 18:00 | 127 | 12:00
| Comilla(s) | 128 | 12:00 | 122 | 19:00 | Mohastangor | 131 | 7:00 | 125 | 21:00
| Comilla(n) | 137 | 19:30 | 133 | 9:00 | Rangpur | 132 | 6:00 | 122 | 21:00
| Chandpur | 133 | 13:00 | 130 | 7:00 | Lalmonirhat | 126 | 5:00 | 117 | 21:00
| Feni | 135 | 19:30 | 128 | 7:00 | Saidpur | 130 | 6:00 | 120 | 21:00
| Chowmuhani | 135 | 18:30 | 128 | 9:00 | Purbasadipur | 126 | 6:00 | 112 | 21:00
| Ashuganj | 135 | 18:00 | 131 | 1:00 | Thakurgaon | 125 | 6:00 | 110 | 21:00
| Daudkandi | 130 | 19:00 | 128 | 15:00 | Palashbari | 128 | 17:00 | 120 | 21:00
| B.Baria | 135 | 9:00 | 129 | 21:00 | Barapukuria | 134 | 7:00 | 126 | 21:00
| Ramganj | 130 | 16:00 | 120 | 22:00 | Panchagar | 124 | 17:00 | 105 | 20:00
| Chaddagram | 137 | 19:30 | 129 | 18:00 | Joldhaka | 128 | 6:00 | 115 | 21:00
| PHP | 132 | 11:00 | 126 | 9:00 | Kurigram | 128 | 7:00 | 119 | 21:00
| Madanhat | 139 | 19:00 | 132 | 10:00

## L-Curve
Date | 2020-07-21
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 132 | 6555 | 3544 | 10099 |  |  |  | QF-LDC-12
0:30 | 172 | 6625.5 | 3564.5 | 10190 | Date: | 2020-07-21
1:00 | 212 | 6696 | 3585 | 10281
1:30 | 181 | 6629 | 3502.5 | 10131.5
2:00 | 150 | 6562 | 3420 | 9982
2:30 | 164.5 | 6513.5 | 3362 | 9875.5 | [5 empty] | Gen. at Eve. Peak | 10787 | 10787 MW (21:00 )
3:00 | 179 | 6465 | 3304 | 9769 | [6 empty] | 21:00
3:30 | 198 | 6354 | 3251 | 9605 | [5 empty] | Gen. at Day Peak | 9311.6 | 9311.6 MW (12:00 )
4:00 | 217 | 6243 | 3198 | 9441 | [6 empty] | 12:00
4:30 | 234 | 6170.5 | 3202.5 | 9373 | [5 empty] | Highest Generation | 10753
5:00 | 251 | 6098 | 3207 | 9305 | [6 empty] | 21:00
5:30 | 311.5 | 5816.1 | 3114.05 | 8930.15
6:00 | 372 | 5534.2 | 3021.1 | 8555.3
6:30 | 335.5 | 5493.7 | 2924.65 | 8418.35
7:00 | 299 | 5453.2 | 2828.2 | 8281.4
7:30 | 302.5 | 5359.95 | 2838.2 | 8198.15
8:00 | 306 | 5266.7 | 2848.2 | 8114.9
8:30 | 328 | 5462.4 | 2854.8 | 8317.2
9:00 | 350 | 5658.1 | 2861.4 | 8519.5
9:30 | 362.5 | 5837.15 | 2875.5 | 8712.65
10:00 | 375 | 6016.2 | 2889.6 | 8905.8
10:30 | 309.5 | 6102.35 | 2883.85 | 8986.2
11:00 | 244 | 6188.5 | 2878.1 | 9066.6
11:30 | 232 | 6329.85 | 2859.25 | 9189.1
12:00 | 220 | 6471.2 | 2840.4 | 9311.6
12:30 | 197.5 | 6541.3 | 2867.25 | 9408.55
13:00 | 175 | 6611.4 | 2894.1 | 9505.5
13:30 | 191 | 6509.9 | 2883.05 | 9392.95
14:00 | 207 | 6408.4 | 2872 | 9280.4
14:30 | 247 | 6468.4 | 2887.3 | 9355.7
15:00 | 287 | 6528.4 | 2902.6 | 9431
15:30 | 319.5 | 6337.45 | 2873.35 | 9210.8
16:00 | 352 | 6146.5 | 2844.1 | 8990.6
16:30 | 381 | 6029.7 | 2843.6 | 8873.3
17:00 | 410 | 5912.9 | 2843.1 | 8756
17:30 | 392 | 5824.1 | 2820.9 | 8645
18:00 | 374 | 5735.3 | 2798.7 | 8534
18:30 | 252 | 6099.15 | 2976.35 | 9075.5
19:00 | 130 | 6463 | 3154 | 9617
19:30 | 35 | 7065 | 3605 | 10670
20:00 | 65 | 6877 | 3649 | 10526 |  |  |  | Executive Engineer
20:30 | 37.5 | 7020.5 | 3619 | 10639.5 |  |  |  | Network Operation Division
21:00 | 10 | 7164 | 3589 | 10753
21:30 | 7.5 | 7118.5 | 3533.5 | 10652
22:00 | 5 | 7073 | 3478 | 10551 |  |  |  |  | Page 6 of 7
22:30 | 47.5 | 6882 | 3502 | 10384
23:00 | 90 | 6691 | 3526 | 10217
23:30 | 111 | 6623 | 3535 | 10158
24:00 | 132 | 6555 | 3544 | 10099
10787 MW (21:00 )
9311.6 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-07-21 |  | Energy | 229052123
[10 empty] | 2020-07-21 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3524 | 935 | 2122 | 2421 | 677 | 148 | 160 | 0 | 120
0:30 | 3682.5 | 937.5 | 2098 | 2391.5 | 691 | 147.5 | 110 | 0 | 136 | Date: | 2020-07-21
1:00 | 3841 | 940 | 2074 | 2362 | 705 | 147 | 60 | 0 | 152
1:30 | 3843.5 | 940 | 2067.5 | 2248.5 | 705 | 146 | 30 | 0 | 151 | [7 empty] | Total Energy | 229.0521 | Total Energy Gen 229.052 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 229.052 MKWHr
2:00 | 3846 | 940 | 2061 | 2135 | 705 | 145 | 0 | 0 | 150 | [7 empty] | Energy not Served | 0
2:30 | 3856.5 | 940 | 2063.5 | 2018 | 705 | 144.5 | 0 | 0 | 148 | [7 empty] | Energy Requirement | 229.0521
3:00 | 3867 | 940 | 2066 | 1901 | 705 | 144 | 0 | 0 | 146
3:30 | 3917.5 | 940 | 2085.5 | 1668.5 | 705.5 | 144 | 0 | 0 | 144 | [6 empty] | Shortage
4:00 | 3968 | 940 | 2105 | 1436 | 706 | 144 | 0 | 0 | 142
4:30 | 3946.5 | 940.5 | 2104 | 1392.5 | 705.5 | 144 | 0 | 0 | 140
5:00 | 3925 | 941 | 2103 | 1349 | 705 | 144 | 0 | 0 | 138
5:30 | 3813.5 | 940.5 | 2017.5 | 1198.5 | 681.5 | 144 | 0 | 0 | 134
6:00 | 3702 | 940 | 1932 | 1048 | 658 | 144 | 0 | 0 | 130
6:30 | 3668 | 940 | 1886 | 1022 | 629.5 | 144 | 0 | 0 | 125 |  |  |  |  | Coal
7:00 | 3634 | 940 | 1840 | 996 | 601 | 144 | 0 | 0 | 120
7:30 | 3584.5 | 938 | 1812.5 | 996 | 600.5 | 144.5 | 0 | 0 | 118 |  |  |  | Oil |  |  |  | ,
8:00 | 3535 | 936 | 1785 | 996 | 600 | 145 | 0 | 0 | 116
8:30 | 3596 | 936 | 1845.5 | 1080 | 592.5 | 145.5 | 0 | 0 | 117
9:00 | 3657 | 936 | 1906 | 1164 | 585 | 146 | 0 | 0 | 118
9:30 | 3655.5 | 935.5 | 1979 | 1299.5 | 572.5 | 146 | 0 | 0 | 118
10:00 | 3654 | 935 | 2052 | 1435 | 560 | 146 | 0 | 0 | 118
10:30 | 3616 | 935 | 2011.5 | 1603.5 | 560 | 146.5 | 0 | 0 | 107
11:00 | 3578 | 935 | 1971 | 1772 | 560 | 147 | 0 | 0 | 96
11:30 | 3577 | 935 | 2014 | 1854 | 560 | 146 | 0 | 0 | 95
12:00 | 3576 | 935 | 2057 | 1936 | 560 | 145 | 0 | 0 | 94
12:30 | 3605 | 935 | 2071 | 1984 | 560 | 144.5 | 5 | 0 | 96
13:00 | 3634 | 935 | 2085 | 2032 | 560 | 144 | 10 | 0 | 98
13:30 | 3634 | 935 | 2085 | 2032 | 560 | 144 | 10 | 0 | 98
14:00 | 3634 | 935 | 2085 | 2032 | 560 | 144 | 10 | 0 | 98
14:30 | 3652 | 935.5 | 1998 | 2064.5 | 558 | 141.5 | 12.5 | 0 | 101
15:00 | 3670 | 936 | 1911 | 2097 | 556 | 139 | 15 | 0 | 104
15:30 | 3650.5 | 935 | 1888.5 | 1911 | 556 | 139 | 15 | 0 | 112
16:00 | 3631 | 934 | 1866 | 1725 | 556 | 139 | 15 | 0 | 120
16:30 | 3645 | 934.5 | 1852 | 1609.5 | 556 | 139.5 | 15 | 0 | 118
17:00 | 3659 | 935 | 1838 | 1494 | 556 | 140 | 15 | 0 | 116
17:30 | 3592.5 | 935 | 1787 | 1500 | 556.5 | 141 | 15 | 0 | 116
18:00 | 3526 | 935 | 1736 | 1506 | 557 | 142 | 15 | 0 | 116
18:30 | 3626 | 934.5 | 1809.5 | 1732.5 | 579.5 | 143 | 120 | 0 | 130
19:00 | 3726 | 934 | 1883 | 1959 | 602 | 144 | 225 | 0 | 144
19:30 | 3660 | 934 | 1904 | 2858 | 691 | 146 | 335 | 0 | 142
20:00 | 3672 | 935 | 1875 | 2721 | 695 | 146 | 338 | 0 | 144
20:30 | 3760 | 935 | 2013 | 2697.5 | 694.5 | 146 | 247.5 | 0 | 146
21:00 | 3848 | 935 | 2151 | 2674 | 694 | 146 | 157 | 0 | 148
21:30 | 3811.5 | 935 | 2124 | 2645 | 685.5 | 146.5 | 157.5 | 0 | 147
22:00 | 3775 | 935 | 2097 | 2616 | 677 | 147 | 158 | 0 | 146
22:30 | 3704 | 935.5 | 2097 | 2518.5 | 677 | 147 | 159 | 0 | 146
23:00 | 3633 | 936 | 2097 | 2421 | 677 | 147 | 160 | 0 | 146
23:30 | 3578.5 | 935.5 | 2109.5 | 2421 | 677 | 147.5 | 160 | 0 | 133 | Max Temp. in Dhaka |  | 30.3° C
24:00 | 3524 | 935 | 2122 | 2421 | 677 | 148 | 160 | 0 | 120
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 229.052 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 229.052 MKWHr
Note on W13: Author:

## Generation
g | 2020-07-20
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 82 | 80 | 79 | 79 | 79 | 79 | 79 | 80 | 81 | 81 | 82 | 80 | 79 | 75 | 74 | 74 | 75 | 77 |  | 79 | 81 | 81 | 81 | 82 | 82 | 83 | 1833905
2 | Karnaphuli Hydro PP Unit-4 & 5 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1552000
3 | Chattogram TPP-1 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 2200000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [19 empty] | 1 | 16 | 25 |  |  |  | 0 | 34585
| Teknaf 20MW PP (Solartech) | [5 empty] | 0.8 | 5.3 |  | 6.1 | 2.2 | 5.8 | 6.1 | 3.9 | 4 |  | 2 | 0.7 | 0.2 | [8 empty] | 46980
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 139 | 146 | 140 | 145 | 139 | 139 | 142 | 142 | 145 | 145 | 146 | 145 | 145 | 143 | 139 | 139 | 139 | 104 |  | 104 | 139 | 139 | 145 | 145 | 139 | 139 | 3289526
10 | Sikalbaha 150MW GTPP(Oil)
Dohazari -Kalaish 100 MW Peaking
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 13381
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | [7 empty] | 40 | 99 | 100 | 94 | 100 | 100 | 100 | 100 | 99 | 100 | 100 |  | 100 | 91 | 92 | 100 | 97 | 97 | 40 | 1603000
17 | Siddhirganj 335 MW CCPP | 296 | 296 | 295 | 296 | 298 | 230 | 230 | 54 | [16 empty] | 10 | 23 | 2156983
18 | Kodda 300 MW PP Unit-2 (Summit) | 195 | 150 | 95 |  |  |  |  | 21 | 56 | 147 | 237 | 264 | 267 | 267 | 267 | 195 | 195 | 195 |  | 212 | 250 | 260 | 270 | 267 | 270 | 268 | 4315634
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 643000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4268250
24
25 | Ghorasal 365 MW CCPP Unit-7 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2876200
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 135 | 135 | 135 | 135 | 135 | 135 |  | 135 | 135 | 135 | 135 | 135 | 100 | 100 | 2750810
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 42 | 42 | 42 | 42 | 41 | 41 | 38 | 38 | 38 | 41 | 41 | 38 | 41 | 41 | 36 | 40 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 30 | 934272
33 | Ashuganj 225 MW CCPP | 191 | 183 | 182 | 198 | 190 | 183 | 183 | 192 | 203 | 197 | 183 | 206 | 189 | 189 | 196 | 189 | 191 | 196 |  | 204 | 183 | 183 | 191 | 183 | 188 | 154 | 4614000
34 | Ashuganj 450 MW CCPP(South) | 290 | 290 | 290 | 315 | 295 | 260 | 260 | 260 | 295 | 270 | 260 | 260 | 265 | 260 | 340 | 270 | 270 | 270 |  | 290 | 265 | 260 | 270 | 265 | 285 | 260 | 6754000
| Ashuganj 450 MW CCPP(North) | 315 | 310 | 315 | 340 | 320 | 310 | 270 | 275 | 300 | 325 | 310 | 310 | 360 | 280 | 280 | 260 | 265 | 270 |  | 285 | 260 | 260 | 305 | 320 | 335 | 320 | 7516900
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 138240
36 | Chandpur 150 MW CCPP | 95 | 96 | 92 | 96 | 96 | 90 | 88 | 96 | 96 | 95 | 90 | 87 | 87 | 97 | 94 | 93 | 90 | 96 |  | 96 | 85 | 85 | 96 | 86 | 95 | 91 | 2224290
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 322 | 323 | 323 | 329 | 330 | 324 | 322 | 322 | 341 | 349 | 322 | 326 | 333 | 324 | 337 | 324 | 322 | 325 |  | 347 | 321 | 325 | 342 | 323 | 329 | 342 | 8078276
40 | Meghnaghat 450 MW CCPP(MPL) | 390 | 390 | 390 | 420 | 420 | 380 | 350 | 320 | 350 | 380 | 380 | 400 | 400 | 370 | 370 | 340 | 320 | 300 |  | 300 | 300 | 300 | 420 | 420 | 400 | 400 | 8914250
41 | Haripur 360MW CCPP(HPL) | 355 | 359 | 356 | 353 | 352 | 309 | 303 | 289 | 354 | 356 | 300 | 351 | 351 | 300 | 300 | 300 | 270 | 250 |  | 300 | 300 | 300 | 350 | 357 | 356 | 356 | 7810000
42 | RPCL 210MW CCPP | 159 | 158 | 158 | 157 | 157 | 159 | 159 | 158 | 157 | 157 | 157 | 140 | 123 | 125 | 124 | 125 | 140 | 140 |  | 140 | 146 | 146 | 144 | 143 | 142 | 157 | 3432280
43
44 | Fenchugonj CCPP Phase-1 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2111000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 20 | 20 | 20 | 22 | 22 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 657410
46 | Shajibazar 330 MW CCPP | 161 | 162 | 163 | 162 | 162 | 162 | 160 | 162 | 161 | 160 | 160 | 161 | 161 | 160 | 161 | 161 | 160 | 160 |  | 161 | 162 | 162 | 161 | 162 |  |  | 3435000
47 | Shahjibazar GTPP Unit- 8 & 9 | 61 | 61 | 61 | 62 | 62 | 62 | 62 | 63 | 61 | 61 | 63 | 61 | 61 | 61 | 61 | 61 | 61 | 52 |  | 61 | 62 | 63 | 61 | 61 | 61 | 61 | 1452768
48 | Shahjibazar 86MW PP (Shahjibazar) | 79 | 79 | 79 | 79 | 79 | 79 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 20 |  | 20 | 80 | 80 | 80 | 80 | 80 | 80 | 1752960
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | [14 empty] | 30 | 100 | 100 | 50 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 1054720
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 |  | 421000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 8 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 237780
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 237024
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 52 | 53 | 53 | 53 | 50 | 50 | 50 | 47 | 50 | 47 | 52 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1245000
56 | Shahjahanulla 25 MW PP | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 16 | 23 | 23 | 23 | 23 | 23 | 16 |  | 16 | 16 | 24 | 24 | 24 | 24 | 24 | 544255
57 | Bibiana-II 341 MW CCPP (Summit) | 295 | 280 | 295 | 300 | 300 | 280 | 295 | 290 | 310 | 310 | 290 | 300 | 300 | 290 | 310 | 290 | 300 | 300 |  | 315 | 280 | 280 | 315 | 300 | 295 | 315 | 7362500
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 17 | 17 | 17 | 17 | 17 | [7 empty] | 35 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 |  | 55 | 55 | 55 | 717783
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 17 | 17 | 17 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 461232
61 | Narshingdi 22 MW PP (Doreen) |  |  | 19 | 19 | 19 | 19 |  |  |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 22 | 22 | 22 | 22 | 22 | 314064
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 17 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 414648
63 | Impoprt (Tripura) | 152 | 150 | 146 | 142 | 138 | 130 | 120 | 116 | 118 | 118 | 96 | 94 | 98 | 102 | 104 | 120 | 116 | 116 |  | 144 | 142 | 144 | 148 | 146 | 146 | 120 | 3083520
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 40 | 41 | 40 | 41 | 35 | 7 | 3 | 4 | 2 | 5 | 7 | 4 | 4 | 4 | 11 | 10 |  | 22 | 22 | 25 | 30 | 38 | 32 | 32 | 528960
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 507384
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 8 | 8 | 8 | 8 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 213660
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 819500
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 11 | 6 | 6 | 8 | 8 | 8 | 8 | 8 | 15 |  | 18 | 21 | 21 | 21 | 21 | 21 | 15 | 391390
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 29 | 29 | 30 | 30 | 30 | 6 | 30 | 24 | 20 | 20 | 28 | 18 | 28 | 28 | 28 | 28 | 29 | 29 |  | 20 | 22 | 22 | 30 | 28 | 26 | 30 | 630900
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 17 |  | 17 | 17 | 17 | 33 | 33 | 33 | 33 | 774300
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 |  |  | 16 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 754400
73 | Ghorashal 108MW PP (Regent) | 22 | 22 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 58 | 76 | 90 | 93 | 93 | 90 | 91 | 91 | 90 |  | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 1486636
| Feni Lanka Power | [19 empty] | 51 | 114 | 9 |  |  |  | 0 | 106020
| Chowmuhani 113 MW | 113 | 113 | 113 | 55 | 55 | 26 | 26 |  |  | 26 | 113 | 113 | 113 | 113 | 113 | 105 | 36 | 36 |  | 57 | 113 | 113 | 113 | 113 | 113 | 113 | 2001720
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [25 empty] | 0 | 0
78 | Gazipur 52 MW PP | [19 empty] | 8 | 32 |  |  |  |  | 0 | 46656
79 | Kodda 150MW PP | [19 empty] | 133 | 116 | 82 | 48 | 48 | 48 | 48 | 348000
80 | Jamalpur 95 MW PP(Powerpac) | 72 | 72 | 72 | 72 | 72 | 16 | 8 | 8 | 8 | 35 | 71 | 90 | 90 | 90 | 89 | 80 | 40 | 40 |  | 46 | 56 | 56 | 95 | 95 | 90 | 95 | 1562880
81 | Jangalia 52 MW PP (Lakdanavi) | 24 | [18 empty] | 2 | 43 | 37 |  |  |  |  | 114187
| Gazipur 100 MW PP | [9 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 |  | 45 | 88 | 80 | 52 | 35 |  | 0 | 548796
| Kaptai 7 MW Solar PP | [5 empty] | 0.3 | 0.6 | 1.4 | 0.8 | 2.1 | 1.2 | 1.4 | 1.9 | 2 | 2 | 1 | 1.1 | 0.1 | [8 empty] | 18720
| Jodiac Power | 35 | 35 | 35 | 17 | [15 empty] | 5 | 54 | 41 | 54 | 54 | 54 | 54 | 432870
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | 96 | 96 | 96 | 82 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 |  | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 1970592
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [19 empty] | 35 | 86 | 90 | 100 | 63 |  | 0 | 381270
86 | Meghnaghat CCPP(Summit) | 145 | 140 | 140 | 145 | 145 | 140 | 140 | 140 | 150 | 145 | 135 | 140 | 135 | 140 | 145 | 140 | 138 | 147 |  | 150 | 130 | 130 | 145 | 130 | 145 | 135 | 3407680
87 | Meghnaghat 100 MW(IEL) | [25 empty] | 0 | 0
| Meghnaghat 104 MW PP (OPCL) | [10 empty] | 50 | 90 | 90 | 90 | 90 | 90 | 52 | 52 |  | 52 | 90 | 72 | 90 | 90 | 90 | 90 | 1104000
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [19 empty] | 10 | 10 |  |  |  |  | 0 | 11160
92 | Fenchuganj 44MW (Energyprima) | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 43 | 46 | 43 | 43 | 43 | 40 |  | 46 | 46 | 43 | 46 | 43 | 43 | 46 | 1068552
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1023820
94 | Gagnagar 102 MW PP (Digital Power) | 93 | 93 | 93 | 93 | 93 | 93 | 97 | 97 | 97 | 100 | 100 | 102 | 102 | 102 | 102 | 93 | 102 | 102 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 2367360
95 | Patenga 50MW PP (Baraka) | [19 empty] | 2 | 40 | 48 | 32 | 10 |  | 0 | 99840
96 | Chattogram 108 MW PP (ECPV) | 45 | 60 | 40 | [16 empty] | 20 | 80 | 89 | 97 | 97 | 91 | 90 | 654720
97 | Katpotti 52 MW PP (Sinha) | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 44 | 32 | 47 | 47 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 1121885
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | [6 empty] | 35 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 45 | 45 | 898722
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 130 | 130 | 130 | 130 | 163 | 130 | 163 | 163 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 130 | 110 | 110 | 110 | 3283773
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0.1 | 0.3 | 0.3 | 0.2 | 0.9 | 0.5 | 0.7 | 0.6 | 1.4 | 0.4 | 0.5 | 0.1 | [9 empty] | 5550
103 | Kamalaghat 54 MW PP(Banco Energy) | 53 | 53 | 53 | 53 | 53 | 17 | 17 | 17 | 17 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1153440
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 100 | 100 | 100 | 70 | 24 | [14 empty] | 17 | 50 | 50 | 50 | 50 | 50 | 50 | 772800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 132 | 132 | 132 | 105 | 84 | 73 | 73 | 76 | 89 | 103 | 108 | 119 | 125 | 126 | 130 | 133 | 132 | 133 |  | 133 | 133 | 133 | 132 | 133 | 133 | 133 | 2820960
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 2278080
116 | Chandpur 200MW (Desh energy) | [25 empty] | 0 | 0
117 | Ashuganj 150MW PP (Midland) | 100 | 50 | [7 empty] | 3 | 83 | 123 | 142 | 142 | 148 | 50 | 50 | 50 |  | 70 | 90 | 140 | 148 | 148 | 50 | 50 | 1771418
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 115 | 109 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2806800
| Anwara 300 MW PP (United) | 234 | 234 | 234 | 234 | 234 | 178 | 178 | 180 | 300 | 306 | 305 | 305 | 305 | 307 | 307 | 200 | 104 | 106 |  | 160 | 251 | 185 | 195 | 198 | 198 | 198 | 5427163
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2414400
120 | Eastern Zone Total | 6696 | 6562 | 6465 | 6243 | 6098 | 5534.2 | 5453.2 | 5266.7 | 5658.1 | 6016.2 | 6188.5 | 6471.2 | 6611.4 | 6408.4 | 6528.4 | 6146.5 | 5912.9 | 5735.3 |  | 6463 | 7065 | 6877 | 7164 | 7073 | 6691 | 6555 | 152451844
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 115 | 115 | 115 | 83 | 83 | 32 | [6 empty] | 16 | 16 | 16 |  |  |  |  | 49 | 115 | 115 | 115 | 115 | 115 | 115 | 1235520
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
| Khulna 225 MW CCPP | [12 empty] | 10 | 10 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 |  |  |  |  | 89843
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | 17 | 17 | [22 empty] | 0 | 100320
130
131
132
133
| Barisal 110 MW PP (Summit ) | 80 | 80 | 48 | 16 | 16 | [14 empty] | 49 | 85 | 110 | 96 | 96 | 96 | 96 | 795840
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 78 | 80 | 78 | 78 | 78 | 77 | 78 | 77 | 77 | 77 | 77 | 77 | 75 | 76 | 77 | 77 | 77 | 77 |  | 75 | 75 | 76 | 78 | 78 | 78 | 77 | 1864313
| Bhola 225 MW CCPP | 88 | 88 | 88 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 |  | 89 | 89 | 89 | 89 | 89 | 88 | 89 | 2149342
140 | Bhola 33 MW PP (Venture) | 35 | 35 | 34 | 34 | 34 | 28 | 25 | 25 | 25 | 25 | 27 | 26 | 27 | 27 | 23 | 23 | 25 | 26 |  | 35 | 38 | 38 | 40 | 41 | 39 | 39 | 714338
141 | Noapara 100 MW PP (Bangla Trac) | 20 | 10 | [21 empty] | 1 | 50 | 50 | 148800
142 | Noapara 40 MW PP (Khanjahan Ali) | 32 | 32 | 32 | 32 | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 24 | 24 | 24 | 8 |  |  |  | 16 | 33 | 33 | 40 | 33 | 33 | 33 | 548250
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 940 | 940 | 940 | 940 | 941 | 940 | 940 | 936 | 936 | 935 | 935 | 935 | 935 | 935 | 936 | 934 | 935 | 935 |  | 934 | 934 | 935 | 935 | 935 | 936 | 935 | 22477090
147 | Bheramara 410 MW CCPP | 380 | 386 | 390 | 390 | 395 | 395 | 405 | 410 | 410 | 410 | 408 | 405 | 345 | 345 | 395 | 395 | 400 | 345 |  | 345 | 345 | 345 | 365 | 355 | 345 | 345 | 9148032
148 | Payra 1320 MW | 555 | 555 | 555 | 555 | 555 | 508 | 451 | 450 | 435 | 410 | 410 | 410 | 410 | 410 | 407 | 407 | 407 | 408 |  | 453 | 542 | 546 | 545 | 527 | 527 | 527 | 12384300
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 151 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 150 | 150 | 150 | 3671300
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 10 | 38 | 50 |  |  |  |  | 41494
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 183 | 184 | 183 | 188 | 190 | 159 | 146 | 147 | 151 | 155 | 148 | 152 | 156 | 180 | 158 | 148 | 147 | 152 |  | 162 | 166 | 168 | 186 | 176 | 180 | 188 | 4222500
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 165 | 167 | 171 | 185 | 187 | 182 | 161 | 158 | 172 | 175 | 159 | 165 | 195 | 172 | 171 | 160 | 159 | 164 |  | 174 | 170 | 168 | 182 | 172 | 178 | 186 | 4365218
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 420 | 416 | 411 | 417 | 417 | 389 | 327 | 350 | 360 | 410 | 420 | 376 | 406 | 360 | 365 | 362 | 364 | 363 |  | 417 | 410 | 380 | 418 | 386 | 420 | 423 | 9331727
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 494160
163 | Bogura 20 MW PP (Energyprima) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 8 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 245160
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 8 | 8 | 10 | 8 | 8 | 10 | 10 | 10 |  | 11 | 11 | 11 | 11 |  |  | 0 | 182268
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern) | [25 empty] | 0 | 0
167 | Katakhali 50 MW Peaking PP | [19 empty] | 13 | 46 | 47 |  |  |  |  | 55565
168 | Santahar 50 MW Peaking PP | [19 empty] | 4 | 20 | 34 |  |  |  |  | 31884
169 | Natore 52 MW PP (Rajlanka) | [19 empty] | 19 | 43 | 52 |  |  |  | 0 | 72480
170 | Chapainawabganj 100 MW Peaking PP | 60 | [18 empty] | 50 | 90 | 100 | 99 | 100 | 100 | 100 | 589416
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 111 | 35 | [17 empty] | 8 | 50 | 51 | 89 | 70 | 35 | 35 | 540480
172 | Confidence Power Bogura Unit-1 113 MW | [25 empty] | 0 | 0
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | [20 empty] | 10 | 10 | 10 | 10 | 12 | 12 | 51000
176 | Rangpur 113 MW PP (Confidence) | 98 | 90 | 52 | [9 empty] | 14 | 39 | 40 | 35 | 34 | 34 |  | 46 | 100 | 96 | 110 | 112 | 112 | 112 | 1041600
177 | Sympa Solar Power 8MW | [5 empty] | 0.1 | 0.2 | 0.2 | 0.4 | 0.6 | 0.1 | 0.4 | 1.1 |  | 0.6 | 1.1 | 1.1 | 0.7 | [8 empty] | 8039
178
178