## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-08-06 | Thursday
|  | Date (day): | 2020-08-06 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13347.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14508 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-08-05 | 2020-08-06 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 35 | 35 | 35 |  | 50 | Unit-2 Under maint
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 180 | 190 | 190
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 40 | 68 | 70 | 70
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 53 | 96 | 100 | 100
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 300 | 346 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 370 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 41 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 145 | 140 | 150 | 150 | 155 |  | GT-1 S/D for gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 30 | 78 | 75 | 75 |  | 25 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 16 | 16 | 16 |  | 6 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 73 | 180 | 150 | 180 | 30 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 24 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 321 | 330 | 330
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 50 | 102 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel Shortage.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 0 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 48 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 37 | 41 | 47 | 47 |  | 33 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 24 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 35 | 50
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 30 | 165 | 300 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 80 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 126 | 133 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 18 | 72 | 104 | 104
| Dhaka area Total |  |  |  |  | 6119 | 5895 | 1992 | 2859 | 4019 | 4334 | 449 | 1029
38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 8 | 25 | 25
40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 0 | 0 | 20 | 0
41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50
42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 102 | 102 | 145 | 145 | 85 |  | Low water level
43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint.
44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 140 | 139 | 140 | 140
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 100 | 100
48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 21 | 21
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 18 | 41 | 15 | 30
51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 34 | 90 | 91 |  | 17 | Engine problem
52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 6.4 | 0 | 5 | 0
53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 178 | 306 | 300 | 300
54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 50 | 54
55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
| Chattogram area Total |  |  |  |  | 2326 | 2266 | 655.4 | 953 | 1411 | 1466 | 445 | 340
57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 100 | 135 | 100 | 100 | 29 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 100 | 100 | 100 | 100 | 34 |  | Gas Shortage
58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 193 | 210 | 220 | 220
59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 295 | 325 | 300 | 300
60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  |  | Under maint
61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 41 | 40 | 40 | 42
62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 40 | 49 | 45 | 45 | 10 |  | Gas shortage
63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 26 | 45 | 55 | 55 | 140 |  | Gas shortage
64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 35 | 150 | 150
66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 42
67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 51 | 91 | 0 | 0 |  | 163 | Under maint
68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 200 | 200
69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 92 | 126 | 157 | 173
71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 52 | 52 | 52
73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 18 | 18 |  | 7 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 100 | 114 | 114 | 114
76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 57 | 60 | 60
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1221 | 1510 | 1728 | 1988 | 348 | 170
77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 144 | 153 | 150 | 150 | 52 |  | Gas shortage
78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 17 | 17 |  | 5 | Engine problem
79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 64 | 74 | 95 | 95
80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1.6 | 0 | 1.6 | 0
81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 192 | 200 | 200 | 200
82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 8 | 62 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 426.6 | 506 | 578.6 | 577 | 52 | 5
83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 58 | 60 | 80 | 80
84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 22 | 30 | 30
85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 217 | 222 | 210 | 210
87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 50 | 51 | 51
88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 41 | 45 | 44 | 44
89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 28 | 29 | 61 | 66
91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 85 | 86 | 86
92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 |  | 231 | Under maint.
93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 21 | 16 | 25 | 25
96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 300 | 341 | 341
97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
| Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
| Sylhet Area Total |  |  |  |  | 2033 | 1988 | 992 | 1031 | 1130 | 1135 | 0 | 631
99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 930 | 935 | 939 | 939
100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 115 | 115 | 115
101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30
102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 145 | 130 | 225
103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 340 | 350 | 360 | 410
105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 16 | 60 | 100
107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105
108 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Khulna Area Total |  |  |  |  | 2288 | 2284 | 1406 | 1601 | 1849 | 2140 | 0 | 0
109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 32 | 110 | 110
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 11 | 21 | 33 | 33
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 88 | 88 | 80 | 81 |  | 113 | GT-2 & ST Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 33 | 76 | 76 | 79 |  | 16 | Engine problem
113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 348 | 529 | 600 | 600
| Barisal Area Total |  |  |  |  | 1054 | 1054 | 480 | 746 | 899 | 903 | 0 | 129
114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 45
120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | S/D for ST Under maint.
121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 158 | 200 | 180 | 220
122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 178 | 193 | 200 | 220
123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 399 | 403 | 414 | 414
124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 26 | 0 | 35
125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 20 | 22 | 22
126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 11 | 10 | 10 | 10
127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 99 | 100 | 100
130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 113 | 113
132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 70 | 109 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 844 | 1068 | 1462 | 1692 | 431 | 3
133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 149 | 150 | 150 | 124 |  | Coal Shortage.
135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 3 | 0 | 10 |  | 10 | Engine problem
137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 112 | 113 | 113
138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4.6 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 154.6 | 264 | 271 | 273 | 294 | 30
| Total |  |  |  |  | 20383 | 19892 | 8171.6 | 10538 | 13347.6 | 14508 | 2019 | 2337
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7894.7675 | 10181 | 12895.4181 | 14016.5067
A. |  | 2020-08-05 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 10666 | MW at | 23:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 8079.3 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10538 | MW
3 | Day peak Generation : |  |  | 8171.6 | MW at | 10:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10181 | MW
4 | Evening peak Generation : |  |  | 10538 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 218.5012 | MKWHr | By Solar | 0.14695 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 131.7495 | MKWHr |  | By Oil: | 44.7665 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 14.3732 | MKWHr |  | By Hydro: | 2.3836 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2019 | MW | Dhaka | 3054 | 3054 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2337 | MW | Chittagong | 1076 | 1076 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 4356 | MW | Khulna | 1323 | 1323 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1111.97 | MMCFD |  |  | Rajshahi | 1107 | 1107 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 154884284.8 | ii) Oil : | Taka | 336649575.93 | Comilla | 1138 | 1138 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 66869075 | Total | Taka | 558402935.73 | Mymensingh | 954 | 954 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.0595 | MKWHr. | Sylhet | 485 | 485 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | 104 | MW (E to W) at | 21:00 | hrs | Barisal | 281 | 281 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -8 | MW at | 3:00 | hrs | Rangpur | 763 | 763 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 34.6° C |  |  | Total | 10181 | 10181 |  | 0
B. |  | 2020-08-06 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 34° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11300 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14508 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8800 | MW
4 | Reserve(Generation end) |  |  |  | 3208 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 231.4892 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8124.1 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.4444 | MKWHr. | ii) HVDC Flow at Peak Time |  | 935 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.6371 | MKWHr. | iii) Maximum HVDC Flow : |  | 941 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 93.06 |  | (b) Today: | 93.81 |  | (c) Rule Curve: |  | 90.6
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-08-05
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 151 | 0 | 290 | 98 | 69 | 0 | 347 |  | 0 | 420 | 150 | 94 | 70 | 0 | 322 | 0 | 150 | 0 | 7 | 74 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 25 | 20 | 24 | 25 | 0 | 0 | 37 | 65 | 0 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 51 | 0 | 0 | 0 | 21 | 40 | 0 | 85 | 95 | 305 | 0 | 209 | 55 | 51 | 39 | 5 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 33 | 19 | 130 | 151 | 95 | 17 | 0 | 58 | 30 | 53 | 45 | 163 | 216 | 28 | 87 | 0 | 0 | 18 | 0 | 10 | 290 | 23 | 11 | 0 | 200 | 0 | 0 | 193 | 0 | 132 | 0 | 100 | 115 | 0 | 0 | 115 | 0 | 0 | 0 | 306 | 0 | 0 | 114 | 0 | 100 | 0 | 104 |  | 941 | 0 | 360 | 0 | 115 | 40 | 0 | 0 | 0 | 0 | 40 | 88 | 37 | 110 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 21 | 12 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 182 | 0 | 77 | 60 | 192 | 0 | 403 | 17 | 0 | 35 | 0 | 113 | 0 | 0 | 109 | 429 |  | 6729 | 3606 | 10335 | 3453 | 941 | 2275 | 2637 | 578 | 102 | 219 | 130 | 0 | 0 | 92.81
2:00 | 35 | 0 | 150 | 0 | 290 | 98 | 69 | 0 | 348 |  | 0 | 420 | 150 | 100 | 63 | 0 | 323 | 0 | 150 | 0 | 7 | 24 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 25 | 12 | 24 | 25 | 0 | 0 | 37 | 65 | 0 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 21 | 40 | 0 | 100 | 100 | 290 | 0 | 209 | 55 | 52 | 39 | 5 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 33 | 19 | 128 | 152 | 95 | 17 | 0 | 58 | 30 | 53 | 45 | 130 | 216 | 28 | 87 | 0 | 0 | 18 | 0 | 10 | 300 | 23 | 11 | 0 | 145 | 0 | 0 | 193 | 0 | 131 | 0 | 100 | 70 | 0 | 0 | 115 | 0 | 0 | 0 | 308 | 0 | 0 | 114 | 0 | 100 | 0 | 104 |  | 940 | 0 | 370 | 0 | 115 | 15 | 0 | 0 | 0 | 0 | 40 | 88 | 38 | 96 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 21 | 12 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 185 | 0 | 77 | 50 | 193 | 0 | 410 | 0 | 0 | 35 | 0 | 113 | 0 | 0 | 109 | 440 |  | 6508 | 3536 | 10044 | 3466 | 940 | 2261 | 2446 | 589 | 102 | 112 | 128 | 0 | 0 | 92.86
3:00 | 35 | 0 | 150 | 0 | 290 | 98 | 69 | 0 | 350 |  | 0 | 420 | 135 | 50 | 64 | 0 | 326 | 0 | 150 | 0 | 7 | 24 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 25 | 12 | 24 | 25 | 0 | 0 | 35 | 65 | 0 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 40 | 0 | 100 | 100 | 280 | 0 | 209 | 55 | 52 | 39 | 5 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 33 | 19 | 126 | 155 | 95 | 17 | 0 | 58 | 30 | 53 | 45 | 130 | 217 | 28 | 84 | 0 | 0 | 18 | 0 | 10 | 290 | 23 | 11 | 0 | 145 | 0 | 0 | 193 | 0 | 132 | 0 | 100 | 70 | 0 | 0 | 115 | 0 | 0 | 0 | 307 | 0 | 0 | 114 | 0 | 100 | 0 | 104 |  | 940 | 0 | 340 | 0 | 115 | 10 | 0 | 0 | 0 | 0 | 40 | 88 | 37 | 96 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 21 | 12 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 184 | 0 | 77 | 50 | 194 | 0 | 402 | 0 | 0 | 35 | 0 | 113 | 0 | 0 | 109 | 526 |  | 6425 | 3578 | 10003 | 3449 | 940 | 2241 | 2382 | 675 | 100 | 90 | 126 | 0 | 0 | 92.91
4:00 | 35 | 0 | 150 | 0 | 290 | 98 | 69 | 0 | 349 |  | 0 | 420 | 140 | 24 | 64 | 0 | 326 | 0 | 120 | 0 | 7 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 25 | 12 | 24 | 25 | 0 | 0 | 35 | 65 | 0 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 40 | 0 | 100 | 100 | 280 | 0 | 210 | 55 | 52 | 39 | 5 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 33 | 19 | 122 | 154 | 95 | 17 | 0 | 58 | 30 | 53 | 45 | 130 | 217 | 28 | 84 | 0 | 0 | 18 | 0 | 10 | 290 | 23 | 11 | 0 | 110 | 0 | 0 | 194 | 0 | 108 | 0 | 100 | 70 | 0 | 0 | 75 | 0 | 0 | 0 | 307 | 0 | 0 | 114 | 0 | 100 | 0 | 104 |  | 941 | 0 | 345 | 0 | 115 | 15 | 0 | 0 | 0 | 0 | 40 | 88 | 36 | 96 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 21 | 12 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 180 | 0 | 75 | 30 | 188 | 0 | 408 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 109 | 530 |  | 6254 | 3531 | 9785 | 3413 | 941 | 2243 | 2208 | 679 | 100 | 79 | 122 | 0 | 0 | 92.96
5:00 | 35 | 0 | 151 | 0 | 290 | 98 | 68 | 0 | 348 |  | 0 | 420 | 145 | 17 | 64 | 0 | 325 | 0 | 120 | 0 | 7 | 7 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 12 | 24 | 25 | 0 | 0 | 35 | 65 | 0 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 41 | 0 | 100 | 100 | 280 | 0 | 210 | 55 | 51 | 39 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 11 | 33 | 19 | 116 | 152 | 95 | 17 | 0 | 59 | 30 | 53 | 46 | 130 | 217 | 28 | 84 | 0 | 0 | 18 | 0 | 10 | 300 | 23 | 11 | 0 | 60 | 0 | 0 | 194 | 0 | 89 | 0 | 100 | 70 | 0 | 0 | 45 | 0 | 0 | 0 | 307 | 0 | 0 | 114 | 0 | 100 | 0 | 94 |  | 941 | 0 | 345 | 0 | 115 | 70 | 0 | 0 | 0 | 0 | 40 | 88 | 31 | 96 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 21 | 12 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 180 | 0 | 75 | 30 | 190 | 0 | 411 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 109 | 520 |  | 6119 | 3576 | 9695 | 3413 | 941 | 2259 | 2063 | 669 | 100 | 134 | 116 | 0 | 0 | 93.01
6:00 | 35 | 0 | 100 | 0 | 290 | 52 | 40 | 0 | 324 |  | 0 | 400 | 130 | 7 | 30 | 0 | 300 | 0 | 115 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 12 | 24 | 25 | 0 | 0 | 35 | 65 | 0 | 0 | 0 | 0 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 40 | 0 | 100 | 100 | 280 | 0 | 200 | 55 | 50 | 38 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 11 | 33 | 19 | 102 | 152 | 95 | 17 | 0.1 | 59 | 30 | 53 | 46 | 130 | 218 | 29 | 40 | 0 | 0 | 18 | 0 | 10 | 285 | 23 | 11 | 0 | 30 | 0 | 0 | 194 | 0 | 60 | 0.28 | 100 | 50 | 0 | 0 | 8 | 0 | 0 | 0.3 | 215 | 0 | 0 | 114 | 0 | 100 | 0 | 30 |  | 941 | 0 | 340 | 0 | 115 | 100 | 0 | 0 | 0 | 0 | 0 | 88 | 23 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 12 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 163 | 0 | 75 | 0 | 184 | 0 | 338 | 0 | 0 | 0 | 0 | 82 | 0 | 0.2 | 109 | 480 |  | 5438.68 | 3292.2 | 8730.88 | 3259 | 941 | 2000 | 1599 | 629 | 100 | 100 | 102 | 0.88 | 0 | 93.06
7:00 | 35 | 0 | 100 | 0 | 290 | 52 | 40 | 0 | 304 |  | 0 | 370 | 135 | 7 | 30 | 0 | 270 | 0 | 70 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 12 | 24 | 25 | 0 | 0 | 36 | 65 | 0 | 0 | 0 | 0 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 13 | 0 | 100 | 100 | 280 | 0 | 200 | 55 | 50 | 38 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 11 | 33 | 19 | 94 | 151 | 48 | 17 | 0.3 | 59 | 30 | 53 | 46 | 130 | 217 | 28 | 10 | 0 | 0 | 18 | 0 | 10 | 280 | 23 | 11 | 0 | 30 | 0 | 0 | 194 | 0 | 60 | 1.49 | 100 | 17 | 0 | 0 | 8 | 0 | 0 | 0.7 | 178 | 0 | 0 | 114 | 0 | 60 | 0 | 18 |  | 941 | 0 | 340 | 0 | 83 | 120 | 0 | 0 | 0 | 0 | 0 | 88 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 12 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 156 | 0 | 78 | 0 | 178 | 0 | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 70 | 450 |  | 5079.49 | 3080.2 | 8159.69 | 3168 | 941 | 1883 | 1250 | 599 | 101 | 120 | 94 | 3.69 | 0 | 93.11
8:00 | 35 | 0 | 100 | 0 | 290 | 52 | 40 | 0 | 305 |  | 0 | 370 | 135 | 7 | 30 | 0 | 270 | 0 | 70 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 12 | 24 | 25 | 0 | 0 | 36 | 65 | 0 | 0 | 0 | 0 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 18 | 0 | 100 | 100 | 280 | 0 | 171 | 55 | 51 | 38 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 11 | 33 | 15 | 92 | 150 | 48 | 17 | 1.2 | 58 | 30 | 53 | 46 | 130 | 216 | 28 | 10 | 0 | 0 | 18 | 0 | 10 | 290 | 23 | 11 | 0 | 28 | 0 | 0 | 192 | 0 | 104 | 5.4 | 100 | 0 | 0 | 0 | 8 | 0 | 0 | 1.2 | 178 | 0 | 0 | 114 | 0 | 60 | 0 | 18 |  | 941 | 0 | 340 | 0 | 49 | 130 | 0 | 0 | 0 | 0 | 0 | 88 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 12 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 151 | 0 | 78 | 0 | 180 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 70 | 422 |  | 5086.8 | 3005.6 | 8092.4 | 3130 | 941 | 1893 | 1223 | 571 | 101 | 130 | 92 | 11.4 | 0 | 93.16
9:00 | 35 | 0 | 100 | 0 | 300 | 54 | 40 | 0 | 300 |  | 0 | 370 | 140 | 7 | 30 | 0 | 270 | 0 | 70 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 24 | 25 | 0 | 0 | 37 | 65 | 0 | 0 | 0 | 0 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 18 | 0 | 100 | 100 | 280 | 0 | 208 | 55 | 51 | 41 | 5 | 0 | 51 | 0 | 0 | 52 | 0 | 0 | 33 | 18 | 84 | 147 | 88 | 17 | 1.8 | 58 | 30 | 50 | 45 | 130 | 216 | 28 | 82 | 0 | 0 | 18 | 0 | 10 | 290 | 23 | 11 | 0 | 30 | 0 | 0 | 192 | 0 | 130 | 0 | 100 | 0 | 0 | 0 | 8 | 0 | 0 | 2 | 178 | 0 | 0 | 114 | 0 | 60 | 0 | 18 |  | 930 | 0 | 340 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 12 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 153 | 0 | 54 | 0 | 176 | 0 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 70 | 350 |  | 5216.8 | 2862.5 | 8079.3 | 3130 | 930 | 1961 | 1247 | 499 | 102 | 120 | 84 | 6.3 | 0 | 93.21
10:00 | 0 | 0 | 100 | 0 | 300 | 53 | 40 | 0 | 300 |  | 0 | 370 | 145 | 7 | 30 | 0 | 300 | 0 | 73 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 24 | 25 | 0 | 0 | 37 | 65 | 0 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 18 | 0 | 100 | 100 | 295 | 0 | 193 | 26 | 51 | 41 | 40 | 0 | 51 | 0 | 0 | 52 | 20 | 8 | 33 | 19 | 92 | 144 | 64 | 17 | 1.6 | 58 | 30 | 47 | 41 | 130 | 217 | 28 | 82 | 0 | 0 | 18 | 0 | 9 | 300 | 21 | 11 | 0 | 30 | 0 | 0 | 192 | 0 | 126 | 0 | 100 | 0 | 0 | 0 | 8 | 0 | 0 | 6.4 | 178 | 0 | 0 | 100 | 0 | 90 | 0 | 18 |  | 930 | 0 | 340 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 88 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 33 | 0 | 178 | 0 | 399 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6 | 70 | 348 |  | 5287 | 2884.6 | 8171.6 | 3196 | 930 | 1981 | 1240 | 498 | 102 | 120 | 92 | 12.6 | 0 | 93.26
11:00 | 0 | 0 | 100 | 0 | 300 | 53 | 40 | 0 | 347 |  | 0 | 370 | 135 | 0 | 30 | 0 | 321 | 0 | 116 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 24 | 25 | 0 | 0 | 38 | 65 | 0 | 0 | 0 | 0 | 0 | 141 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 17 | 0 | 100 | 100 | 280 | 0 | 181 | 26 | 50 | 41 | 46 | 0 | 43 | 0 | 0 | 52 | 20 | 8 | 33 | 19 | 94 | 147 | 8 | 17 | 1.3 | 58 | 30 | 50 | 41 | 130 | 209 | 28 | 83 | 0 | 0 | 18 | 0 | 10 | 285 | 21 | 11 | 0 | 30 | 0 | 0 | 192 | 0 | 68 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 123 | 0 | 0 | 51 | 0 | 100 | 0 | 18 |  | 929 | 0 | 340 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 88 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 182 | 0 | 33 | 0 | 175 | 0 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4 | 70 | 347 |  | 5114.5 | 2889.4 | 8003.9 | 3249 | 929 | 1998 | 1000 | 497 | 103 | 120 | 94 | 13.9 | 0 | 93.31
12:00 | 0 | 0 | 200 | 0 | 300 | 54 | 40 | 0 | 343 |  | 0 | 400 | 140 | 0 | 30 | 0 | 315 | 0 | 184 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 12 | 24 | 25 | 0 | 0 | 38 | 65 | 0 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 15 | 0 | 100 | 100 | 280 | 0 | 180 | 26 | 51 | 41 | 44 | 0 | 43 | 0 | 0 | 52 | 20 | 11 | 33 | 0 | 98 | 147 | 8 | 0 | 2.4 | 58 | 30 | 53 | 41 | 163 | 207 | 27 | 82 | 0 | 0 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 30 | 0 | 0 | 192 | 0 | 35 | 13.8 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6 | 124 | 0 | 0 | 30 | 0 | 100 | 0 | 18 |  | 930 | 0 | 340 | 0 | 16 | 80 | 0 | 0 | 0 | 0 | 0 | 82 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 109 | 0 | 33 | 0 | 179 | 0 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9 | 70 | 348 |  | 5283.8 | 2754.9 | 8038.7 | 3309 | 930 | 2039 | 952 | 498 | 103 | 80 | 98 | 29.7 | 0 | 93.36
13:00 | 30 | 0 | 160 | 0 | 300 | 54 | 40 | 0 | 341 |  | 0 | 400 | 140 | 0 | 30 | 0 | 313 | 0 | 175 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 12 | 24 | 25 | 0 | 0 | 38 | 65 | 0 | 0 | 0 | 0 | 0 | 141 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 105 | 100 | 345 | 0 | 182 | 26 | 50 | 41 | 40 | 0 | 43 | 0 | 0 | 43 | 20 | 11 | 33 | 0 | 94 | 144 | 8 | 17 | 1.9 | 57 | 30 | 53 | 41 | 130 | 207 | 27 | 81 | 0 | 0 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 45 | 0 | 0 | 192 | 0 | 50 | 9 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 106 | 0 | 0 | 17 | 0 | 100 | 0 | 18 |  | 935 | 0 | 340 | 0 | 16 | 30 | 0 | 0 | 0 | 0 | 0 | 76 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 99 | 0 | 33 | 0 | 175 | 0 | 396 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8 | 35 | 329 |  | 5271.1 | 2663.8 | 7934.9 | 3333 | 935 | 2034 | 907 | 479 | 103 | 30 | 94 | 19.9 | 0 | 93.41
14:00 | 35 | 0 | 160 | 0 | 300 | 72 | 40 | 0 | 300 |  | 0 | 450 | 145 | 0 | 30 | 0 | 313 | 0 | 140 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 12 | 24 | 25 | 0 | 0 | 37 | 65 | 0 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 18 | 0 | 135 | 100 | 290 | 0 | 180 | 26 | 50 | 38 | 37 | 0 | 43 | 0 | 0 | 52 | 20 | 8 | 33 | 0 | 106 | 148 | 8 | 17 | 1.8 | 59 | 30 | 53 | 44 | 130 | 206 | 27 | 80 | 0 | 0 | 18 | 0 | 10 | 295 | 16 | 11 | 0 | 49 | 0 | 0 | 190 | 0 | 54 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 212 | 0 | 0 | 17 | 0 | 100 | 0 | 53 |  | 933 | 0 | 340 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 0 | 33 | 0 | 192 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2 | 35 | 305 |  | 5426 | 2572.2 | 7998.2 | 3312 | 933 | 2008 | 1068 | 455 | 102 | 0 | 106 | 14.2 | 0 | 93.46
15:00 | 35 | 0 | 200 | 0 | 300 | 88 | 50 | 0 | 340 |  | 0 | 450 | 135 | 3 | 40 | 0 | 280 | 0 | 108 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 35 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 18 | 0 | 135 | 100 | 310 | 0 | 206 | 26 | 51 | 38 | 39 | 0 | 43 | 0 | 0 | 52 | 20 | 8 | 33 | 0 | 106 | 144 | 40 | 17 | 1.8 | 56 | 30 | 51 | 42 | 163 | 205 | 28 | 82 | 0 | 0 | 18 | 0 | 10 | 285 | 20 | 11 | 0 | 77 | 0 | 0 | 200 | 0 | 70 | 12.7 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 302 | 0 | 0 | 17 | 0 | 100 | 0 | 90 |  | 932 | 0 | 340 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 43 | 0 | 34 | 0 | 191 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6 | 60 | 315 |  | 5598.2 | 2562.6 | 8160.8 | 3094 | 932 | 2101 | 1342 | 464 | 100 | 0 | 106 | 21.8 | 0 | 93.51
16:00 | 35 | 0 | 120 | 0 | 300 | 94 | 67 | 0 | 340 |  | 0 | 450 | 135 | 7 | 65 | 0 | 280 | 0 | 110 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 24 | 25 | 0 | 0 | 34 | 65 | 0 | 0 | 0 | 0 | 0 | 104 | 0 |  | 0 | 0 | 15 | 0 | 0 | 0 | 21 | 19 | 0 | 135 | 100 | 310 | 0 | 208 | 26 | 91 | 38 | 42 | 0 | 43 | 0 | 0 | 34 | 20 | 8 | 33 | 15 | 108 | 145 | 40 | 0 | 2 | 56 | 30 | 52 | 42 | 163 | 207 | 20 | 85 | 0 | 0 | 18 | 0 | 10 | 280 | 20 | 5 | 0 | 60 | 0 | 0 | 160 | 0 | 79 | 5.2 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 196 | 0 | 0 | 0 | 0 | 100 | 0 | 70 |  | 936 | 0 | 285 | 0 | 16 | 30 | 0 | 0 | 0 | 0 | 0 | 88 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 96 | 0 | 34 | 0 | 174 | 0 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2 | 35 | 300 |  | 5543.8 | 2525.2 | 8069 | 3166 | 936 | 2117 | 1137 | 449 | 99 | 45 | 108 | 12 | 0 | 93.53
17:00 | 35 | 0 | 100 | 0 | 280 | 23 | 68 | 0 | 300 |  | 0 | 450 | 140 | 7 | 48 | 0 | 280 | 0 | 115 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 12 | 33 | 25 | 0 | 0 | 34 | 65 | 0 | 0 | 0 | 0 | 0 | 104 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 21 | 29 | 0 | 135 | 100 | 340 | 0 | 181 | 26 | 97 | 38 | 44 | 0 | 15 | 0 | 0 | 34 | 20 | 8 | 33 | 15 | 100 | 152 | 40 | 17 | 0.1 | 56 | 30 | 14 | 10 | 163 | 207 | 29 | 10 | 0 | 0 | 18 | 0 | 10 | 290 | 22 | 5 | 0 | 60 | 0 | 0 | 120 | 0 | 65 | 3.1 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 160 | 0 | 0 | 0 | 0 | 100 | 0 | 53 |  | 935 | 0 | 285 | 0 | 16 | 35 | 0 | 0 | 0 | 0 | 0 | 88 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 152 | 0 | 33 | 0 | 171 | 0 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 35 | 300 |  | 5187.8 | 2611.8 | 7799.6 | 3253 | 935 | 1889 | 1018 | 449 | 99 | 52 | 100 | 4.6 | 0 | 93.55
18:00 | 35 | 0 | 100 | 0 | 260 | 23 | 68 | 0 | 270 |  | 0 | 340 | 130 | 7 | 48 | 0 | 250 | 0 | 88 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 12 | 33 | 25 | 0 | 0 | 35 | 65 | 0 | 0 | 0 | 0 | 0 | 104 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 21 | 31 | 0 | 120 | 100 | 270 | 0 | 181 | 26 | 80 | 40 | 45 | 0 | 15 | 0 | 0 | 34 | 20 | 8 | 33 | 15 | 94 | 155 | 40 | 17 | 0.1 | 56 | 0 | 13 | 5 | 130 | 207 | 29 | 40 | 0 | 0 | 18 | 0 | 10 | 275 | 8 | 5 | 0 | 60 | 0 | 0 | 120 | 0 | 65 | 0.3 | 100 | 0 | 20 | 0 | 2 | 0 | 0 | 0.1 | 160 | 0 | 0 | 0 | 42 | 100 | 0 | 53 |  | 935 | 0 | 285 | 0 | 16 | 85 | 0 | 0 | 0 | 0 | 0 | 87 | 14 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 9 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 156 | 0 | 33 | 0 | 167 | 0 | 286 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 35 | 300 |  | 4864.5 | 2601.2 | 7465.7 | 3034 | 935 | 1653 | 1098 | 449 | 100 | 102 | 94 | 0.7 | 0 | 93.57
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 0 | 180 | 0 | 300 | 97 | 68 | 0 | 346 |  | 0 | 450 | 140 | 20 | 48 | 0 | 324 | 0 | 150 | 0 | 11 | 50 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 16 | 25 | 12 | 33 | 25 | 0 | 0 | 36 | 65 | 0 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 102 | 0 | 11 | 0 | 21 | 40 | 0 | 135 | 100 | 310 | 0 | 207 | 29 | 97 | 40 | 47 | 0 | 15 | 0 | 0 | 34 | 20 | 8 | 33 | 18 | 120 | 152 | 95 | 17 | 0 | 56 | 0 | 33 | 25 | 163 | 204 | 29 | 85 | 0 | 0 | 18 | 0 | 10 | 280 | 8 | 8 | 0 | 75 | 0 | 0 | 134 | 0 | 76 | 0 | 100 | 0 | 30 | 0 | 19 | 0 | 0 | 0 | 301 | 0 | 0 | 42 | 57 | 100 | 0 | 72 |  | 935 | 0 | 370 | 0 | 62 | 120 | 0 | 0 | 0 | 0 | 0 | 88 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 24 | 20 | 11 | 8 | 0 | 0 | 149 | 0 | 3 | 0 | 0 | 164 | 0 | 65 | 0 | 185 | 0 | 385 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 70 | 342 |  | 6213 | 3118 | 9331 | 3535 | 935 | 2191 | 1643 | 491 | 101 | 315 | 120 | 0 | 0 | 93.59
19:30 | 35 | 0 | 180 | 0 | 300 | 96 | 68 | 0 | 346 |  | 0 | 450 | 120 | 92 | 50 | 0 | 324 | 0 | 110 | 0 | 30 | 50 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 16 | 25 | 12 | 33 | 25 | 0 | 0 | 36 | 65 | 0 | 0 | 2 | 0 | 0 | 139 | 0 |  | 0 | 0 | 102 | 0 | 34 | 0 | 21 | 40 | 0 | 135 | 100 | 300 | 0 | 209 | 45 | 80 | 40 | 48 | 0 | 30 | 0 | 0 | 52 | 20 | 8 | 33 | 18 | 124 | 155 | 95 | 17 | 0 | 60 | 22 | 50 | 35 | 163 | 208 | 30 | 85 | 0 | 0 | 18 | 0 | 10 | 270 | 8 | 11 | 0 | 145 | 0 | 0 | 200 | 0 | 100 | 0 | 100 | 0 | 30 | 0 | 45 | 0 | 0 | 0 | 305 | 8 | 0 | 114 | 57 | 100 | 0 | 72 |  | 936 | 0 | 345 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 33 | 88 | 23 | 32 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 27 | 20 | 11 | 8 | 0 | 0 | 149 | 0 | 3 | 0 | 0 | 185 | 0 | 79 | 0 | 192 | 0 | 353 | 0 | 0 | 0 | 0 | 107 | 0 | 0 | 90 | 422 |  | 6639 | 3437 | 10076 | 3510 | 936 | 2222 | 2229 | 571 | 101 | 383 | 124 | 0 | 0 | 0
20:00 | 35 | 0 | 180 | 0 | 300 | 96 | 67 | 0 | 350 |  | 0 | 450 | 135 | 60 | 65 | 0 | 323 | 0 | 144 | 0 | 45 | 50 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 25 | 16 | 33 | 25 | 0 | 0 | 36 | 65 | 0 | 0 | 5 | 0 | 0 | 139 | 0 |  | 0 | 0 | 102 | 0 | 34 | 0 | 21 | 40 | 0 | 135 | 100 | 300 | 0 | 211 | 45 | 91 | 40 | 48 | 0 | 45 | 0 | 0 | 52 | 20 | 8 | 33 | 18 | 120 | 155 | 95 | 17 | 0 | 60 | 22 | 49 | 47 | 163 | 208 | 29 | 85 | 0 | 0 | 18 | 0 | 10 | 270 | 8 | 11 | 0 | 160 | 0 | 0 | 200 | 0 | 128 | 0 | 100 | 0 | 30 | 0 | 45 | 0 | 0 | 0 | 305 | 0 | 0 | 114 | 57 | 100 | 0 | 72 |  | 936 | 0 | 340 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 33 | 88 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 27 | 21 | 11 | 8 | 0 | 0 | 149 | 0 | 3 | 0 | 0 | 185 | 0 | 77 | 0 | 192 | 0 | 377 | 0 | 0 | 0 | 0 | 107 | 0 | 0 | 100 | 488 |  | 6730 | 3532 | 10262 | 3554 | 936 | 2275 | 2256 | 637 | 101 | 383 | 120 | 0 | 0 | 93.61
21:00 | 35 | 0 | 180 | 0 | 300 | 96 | 68 | 0 | 346 |  | 0 | 450 | 140 | 41 | 78 | 0 | 321 | 0 | 180 | 0 | 24 | 50 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 25 | 16 | 33 | 25 | 0 | 0 | 37 | 65 | 0 | 0 | 8 | 0 | 0 | 139 | 0 |  | 0 | 0 | 102 | 0 | 34 | 0 | 21 | 41 | 0 | 135 | 100 | 325 | 0 | 210 | 45 | 91 | 40 | 49 | 0 | 51 | 0 | 0 | 52 | 20 | 8 | 33 | 19 | 126 | 153 | 74 | 17 | 0 | 60 | 22 | 50 | 45 | 163 | 222 | 29 | 85 | 0 | 0 | 18 | 0 | 10 | 300 | 16 | 11 | 0 | 165 | 0 | 0 | 200 | 0 | 133 | 0 | 100 | 0 | 35 | 0 | 62 | 0 | 0 | 0 | 306 | 0 | 0 | 114 | 57 | 100 | 0 | 72 |  | 935 | 0 | 350 | 0 | 115 | 145 | 0 | 0 | 0 | 0 | 40 | 88 | 21 | 32 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 26 | 20 | 10 | 8 | 0 | 0 | 149 | 0 | 3 | 0 | 0 | 200 | 0 | 76 | 16 | 193 | 0 | 403 | 0 | 0 | 0 | 0 | 112 | 0 | 0 | 109 | 529 |  | 6859 | 3679 | 10538 | 3659 | 935 | 2329 | 2286 | 678 | 102 | 423 | 126 | 0 | 0 | 93.63
22:00 | 35 | 0 | 180 | 0 | 300 | 96 | 67 | 0 | 347 |  | 0 | 450 | 150 | 41 | 78 | 0 | 321 | 0 | 180 | 0 | 24 | 50 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 25 | 20 | 33 | 25 | 0 | 0 | 37 | 65 | 0 | 0 | 8 | 0 | 0 | 140 | 0 |  | 0 | 0 | 102 | 0 | 36 | 0 | 21 | 41 | 0 | 135 | 100 | 325 | 0 | 209 | 45 | 90 | 38 | 48 | 0 | 51 | 0 | 0 | 52 | 20 | 8 | 33 | 19 | 128 | 153 | 72 | 17 | 0 | 60 | 22 | 52 | 45 | 163 | 218 | 29 | 85 | 0 | 0 | 18 | 0 | 10 | 310 | 24 | 11 | 0 | 165 | 0 | 0 | 200 | 0 | 131 | 0 | 100 | 17 | 40 | 0 | 75 | 0 | 0 | 0 | 306 | 0 | 0 | 114 | 56 | 100 | 0 | 72 |  | 936 | 0 | 350 | 0 | 115 | 150 | 0 | 0 | 0 | 0 | 40 | 88 | 22 | 32 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 26 | 20 | 7 | 8 | 0 | 0 | 150 | 0 | 3 | 0 | 0 | 198 | 0 | 76 | 40 | 191 | 0 | 404 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 109 | 526 |  | 6919 | 3703 | 10622 | 3660 | 936 | 2339 | 2353 | 676 | 102 | 428 | 128 | 0 | 0 | 93.65
23:00 | 35 | 0 | 200 | 0 | 300 | 95 | 67 | 0 | 344 |  | 0 | 450 | 150 | 41 | 91 | 0 | 319 | 0 | 185 | 0 | 24 | 50 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 25 | 20 | 33 | 25 | 0 | 0 | 37 | 65 | 0 | 0 | 8 | 0 | 0 | 144 | 0 |  | 0 | 0 | 102 | 0 | 31 | 0 | 21 | 40 | 0 | 135 | 100 | 350 | 0 | 208 | 45 | 0 | 42 | 47 | 0 | 51 | 0 | 0 | 52 | 20 | 8 | 33 | 19 | 130 | 151 | 72 | 17 | 0 | 58 | 22 | 53 | 47 | 163 | 215 | 28 | 85 | 0 | 0 | 18 | 0 | 10 | 315 | 24 | 11 | 0 | 95 | 0 | 0 | 200 | 0 | 134 | 0 | 100 | 95 | 0 | 0 | 102 | 0 | 0 | 0 | 306 | 0 | 0 | 114 | 56 | 100 | 0 | 72 |  | 930 | 0 | 400 | 0 | 115 | 150 | 0 | 0 | 0 | 0 | 40 | 88 | 28 | 64 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 26 | 20 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 201 | 0 | 77 | 45 | 194 | 0 | 387 | 0 | 0 | 0 | 0 | 112 | 0 | 0 | 109 | 527 |  | 6886 | 3780 | 10666 | 3673 | 930 | 2334 | 2395 | 677 | 102 | 425 | 130 | 0 | 0 | 93.67
24:00 | 35 | 0 | 200 | 0 | 300 | 96 | 67 | 0 | 346 |  | 0 | 420 | 150 | 41 | 95 | 0 | 323 | 0 | 160 | 0 | 24 | 50 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 25 | 20 | 33 | 25 | 0 | 0 | 38 | 65 | 0 | 0 | 8 | 0 | 0 | 139 | 0 |  | 0 | 0 | 102 | 0 | 33 | 0 | 21 | 41 | 0 | 135 | 100 | 320 | 0 | 210 | 45 | 0 | 39 | 48 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 33 | 19 | 128 | 153 | 72 | 17 | 0 | 59 | 22 | 53 | 47 | 163 | 216 | 29 | 82 | 0 | 0 | 18 | 0 | 10 | 310 | 24 | 11 | 0 | 95 | 0 | 0 | 193 | 0 | 133 | 0 | 100 | 120 | 0 | 0 | 115 | 0 | 0 | 0 | 307 | 0 | 0 | 114 | 56 | 100 | 0 | 72 |  | 930 | 0 | 345 | 0 | 115 | 150 | 0 | 0 | 0 | 0 | 40 | 89 | 29 | 64 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 26 | 21 | 12 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 198 | 0 | 77 | 70 | 192 | 0 | 407 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 109 | 556 |  | 6838 | 3800 | 10638 | 3563 | 930 | 2325 | 2458 | 706 | 103 | 425 | 128 | 0 | 0 | 93.69
KWH | 705000 | 0 | 3469000 | 0 | 6953045 | 1744863 | 1381408 | 0 | 7973000 |  | 0 | 9037000 | 3360175 | 627840 | 1324272 | 0 | 7377985 | 0 | 3447000 | 0 | 241920 | 768096 | 513600 | 0 | 0 | 0 | 0 | 18000 | 14915 | 212268 | 235368 | 600000 | 337500 | 656100 | 603000 | 0 | 0 | 815580 | 1568000 | 0 | 0 | 40444 | 0 | 0 | 3042196 | 0 |  | 0 | 0 | 720219 | 0 | 185280 | 0 | 476448 | 733440 | 0 | 2721125 | 2384284 | 7474500 | 0 | 4854000 | 1003636 | 1363790 | 891720 | 732960 | 0 | 1080548 | 0 | 0 | 1192301 | 453816 | 196740 | 806700 | 363550 | 2637120 | 3528400 | 1467840 | 335088 | 15400 | 1371000 | 637440 | 1141200 | 975960 | 3562281 | 4911000 | 662592 | 1665600 | 0 | 0 | 408000 | 0 | 233640 | 7216700 | 439320 | 240000 | 0 | 2200472 | 0 | 0 | 4423200 | 0 | 2335680 | 46305 | 2388480 | 749760 | 209090 | 0 | 987600 | 0 | 0 | 30000 | 5652982 | 10684 | 0 | 1961940 | 383880 | 2273280 | 0 | 1435200 |  | 22444364 | 0 | 8437824 | 0 | 1591680 | 1424772 | 0 | 0 | 0 | 0 | 421500 | 2144306 | 467723 | 892128 | 0 | 0 | 0 | 0 | 0 | 748680 | 0 | 0 | 0 | 0 | 139749 | 456720 | 249624 | 175770 | 0 | 0 | 3660900 | 0 | 12000 | 0 | 0 | 3999909 | 0 | 1419476 | 479040 | 4878545 | 0 | 9091690 | 73440 | 0 | 118656 | 0 | 1260480 | 0 | 55249 | 1904928 | 10712300 |  | 141239766 | 77261453 | 218501219 | 81582061 | 22444364 | 50167469 | 41207451 | 14373200 | 2383580 | 3559020 | 2637120 | 146954 | 0
Fuel Cost | 1156200 | 0 | 5064740 | 0 | 7717879.95 | 2303219.16 | 2348393.6 | 0 | 8212190 |  | 0 | 9850330 | 3729794.25 | 4765305.6 | 9124234.08 | 0 | 7673104.4 | 0 | 5963310 | 0 | 1821657.6 | 7005035.52 | 5053824 | 0 | 0 | 0 | 0 | 131400 | 115292.95 | 2092962.48 | 176526 | 450000 | 0 | 0 | 0 | 0 | 0 | 220206.6 | 423360 | 0 | 0 | 375724.76 | 0 | 0 | 5171733.2 | 0 |  | 0 | 0 | 6986124.3 | 0 | 1611936 | 0 | 600324.48 | 2178316.8 | 0 | 4027265 | 3504897.48 | 5531130 | 0 | 4465680 | 1294690.44 | 1568358.5 | 1007643.6 | 1026144 | 0 | 1847737.08 | 0 | 0 | 11386474.55 | 576346.32 | 147555 | 1411725 | 272662.5 | 19778400 | 3740104 | 13327987.2 | 425561.76 | 245476 | 2248440 | 1019904 | 2031336 | 1522497.6 | 4061000.34 | 5107440 | 1305306.24 | 3181296 | 0 | 0 | 893520 | 0 | 476625.6 | 7288867 | 329490 | 182400 | 0 | 16635568.32 | 0 | 0 | 23000640 | 0 | 22983091.2 | 541305.45 | 19466112 | 8134896 | 1474084.5 | 0 | 9006912 | 0 | 0 | 0 | 42736543.92 | 93057.64 | 0 | 19580161.2 | 3289851.6 | 15140044.8 | 0 | 0 |  | 129279536.64 | 0 | 8859715.2 | 0 | 12510604.8 | 19747339.92 | 0 | 0 | 0 | 0 | 4392030 | 2423065.78 | 724970.65 | 8707169.28 | 0 | 0 | 0 | 0 | 0 | 6625818 | 0 | 0 | 0 | 0 | 1355565.3 | 876902.4 | 386917.2 | 133057.89 | 0 | 0 | 19842078 | 0 | 342360 | 0 | 0 | 5279879.88 | 0 | 2129214 | 8148470.4 | 5707897.65 | 0 | 9000773.1 | 766713.6 | 0 | 1126045.44 | 0 | 9781324.8 | 0 | 610501.45 | 14077417.92 | 47026997 |  | 389639355.57 | 319862366.3 | 709501721.87 | 94142863.83 | 129279536.64 | 60741420.97 | 296538544.41 | 66869075 | 643566.6 | 40111031.52 | 19778400 | 1397282.9 | 0
Yesterday Day Peak | 0 | 0 | 100 | 0 | 300 | 53 | 40 | 0 | 300 |  | 0 | 370 | 145 | 7 | 30 | 0 | 300 | 0 | 73 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 24 | 25 | 0 | 0 | 37 | 65 | 0 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 18 | 0 | 100 | 100 | 295 | 0 | 193 | 26 | 51 | 41 | 40 | 0 | 51 | 0 | 0 | 52 | 20 | 8 | 33 | 19 | 92 | 144 | 64 | 17 | 1.6 | 58 | 30 | 47 | 41 | 130 | 217 | 28 | 82 | 0 | 0 | 18 | 0 | 9 | 300 | 21 | 11 | 0 | 30 | 0 | 0 | 192 | 0 | 126 | 0 | 100 | 0 | 0 | 0 | 8 | 0 | 0 | 6.4 | 178 | 0 | 0 | 100 | 0 | 90 | 0 | 18 |  | 930 | 0 | 340 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 88 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 33 | 0 | 178 | 0 | 399 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6 | 70 | 348 |  | 8171.6 | DayPeak
Yesterday Evening Peak | 35 | 0 | 180 | 0 | 300 | 96 | 68 | 0 | 346 | 0 | 0 | 450 | 140 | 41 | 78 | 0 | 321 | 0 | 180 | 0 | 24 | 50 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 25 | 16 | 33 | 25 | 0 | 0 | 37 | 65 | 0 | 0 | 8 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 102 | 0 | 34 | 0 | 21 | 41 | 0 | 135 | 100 | 325 | 0 | 210 | 45 | 91 | 40 | 49 | 0 | 51 | 0 | 0 | 52 | 20 | 8 | 33 | 19 | 126 | 153 | 74 | 17 | 0 | 60 | 22 | 50 | 45 | 163 | 222 | 29 | 85 | 0 | 0 | 18 | 0 | 10 | 300 | 16 | 11 | 0 | 165 | 0 | 0 | 200 | 0 | 133 | 0 | 100 | 0 | 35 | 0 | 62 | 0 | 0 | 0 | 306 | 0 | 0 | 114 | 57 | 100 | 0 | 72 |  | 935 | 0 | 350 | 0 | 115 | 145 | 0 | 0 | 0 | 0 | 40 | 88 | 21 | 32 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 26 | 20 | 10 | 8 | 0 | 0 | 149 | 0 | 3 | 0 | 0 | 200 | 0 | 76 | 16 | 193 | 0 | 403 | 0 | 0 | 0 | 0 | 112 | 0 | 0 | 109 | 529 |  | 10538 | EvPeak
Forecast for Evening | 35 | 0 | 190 | 0 | 300 | 100 | 70 | 0 | 360 | 0 | 0 | 450 | 150 | 100 | 75 | 55 | 330 | 0 | 180 | 0 | 100 | 102 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 22 | 33 | 25 | 50 | 0 | 80 | 65 | 0 | 0 | 25 | 0 | 0 | 140 | 0 | 0 | 0 |  | 100 | 100 | 91 | 50 | 21 | 30 | 0 | 100 | 100 | 300 | 0 | 220 | 55 | 0 | 42 | 45 | 0 | 51 | 0 | 42 | 52 | 22 | 11 | 33 | 18 | 173 | 150 | 95 | 17 | 0 | 80 | 30 | 51 | 44 | 163 | 210 | 66 | 86 | 0 | 0 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 0 | 300 | 54 | 110 | 114 | 60 | 100 | 0 | 104 |  | 939 | 16 | 410 | 0 | 115 | 225 | 0 | 0 | 30 | 60 | 40 | 81 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 0 | 50 | 45 | 52 | 35 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 10 | 0 | 0 | 220 | 0 | 79 | 100 | 220 | 0 | 414 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 600
Forecast for Day | 35 | 0 | 190 | 0 | 300 | 100 | 70 | 0 | 360 | 0 | 0 | 450 | 150 | 100 | 75 | 55 | 330 | 0 | 150 | 0 | 100 | 102 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 22 | 33 | 25 | 35 | 0 | 80 | 65 | 0 | 0 | 25 | 0 | 0 | 140 | 0 | 0 | 0 |  | 100 | 100 | 90 | 50 | 21 | 15 | 0 | 100 | 100 | 300 | 0 | 220 | 55 | 0 | 40 | 45 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 18 | 157 | 150 | 95 | 17 | 1.6 | 80 | 30 | 51 | 44 | 163 | 210 | 61 | 86 | 0 | 0 | 18 | 0 | 10 | 341 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 80 | 149 | 20 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 5 | 300 | 50 | 50 | 114 | 60 | 100 | 0 | 104 |  | 939 | 0 | 360 | 0 | 115 | 130 | 0 | 0 | 0 | 0 | 40 | 80 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 50 | 0 | 52 | 0 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 180 |  | 76 | 60 | 200 | 0 | 414 | 105 | 0 | 113 | 100 | 113 | 0 | 8 | 113 | 600
Generation at 08:00(Today) | 35 | 0 | 150 | 0 | 260 | 98 | 67 | 0 | 306 | 0 | 0 | 350 | 140 |  | 48 | 0 | 250 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 13 | 25 | 20 | 33 | 25 | 0 | 0 | 37 | 65 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 18 | 0 | 100 | 80 | 285 | 0 | 212 | 45 | 0 | 35 | 46 | 0 | 45 | 0 | 0 | 43 | 21 | 8 | 33 | 15 | 92 | 155 | 8 | 17 | 0.3 | 60 | 22 | 53 | 48 | 100 | 213 | 29 | 80 | 0 | 0 | 18 | 0 | 10 | 285 | 16 | 8 | 0 | 9 | 0 | 0 | 194 | 0 | 70 | 0.8 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4 | 197 | 0 | 0 | 0 | 57 | 70 | 0 | 53 | 0 | 929 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 174 | 0 | 74 | 0 | 172 | 0 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 0 | 459 | 0
199
| Minimum Generation |  | 8079.3 | 9:00
| Highest Generation |  | 10666 | 23:00
| Day Peak Generation |  | 8171.6 | 10:00
| Evening Peak Generation |  | 10538 | 21:00
| HVDC Max Flow |  | 941 | 1:00
| HVDC EvPeak Flow |  | 935 | 21:00
| Load factor L.F |  | 85.36%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-08-06
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-08-05 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8171.6 | MW Hour : | 10:00 | Min. Gen. at | 8:00 | 8124.1 | MW
Evening Peak Generation : |  | 10538 | MW Hour : | 21:00 | Available Max Generation : |  | 14508 | MW
E.P. Demand (at gen end) : |  | 10538 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 11300 | MW
Maximum Generation : |  | 10666 | MW Hour : | 23:00 | Reserve(Generation end) |  | 3208 | MW
Total Gen. (MKWH) : |  | 218.5012 | System Load Factor : | 85.36% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -8 | MW at | 3:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-08-06
Actual : | 93.81 | Ft.(MSL) , | Rule curve : | 90.6 | Ft.( MSL )
Gas Consumed : | Total = | 1111.97 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 154884284.8
: |  | Coal : | 66869075 | Oil : | 336649575.93 | Total : | 558402935.73
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4062.2356 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1382.2135 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1238.5652 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1119.2005 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1011.3764 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 816.1471 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 455.283 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 210.1077 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 629.4582 |  |  | 0 | 0%
Total | 0 |  | 10924.5872 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down | 10) Haripur-412 MW.
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 11) Baghabari-1,2
|  |  |  | 2) Bibiyana #3 | 12) Chandpur-163 MW.
3) Ghorasal Unit-1,2,3,5
4) Ashuganj unit-3,5
5) Bhola-225 MW GT-2 & ST
6) Kaptai-2
7) Raozan #1,2
8) Sirajganj #1
9) Sylhet-225 MW.
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Hasnabad 230/132 kV T03 transformer was under shut down 08:02 to 15:52 for C/M.
b) Kishoreganj 132/33 kV T1 transformer was under shut down from 10:20 to 12:06 for C/M. |  |  |  |  | About 20 MW power interruption occurred under Kishoreganj S/S area
from 10:20 to 12:06.
c) Tangail 132/33 kV T2 transformer was under shut down from 08:19 to 12:03 for C/M.
d) Kabirpur 132 kV Bus-1 was under shut down from 07:06 to 09:26 for C/M.
e) Mymensingh-Netrokona 132 kV Ckt-1 was under shut down from 09:35 to 12:10 for C/M.
f) Mymensingh-Netrokona 132 kV Ckt-2 was under shut down from 12:18 to 14:47 for C/M.
g) Sirajganj unit-2 ST tripped at 11:11 due to damper problem and was synchronized at 15:16.
h) Bogura-Natore 132 kV Ckt-2 tripped at 09:01 from both ends showing Dist. Z2, U/V at Natore
end & Dist. A,B, Z1 at Bogura end and was switched on at 09:36.
i) Sikalbaha-Dohazari 132 kV Ckt-1 tripped at 12:33 from both ends showing Dist. Z2 at Dohazari
end & Dist. Z1, Y-phase, General trip at Sikalbaha end and was switched on at 19:44.
j) Dohazari 132/33 kV T2 transformer was under shut down from 12:24 to 14:23 due to relay(O/C to E/F) change.
k) Khulna 225 MW ST tripped at 13:15 due to governor valve problem was synchronized at 16:58.
l) Sikalbaha-Dohazari 132 kV Ckt-2 tripped at 12:45 from Sikalbaha end showing General trip |  |  |  |  | About 40 MW power interruption occurred under Dohazari S/S area &
and was switched on at 12:48. |  |  |  |  | 61 MW at Cox's Bazar S/S area from 12:45 to 12:48.
m) Bogura-Natore 132 kV Ckt-2 was under shut down from 13:48 to 15:20 for line checking by Natore.
n) Fenchuganj-Sreemangal 132 kV both Ckts tripped at 17:13 from both ends showing Dist. Z2, 67N at Fenchuganj
end & Dist. Z1 A,B phase at Sreemangal end and Ckt-2 was switched on at 17:42 & Ckt-1 till now under S/D.
o) Faridpur 132/33 kV T2 transformer was under shut down from 21:14 to 23:57 due to R/H at R-phase & B-phase
of incoming CT.
p) Chandpur 150 MW CCPP GT was shut down at 22:10 due to problem with cooling fan.
was synchronized at 11:05.
q) Chowmuhuni 132/33 kV T1 & T3 transformer tripped at 02:55(06/08/2020) from 33 kV side showing O/C as |  |  |  |  | About 136 MW power interruption occurred under Chowmuhuni S/S area
Y-phase loop between breaker & CT of 33 kV Sonaimuri feeder got snapped and were switched on at 03:10(06/08/2020) |  |  |  |  | from 02:55(06/08/2020) to 03:10(06/08/2020).
r) Bogura 230/132 kV T03 transformer tripped at 03:47(06/08/2020) showing winding temperature high.
s) Khulna©-KPCL-2 132 kV Ckt was under shut down from 07:26(06/08/2020) to 11:06(06/08/2020) for C/M.
t) Bagerhat 132/33 kV T1 transformer tripped at 07:25(06/08/2020) from 33 kV side showing E/F due to
33 kV Pirozpur feeder fault and was switched on at 07:30(06/08/2020)

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-08-05 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 705000 | Unit-2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 180 | 3469000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 6953045
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 68 | 1381408
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 96 | 1744863
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 346 | 7973000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9037000
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 41 | 627840 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 140 | 3360175 | FGMO & GT-1 Under maint.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 78 | 1324272 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 0 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 16 | 235368 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 180 | 3447000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 24 | 241920 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 321 | 7377985
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 50 | 768096 | High voltage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel Shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 18000 | Reserve
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 48 | 513600 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 14915 | Reserve
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 212268 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 41 | 937500 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 656100
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 603000 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 165 | 2200472 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 133 | 2335680 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 0 | Reserve
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 72 | 1435200 | Low demand
| Dhaka area Total |  |  |  | 5895 | 2859 | 57572707
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 8 | 40444 | Low demand
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 46305
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | Reserve
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 102 | 2383580 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under S/D.
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 139 | 3042196
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 720219
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2388480
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 476448
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 41 | 733440
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 34 | 185280 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 30000
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 306 | 5652982
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 10684 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2273280
| Chattogram area Total |  |  |  | 2266 | 953 | 17983338
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 135 | 2721125 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 100 | 2384284 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 210 | 4854000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 325 | 7474500 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 40 | 891720
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 49 | 732960 | Engine problem
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 45 | 1003636 | Engine problem
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1080548
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 35 | 209090 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 91 | 1363790 | ST under maint.
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 749760 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 453816
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 196740
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 126 | 2637120
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 806700
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 1192301
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 19 | 363550 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1961940
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 57 | 383880 | Low demand
| Cumilla Area Total |  |  |  | 2980 | 1510 | 31461460
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 153 | 3528400 | Engine problem
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 335088 | Engine problem
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 74 | 1467840
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 15400
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 4423200 | Low demand
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 62 | 987600 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 506 | 10757528
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1371000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 22 | 637440 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3562281
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 222 | 4911000
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1141200
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 45 | 975960
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 240000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 29 | 662592 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1665600
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | Under maint.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 408000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 439320
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7216700
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 233640
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1031 | 23464733
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 935 | 22444364
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 1591680
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 145 | 1424772 | Low demand
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 350 | 8437824 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 421500
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 16 | 479040 | Low demand
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 73440 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Reserve
| Khulna Area Total |  |  |  | 2284 | 1601 | 34872620
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 892128 | Low demand
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 21 | 467723
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 88 | 2144306 | GT-2 Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 76 | 1419476 | Engine problem
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 529 | 10712300
| Barisal Area Total |  |  |  | 1054 | 746 | 15635933
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage.
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 200 | 3999909 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 193 | 4878545 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 403 | 9091690 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 26 | 139749
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 20 | 456720
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 10 | 249624
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 175770 | Engine problem
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 99 | 748680
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 118656 | Reserve
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 1904928
| Rajshahi Area Total |  |  |  | 2183 | 1068 | 21764271
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 149 | 3660900 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 3 | 12000 | Low demand
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 112 | 1260480
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 55249
| Rangpur Area Total |  |  |  | 605 | 264 | 4988629
| Total |  |  |  | 19892 | 10538 | 218501219
| Eastern Grid Total |  |  |  | 13766 | 6859 | 141239766
| Western Grid Total |  |  |  | 6126 | 3679 | 77261453
| National Grid Total |  |  |  | 19892 | 10538 | 218501219
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-08-05
(a) ENTIRE EASTERN GRID : |  | 6707 | MW | (b) ENTIRE WESTERN GRID : |  | 3474 | MW
i) Dhaka area |  | 3054 | MW | i) Khulna area |  | 1323 | MW
ii) Chittagong area |  | 1076 | MW | ii) Rajshahi area |  | 1107 | MW
iii) Comilla area |  | 1138 | MW | iii) Barisal area |  | 281 | MW
iv) Mymensingh area |  | 954 | MW | iv) Rangpur area |  | 763 | MW
v) Sylhet area |  | 485 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 10181 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 96 | 24:00 | Sherpur | 110 | 23:00 | Jhenida | 106 | 19:30
Munsiganj | 120 | 21:00 | Srimongal | 52 | 21:00 | Bottail | 120 | 21:00
Sonargaon | 68 | 24:00 | Shahjibazar | 110 | 21:00 | G.K Project | 56 | 22:00
Shyampur | 110 | 23:00 | Fenchuganj | 44 | 1:00 | Faridpur | 183 | 0.041667
Bhulta | 117 | 24:00 | Kulawara | 49 | 23:00 | Madaripur | 102 | 0.91667
Madanganj | 38 | 18:30 | Sylhet | 130 | 20:00 | Sariatpur | 68 | 1:00
Shitalakhya | 65 | 15:00 | Chatak | 29 | 1:00 | Gopalganj | 86 | 21:00
Rahim steel | 0 | 1:00 | Sunamganj | 48 | 1:00 | Bagerhat | 89 | 21:00
Matuail | 42 | 21:00 | Biani Bazar | 59 | 23:00 | Mongla | 30 | 24:00
Ghorasal | 75 | 22:00 | Comilla (S) | 130 | 23:00 | Satkhira | 88 | 0.041667
Narsingdi | 142 | 23:00 | Comilla(N) | 141 | 22:00 | Gallamari | 36 | 13:00
Haripur (SBU) | 67 | 23:00 | Chandpur | 102 | 19:30 | Magura | 50 | 0.875
Ullon | 54 | 19:00 | Feni | 132 | 22:00 | Norail | 39 | 21:00
Hasnabad | 158 | 21:00 | Chowmuhani | 154 | 23:00 | Chuadanga | 86 | 20:00
Magbazar | 86 | 13:00 | Ashuganj | 54 | 22:00 | Barisal(N) | 48 | 0.041667
Maniknagar | 70 | 10:00 | Daudkandi | 140 | 22:00 | Barisal (S) | 90 | 0.875
Bangabhaban | 32 | 12:00 | B.Baria | 170 | 21:00 | Patuakhali | 119 | 0.041667
Narinda | 56 | 13:00 | Ramganj | 118 | 22:00 | Bhandaria | 50 | 0.041667
Dhanmondi | 152 | 13:00 | Chaddagram | 41 | 22:00 | Borhan Uddin | 40 | 4:00
Lalbag | 37 | 13:00 | PHP | 3 | 9:00 | Ishurdi | 54 | 21:00
Madartek | 64 | 23:00 | Madunaghat | 52 | 15:00 | Ruppur Paromanobik | 2 | 20:00
Dhaka University |  |  | Hathazari | 96 | 0.83333 | Natore | 122 | 1:00
Fatullah | 16 | 0.875 | Khulshi | 176 | 0.83333 | Bogra | 150 | 22:00
Mirpur | 85 | 19:00 | Halishahar | 114 | 0.8125 | Noagaon | 113 | 1:00
Kalyanpur | 75 | 19:00 | Baraulia | 108 | 0.70833 | Rajshahi | 140 | 21:00
Gulshan | 94 | 19:00 | Sikalbaha | 26 | 0.625 | Rajshahi New | 11 | 23:00
Uttara | 70 | 15:00 | Dohazari | 102 | 0.8125 | C.Nawabganj | 67 | 23:00
Uttara New | 21 | 19:00 | Cox'sbazar | 97 | 0.79167 | Amnura | 51 | 21:00
Kamrangirchar | 60 | 19:30 | Chandraghona | 30 | 0.79167 | Pabna | 109 | 20:00
Savar | 90 | 16:00 | Kaptai | 4.4 | 0.79167 | Shahjadpur | 98 | 1:00
Bhasantec | 128 | 13:00 | A. Khaer Stl. | 0 | 0.041667 | Serajganj | 92 | 1:00
Agargaon | 64 | 13:00 | Bakulia | 86 | 0.83333 | Niyamatpur | 56 | 1:00
Satmosjid | 90 | 19:00 | Julda | 18 | 0.79167 | Joypurhat | 54 | 21:00
Tongi | 89 | 0.8125 | TK chemical | 23 | 0.041667 | Sherpur(Bogura) | 42 | 19:30
Kabirpur | 136 | 13:00 | Modern Steel | 0.2 | 0.041667 | Mohastangor | 52 | 1:00
Basundhara | 110 | 15:00 | Shahmirpur | 27 | 0.91667 | Rangpur | 159 | 19:30
Manikganj | 64 | 21:00 | Khagrachhari | 25 | 0.16667 | Lalmonirhat | 62 | 21:00
Joydevpur | 137 | 21:00 | Matarbari | 35 | 0.875 | Saidpur | 110 | 22:00
New Tongi | 62 | 15:00 | Baroiar Hat | 38 | 0.79167 | Purbasadipur | 90 | 1:00
Korda | 130 | 21:00 | Rangamati | 12 | 0.79167 | Thakurgaon | 86 | 21:00
Dhamrai | 74 | 21:00 | Abul Khair 230 | 28 | 0.083333 | Palashbari | 123 | 23:00
Rajendrapur | 78 | 22:00 | BSRM | 162 | 0.41667 | Barapukuria | 47 | 2:00
Valuka | 78 | 21:00 | GPH Ispat | 69 | 0.5 | Panchagar | 52 | 21:00
Tangail | 188 | 21:00 | Goalpara | 15 | 0.5 | Joldhaka | 32 | 21:00
Mymensing | 215 | 23:00 | Central s/s | 87 | 19:30 | Kurigram | 58 | 20:00
Kishorganj | 159 | 21:00 | Noapara | 43 | 22:00
Netrokona | 122 | 1:00 | Jessore | 116 | 21:00
Jamalpur | 138 | 23:00 | Benapol | 36 | 1:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-08-05 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 394 | 19:30 | 386 | 22:00 | Kaliakoir | 378 | 0.16667 | 369 | 0.58333
| Bheramara | 402 | 24:00 | 396 | 20:00 | Bhulta | 391 | 0.16667 | 382 | 0.54167
| Ashuganj(N) | 396 | 19:30 | 388 | 10:00 | Gopalganj | 418 | 0.625 | 390 | 0.91667
| Payra | 418 | 14:00 | 406 | 3:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 21:00 | 232 | 1:00 | Comilla (N) | 233 | 19:30 | 228 | 17:00
| Ishurdi | 238 | 18:00 | 225 | 22:00 | Hathazari | 222 | 21:00 | 212 | 17:00
| Ashuganj | 237 | 20:00 | 231 | 11:00 | Megnaghat | 232 | 1:00 | 230 | 9:00
| Serajganj | 232 | 10:00 | 225 | 23:00 | Fenchuganj | 236 | 11:00 | 230 | 23:00
| Baghabari | 243 | 18:00 | 232 | 1:00 | Siddhirganj | 234 | 1:00 | 227 | 12:00
| Barapukuria | 235 | 18:00 | 223 | 23:00 | Maniknagar | 232 | 4:00 | 226 | 13:00
| Bogra | 228 | 18:00 | 214 | 24:00 | Agargaon | 228 | 1:00 | 222 | 13:00
| Rajshahi | 231 | 18:00 | 217 | 23:00 | Barisal | 248 | 15:00 | 229 | 22:00
| Khulna South | 228 | 16:00 | 217 | 19:00 | AKSML | 219 | 20:00 | 210 | 17:00
| Rampura | 229 | 4:00 | 222 | 13:00 | BSRM | 223 | 19:30 | 212 | 17:00
| Haripur | 231 | 1:00 | 225 | 14:00 | Bibiyana | 235 | 6:00 | 229 | 17:00
| Hasnabad | 230 | 1:00 | 224 | 11:00 | Bhulta | 233 | 4:00 | 226 | 13:00
| Shyampur | 227 | 1:00 | 222 | 13:00 | Ashuganj (S) | 234 | 1:00 | 232 | 10:00
| Aminbazar | 230 | 1:00 | 224 | 11:00 | Kaliakoir | 232 | 1:00 | 225 | 14:00
| Tongi | 230 | 19:00 | 218 | 15:00 | GPH | 221 | 1:00 | 207 | 17:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 133 | 1:00 | 129 | 11:00 | Hathazari | 132 | 0.77083 | 127 | 0.70833
| Munsiganj | 133 | 1:00 | 126 | 13:00 | Khulshi | 132 | 0.8125 | 125 | 0.70833
| Sonargaon | 133 | 1:00 | 127 | 7:00 | Halishahar | 134 | 0.8125 | 126 | 0.70833
| Shyampur | 134 | 1:00 | 130 | 13:00 | Baraulia | 133 | 0.875 | 127 | 0.70833
| Bhulta | 126 | 1:00 | 123 | 8:00 | Sikalbaha | 135 | 19:30 | 127 | 0.70833
| Madanganj | 133 | 18:00 | 131 | 1:00 | Dohazari | 129 | 7:00 | 121 | 0.77083
| Shitalakhya | 140 | 1:00 | 131 | 13:00 | Cox'sbazar | 128 | 0.375 | 113 | 0.75
| Rahim steal | 133 | 1:00 | 129 | 11:00 | Chandraghona | 133 | 0.8125 | 127 | 0.70833
| Matuail | 133 | 1:00 | 129 | 11:00 | Kaptai | 133 | 21:00 | 128 | 0.54167
| Ghorasal | 138 | 19:30 | 136 | 1:00 | A. Khaer Stl. | 131 | 0.125 | 128 | 15:00
| Narsinghdi | 129 | 18:30 | 124 | 10:00 | Bakulia | 133 | 0.8125 | 126 | 0.70833
| Haripur (SBU) | 136 | 1:00 | 129 | 12:00 | Julda | 133 | 0.041667 | 127 | 0.70833
| Ullon | 135 | 7:00 | 130 | 13:00 | TK Chemical | 134 | 0.8125 | 128 | 17:00
| Hasnabad | 138 | 1:00 | 130 | 13:00 | Modern Steel | 133 | 0.83333 | 127 | 0.70833
| Magbazar | 135 | 3:00 | 130 | 12:00 | Shahmirpur | 134 | 0.8125 | 128 | 0.70833
| Maniknagar | 135 | 2:00 | 131 | 13:00 | Khagrachhari | 131 | 0.16667 | 126 | 0.70833
| Bangabhaban | 135 | 2:00 | 131 | 13:00 | Matarbari | 130 | 0.41667 | 115 | 0.77083
| Narinda | 135 | 2:00 | 131 | 13:00 | Baroiar Hat | 131 | 0.33333 | 126 | 0.041667
| Dhanmondi | 135 | 7:00 | 130 | 13:00 | Rangamati | 132 | 0.8125 | 127 | 17:00
| Lalbag | 138 | 1:00 | 131 | 13:00 | Goalpara S/S | 137 | 9:00 | 133 | 18:30
| Madartek | 135 | 3:00 | 130 | 13:00 | Khulna Central S/S | 138 | 0.66667 | 132 | 19:00
| Dhaka University |  |  |  |  | Noapara | 137 | 16:00 | 129 | 19:30
| Fatuiiah | 135 | 0.041667 | 131 | 13:00 | Jessore | 135 | 16:00 | 120 | 22:00
| Mirpur | 133 | 5:00 | 130 | 15:00 | Benapol | 134 | 16:00 | 121 | 19:00
| Kalyanpur | 134 | 7:00 | 130 | 12:00 | Jhenida | 132 | 0.66667 | 116 | 21:00
| Gulshan | 134 | 3:00 | 130 | 12:00 | Bottail | 134 | 18:00 | 125 | 21:00
| Uttara | 134 | 6:00 | 130 | 12:00 | G.K Project | 140 | 0.75 | 132 | 23:00
| Uttara New | 135 | 7:00 | 128 | 12:00 | Faridpur | 135 | 14:00 | 123 | 23:00
| Kamrangirchar | 136 | 2:00 | 128 | 13:00 | Madaripur | 140 | 0.58333 | 127 | 22:00
| Savar | 133 | 6:00 | 129 | 14:00 | Shariyatpur S/S | 140 | 0.58333 | 124 | 23:00
| Bhasantec | 134 | 3:00 | 129 | 13:00 | Gopalganj | 141 | 14:00 | 124 | 22:00
| Agargaon | 134 | 4:00 | 130 | 13:00 | Bagerhat | 138 | 16:00 | 128 | 19:00
| Satmosjid | 134 | 5:00 | 129 | 13:00 | Mongla | 134 | 0.70833 | 125 | 4:00
| Tongi | 137 | 0.33333 | 132 | 13:00 | Satkhira | 138 | 0.33333 | 129 | 21:00
| Kabirpur | 135 | 7:00 | 130 | 22:00 | Gallamari | 138 | 8:00 | 132 | 19:00
| Basundhara | 134 | 19:30 | 129 | 14:00 | Magura | 134 | 16:00 | 113 | 21:00
| Manikganj | 137 | 20:00 | 132 | 14:00 | Norail | 131 | 0.66667 | 110 | 21:00
| Joydevpur | 140 | 2:00 | 135 | 7:00 | Chuadanga | 129 | 16:00 | 106 | 21:00
| New Tongi | 136 | 0.041667 | 130 | 13:00 | Barisal(N) | 142 | 15:00 | 126 | 22:00
| Kodda | 135 | 9:00 | 125 | 0.45833 | Barisal (S) | 140 | 0.625 | 124 | 22:00
| Dhamrai | 135 | 12:00 | 129 | 22:00 | Patuakhali(S) | 140 | 0.54167 | 120 | 22:00
| Rajendrapur | 133 | 8:00 | 123 | 13:00 | Bhandaria | 140 | 13:00 | 120 | 22:00
| Valuka | 126 | 16:00 | 112 | 22:00 | Ishurdi | 138 | 18:00 | 131 | 22:00
| Tangail | 136 | 12:00 | 125 | 22:00 | Ruppur Paromanobik | 137 | 18:00 | 130 | 22:00
| Mymensing | 129 | 16:00 | 115 | 22:00 | Natore | 135 | 18:00 | 124 | 23:00
| Kishorganj | 128 | 12:00 | 117 | 22:00 | Bogra | 134 | 18:00 | 122 | 23:00
| Netrokona | 125 | 17:00 | 110 | 22:00 | Noagaon | 130 | 18:00 | 117 | 23:00
| Jamalpur | 136 | 19:00 | 126 | 22:00 | Rajshahi | 132 | 18:00 | 122 | 22:00
| Sherpur | 135 | 9:00 | 124 | 22:00 | Rajshahi New | 132 | 18:00 | 122 | 22:00
| Srimongal | 134 | 10:00 | 128 | 0.91667 | C.Nawabganj | 130 | 18:00 | 121 | 22:00
| Shahjibazar | 133 | 12:00 | 126 | 0.91667 | Amnura | 131 | 18:00 | 120 | 23:00
| Fenchuganj | 133 | 12:00 | 125 | 0.95833 | Pabna | 135 | 18:00 | 128 | 22:00
| Khulawara | 132 | 12:00 | 125 | 0.95833 | Shahjadpur | 139 | 18:00 | 131 | 22:00
| Sylhet | 128 | 10:00 | 119 | 0.95833 | Serajganj | 134 | 18:00 | 125 | 22:00
| Chatak | 128 | 10:00 | 118 | 22:00 | Niyamatpur | 129 | 18:30 | 114 | 23:00
| Sunamganj | 127 | 12:00 | 114 | 0.041667 | Joypurhat | 130 | 18:00 | 115 | 23:00
| Biani Bazar | 128 | 10:00 | 118 | 0.95833 | Sherpur(Bogura) | 134 | 18:00 | 123 | 23:00
| Comilla(s) | 126 | 7:00 | 121 | 19:00 | Mohastangor | 132 | 18:00 | 119 | 23:00
| Comilla(n) | 135 | 8:00 | 130 | 19:00 | Rangpur | 129 | 18:30 | 114 | 23:00
| Chandpur | 126 | 11:00 | 122 | 18:00 | Lalmonirhat | 123 | 15:00 | 110 | 23:00
| Feni | 131 | 8:00 | 125 | 16:00 | Saidpur | 130 | 18:30 | 114 | 23:00
| Chowmuhani | 125 | 7:00 | 120 | 17:00 | Purbasadipur | 127 | 18:30 | 111 | 22:00
| Ashuganj | 133 | 18:00 | 130 | 23:00 | Thakurgaon | 127 | 18:00 | 105 | 23:00
| Daudkandi | 130 | 16:00 | 126 | 22:00 | Palashbari | 129 | 18:30 | 115 | 23:00
| B.Baria | 131 | 11:00 | 123 | 22:00 | Barapukuria | 135 | 18:00 | 123 | 23:00
| Ramganj | 119 | 19:30 | 118 | 18:00 | Panchagar | 122 | 18:00 | 100 | 23:00
| Chaddagram | 131 | 7:00 | 117 | 15:00 | Joldhaka | 128 | 18:30 | 110 | 23:00
| PHP | 130 | 8:00 | 122 | 17:00 | Kurigram | 122 | 18:00 | 107 | 23:00
| Madanhat | 135 | 19:30 | 129 | 16:00

## L-Curve
Date | 2020-08-05
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 157 | 6838 | 3800 | 10638 |  |  |  | QF-LDC-12
0:30 | 81 | 6783.5 | 3703 | 10486.5 | Date: | 2020-08-05
1:00 | 5 | 6729 | 3606 | 10335
1:30 | 5 | 6618.5 | 3571 | 10189.5
2:00 | 5 | 6508 | 3536 | 10044
2:30 | 6.5 | 6466.5 | 3557 | 10023.5 | [5 empty] | Gen. at Eve. Peak | 10538 | 10538 MW (21:00 )
3:00 | 8 | 6425 | 3578 | 10003 | [6 empty] | 21:00
3:30 | 93 | 6339.5 | 3554.5 | 9894 | [5 empty] | Gen. at Day Peak | 8171.6 | 8171.6 MW (10:00 )
4:00 | 178 | 6254 | 3531 | 9785 | [6 empty] | 10:00
4:30 | 212 | 6186.5 | 3553.5 | 9740 | [5 empty] | Highest Generation | 10666
5:00 | 246 | 6119 | 3576 | 9695 | [6 empty] | 23:00
5:30 | 284 | 5778.84 | 3434.1 | 9212.94
6:00 | 322 | 5438.68 | 3292.2 | 8730.88
6:30 | 343.5 | 5259.085 | 3186.2 | 8445.285
7:00 | 365 | 5079.49 | 3080.2 | 8159.69
7:30 | 397.5 | 5083.145 | 3042.9 | 8126.045
8:00 | 430 | 5086.8 | 3005.6 | 8092.4
8:30 | 423.5 | 5151.8 | 2934.05 | 8085.85
9:00 | 417 | 5216.8 | 2862.5 | 8079.3
9:30 | 444.5 | 5251.9 | 2873.55 | 8125.45
10:00 | 472 | 5287 | 2884.6 | 8171.6
10:30 | 509 | 5200.75 | 2887 | 8087.75
11:00 | 546 | 5114.5 | 2889.4 | 8003.9
11:30 | 480.5 | 5199.15 | 2822.15 | 8021.3
12:00 | 415 | 5283.8 | 2754.9 | 8038.7
12:30 | 416.5 | 5277.45 | 2709.35 | 7986.8
13:00 | 418 | 5271.1 | 2663.8 | 7934.9
13:30 | 434 | 5348.55 | 2618 | 7966.55
14:00 | 450 | 5426 | 2572.2 | 7998.2
14:30 | 419 | 5512.1 | 2567.4 | 8079.5
15:00 | 388 | 5598.2 | 2562.6 | 8160.8
15:30 | 422 | 5571 | 2543.9 | 8114.9
16:00 | 456 | 5543.8 | 2525.2 | 8069
16:30 | 485.5 | 5365.8 | 2568.5 | 7934.3
17:00 | 515 | 5187.8 | 2611.8 | 7799.6
17:30 | 496 | 5026.15 | 2606.5 | 7632.65
18:00 | 477 | 4864.5 | 2601.2 | 7465.7
18:30 | 291 | 5538.75 | 2859.6 | 8398.35
19:00 | 105 | 6213 | 3118 | 9331
19:30 | 29 | 6639 | 3437 | 10076
20:00 | 65 | 6730 | 3532 | 10262 |  |  |  | Executive Engineer
20:30 | 84.5 | 6794.5 | 3605.5 | 10400 |  |  |  | Network Operation Division
21:00 | 104 | 6859 | 3679 | 10538
21:30 | 83.5 | 6889 | 3691 | 10580
22:00 | 63 | 6919 | 3703 | 10622 |  |  |  |  | Page 6 of 7
22:30 | 122.5 | 6902.5 | 3741.5 | 10644
23:00 | 182 | 6886 | 3780 | 10666
23:30 | 169.5 | 6862 | 3790 | 10652
24:00 | 157 | 6838 | 3800 | 10638
10538 MW (21:00 )
8171.6 MW (10:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-08-05 |  | Energy | 218501219
[10 empty] | 2020-08-05 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3563 | 930 | 2325 | 2395 | 706 | 103 | 425 | 0 | 128
0:30 | 3508 | 935.5 | 2300 | 2516 | 642 | 102.5 | 322 | 0 | 129 | Date: | 2020-08-05
1:00 | 3453 | 941 | 2275 | 2637 | 578 | 102 | 219 | 0 | 130
1:30 | 3459.5 | 940.5 | 2268 | 2541.5 | 583.5 | 102 | 165.5 | 0 | 129 | [7 empty] | Total Energy | 218.5012 | Total Energy Gen 218.501 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 218.501 MKWHr
2:00 | 3466 | 940 | 2261 | 2446 | 589 | 102 | 112 | 0 | 128 | [7 empty] | Energy not Served | 0
2:30 | 3457.5 | 940 | 2251 | 2414 | 632 | 101 | 101 | 0 | 127 | [7 empty] | Energy Requirement | 218.5012
3:00 | 3449 | 940 | 2241 | 2382 | 675 | 100 | 90 | 0 | 126
3:30 | 3431 | 940.5 | 2242 | 2295 | 677 | 100 | 84.5 | 0 | 124 | [6 empty] | Shortage
4:00 | 3413 | 941 | 2243 | 2208 | 679 | 100 | 79 | 0 | 122
4:30 | 3413 | 941 | 2251 | 2135.5 | 674 | 100 | 106.5 | 0 | 119
5:00 | 3413 | 941 | 2259 | 2063 | 669 | 100 | 134 | 0 | 116
5:30 | 3336 | 941 | 2129.5 | 1831 | 649 | 100 | 117 | 0 | 109
6:00 | 3259 | 941 | 2000 | 1599 | 629 | 100 | 100 | 0 | 102
6:30 | 3213.5 | 941 | 1941.5 | 1424.5 | 614 | 100.5 | 110 | 0 | 98 |  |  |  |  | Coal
7:00 | 3168 | 941 | 1883 | 1250 | 599 | 101 | 120 | 0 | 94
7:30 | 3149 | 941 | 1888 | 1236.5 | 585 | 101 | 125 | 0 | 93 |  |  |  | Oil |  |  |  | ,
8:00 | 3130 | 941 | 1893 | 1223 | 571 | 101 | 130 | 0 | 92
8:30 | 3130 | 935.5 | 1927 | 1235 | 535 | 101.5 | 125 | 0 | 88
9:00 | 3130 | 930 | 1961 | 1247 | 499 | 102 | 120 | 0 | 84
9:30 | 3163 | 930 | 1971 | 1243.5 | 498.5 | 102 | 120 | 0 | 88
10:00 | 3196 | 930 | 1981 | 1240 | 498 | 102 | 120 | 0 | 92
10:30 | 3222.5 | 929.5 | 1989.5 | 1120 | 497.5 | 102.5 | 120 | 0 | 93
11:00 | 3249 | 929 | 1998 | 1000 | 497 | 103 | 120 | 0 | 94
11:30 | 3279 | 929.5 | 2018.5 | 976 | 497.5 | 103 | 100 | 0 | 96
12:00 | 3309 | 930 | 2039 | 952 | 498 | 103 | 80 | 0 | 98
12:30 | 3321 | 932.5 | 2036.5 | 929.5 | 488.5 | 103 | 55 | 0 | 96
13:00 | 3333 | 935 | 2034 | 907 | 479 | 103 | 30 | 0 | 94
13:30 | 3333 | 935 | 2034 | 907 | 479 | 103 | 30 | 0 | 94
14:00 | 3333 | 935 | 2034 | 907 | 479 | 103 | 30 | 0 | 94
14:30 | 3213.5 | 933.5 | 2067.5 | 1124.5 | 471.5 | 101.5 | 15 | 0 | 100
15:00 | 3094 | 932 | 2101 | 1342 | 464 | 100 | 0 | 0 | 106
15:30 | 3130 | 934 | 2109 | 1239.5 | 456.5 | 99.5 | 22.5 | 0 | 107
16:00 | 3166 | 936 | 2117 | 1137 | 449 | 99 | 45 | 0 | 108
16:30 | 3209.5 | 935.5 | 2003 | 1077.5 | 449 | 99 | 48.5 | 0 | 104
17:00 | 3253 | 935 | 1889 | 1018 | 449 | 99 | 52 | 0 | 100
17:30 | 3143.5 | 935 | 1771 | 1058 | 449 | 99.5 | 77 | 0 | 97
18:00 | 3034 | 935 | 1653 | 1098 | 449 | 100 | 102 | 0 | 94
18:30 | 3284.5 | 935 | 1922 | 1370.5 | 470 | 100.5 | 208.5 | 0 | 107
19:00 | 3535 | 935 | 2191 | 1643 | 491 | 101 | 315 | 0 | 120
19:30 | 3510 | 936 | 2222 | 2229 | 571 | 101 | 383 | 0 | 124
20:00 | 3554 | 936 | 2275 | 2256 | 637 | 101 | 383 | 0 | 120
20:30 | 3606.5 | 935.5 | 2302 | 2271 | 657.5 | 101.5 | 403 | 0 | 123
21:00 | 3659 | 935 | 2329 | 2286 | 678 | 102 | 423 | 0 | 126
21:30 | 3659.5 | 935.5 | 2334 | 2319.5 | 677 | 102 | 425.5 | 0 | 127
22:00 | 3660 | 936 | 2339 | 2353 | 676 | 102 | 428 | 0 | 128
22:30 | 3666.5 | 933 | 2336.5 | 2374 | 676.5 | 102 | 426.5 | 0 | 129
23:00 | 3673 | 930 | 2334 | 2395 | 677 | 102 | 425 | 0 | 130
23:30 | 3618 | 930 | 2329.5 | 2395 | 691.5 | 102.5 | 425 | 0 | 129 | Max Temp. in Dhaka |  | 34.6° C
24:00 | 3563 | 930 | 2325 | 2395 | 706 | 103 | 425 | 0 | 128
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 218.501 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 218.501 MKWHr
Note on W13: Author:

## Generation
g | 2020-08-05
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 37 | 37 | 35 | 35 | 35 | 35 | 36 | 36 | 37 | 37 | 38 | 38 | 38 | 37 | 35 | 34 | 34 | 35 |  | 36 | 36 | 36 | 37 | 37 | 37 | 38 | 815580
2 | Karnaphuli Hydro PP Unit-4 & 5 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1568000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [20 empty] | 2 | 5 | 8 | 8 | 8 | 8 | 40444
| Teknaf 20MW PP (Solartech) | [5 empty] | 0.28 | 1.49 | 5.4 |  |  |  | 13.8 | 9 |  | 12.7 | 5.2 | 3.1 | 0.3 | [8 empty] | 46305
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 140 | 140 | 140 | 139 | 139 | 104 | 104 | 104 | 105 | 140 | 141 | 139 | 141 | 139 |  | 104 | 104 | 104 |  | 139 | 139 | 139 | 139 | 140 | 144 | 139 | 3042196
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 17 | [13 empty] | 15 | 17 | 17 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 720219
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 150 | 150 | 150 | 120 | 120 | 115 | 70 | 70 | 70 | 73 | 116 | 184 | 175 | 140 | 108 | 110 | 115 | 88 |  | 150 | 110 | 144 | 180 | 180 | 185 | 160 | 3447000
17 | Siddhirganj 335 MW CCPP | 322 | 323 | 326 | 326 | 325 | 300 | 270 | 270 | 270 | 300 | 321 | 315 | 313 | 313 | 280 | 280 | 280 | 250 |  | 324 | 324 | 323 | 321 | 321 | 319 | 323 | 7377985
18 | Kodda 300 MW PP Unit-2 (Summit) | 200 | 145 | 145 | 110 | 60 | 30 | 30 | 28 | 30 | 30 | 30 | 30 | 45 | 49 | 77 | 60 | 60 | 60 |  | 75 | 145 | 160 | 165 | 165 | 95 | 95 | 2200472
19 | Ashuganj 195MW PP (APSCL-United) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 29 | 45 | 45 | 45 | 45 | 45 | 45 | 1003636
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  |  |  | 30 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 705000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 151 | 150 | 150 | 150 | 151 | 100 | 100 | 100 | 100 | 100 | 100 | 200 | 160 | 160 | 200 | 120 | 100 | 100 |  | 180 | 180 | 180 | 180 | 180 | 200 | 200 | 3469000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 280 | 260 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 6953045
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 85 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 105 | 135 | 135 | 135 | 135 | 120 |  | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 2721125
30 | Ashuganj TPP Unit- 5 | 95 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2384284
32 | Ashuganj 50 MW PP | 39 | 39 | 39 | 39 | 39 | 38 | 38 | 38 | 41 | 41 | 41 | 41 | 41 | 38 | 38 | 38 | 38 | 40 |  | 40 | 40 | 40 | 40 | 38 | 42 | 39 | 891720
33 | Ashuganj 225 MW CCPP | 209 | 209 | 209 | 210 | 210 | 200 | 200 | 171 | 208 | 193 | 181 | 180 | 182 | 180 | 206 | 208 | 181 | 181 |  | 207 | 209 | 211 | 210 | 209 | 208 | 210 | 4854000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 305 | 290 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 295 | 280 | 280 | 345 | 290 | 310 | 310 | 340 | 270 |  | 310 | 300 | 300 | 325 | 325 | 350 | 320 | 7474500
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 40 | 46 | 44 | 40 | 37 | 39 | 42 | 44 | 45 |  | 47 | 48 | 48 | 49 | 48 | 47 | 48 | 732960
36 | Chandpur 150 MW CCPP | 51 | 52 | 52 | 52 | 51 | 50 | 50 | 51 | 51 | 51 | 50 | 51 | 50 | 50 | 51 | 91 | 97 | 80 |  | 97 | 80 | 91 | 91 | 90 |  |  | 1363790
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 420 | 420 | 420 | 420 | 420 | 400 | 370 | 370 | 370 | 370 | 370 | 400 | 400 | 450 | 450 | 450 | 450 | 340 |  | 450 | 450 | 450 | 450 | 450 | 450 | 420 | 9037000
41 | Haripur 360MW CCPP(HPL) | 347 | 348 | 350 | 349 | 348 | 324 | 304 | 305 | 300 | 300 | 347 | 343 | 341 | 300 | 340 | 340 | 300 | 270 |  | 346 | 346 | 350 | 346 | 347 | 344 | 346 | 7973000
42 | RPCL 210MW CCPP | 151 | 152 | 155 | 154 | 152 | 152 | 151 | 150 | 147 | 144 | 147 | 147 | 144 | 148 | 144 | 145 | 152 | 155 |  | 152 | 155 | 155 | 153 | 153 | 151 | 153 | 3528400
43
44 | Fenchugonj CCPP Phase-1 | 58 | 58 | 58 | 58 | 59 | 59 | 59 | 58 | 58 | 58 | 58 | 58 | 57 | 59 | 56 | 56 | 56 | 56 |  | 56 | 60 | 60 | 60 | 60 | 58 | 59 | 1371000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 637440
46 | Shajibazar 330 MW CCPP | 216 | 216 | 217 | 217 | 217 | 218 | 217 | 216 | 216 | 217 | 209 | 207 | 207 | 206 | 205 | 207 | 207 | 207 |  | 204 | 208 | 208 | 222 | 218 | 215 | 216 | 4911000
47 | Shahjibazar GTPP Unit- 8 & 9 | 28 | 28 | 28 | 28 | 28 | 29 | 28 | 28 | 28 | 28 | 28 | 27 | 27 | 27 | 28 | 20 | 29 | 29 |  | 29 | 30 | 29 | 29 | 29 | 28 | 29 | 662592
48 | Shahjibazar 86MW PP (Shahjibazar) | 87 | 87 | 84 | 84 | 84 | 40 | 10 | 10 | 82 | 82 | 83 | 82 | 81 | 80 | 82 | 85 | 10 | 40 |  | 85 | 85 | 85 | 85 | 85 | 85 | 82 | 1665600
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 408000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 233640
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 5 | 5 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 240000
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 47 | 50 | 53 | 53 | 53 | 51 | 52 | 14 | 13 |  | 33 | 50 | 49 | 50 | 52 | 53 | 53 | 1141200
56 | Shahjahanulla 25 MW PP | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 21 | 21 | 16 | 16 | 16 | 20 | 20 | 22 | 8 |  | 8 | 8 | 8 | 16 | 24 | 24 | 24 | 439320
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 300 | 290 | 290 | 300 | 285 | 280 | 290 | 290 | 300 | 285 | 290 | 290 | 295 | 285 | 280 | 290 | 275 |  | 280 | 270 | 270 | 300 | 310 | 315 | 310 | 7216700
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 17 | 17 | 17 | 17 | [15 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 212268
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 476448
61 | Narshingdi 22 MW PP (Doreen) |  |  | 16 | 16 | 16 | 16 | 16 | 16 |  |  |  | 16 | 16 | 16 |  |  | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 235368
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 |  | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 335088
63 | Impoprt (Tripura) | 130 | 128 | 126 | 122 | 116 | 102 | 94 | 92 | 84 | 92 | 94 | 98 | 94 | 106 | 106 | 108 | 100 | 94 |  | 120 | 124 | 120 | 126 | 128 | 130 | 128 | 2637120
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 40 | 40 | 41 | 40 | 13 | 18 | 18 | 18 | 17 | 15 | 21 | 18 | 18 | 19 | 29 | 31 |  | 40 | 40 | 40 | 41 | 41 | 40 | 41 | 733440
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 453816
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 8 | 8 | 11 | 11 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 196740
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 806700
68 | Cumilla 25 MW PP (Summit) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 15 | 18 | 19 | 19 |  |  |  |  | 15 | 15 | 15 |  | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 363550
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 20 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 |  | 12 | 12 | 16 | 16 | 20 | 20 | 20 | 337500
71 | Maona 33 MW PP(Summit) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 656100
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 603000
73 | Ghorashal 108MW PP (Regent) | 98 | 98 | 98 | 98 | 98 | 52 | 52 | 52 | 54 | 53 | 53 | 54 | 54 | 72 | 88 | 94 | 23 | 23 |  | 97 | 96 | 96 | 96 | 96 | 95 | 96 | 1744863
| Feni Lanka Power | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 100 | 51 | 30 | 17 | 17 | 17 |  |  |  |  | 42 | 114 | 114 | 114 | 114 | 114 | 114 | 1961940
| Chowmuhani 113 MW | [17 empty] | 42 |  | 57 | 57 | 57 | 57 | 56 | 56 | 56 | 383880
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | [9 empty] | 11 | 30 | 45 | 24 | 24 | 24 | 24 | 241920
78 | Gazipur 52 MW PP
79 | Kodda 150MW PP | 60 | 48 | 48 | 32 | 32 | [14 empty] | 16 | 32 | 32 | 48 | 48 | 48 | 48 | 513600
80 | Jamalpur 95 MW PP(Powerpac) | 95 | 95 | 95 | 95 | 95 | 95 | 48 | 48 | 88 | 64 | 8 | 8 | 8 | 8 | 40 | 40 | 40 | 40 |  | 95 | 95 | 95 | 74 | 72 | 72 | 72 | 1467840
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 43 | 52 | 52 | 34 | 34 | 34 |  | 34 | 52 | 52 | 52 | 52 | 52 | 52 | 1192301
| Gazipur 100 MW PP | [25 empty] | 0 | 0
| Kaptai 7 MW Solar PP | [5 empty] | 0.3 | 0.7 | 1.2 | 2 | 6.4 | 5.2 | 5.6 | 2.2 | 5.2 | 0.7 | 0.6 | 0.6 | 0.1 | [8 empty] | 30000
| Jodiac Power | [20 empty] | 8 |  |  |  |  | 0 | 10684
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | 70 | 63 | 64 | 64 | 64 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 40 | 65 | 48 | 48 |  | 48 | 50 | 65 | 78 | 78 | 91 | 95 | 1324272
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP(Summit) | 150 | 150 | 135 | 140 | 145 | 130 | 135 | 135 | 140 | 145 | 135 | 140 | 140 | 145 | 135 | 135 | 140 | 130 |  | 140 | 120 | 135 | 140 | 150 | 150 | 150 | 3360175
87 | Meghnaghat 100 MW(IEL) | 94 | 100 | 50 | 24 | 17 | 7 | 7 | 7 | 7 | 7 |  |  |  |  | 3 | 7 | 7 | 7 |  | 20 | 92 | 60 | 41 | 41 | 41 | 41 | 627840
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 104 | 94 | 30 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 53 | 90 | 70 | 53 | 53 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 1435200
88 | Ghorashal 78.5 MW PP(MAX) | 69 | 69 | 69 | 69 | 68 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 50 | 67 | 68 | 68 |  | 68 | 68 | 67 | 68 | 67 | 67 | 67 | 1381408
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44MW (Energyprima) | 45 | 45 | 45 | 45 | 46 | 46 | 46 | 46 | 45 | 41 | 41 | 41 | 41 | 44 | 42 | 42 | 10 | 5 |  | 25 | 35 | 47 | 45 | 45 | 47 | 47 | 975960
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 43 | 43 | 15 | 15 |  | 15 | 30 | 45 | 51 | 51 | 51 | 51 | 1080548
94 | Gagnagar 102 MW PP (Digital Power) | 74 | 24 | 24 | 24 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 768096
95 | Patenga 50MW PP (Baraka)
96 | Chattogram 108 MW PP (ECPV) | [19 empty] | 11 | 34 | 34 | 34 | 36 | 31 | 33 | 185280
97 | Katpotti 52 MW PP (Sinha)
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | [25 empty] | 0 | 0
100 | Manikganj 55 MW PP (Northern) | [19 empty] | 17 | 17 |  |  |  |  | 0 | 14915
101 | Kushiara 163 MW CCPP (KP) | 163 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 163 | 130 | 130 | 163 | 163 | 163 | 130 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3562281
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0.1 | 0.3 | 1.2 | 1.8 | 1.6 | 1.3 | 2.4 | 1.9 | 1.8 | 1.8 | 2 | 0.1 | 0.1 | [8 empty] | 15400
103 | Kamalaghat 54 MW PP(Banco Energy) | [19 empty] | 17 | 17 |  |  |  |  | 0 | 18000
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 193 | 193 | 193 | 194 | 194 | 194 | 194 | 192 | 192 | 192 | 192 | 192 | 192 | 190 | 200 | 160 | 120 | 120 |  | 134 | 200 | 200 | 200 | 200 | 200 | 193 | 4423200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 132 | 131 | 132 | 108 | 89 | 60 | 60 | 104 | 130 | 126 | 68 | 35 | 50 | 54 | 70 | 79 | 65 | 65 |  | 76 | 100 | 128 | 133 | 131 | 134 | 133 | 2335680
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 90 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2388480
116 | Chandpur 200MW (Desh energy) | 115 | 70 | 70 | 70 | 70 | 50 | 17 | [16 empty] | 17 | 95 | 120 | 749760
117 | Ashuganj 150MW PP (Midland) | [17 empty] | 20 |  | 30 | 30 | 30 | 35 | 40 |  | 0 | 209090
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 75 | 45 | 8 | 8 | 8 | 8 | 8 | [7 empty] | 2 |  | 19 | 45 | 45 | 62 | 75 | 102 | 115 | 987600
| Anwara 300 MW PP (United) | 306 | 308 | 307 | 307 | 307 | 215 | 178 | 178 | 178 | 178 | 123 | 124 | 106 | 212 | 302 | 196 | 160 | 160 |  | 301 | 305 | 305 | 306 | 306 | 306 | 307 | 5652982
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 60 | 60 | 60 | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2273280
120 | Eastern Zone Total | 6729 | 6508 | 6425 | 6254 | 6119 | 5438.68 | 5079.49 | 5086.8 | 5216.8 | 5287 | 5114.5 | 5283.8 | 5271.1 | 5426 | 5598.2 | 5543.8 | 5187.8 | 4864.5 |  | 6213 | 6639 | 6730 | 6859 | 6919 | 6886 | 6838 | 141239766
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 115 | 115 | 115 | 115 | 115 | 115 | 83 | 49 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 62 | 115 | 115 | 115 | 115 | 115 | 115 | 1591680
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
| Khulna 225 MW CCPP | 40 | 15 | 10 | 15 | 70 | 100 | 120 | 130 | 120 | 120 | 120 | 80 | 30 |  |  | 30 | 35 | 85 |  | 120 | 120 | 120 | 145 | 150 | 150 | 150 | 1424772
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | [24 empty] | 0 | 73440
130
131
132
133
| Barisal 110 MW PP (Summit ) | 110 | 96 | 96 | 96 | 96 | 64 | 32 | 16 | [9 empty] | 16 |  | 16 | 32 | 32 | 32 | 32 | 64 | 64 | 892128
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 77 | 77 | 77 | 75 | 75 | 75 | 78 | 78 | 54 | 33 | 33 | 33 | 33 | 33 | 34 | 34 | 33 | 33 |  | 65 | 79 | 77 | 76 | 76 | 77 | 77 | 1419476
| Bhola 225 MW CCPP | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 87 | 88 | 88 | 82 | 76 | 76 | 88 | 88 | 88 | 87 |  | 88 | 88 | 88 | 88 | 88 | 88 | 89 | 2144306
140 | Bhola 33 MW PP (Venture) | 37 | 38 | 37 | 36 | 31 | 23 | 24 | 19 | 7 | 11 | 9 | 13 | 6 | 6 | 9 | 14 | 12 | 14 |  | 22 | 23 | 24 | 21 | 22 | 28 | 29 | 467723
141 | Noapara 100 MW PP (Bangla Trac) | 60 | 50 | 50 | 30 | 30 | [17 empty] | 16 | 40 | 45 | 70 | 479040
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 40 | 40 | 40 | [15 empty] | 33 | 33 | 40 | 40 | 40 | 40 | 421500
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 941 | 940 | 940 | 941 | 941 | 941 | 941 | 941 | 930 | 930 | 929 | 930 | 935 | 933 | 932 | 936 | 935 | 935 |  | 935 | 936 | 936 | 935 | 936 | 930 | 930 | 22444364
147 | Bheramara 410 MW CCPP | 360 | 370 | 340 | 345 | 345 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 285 | 285 | 285 |  | 370 | 345 | 340 | 350 | 350 | 400 | 345 | 8437824
148 | Payra 1320 MW | 429 | 440 | 526 | 530 | 520 | 480 | 450 | 422 | 350 | 348 | 347 | 348 | 329 | 305 | 315 | 300 | 300 | 300 |  | 342 | 422 | 488 | 529 | 526 | 527 | 556 | 10712300
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 150 | 150 | 150 | 150 | 150 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 150 | 150 | 150 | 3660900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 182 | 185 | 184 | 180 | 180 | 163 | 156 | 151 | 153 | 158 | 182 | 109 | 99 | 100 | 43 | 96 | 152 | 156 |  | 164 | 185 | 185 | 200 | 198 | 201 | 198 | 3999909
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 192 | 193 | 194 | 188 | 190 | 184 | 178 | 180 | 176 | 178 | 175 | 179 | 175 | 192 | 191 | 174 | 171 | 167 |  | 185 | 192 | 192 | 193 | 191 | 194 | 192 | 4878545
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 403 | 410 | 402 | 408 | 411 | 338 | 329 | 328 | 367 | 399 | 384 | 358 | 396 | 342 | 342 | 327 | 362 | 286 |  | 385 | 353 | 377 | 403 | 404 | 387 | 407 | 9091690
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 19 | 20 |  | 20 | 20 | 21 | 20 | 20 | 20 | 21 | 456720
163 | Bogura 20 MW PP (Energyprima) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 9 |  | 11 | 11 | 11 | 10 | 7 | 10 | 12 | 249624
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 175770
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [19 empty] | 24 | 27 | 27 | 26 | 26 | 26 | 26 | 139749
169 | Natore 52 MW PP (Rajlanka)
170 | Chapainawabganj 100 MW Peaking PP | 68 | 32 | 32 | 32 | 32 | [14 empty] | 50 | 99 | 99 | 99 | 99 | 99 | 99 | 748680
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 35 | [22 empty] | 0 | 118656
172 | Confidence Power Bogura Unit-1 113 MW | 109 | 109 | 109 | 109 | 109 | 109 | 70 | 70 | 70 | 70 | 70 | 70 | 35 | 35 | 60 | 35 | 35 | 35 |  | 70 | 90 | 100 | 109 | 109 | 109 | 109 | 1904928
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | [19 empty] | 3 | 3 | 3 | 3 | 3 | 0 | 0 | 12000
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 113 | 113 | 113 | 82 | [13 empty] | 29 | 107 | 107 | 112 | 113 | 112 | 113 | 1260480
177 | Sympa Solar Power 8MW | [5 empty] | 0.2 | 1.2 | 3.6 | 2.5 | 4.6 | 7.4 | 7.9 | 6.8 | 7.2 | 6.6 | 4.2 | 0.8 | 0.2 | [8 empty] | 55249
178
178