## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-08-09 | Sunday
|  | Date (day): | 2020-08-09 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13588.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14702 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-08-08 | 2020-08-09 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit-2 Under maint
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 100 | 100 | 110 | 110
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 270 | 300 | 300
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 13 | 0 | 0 | 0
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 342 | 351 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 89 | 93 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 140 | 120 | 150 | 150 | 155 |  | GT-1 S/D for gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 94 | 96 | 100 | 100 |  | 0 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 5 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 40 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 19 | 16 | 16 |  | 6 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 180 | 180 | 150 | 180 | 30 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 50 | 100 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 318 | 327 | 330 | 330
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 93 | 93 | 102 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel Shortage.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 53 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 149 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 47 | 50 | 47 | 47 |  | 33 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33 |  | 0 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 232 | 285 | 300 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 80 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 137 | 149 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 105 | 100 | 100
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
| Dhaka area Total |  |  |  |  | 6119 | 5895 | 2983 | 3530 | 3917 | 4217 | 449 | 806
38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19.3 | 0 | 20 | 0
41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50
42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 105 | 142 | 145 | 145 | 85 |  | Low water level
43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint.
44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 140 | 138 | 140 | 140
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 68 | 100 | 100
46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 2 | 6 | 8 | 0 |  | 98 | Under maint.
47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 100 | 100
48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 100 | 100 | 100
50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 21 | 21
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 6 | 29 | 20 | 30
51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 95 | 90 | 91 |  | 17 | Engine problem
52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5.2 | 0 | 5 | 0
53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 308 | 307 | 300 | 300
54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 54 | 50 | 54
55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| Chattogram area Total |  |  |  |  | 2326 | 2266 | 818.5 | 1234 | 1424 | 1466 | 445 | 340
57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 135 | 135 | 135 | 100 | 29 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 100 | 130 | 100 | 34 |  | Gas Shortage
58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 183 | 182 | 220 | 220
59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 260 | 360 | 360
60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 360 | 250
61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 31 | 35 | 40 | 42
62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 47 | 49 | 52 | 52 | 3 |  | Gas shortage
63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 83 | 0 | 0 | 0 | 195 |  | Gas shortage
64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 0 | 0 | 0
65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 0 | 150
66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 42
67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 81 | 90 | 90 |  | 73
68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 200 | 200 | 200
69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 20 | 22 | 22
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 136 | 164 | 157 | 173
71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 52 | 52 | 52
73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 18 | 18 | 18 |  | 7 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 114 | 114 | 114
76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 56 | 60 | 60
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1241 | 1507 | 2054 | 2289 | 396 | 80
77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 149 | 157 | 155 | 160 | 42 |  | Gas shortage
78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 14 | 17 | 17 | 17 |  | 5 | Engine problem
79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 72 | 72 | 95 | 95
80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1.4 | 0 | 1.6 | 0
81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 200 | 200 | 200 | 200
82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 8 | 115 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 444.4 | 561 | 583.6 | 587 | 42 | 5
83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 81 | 88 | 88 | 90
84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30
85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 209 | 210 | 210 | 210
87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 50 | 51 | 51
88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 48 | 48 | 44 | 44
89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 28 | 29 | 61 | 66
91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 85 | 86 | 86
92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 |  | 231 | Under maint.
93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25
96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 290 | 341 | 341
97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
| Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1034 | 1056 | 1138 | 1145 | 0 | 631
99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 923 | 922 | 920 | 920
100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 49 | 115 | 115 | 115
101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30
102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 120 | 130 | 225
103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 325 | 405 | 360 | 410
105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 70 | 60 | 100
107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 105 | 105 | 105
108 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Khulna Area Total |  |  |  |  | 2288 | 2284 | 1417 | 1777 | 1830 | 2121 | 0 | 0
109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 110 | 110
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 22 | 38 | 33 | 33
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 90 | 89 | 90 | 90 |  | 104 | GT-2 & ST Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 75 | 76 | 76 | 79 |  | 16 | Engine problem
113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 460 | 530 | 600 | 600
| Barisal Area Total |  |  |  |  | 1054 | 1054 | 647 | 843 | 909 | 912 | 0 | 120
114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 44 | 0 | 45
120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | S/D for ST Under maint.
121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 155 | 184 | 180 | 220
122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 190 | 186 | 200 | 220
123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 405 | 384 | 414 | 414
124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 33 | 0 | 35
125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 20 | 22 | 22
126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 8 | 11 | 10 | 10
127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 43 | 52 | 52
129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 98 | 100 | 100
130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 92 | 113 | 113
132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 109 | 109 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 896 | 1262 | 1462 | 1692 | 431 | 3
133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 140 | 150 | 150 | 124 |  | Coal Shortage.
135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 34 | 113 | 113 | 113
138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 0.8 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 184.8 | 253 | 271 | 273 | 294 | 30
| Total |  |  |  |  | 20383 | 19892 | 9665.7 | 12023 | 13588.6 | 14702 | 2057 | 2015
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9238.007 | 11491 | 12987.3245 | 14051.4582
A. |  | 2020-08-08 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 12023 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 8458 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12023 | MW
3 | Day peak Generation : |  |  | 9665.7 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11491 | MW
4 | Evening peak Generation : |  |  | 12023 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 246.7791 | MKWHr | By Solar | 0.18571 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 137.0033 | MKWHr |  | By Oil: | 64.9441 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 16.3075 | MKWHr |  | By Hydro: | 2.8927 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2057 | MW | Dhaka | 3581 | 3581 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2015 | MW | Chittagong | 1142 | 1142 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 4072 | MW | Khulna | 1558 | 1558 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1145.11 | MMCFD |  |  | Rajshahi | 1300 | 1300 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 161657008.468 | ii) Oil : | Taka | 508192487.44 | Comilla | 1199 | 1199 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 75339846 | Total | Taka | 745189341.908 | Mymensingh | 1008 | 1008 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.1245 | MKWHr. | Sylhet | 529 | 529 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -6 | MW (E to W) at | 21:00 | hrs | Barisal | 364 | 364 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -39 | MW at | 1:00 | hrs | Rangpur | 810 | 810 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 34.3° C |  |  | Total | 11491 | 11491 |  | 0
B. |  | 2020-08-09 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 33.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12400 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14702 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10200 | MW
4 | Reserve(Generation end) |  |  |  | 2302 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 254.5172 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9079.2 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.0502 | MKWHr. | ii) HVDC Flow at Peak Time |  | 922 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.3955 | MKWHr. | iii) Maximum HVDC Flow : |  | 923 | MW at | 9:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 94.39 |  | (b) Today: | 94.64 |  | (c) Rule Curve: |  | 91.56
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-08-08
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 0 | 60 | 300 | 98 | 0 | 0 | 336 |  | 0 | 450 | 130 | 100 | 97 | 0 | 326 | 0 | 145 | 0 | 100 | 40 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 25 | 26 | 33 | 31 | 0 | 0 | 74 | 65 | 0 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 18 | 42 | 0 | 135 | 100 | 300 | 0 | 208 | 92 | 85 | 41 | 49 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 32 | 20 | 136 | 156 | 72 | 14 | 0 | 88 | 30 | 53 | 48 | 163 | 208 | 29 | 85 | 0 | 0 | 18 | 0 | 10 | 285 | 24 | 11 | 0 | 245 | 0 | 0 | 192 | 0 | 149 | 0 | 100 | 18 | 50 | 0 | 115 | 0 | 0 | 0 | 307 | 0 | 0 | 43 | 56 | 100 | 0 | 104 |  | 912 | 0 | 310 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 89 | 37 | 16 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 43 | 52 | 31 | 20 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 196 | 0 | 77 | 60 | 195 | 0 | 391 | 53 | 0 | 111 | 0 | 113 | 0 | 0 | 109 | 556 |  | 6896 | 3908 | 10804 | 3477 | 912 | 2298 | 2768 | 705 | 139 | 369 | 136 | 0 | 0 | 94.34
2:00 | 35 | 0 | 0 | 70 | 300 | 97 | 0 | 0 | 336 |  | 0 | 450 | 135 | 75 | 97 | 0 | 327 | 0 | 145 | 0 | 60 | 40 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 25 | 22 | 33 | 31 | 0 | 0 | 75 | 65 | 0 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 18 | 42 | 0 | 135 | 100 | 300 | 0 | 205 | 92 | 90 | 41 | 48 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 32 | 20 | 138 | 157 | 71 | 14 | 0 | 88 | 30 | 53 | 48 | 163 | 210 | 29 | 85 | 0 | 0 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 145 | 0 | 0 | 192 | 0 | 149 | 0 | 100 | 17 | 50 | 0 | 115 | 0 | 0 | 0 | 307 | 0 | 0 | 17 | 56 | 100 | 0 | 104 |  | 912 | 0 | 310 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 89 | 37 | 16 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 43 | 43 | 15 | 20 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 190 | 0 | 77 | 10 | 194 | 0 | 399 | 0 | 0 | 111 | 0 | 113 | 0 | 0 | 109 | 557 |  | 6687 | 3785 | 10472 | 3486 | 912 | 2299 | 2468 | 706 | 140 | 323 | 138 | 0 | 0 | 94.35
3:00 | 35 | 0 | 0 | 90 | 300 | 97 | 0 | 0 | 336 |  | 0 | 450 | 140 | 50 | 97 | 0 | 325 | 0 | 145 | 0 | 50 | 40 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 25 | 22 | 25 | 31 | 0 | 0 | 75 | 65 | 0 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 42 | 0 | 135 | 100 | 300 | 0 | 203 | 92 | 90 | 41 | 48 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 32 | 20 | 134 | 157 | 71 | 14 | 0 | 88 | 30 | 53 | 48 | 163 | 209 | 29 | 85 | 0 | 0 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 95 | 0 | 0 | 192 | 0 | 149 | 0 | 90 | 17 | 10 | 0 | 115 | 0 | 0 | 0 | 307 | 0 | 0 | 17 | 56 | 100 | 0 | 104 |  | 912 | 0 | 330 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 89 | 37 | 16 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 24 | 0 | 20 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 191 | 0 | 75 | 0 | 192 | 0 | 406 | 0 | 0 | 111 | 0 | 113 | 0 | 0 | 109 | 558 |  | 6521 | 3723 | 10244 | 3508 | 912 | 2314 | 2280 | 707 | 140 | 249 | 134 | 0 | 0 | 94.36
4:00 | 35 | 0 | 0 | 90 | 300 | 98 | 40 | 0 | 352 |  | 0 | 450 | 130 | 50 | 64 | 0 | 328 | 0 | 175 | 0 | 50 | 7 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 25 | 22 | 25 | 31 | 0 | 0 | 74 | 65 | 0 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 42 | 0 | 135 | 100 | 300 | 0 | 197 | 92 | 90 | 41 | 48 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 32 | 20 | 134 | 157 | 71 | 14 | 0 | 88 | 30 | 53 | 48 | 163 | 210 | 29 | 85 | 0 | 0 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 95 | 0 | 0 | 192 | 0 | 105 | 0 | 100 | 17 | 10 | 0 | 115 | 0 | 0 | 0 | 307 | 0 | 0 | 17 | 56 | 100 | 0 | 54 |  | 912 | 0 | 330 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 89 | 36 | 16 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 8 | 0 | 20 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 195 | 0 | 75 | 0 | 194 | 0 | 386 | 0 | 0 | 70 | 0 | 113 | 0 | 0 | 109 | 558 |  | 6456 | 3651 | 10107 | 3543 | 912 | 2360 | 2063 | 707 | 139 | 249 | 134 | 0 | 0 | 94.37
5:00 | 35 | 0 | 0 | 100 | 300 | 98 | 71 | 0 | 350 |  | 0 | 450 | 140 | 50 | 64 | 0 | 326 | 0 | 175 | 0 | 20 | 7 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 25 | 22 | 25 | 31 | 0 | 0 | 72 | 65 | 0 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 42 | 0 | 135 | 100 | 300 | 0 | 190 | 92 | 91 | 38 | 49 | 0 | 51 | 0 | 0 | 52 | 18 | 8 | 32 | 18 | 132 | 156 | 71 | 14 | 0 | 88 | 30 | 50 | 48 | 163 | 211 | 29 | 85 | 0 | 0 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 45 | 0 | 0 | 192 | 0 | 101 | 0 | 90 | 17 | 0 | 0 | 115 | 0 | 0 | 0 | 307 | 0 | 0 | 50 | 0 | 100 | 0 | 54 |  | 911 | 0 | 330 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 89 | 36 | 16 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 188 | 0 | 75 | 0 | 194 | 0 | 413 | 0 | 0 | 35 | 0 | 113 | 0 | 0 | 109 | 540 |  | 6345 | 3609 | 9954 | 3529 | 911 | 2404 | 1903 | 689 | 137 | 249 | 132 | 0 | 0 | 94.38
6:00 | 35 | 0 | 0 | 100 | 300 | 98 | 72 | 0 | 350 |  | 0 | 400 | 140 | 25 | 62 | 0 | 280 | 0 | 115 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 25 | 20 | 25 | 14 | 0 | 0 | 74 | 65 | 0 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 42 | 0 | 135 | 80 | 300 | 0 | 213 | 55 | 91 | 38 | 50 | 0 | 51 | 0 | 0 | 52 | 18 | 8 | 32 | 18 | 118 | 157 | 71 | 14 | 0.1 | 88 | 30 | 50 | 49 | 163 | 208 | 29 | 85 | 0 | 0 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 30 | 0 | 0 | 192 | 0 | 86 | 0.8 | 100 | 0 | 0 | 0 | 40 | 0 | 0 | 0.1 | 254 | 0 | 0 | 22 | 0 | 100 | 0 | 20 |  | 911 | 0 | 340 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 187 | 0 | 75 | 0 | 192 | 0 | 412 | 0 | 0 | 0 | 0 | 96 | 0 | 0.1 | 50 | 500 |  | 5820 | 3329.1 | 9149.1 | 3412 | 911 | 2313 | 1462 | 649 | 139 | 144 | 118 | 1.1 | 0 | 94.39
7:00 | 35 | 0 | 0 | 100 | 300 | 98 | 71 | 0 | 309 |  | 0 | 400 | 145 | 7 | 48 | 0 | 280 | 0 | 115 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 25 | 20 | 25 | 14 | 0 | 0 | 74 | 65 | 0 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 33 | 0 | 135 | 80 | 300 | 0 | 213 | 55 | 91 | 31 | 49 | 0 | 51 | 0 | 0 | 52 | 18 | 8 | 32 | 15 | 126 | 156 | 8 | 14 | 0.3 | 88 | 30 | 50 | 49 | 163 | 212 | 29 | 85 | 0 | 0 | 18 | 0 | 10 | 285 | 24 | 11 | 0 | 30 | 0 | 0 | 200 | 0 | 51 | 4.4 | 90 | 0 | 0 | 0 | 8 | 0 | 0 | 1.5 | 161 | 0 | 0 | 17 | 0 | 70 | 0 | 18 |  | 911 | 0 | 350 | 0 | 83 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 178 | 0 | 62 | 0 | 174 | 0 | 386 | 0 | 0 | 0 | 0 | 37 | 0 | 0.8 | 35 | 476 |  | 5480.2 | 3138.8 | 8619 | 3388 | 911 | 2212 | 1067 | 625 | 139 | 144 | 126 | 7 | 0 | 94.4
8:00 | 35 | 0 | 0 | 100 | 300 | 98 | 70 | 0 | 309 |  | 0 | 400 | 145 | 7 | 48 | 0 | 280 | 0 | 145 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 25 | 20 | 25 | 26 | 0 | 0 | 36 | 65 | 0 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 3 | 0 | 135 | 80 | 295 | 0 | 213 | 55 | 91 | 31 | 49 | 0 | 51 | 0 | 0 | 52 | 18 | 8 | 32 | 15 | 124 | 155 | 8 | 14 | 0.6 | 88 | 30 | 50 | 49 | 163 | 212 | 28 | 83 | 0 | 0 | 18 | 0 | 10 | 295 | 24 | 11 | 0 | 30 | 0 | 0 | 200 | 0 | 50 | 0 | 100 | 0 | 0 | 0 | 8 | 0 | 0 | 2.4 | 125 | 0 | 0 | 17 | 0 | 70 | 0 | 18 |  | 912 | 0 | 350 | 0 | 49 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 155 | 0 | 62 | 0 | 171 | 0 | 396 | 0 | 0 | 0 | 0 | 34 | 0 | 3 | 35 | 450 |  | 5428 | 3030 | 8458 | 3403 | 912 | 2189 | 1003 | 600 | 101 | 120 | 124 | 6 | 0 | 94.41
9:00 | 35 | 0 | 0 | 100 | 300 | 95 | 71 | 0 | 308 |  | 0 | 420 | 120 | 20 | 48 | 0 | 300 | 0 | 185 | 0 | 2 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 25 | 20 | 25 | 26 | 0 | 0 | 36 | 65 | 0 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 3 | 0 | 135 | 80 | 260 | 0 | 213 | 55 | 87 | 31 | 48 | 0 | 51 | 0 | 0 | 52 | 18 | 8 | 32 | 18 | 124 | 154 | 48 | 14 | 0.6 | 81 | 30 | 50 | 49 | 130 | 212 | 29 | 83 | 0 | 0 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 55 | 0 | 0 | 200 | 0 | 82 | 10.4 | 90 | 0 | 0 | 0 | 8 | 0 | 0 | 3.7 | 271 | 0 | 0 | 17 | 0 | 100 | 0 | 90 |  | 923 | 0 | 345 | 0 | 49 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 182 | 0 | 77 | 0 | 186 | 0 | 332 | 0 | 0 | 0 | 0 | 34 | 0 | 3.4 | 100 | 438 |  | 5786.7 | 3085.4 | 8872.1 | 3452 | 923 | 2120 | 1426 | 588 | 101 | 120 | 124 | 18.1 | 0 | 94.42
10:00 | 35 | 0 | 0 | 100 | 300 | 94 | 70 | 0 | 309 |  | 0 | 420 | 130 | 50 | 85 | 0 | 300 | 0 | 185 | 0 | 7 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 16 | 25 | 20 | 25 | 26 | 0 | 0 | 37 | 65 | 0 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 4 | 0 | 135 | 80 | 280 | 0 | 210 | 55 | 90 | 31 | 48 | 0 | 51 | 0 | 0 | 52 | 18 | 8 | 25 | 18 | 130 | 151 | 48 | 14 | 1.2 | 82 | 30 | 50 | 49 | 130 | 210 | 28 | 85 | 0 | 0 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 143 | 0 | 0 | 200 | 0 | 149 | 17 | 100 | 0 | 0 | 0 | 8 | 0 | 0 | 4.2 | 269 | 0 | 0 | 17 | 0 | 100 | 0 | 104 |  | 923 | 0 | 344 | 0 | 49 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 170 | 0 | 77 | 0 | 191 | 0 | 364 | 0 | 0 | 0 | 0 | 36 | 0 | 4.2 | 109 | 440 |  | 6111.4 | 3124.2 | 9235.6 | 3456 | 923 | 2165 | 1723 | 590 | 102 | 120 | 130 | 26.6 | 0 | 94.43
11:00 | 35 | 0 | 20 | 100 | 300 | 89 | 40 | 0 | 341 |  | 0 | 420 | 135 | 54 | 95 | 0 | 320 | 0 | 175 | 0 | 8 | 74 | 0 | 0 | 0 | 0 | 0 | 10 | 17 | 0 | 0 | 25 | 22 | 25 | 33 | 0 | 0 | 37 | 65 | 0 | 0 | 5 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 2 | 0 | 135 | 80 | 260 | 0 | 184 | 85 | 90 | 31 | 48 | 0 | 51 | 0 | 0 | 52 | 18 | 5 | 25 | 18 | 130 | 150 | 48 | 14 | 0.7 | 80 | 30 | 47 | 49 | 163 | 209 | 28 | 85 | 0 | 0 | 18 | 0 | 10 | 310 | 24 | 11 | 0 | 153 | 0 | 0 | 190 | 0 | 149 | 19.3 | 90 | 0 | 0 | 0 | 8 | 0 | 0 | 3.2 | 305 | 0 | 0 | 17 | 0 | 100 | 0 | 104 |  | 923 | 0 | 330 | 0 | 49 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 7 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 171 | 0 | 75 | 0 | 192 | 0 | 401 | 0 | 0 | 0 | 0 | 35 | 0 | 4.9 | 109 | 450 |  | 6231.2 | 3157.9 | 9389.1 | 3413 | 923 | 2266 | 1807 | 600 | 102 | 120 | 130 | 28.1 | 0 | 94.44
12:00 | 35 | 0 | 100 | 100 | 300 | 13 | 40 | 0 | 342 |  | 0 | 420 | 140 | 89 | 94 | 5 | 318 | 0 | 180 | 0 | 50 | 93 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 16 | 25 | 22 | 25 | 33 | 0 | 0 | 40 | 65 | 0 | 0 | 25 | 0 | 0 | 140 | 0 |  | 0 | 2 | 0 | 0 | 0 | 0 | 18 | 6 | 0 | 135 | 80 | 270 | 0 | 183 | 83 | 90 | 31 | 47 | 0 | 51 | 0 | 0 | 52 | 18 | 5 | 25 | 18 | 136 | 149 | 72 | 14 | 1.4 | 81 | 30 | 47 | 48 | 163 | 209 | 28 | 85 | 0 | 0 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 232 | 0 | 0 | 200 | 0 | 137 | 19.3 | 90 | 0 | 0 | 0 | 8 | 0 | 0 | 5.2 | 308 | 0 | 0 | 17 | 0 | 100 | 0 | 104 |  | 923 | 0 | 325 | 0 | 49 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 155 | 0 | 75 | 0 | 190 | 0 | 405 | 0 | 0 | 0 | 0 | 34 | 0 | 0.8 | 109 | 460 |  | 6520.9 | 3144.8 | 9665.7 | 3499 | 923 | 2166 | 2078 | 610 | 105 | 122 | 136 | 26.7 | 0 | 94.45
13:00 | 35 | 0 | 200 | 100 | 300 | 0 | 0 | 0 | 342 |  | 0 | 420 | 145 | 95 | 94 | 15 | 316 | 0 | 180 | 0 | 60 | 93 | 0 | 0 | 0 | 0 | 0 | 53 | 35 | 4 | 16 | 25 | 22 | 25 | 33 | 0 | 0 | 40 | 65 | 0 | 0 | 25 | 0 | 0 | 139 | 0 |  | 0 | 4 | 0 | 0 | 0 | 0 | 18 | 6 | 0 | 135 | 80 | 310 | 0 | 197 | 83 | 90 | 33 | 47 | 0 | 51 | 0 | 0 | 52 | 20 | 3 | 25 | 18 | 140 | 149 | 80 | 14 | 0.9 | 82 | 30 | 44 | 48 | 163 | 208 | 28 | 87 | 0 | 0 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 263 | 0 | 0 | 200 | 0 | 148 | 11 | 90 | 0 | 1 | 0 | 16 | 17 | 0 | 4.2 | 306 | 0 | 0 | 8 | 0 | 100 | 0 | 104 |  | 923 | 0 | 310 | 0 | 54 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 192 | 0 | 76 | 0 | 196 | 0 | 396 | 0 | 0 | 0 | 0 | 34 | 0 | 2.8 | 109 | 460 |  | 6744.1 | 3173.8 | 9917.9 | 3680 | 923 | 2116 | 2201 | 610 | 105 | 124 | 140 | 18.9 | 0 | 94.46
14:00 | 35 | 0 | 160 | 100 | 300 | 0 | 0 | 0 | 343 |  | 0 | 400 | 140 | 100 | 94 | 32 | 316 | 0 | 180 | 0 | 90 | 93 | 0 | 2 | 0 | 0 | 0 | 53 | 55 | 35 | 16 | 25 | 20 | 25 | 33 | 0 | 0 | 40 | 65 | 0 | 0 | 0 | 0 | 0 | 141 | 0 |  | 0 | 6 | 0 | 0 | 12 | 0 | 18 | 3 | 0 | 135 | 80 | 290 | 0 | 182 | 83 | 90 | 38 | 47 | 0 | 51 | 0 | 0 | 52 | 20 | 8 | 25 | 20 | 144 | 118 | 88 | 17 | 1.3 | 82 | 30 | 44 | 48 | 163 | 213 | 28 | 85 | 0 | 0 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 273 | 0 | 0 | 200 | 0 | 149 | 6.48 | 90 | 0 | 25 | 0 | 50 | 17 | 0 | 1.9 | 307 | 1 | 0 | 0 | 0 | 100 | 0 | 104 |  | 922 | 0 | 295 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 175 | 0 | 77 | 0 | 184 | 0 | 339 | 0 | 0 | 0 | 0 | 35 | 0 | 1.4 | 109 | 470 |  | 6801.68 | 3126.4 | 9928.08 | 3548 | 922 | 2047 | 2405 | 620 | 105 | 126 | 144 | 11.08 | 0 | 94.48
15:00 | 35 | 0 | 100 | 100 | 285 | 0 | 0 | 0 | 345 |  | 0 | 400 | 140 | 100 | 94 | 40 | 320 | 0 | 180 | 0 | 100 | 93 | 0 | 20 | 0 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 20 | 25 | 33 | 0 | 0 | 40 | 65 | 0 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 8 | 0 | 0 | 0 | 0 | 18 | 2 | 0 | 135 | 80 | 290 | 0 | 184 | 83 | 90 | 38 | 45 | 0 | 51 | 0 | 0 | 52 | 20 | 8 | 29 | 20 | 150 | 116 | 88 | 17 | 2.3 | 82 | 30 | 44 | 48 | 163 | 211 | 28 | 85 | 0 | 0 | 18 | 0 | 10 | 295 | 24 | 11 | 0 | 286 | 0 | 0 | 190 | 0 | 149 | 6.71 | 90 | 0 | 71 | 0 | 85 | 52 | 0 | 3.2 | 307 | 17 | 0 | 35 | 0 | 100 | 0 | 104 |  | 923 | 0 | 310 | 0 | 103 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 163 | 0 | 75 | 0 | 181 | 0 | 391 | 0 | 0 | 0 | 0 | 97 | 0 | 0.6 | 109 | 470 |  | 6953.21 | 3246.6 | 10199.81 | 3482 | 923 | 2095 | 2685 | 619 | 105 | 128 | 150 | 12.81 | 0 | 94.5
16:00 | 35 | 0 | 100 | 100 | 240 | 0 | 0 | 0 | 345 |  | 0 | 400 | 130 | 100 | 94 | 55 | 320 | 0 | 180 | 0 | 100 | 93 | 0 | 20 | 0 | 0 | 0 | 53 | 55 | 35 | 19 | 25 | 20 | 33 | 33 | 0 | 0 | 40 | 65 | 0 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 8 | 0 | 0 | 0 | 0 | 16 | 2 | 0 | 135 | 80 | 290 | 0 | 182 | 83 | 82 | 35 | 46 | 0 | 51 | 0 | 0 | 52 | 20 | 8 | 30 | 20 | 146 | 121 | 88 | 17 | 0.6 | 82 | 30 | 49 | 48 | 163 | 210 | 28 | 85 | 0 | 0 | 18 | 0 | 10 | 290 | 24 | 5 | 0 | 286 | 0 | 0 | 190 | 0 | 149 | 8 | 100 | 0 | 70 | 0 | 85 | 35 | 0 | 0.5 | 305 | 17 | 0 | 35 | 0 | 100 | 0 | 104 |  | 923 | 0 | 320 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 153 | 0 | 79 | 0 | 178 | 0 | 393 | 0 | 0 | 0 | 0 | 113 | 0 | 0.5 | 90 | 470 |  | 6868.1 | 3279.5 | 10147.6 | 3426 | 923 | 2100 | 2669 | 620 | 105 | 149 | 146 | 9.6 | 0 | 94.52
17:00 | 35 | 0 | 100 | 100 | 240 | 0 | 0 | 0 | 345 |  | 0 | 400 | 120 | 75 | 94 | 30 | 320 | 0 | 175 | 0 | 70 | 48 | 0 | 20 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 25 | 20 | 33 | 33 | 0 | 0 | 40 | 65 | 0 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 8 | 0 | 0 | 0 | 0 | 18 | 19 | 0 | 135 | 80 | 290 | 0 | 182 | 83 | 80 | 35 | 47 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 32 | 20 | 140 | 138 | 48 | 14 | 1 | 82 | 30 | 50 | 48 | 163 | 211 | 29 | 85 | 0 | 0 | 18 | 0 | 10 | 280 | 24 | 0 | 0 | 220 | 0 | 0 | 200 | 0 | 149 | 6.24 | 100 | 0 | 40 | 0 | 16 | 17 | 0 | 0.2 | 305 | 0 | 0 | 0 | 0 | 90 | 0 | 104 |  | 923 | 0 | 330 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 155 | 0 | 80 | 0 | 173 | 0 | 384 | 0 | 0 | 0 | 0 | 77 | 0 | 0.8 | 70 | 470 |  | 6430.44 | 3239.8 | 9670.24 | 3441 | 923 | 2099 | 2165 | 620 | 105 | 169 | 140 | 8.24 | 0 | 94.54
18:00 | 35 | 0 | 100 | 100 | 240 | 0 | 0 | 0 | 305 |  | 0 | 370 | 135 | 55 | 94 | 30 | 280 | 0 | 120 | 0 | 50 | 48 | 0 | 20 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 25 | 20 | 33 | 33 | 0 | 0 | 40 | 65 | 0 | 0 | 0 | 0 | 0 | 103 | 0 |  | 0 | 8 | 0 | 0 | 0 | 0 | 18 | 20 | 0 | 135 | 80 | 290 | 0 | 182 | 83 | 88 | 35 | 20 | 0 | 51 | 0 | 0 | 43 | 21 | 8 | 32 | 16 | 128 | 139 | 48 | 17 | 0.1 | 82 | 30 | 25 | 20 | 110 | 208 | 28 | 40 | 0 | 0 | 18 | 0 | 10 | 270 | 24 | 2 | 0 | 165 | 0 | 0 | 200 | 0 | 134 | 0.7 | 100 | 0 | 40 | 0 | 16 | 17 | 0 | 0 | 252 | 0 | 0 | 0 | 0 | 70 | 0 | 72 |  | 923 | 0 | 350 | 0 | 68 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 156 | 0 | 44 | 0 | 173 | 0 | 380 | 0 | 0 | 0 | 0 | 40 | 0 | 0.1 | 35 | 470 |  | 5820.8 | 3101.1 | 8921.9 | 3337 | 923 | 1802 | 1837 | 620 | 105 | 169 | 128 | 0.9 | 0 | 94.55
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 0 | 100 | 100 | 240 | 0 | 0 | 0 | 341 |  | 0 | 450 | 120 | 75 | 84 | 34 | 321 | 0 | 175 | 0 | 65 | 84 | 65 | 30 | 0 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 12 | 33 | 33 | 11 | 0 | 40 | 65 | 0 | 0 | 0 | 0 | 0 | 141 | 0 |  | 0 | 8 | 102 | 0 | 0 | 7 | 18 | 25 | 0 | 135 | 80 | 320 | 0 | 194 | 130 | 90 | 35 | 20 | 0 | 51 | 0 | 38 | 34 | 21 | 8 | 32 | 18 | 160 | 135 | 64 | 17 | 0 | 82 | 30 | 37 | 35 | 163 | 207 | 28 | 85 | 0 | 0 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 188 | 196 | 0 | 200 | 13 | 142 | 0 | 100 | 3 | 48 | 0 | 18 | 70 | 4 | 0 | 307 | 25 | 0 | 50 | 16 | 70 | 0 | 104 |  | 923 | 0 | 370 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 8 | 89 | 24 | 48 | 0 | 0 | 0 | 22 | 5 | 97 | 0 | 0 | 25 | 19 | 20 | 20 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 168 | 0 | 81 | 7 | 185 | 0 | 388 | 24 | 0 | 23 | 0 | 60 | 0 | 0 | 90 | 475 |  | 7187 | 3575 | 10762 | 3557 | 923 | 2171 | 2719 | 625 | 105 | 502 | 160 | 0 | 0 | 94.56
19:30 | 35 | 0 | 100 | 100 | 240 | 0 | 0 | 0 | 352 |  | 0 | 450 | 130 | 93 | 78 | 55 | 322 | 0 | 135 | 0 | 100 | 93 | 149 | 40 | 0 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 24 | 33 | 33 | 42 | 0 | 40 | 65 | 0 | 0 | 2 | 0 | 0 | 139 | 0 |  | 0 | 6 | 102 | 10 | 26 | 30 | 18 | 14 | 0 | 135 | 80 | 310 | 0 | 181 | 130 | 80 | 38 | 20 | 0 | 51 | 0 | 42 | 52 | 21 | 8 | 32 | 18 | 158 | 141 | 64 | 17 | 0 | 89 | 30 | 50 | 48 | 163 | 214 | 28 | 85 | 0 | 0 | 18 | 0 | 10 | 260 | 24 | 11 | 0 | 285 | 53 | 0 | 200 | 51 | 149 | 0 | 90 | 34 | 120 | 0 | 115 | 105 | 40 | 0 | 307 | 54 | 0 | 114 | 57 | 100 | 0 | 104 |  | 923 | 0 | 312 | 0 | 115 | 135 | 0 | 0 | 0 | 0 | 40 | 84 | 35 | 110 | 0 | 0 | 0 | 50 | 5 | 98 | 0 | 0 | 42 | 44 | 30 | 17 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 176 | 0 | 77 | 90 | 182 | 0 | 371 | 105 | 0 | 70 | 0 | 107 | 0 | 0 | 109 | 500 |  | 7849 | 3996 | 11845 | 3460 | 923 | 2144 | 3746 | 650 | 105 | 659 | 158 | 0 | 0 | 0
20:00 | 35 | 0 | 100 | 100 | 240 | 0 | 0 | 0 | 351 |  | 0 | 450 | 140 | 93 | 78 | 55 | 315 | 0 | 95 | 0 | 100 | 93 | 149 | 40 | 0 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 25 | 33 | 33 | 42 | 0 | 77 | 65 | 0 | 0 | 18 | 0 | 0 | 139 | 0 |  | 0 | 6 | 102 | 10 | 25 | 37 | 18 | 19 | 0 | 135 | 80 | 260 | 0 | 181 | 157 | 87 | 38 | 40 | 0 | 51 | 0 | 42 | 52 | 21 | 8 | 32 | 18 | 166 | 141 | 72 | 17 | 0 | 88 | 30 | 50 | 48 | 130 | 210 | 29 | 85 | 0 | 0 | 18 | 0 | 10 | 270 | 24 | 11 | 0 | 285 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 125 | 103 | 0 | 103 | 102 | 45 | 0 | 307 | 54 | 0 | 114 | 56 | 100 | 0 | 104 |  | 921 | 0 | 310 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 89 | 36 | 110 | 0 | 0 | 0 | 50 | 13 | 98 | 0 | 0 | 47 | 44 | 33 | 20 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 164 | 0 | 78 | 80 | 175 | 0 | 310 | 105 | 0 | 90 | 0 | 104 | 0 | 0 | 109 | 510 |  | 7838 | 3940 | 11778 | 3351 | 921 | 2116 | 3762 | 660 | 142 | 660 | 166 | 0 | 0 | 94.57
21:00 | 35 | 0 | 100 | 100 | 270 | 0 | 0 | 0 | 351 |  | 0 | 450 | 120 | 93 | 96 | 55 | 327 | 0 | 180 | 0 | 100 | 93 | 149 | 40 | 0 | 0 | 0 | 53 | 55 | 35 | 19 | 25 | 25 | 33 | 33 | 50 | 0 | 77 | 65 | 0 | 0 | 25 | 0 | 0 | 138 | 0 |  | 0 | 6 | 102 | 0 | 95 | 50 | 18 | 29 | 0 | 135 | 100 | 260 | 0 | 182 | 0 | 81 | 35 | 49 | 0 | 0 | 0 | 0 | 52 | 20 | 8 | 33 | 18 | 164 | 157 | 72 | 17 | 0 | 88 | 30 | 50 | 48 | 163 | 210 | 29 | 85 | 0 | 0 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 285 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 200 | 0 | 0 | 115 | 105 | 68 | 0 | 307 | 54 | 0 | 114 | 56 | 100 | 0 | 104 |  | 922 | 0 | 405 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 89 | 38 | 110 | 0 | 0 | 0 | 50 | 0 | 98 | 0 | 0 | 44 | 43 | 33 | 20 | 11 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 184 | 0 | 76 | 70 | 186 | 0 | 384 | 105 | 0 | 92 | 0 | 113 | 0 | 0 | 109 | 530 |  | 7888 | 4135 | 12023 | 3631 | 922 | 2054 | 3838 | 670 | 142 | 602 | 164 | 0 | 0 | 94.58
22:00 | 35 | 0 | 100 | 100 | 270 | 0 | 0 | 0 | 351 |  | 0 | 450 | 125 | 100 | 96 | 55 | 329 | 0 | 180 | 0 | 100 | 93 | 149 | 40 | 0 | 0 | 0 | 53 | 55 | 35 | 19 | 25 | 28 | 33 | 33 | 32 | 0 | 77 | 65 | 0 | 0 | 25 | 0 | 0 | 138 | 0 |  | 0 | 8 | 85 | 0 | 98 | 26 | 18 | 32 | 0 | 135 | 130 | 260 | 0 | 181 | 0 | 88 | 35 | 51 | 0 | 0 | 0 | 0 | 52 | 20 | 11 | 33 | 18 | 170 | 156 | 71 | 17 | 0 | 88 | 30 | 50 | 48 | 163 | 209 | 29 | 87 | 0 | 0 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 285 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 140 | 0 | 0 | 115 | 105 | 17 | 0 | 307 | 54 | 0 | 114 | 56 | 100 | 0 | 104 |  | 922 | 0 | 400 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 89 | 39 | 110 | 0 | 0 | 0 | 50 | 0 | 98 | 0 | 0 | 44 | 43 | 30 | 20 | 11 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 187 | 0 | 78 | 70 | 182 | 0 | 399 | 105 | 0 | 92 | 0 | 113 | 0 | 0 | 109 | 530 |  | 7779 | 4144 | 11923 | 3667 | 922 | 2069 | 3699 | 670 | 142 | 584 | 170 | 0 | 0 | 94.59
23:00 | 35 | 0 | 100 | 100 | 270 | 0 | 0 | 0 | 351 |  | 0 | 450 | 140 | 100 | 96 | 55 | 324 | 0 | 180 | 0 | 100 | 93 | 149 | 0 | 0 | 0 | 0 | 53 | 55 | 17 | 19 | 25 | 28 | 33 | 30 | 0 | 0 | 82 | 65 | 0 | 0 | 25 | 0 | 0 | 139 | 0 |  | 0 | 8 | 85 | 0 | 97 | 19 | 18 | 34 | 0 | 135 | 130 | 280 | 0 | 201 | 0 | 91 | 35 | 50 | 0 | 0 | 0 | 0 | 52 | 20 | 11 | 33 | 18 | 170 | 153 | 71 | 17 | 0 | 87 | 30 | 50 | 48 | 163 | 211 | 28 | 88 | 0 | 0 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 285 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 80 | 0 | 0 | 115 | 105 | 17 | 0 | 307 | 54 | 0 | 114 | 57 | 100 | 0 | 104 |  | 922 | 0 | 400 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 89 | 39 | 110 | 0 | 0 | 0 | 50 | 0 | 97 | 0 | 0 | 44 | 52 | 32 | 20 | 11 | 8 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 186 | 0 | 77 | 70 | 185 | 0 | 406 | 105 | 0 | 92 | 0 | 113 | 0 | 0 | 109 | 532 |  | 7687 | 4163 | 11850 | 3702 | 922 | 2087 | 3566 | 671 | 147 | 585 | 170 | 0 | 0 | 94.6
24:00 | 35 | 0 | 100 | 100 | 270 | 0 | 0 | 0 | 351 |  | 0 | 450 | 140 | 100 | 97 | 55 | 326 | 0 | 185 | 0 | 100 | 93 | 133 | 0 | 0 | 0 | 0 | 53 | 55 | 17 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 84 | 65 | 0 | 0 | 25 | 0 | 0 | 140 | 0 |  | 0 | 8 | 51 | 0 | 97 | 19 | 18 | 36 | 0 | 135 | 130 | 260 | 0 | 189 | 0 | 91 | 32 | 52 | 0 | 0 | 0 | 0 | 52 | 20 | 11 | 33 | 18 | 166 | 155 | 72 | 17 | 0 | 87 | 30 | 50 | 48 | 163 | 209 | 29 | 88 | 0 | 0 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 285 | 0 | 0 | 192 | 0 | 149 | 0 | 100 | 70 | 0 | 0 | 115 | 17 | 17 | 0 | 307 | 54 | 0 | 114 | 56 | 100 | 0 | 104 |  | 922 | 0 | 400 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 89 | 38 | 110 | 0 | 0 | 0 | 50 | 0 | 97 | 0 | 0 | 44 | 52 | 31 | 20 | 11 | 8 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 196 | 0 | 77 | 70 | 181 | 0 | 409 | 105 | 0 | 92 | 0 | 113 | 0 | 0 | 109 | 532 |  | 7521 | 4174 | 11695 | 3685 | 922 | 2103 | 3461 | 675 | 149 | 534 | 166 | 0 | 0 | 94.61
KWH | 738000 | 0 | 1479000 | 2441250 | 6726800 | 1117590 | 766752 | 0 | 8048000 |  | 0 | 9592750 | 3235055 | 1737600 | 2036208 | 534528 | 7438412 | 0 | 4230000 | 0 | 1460160 | 1439280 | 1021440 | 283548 | 0 | 0 | 0 | 681480 | 623923 | 466897 | 345564 | 600000 | 519840 | 700300 | 770800 | 153432 | 0 | 1324702 | 1568000 | 0 | 0 | 181161 | 0 | 0 | 3364032 | 0 |  | 0 | 86200 | 497340 | 9720 | 487680 | 161760 | 435648 | 564000 | 0 | 3196085 | 2163888 | 7298600 | 0 | 4705000 | 1656000 | 2054580 | 756576 | 1116960 | 0 | 1043883 | 0 | 54768 | 1234205 | 465516 | 186120 | 729400 | 440320 | 3395520 | 3443040 | 1531200 | 329796 | 9600 | 2023000 | 712920 | 1141200 | 1135584 | 3742936 | 4871000 | 692448 | 1963200 | 0 | 0 | 416000 | 0 | 246780 | 7175000 | 550848 | 237024 | 0 | 4589125 | 101222 | 0 | 4627200 | 25861 | 3157920 | 120555 | 2305920 | 764640 | 677465 | 0 | 1632000 | 709128 | 194871 | 31189 | 6844800 | 348732 | 0 | 1036260 | 568680 | 2284800 | 0 | 2144640 |  | 22050182 | 0 | 8395200 | 0 | 2248320 | 2998676 | 0 | 0 | 0 | 0 | 422250 | 2153959 | 697440 | 672960 | 0 | 0 | 0 | 259408 | 12778 | 1208184 | 0 | 0 | 298510 | 384960 | 222795 | 469680 | 244908 | 193284 | 0 | 0 | 3640700 | 0 | 0 | 0 | 0 | 4470355 | 0 | 1769495 | 544320 | 4906500 | 0 | 9330054 | 614880 | 0 | 963552 | 0 | 1911360 | 0 | 24370 | 2250336 | 12666800 |  | 160752857 | 86026216 | 246779073 | 85181105 | 22050182 | 51822212 | 58284039 | 16307500 | 2892702 | 6660099 | 3395520 | 185714 | 0
Fuel Cost | 1210320 | 0 | 2159340 | 3588637.5 | 7466748 | 1475218.8 | 1303478.4 | 0 | 8289440 |  | 0 | 10456097.5 | 3590911.05 | 13188384 | 14029473.12 | 4522106.88 | 7735948.48 | 0 | 7317900 | 0 | 10995004.8 | 13126233.6 | 10050969.6 | 2614312.56 | 0 | 0 | 0 | 4974804 | 4822924.79 | 4603604.42 | 259173 | 450000 | 0 | 0 | 0 | 1483687.44 | 0 | 357669.54 | 423360 | 0 | 0 | 1682985.69 | 0 | 0 | 5718854.4 | 0 |  | 0 | 833554 | 4824198 | 92826 | 4242816 | 1281139.2 | 548916.48 | 1675080 | 0 | 4730205.8 | 3180915.36 | 5400964 | 0 | 4328600 | 2136240 | 2362767 | 854930.88 | 1563744 | 0 | 1785039.93 | 0 | 553156.8 | 11786657.75 | 591205.32 | 139590 | 1276450 | 330240 | 25466400 | 3649622.4 | 13903296 | 418840.92 | 153024 | 3317720 | 1140672 | 2031336 | 1771511.04 | 4266947.04 | 5065840 | 1364122.56 | 3749712 | 0 | 0 | 911040 | 0 | 503431.2 | 7246750 | 413136 | 180138.24 | 0 | 34693785 | 1718749.56 | 0 | 24061440 | 432395.92 | 31073932.8 | 1409287.95 | 18793248 | 8296344 | 4776128.25 | 0 | 14883840 | 6701259.6 | 1697326.41 | 0 | 51746688 | 3037455.72 | 0 | 10341874.8 | 4873587.6 | 15216768 | 0 | 0 |  | 127009048.32 | 0 | 8814960 | 0 | 17671795.2 | 41561649.36 | 0 | 0 | 0 | 0 | 4399845 | 2433973.67 | 1081032 | 6568089.6 | 0 | 0 | 0 | 2552574.72 | 129824.48 | 10692428.4 | 0 | 0 | 2892561.9 | 3730262.4 | 2161111.5 | 901785.6 | 379607.4 | 146315.988 | 0 | 0 | 19732594 | 0 | 0 | 0 | 0 | 5900868.6 | 0 | 2654242.5 | 9258883.2 | 5740605 | 0 | 9236753.46 | 6419347.2 | 0 | 9144108.48 | 0 | 14832153.6 | 0 | 269288.5 | 16629983.04 | 55607252 |  | 511724475.1 | 388552945.118 | 900277420.218 | 99149561.598 | 127009048.32 | 62507446.87 | 431940458.68 | 75339846 | 781029.54 | 76252028.76 | 25466400 | 1831600.45 | 0
Yesterday Day Peak | 35 | 0 | 100 | 100 | 300 | 13 | 40 | 0 | 342 |  | 0 | 420 | 140 | 89 | 94 | 5 | 318 | 0 | 180 | 0 | 50 | 93 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 16 | 25 | 22 | 25 | 33 | 0 | 0 | 40 | 65 | 0 | 0 | 25 | 0 | 0 | 140 | 0 |  | 0 | 2 | 0 | 0 | 0 | 0 | 18 | 6 | 0 | 135 | 80 | 270 | 0 | 183 | 83 | 90 | 31 | 47 | 0 | 51 | 0 | 0 | 52 | 18 | 5 | 25 | 18 | 136 | 149 | 72 | 14 | 1.4 | 81 | 30 | 47 | 48 | 163 | 209 | 28 | 85 | 0 | 0 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 232 | 0 | 0 | 200 | 0 | 137 | 19.3 | 90 | 0 | 0 | 0 | 8 | 0 | 0 | 5.2 | 308 | 0 | 0 | 17 | 0 | 100 | 0 | 104 |  | 923 | 0 | 325 | 0 | 49 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 155 | 0 | 75 | 0 | 190 | 0 | 405 | 0 | 0 | 0 | 0 | 34 | 0 | 0.8 | 109 | 460 |  | 9665.7 | DayPeak
Yesterday Evening Peak | 35 | 0 | 100 | 100 | 270 | 0 | 0 | 0 | 351 | 0 | 0 | 450 | 120 | 93 | 96 | 55 | 327 | 0 | 180 | 0 | 100 | 93 | 149 | 40 | 0 | 0 | 0 | 53 | 55 | 35 | 19 | 25 | 25 | 33 | 33 | 50 | 0 | 77 | 65 | 0 | 0 | 25 | 0 | 0 | 138 | 0 | 0 | 0 | 6 | 102 | 0 | 95 | 50 | 18 | 29 | 0 | 135 | 100 | 260 | 0 | 182 | 0 | 81 | 35 | 49 | 0 | 0 | 0 | 0 | 52 | 20 | 8 | 33 | 18 | 164 | 157 | 72 | 17 | 0 | 88 | 30 | 50 | 48 | 163 | 210 | 29 | 85 | 0 | 0 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 285 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 200 | 0 | 0 | 115 | 105 | 68 | 0 | 307 | 54 | 0 | 114 | 56 | 100 | 0 | 104 |  | 922 | 0 | 405 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 89 | 38 | 110 | 0 | 0 | 0 | 50 | 0 | 98 | 0 | 0 | 44 | 43 | 33 | 20 | 11 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 184 | 0 | 76 | 70 | 186 | 0 | 384 | 105 | 0 | 92 | 0 | 113 | 0 | 0 | 109 | 530 |  | 12023 | EvPeak
Forecast for Evening | 35 | 0 | 100 | 110 | 300 | 0 | 0 | 0 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 330 | 0 | 180 | 0 | 100 | 102 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 22 | 33 | 33 | 50 | 0 | 80 | 65 | 0 | 0 | 25 | 0 | 0 | 140 | 0 | 0 | 0 |  | 100 | 100 | 91 | 50 | 21 | 30 | 0 | 100 | 100 | 360 | 250 | 220 | 0 | 90 | 42 | 52 | 0 | 0 | 0 | 42 | 52 | 22 | 11 | 33 | 18 | 173 | 160 | 95 | 17 | 0 | 90 | 30 | 51 | 44 | 163 | 210 | 66 | 86 | 0 | 0 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 0 | 300 | 54 | 110 | 114 | 60 | 100 | 0 | 104 |  | 920 | 16 | 410 | 0 | 115 | 225 | 0 | 0 | 30 | 60 | 40 | 90 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 0 | 50 | 45 | 52 | 35 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 10 | 0 | 0 | 220 | 0 | 79 | 100 | 220 | 0 | 414 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 600
Forecast for Day | 35 | 0 | 100 | 110 | 300 | 0 | 0 | 0 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 330 | 0 | 150 | 0 | 100 | 102 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 22 | 33 | 33 | 50 | 0 | 80 | 65 | 0 | 0 | 25 | 0 | 0 | 140 | 0 | 0 | 0 | 8 | 100 | 100 | 90 | 50 | 21 | 20 | 0 | 135 | 130 | 360 | 360 | 220 | 0 | 90 | 40 | 52 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 18 | 157 | 155 | 95 | 17 | 1.6 | 88 | 30 | 51 | 44 | 163 | 210 | 61 | 86 | 0 | 0 | 18 | 0 | 10 | 341 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 80 | 149 | 20 | 100 | 200 | 0 | 0 | 115 | 100 | 100 | 5 | 300 | 50 | 50 | 114 | 60 | 100 | 0 | 104 |  | 920 | 0 | 360 | 0 | 115 | 130 | 0 | 0 | 0 | 0 | 40 | 90 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 50 | 0 | 52 | 0 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 180 |  | 76 | 60 | 200 | 0 | 414 | 105 | 0 | 113 | 100 | 113 | 0 | 8 | 113 | 600
Generation at 08:00(Today) | 35 | 0 | 100 | 110 | 300 | 0 | 0 | 0 | 303 | 0 | 0 | 370 | 145 |  | 64 | 0 | 300 | 0 | 118 | 0 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 24 | 33 | 33 | 0 | 0 | 79 | 65 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 16 | 5 | 0 | 135 | 130 | 315 | 0 | 192 | 0 | 90 | 32 | 52 | 0 | 0 | 0 | 0 | 34 | 18 | 11 | 32 | 11 | 122 | 153 | 48 | 0 | 1.1 | 87 | 30 | 50 | 48 | 130 | 209 | 28 | 85 | 0 | 0 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 75 | 0 | 0 | 200 | 0 | 101 | 8.4 | 100 | 0 | 0 | 0 | 8 | 0 | 0 | 2.6 | 307 | 0 | 0 | 0 | 57 | 100 | 0 | 104 | 0 | 910 | 0 | 350 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 187 | 0 | 75 | 0 | 194 | 0 | 409 | 0 | 0 | 0 | 0 | 34 | 0 | 0.1 | 35 | 516 | 0
199
| Minimum Generation |  | 8458 | 8:00
| Highest Generation |  | 12023 | 21:00
| Day Peak Generation |  | 9665.7 | 12:00
| Evening Peak Generation |  | 12023 | 21:00
| HVDC Max Flow |  | 923 | 9:00
| HVDC EvPeak Flow |  | 922 | 21:00
| Load factor L.F |  | 85.52%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-08-09
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-08-08 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9665.7 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 9079.2 | MW
Evening Peak Generation : |  | 12023 | MW Hour : | 21:00 | Available Max Generation : |  | 14702 | MW
E.P. Demand (at gen end) : |  | 12023 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12400 | MW
Maximum Generation : |  | 12023 | MW Hour : | 21:00 | Reserve(Generation end) |  | 2302 | MW
Total Gen. (MKWH) : |  | 246.7791 | System Load Factor : | 85.52% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -39 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-08-09
Actual : | 94.64 | Ft.(MSL) , | Rule curve : | 91.56 | Ft.( MSL )
Gas Consumed : | Total = | 1145.11 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 161657008.468
: |  | Coal : | 75339846 | Oil : | 508192487.44 | Total : | 745189341.908
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4406.3886 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1501.7397 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1346.1013 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1216.5263 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1099.2413 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 887.0572 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 491.7216 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 228.2802 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 684.163 |  |  | 0 | 0%
Total | 0 |  | 11861.2192 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down | 10) Haripur-412 MW.
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 11) Baghabari-1,2
2) Bibiyana #3
3) Ghorasal Unit-2,3,
4) Ashuganj unit-3
5) Bhola-225 MW GT-2 & ST
6) Kaptai-2
7) Raozan #1,2
8) Sirajganj #1
9) Sylhet-225 MW.
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Madunaghat 132/33 kV T1 transformer was shut down from 11:06 to 12:58 for C/M.
b) Ramganj 132/33 kV T2 transformer was shut down from 09:16 to 11:05 for C/M. |  |  |  |  | About 12 MW power interruption occurred under Ramganj S/S area
from 09:16 to 11:05.
c) Faridpur 132/33 kV T2 transformer was under shut down from 11:25 to 12:26 due to oil leakage maintenance |  |  |  |  | About 35 MW power interruption occurred under Faridpur S/S area
of B-phase CT. |  |  |  |  | from 11:25 to 12:26.
d) Madunaghat-Chandraghona 132 kV Ckt-2 tripped at 12:05 from both end showing dist Z1 from both end
and was switched on at 12:17.
e) After maintenance Ghorasal #04 was synchronized at 10:19.
f) Khulna(S)-Khulna© 132 kV Ckt-1 was shut down from 12:45 to 15:57 for protection test at Khulna(S) end.
g) Jhenaidah 132/33 kV T1 transformer was shut down from 14:28 to 17:04 due to red hot maintenance at |  |  |  |  | About 36 MW power interruption occurred under Jhenaidah S/S area
33 kV incoming isolator. |  |  |  |  | from 14:28 to 17:04.
h) Ruppur 132/33 kV T1 transformer was shut down from 12:19 to 14:50 for measurement of earth resistance.
i) Ruppur 132/33 kV T2 transformer was shut down from 14:56 to 15:18 for measurement of earth resistance.
j) Ashuganj Modular tripped at 20:13 showing E/F relay at the same time Ashuganj Midland 150 MW,
Ashuganj Midland 51 MW are got tripped .
k) Netrokona 132/33 kV T1 transformer is under shut down since 07:02 for C/M. |  |  |  |  | About 05 MW power interruption occurred under Netrokona S/S area
since 07:02 to till now.
l) Natore 132/33 kV T2 transformer under 33 kV CB was shut down from 07:13 to 08:47 for red hot maintenance
at 33 kV bushing.
m) After maintenance Meghnaghat Summit GT-1 was synchronized at 07:29.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-08-08 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 738000 | Unit-2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 100 | 1479000 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 100 | 2441250
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 270 | 6726800
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 766752 | Gas Shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 1117590 | Gas Shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 351 | 8048000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9592750
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 93 | 1737600 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 120 | 3235055 | FGMO & GT-1 Under maint.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 96 | 2036208
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 534528
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 40 | 283548 | Low demand
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 345564 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 180 | 4230000
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 1460160
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 327 | 7438412
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 1439280 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel Shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 681480
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 1021440
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 623923
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 466897
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 50 | 1119840 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 700300
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 770800
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 50 | 153432
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 285 | 4589125
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 101222 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 25861 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3157920
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 709128
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2144640
| Dhaka area Total |  |  |  | 5895 | 3530 | 69916505
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 181161
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 120555
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 161760
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 142 | 2892702 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under S/D.
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 138 | 3364032
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 68 | 194871 | Low demand
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 6 | 86200 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 497340
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 9720 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2305920
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 435648
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 29 | 564000
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 95 | 487680
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 31189
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 307 | 6844800
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 348732
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2284800
| Chattogram area Total |  |  |  | 2266 | 1234 | 20811110
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 135 | 3196085
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 100 | 2163888
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 182 | 4705000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 260 | 7298600 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 35 | 756576
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 49 | 1116960 | Engine problem
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 1656000
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 1043883
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 677465 | Reserve
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 54768
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 81 | 2054580 | ST under maint.
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 764640 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 465516
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 186120
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 164 | 3395520
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 729400
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 1234205
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 18 | 440320 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1036260
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 56 | 568680 | Fuel shortage
| Cumilla Area Total |  |  |  | 2980 | 1507 | 33544466
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 157 | 3443040 | Engine problem
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 329796 | Engine problem
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 72 | 1531200 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9600
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 4627200
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1632000 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 561 | 11572836
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 88 | 2023000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 712920 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3742936
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 210 | 4871000
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1141200
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 48 | 1135584
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 237024
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 29 | 692448 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1963200
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | Under maint.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 416000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 550848
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7175000
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 246780
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1056 | 24907940
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 922 | 22050182
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 2248320
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 120 | 2998676 | Low demand
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 405 | 8395200 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 422250
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 70 | 544320
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 614880
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Reserve
| Khulna Area Total |  |  |  | 2284 | 1777 | 37273828
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 672960
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 38 | 697440
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 89 | 2153959 | GT-2 Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 76 | 1769495 | Engine problem
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 530 | 12666800 | Frequency control
| Barisal Area Total |  |  |  | 1054 | 843 | 17960654
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 259408 | Low demand
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 12778 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 44 | 298510
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage.
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 184 | 4470355 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 186 | 4906500 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 384 | 9330054 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 33 | 222795
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 20 | 469680
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 11 | 244908
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 193284 | Engine problem
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 384960
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 98 | 1208184
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 92 | 963552 | Engine problem
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 2250336
| Rajshahi Area Total |  |  |  | 2183 | 1262 | 25215304
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 140 | 3640700 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1911360
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 24370
| Rangpur Area Total |  |  |  | 605 | 253 | 5576430
| Total |  |  |  | 19892 | 12023 | 246779073
| Eastern Grid Total |  |  |  | 13766 | 7888 | 160752857
| Western Grid Total |  |  |  | 6126 | 4135 | 86026216
| National Grid Total |  |  |  | 19892 | 12023 | 246779073
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-08-08
(a) ENTIRE EASTERN GRID : |  | 7459 | MW | (b) ENTIRE WESTERN GRID : |  | 4032 | MW
i) Dhaka area |  | 3581 | MW | i) Khulna area |  | 1558 | MW
ii) Chittagong area |  | 1142 | MW | ii) Rajshahi area |  | 1300 | MW
iii) Comilla area |  | 1199 | MW | iii) Barisal area |  | 364 | MW
iv) Mymensingh area |  | 1008 | MW | iv) Rangpur area |  | 810 | MW
v) Sylhet area |  | 529 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11491 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 118 | 15:00 | Sherpur | 108 | 19:30 | Jhenida | 116 | 19:30
Munsiganj | 122 | 21:00 | Srimongal | 52 | 19:30 | Bottail | 136 | 19:30
Sonargaon | 77 | 23:00 | Shahjibazar | 122 | 21:00 | G.K Project | 58 | 21:00
Shyampur | 152 | 0:00 | Fenchuganj | 49 | 19:00 | Faridpur | 198 | 0.875
Bhulta | 150 | 0:00 | Kulawara | 46 | 22:00 | Madaripur | 106 | 0.91667
Madanganj | 53 | 16:00 | Sylhet | 136 | 19:00 | Sariatpur | 70 | 21:00
Shitalakhya | 87 | 12:00 | Chatak | 29 | 21:00 | Gopalganj | 92 | 19:30
Rahim steel | 3 | 15:00 | Sunamganj | 47 | 21:00 | Bagerhat | 98 | 21:00
Matuail | 60 | 15:00 | Biani Bazar | 60 | 21:00 | Mongla | 32 | 10:00
Ghorasal | 80 | 23:00 | Comilla (S) | 170 | 22:00 | Satkhira | 116 | 0.875
Narsingdi | 157 | 20:00 | Comilla(N) | 104 | 19:30 | Gallamari | 47 | 19:30
Haripur (SBU) | 82 | 11:00 | Chandpur | 116 | 21:00 | Magura | 54 | 0.875
Ullon | 58 | 19:00 | Feni | 127 | 22:00 | Norail | 42 | 19:30
Hasnabad | 178 | 19:30 | Chowmuhani | 174 | 21:00 | Chuadanga | 92 | 19:30
Magbazar | 91 | 14:00 | Ashuganj | 59 | 21:00 | Barisal(N) | 47 | 0.95833
Maniknagar | 74 | 19:00 | Daudkandi | 145 | 19:30 | Barisal (S) | 98 | 0.8125
Bangabhaban | 20 | 12:00 | B.Baria | 166 | 22:00 | Patuakhali | 127 | 0.91667
Narinda | 72 | 13:00 | Ramganj | 118 | 21:00 | Bhandaria | 60 | 0.875
Dhanmondi | 143 | 13:00 | Chaddagram | 40 | 22:00 | Borhan Uddin | 43 | 20:00
Lalbag | 55 | 13:00 | PHP | 11 | 17:00 | Ishurdi | 62 | 21:00
Madartek | 69 | 23:00 | Madunaghat | 56 | 19:00 | Ruppur Paromanobik | 2 | 1:00
Dhaka University |  |  | Hathazari | 97 | 0.91667 | Natore | 129 | 21:00
Fatullah | 24 | 0.625 | Khulshi | 198 | 0.58333 | Bogra | 165 | 21:00
Mirpur | 99 | 19:00 | Halishahar | 137 | 0.8125 | Noagaon | 125 | 22:00
Kalyanpur | 87 | 19:00 | Baraulia | 134 | 0.79167 | Rajshahi | 159 | 24:00
Gulshan | 108 | 13:00 | Sikalbaha | 26 | 0.83333 | Rajshahi New | 12 | 21:00
Uttara | 81 | 19:00 | Dohazari | 94 | 0.83333 | C.Nawabganj | 74 | 21:00
Uttara New | 26 | 19:00 | Cox'sbazar | 104 | 0.83333 | Amnura | 54 | 21:00
Kamrangirchar | 76 | 19:00 | Chandraghona | 32 | 0.8125 | Pabna | 126 | 21:00
Savar | 129 | 16:00 | Kaptai | 4.6 | 0.79167 | Shahjadpur | 106 | 22:00
Bhasantec | 138 | 19:00 | A. Khaer Stl. | 0 | 0.041667 | Serajganj | 97 | 21:00
Agargaon | 60 | 19:00 | Bakulia | 94 | 0.79167 | Niyamatpur | 63 | 22:00
Satmosjid | 101 | 19:30 | Julda | 16 | 0.041667 | Joypurhat | 56 | 20:00
Tongi | 116 | 0.45833 | TK chemical | 26.5 | 0.875 | Sherpur(Bogura) | 47 | 20:00
Kabirpur | 192 | 14:00 | Modern Steel | 0.2 | 0.041667 | Mohastangor | 53 | 23:00
Basundhara | 125 | 19:00 | Shahmirpur | 31 | 0.58333 | Rangpur | 157 | 20:00
Manikganj | 72 | 21:00 | Khagrachhari | 25 | 0.8125 | Lalmonirhat | 62 | 23:00
Joydevpur | 157 | 21:00 | Matarbari | 34.5 | 0.875 | Saidpur | 108 | 20:00
New Tongi | 88 | 15:00 | Baroiar Hat | 38 | 0.79167 | Purbasadipur | 106 | 21:00
Korda | 210 | 12:00 | Rangamati | 12 | 0.79167 | Thakurgaon | 78 | 1:00
Dhamrai | 90 | 20:00 | Abul Khair 230 | 42 | 0 | Palashbari | 131 | 23:00
Rajendrapur | 82 | 20:00 | BSRM | 102 | 0.5 | Barapukuria | 51 | 21:00
Valuka | 104 | 16:00 | GPH Ispat | 81 | 0.54167 | Panchagar | 49 | 19:00
Tangail | 201 | 22:00 | Goalpara | 29 | 0.8125 | Joldhaka | 29 | 1:00
Mymensing | 223 | 22:00 | Central s/s | 90 | 22:00 | Kurigram | 56 | 20:00
Kishorganj | 159 | 21:00 | Noapara | 58 | 20:00
Netrokona | 112 | 21:00 | Jessore | 126 | 19:30
Jamalpur | 147 | 21:00 | Benapol | 42 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-08-08 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 396 | 21:00 | 387 | 13:00 | Kaliakoir | 377 | 0.083333 | 369 | 0.5
| Bheramara | 400 | 7:00 | 393 | 19:30 | Bhulta | 392 | 0.041667 | 373 | 0.54167
| Ashuganj(N) | 397 | 2:00 | 378 | 13:00 | Gopalganj | 414 | 0.33333 | 390 | 0.875
| Payra | 416 | 8:00 | 403 | 21:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 1:00 | 230 | 14:00 | Comilla (N) | 235 | 20:00 | 228 | 13:00
| Ishurdi | 236 | 17:00 | 228 | 19:30 | Hathazari | 226 | 21:00 | 214 | 11:00
| Ashuganj | 238 | 1:00 | 233 | 13:00 | Megnaghat | 234 | 22:00 | 228 | 13:00
| Serajganj | 233 | 14:00 | 228 | 3:00 | Fenchuganj | 236 | 23:00 | 232 | 22:00
| Baghabari | 240 | 18:30 | 236 | 21:00 | Siddhirganj | 233 | 24:00 | 228 | 11:00
| Barapukuria | 234 | 18:00 | 222 | 22:00 | Maniknagar | 232 | 25:00 | 227 | 11:00
| Bogra | 228 | 14:00 | 217 | 21:00 | Agargaon | 229 | 26:00 | 222 | 13:00
| Rajshahi | 230 | 18:00 | 220 | 3:00 | Barisal | 246 | 27:00 | 233 | 3:00
| Khulna South | 229 | 17:00 | 219 | 3:00 | AKSML | 226 | 28:00 | 214 | 8:00
| Rampura | 230 | 20:00 | 225 | 11:00 | BSRM | 226 | 29:00 | 216 | 11:00
| Haripur | 228 | 9:00 | 226 | 10:00 | Bibiyana | 236 | 31:00 | 232 | 13:00
| Hasnabad | 230 | 1:00 | 225 | 12:00 | Bhulta | 233 | 32:00 | 226 | 13:00
| Shyampur | 228 | 1:00 | 222 | 12:00 | Ashuganj (S) | 236 | 1:00 | 229 | 13:00
| Aminbazar | 230 | 1:00 | 224 | 11:00 | Kaliakoir | 232 | 19:30 | 223 | 10:00
| Tongi | 228 | 4:00 | 215 | 13:00 | GPH | 224 | 19:30 | 212 | 11:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 134 | 18:30 | 130 | 8:00 | Hathazari | 135 | 0.8125 | 130 | 0.5
| Munsiganj | 136 | 19:30 | 129 | 7:00 | Khulshi | 134 | 0.8125 | 128 | 0.29167
| Sonargaon | 136 | 19:00 | 130 | 9:00 | Halishahar | 139 | 0.83333 | 130 | 0.33333
| Shyampur | 135 | 20:00 | 130 | 11:00 | Baraulia | 135 | 0.83333 | 127 | 0.625
| Bhulta | 128 | 19:30 | 123 | 5:00 | Sikalbaha | 138 | 20:00 | 130 | 0.29167
| Madanganj | 133 | 20:00 | 128 | 6:00 | Dohazari | 134 | 20:00 | 126 | 0.625
| Shitalakhya | 142 | 19:00 | 133 | 10:00 | Cox'sbazar | 124 | 0.8125 | 118 | 0.625
| Rahim steal | 134 | 19:00 | 129 | 7:00 | Chandraghona | 136 | 0.83333 | 130 | 0.54167
| Matuail | 134 | 18:30 | 130 | 8:00 | Kaptai | 135 | 19:30 | 130 | 0.29167
| Ghorasal | 138 | 1:00 | 137 | 14:00 | A. Khaer Stl. | 134 | 0.8125 | 127 | 8:00
| Narsinghdi | 130 | 18:00 | 123 | 10:00 | Bakulia | 136 | 0.8125 | 128 | 0.33333
| Haripur (SBU) | 135 | 19:00 | 129 | 9:00 | Julda | 133 | 0.75 | 130 | 0.16667
| Ullon | 135 | 3:00 | 131 | 10:00 | TK Chemical | 137 | 0.83333 | 129 | 18:00
| Hasnabad | 138 | 19:30 | 134 | 9:00 | Modern Steel | 136 | 0.875 | 130 | 0.375
| Magbazar | 135 | 2:00 | 130 | 10:00 | Shahmirpur | 137 | 0.83333 | 129 | 0.58333
| Maniknagar | 133 | 19:30 | 130 | 10:00 | Khagrachhari | 134 | 0.8125 | 128 | 0.625
| Bangabhaban | 133 | 19:30 | 130 | 10:00 | Matarbari | 128 | 0.83333 | 120 | 0.041667
| Narinda | 133 | 19:30 | 130 | 10:00 | Baroiar Hat | 131 | 0.8125 | 124 | 0.5
| Dhanmondi | 135 | 3:00 | 131 | 10:00 | Rangamati | 135 | 0.83333 | 129 | 13:00
| Lalbag | 140 | 19:30 | 132 | 10:00 | Goalpara S/S | 138 | 17:00 | 132 | 13:00
| Madartek | 134 | 4:00 | 130 | 10:00 | Khulna Central S/S | 138 | 0.70833 | 130 | 8:00
| Dhaka University |  |  |  |  | Noapara | 135 | 18:30 | 129 | 13:00
| Fatuiiah | 137 | 0.79167 | 130 | 9:00 | Jessore | 130 | 17:00 | 121 | 21:00
| Mirpur | 133 | 20:00 | 129 | 12:00 | Benapol | 131 | 17:00 | 123 | 21:00
| Kalyanpur | 134 | 19:30 | 130 | 12:00 | Jhenida | 128 | 0.70833 | 113 | 21:00
| Gulshan | 133 | 6:00 | 130 | 12:00 | Bottail | 132 | 17:00 | 123 | 21:00
| Uttara | 133 | 1:00 | 127 | 12:00 | G.K Project | 139 | 0.77083 | 132 | 21:00
| Uttara New | 136 | 21:00 | 129 | 13:00 | Faridpur | 133 | 8:00 | 126 | 1:00
| Kamrangirchar | 139 | 19:30 | 130 | 12:00 | Madaripur | 140 | 0.25 | 131 | 23:00
| Savar | 132 | 14:00 | 128 | 12:00 | Shariyatpur S/S | 137 | 0.29167 | 129 | 19:00
| Bhasantec | 132 | 6:00 | 128 | 12:00 | Gopalganj | 140 | 8:00 | 127 | 22:00
| Agargaon | 134 | 1:00 | 130 | 12:00 | Bagerhat | 134 | 9:00 | 128 | 13:00
| Satmosjid | 133 | 2:00 | 129 | 12:00 | Mongla | 131 | 0.8125 | 123 | 13:00
| Tongi | 139 | 0.79167 | 131 | 13:00 | Satkhira | 136 | 0.70833 | 130 | 21:00
| Kabirpur | 134 | 18:30 | 129 | 23:00 | Gallamari | 138 | 17:00 | 133 | 12:00
| Basundhara | 134 | 20:00 | 129 | 11:00 | Magura | 126 | 12:00 | 112 | 19:30
| Manikganj | 140 | 21:00 | 130 | 12:00 | Norail | 124 | 0.70833 | 106 | 21:00
| Joydevpur | 141 | 19:30 | 135 | 10:00 | Chuadanga | 121 | 17:00 | 100 | 21:00
| New Tongi | 137 | 0.8125 | 129 | 12:00 | Barisal(N) | 138 | 6:00 | 132 | 1:00
| Kodda | 138 | 22:00 | 123 | 0.375 | Barisal (S) | 138 | 0.375 | 130 | 19:00
| Dhamrai | 133 | 18:00 | 128 | 23:00 | Patuakhali(S) | 136 | 0.33333 | 123 | 2:00
| Rajendrapur | 136 | 21:00 | 123 | 8:00 | Bhandaria | 130 | 19:30 | 125 | 1:00
| Valuka | 125 | 18:30 | 112 | 22:00 | Ishurdi | 137 | 18:30 | 130 | 15:00
| Tangail | 134 | 17:00 | 127 | 2:00 | Ruppur Paromanobik | 135 | 16:00 | 130 | 22:00
| Mymensing | 131 | 18:00 | 114 | 22:00 | Natore | 132 | 18:30 | 125 | 21:00
| Kishorganj | 128 | 18:00 | 116 | 22:00 | Bogra | 131 | 18:00 | 122 | 21:00
| Netrokona | 125 | 18:00 | 110 | 22:00 | Noagaon | 128 | 18:30 | 116 | 22:00
| Jamalpur | 137 | 14:00 | 127 | 19:00 | Rajshahi | 130 | 18:00 | 123 | 21:00
| Sherpur | 138 | 15:00 | 125 | 19:00 | Rajshahi New | 130 | 17:00 | 123 | 21:00
| Srimongal | 135 | 7:00 | 127 | 0.875 | C.Nawabganj | 130 | 18:30 | 120 | 21:00
| Shahjibazar | 133 | 6:00 | 127 | 0.875 | Amnura | 132 | 18:30 | 119 | 22:00
| Fenchuganj | 133 | 7:00 | 127 | 0.95833 | Pabna | 135 | 18:30 | 128 | 2:00
| Khulawara | 132 | 7:00 | 127 | 0.875 | Shahjadpur | 137 | 5:00 | 134 | 20:00
| Sylhet | 130 | 7:00 | 122 | 0.79167 | Serajganj | 132 | 18:30 | 125 | 21:00
| Chatak | 127 | 7:00 | 119 | 21:00 | Niyamatpur | 128 | 18:30 | 113 | 22:00
| Sunamganj | 125 | 6:00 | 116 | 0.91667 | Joypurhat | 126 | 18:30 | 113 | 22:00
| Biani Bazar | 128 | 7:00 | 119 | 0.875 | Sherpur(Bogura) | 132 | 18:30 | 124 | 21:00
| Comilla(s) | 128 | 8:00 | 119 | 20:00 | Mohastangor | 129 | 18:30 | 120 | 21:00
| Comilla(n) | 137 | 19:30 | 132 | 13:00 | Rangpur | 125 | 15:00 | 111 | 21:00
| Chandpur | 135 | 20:00 | 120 | 9:00 | Lalmonirhat | 120 | 15:00 | 106 | 21:00
| Feni | 133 | 20:00 | 124 | 17:00 | Saidpur | 124 | 6:00 | 110 | 20:00
| Chowmuhani | 129 | 19:30 | 120 | 7:00 | Purbasadipur | 121 | 17:00 | 102 | 22:00
| Ashuganj | 135 | 18:00 | 130 | 1:00 | Thakurgaon | 121 | 17:00 | 104 | 21:00
| Daudkandi | 134 | 20:00 | 128 | 8:00 | Palashbari | 125 | 18:00 | 110 | 22:0
| B.Baria | 130 | 7:00 | 123 | 22:00 | Barapukuria | 132 | 18:00 | 120 | 21:00
| Ramganj | 124 | 20:00 | 114 | 15:00 | Panchagar | 119 | 17:00 | 97 | 23:00
| Chaddagram | 134 | 21:00 | 125 | 14:00 | Joldhaka | 125 | 18:30 | 104 | 21:00
| PHP | 132 | 21:00 | 123 | 12:00 | Kurigram | 121 | 16:00 | 102 | 21:00
| Madanhat | 139 | 20:00 | 131 | 8:00

## L-Curve
Date | 2020-08-08
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 90 | 7521 | 4174 | 11695 |  |  |  | QF-LDC-12
0:30 | 64.5 | 7208.5 | 4041 | 11249.5 | Date: | 2020-08-08
1:00 | 39 | 6896 | 3908 | 10804
1:30 | 34 | 6791.5 | 3846.5 | 10638
2:00 | 29 | 6687 | 3785 | 10472
2:30 | 29.5 | 6604 | 3754 | 10358 | [5 empty] | Gen. at Eve. Peak | 12023 | 12023 MW (21:00 )
3:00 | 30 | 6521 | 3723 | 10244 | [6 empty] | 21:00
3:30 | 32.5 | 6488.5 | 3687 | 10175.5 | [5 empty] | Gen. at Day Peak | 9665.7 | 9665.7 MW (12:00 )
4:00 | 35 | 6456 | 3651 | 10107 | [6 empty] | 12:00
4:30 | 74 | 6400.5 | 3630 | 10030.5 | [5 empty] | Highest Generation | 12023
5:00 | 113 | 6345 | 3609 | 9954 | [6 empty] | 21:00
5:30 | 153.5 | 6082.5 | 3469.05 | 9551.55
6:00 | 194 | 5820 | 3329.1 | 9149.1
6:30 | 244 | 5650.1 | 3233.95 | 8884.05
7:00 | 294 | 5480.2 | 3138.8 | 8619
7:30 | 295.5 | 5454.1 | 3084.4 | 8538.5
8:00 | 297 | 5428 | 3030 | 8458
8:30 | 340 | 5607.35 | 3057.7 | 8665.05
9:00 | 383 | 5786.7 | 3085.4 | 8872.1
9:30 | 391.5 | 5949.05 | 3104.8 | 9053.85
10:00 | 400 | 6111.4 | 3124.2 | 9235.6
10:30 | 376.5 | 6171.3 | 3141.05 | 9312.35
11:00 | 353 | 6231.2 | 3157.9 | 9389.1
11:30 | 334 | 6376.05 | 3151.35 | 9527.4
12:00 | 315 | 6520.9 | 3144.8 | 9665.7
12:30 | 363.5 | 6632.5 | 3159.3 | 9791.8
13:00 | 412 | 6744.1 | 3173.8 | 9917.9
13:30 | 392 | 6772.89 | 3150.1 | 9922.99
14:00 | 372 | 6801.68 | 3126.4 | 9928.08
14:30 | 367 | 6877.445 | 3186.5 | 10063.945
15:00 | 362 | 6953.21 | 3246.6 | 10199.81
15:30 | 366 | 6910.655 | 3263.05 | 10173.705
16:00 | 370 | 6868.1 | 3279.5 | 10147.6
16:30 | 462.5 | 6649.27 | 3259.65 | 9908.92
17:00 | 555 | 6430.44 | 3239.8 | 9670.24
17:30 | 552.5 | 6125.62 | 3170.45 | 9296.07
18:00 | 550 | 5820.8 | 3101.1 | 8921.9
18:30 | 407 | 6503.9 | 3338.05 | 9841.95
19:00 | 264 | 7187 | 3575 | 10762
19:30 | 19 | 7849 | 3996 | 11845
20:00 | 17 | 7838 | 3940 | 11778 |  |  |  | Executive Engineer
20:30 | 11.5 | 7863 | 4037.5 | 11900.5 |  |  |  | Network Operation Division
21:00 | 6 | 7888 | 4135 | 12023
21:30 | 54 | 7833.5 | 4139.5 | 11973
22:00 | 102 | 7779 | 4144 | 11923 |  |  |  |  | Page 6 of 7
22:30 | 89.5 | 7733 | 4153.5 | 11886.5
23:00 | 77 | 7687 | 4163 | 11850
23:30 | 83.5 | 7604 | 4168.5 | 11772.5
24:00 | 90 | 7521 | 4174 | 11695
12023 MW (21:00 )
9665.7 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-08-08 |  | Energy | 246779073
[10 empty] | 2020-08-08 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3685 | 922 | 2103 | 3566 | 675 | 149 | 534 | 0 | 166
0:30 | 3581 | 917 | 2200.5 | 3167 | 690 | 144 | 451.5 | 0 | 151 | Date: | 2020-08-08
1:00 | 3477 | 912 | 2298 | 2768 | 705 | 139 | 369 | 0 | 136
1:30 | 3481.5 | 912 | 2298.5 | 2618 | 705.5 | 139.5 | 346 | 0 | 137 | [7 empty] | Total Energy | 246.7791 | Total Energy Gen 246.779 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 246.779 MKWHr
2:00 | 3486 | 912 | 2299 | 2468 | 706 | 140 | 323 | 0 | 138 | [7 empty] | Energy not Served | 0
2:30 | 3497 | 912 | 2306.5 | 2374 | 706.5 | 140 | 286 | 0 | 136 | [7 empty] | Energy Requirement | 246.7791
3:00 | 3508 | 912 | 2314 | 2280 | 707 | 140 | 249 | 0 | 134
3:30 | 3525.5 | 912 | 2337 | 2171.5 | 707 | 139.5 | 249 | 0 | 134 | [6 empty] | Shortage
4:00 | 3543 | 912 | 2360 | 2063 | 707 | 139 | 249 | 0 | 134
4:30 | 3536 | 911.5 | 2382 | 1983 | 698 | 138 | 249 | 0 | 133
5:00 | 3529 | 911 | 2404 | 1903 | 689 | 137 | 249 | 0 | 132
5:30 | 3470.5 | 911 | 2358.5 | 1682.5 | 669 | 138 | 196.5 | 0 | 125
6:00 | 3412 | 911 | 2313 | 1462 | 649 | 139 | 144 | 0 | 118
6:30 | 3400 | 911 | 2262.5 | 1264.5 | 637 | 139 | 144 | 0 | 122 |  |  |  |  | Coal
7:00 | 3388 | 911 | 2212 | 1067 | 625 | 139 | 144 | 0 | 126
7:30 | 3395.5 | 911.5 | 2200.5 | 1035 | 612.5 | 120 | 132 | 0 | 125 |  |  |  | Oil |  |  |  | ,
8:00 | 3403 | 912 | 2189 | 1003 | 600 | 101 | 120 | 0 | 124
8:30 | 3427.5 | 917.5 | 2154.5 | 1214.5 | 594 | 101 | 120 | 0 | 124
9:00 | 3452 | 923 | 2120 | 1426 | 588 | 101 | 120 | 0 | 124
9:30 | 3454 | 923 | 2142.5 | 1574.5 | 589 | 101.5 | 120 | 0 | 127
10:00 | 3456 | 923 | 2165 | 1723 | 590 | 102 | 120 | 0 | 130
10:30 | 3434.5 | 923 | 2215.5 | 1765 | 595 | 102 | 120 | 0 | 130
11:00 | 3413 | 923 | 2266 | 1807 | 600 | 102 | 120 | 0 | 130
11:30 | 3456 | 923 | 2216 | 1942.5 | 605 | 103.5 | 121 | 0 | 133
12:00 | 3499 | 923 | 2166 | 2078 | 610 | 105 | 122 | 0 | 136
12:30 | 3589.5 | 923 | 2141 | 2139.5 | 610 | 105 | 123 | 0 | 138
13:00 | 3680 | 923 | 2116 | 2201 | 610 | 105 | 124 | 0 | 140
13:30 | 3680 | 923 | 2116 | 2201 | 610 | 105 | 124 | 0 | 140
14:00 | 3680 | 923 | 2116 | 2201 | 610 | 105 | 124 | 0 | 140
14:30 | 3581 | 923 | 2105.5 | 2443 | 614.5 | 105 | 126 | 0 | 145
15:00 | 3482 | 923 | 2095 | 2685 | 619 | 105 | 128 | 0 | 150
15:30 | 3454 | 923 | 2097.5 | 2677 | 619.5 | 105 | 138.5 | 0 | 148
16:00 | 3426 | 923 | 2100 | 2669 | 620 | 105 | 149 | 0 | 146
16:30 | 3433.5 | 923 | 2099.5 | 2417 | 620 | 105 | 159 | 0 | 143
17:00 | 3441 | 923 | 2099 | 2165 | 620 | 105 | 169 | 0 | 140
17:30 | 3389 | 923 | 1950.5 | 2001 | 620 | 105 | 169 | 0 | 134
18:00 | 3337 | 923 | 1802 | 1837 | 620 | 105 | 169 | 0 | 128
18:30 | 3447 | 923 | 1986.5 | 2278 | 622.5 | 105 | 335.5 | 0 | 144
19:00 | 3557 | 923 | 2171 | 2719 | 625 | 105 | 502 | 0 | 160
19:30 | 3460 | 923 | 2144 | 3746 | 650 | 105 | 659 | 0 | 158
20:00 | 3351 | 921 | 2116 | 3762 | 660 | 142 | 660 | 0 | 166
20:30 | 3491 | 921.5 | 2085 | 3800 | 665 | 142 | 631 | 0 | 165
21:00 | 3631 | 922 | 2054 | 3838 | 670 | 142 | 602 | 0 | 164
21:30 | 3649 | 922 | 2061.5 | 3768.5 | 670 | 142 | 593 | 0 | 167
22:00 | 3667 | 922 | 2069 | 3699 | 670 | 142 | 584 | 0 | 170
22:30 | 3684.5 | 922 | 2078 | 3632.5 | 670.5 | 144.5 | 584.5 | 0 | 170
23:00 | 3702 | 922 | 2087 | 3566 | 671 | 147 | 585 | 0 | 170
23:30 | 3693.5 | 922 | 2095 | 3566 | 673 | 148 | 559.5 | 0 | 168 | Max Temp. in Dhaka |  | 34.3° C
24:00 | 3685 | 922 | 2103 | 3566 | 675 | 149 | 534 | 0 | 166
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 246.779 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 246.779 MKWHr
Note on W13: Author:

## Generation
g | 2020-08-08
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 74 | 75 | 75 | 74 | 72 | 74 | 74 | 36 | 36 | 37 | 37 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 77 | 77 | 77 | 82 | 84 | 1324702
2 | Karnaphuli Hydro PP Unit-4 & 5 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1568000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [10 empty] | 5 | 25 | 25 | [7 empty] | 2 | 18 | 25 | 25 | 25 | 25 | 181161
| Teknaf 20MW PP (Solartech) | [5 empty] | 0.8 | 4.4 |  | 10.4 | 17 | 19.3 | 19.3 | 11 | 6.48 | 6.71 | 8 | 6.24 | 0.7 | [8 empty] | 120555
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 139 | 140 | 139 | 140 | 139 | 139 | 139 | 145 | 139 | 140 | 139 | 140 | 139 | 141 | 140 | 139 | 139 | 103 |  | 141 | 139 | 139 | 138 | 138 | 139 | 140 | 3364032
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 102 | 102 | 102 | 102 | 85 | 85 | 51 | 497340
12 | Hathazari 100 MW peaking PP | [11 empty] | 2 | 4 | 6 | 8 | 8 | 8 | 8 |  | 8 | 6 | 6 | 6 | 8 | 8 | 8 | 86200
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [19 empty] | 4 | 40 | 45 | 68 | 17 | 17 | 17 | 194871
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [19 empty] | 38 | 42 | 42 |  |  |  |  | 54768
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 145 | 145 | 145 | 175 | 175 | 115 | 115 | 145 | 185 | 185 | 175 | 180 | 180 | 180 | 180 | 180 | 175 | 120 |  | 175 | 135 | 95 | 180 | 180 | 180 | 185 | 4230000
17 | Siddhirganj 335 MW CCPP | 326 | 327 | 325 | 328 | 326 | 280 | 280 | 280 | 300 | 300 | 320 | 318 | 316 | 316 | 320 | 320 | 320 | 280 |  | 321 | 322 | 315 | 327 | 329 | 324 | 326 | 7438412
18 | Kodda 300 MW PP Unit-2 (Summit) | 245 | 145 | 95 | 95 | 45 | 30 | 30 | 30 | 55 | 143 | 153 | 232 | 263 | 273 | 286 | 286 | 220 | 165 |  | 188 | 285 | 285 | 285 | 285 | 285 | 285 | 4589125
19 | Ashuganj 195MW PP (APSCL-United) | 92 | 92 | 92 | 92 | 92 | 55 | 55 | 55 | 55 | 55 | 85 | 83 | 83 | 83 | 83 | 83 | 83 | 83 |  | 130 | 130 | 157 |  |  |  |  | 1656000
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 738000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | [10 empty] | 20 | 100 | 200 | 160 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1479000
23 | Ghorasal TPP Unit-5 | 60 | 70 | 90 | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2441250
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 285 | 240 | 240 | 240 |  | 240 | 240 | 240 | 270 | 270 | 270 | 270 | 6726800
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 |  | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 3196085
30 | Ashuganj TPP Unit- 5 | 100 | 100 | 100 | 100 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 100 | 130 | 130 | 130 | 2163888
32 | Ashuganj 50 MW PP | 41 | 41 | 41 | 41 | 38 | 38 | 31 | 31 | 31 | 31 | 31 | 31 | 33 | 38 | 38 | 35 | 35 | 35 |  | 35 | 38 | 38 | 35 | 35 | 35 | 32 | 756576
33 | Ashuganj 225 MW CCPP | 208 | 205 | 203 | 197 | 190 | 213 | 213 | 213 | 213 | 210 | 184 | 183 | 197 | 182 | 184 | 182 | 182 | 182 |  | 194 | 181 | 181 | 182 | 181 | 201 | 189 | 4705000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 295 | 260 | 280 | 260 | 270 | 310 | 290 | 290 | 290 | 290 | 290 |  | 320 | 310 | 260 | 260 | 260 | 280 | 260 | 7298600
35 | Ashuganj 55 MW PP (Precision) | 49 | 48 | 48 | 48 | 49 | 50 | 49 | 49 | 48 | 48 | 48 | 47 | 47 | 47 | 45 | 46 | 47 | 20 |  | 20 | 20 | 40 | 49 | 51 | 50 | 52 | 1116960
36 | Chandpur 150 MW CCPP | 85 | 90 | 90 | 90 | 91 | 91 | 91 | 91 | 87 | 90 | 90 | 90 | 90 | 90 | 90 | 82 | 80 | 88 |  | 90 | 80 | 87 | 81 | 88 | 91 | 91 | 2054580
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 400 | 400 | 400 | 420 | 420 | 420 | 420 | 420 | 400 | 400 | 400 | 400 | 370 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 9592750
41 | Haripur 360MW CCPP(HPL) | 336 | 336 | 336 | 352 | 350 | 350 | 309 | 309 | 308 | 309 | 341 | 342 | 342 | 343 | 345 | 345 | 345 | 305 |  | 341 | 352 | 351 | 351 | 351 | 351 | 351 | 8048000
42 | RPCL 210MW CCPP | 156 | 157 | 157 | 157 | 156 | 157 | 156 | 155 | 154 | 151 | 150 | 149 | 149 | 118 | 116 | 121 | 138 | 139 |  | 135 | 141 | 141 | 157 | 156 | 153 | 155 | 3443040
43
44 | Fenchugonj CCPP Phase-1 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 81 | 82 | 80 | 81 | 82 | 82 | 82 | 82 | 82 | 82 |  | 82 | 89 | 88 | 88 | 88 | 87 | 87 | 2023000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 712920
46 | Shajibazar 330 MW CCPP | 208 | 210 | 209 | 210 | 211 | 208 | 212 | 212 | 212 | 210 | 209 | 209 | 208 | 213 | 211 | 210 | 211 | 208 |  | 207 | 214 | 210 | 210 | 209 | 211 | 209 | 4871000
47 | Shahjibazar GTPP Unit- 8 & 9 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 28 | 29 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 29 | 28 |  | 28 | 28 | 29 | 29 | 29 | 28 | 29 | 692448
48 | Shahjibazar 86MW PP (Shahjibazar) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 83 | 83 | 85 | 85 | 85 | 87 | 85 | 85 | 85 | 85 | 40 |  | 85 | 85 | 85 | 85 | 87 | 88 | 88 | 1963200
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 416000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 246780
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 |  | 2 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 237024
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 47 | 44 | 44 | 44 | 49 | 50 | 25 |  | 37 | 50 | 50 | 50 | 50 | 50 | 50 | 1141200
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 550848
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 280 | 290 | 300 | 290 | 290 | 285 | 295 | 290 | 300 | 310 | 280 | 290 | 300 | 295 | 290 | 280 | 270 |  | 300 | 260 | 270 | 290 | 280 | 290 | 300 | 7175000
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 17 | 17 | [10 empty] | 4 | 35 | 55 | 35 | 35 | 35 |  | 55 | 55 | 55 | 35 | 35 | 17 | 17 | 466897
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 16 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 435648
61 | Narshingdi 22 MW PP (Doreen) | 16 | 16 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 16 |  | 16 | 16 | 16 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 345564
62 | Tangail 22 MW PP (Doreen) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 17 | 17 | 17 | 14 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 329796
63 | Impoprt (Tripura) | 136 | 138 | 134 | 134 | 132 | 118 | 126 | 124 | 124 | 130 | 130 | 136 | 140 | 144 | 150 | 146 | 140 | 128 |  | 160 | 158 | 166 | 164 | 170 | 170 | 166 | 3395520
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 33 | 3 | 3 | 4 | 2 | 6 | 6 | 3 | 2 | 2 | 19 | 20 |  | 25 | 14 | 19 | 29 | 32 | 34 | 36 | 564000
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 20 | 20 | 20 | 21 | 21 |  | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 465516
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 3 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 186120
67 | Jangalia 33MW PP (Summit) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 25 | 25 | 25 | 25 | 25 | 29 | 30 | 32 | 32 |  | 32 | 32 | 32 | 33 | 33 | 33 | 33 | 729400
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 18 | 18 | 15 | 15 | 18 | 18 | 18 | 18 | 18 | 20 | 20 | 20 | 20 | 16 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 440320
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 26 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 20 | 20 | 22 | 22 | 22 | 20 | 20 | 20 | 20 | 20 |  | 12 | 24 | 25 | 25 | 28 | 28 | 28 | 519840
71 | Maona 33 MW PP(Summit) | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 700300
72 | Rupganj 33 MW PP(Summit) | 31 | 31 | 31 | 31 | 31 | 14 | 14 | 26 | 26 | 26 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 30 | 33 | 770800
73 | Ghorashal 108MW PP (Regent) | 98 | 97 | 97 | 98 | 98 | 98 | 98 | 98 | 95 | 94 | 89 | 13 | [14 empty] | 1117590
| Feni Lanka Power | 43 | 17 | 17 | 17 | 50 | 22 | 17 | 17 | 17 | 17 | 17 | 17 | 8 |  | 35 | 35 |  |  |  | 50 | 114 | 114 | 114 | 114 | 114 | 114 | 1036260
| Chowmuhani 113 MW | 56 | 56 | 56 | 56 | [15 empty] | 16 | 57 | 56 | 56 | 56 | 57 | 56 | 568680
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 60 | 50 | 50 | 20 |  |  |  | 2 | 7 | 8 | 50 | 60 | 90 | 100 | 100 | 70 | 50 |  | 65 | 100 | 100 | 100 | 100 | 100 | 100 | 1460160
78 | Gazipur 52 MW PP | [19 empty] | 11 | 42 | 42 | 50 | 32 |  |  | 153432
79 | Kodda 150MW PP | 78 | 48 | 32 | 32 | 32 | [14 empty] | 65 | 149 | 149 | 149 | 149 | 149 | 133 | 1021440
80 | Jamalpur 95 MW PP(Powerpac) | 72 | 71 | 71 | 71 | 71 | 71 | 8 | 8 | 48 | 48 | 48 | 72 | 80 | 88 | 88 | 88 | 48 | 48 |  | 64 | 64 | 72 | 72 | 71 | 71 | 72 | 1531200
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 43 |  | 34 | 52 | 52 | 52 | 52 | 52 | 52 | 1234205
| Gazipur 100 MW PP | [12 empty] | 17 | 17 | 52 | 35 | 17 | 17 |  | 70 | 105 | 102 | 105 | 105 | 105 | 17 | 709128
| Kaptai 7 MW Solar PP | [5 empty] | 0.1 | 1.5 | 2.4 | 3.7 | 4.2 | 3.2 | 5.2 | 4.2 | 1.9 | 3.2 | 0.5 | 0.2 | [9 empty] | 31189
| Jodiac Power | [13 empty] | 1 | 17 | 17 |  |  |  | 25 | 54 | 54 | 54 | 54 | 54 | 54 | 348732
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | 97 | 97 | 97 | 64 | 64 | 62 | 48 | 48 | 48 | 85 | 95 | 94 | 94 | 94 | 94 | 94 | 94 | 94 |  | 84 | 78 | 78 | 96 | 96 | 96 | 97 | 2036208
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [13 empty] | 2 | 20 | 20 | 20 | 20 |  | 30 | 40 | 40 | 40 | 40 |  |  | 283548
86 | Meghnaghat CCPP(Summit) | 130 | 135 | 140 | 130 | 140 | 140 | 145 | 145 | 120 | 130 | 135 | 140 | 145 | 140 | 140 | 130 | 120 | 135 |  | 120 | 130 | 140 | 120 | 125 | 140 | 140 | 3235055
87 | Meghnaghat 100 MW(IEL) | 100 | 75 | 50 | 50 | 50 | 25 | 7 | 7 | 20 | 50 | 54 | 89 | 95 | 100 | 100 | 100 | 75 | 55 |  | 75 | 93 | 93 | 93 | 100 | 100 | 100 | 1737600
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 54 | 54 | 20 | 18 | 18 | 90 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 72 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 2144640
88 | Ghorashal 78.5 MW PP(MAX) |  |  |  | 40 | 71 | 72 | 71 | 70 | 71 | 70 | 40 | 40 | [14 empty] | 766752
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [20 empty] | 10 | 10 |  |  |  |  | 9720
92 | Fenchuganj 44MW (Energyprima) | 48 | 48 | 48 | 48 | 48 | 49 | 49 | 49 | 49 | 49 | 49 | 48 | 48 | 48 | 48 | 48 | 48 | 20 |  | 35 | 48 | 48 | 48 | 48 | 48 | 48 | 1135584
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 |  |  |  |  | 1043883
94 | Gagnagar 102 MW PP (Digital Power) | 40 | 40 | 40 | 7 | 7 | 7 | 7 | 7 | 40 | 50 | 74 | 93 | 93 | 93 | 93 | 93 | 48 | 48 |  | 84 | 93 | 93 | 93 | 93 | 93 | 93 | 1439280
95 | Patenga 50MW PP (Baraka) | [19 empty] | 7 | 30 | 37 | 50 | 26 | 19 | 19 | 161760
96 | Chattogram 108 MW PP (ECPV) | 12 | 12 | [11 empty] | 12 | [6 empty] | 26 | 25 | 95 | 98 | 97 | 97 | 487680
97 | Katpotti 52 MW PP (Sinha) | [26 empty] | 0
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | [11 empty] | 5 | 15 | 32 | 40 | 55 | 30 | 30 |  | 34 | 55 | 55 | 55 | 55 | 55 | 55 | 534528
100 | Manikganj 55 MW PP (Northern) | [9 empty] | 17 | 17 | 17 | 35 | 55 | 55 | 55 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 623923
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 130 | 130 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 110 |  | 163 | 163 | 130 | 163 | 163 | 163 | 163 | 3742936
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0.1 | 0.3 | 0.6 | 0.6 | 1.2 | 0.7 | 1.4 | 0.9 | 1.3 | 2.3 | 0.6 | 1 | 0.1 | [8 empty] | 9600
103 | Kamalaghat 54 MW PP(Banco Energy) | [10 empty] | 10 | 53 | 53 | 53 | 53 | 53 | 35 | 35 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 681480
104 | Keranigonj 300 MW PP (APR) | [19 empty] | 196 | 53 | [5 empty] | 101222
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 192 | 192 | 192 | 192 | 192 | 192 | 200 | 200 | 200 | 200 | 190 | 200 | 200 | 200 | 190 | 190 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 192 | 4627200
112 | Aurahati 100MW PP (Aggreko) | [19 empty] | 13 | 51 | [5 empty] | 25861
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 149 | 105 | 101 | 86 | 51 | 50 | 82 | 149 | 149 | 137 | 148 | 149 | 149 | 149 | 149 | 134 |  | 142 | 149 | 149 | 149 | 149 | 149 | 149 | 3157920
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 90 | 100 | 90 | 100 | 90 | 100 | 90 | 100 | 90 | 90 | 90 | 90 | 90 | 100 | 100 | 100 |  | 100 | 90 | 100 | 100 | 100 | 100 | 100 | 2305920
116 | Chandpur 200MW (Desh energy) | 18 | 17 | 17 | 17 | 17 | [14 empty] | 3 | 34 | 125 | 200 | 140 | 80 | 70 | 764640
117 | Ashuganj 150MW PP (Midland) | 50 | 50 | 10 | 10 | [8 empty] | 1 | 25 | 71 | 70 | 40 | 40 |  | 48 | 120 | 103 |  |  |  |  | 677465
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 115 | 40 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 50 | 85 | 85 | 16 | 16 |  | 18 | 115 | 103 | 115 | 115 | 115 | 115 | 1632000
| Anwara 300 MW PP (United) | 307 | 307 | 307 | 307 | 307 | 254 | 161 | 125 | 271 | 269 | 305 | 308 | 306 | 307 | 307 | 305 | 305 | 252 |  | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 6844800
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 70 | 70 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 70 |  | 70 | 100 | 100 | 100 | 100 | 100 | 100 | 2284800
120 | Eastern Zone Total | 6896 | 6687 | 6521 | 6456 | 6345 | 5820 | 5480.2 | 5428 | 5786.7 | 6111.4 | 6231.2 | 6520.9 | 6744.1 | 6801.68 | 6953.21 | 6868.1 | 6430.44 | 5820.8 |  | 7187 | 7849 | 7838 | 7888 | 7779 | 7687 | 7521 | 160752857
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 115 | 115 | 115 | 115 | 115 | 115 | 83 | 49 | 49 | 49 | 49 | 49 | 54 | 99 | 103 | 115 | 115 | 68 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2248320
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
| Khulna 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 135 | 120 | 120 | 120 | 120 | 120 | 2998676
129 | Rupsha 105 MW PP (Orion rupsha) | 53 | [18 empty] | 24 | 105 | 105 | 105 | 105 | 105 | 105 | 614880
130
131
132
133
| Barisal 110 MW PP (Summit ) | 16 | 16 | 16 | 16 | 16 | [14 empty] | 48 | 110 | 110 | 110 | 110 | 110 | 110 | 672960
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 77 | 77 | 75 | 75 | 75 | 75 | 62 | 62 | 77 | 77 | 75 | 75 | 76 | 77 | 75 | 79 | 80 | 44 |  | 81 | 77 | 78 | 76 | 78 | 77 | 77 | 1769495
| Bhola 225 MW CCPP | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 90 | 90 | 90 | 90 | 90 | 88 | 89 | 90 | 89 | 89 |  | 89 | 84 | 89 | 89 | 89 | 89 | 89 | 2153959
140 | Bhola 33 MW PP (Venture) | 37 | 37 | 37 | 36 | 36 | 30 | 25 | 16 | 20 | 21 | 22 | 22 | 24 | 25 | 26 | 24 | 22 | 23 |  | 24 | 35 | 36 | 38 | 39 | 39 | 38 | 697440
141 | Noapara 100 MW PP (Bangla Trac) | 60 | 10 | [17 empty] | 7 | 90 | 80 | 70 | 70 | 70 | 70 | 544320
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 40 | 40 | 40 | [14 empty] | 8 | 40 | 40 | 40 | 40 | 40 | 40 | 422250
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 912 | 912 | 912 | 912 | 911 | 911 | 911 | 912 | 923 | 923 | 923 | 923 | 923 | 922 | 923 | 923 | 923 | 923 |  | 923 | 923 | 921 | 922 | 922 | 922 | 922 | 22050182
147 | Bheramara 410 MW CCPP | 310 | 310 | 330 | 330 | 330 | 340 | 350 | 350 | 345 | 344 | 330 | 325 | 310 | 295 | 310 | 320 | 330 | 350 |  | 370 | 312 | 310 | 405 | 400 | 400 | 400 | 8395200
148 | Payra 1320 MW | 556 | 557 | 558 | 558 | 540 | 500 | 476 | 450 | 438 | 440 | 450 | 460 | 460 | 470 | 470 | 470 | 470 | 470 |  | 475 | 500 | 510 | 530 | 530 | 532 | 532 | 12666800
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 150 | 150 | 150 |  | 150 | 150 | 150 | 140 | 140 | 139 | 143 | 3640700
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 22 | 50 | 50 | 50 | 50 | 50 | 50 | 259408
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 196 | 190 | 191 | 195 | 188 | 187 | 178 | 155 | 182 | 170 | 171 | 155 | 192 | 175 | 163 | 153 | 155 | 156 |  | 168 | 176 | 164 | 184 | 187 | 186 | 196 | 4470355
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 195 | 194 | 192 | 194 | 194 | 192 | 174 | 171 | 186 | 191 | 192 | 190 | 196 | 184 | 181 | 178 | 173 | 173 |  | 185 | 182 | 175 | 186 | 182 | 185 | 181 | 4906500
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 391 | 399 | 406 | 386 | 413 | 412 | 386 | 396 | 332 | 364 | 401 | 405 | 396 | 339 | 391 | 393 | 384 | 380 |  | 388 | 371 | 310 | 384 | 399 | 406 | 409 | 9330054
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [19 empty] | 5 | 5 | 13 |  |  |  |  | 12778
162 | Bogra 22 MW PP (GBB) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 |  | 20 | 17 | 20 | 20 | 20 | 20 | 20 | 469680
163 | Bogura 20 MW PP (Energyprima) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 10 | 8 | 8 | 7 | 8 | 8 | 8 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 244908
164 | Ullapara 11 MW PP (Summit) | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 193284
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern) | [26 empty] | 0
167 | Katakhali 50 MW Peaking PP | 43 | 43 | [17 empty] | 25 | 42 | 47 | 44 | 44 | 44 | 44 | 298510
168 | Santahar 50 MW Peaking PP | 31 | 15 | [17 empty] | 20 | 30 | 33 | 33 | 30 | 32 | 31 | 222795
169 | Natore 52 MW PP (Rajlanka) | 52 | 43 | 24 | 8 | [15 empty] | 19 | 44 | 44 | 43 | 43 | 52 | 52 | 384960
170 | Chapainawabganj 100 MW Peaking PP | 97 | 97 | 97 | 97 | 97 | 24 | 24 | [8 empty] | 21 | 41 | 41 |  | 97 | 98 | 98 | 98 | 98 | 97 | 97 | 1208184
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 111 | 111 | 111 | 70 | 35 | [14 empty] | 23 | 70 | 90 | 92 | 92 | 92 | 92 | 963552
172 | Confidence Power Bogura Unit-1 113 MW | 109 | 109 | 109 | 109 | 109 | 50 | 35 | 35 | 100 | 109 | 109 | 109 | 109 | 109 | 109 | 90 | 70 | 35 |  | 90 | 109 | 109 | 109 | 109 | 109 | 109 | 2250336
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 113 | 113 | 113 | 96 | 37 | 34 | 34 | 36 | 35 | 34 | 34 | 35 | 97 | 113 | 77 | 40 |  | 60 | 107 | 104 | 113 | 113 | 113 | 113 | 1911360
177 | Sympa Solar Power 8MW | [5 empty] | 0.1 | 0.8 | 3 | 3.4 | 4.2 | 4.9 | 0.8 | 2.8 | 1.4 | 0.6 | 0.5 | 0.8 | 0.1 | [8 empty] | 24370
178
178