## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-08-24 | Saturday
|  | Date (day): | 2019-08-24 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13749 | MW |  |  | (b) At Evening Peak Hour : |  | 15416 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-08-23 | 2019-08-24 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 70 | 70 | 70 | 70 | 15 |  | Gas shortage
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 169 | 209 | 190 | 190
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 380 | 350 | 350
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 50 | 50 | 78 | 78
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 13 | 12 | 90 | 90 |  | 18 | Machine problem
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Machine problem
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 353 | 346 | 350 | 350 |  |  | FGMO
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 303 | 351 | 350 | 350
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 360 | 360 | 360 | 360 |  | 90 | Machine problem
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 282 | 270 | 280 | 280 |  |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 79 | 180 | 200 | 200 | 10 |  | Gas shortage
| Siddhirganj Desh |  | HSD | QRPP | 96*1.2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217 | 217 | 217 | 10 | 52 | 20 | 40 |  |  | ST Commissioning
| Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 7 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 18 | 47 | 46 | 46 |  | 5 | Engine problem
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 130 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 72 | 72 | 72 |  | 36 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 42 | 54 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 24 | 29 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 51 | 51 | 51
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 53 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 53 | 106 | 100 | 100
| Dhaka area Total |  |  |  |  | 5929 | 5693 | 2198 | 3009 | 3969 | 4589 | 130 | 697
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Under maint.
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 14 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 12 | 48 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 216 | 212 | 215 | 215
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 211 | 204 | 215 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 100 | 130 | 130 | 130
44 | Sikalbaha 51 MW PP(Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | Contract expired
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 17 | 50 | 100
46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D
47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 50 | 85
48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 10 | 100 | 100
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 10 | 90 | 100 | 100
50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 31 | 39 | 30 | 40
51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 44 | 95 | 97 |  | 11 | Engine problem
52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.12 | 0 | 4.4 | 0
53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 52 | 140 | 230 | 260
| Jodiac Power |  | HFO | IPP | 54.36 | 0 | 0 | 0 | 0 | 0 | 0
| Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 0 | 0 | 17 | 17 | 113 | 113
| Chattogram area Total |  |  |  |  | 2113 | 2053 | 799.12 | 1183 | 1549.4 | 1652 | 260 | 109
54 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 80 | 100 | 100 | 34 |  | Gas shortage
55 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 199 | 179 | 225 | 225
56 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 360 | 345 | 360 | 360 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 353 | 305 | 360 | 360 |  |  | FGMO
58 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 33 | 33 | 33 | 33 |  | 12 | Engine problem
59 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 10 | 55 | 30 | 55
60 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract expired
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 26 | 8 | 68 | 68 | 127 |  | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 10 | 43 | 43 | 43 |  | 8 | Engine problem
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 50 | 150 | 150
64 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract expired
65 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
66 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 138 | 138 | 140 | 140
67 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 17 | 200 | 200 | 200
68 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
69 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 128 | 178 | 151 | 191
70 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 52 | 52 | 52
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 20 | 20 | 20 |  | 5 | Engine problem
73 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1435 | 1749 | 1998 | 2313 | 425 | 25
74 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 173 | 205 | 204 | 204
75 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
76 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 74 | 89 | 95 | 95
77 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0 | 0 | 1.6 | 0
78 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 50 | 150 | 200 | 200
79 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 115 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 317 | 579 | 635.6 | 634 | 0 | 0
80 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 60 | 60 | 60
81 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 43 | 43 | 58 | 58
82 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 100 | 163 | 163 | 163
83 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 147 | 145 | 160 | 160 |  |  | FGMO
84 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 11 | 50 | 51 | 51
85 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 10 | 49 | 50 | 50
86 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
87 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 64 | 63 | 63 |  |  | FGMO
88 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 79 | 75 | 75
89 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 10 | 43 | 45 | 45 |  | 5 | Engine problem
90 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 78 | 110 | 68 | 110
91 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18 |  | 2
92 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 13 | 44 | 42 | 43 |  | 7 | Engine problem
93 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 24 | 24
94 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 295 | 300 | 320 |  |  | FGMO
95 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285 MW | 285 | 285 | 212 | 232 | 200 | 220
96 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1879 | 1834 | 1117 | 1437 | 1398 | 1481 | 0 | 14
97 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 32
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 903 | 903 | 903 | 903
| Khulna 115 MW PP (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
98 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 59 | 99 | 115 | 115
99 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 32 | 0 | 42
100 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 200 | 200
101 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 53 | 0 | 75
102 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 300 | 410 | 320 | 410
103 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 40 | 40 | 40 | 40
| Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
104 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 50 | 80 | 100
105 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 89 | 105 | 105 | 105
106 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 87 | 42 | 50 | 100 |  | 5 | Engine problem
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 1478 | 1734 | 1813 | 2122 | 0 | 5
107 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 70 | 110
108 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
109 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 24 | 38 | 25 | 35
110 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 180 | 170 | 180 | 180
111 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 41 | 97 | 50 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 245 | 415 | 325 | 450 | 0 | 0
112 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 55 | 55 | 60 | 60 | 11 |  | Gas Shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
113 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
114 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 25 | 0 | 30
115 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 12 | 50 | 40 | 50
116 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 16 | 50 | 50 | 50
117 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 45 | 47 | 47
118 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 203 | 190 | 215 | 215 |  |  | FGMO
119 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas Shortage
120 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 195 | 191 | 205 | 215 |  |  | FGMO
121 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 0 | 0 | 400 | 400
122 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 29 | 0 | 35
123 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
124 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 14 | 16 | 16 | 15
125 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
126 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 8 | 52 | 52 | 52
127 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 94 | 80 | 100
128 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
129 | Bagura 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 36 | 113 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 569 | 993 | 1561 | 1665 | 231 | 100
130 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 94 | 95 | 98 | 98
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
131 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 270 | 270 | 280 | 280
132 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
133 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 18
| Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 0 | 0 | 35 | 113 | 114 | 114 |  |  | On test
| Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 2.04 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 572 | 492 | 401.04 | 478 | 500 | 510 | 0 | 105
| Total |  |  |  |  | 18969 | 18446 | 8559.16 | 11577 | 13749 | 15416 | 1046 | 1055
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8040.1542 | 10875 | 12915.2954 | 14481.2127
A. |  | 2019-08-23 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 11577 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 8126.4 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11577 | MW
3 | Day peak Generation : |  |  | 8559.16 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10875 | MW
4 | Evening peak Generation : |  |  | 11577 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 233.1527 | MKWHr | By Solar | 0.16198 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 152.1508 | MKWHr |  | By Oil: | 42.3012 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 8.8164 | MKWHr |  | By Hydro: | 4.9462 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1046 | MW | Dhaka | 3553 | 3553 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1055 | MW | Chittagong | 1108 | 1108 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2101 | MW | Khulna | 1393 | 1393 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1326.25 | MMCFD |  |  | Rajshahi | 1207 | 1207 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 146263468.896 | ii) Oil : | Taka | 349981034.52 | Comilla | 1117 | 1117 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 41230686.66 | Total | Taka | 537475190.076 | Mymensingh | 958 | 958 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 1.626 | MKWHr. | Sylhet | 468 | 468 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -301 | MW (E to W) at | 21:00 | hrs | Barisal | 338 | 338 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -301 | MW at | 21:00 | hrs | Rangpur | 733 | 733 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33° C |  |  | Total | 10875 | 10875 |  | 0
B. |  | 2019-08-24 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 33.6° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15416 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9500 | MW
4 | Reserve(Generation end) |  |  |  | 3416 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 241.6716 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8149 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.1396 | MKWHr. | ii) HVDC Flow at Peak Time |  | 903 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.6365 | MKWHr. | iii) Maximum HVDC Flow : |  | 905 | MW at | 6:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 105.34 |  | (b) Today: | 105.47 |  | (c) Rule Curve: |  | 96.36
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-08-23
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence) | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 70 | 168 | 0 | 0 | 340 | 91 | 71 | 355 | 355 |  | 0 | 360 | 280 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 82 | 0 | 72 | 0 | 39 | 53 | 55 | 35 | 22 | 25 | 27 | 33 | 33 | 51 | 0 | 124 | 90 | 100 | 0 | 25 | 185 | 0 | 130 | 0 |  | 0 | 0 | 39 | 10 | 97 | 50 | 22 | 40 | 0 | 0 | 80 | 356 | 305 | 193 | 26 | 138 | 33 | 54 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 33 | 20 | 180 | 157 | 95 | 20 | 0 | 60 | 43 | 50 | 50 | 163 | 146 | 64 | 79 | 43 | 116 | 18 | 46 | 10 | 315 | 16 | 8 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 100 | 200 | 20 | 240 | 115 | 105 | 0 | 0 | 104 | 0 | 50 |  | 776 | 0 | 300 | 0 | 83 | 0 | 0 | 0 | 5 | 51 | 40 | 180 | 38 | 96 | 0 | 0 | 60 | 50 | 0 | 70 | 12 | 50 | 0 | 52 | 21 | 22 | 16 | 11 | 95 | 0 | 270 | 0 | 16 | 199 | 0 | 0 | 0 | 97 | 0 | 199 | 0 | 300 | 105 | 0 | 113 | 87 | 107 | 0 | 0 |  | 7796 | 3521 | 11317 | 4686 | 776 | 2269 | 2493 | 365 | 214 | 334 | 180 | 0 | 0 | 105.34
2:00 | 70 | 168 | 0 | 0 | 340 | 91 | 71 | 350 | 355 |  | 0 | 360 | 275 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 32 | 0 | 72 | 0 | 39 | 35 | 55 | 0 | 22 | 25 | 27 | 33 | 33 | 25 | 0 | 124 | 90 | 100 | 0 | 0 | 185 | 0 | 130 | 0 |  | 0 | 0 | 17 | 10 | 97 | 50 | 22 | 41 | 0 | 0 | 80 | 347 | 290 | 189 | 26 | 138 | 33 | 54 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 33 | 20 | 176 | 158 | 95 | 20 | 0 | 60 | 43 | 28 | 16 | 163 | 145 | 64 | 79 | 40 | 116 | 18 | 45 | 10 | 310 | 16 | 8 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 100 | 200 | 20 | 233 | 115 | 105 | 0 | 0 | 106 | 0 | 50 |  | 776 | 0 | 300 | 0 | 66 | 0 | 0 | 0 | 0 | 51 | 40 | 180 | 38 | 64 | 0 | 0 | 60 | 0 | 0 | 48 | 12 | 50 | 0 | 52 | 20 | 22 | 16 | 11 | 95 | 0 | 270 | 0 | 16 | 195 | 0 | 0 | 0 | 97 | 0 | 195 | 0 | 300 | 105 | 0 | 113 | 87 | 107 | 0 | 0 |  | 7509 | 3386 | 10895 | 4638 | 776 | 2205 | 2337 | 365 | 214 | 184 | 176 | 0 | 0 | 105.34
3:00 | 70 | 168 | 0 | 0 | 340 | 91 | 70 | 348 | 355 |  | 0 | 360 | 265 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 32 | 0 | 72 | 0 | 39 | 35 | 17 | 0 | 22 | 25 | 27 | 33 | 33 | 25 | 0 | 126 | 90 | 100 | 0 | 0 | 184 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 62 | 50 | 22 | 41 | 0 | 0 | 80 | 345 | 290 | 180 | 26 | 138 | 33 | 54 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 33 | 20 | 172 | 172 | 95 | 20 | 0 | 60 | 43 | 42 | 25 | 163 | 146 | 64 | 79 | 43 | 110 | 18 | 46 | 10 | 310 | 16 | 8 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 100 | 200 | 20 | 232 | 115 | 105 | 0 | 0 | 107 | 0 | 50 |  | 776 | 0 | 300 | 0 | 49 | 0 | 0 | 0 | 0 | 51 | 24 | 180 | 36 | 64 | 0 | 0 | 60 | 0 | 0 | 48 | 12 | 50 | 0 | 34 | 0 | 22 | 16 | 8 | 95 | 0 | 270 | 0 | 16 | 193 | 0 | 0 | 0 | 97 | 0 | 193 | 0 | 300 | 105 | 0 | 113 | 87 | 107 | 0 | 0 |  | 7368 | 3306 | 10674 | 4625 | 776 | 2229 | 2144 | 365 | 216 | 147 | 172 | 0 | 0 | 105.34
4:00 | 70 | 168 | 0 | 0 | 340 | 91 | 70 | 350 | 355 |  | 0 | 360 | 290 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 39 | 17 | 0 | 0 | 0 | 25 | 27 | 33 | 33 | 0 | 0 | 126 | 90 | 100 | 0 | 0 | 184 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 10 | 50 | 22 | 41 | 0 | 0 | 80 | 345 | 290 | 181 | 26 | 138 | 33 | 54 | 0 | 43 | 0 | 0 | 25 | 19 | 11 | 33 | 20 | 168 | 172 | 95 | 20 | 0 | 60 | 43 | 42 | 50 | 163 | 145 | 64 | 79 | 43 | 110 | 18 | 45 | 10 | 290 | 16 | 8 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 100 | 140 | 0 | 233 | 115 | 105 | 0 | 0 | 107 | 0 | 50 |  | 776 | 0 | 300 | 0 | 49 | 0 | 0 | 0 | 0 | 40 | 0 | 180 | 34 | 48 | 0 | 0 | 60 | 0 | 0 | 48 | 12 | 50 | 0 | 34 | 0 | 22 | 16 | 8 | 95 | 0 | 270 | 0 | 0 | 196 | 0 | 0 | 0 | 96 | 0 | 194 | 0 | 300 | 70 | 0 | 113 | 86 | 107 | 0 | 0 |  | 7075 | 3204 | 10279 | 4610 | 776 | 2230 | 1826 | 365 | 216 | 88 | 168 | 0 | 0 | 105.34
5:00 | 70 | 168 | 0 | 0 | 340 | 91 | 70 | 345 | 358 |  | 0 | 360 | 265 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 39 | 17 | 0 | 0 | 0 | 25 | 27 | 33 | 17 | 0 | 0 | 126 | 90 | 100 | 0 | 0 | 184 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 10 | 30 | 22 | 41 | 0 | 0 | 80 | 345 | 290 | 180 | 26 | 138 | 33 | 54 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 162 | 174 | 95 | 20 | 0 | 60 | 43 | 42 | 50 | 163 | 145 | 64 | 79 | 43 | 110 | 18 | 45 | 10 | 280 | 16 | 8 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 100 | 17 | 0 | 232 | 115 | 70 | 0 | 0 | 107 | 0 | 50 |  | 904 | 0 | 300 | 0 | 49 | 0 | 0 | 0 | 0 | 35 | 0 | 180 | 33 | 48 | 0 | 0 | 60 | 0 | 0 | 24 | 12 | 32 | 0 | 34 | 0 | 22 | 16 | 8 | 95 | 0 | 270 | 0 | 0 | 192 | 0 | 0 | 0 | 96 | 0 | 187 | 0 | 300 | 70 | 0 | 113 | 87 | 76 | 0 | 0 |  | 6757 | 3243 | 10000 | 4578 | 904 | 2222 | 1494 | 365 | 216 | 59 | 162 | 0 | 0 | 105.34
6:00 | 70 | 168 | 0 | 0 | 340 | 12 | 50 | 344 | 358 |  | 0 | 360 | 260 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 17 | 0 | 0 | 0 | 25 | 23 | 33 | 17 | 0 | 0 | 123 | 90 | 100 | 0 | 0 | 184 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 0 | 12 | 22 | 41 | 0 | 0 | 80 | 345 | 290 | 181 | 26 | 138 | 33 | 10 | 0 | 10 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 144 | 188 | 95 | 20 | 0 | 60 | 43 | 11 | 10 | 163 | 145 | 64 | 10 | 10 | 70 | 18 | 20 | 10 | 270 | 16 | 8 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 10 | 17 | 0 | 231 | 115 | 52 | 0 | 0.23 | 107 | 0 | 17 |  | 905 | 0 | 300 | 0 | 16 | 0 | 0 | 0 | 0 | 28 | 0 | 180 | 31 | 48 | 0 | 0 | 60 | 0 | 0 | 24 | 12 | 32 | 0 | 34 | 0 | 22 | 16 | 8 | 95 | 0 | 270 | 0 | 0 | 190 | 0 | 0 | 0 | 63 | 0 | 187 | 0 | 300 | 35 | 0 | 36 | 87 | 34 | 0 | 0 |  | 6028.23 | 3013 | 9041.23 | 4444 | 905 | 1803 | 1115 | 365 | 213 | 52 | 144 | 0.23 | 0 | 105.34
7:00 | 70 | 168 | 0 | 0 | 340 | 12 | 50 | 344 | 303 |  | 0 | 360 | 250 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 17 | 0 | 0 | 0 | 25 | 23 | 33 | 8 | 0 | 0 | 122 | 90 | 100 | 0 | 0 | 185 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 0 | 12 | 22 | 40 | 0 | 0 | 80 | 260 | 250 | 181 | 26 | 137 | 33 | 10 | 0 | 10 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 130 | 188 | 16 | 20 | 0.1 | 60 | 43 | 11 | 10 | 100 | 145 | 64 | 10 | 10 | 68 | 18 | 14 | 10 | 290 | 16 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 2 | 10 | 17 | 0 | 192 | 115 | 53 | 0 | 2 | 53 | 0 | 17 |  | 905 | 0 | 300 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 27 | 48 | 0 | 0 | 60 | 0 | 0 | 0 | 12 | 16 | 0 | 34 | 0 | 22 | 16 | 8 | 95 | 0 | 270 | 0 | 0 | 181 | 0 | 0 | 0 | 55 | 0 | 162 | 0 | 300 | 35 | 0 | 36 | 87 | 35 | 0 | 0 |  | 5561.1 | 2899 | 8460.1 | 4224 | 905 | 1686 | 934 | 365 | 212 | 0 | 130 | 4.1 | 0 | 105.33
8:00 | 70 | 168 | 0 | 0 | 300 | 13 | 50 | 345 | 271 |  | 0 | 360 | 250 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 17 | 0 | 0 | 22 | 25 | 23 | 33 | 8 | 0 | 0 | 121 | 90 | 100 | 0 | 0 | 186 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 0 | 12 | 22 | 31 | 0 | 0 | 80 | 260 | 255 | 181 | 26 | 134 | 33 | 10 | 0 | 10 | 0 | 0 | 0 | 19 | 11 | 33 | 12 | 122 | 189 | 16 | 20 | 0.5 | 60 | 43 | 11 | 10 | 100 | 146 | 50 | 10 | 10 | 68 | 18 | 14 | 10 | 290 | 16 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 9 | 10 | 17 | 0 | 192 | 50 | 53 | 0 | 2.62 | 52 | 0 | 17 |  | 904 | 0 | 270 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 40 | 179 | 25 | 16 | 0 | 0 | 60 | 0 | 0 | 0 | 12 | 16 | 0 | 8 | 0 | 22 | 16 | 8 | 92 | 0 | 270 | 0 | 0 | 174 | 0 | 0 | 0 | 23 | 0 | 157 | 0 | 270 | 53 | 0 | 36 | 87 | 35 | 0 | 1 |  | 5421.12 | 2823 | 8244.12 | 4148 | 904 | 1582 | 902 | 362 | 211 | 0 | 122 | 13.12 | 0 | 105.33
9:00 | 70 | 169 | 0 | 0 | 300 | 12 | 50 | 344 | 274 |  | 0 | 360 | 278 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 17 | 0 | 0 | 22 | 25 | 23 | 0 | 24 | 0 | 0 | 122 | 90 | 100 | 0 | 0 | 184 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 0 | 12 | 22 | 31 | 0 | 0 | 80 | 260 | 250 | 182 | 26 | 138 | 33 | 10 | 0 | 10 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 122 | 186 | 24 | 20 | 0.4 | 60 | 43 | 11 | 10 | 100 | 146 | 62 | 10 | 10 | 67 | 18 | 14 | 10 | 280 | 16 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 15 | 10 | 17 | 0 | 193 | 50 | 53 | 0 | 3 | 52 | 0 | 17 |  | 904 | 0 | 270 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 40 | 179 | 15 | 16 | 0 | 0 | 60 | 0 | 0 | 0 | 12 | 16 | 0 | 8 | 0 | 22 | 16 | 8 | 94 | 0 | 270 | 0 | 0 | 170 | 0 | 0 | 0 | 42 | 0 | 156 | 0 | 133 | 53 | 0 | 36 | 87 | 35 | 0 | 4 |  | 5431.4 | 2695 | 8126.4 | 4139 | 904 | 1446 | 917 | 364 | 212 | 0 | 122 | 22.4 | 0 | 105.33
10:00 | 70 | 169 | 0 | 0 | 300 | 12 | 50 | 354 | 273 |  | 0 | 360 | 292 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 17 | 0 | 0 | 22 | 25 | 22 | 0 | 24 | 0 | 0 | 122 | 90 | 100 | 0 | 0 | 206 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 0 | 12 | 22 | 31 | 0 | 0 | 80 | 280 | 270 | 197 | 26 | 138 | 33 | 10 | 0 | 10 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 122 | 185 | 49 | 20 | 1.2 | 60 | 43 | 13 | 10 | 100 | 144 | 61 | 10 | 10 | 68 | 18 | 14 | 10 | 310 | 16 | 8 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 12 | 10 | 17 | 0 | 202 | 0 | 53 | 0 | 5 | 52 | 0 | 17 |  | 903 | 0 | 270 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 40 | 179 | 23 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 12 | 16 | 0 | 8 | 0 | 22 | 16 | 8 | 95 | 0 | 270 | 0 | 0 | 171 | 0 | 0 | 0 | 42 | 0 | 167 | 0 | 0 | 53 | 0 | 36 | 87 | 35 | 0 | 3 |  | 5554.2 | 2565 | 8119.2 | 4252 | 903 | 1352 | 892 | 365 | 212 | 0 | 122 | 21.2 | 0 | 105.34
11:00 | 70 | 169 | 0 | 0 | 300 | 13 | 50 | 351 | 273 |  | 0 | 360 | 277 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 17 | 0 | 0 | 22 | 25 | 22 | 21 | 24 | 0 | 0 | 124 | 90 | 100 | 0 | 0 | 205 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 0 | 12 | 22 | 31 | 0 | 0 | 80 | 275 | 265 | 193 | 26 | 138 | 33 | 10 | 0 | 10 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 124 | 184 | 68 | 20 | 0 | 60 | 43 | 11 | 10 | 100 | 144 | 61 | 10 | 10 | 68 | 18 | 13 | 10 | 315 | 16 | 8 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 11 | 10 | 17 | 0 | 200 | 0 | 53 | 0 | 4 | 52 | 0 | 17 |  | 904 | 0 | 270 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 40 | 179 | 23 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 16 | 0 | 8 | 0 | 22 | 10 | 8 | 94 | 0 | 270 | 0 | 0 | 182 | 0 | 0 | 0 | 41 | 0 | 165 | 0 | 0 | 53 | 0 | 36 | 87 | 35 | 0 | 4 |  | 5598 | 2563 | 8161 | 4256 | 904 | 1348 | 932 | 364 | 214 | 0 | 124 | 19 | 0 | 105.34
12:00 | 70 | 169 | 0 | 0 | 300 | 13 | 50 | 353 | 303 |  | 0 | 360 | 282 | 0 | 0 | 0 | 10 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 17 | 0 | 0 | 22 | 25 | 17 | 33 | 24 | 0 | 0 | 126 | 90 | 100 | 0 | 0 | 211 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 0 | 12 | 22 | 31 | 0 | 0 | 80 | 360 | 353 | 199 | 26 | 138 | 33 | 10 | 0 | 10 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 128 | 173 | 74 | 20 | 0 | 60 | 43 | 11 | 10 | 100 | 147 | 61 | 10 | 10 | 78 | 18 | 13 | 10 | 310 | 16 | 8 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 14 | 10 | 17 | 0 | 212 | 0 | 53 | 0 | 4.12 | 52 | 0 | 17 |  | 903 | 0 | 300 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 40 | 180 | 24 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 16 | 0 | 8 | 0 | 22 | 14 | 8 | 94 | 0 | 270 | 0 | 0 | 203 | 0 | 0 | 0 | 41 | 0 | 195 | 0 | 0 | 89 | 0 | 36 | 87 | 35 | 0 | 2.04 |  | 5866.12 | 2693.04 | 8559.16 | 4556 | 903 | 1378 | 994 | 364 | 216 | 0 | 128 | 20.16 | 0 | 105.35
13:00 | 70 | 169 | 0 | 0 | 300 | 13 | 50 | 372 | 303 |  | 0 | 360 | 281 | 0 | 0 | 0 | 13 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 17 | 0 | 0 | 22 | 25 | 14 | 33 | 24 | 0 | 0 | 126 | 90 | 100 | 0 | 0 | 208 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 12 | 22 | 31 | 0 | 0 | 80 | 360 | 330 | 201 | 26 | 138 | 33 | 10 | 0 | 10 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 130 | 172 | 82 | 20 | 1 | 60 | 43 | 11 | 10 | 130 | 146 | 61 | 10 | 10 | 77 | 18 | 13 | 10 | 320 | 16 | 8 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 5 | 10 | 17 | 0 | 243 | 0 | 53 | 0 | 4 | 52 | 0 | 17 |  | 903 | 0 | 300 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 40 | 180 | 26 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 32 | 0 | 24 | 0 | 22 | 16 | 8 | 95 | 0 | 270 | 0 | 0 | 199 | 0 | 0 | 0 | 42 | 0 | 207 | 0 | 0 | 88 | 0 | 36 | 87 | 35 | 0 | 3 |  | 6001 | 2746 | 8747 | 4658 | 903 | 1423 | 1039 | 365 | 216 | 0 | 130 | 13 | 0 | 105.35
14:00 | 70 | 169 | 0 | 0 | 300 | 0 | 0 | 350 | 303 |  | 0 | 360 | 275 | 0 | 0 | 0 | 22 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 17 | 0 | 0 | 22 | 25 | 14 | 33 | 24 | 0 | 0 | 126 | 90 | 100 | 0 | 0 | 204 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 12 | 22 | 31 | 0 | 0 | 80 | 340 | 315 | 190 | 26 | 138 | 33 | 10 | 0 | 10 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 134 | 169 | 82 | 20 | 1.8 | 60 | 43 | 11 | 10 | 130 | 148 | 61 | 10 | 10 | 80 | 18 | 13 | 10 | 300 | 16 | 8 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 10 | 10 | 17 | 0 | 245 | 37 | 53 | 0 | 5.15 | 52 | 0 | 17 |  | 903 | 0 | 300 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 40 | 180 | 26 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 32 | 0 | 25 | 0 | 22 | 16 | 8 | 95 | 0 | 270 | 0 | 0 | 185 | 0 | 0 | 0 | 42 | 0 | 203 | 0 | 0 | 88 | 0 | 36 | 86 | 35 | 0 | 1.6 |  | 5900.95 | 2726.6 | 8627.55 | 4581 | 903 | 1340 | 1070 | 365 | 216 | 0 | 134 | 18.55 | 0 | 105.36
15:00 | 70 | 169 | 0 | 0 | 300 | 0 | 0 | 375 | 347 |  | 0 | 360 | 282 | 0 | 0 | 0 | 32 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 17 | 0 | 0 | 22 | 25 | 14 | 33 | 25 | 0 | 0 | 121 | 90 | 100 | 0 | 0 | 206 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 12 | 22 | 40 | 0 | 0 | 80 | 360 | 320 | 187 | 26 | 138 | 33 | 30 | 0 | 10 | 0 | 0 | 0 | 18 | 11 | 33 | 20 | 144 | 172 | 82 | 20 | 0.9 | 60 | 43 | 11 | 10 | 163 | 148 | 60 | 10 | 43 | 97 | 18 | 40 | 10 | 330 | 16 | 8 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 12 | 10 | 17 | 0 | 239 | 98 | 53 | 0 | 1.11 | 52 | 0 | 17 |  | 903 | 0 | 330 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 40 | 180 | 27 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 32 | 0 | 25 | 0 | 22 | 16 | 8 | 95 | 0 | 270 | 0 | 0 | 202 | 0 | 0 | 0 | 47 | 0 | 207 | 0 | 0 | 88 | 0 | 36 | 86 | 41 | 0 | 0.7 |  | 6277.01 | 2788.7 | 9065.71 | 4742 | 903 | 1542 | 1144 | 365 | 211 | 0 | 144 | 14.71 | 0 | 105.36
16:00 | 70 | 169 | 0 | 0 | 300 | 13 | 0 | 374 | 348 |  | 0 | 360 | 280 | 0 | 0 | 0 | 40 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 18 | 17 | 0 | 0 | 22 | 25 | 14 | 33 | 25 | 0 | 0 | 119 | 90 | 100 | 0 | 0 | 205 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 12 | 22 | 40 | 0 | 0 | 80 | 270 | 305 | 189 | 8 | 138 | 33 | 30 | 0 | 10 | 0 | 0 | 0 | 18 | 11 | 33 | 20 | 140 | 122 | 90 | 20 | 0.3 | 60 | 43 | 24 | 17 | 163 | 145 | 61 | 10 | 43 | 89 | 18 | 42 | 10 | 320 | 24 | 8 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 5 | 10 | 17 | 0 | 234 | 101 | 53 | 0 | 1.4 | 53 | 0 | 17 |  | 903 | 0 | 330 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 32 | 174 | 25 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 32 | 0 | 25 | 0 | 22 | 16 | 8 | 94 | 0 | 270 | 0 | 0 | 198 | 0 | 0 | 0 | 50 | 0 | 206 | 0 | 0 | 88 | 0 | 36 | 86 | 45 | 0 | 2 |  | 6121.7 | 2775 | 8896.7 | 4601 | 903 | 1551 | 1120 | 364 | 209 | 0 | 140 | 8.7 | 0 | 105.36
17:00 | 70 | 169 | 0 | 0 | 250 | 13 | 0 | 352 | 303 |  | 0 | 360 | 281 | 0 | 0 | 0 | 32 | 0 | 123 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 17 | 0 | 0 | 22 | 25 | 14 | 33 | 29 | 0 | 0 | 119 | 90 | 100 | 0 | 0 | 204 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 0 | 12 | 22 | 41 | 0 | 0 | 80 | 270 | 270 | 187 | 8 | 137 | 33 | 30 | 0 | 10 | 0 | 0 | 0 | 17 | 11 | 33 | 20 | 134 | 140 | 82 | 20 | 0.2 | 60 | 43 | 47 | 49 | 100 | 144 | 62 | 10 | 43 | 89 | 18 | 41 | 10 | 290 | 24 | 8 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 2 | 10 | 17 | 0 | 234 | 108 | 53 | 0 | 0 | 53 | 0 | 17 |  | 903 | 0 | 300 | 0 | 16 | 0 | 0 | 0 | 0 | 30 | 32 | 174 | 25 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 32 | 0 | 8 | 0 | 22 | 16 | 8 | 93 | 0 | 270 | 0 | 0 | 180 | 0 | 0 | 0 | 50 | 0 | 175 | 0 | 0 | 53 | 0 | 37 | 86 | 35 | 0 | 0.2 |  | 5847.2 | 2612.2 | 8459.4 | 4337 | 903 | 1468 | 1013 | 363 | 209 | 30 | 134 | 2.4 | 0 | 105.37
18:00 | 70 | 169 | 0 | 0 | 240 | 16 | 0 | 270 | 273 |  | 0 | 360 | 265 | 0 | 0 | 0 | 32 | 0 | 101 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 17 | 0 | 0 | 22 | 25 | 14 | 33 | 29 | 0 | 0 | 119 | 90 | 100 | 0 | 0 | 204 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 0 | 12 | 22 | 40 | 0 | 0 | 80 | 270 | 270 | 155 | 8 | 140 | 33 | 30 | 0 | 10 | 0 | 0 | 0 | 18 | 11 | 33 | 20 | 126 | 143 | 90 | 20 | 0 | 60 | 43 | 50 | 46 | 100 | 145 | 63 | 10 | 43 | 71 | 18 | 41 | 10 | 280 | 24 | 8 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 10 | 17 | 0 | 232 | 108 | 53 | 0 | 0 | 53 | 0 | 17 |  | 903 | 0 | 230 | 0 | 16 | 0 | 0 | 0 | 30 | 35 | 32 | 173 | 25 | 16 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 32 | 0 | 8 | 0 | 22 | 16 | 8 | 93 | 0 | 270 | 0 | 0 | 166 | 0 | 0 | 0 | 45 | 0 | 156 | 0 | 0 | 53 | 0 | 37 | 86 | 35 | 0 | 0 |  | 5634 | 2554 | 8188 | 4076 | 903 | 1425 | 1021 | 363 | 209 | 65 | 126 | 0 | 0 | 105.37
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 70 | 169 | 0 | 0 | 350 | 12 | 0 | 300 | 303 |  | 0 | 360 | 268 | 4 | 5 | 15 | 52 | 0 | 155 | 0 | 2 | 16 | 60 | 10 | 67 | 0 | 18 | 53 | 55 | 17 | 22 | 25 | 14 | 33 | 29 | 36 | 0 | 119 | 90 | 100 | 0 | 25 | 204 | 0 | 130 | 0 |  | 0 | 0 | 85 | 10 | 12 | 38 | 22 | 38 | 0 | 0 | 80 | 310 | 300 | 180 | 8 | 138 | 33 | 30 | 0 | 10 | 0 | 0 | 21 | 18 | 5 | 33 | 20 | 170 | 181 | 90 | 20 | 0 | 60 | 43 | 50 | 46 | 163 | 144 | 63 | 79 | 43 | 102 | 18 | 46 | 10 | 310 | 24 | 8 | 0 | 12 | 0 | 0 | 65 | 0 | 17 | 0 | 76 | 75 | 6 | 232 | 115 | 89 | 17 | 0 | 103 | 0 | 17 |  | 903 | 0 | 410 | 0 | 66 | 0 | 0 | 0 | 32 | 60 | 32 | 174 | 28 | 110 | 0 | 0 | 55 | 42 | 10 | 50 | 50 | 50 | 40 | 39 | 15 | 22 | 16 | 8 | 94 | 0 | 270 | 0 | 15 | 189 | 0 | 0 | 0 | 81 | 22 | 184 | 0 | 0 | 88 | 0 | 75 | 82 | 95 | 0 | 0 |  | 7073 | 3407 | 10480 | 4707 | 903 | 1655 | 2063 | 364 | 209 | 409 | 170 | 0 | 0 | 105.37
19:30 | 70 | 169 | 0 | 0 | 350 | 0 | 0 | 344 | 303 |  | 0 | 360 | 245 | 20 | 15 | 30 | 52 | 0 | 100 | 0 | 0 | 64 | 149 | 0 | 72 | 0 | 23 | 53 | 55 | 17 | 22 | 25 | 14 | 33 | 29 | 51 | 0 | 119 | 90 | 100 | 0 | 25 | 204 | 0 | 130 | 0 |  | 0 | 0 | 85 | 10 | 40 | 39 | 22 | 38 | 0 | 0 | 80 | 340 | 305 | 179 | 8 | 135 | 33 | 30 | 0 | 30 | 0 | 0 | 52 | 19 | 5 | 33 | 20 | 174 | 204 | 90 | 20 | 0 | 60 | 43 | 50 | 49 | 100 | 144 | 50 | 79 | 43 | 102 | 18 | 44 | 10 | 280 | 24 | 8 | 0 | 15 | 0 | 0 | 170 | 0 | 70 | 0 | 90 | 200 | 50 | 231 | 115 | 89 | 17 | 0 | 140 | 0 | 17 |  | 904 | 0 | 380 | 0 | 99 | 0 | 0 | 0 | 33 | 56 | 32 | 162 | 36 | 110 | 0 | 0 | 55 | 50 | 21 | 94 | 50 | 50 | 46 | 52 | 18 | 22 | 16 | 11 | 94 | 0 | 270 | 0 | 0 | 206 | 0 | 0 | 0 | 90 | 50 | 187 | 0 | 0 | 100 | 0 | 108 | 70 | 100 | 0 | 0 |  | 7632 | 3572 | 11204 | 4718 | 904 | 1588 | 2695 | 364 | 209 | 552 | 174 | 0 | 0 | 0
20:00 | 70 | 169 | 0 | 0 | 350 | 12 | 0 | 345 | 303 |  | 0 | 360 | 264 | 30 | 15 | 15 | 52 | 0 | 100 | 0 | 0 | 64 | 149 | 0 | 72 | 0 | 47 | 53 | 55 | 17 | 22 | 25 | 29 | 33 | 29 | 51 | 0 | 119 | 90 | 100 | 0 | 25 | 204 | 0 | 130 | 0 |  | 0 | 0 | 85 | 10 | 42 | 42 | 22 | 37 | 0 | 0 | 80 | 340 | 305 | 179 | 8 | 140 | 33 | 55 | 0 | 43 | 0 | 0 | 52 | 19 | 5 | 33 | 20 | 176 | 205 | 90 | 20 | 0 | 60 | 43 | 50 | 49 | 100 | 145 | 63 | 79 | 43 | 110 | 18 | 46 | 10 | 270 | 24 | 8 | 0 | 40 | 0 | 0 | 150 | 0 | 82 | 0 | 90 | 198 | 50 | 232 | 115 | 89 | 17 | 0 | 140 | 0 | 17 |  | 903 | 0 | 360 | 0 | 99 | 0 | 0 | 0 | 32 | 55 | 32 | 168 | 36 | 110 | 0 | 0 | 55 | 50 | 39 | 94 | 50 | 50 | 47 | 52 | 30 | 22 | 16 | 11 | 94 | 0 | 270 | 0 | 0 | 201 | 0 | 0 | 0 | 94 | 50 | 187 | 0 | 0 | 105 | 0 | 110 | 69 | 109 | 0 | 0 |  | 7778 | 3600 | 11378 | 4744 | 903 | 1633 | 2768 | 364 | 209 | 581 | 176 | 0 | 0 | 105.38
21:00 | 70 | 209 | 0 | 0 | 380 | 12 | 50 | 346 | 351 |  | 0 | 360 | 270 | 0 | 0 | 0 | 52 | 0 | 180 | 0 | 0 | 7 | 130 | 0 | 72 | 0 | 47 | 53 | 55 | 17 | 22 | 25 | 29 | 33 | 29 | 51 | 0 | 122 | 90 | 100 | 0 | 25 | 204 | 0 | 130 | 0 |  | 0 | 0 | 85 | 10 | 44 | 48 | 22 | 39 | 0 | 0 | 80 | 345 | 305 | 179 | 8 | 138 | 33 | 55 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 33 | 20 | 178 | 205 | 89 | 20 | 0 | 60 | 43 | 50 | 49 | 163 | 145 | 64 | 79 | 43 | 110 | 18 | 44 | 10 | 295 | 24 | 8 | 0 | 0 | 0 | 0 | 150 | 0 | 53 | 0 | 90 | 200 | 50 | 232 | 115 | 106 | 17 | 0 | 140 | 0 | 17 |  | 903 | 0 | 410 | 0 | 99 | 0 | 0 | 0 | 32 | 53 | 40 | 170 | 38 | 110 | 0 | 0 | 55 | 50 | 25 | 94 | 50 | 50 | 45 | 52 | 29 | 22 | 16 | 11 | 95 | 0 | 270 | 0 | 0 | 190 | 0 | 0 | 0 | 97 | 50 | 191 | 0 | 0 | 105 | 0 | 113 | 42 | 113 | 0 | 0 |  | 7957 | 3620 | 11577 | 4950 | 903 | 1824 | 2602 | 365 | 212 | 543 | 178 | 0 | 0 | 105.38
22:00 | 70 | 209 | 0 | 0 | 380 | 12 | 50 | 345 | 354 |  | 0 | 360 | 260 | 0 | 0 | 0 | 52 | 0 | 145 | 0 | 0 | 7 | 64 | 0 | 72 | 0 | 47 | 53 | 55 | 17 | 22 | 25 | 31 | 33 | 29 | 51 | 0 | 122 | 90 | 100 | 0 | 25 | 204 | 0 | 130 | 0 |  | 0 | 0 | 85 | 10 | 44 | 50 | 22 | 42 | 0 | 0 | 80 | 345 | 305 | 180 | 8 | 133 | 33 | 53 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 33 | 20 | 180 | 203 | 90 | 20 | 0 | 60 | 43 | 50 | 49 | 130 | 144 | 64 | 79 | 43 | 110 | 18 | 46 | 10 | 290 | 24 | 8 | 0 | 0 | 0 | 0 | 150 | 0 | 15 | 0 | 90 | 200 | 50 | 232 | 115 | 106 | 17 | 0 | 143 | 0 | 17 |  | 904 | 0 | 410 | 0 | 99 | 0 | 0 | 0 | 27 | 47 | 40 | 172 | 39 | 110 | 23 | 0 | 60 | 50 | 0 | 94 | 50 | 50 | 45 | 43 | 20 | 22 | 16 | 11 | 95 | 0 | 269 | 0 | 0 | 182 | 0 | 0 | 0 | 97 | 76 | 188 | 0 | 95 | 105 | 0 | 113 | 17 | 107 | 0 | 0 |  | 7778 | 3676 | 11454 | 4905 | 904 | 1888 | 2546 | 364 | 212 | 455 | 180 | 0 | 0 | 105.38
23:00 | 70 | 200 | 0 | 0 | 380 | 12 | 40 | 346 | 351 |  | 0 | 360 | 281 | 0 | 0 | 0 | 49 | 0 | 145 | 0 | 0 | 7 | 32 | 0 | 72 | 0 | 47 | 35 | 35 | 17 | 22 | 25 | 31 | 33 | 29 | 51 | 0 | 126 | 90 | 100 | 0 | 25 | 208 | 0 | 130 | 0 |  | 0 | 0 | 66 | 10 | 44 | 50 | 22 | 42 | 0 | 0 | 80 | 350 | 330 | 193 | 8 | 138 | 33 | 55 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 33 | 20 | 178 | 188 | 90 | 20 | 0 | 60 | 43 | 50 | 49 | 130 | 147 | 64 | 79 | 43 | 123 | 18 | 45 | 10 | 290 | 24 | 8 | 0 | 0 | 0 | 0 | 150 | 0 | 15 | 0 | 90 | 200 | 0 | 235 | 115 | 105 | 0 | 0 | 143 | 0 | 17 |  | 902 | 16 | 410 | 0 | 99 | 0 | 0 | 0 | 25 | 47 | 40 | 172 | 38 | 110 | 23 | 0 | 60 | 0 | 0 | 94 | 12 | 50 | 45 | 43 | 20 | 22 | 16 | 11 | 94 | 0 | 270 | 0 | 0 | 181 | 0 | 0 | 0 | 96 | 97 | 193 | 0 | 94 | 105 | 0 | 113 | 17 | 99 | 0 | 0 |  | 7677 | 3614 | 11291 | 4954 | 902 | 1873 | 2436 | 364 | 216 | 368 | 178 | 0 | 0 | 105.38
24:00 | 70 | 198 | 0 | 0 | 380 | 12 | 40 | 356 | 357 |  | 0 | 360 | 246 | 0 | 0 | 0 | 48 | 0 | 140 | 0 | 0 | 0 | 32 | 0 | 72 | 0 | 47 | 35 | 17 | 17 | 22 | 25 | 31 | 33 | 29 | 51 | 0 | 126 | 90 | 100 | 0 | 25 | 204 | 0 | 130 | 0 |  | 0 | 0 | 42 | 10 | 44 | 50 | 22 | 42 | 0 | 0 | 80 | 345 | 310 | 180 | 8 | 132 | 33 | 56 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 33 | 20 | 174 | 204 | 90 | 20 | 0 | 60 | 43 | 50 | 50 | 130 | 144 | 65 | 79 | 45 | 110 | 18 | 35 | 10 | 295 | 24 | 8 | 0 | 0 | 0 | 0 | 150 | 0 | 15 | 0 | 100 | 200 | 0 | 232 | 115 | 105 | 0 | 0 | 143 | 0 | 17 |  | 903 | 16 | 410 | 0 | 115 | 0 | 0 | 0 | 25 | 47 | 40 | 161 | 38 | 110 | 0 | 0 | 60 | 0 | 0 | 93 | 12 | 50 | 45 | 43 | 20 | 22 | 16 | 11 | 94 | 0 | 270 | 0 | 0 | 177 | 0 | 0 | 0 | 97 | 100 | 186 | 0 | 223 | 105 | 0 | 113 | 35 | 114 | 0 | 0 |  | 7556 | 3751 | 11307 | 4884 | 903 | 2008 | 2438 | 364 | 216 | 320 | 174 | 0 | 0 | 105.38
KWH | 1520000 | 4430000 | 0 | 0 | 7747564 | 740181 | 1022336 | 8502270 | 7648000 |  | 0 | 8113750 | 6631360 | 42240 | 24864 | 63450 | 481746 | 0 | 3163000 | 0 | 7680 | 137520 | 689760 | 13431 | 723840 | 0 | 795504 | 703800 | 405502 | 176104 | 424728 | 600000 | 529740 | 744700 | 643000 | 422004 | 0 | 2774176 | 2172000 | 2400000 | 0 | 188929 | 4746346 | 0 | 2916550 | 0 |  | 0 | 0 | 497444 | 257760 | 541440 | 676320 | 515616 | 878880 | 0 | 0 | 1913438 | 8029300 | 7139000 | 4510000 | 485090 | 3270220 | 764784 | 852480 | 0 | 696952 | 0 | 0 | 471398 | 442332 | 241560 | 817900 | 481800 | 3636480 | 4067440 | 1884480 | 459972 | 6900 | 1421000 | 1032000 | 746400 | 75996 | 3424533 | 3280000 | 1480608 | 1057920 | 733320 | 2298190 | 441320 | 779720 | 250920 | 7447500 | 443064 | 183360 | 0 | 57709 | 0 | 0 | 1747200 | 0 | 231840 | 102330 | 1151040 | 2148480 | 272654 | 5469000 | 2052000 | 1069752 | 71927 | 30240 | 2057454 | 0 | 600506 |  | 21139636 | 25600 | 8032896 | 0 | 1435200 | 0 | 0 | 0 | 202080 | 607744 | 726750 | 4342441 | 710285 | 1118400 | 47250 | 0 | 1375000 | 273571 | 69885 | 765744 | 452480 | 874755 | 228775 | 684480 | 159912 | 512640 | 365328 | 211068 | 2268218 | 0 | 6548200 | 0 | 66000 | 4864800 | 0 | 0 | 0 | 1602741 | 427200 | 4694518 | 0 | 2933545 | 2142720 | 0 | 1749696 | 1812816 | 1614720 | 0 | 22515 |  | 158043044 | 75109609 | 233152653 | 111072271 | 21139636 | 41078517 | 38667405 | 8816418 | 4946176 | 3633765 | 3636480 | 161985 | 0
Fuel Cost | 1702400 | 4784400 | 0 | 0 | 5733197.36 | 717975.57 | 1492610.56 | 6121634.4 | 5812480 |  | 0 | 6491000 | 5968224 | 430848 | 269277.12 | 650997 | 597365.04 | 0 | 3953750 | 0 | 85248 | 1397203.2 | 6835521.6 | 140756.88 | 6586944 | 0 | 7445917.44 | 6749442 | 3868489.08 | 1753995.84 | 318546 | 450000 | 0 | 0 | 0 | 4042798.32 | 0 | 721285.76 | 564720 | 3672000 | 0 | 1815607.69 | 4983663.3 | 0 | 3704018.5 | 0 |  | 0 | 0 | 5218187.56 | 2652350.4 | 5149094.4 | 6330355.2 | 474366.72 | 2443286.4 | 0 | 0 | 2009109.9 | 5941682 | 5996760 | 4149200 | 475388.2 | 4349392.6 | 627122.88 | 878054.4 | 0 | 996641.36 | 0 | 0 | 4431141.2 | 451178.64 | 181170 | 1545831 | 361350 | 25091712 | 3335300.8 | 17921404.8 | 469171.44 | 113160 | 1932560 | 1403520 | 1015104 | 94995 | 4246420.92 | 3017600 | 2206105.92 | 1861939.2 | 813985.2 | 3493248.8 | 701698.8 | 912272.4 | 589662 | 5287725 | 332298 | 139353.6 | 0 | 604213.23 | 0 | 0 | 16808064 | 0 | 2339265.6 | 1180888.2 | 10727692.8 | 20152742.4 | 2554767.98 | 5140860 | 17996040 | 9531490.32 | 679710.15 | 0 | 18969725.88 | 0 | 0 |  | 57077017.2 | 748800 | 6265658.88 | 0 | 13835328 | 0 | 0 | 0 | 2344128 | 7961446.4 | 7187557.5 | 3473952.8 | 1100941.75 | 12011616 | 1566337.5 | 0 | 2585000 | 3047580.94 | 856091.25 | 7580865.6 | 4692217.6 | 10243381.05 | 2756738.75 | 6817420.8 | 1575133.2 | 563904 | 602791.2 | 159778.476 | 14448548.66 | 0 | 26782138 | 0 | 1863180 | 4281024 | 0 | 0 | 0 | 2548358.19 | 7219680 | 4131175.84 | 0 | 2141487.85 | 20270131.2 | 0 | 16062209.28 | 16152190.56 | 15081484.8 | 0 | 0 |  | 336188677.96 | 286035295.276 | 622223973.236 | 105176445.696 | 57077017.2 | 41087023.2 | 307627023.72 | 41230686.66 | 1286005.76 | 42354010.8 | 25091712 | 1294048.2 | 0
Yesterday Day Peak | 70 | 169 | 0 | 0 | 300 | 13 | 50 | 353 | 303 |  | 0 | 360 | 282 | 0 | 0 | 0 | 10 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 17 | 0 | 0 | 22 | 25 | 17 | 33 | 24 | 0 | 0 | 126 | 90 | 100 | 0 | 0 | 211 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 0 | 12 | 22 | 31 | 0 | 0 | 80 | 360 | 353 | 199 | 26 | 138 | 33 | 10 | 0 | 10 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 128 | 173 | 74 | 20 | 0 | 60 | 43 | 11 | 10 | 100 | 147 | 61 | 10 | 10 | 78 | 18 | 13 | 10 | 310 | 16 | 8 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 14 | 10 | 17 | 0 | 212 | 0 | 53 | 0 | 4.12 | 52 | 0 | 17 |  | 903 | 0 | 300 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 40 | 180 | 24 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 16 | 0 | 8 | 0 | 22 | 14 | 8 | 94 | 0 | 270 | 0 | 0 | 203 | 0 | 0 | 0 | 41 | 0 | 195 | 0 | 0 | 89 | 0 | 36 | 87 | 35 | 0 | 2.04 |  | 8559.16 | DayPeak
Yesterday Evening Peak | 70 | 209 | 0 | 0 | 380 | 12 | 50 | 346 | 351 | 0 | 0 | 360 | 270 | 0 | 0 | 0 | 52 | 0 | 180 | 0 | 0 | 7 | 130 | 0 | 72 | 0 | 47 | 53 | 55 | 17 | 22 | 25 | 29 | 33 | 29 | 51 | 0 | 122 | 90 | 100 | 0 | 25 | 204 | 0 | 130 | 0 | 0 | 0 | 0 | 85 | 10 | 44 | 48 | 22 | 39 | 0 | 0 | 80 | 345 | 305 | 179 | 8 | 138 | 33 | 55 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 33 | 20 | 178 | 205 | 89 | 20 | 0 | 60 | 43 | 50 | 49 | 163 | 145 | 64 | 79 | 43 | 110 | 18 | 44 | 10 | 295 | 24 | 8 | 0 | 0 | 0 | 0 | 150 | 0 | 53 | 0 | 90 | 200 | 50 | 232 | 115 | 106 | 17 | 0 | 140 | 0 | 17 |  | 903 | 0 | 410 | 0 | 99 | 0 | 0 | 0 | 32 | 53 | 40 | 170 | 38 | 110 | 0 | 0 | 55 | 50 | 25 | 94 | 50 | 50 | 45 | 52 | 29 | 22 | 16 | 11 | 95 | 0 | 270 | 0 | 0 | 190 | 0 | 0 | 0 | 97 | 50 | 191 | 0 | 0 | 105 | 0 | 113 | 42 | 113 | 0 | 0 |  | 11577 | EvPeak
Forecast for Evening | 70 | 190 | 0 | 0 | 350 | 90 | 78 | 350 | 350 | 0 | 0 | 360 | 280 | 100 | 100 | 55 | 40 | 0 | 200 | 0 | 100 | 100 | 149 | 100 | 72 | 0 | 46 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 125 | 90 | 100 | 0 | 25 | 215 | 0 | 130 | 0 | 0 | 0 | 0 | 85 | 100 | 97 | 50 | 22 | 40 | 0 | 0 | 100 | 360 | 360 | 225 | 68 | 140 | 33 | 55 | 0 | 43 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 191 | 204 | 95 | 20 | 0 | 60 | 58 | 51 | 50 | 163 | 160 | 63 | 75 | 45 | 110 | 18 | 43 | 10 | 320 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 220 | 115 | 100 | 100 | 0 | 260 |  | 113 |  | 903 | 32 | 410 | 0 | 115 | 200 | 0 | 0 | 42 | 75 | 40 | 180 | 35 | 110 | 30 | 0 | 60 | 50 | 30 | 100 | 50 | 50 | 47 | 52 | 35 | 22 | 15 | 11 | 98 | 0 | 280 | 0 | 18 | 215 | 0 | 0 | 0 | 95 | 100 | 215 | 0 | 400 | 105 | 200 | 113 | 100 | 114 | 0
Forecast for Day | 70 | 190 | 0 | 0 | 350 | 90 | 78 | 350 | 350 | 0 | 0 | 360 | 280 | 100 | 100 | 55 | 20 | 0 | 200 | 0 | 100 | 100 | 149 | 100 | 72 | 0 | 46 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 125 | 90 | 100 | 0 | 25 | 215 | 0 | 130 | 0 | 0 | 0 | 0 | 50 | 100 | 95 | 50 | 22 | 30 | 0 | 0 | 100 | 360 | 360 | 225 | 68 | 140 | 33 | 30 | 0 | 43 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 151 | 204 | 95 | 20 | 1.6 | 60 | 58 | 51 | 50 | 163 | 160 | 63 | 75 | 45 | 68 | 18 | 42 | 10 | 300 | 24 | 11 | 0 | 200 | 0 | 0 | 200 | 0 | 149 | 20 | 100 | 200 | 150 | 200 | 115 | 100 | 50 | 4.4 | 230 |  | 113 |  | 903 | 0 | 320 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 180 | 25 | 70 | 0 | 0 | 60 | 50 | 0 | 80 | 40 | 50 | 47 | 52 | 0 | 22 | 16 | 11 | 98 | 0 | 280 | 0 | 0 | 215 | 0 | 0 | 0 | 50 | 80 | 205 | 0 | 400 | 105 | 100 | 113 | 50 | 114 | 0 | 8
Generation at 08:00(Today) | 70 | 158 | 0 | 0 | 280 | 12 | 40 | 347 | 282 | 0 | 0 | 330 | 282 | 0 | 0 | 0 | 48 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 24 | 17 | 0 | 0 | 22 | 25 | 24 | 33 | 29 | 0 | 0 | 126 | 90 | 100 | 0 | 0 | 204 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 6 | 22 | 8 | 0 | 0 | 80 | 360 | 275 | 189 | 8 | 90 | 33 | 30 | 0 | 5 | 0 | 0 | 8 | 19 | 11 | 33 | 18 | 92 | 203 | 0 | 20 | 0.7 | 60 | 43 | 5 | 5 | 100 | 147 | 64 | 10 | 5 | 61 | 18 | 14 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 3 | 10 | 50 | 0 | 238 | 80 | 52 | 0 | 1.02 | 16 | 0 | 17 | 0 | 891 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 23 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 12 | 16 | 0 | 0 | 0 | 22 | 16 | 5 | 95 | 0 | 270 | 0 | 0 | 177 | 0 | 0 | 0 | 64 | 0 | 163 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 8126.4 | 9:00
| Highest Generation |  | 11577 | 21:00
| Day Peak Generation |  | 8559.16 | 12:00
| Evening Peak Generation |  | 11577 | 21:00
| HVDC Max Flow |  | 905 | 6:00
| HVDC EvPeak Flow |  | 903 | 21:00
| Load factor L.F |  | 83.91%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-08-24
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-08-23 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8559.16 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 8149 | MW
Evening Peak Generation : |  | 11577 | MW Hour : | 21:00 | Available Max Generation : |  | 15416 | MW
E.P. Demand (at gen end) : |  | 11577 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12000 | MW
Maximum Generation : |  | 11577 | MW Hour : | 21:00 | Reserve(Generation end) |  | 3416 | MW
Total Gen. (MKWH) : |  | 233.1527 | System Load Factor : | 83.91% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -301 | MW at | 21:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-08-24
Actual : | 105.47 | Ft.(MSL) , | Rule curve : | 96.36 | Ft.( MSL )
Gas Consumed : | Total = | 1326.25 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 146263468.896
|  | Coal : | 41230686.66 | Oil : | 349981034.52 | Total : | 537475190.076
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4195.1811 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1428.3862 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1280.1061 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1156.7973 |  |  | 0 | 0%
) | 0 | 0:00 | 1045.3184 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 843.5395 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 469.3591 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 217.1277 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 650.5906 |  |  | 0 | 0%
Total | 0 |  | 11286.406 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit- 2. | 7) Ghorasal Unit-5
|  |  |  | 2) Khulna ST 110 MW | 8) Ghorashal Unit-4
|  |  |  | 3) Sikalbaha ST 60 MW | 9) Sirajganj Unit-2
|  |  |  | 4) Siddhirganj ST | 10) Siddhirganj 335 MW.
|  |  |  | 5) Ashuganj #4 | 11) Ashuganj #3
6) Baghabari 100 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Haripur-Ullon 132 kV Ckt-2 tripped from both end at 08:13 showing Dist. R-phase, Z2 at Haripur end &
Dist. R-phase Z1 at Ullon end and was switched on at 08:30.
b) Manikganj GT-2 with Ckt-2 were switched on at 08:42.
c) Sirajganj unit-4 was under shut down from 09:28 to 21:00 due to work at Sirajganj 230 kV S/S by PGCB.
d) Siddhirganj 335 MW GT synchronized at 11:29 on test of STG commissioning.
e) Sunamganj 132/33 kV T1 transformer was under shut down from 10:27 to 11:27 due to red hot at 33 kV side.
f) Faridpur 132/33 kV T2 transformer was under shut down from 09:35 to 13:02 due to D/W.
g) Faridpur S/S-Faridpur P/S Ckt was under shut down from 09:40 to 12:45 due to D/W.
h) Tongi-Ghorashal 230 kV Ckt-1 tripped from both end at 13:40 showing O/C at Tongi end & DRT, DRF-238 at
Ghorashal end and was switched on at 14:11.
i) Kustia-Bheramara 132 kV Ckt-2 was under shut down from 15:31 to 17:11 due to red hot.
j) Bogura-Bogura Confidence 132 kV Ckt(new) was closed at 16:34.
k) Chapainawabganj 132/33 kV T4 transformer tripped at 16:57 due to O/C and was switched on at 17:05. |  |  |  |  | About 6 MW power interruption occurred under Chapainawabganj S/S
area from 16:57 to 17:05.
l) Rampura-Mogbazar 132 kV Ckt-1 was under shut down from 20:55 to 00:20(24/08/2019) due to red hot
Mogbazar end.
m) Sreemongal132/33 kV T1 & T2 transformers tripped at 21:05 due to 33 kV Sreemongal feeder fault and |  |  |  |  | About 15 MW power interruption occurred under Sreemongal S/S
were switched on at 21:24 & 21:10 respectively. |  |  |  |  | area from 21:05 to 21:24.
n) Mymensing-Netrokona 132 kV Ckt-2 was shut down at 05:52(24/08/2019) for C/M.
o) Rangpur-Lalmonirhat 132 kV single Ckt was shut down at 06:10(24/08/2019) for D/W. |  |  |  |  | About 80 MW power interruption occurred under Lalmonirhat S/S
area from 06:44(24/08/2019).
p) Chandpur CCPP 150 MW tripped at 04:10(24/08/2019) and GT was synchronized at 07:39(24/08/2019).
q) Gopalganj-Madaripur 132 kV single Ckt was shut down at 07:01 for C/M. |  |  |  |  | About 65 MW power interruption occurred under Gopalganj S/S
area from 07:01(24/08/2019).
r) Bottail 132/33 kV T1 transformer along with 33 kV bus-1 was under shut down from 07:14(24/08/2019) to |  |  |  |  | About 33 MW power interruption occurred under Bottail S/S
09:01(24/08/2019) due to red hot maintenance at 33 kV Kumarkhai feeder. |  |  |  |  | area from 07:14(24/08/2019) to 09:01(24/08/2019).
s) Ramganj 132/33 kV T1 transformer's 33 kV bus was under shut down from 22:11 to 23:01 due to red hot |  |  |  |  | About 35 MW power interruption occurred under Ramganj S/S
maintenance at 33 kv bus DS. |  |  |  |  | area from 21:11 to 23:01.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-08-23 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 70 | 1520000
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 209 | 4430000
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 380 | 7747564
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 50 | 1022336 | Frequency control
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 12 | 740181 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 346 | 8502270 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 351 | 7648000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 360 | 8113750 | Machine problem
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 42240 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 270 | 6631360 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 24864 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 63450 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 13431 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 424728
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 180 | 3163000 | FGMO
| Siddhirganj Desh |  | QRPP | 96*1.2 | 0 | 0 | 0 | Contract Expired
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 7680 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217 | 217 | 52 | 481746
| Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 7 | 137520 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 47 | 795504
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 703800
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 130 | 689760 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 405502
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 176104 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 72 | 723840 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 54 | 1129740 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 744700
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 29 | 643000
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 422004
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 57709 | Reserve
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 53 | 231840 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 106 | 1069752
| Dhaka area Total |  |  |  | 5693 | 3009 | 58507375
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 188929
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 102330
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 48 | 676320
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 212 | 4946176
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4746346 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 130 | 2916550 | FGMO
44 | Sikalbaha 51 MW PP(Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 0 | 0 | Contract Expired
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 17 | 71927 | Low demand
46 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
47 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 497444
48 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 257760 | Low demand
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 1151040 | Engine problem
50 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 515616
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 39 | 878880
51 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 44 | 541440 | Low demand
52 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 30240
53 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 140 | 2057454 | Transformer overload.
| Jodiac Power |  | IPP | 54.36 | 0 | 0 | 0 | on test
| Karnaphuli Power Ltd. |  | IPP | 110 | 0 | 17 | 600506 | Low demand
| Chattogram area Total |  |  |  | 2053 | 1183 | 22578958
54 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 1913438 | Gas shortage
55 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 179 | 4510000 | FGMO
56 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 345 | 8029300 | FGMO
57 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 7139000 | FGMO
58 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 33 | 764784 | Engine problem
59 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 55 | 852480
60 | Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
61 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 485090 | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 696952 | Engine problem
63 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 50 | 272654 | Transformer overload.
64 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
65 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
66 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 138 | 3270220
67 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 2148480
68 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 442332
69 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 241560
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 178 | 3636480
70 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 817900
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 471398
72 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 481800 | Engine problem
73 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1749 | 36173868
74 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 205 | 4067440
75 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 459972
76 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 89 | 1884480
77 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 6900
78 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 150 | 1747200 | Low demand
79 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2052000
| Mymensingh Area Total |  |  |  | 637 | 579 | 10217992
80 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1421000
81 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 1032000
82 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3424533
83 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 145 | 3280000 | GT-2 under maint.
84 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 746400
85 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 49 | 75996
86 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 183360 | Engine problem
87 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 64 | 1480608 | FGMO
88 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 79 | 1057920 | Engine problem
89 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 43 | 733320 | Engine problem
90 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 110 | 2298190
91 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 441320
92 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 44 | 779720 | Engine problem
93 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 443064
94 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7447500 | FGMO
95 | Bibiyana-III 400 MW CCPP |  | PDB | 285 MW | 285 | 232 | 5469000 | Test
96 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 250920
| Sylhet Area Total |  |  |  | 1834 | 1437 | 30564851
97 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 25600 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 903 | 21139636
| Khulna 115 MW PP (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
98 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 1435200 | Engine problem
99 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 32 | 202080
100 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
101 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 53 | 607744
102 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 410 | 8032896
103 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 726750
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
104 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 50 | 427200 | Low demand
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 2142720
106 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 42 | 1812816 | Low demand
| Khulna Area Total |  |  |  | 2314 | 1734 | 36552642
107 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1118400
108 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 47250 | Reserve
109 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 38 | 710285
110 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 170 | 4342441
111 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 97 | 1602741
| Barisal Area Total |  |  |  | 462 | 415 | 7821117
112 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 55 | 1375000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
113 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 273571
114 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 25 | 69885
115 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 452480
116 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 874755
117 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 45 | 228775
118 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 190 | 4864800 | FGMO
119 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
120 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 191 | 4694518 | FGMO
121 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 0 | 2933545 | Under maint.
122 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 29 | 159912
123 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 512640
124 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 16 | 365328
125 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 211068
126 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 684480
127 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 765744
128 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
129 | Bagura 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1749696
| Rajshahi Area Total |  |  |  | 2070 | 993 | 20216197
130 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 95 | 2268218
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
131 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 270 | 6548200
132 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
133 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 66000 | Reserve
| Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 0 | 113 | 1614720 | On test
| Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 22515
| Rangpur Area Total |  |  |  | 492 | 478 | 10519653
| Total |  |  |  | 18446 | 11577 | 233152653
| Eastern Grid Total |  |  |  | 13108 | 7957 | 158043044
| Western Grid Total |  |  |  | 5338 | 3620 | 75109609
| National Grid Total |  |  |  | 18446 | 11577 | 233152653
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-08-23
(a) ENTIRE EASTERN GRID : |  | 7204 | MW | (b) ENTIRE WESTERN GRID : |  | 3671 | MW
i) Dhaka area |  | 3553 | MW | i) Khulna area |  | 1393 | MW
ii) Chittagong area |  | 1108 | MW | ii) Rajshahi area |  | 1207 | MW
iii) Comilla area |  | 1117 | MW | iii) Barisal area |  | 338 | MW
iv) Mymensingh area |  | 958 | MW | iv) Rangpur area |  | 733 | MW
v) Sylhet area |  | 468 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 10875 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 110 | 100 | Sherpur | 108 | 2200 | Jhenida | 110 | 1930
Munsiganj | 118 | 2200 | Srimongal | 40 | 2000 | Bottail | 110 | 100
Sonargaon | 68 | 1600 | Shahjibazar | 117 | 1930 | G.K Project | 55 | 1930
Shyampur | 176 | 100 | Fenchuganj | 44 | 2100 | Faridpur | 168 | 2000
Bhulta | 140 | 100 | Kulawara | 45 | 2200 | Madaripur | 114 | 2200
Madanganj | 51 | 100 | Sylhet | 136 | 2200 | Sariatpur | 46 | 2200
Shitalakhya | 84 | 100 | Chatak | 27 | 200 | Gopalganj | 88 | 1930
Rahim steel | 8 | 900 | Sunamganj | 46 | 2200 | Bagerhat | 84 | 2100
Matuail | 72 | 200 | Biani Bazar | 56 | 2100 | Mongla | 36 | 100
Ghorasal | 72 | 2200 | Comilla (S) | 180 | 2200 | Satkhira | 102 | 2200
Narsingdi | 132 | 100 | Comilla(N) | 121 | 2000 | Gallamari | 46 | 100
Haripur (SBU) | 72 | 2400 | Chandpur | 108 | 2100 | Magura | 54 | 1930
Ullon | 74 | 2000 | Feni | 128 | 2200 | Norail | 24 | 1900
Hasnabad | 188 | 2200 | Chowmuhani | 174 | 2000 | Chuadanga | 87 | 2200
Magbazar | 106 | 2000 | Ashuganj | 53 | 2400 | Barisal(N) | 45 | 2300
Maniknagar | 98 | 2000 | Daudkandi | 126 | 2100 | Barisal (S) | 100 | 100
Bangabhaban | 14 | 1200 | B.Baria | 147 | 2100 | Patuakhali | 110 | 2200
Narinda | 72 | 1200 | Ramganj | 96 | 2100 | Bhandaria | 55 | 2100
Dhanmondi | 124 | 2100 | Madunaghat | 53.5 | 2000 | Borhan Uddin | 38 | 2200
Lalbag | 61 | 1930 | Hathazari | 97 | 2000 | Ishurdi | 61 | 2100
Madartek | 56 | 2300 | Khulshi | 182 | 2300 | Ruppur Paromanobik | 2 | 1100
Mirpur | 100 | 1930 | Halishahar | 136 | 2000 | Natore | 123 | 2100
Kalyanpur | 111 | 2000 | Baraulia | 157 | 2300 | Bogra | 235 | 2000
Gulshan | 118 | 2000 | Sikalbaha | 19 | 1900 | Noagaon | 117 | 2100
Uttara | 79 | 2000 | Dohazari | 92 | 2100 | Rajshahi | 148 | 2000
Uttara New | 13 | 2000 | Cox'sbazar | 92 | 1930 | C.Nawabganj | 73 | 2100
Kamrangirchar | 49 | 1930 | Chandraghona | 28 | 1930 | Amnura | 41 | 1930
Savar | 109 | 2100 | Kaptai | 4.5 | 1900 | Pabna | 108 | 2100
Bhasantec | 147 | 2000 | A. Khaer Stl. | 0 | 0 | Shahjadpur | 95 | 2100
Agargaon | 52 | 2100 | Bakulia | 92 | 2400 | Serajganj | 94 | 2000
Satmosjid | 107 | 1930 | Julda | 22 | 100 | Niyamatpur | 59 | 2100
Tongi | 127 | 100 | TK chemical | 16.4 | 1900 | Joypurhat | 52 | 2000
Kabirpur | 166 | 2200 | Modern Steel | 12 | 200 | Mohastangor | 15 | 100
Basundhara | 118 | 1930 | Shahmirpur | 28 | 100 | Rangpur | 141 | 100
Manikganj | 92 | 2100 | Khagrachhari | 20 | 1900 | Lalmonirhat | 70 | 1900
Joydevpur | 192 | 2100 | Matarbari | 27.5 | 2200 | Saidpur | 102 | 2000
New Tongi | 79 | 2100 | Baroiar Hat | 36 | 1900 | Purbasadipur | 107 | 100
Korda | 194 | 200 | Rangamati | 12 | 1900 | Thakurgaon | 74 | 400
Dhamrai | 56 | 2200 | Abul Khair 230 | 130 | 100 | Palashbari | 119 | 2100
Valuka | 82 | 100 | BSRM | 107 | 100 | Barapukuria | 51 | 2100
Tangail | 197 | 2100 | Goalpara | 24 | 2300 | Panchagar | 41 | 2000
Mymensing | 228 | 2200 | Central s/s | 90 | 1930 | Joldhaka | 29 | 2100
Kishorganj | 128 | 2200 | Noapara | 72 | 2100 | Kurigram | 39 | 100
Netrokona | 100 | 2000 | Jessore | 106 | 2000
Jamalpur | 133 | 2000 | Benapol | 42 | 2000
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-08-23
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | 126
Bibiyana | 389 | 5:00 | 383 | 13:00 | Kaliakoir | 367 | 19:30 | 360
Bheramara | 400 | 4:00 | 389 | 19:30 | Bhulta | 385 | 20:00 | 375
Ashuganj(N) | 386 | 3:00 | 379 | 11:00
230 KV | KV |  | KV |  | 230 KV | KV |  | 11:00
Ghorasal | 230 | 1:00 | 226 | 10:00 | Hathazari | 219 | 7:00 | 215
Ishurdi | 236 | 18:00 | 224 | 21:00 | Megnaghat | 224 | 19:00 | 219
Ashuganj | 236 | 7:00 | 231 | 10:00 | Fenchuganj | 234 | 6:00 | 231
Serajganj | 230 | 6:00 | 221 | 23:00 | Siddhirganj | 223 | 4:00 | 218
Baghabari | 233 | 7:00 | 226 | 23:00 | Maniknagar | 220 | 6:00 | 216
Barapukuria | 233 | 7:00 | 223 | 22:00 | Old Airport | 220 | 19:30 | 213
Bogra | 224 | 18:00 | 210 | 21:00 | Barisal | 227 | 6:00 | 220
Khulna South | 230 | 18:00 | 216 | 21:00 | AKSML | 216 | 5:00 | 211
Rampura | 220 | 1:00 | 218 | 10:00 | BSRM | 218 | 4:00 | 213
Haripur | 220 | 1:00 | 217 | 12:00 | Bibiyana | 232 | 3:00 | 227
Hasnabad | 221 | 19:00 | 215 | 15:00 | Bhulta | 224 | 19:30 | 217
Aminbazar | 220 | 2:00 | 214 | 15:00 | Ashuganj (S) | 233 | 2:00 | 228
Tongi | 220 | 20:00 | 210 | 14:00 | Kaliakoir | 224 | 19:30 | 218
Comilla (N) | 227 | 9:00 | 224 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 133 | 1930 | 130 | 1000 | Khulshi | 128 | 100 | 125
Munsiganj | 133 | 1900 | 128 | 1500 | Halishahar | 132 | 1930 | 128
Megnaghat | 130 | 400 | 126 | 1000 | Baraulia | 130 | 1800 | 127
Shyampur | 131 | 1930 | 126 | 1600 | Sikalbaha | 132 | 2100 | 129
Bhulta | 128 | 400 | 125 | 1400 | Dohazari | 130 | 1600 | 126
Madanganj | 132 | 1900 | 125 | 1200 | Cox'sbazar | 123 | 1600 | 117
Shitalakhya | 134 | 1900 | 126 | 1200 | Chandraghona | 132 | 700 | 130
Rahim steal | 132 | 200 | 130 | 1200 | Kaptai | 132 | 1800 | 130
Matuail | 131 | 700 | 129 | 1300 | A. Khaer Stl. | 130 | 300 | 127
Ghorasal | 135 | 100 | 132 | 900 | Bakulia | 131 | 1930 | 127
Narsinghdi | 130 | 1100 | 124 | 100 | Julda | 131 | 2100 | 128
Haripur (SBU) | 132 | 500 | 130 | 1200 | TK Chemical | 129 | 100 | 131
Ullon | 132 | 600 | 128 | 1200 | Modern Steel | 131 | 100 | 128
Hasnabad | 130 | 2000 | 127 | 1200 | Shahmirpur | 131 | 1900 | 127
Magbazar | 133 | 600 | 128 | 1100 | Khagrachhari | 131 | 700 | 128
Maniknagar | 135 | 600 | 132 | 1500 | Matarbari | 132 | 2100 | 120
Bangabhaban | 135 | 600 | 132 | 1500 | Baroiar Hat | 126 | 700 | 121
Narinda | 135 | 600 | 132 | 1500 | Rangamati | 131 | 100 | 129
Dhanmondi | 132 | 600 | 128 | 1200 | Goalpara | 139 | 1800 | 130
Lalbag | 131 | 1930 | 125 | 1200 | Central s/s | 138 | 800 | 130
Madartek | 132 | 600 | 128 | 1100 | Noapara | 136 | 800 | 127
Mirpur | 134 | 200 | 128 | 1100 | Jessore | 131 | 800 | 117
Kalyanpur | 135 | 2000 | 130 | 1200 | Benapol | 129 | 700 | 118
Gulshan | 132 | 600 | 127 | 1100 | Jhenida | 137 | 900 | 114
Uttara | 131 | 200 | 125 | 1500 | Bottail | 139 | 1200 | 125
Uttara New | 133 | 1900 | 124 | 1500 | G.K Project | 143 | 900 | 135
Kamrangirchar | 132 | 1900 | 126 | 1200 | Faridpur | 133 | 1000 | 118
Savar | 133 | 600 | 125 | 1600 | Madaripur | 134 | 1800 | 120
Bhasantec | 135 | 100 | 116 | 600 | Sariatpur | 132 | 1100 | 118
Agargaon | 133 | 600 | 129 | 1200 | Gopalganj | 139 | 1800 | 123
Satmosjid | 133 | 600 | 129 | 1200 | Bagerhat | 136 | 700 | 129
Tongi | 135 | 2000 | 126 | 1400 | Mongla | 134 | 1600 | 126
Kabirpur | 133 | 1830 | 128 | 2100 | Satkhira | 137 | 1000 | 126
Basundhara | 132 | 1930 | 124 | 1500 | Gallamari | 139 | 800 | 129
Manikganj | 138 | 1930 | 128 | 1500 | Magura | 131 | 1800 | 111
Joydevpur | 140 | 1930 | 131 | 1200 | Norail | 130 | 1800 | 112
New Tongi | 134 | 1930 | 125 | 1500 | Chuadanga | 123 | 800 | 104
Kodda | 135 | 1930 | 122 | 1500 | Barisal(N) | 136 | 1830 | 130
Dhamrai | 131 | 1830 | 127 | 2100 | Barisal (S) | 135 | 700 | 129
Valuka | 127 | 1800 | 117 | 2200 | Patuakhali | 134 | 700 | 126
Tangail | 130 | 700 | 123 | 2100 | Bhandaria | 135 | 1800 | 126
Mymensing | 129 | 1800 | 119 | 1000 | Ishurdi | 140 | 1800 | 133
Kishorganj | 129 | 1800 | 121 | 2100 | Ruppur Paromanobik | 139 | 800 | 134
Netrokona | 128 | 1800 | 117 | 2100 | Natore | 136 | 1800 | 128
Jamalpur | 137 | 1930 | 116 | 1000 | Bogra | 135 | 800 | 125
Sherpur | 137 | 1700 | 120 | 700 | Noagaon | 130 | 700 | 119
Srimongal | 135 | 1800 | 131 | 400 | Rajshahi | 132 | 1800 | 125
Shahjibazar | 133 | 1800 | 129 | 1300 | C.Nawabganj | 130 | 1800 | 121
Fenchuganj | 134 | 1800 | 131 | 100 | Amnura | 130 | 1930 | 122
Khulawara | 133 | 1800 | 130 | 100 | Pabna | 139 | 1800 | 129
Sylhet | 133 | 1700 | 130 | 1000 | Shahjadpur | 141 | 700 | 134
Chatak | 133 | 1800 | 128 | 1300 | Serajganj | 136 | 800 | 130
Sunamganj | 130 | 400 | 126 | 2200 | Niyamatpur | 128 | 700 | 113
Biani Bazar | 131 | 400 | 128 | 1300 | Joypurhat | 130 | 700 | 115
Comilla(s) | 125 | 600 | 119 | 1200 | Mohastangor | 133 | 700 | 123
Comilla(n) | 133 | 900 | 131 | 1100 | Rangpur | 129 | 700 | 116
Chandpur | 130 | 700 | 126 | 1500 | Lalmonirhat | 126 | 1300 | 112
Feni | 125 | 700 | 120 | 1600 | Saidpur | 128 | 1800 | 115
Chowmuhani | 124 | 700 | 115 | 1500 | Purbasadipur | 128 | 1800 | 114
Ashuganj | 134 | 700 | 131 | 2100 | Thakurgaon | 124 | 1800 | 104
Daudkandi | 129 | 700 | 125 | 1500 | Palashbari | 130 | 1830 | 120
B.Baria | 130 | 1700 | 127 | 1200 | Barapukuria | 133 | 700 | 124

## L-Curve
Date | 2019-08-23
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 52 | 7556 | 3751 | 11307 |  |  |  | QF-LDC-12
0:30 | 126 | 7676 | 3636 | 11312 | Date: | 2019-08-23
1:00 | 200 | 7796 | 3521 | 11317
1:30 | 195 | 7652.5 | 3453.5 | 11106
2:00 | 190 | 7509 | 3386 | 10895
2:30 | 205 | 7438.5 | 3346 | 10784.5 | [5 empty] | Gen. at Eve. Peak | 11577 | 11577 MW (21:00 )
3:00 | 220 | 7368 | 3306 | 10674 | [6 empty] | 21:00
3:30 | 200 | 7221.5 | 3255 | 10476.5 | [5 empty] | Gen. at Day Peak | 8559.16 | 8559.16 MW (12:00 )
4:00 | 180 | 7075 | 3204 | 10279 | [6 empty] | 12:00
4:30 | 150 | 6916 | 3223.5 | 10139.5 | [5 empty] | Highest Generation | 11577
5:00 | 120 | 6757 | 3243 | 10000 | [6 empty] | 21:00
5:30 | 110 | 6392.615 | 3128 | 9520.615
6:00 | 100 | 6028.23 | 3013 | 9041.23
6:30 | 160 | 5794.665 | 2956 | 8750.665
7:00 | 220 | 5561.1 | 2899 | 8460.1
7:30 | 235 | 5491.11 | 2861 | 8352.11
8:00 | 250 | 5421.12 | 2823 | 8244.12
8:30 | 235 | 5426.26 | 2759 | 8185.26
9:00 | 220 | 5431.4 | 2695 | 8126.4
9:30 | 220 | 5492.8 | 2630 | 8122.8
10:00 | 220 | 5554.2 | 2565 | 8119.2
10:30 | 243 | 5576.1 | 2564 | 8140.1
11:00 | 266 | 5598 | 2563 | 8161
11:30 | 223 | 5732.06 | 2628.02 | 8360.08
12:00 | 180 | 5866.12 | 2693.04 | 8559.16
12:30 | 131.5 | 5933.56 | 2719.52 | 8653.08
13:00 | 83 | 6001 | 2746 | 8747
13:30 | 80.5 | 5950.975 | 2736.3 | 8687.275
14:00 | 78 | 5900.95 | 2726.6 | 8627.55
14:30 | 70 | 6088.98 | 2757.65 | 8846.63
15:00 | 62 | 6277.01 | 2788.7 | 9065.71
15:30 | 113.5 | 6199.355 | 2781.85 | 8981.205
16:00 | 165 | 6121.7 | 2775 | 8896.7
16:30 | 175 | 5984.45 | 2693.6 | 8678.05
17:00 | 185 | 5847.2 | 2612.2 | 8459.4
17:30 | 195 | 5740.6 | 2583.1 | 8323.7
18:00 | 205 | 5634 | 2554 | 8188
18:30 | 165 | 6353.5 | 2980.5 | 9334
19:00 | 125 | 7073 | 3407 | 10480
19:30 | 170 | 7632 | 3572 | 11204
20:00 | 150 | 7778 | 3600 | 11378 |  |  |  | Executive Engineer
20:30 | 225.5 | 7867.5 | 3610 | 11477.5 |  |  |  | Network Operation Division
21:00 | 301 | 7957 | 3620 | 11577
21:30 | 259 | 7867.5 | 3648 | 11515.5
22:00 | 217 | 7778 | 3676 | 11454 |  |  |  |  | Page 6 of 7
22:30 | 167.5 | 7727.5 | 3645 | 11372.5
23:00 | 118 | 7677 | 3614 | 11291
23:30 | 85 | 7616.5 | 3682.5 | 11299
24:00 | 52 | 7556 | 3751 | 11307
11577 MW (21:00 )
8559.16 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-08-23 |  | Energy | 233152653
[10 empty] | 2019-08-23 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4884 | 903 | 2008 | 2438 | 364 | 216 | 320 | 0 | 174
0:30 | 4785 | 839.5 | 2138.5 | 2465.5 | 364.5 | 215 | 327 | 0 | 177 | Date: | 2019-08-23
1:00 | 4686 | 776 | 2269 | 2493 | 365 | 214 | 334 | 0 | 180
1:30 | 4662 | 776 | 2237 | 2415 | 365 | 214 | 259 | 0 | 178 | [7 empty] | Total Energy | 233.1527 | Total Energy Gen 233.153 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 233.153 MKWHr
2:00 | 4638 | 776 | 2205 | 2337 | 365 | 214 | 184 | 0 | 176 | [7 empty] | Energy not Served | 0
2:30 | 4631.5 | 776 | 2217 | 2240.5 | 365 | 215 | 165.5 | 0 | 174 | [7 empty] | Energy Requirement | 233.1527
3:00 | 4625 | 776 | 2229 | 2144 | 365 | 216 | 147 | 0 | 172
3:30 | 4617.5 | 776 | 2229.5 | 1985 | 365 | 216 | 117.5 | 0 | 170 | [6 empty] | Shortage
4:00 | 4610 | 776 | 2230 | 1826 | 365 | 216 | 88 | 0 | 168
4:30 | 4594 | 840 | 2226 | 1660 | 365 | 216 | 73.5 | 0 | 165
5:00 | 4578 | 904 | 2222 | 1494 | 365 | 216 | 59 | 0 | 162
5:30 | 4511 | 904.5 | 2012.5 | 1304.5 | 365 | 214.5 | 55.5 | 0 | 153
6:00 | 4444 | 905 | 1803 | 1115 | 365 | 213 | 52 | 0 | 144
6:30 | 4334 | 905 | 1744.5 | 1024.5 | 365 | 212.5 | 26 | 0 | 137 |  |  |  |  | Coal
7:00 | 4224 | 905 | 1686 | 934 | 365 | 212 | 0 | 0 | 130
7:30 | 4186 | 904.5 | 1634 | 918 | 363.5 | 211.5 | 0 | 0 | 126 |  |  |  | Oil |  |  |  | ,
8:00 | 4148 | 904 | 1582 | 902 | 362 | 211 | 0 | 0 | 122
8:30 | 4143.5 | 904 | 1514 | 909.5 | 363 | 211.5 | 0 | 0 | 122
9:00 | 4139 | 904 | 1446 | 917 | 364 | 212 | 0 | 0 | 122
9:30 | 4195.5 | 903.5 | 1399 | 904.5 | 364.5 | 212 | 0 | 0 | 122
10:00 | 4252 | 903 | 1352 | 892 | 365 | 212 | 0 | 0 | 122
10:30 | 4254 | 903.5 | 1350 | 912 | 364.5 | 213 | 0 | 0 | 123
11:00 | 4256 | 904 | 1348 | 932 | 364 | 214 | 0 | 0 | 124
11:30 | 4406 | 903.5 | 1363 | 963 | 364 | 215 | 0 | 0 | 126
12:00 | 4556 | 903 | 1378 | 994 | 364 | 216 | 0 | 0 | 128
12:30 | 4607 | 903 | 1400.5 | 1016.5 | 364.5 | 216 | 0 | 0 | 129
13:00 | 4658 | 903 | 1423 | 1039 | 365 | 216 | 0 | 0 | 130
13:30 | 4658 | 903 | 1423 | 1039 | 365 | 216 | 0 | 0 | 130
14:00 | 4658 | 903 | 1423 | 1039 | 365 | 216 | 0 | 0 | 130
14:30 | 4700 | 903 | 1482.5 | 1091.5 | 365 | 213.5 | 0 | 0 | 137
15:00 | 4742 | 903 | 1542 | 1144 | 365 | 211 | 0 | 0 | 144
15:30 | 4671.5 | 903 | 1546.5 | 1132 | 364.5 | 210 | 0 | 0 | 142
16:00 | 4601 | 903 | 1551 | 1120 | 364 | 209 | 0 | 0 | 140
16:30 | 4469 | 903 | 1509.5 | 1066.5 | 363.5 | 209 | 15 | 0 | 137
17:00 | 4337 | 903 | 1468 | 1013 | 363 | 209 | 30 | 0 | 134
17:30 | 4206.5 | 903 | 1446.5 | 1017 | 363 | 209 | 47.5 | 0 | 130
18:00 | 4076 | 903 | 1425 | 1021 | 363 | 209 | 65 | 0 | 126
18:30 | 4391.5 | 903 | 1540 | 1542 | 363.5 | 209 | 237 | 0 | 148
19:00 | 4707 | 903 | 1655 | 2063 | 364 | 209 | 409 | 0 | 170
19:30 | 4718 | 904 | 1588 | 2695 | 364 | 209 | 552 | 0 | 174
20:00 | 4744 | 903 | 1633 | 2768 | 364 | 209 | 581 | 0 | 176
20:30 | 4847 | 903 | 1728.5 | 2685 | 364.5 | 210.5 | 562 | 0 | 177
21:00 | 4950 | 903 | 1824 | 2602 | 365 | 212 | 543 | 0 | 178
21:30 | 4927.5 | 903.5 | 1856 | 2574 | 364.5 | 212 | 499 | 0 | 179
22:00 | 4905 | 904 | 1888 | 2546 | 364 | 212 | 455 | 0 | 180
22:30 | 4929.5 | 903 | 1880.5 | 2491 | 364 | 214 | 411.5 | 0 | 179
23:00 | 4954 | 902 | 1873 | 2436 | 364 | 216 | 368 | 0 | 178
23:30 | 4919 | 902.5 | 1940.5 | 2437 | 364 | 216 | 344 | 0 | 176 | Max Temp. in Dhaka |  | 33° C
24:00 | 4884 | 903 | 2008 | 2438 | 364 | 216 | 320 | 0 | 174
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 233.153 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 233.153 MKWHr
Note on W13: Author:

## Generation
2019-08-23
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 124 | 124 | 126 | 126 | 126 | 123 | 122 | 121 | 122 | 122 | 124 | 126 | 126 | 126 | 121 | 119 | 119 | 119 |  | 119 | 119 | 119 | 122 | 122 | 126 | 126 | 2774176
2 | Karnaphuli Hydro PP Unit-4 & 5 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2172000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 0 | [17 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 188929
| Teknaf 20MW PP (Solartech) | [6 empty] | 2 | 9 | 15 | 12 | 11 | 14 | 5 | 10 | 12 | 5 | 2 | 0 | [8 empty] | 102330
6 | Sikalbaha 225MW CCPP (Gas) | 185 | 185 | 184 | 184 | 184 | 184 | 185 | 186 | 184 | 206 | 205 | 211 | 208 | 204 | 206 | 205 | 204 | 204 |  | 204 | 204 | 204 | 204 | 204 | 208 | 204 | 4746346
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 130 | 130 | 130 | 130 | 130 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 130 | 130 | 130 | 100 | 100 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 2916550
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 39 | 17 | 0 | [16 empty] | 85 | 85 | 85 | 85 | 85 | 66 | 42 | 497444
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [19 empty] | 17 | 17 | 17 | 17 | 17 |  |  | 71927
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 151 | 151 | 151 | 151 | 151 | 80 | 70 | 70 | 78 | 79 | 79 | 79 | 120 | 120 | 156 | 180 | 123 | 101 |  | 155 | 100 | 100 | 180 | 145 | 145 | 140 | 3163000
17 | Siddhirganj 335 MW CCPP | [10 empty] | 0 | 10 | 13 | 22 | 32 | 40 | 32 | 32 |  | 52 | 52 | 52 | 52 | 52 | 49 | 48 | 481746
18 | Kodda 300 MW PP Unit-2 (Summit) | [19 empty] | 12 | 15 | 40 | 0 |  |  |  | 57709
19 | Ashuganj 195MW PP (APSCL-United) | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 485090
20 | Ghorasal TPP (Unit-1&2) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1520000
21 | Ghorasal Repowered CCPP Unit-3 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 |  | 169 | 169 | 169 | 209 | 209 | 200 | 198 | 4430000
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 250 | 240 |  | 350 | 350 | 350 | 380 | 380 | 380 | 380 | 7747564
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1913438
32 | Ashuganj 50 MW PP | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 764784
33 | Ashuganj 225 MW CCPP | 193 | 189 | 180 | 181 | 180 | 181 | 181 | 181 | 182 | 197 | 193 | 199 | 201 | 190 | 187 | 189 | 187 | 155 |  | 180 | 179 | 179 | 179 | 180 | 193 | 180 | 4510000
34 | Ashuganj 450 MW CCPP(South) | 305 | 290 | 290 | 290 | 290 | 290 | 250 | 255 | 250 | 270 | 265 | 353 | 330 | 315 | 320 | 305 | 270 | 270 |  | 300 | 305 | 305 | 305 | 305 | 330 | 310 | 7139000
| Ashuganj 450 MW CCPP(North) | 356 | 347 | 345 | 345 | 345 | 345 | 260 | 260 | 260 | 280 | 275 | 360 | 360 | 340 | 360 | 270 | 270 | 270 |  | 310 | 340 | 340 | 345 | 345 | 350 | 345 | 8029300
35 | Ashuganj 55 MW PP (Precision) | 54 | 54 | 54 | 54 | 54 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 30 | 30 | 30 | 30 |  | 30 | 30 | 55 | 55 | 53 | 55 | 56 | 852480
36 | Chandpur 150 MW CCPP | 138 | 138 | 138 | 138 | 138 | 138 | 137 | 134 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 137 | 140 |  | 138 | 135 | 140 | 138 | 133 | 138 | 132 | 3270220
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 355 | 350 | 348 | 350 | 345 | 344 | 344 | 345 | 344 | 354 | 351 | 353 | 372 | 350 | 375 | 374 | 352 | 270 |  | 300 | 344 | 345 | 346 | 345 | 346 | 356 | 8502270
40 | Meghnaghat 450 MW CCPP(MPL) | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 |  | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 8113750
41 | Haripur 360MW CCPP(HPL) | 355 | 355 | 355 | 355 | 358 | 358 | 303 | 271 | 274 | 273 | 273 | 303 | 303 | 303 | 347 | 348 | 303 | 273 |  | 303 | 303 | 303 | 351 | 354 | 351 | 357 | 7648000
42 | RPCL 210MW CCPP | 157 | 158 | 172 | 172 | 174 | 188 | 188 | 189 | 186 | 185 | 184 | 173 | 172 | 169 | 172 | 122 | 140 | 143 |  | 181 | 204 | 205 | 205 | 203 | 188 | 204 | 4067440
43
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1421000
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1032000
46 | Shajibazar 330 MW CCPP | 146 | 145 | 146 | 145 | 145 | 145 | 145 | 146 | 146 | 144 | 144 | 147 | 146 | 148 | 148 | 145 | 144 | 145 |  | 144 | 144 | 145 | 145 | 144 | 147 | 144 | 3280000
47 | Shahjibazar GTPP Unit- 8 & 9 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 50 | 62 | 61 | 61 | 61 | 61 | 61 | 60 | 61 | 62 | 63 |  | 63 | 50 | 63 | 64 | 64 | 64 | 65 | 1480608
48 | Shahjibazar 86MW PP (Shahjibazar) | 79 | 79 | 79 | 79 | 79 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 1057920
49 | Shahjibazar 50MW PP (EPL) | 43 | 40 | 43 | 43 | 43 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 45 | 733320
50 | Sylhet 150 MW CCPP | 116 | 116 | 110 | 110 | 110 | 70 | 68 | 68 | 67 | 68 | 68 | 78 | 77 | 80 | 97 | 89 | 89 | 71 |  | 102 | 102 | 110 | 110 | 110 | 123 | 110 | 2298190
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 441320
52 | Sylhet 50MW PP (EPL) | 46 | 45 | 46 | 45 | 45 | 20 | 14 | 14 | 14 | 14 | 13 | 13 | 13 | 13 | 40 | 42 | 41 | 41 |  | 46 | 44 | 46 | 44 | 46 | 45 | 35 | 779720
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 250920
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 183360
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 28 | 42 | 42 | 42 | 11 | 11 | 11 | 11 | 13 | 11 | 11 | 11 | 11 | 11 | 24 | 47 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 746400
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 443064
57 | Bibiana-II 341 MW CCPP (Summit) | 315 | 310 | 310 | 290 | 280 | 270 | 290 | 290 | 280 | 310 | 315 | 310 | 320 | 300 | 330 | 320 | 290 | 280 |  | 310 | 280 | 270 | 295 | 290 | 290 | 295 | 7447500
58 | Nababganj 55 MW PP (Southern power ) | 35 | 0 | [17 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 176104
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 515616
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 0 |  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 424728
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 459972
63 | Impoprt (Tripura) | 180 | 176 | 172 | 168 | 162 | 144 | 130 | 122 | 122 | 122 | 124 | 128 | 130 | 134 | 144 | 140 | 134 | 126 |  | 170 | 174 | 176 | 178 | 180 | 178 | 174 | 3636480
64 | Malancha, Ctg. EPZ (United) | 40 | 41 | 41 | 41 | 41 | 41 | 40 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 40 | 40 | 41 | 40 |  | 38 | 38 | 37 | 39 | 42 | 42 | 42 | 878880
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 17 | 18 |  | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 442332
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 5 | 5 | 5 | 11 | 11 | 11 | 11 | 241560
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 817900
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 12 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 481800
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 27 | 27 | 27 | 27 | 27 | 23 | 23 | 23 | 23 | 22 | 22 | 17 | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 | 29 | 29 | 31 | 31 | 31 | 529740
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 |  | 21 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 744700
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 17 | 17 | 8 | 8 | 24 | 24 | 24 | 24 | 24 | 24 | 25 | 25 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 643000
73 | Ghorashal 108MW PP (Regent) | 91 | 91 | 91 | 91 | 91 | 12 | 12 | 13 | 12 | 12 | 13 | 13 | 13 | 0 |  | 13 | 13 | 16 |  | 12 |  | 12 | 12 | 12 | 12 | 12 | 740181
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [19 empty] | 2 |  | 0 |  |  |  |  | 7680
78 | Gazipur 52 MW PP | 51 | 25 | 25 | 0 | [15 empty] | 36 | 51 | 51 | 51 | 51 | 51 | 51 | 422004
79 | Kodda 150MW PP | 82 | 32 | 32 | 0 | [15 empty] | 60 | 149 | 149 | 130 | 64 | 32 | 32 | 689760
80 | Jamalpur 95 MW PP(Powerpac) | 95 | 95 | 95 | 95 | 95 | 95 | 16 | 16 | 24 | 49 | 68 | 74 | 82 | 82 | 82 | 90 | 82 | 90 |  | 90 | 90 | 90 | 89 | 90 | 90 | 90 | 1884480
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | 25 | 0 | [14 empty] | 21 | 52 | 52 | 52 | 52 | 52 | 52 | 471398
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 70 | 52 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 |  | 89 | 89 | 89 | 106 | 106 | 105 | 105 | 1069752
| Kaptai 7 MW Solar PP |  |  |  |  | 0 | 0.23 | 2 | 2.62 | 3 | 5 | 4 | 4.12 | 4 | 5.15 | 1.11 | 1.4 | 0 | [9 empty] | 30240
Jodiac Power
| Karnaphuli Power Ltd. | 50 | 50 | 50 | 50 | 50 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 600506
82 | Madanganj 102 PP(Summit) | [19 empty] | 5 | 15 | 15 | 0 |  |  |  | 24864
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [19 empty] | 10 | [6 empty] | 13431
86 | Meghnaghat CCPP(Summit) | 280 | 275 | 265 | 290 | 265 | 260 | 250 | 250 | 278 | 292 | 277 | 282 | 281 | 275 | 282 | 280 | 281 | 265 |  | 268 | 245 | 264 | 270 | 260 | 281 | 246 | 6631360
87 | Meghnaghat 100 MW(IEL) | [19 empty] | 4 | 20 | 30 |  |  |  |  | 42240
88 | Ghorashal 78.5 MW PP(MAX) | 71 | 71 | 70 | 70 | 70 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | [9 empty] | 50 | 50 | 40 | 40 | 1022336
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 257760
92 | Fenchuganj 44MW (Energyprima) | 50 | 16 | 25 | 50 | 50 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 17 | 49 | 46 |  | 46 | 49 | 49 | 49 | 49 | 49 | 50 | 75996
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 30 | 43 | 43 | 43 | 43 | 43 | 696952
94 | Gagnagar 102 MW PP (Digital Power) | 0 | [18 empty] | 16 | 64 | 64 | 7 | 7 | 7 | 0 | 137520
95 | Patenga 50MW PP (Baraka) | 50 | 50 | 50 | 50 | 30 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 38 | 39 | 42 | 48 | 50 | 50 | 50 | 676320
96 | Chattogram 108 MW PP (ECPV) | 97 | 97 | 62 | 10 | 10 | 0 | [13 empty] | 12 | 40 | 42 | 44 | 44 | 44 | 44 | 541440
97 | Katpotti 52 MW PP (Sinha) | 39 | 39 | 39 | 39 | 39 | 37 | 38 | 39 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 23 | 47 | 47 | 47 | 47 | 47 | 795504
98 | Bosila 108MW PP(CLC) | 72 | 72 | 72 | 72 | 16 | 0 | [9 empty] | 4 | 8 | 8 |  | 67 | 72 | 72 | 72 | 72 | 72 | 72 | 723840
99 | Madanganj-55 MW PP(Summit) | [19 empty] | 15 | 30 | 15 | 0 |  |  |  | 63450
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 17 | 0 | [15 empty] | 55 | 55 | 55 | 55 | 55 | 35 | 17 | 405502
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 163 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 130 | 163 | 163 | 100 | 100 |  | 163 | 100 | 100 | 163 | 130 | 130 | 130 | 3424533
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0.1 | 0.5 | 0.4 | 1.2 | 0 | 0 | 1 | 1.8 | 0.9 | 0.3 | 0.2 | [9 empty] | 6900
103 | Kamalaghat 54 MW PP(Banco Energy) | 53 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 53 | 53 | 53 | 53 | 53 | 35 | 35 | 703800
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 140 | 140 | 80 | 32 | 32 | 32 | 7 | 7 | 7 | 9 | 45 | 50 | 50 | 50 | 50 | 16 | 16 | 16 |  | 65 | 170 | 150 | 150 | 150 | 150 | 150 | 1747200
112 | Aurahati 100MW PP (Aggreko) | [26 empty] | 0
114 | Kodda 149 MW PP Unit-1 (Summit) | 0 | [18 empty] | 17 | 70 | 82 | 53 | 15 | 15 | 15 | 231840
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 76 | 90 | 90 | 90 | 90 | 90 | 100 | 1151040
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 200 | 140 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 75 | 200 | 198 | 200 | 200 | 200 | 200 | 2148480
117 | Ashuganj 150MW PP (Midland) | 20 | 20 | 20 | 0 | [15 empty] | 6 | 50 | 50 | 50 | 50 |  |  | 272654
118 | Bibiyana-III 400 MW CCPP | 240 | 233 | 232 | 233 | 232 | 231 | 192 | 192 | 193 | 202 | 200 | 212 | 243 | 245 | 239 | 234 | 234 | 232 |  | 232 | 231 | 232 | 232 | 232 | 235 | 232 | 5469000
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 50 | 50 | 0 |  |  |  | 37 | 98 | 101 | 108 | 108 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2052000
| Anwara 300 MW PP (United) | 104 | 106 | 107 | 107 | 107 | 107 | 53 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 53 | 53 | 53 |  | 103 | 140 | 140 | 140 | 143 | 143 | 143 | 2057454
120 | Eastern Zone Total | 7796 | 7509 | 7368 | 7075 | 6757 | 6028.23 | 5561.1 | 5421.12 | 5431.4 | 5554.2 | 5598 | 5866.12 | 6001 | 5900.95 | 6277.01 | 6121.7 | 5847.2 | 5634 |  | 7073 | 7632 | 7778 | 7957 | 7778 | 7677 | 7556 | 158043044
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 83 | 66 | 49 | 49 | 49 | 16 | 16 | 49 | 49 | 49 | 49 | 59 | 66 | 66 | 66 | 66 | 16 | 16 |  | 66 | 99 | 99 | 99 | 99 | 99 | 115 | 1435200
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 5 | 0 | [14 empty] | 0 | 30 |  | 32 | 33 | 32 | 32 | 27 | 25 | 25 | 202080
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 105 | 70 | 70 | 35 | 35 | 53 | 53 | 53 | 53 | 89 | 88 | 88 | 88 | 88 | 53 | 53 |  | 88 | 100 | 105 | 105 | 105 | 105 | 105 | 2142720
130
131
132
133
| Barisal 110 MW PP (Summit ) | 96 | 64 | 64 | 48 | 48 | 48 | 48 | 16 | 16 | 0 | [6 empty] | 0 | 16 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 1118400
136 | Barisal GT PP Unit-1& 2 | [23 empty] | 23 | 23 | 0 | 47250
137 | Bhola 95 MW PP (Aggreko) | 97 | 97 | 97 | 96 | 96 | 63 | 55 | 23 | 42 | 42 | 41 | 41 | 42 | 42 | 47 | 50 | 50 | 45 |  | 81 | 90 | 94 | 97 | 97 | 96 | 97 | 1602741
| Bhola 225 MW CCPP | 180 | 180 | 180 | 180 | 180 | 180 | 179 | 179 | 179 | 179 | 179 | 180 | 180 | 180 | 180 | 174 | 174 | 173 |  | 174 | 162 | 168 | 170 | 172 | 172 | 161 | 4342441
140 | Bhola 33 MW PP (Venture) | 38 | 38 | 36 | 34 | 33 | 31 | 27 | 25 | 15 | 23 | 23 | 24 | 26 | 26 | 27 | 25 | 25 | 25 |  | 28 | 36 | 36 | 38 | 39 | 38 | 38 | 710285
141 | Noapara 100 MW PP (Bangla Trac) | [19 empty] | 22 | 50 | 50 | 50 | 76 | 97 | 100 | 427200
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 24 | 0 |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 32 | 32 | 32 |  | 32 | 32 | 32 | 40 | 40 | 40 | 40 | 726750
143 | Gopalganj 100 MW Peaking PP | 51 | 51 | 51 | 40 | 35 | 28 | 0 | [9 empty] | 30 | 35 |  | 60 | 56 | 55 | 53 | 47 | 47 | 47 | 607744
144 | Bheramara GTPP Unit-1,2 & 3 | [24 empty] | 16 | 16 | 25600
145 | Madhumati 100 MW PP | 87 | 87 | 87 | 86 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 86 | 86 | 86 | 86 | 86 |  | 82 | 70 | 69 | 42 | 17 | 17 | 35 | 1812816
146 | Bheramara HVDC | 776 | 776 | 776 | 776 | 904 | 905 | 905 | 904 | 904 | 903 | 904 | 903 | 903 | 903 | 903 | 903 | 903 | 903 |  | 903 | 904 | 903 | 903 | 904 | 902 | 903 | 21139636
147 | Bheramara 360 MW CCPP | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 270 | 270 | 270 | 270 | 300 | 300 | 300 | 330 | 330 | 300 | 230 |  | 410 | 380 | 360 | 410 | 410 | 410 | 410 | 8032896
148
149
150 | Barapukuria TPP Unit-1 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 92 | 94 | 95 | 94 | 94 | 95 | 95 | 95 | 94 | 93 | 93 |  | 94 | 94 | 94 | 95 | 95 | 94 | 94 | 2268218
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 269 | 270 | 270 | 6548200
153 | Baghabari 71 MW GTPP | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 60 | 60 | 60 | 1375000
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 50 | 0 | [17 empty] | 42 | 50 | 50 | 50 | 50 | 0 | 0 | 273571
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 199 | 195 | 193 | 196 | 192 | 190 | 181 | 174 | 170 | 171 | 182 | 203 | 199 | 185 | 202 | 198 | 180 | 166 |  | 189 | 206 | 201 | 190 | 182 | 181 | 177 | 4864800
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 199 | 195 | 193 | 194 | 187 | 187 | 162 | 157 | 156 | 167 | 165 | 195 | 207 | 203 | 207 | 206 | 175 | 156 |  | 184 | 187 | 187 | 191 | 188 | 193 | 186 | 4694518
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 270 | 133 | 0 | [12 empty] | 0 | 95 | 94 | 223 | 2933545
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [19 empty] | 10 | 21 | 39 | 25 | 0 | 0 |  | 69885
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 512640
163 | Bogura 20 MW PP (Energyprima) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 10 | 14 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 365328
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 211068
165 | Amnura 50 MW PP(Sinha) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 50 | 50 | 50 | 50 | 50 | 12 | 12 | 452480
166 | Katakhali 50 MW PP (Northern) | 50 | 50 | 50 | 50 | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 32 | 32 | 32 | 32 | 32 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 874755
167 | Katakhali 50 MW Peaking PP | [19 empty] | 40 | 46 | 47 | 45 | 45 | 45 | 45 | 228775
168 | Santahar 50 MW Peaking PP | 21 | 20 | 0 | [16 empty] | 15 | 18 | 30 | 29 | 20 | 20 | 20 | 159912
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 34 | 34 | 34 | 34 | 34 | 8 | 8 | 8 | 8 | 8 | 24 | 25 | 25 | 25 | 8 | 8 |  | 39 | 52 | 52 | 52 | 43 | 43 | 43 | 684480
170 | Chapainawabganj 100 MW Peaking PP | 70 | 48 | 48 | 48 | 24 | 24 | 0 | [12 empty] | 50 | 94 | 94 | 94 | 94 | 94 | 93 | 765744
171 | Baghabari 200 MW PP (Paramount)
172 | Bagura 113 MW PP (Confidence) | 113 | 113 | 113 | 113 | 113 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 37 | 37 |  | 75 | 108 | 110 | 113 | 113 | 113 | 113 | 1749696
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 16 | 16 | 16 | 0 | [15 empty] | 15 | 0 | [5 empty] | 66000
176 | Rangpur 113 MW PP (Confidence) | 107 | 107 | 107 | 107 | 76 | 34 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 | 45 | 35 | 35 |  | 95 | 100 | 109 | 113 | 107 | 99 | 114 | 1614720
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 1 | 4 | 3 | 4 | 2.04 | 3 | 1.6 | 0.7 | 2 | 0.2 | [9 empty] | 22515
178
178