## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-08-18 | Tuesday
|  |  | Date (day): | 2020-08-18 |  | Tuesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13697.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14851 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-08-17 | 2020-08-18 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 28 | 28 | 28 | 28 |  | 57 | Unit-2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 110 | 110 | 110 | 110
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 69 | 66 | 78 | 78
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 94 | 99 | 100 | 100 |  | 8 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under maint.
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 347 | 355 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 350 | 400 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 7 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 300 | 280 | 305 | 305
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 80 | 96 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 20 | 100 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 91 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 204 | 180 | 210 | 210
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 93 | 16 | 85 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 1 | 47 | 49 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 53 | 53 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 149 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 50 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 55 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 8 | 35 | 50
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 267 | 286 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 80 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 131 | 133 | 131 | 131 |  | 18 | Engine problem
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 89 | 70 | 100 | 100
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 17 | 104 | 104
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 2634 | 2908 | 3586 | 3880 | 423 | 1379
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 110 | 110 | 110 | 70 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 8 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 17.86 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 16 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 157 | 158 | 158 | 158 | 72 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 230 | 164 | 165 | 165 | 60 |  | Gas shortage
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 50 | 104 | 105 | 105 | 50 |  | Gas shortage
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 37 | 100 | 100
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 100 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 28 | 10 | 25
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 72 | 91 | 97 | 97 |  | 11 | Engine problem
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2.9 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 179 | 234 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 50 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 1034.76 | 1202 | 1663 | 1717 | 432 | 109
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 80 | 100 | 129 | 129
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 192 | 216 | 220 | 220
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 290 | 300 | 360 | 360
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 275 | 360 | 360
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 25 | 38 | 38
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 20 | 20 | 35 |  | Gas shortage
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 16 | 16 | 16 | 179 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 10 | 51 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 30 | 100 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 42
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 96 | 87 | 92 | 96 |  | 67 | ST under shut down
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 200 | 200
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 112 | 142 | 163 | 173
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 43 | 43 | 43
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 20 | 20 | 20 |  | 5 | Engine problem
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 114 | 114 | 114
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 47 | 57 | 60 | 60 | 53 |  | Fuel shortage.
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1249 | 1608 | 2094 | 2350 | 536 | 72
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 138 | 124 | 157 | 157 | 45 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 20 | 20 | 20
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 56 | 72 | 72 | 72 |  | 23 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.5 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 200 | 200 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 16 | 115 | 115 | 115
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 429.5 | 531 | 565.6 | 564 | 45 | 23
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 86 | 88 | 88 | 88
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 130 | 163 | 163
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 205 | 198 | 210 | 210
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 50 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 45 | 49 | 49 | 49
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 63 | 63 | 61 | 66
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 85 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 50 | 80 | 80 | 80 |  | 151 | Engine problem
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 270 | 341 | 341
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1091 | 1106 | 1223 | 1228 | 0 | 551
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 917 | 916 | 928 | 928
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 115 | 115 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 230 | 180 | 225
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 355 | 340 | 410 | 410
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 60 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 55 | 90 | 90 |  | 15 | Engine problem
| 108 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1507 | 1796 | 1923 | 2114 | 0 | 15
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 64 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 19 | 30 | 33 | 33
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 89 | 89 | 89 | 89 |  | 105 | GT-2 & ST Under maint.
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 43 | 78 | 76 | 76 |  | 19 | Engine problem
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 465 | 622 | 470 | 660
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 616 | 883 | 778 | 968 | 0 | 124
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 70 | 70 | 70 | 30 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 43
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 35 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 25 | 50 | 50
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 44 | 0 | 45
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | S/D for ST Under maint.
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 171 | 177 | 220 | 220
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 150 | 180 | 220 | 220
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 403 | 388 | 414 | 414
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 26 | 0 | 35
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 17 | 18 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 11 | 11 | 10 | 10
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 10 | 10
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 52 | 52 | 52
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 96 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 23 | 94 | 113 | 113
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 109 | 109 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 892 | 1386 | 1594 | 1757 | 361 | 0
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 149 | 149 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 100 | 113 | 113 | 113
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3.5 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 252.5 | 262 | 271 | 273 | 294 | 30
|  | Total |  |  |  |  | 20383 | 19892 | 9705.76 | 11682 | 13697.6 | 14851 | 2091 | 2303
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9272.8974 | 11161 | 13086.7072 | 14188.6673
| A. |  | 2020-08-17 | (Yesterday) |  |  |  |  | Monday
| 1 | Highest Generation : |  |  | 11682 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 8409.87 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11682 | MW
| 3 | Day peak Generation : |  |  | 9705.76 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11161 | MW
| 4 | Evening peak Generation : |  |  | 11682 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 242.3488 | MKWHr | By Solar | 0.13428 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 130.5371 | MKWHr |  | By Oil: | 66.4831 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 16.6355 | MKWHr |  | By Hydro: | 3.7123 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2091 | MW | Dhaka | 3804 | 3804 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2303 | MW | Chittagong | 1034 | 1034 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4394 | MW | Khulna | 1454 | 1454 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1138.05 | MMCFD |  |  | Rajshahi | 1274 | 1274 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 151706536.568 | ii) Oil : | Taka | 506614200.32 | Comilla | 1043 | 1043 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 76790993 | Total | Taka | 735111729.888 | Mymensingh | 975 | 975 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.002 | MKWHr. | Sylhet | 480 | 480 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 270 | MW (E to W) at | 21:00 | hrs | Barisal | 315 | 315 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 63 | MW at | 4:00 | hrs | Rangpur | 782 | 782 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 31.5° C |  |  | Total | 11161 | 11161 |  | 0
| B. |  | 2020-08-18 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 33.1° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 11900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14851 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 9900 | MW
| 4 | Reserve(Generation end) |  |  |  | 2951 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 246.8713 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8485 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.9695 | MKWHr. | ii) HVDC Flow at Peak Time |  | 916 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.8771 | MKWHr. | iii) Maximum HVDC Flow : |  | 917 | MW at | 9:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 94.05 |  | (b) Today: | 93.89 |  | (c) Rule Curve: |  | 94.44
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-08-17
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 28 | 0 | 0 | 110 | 0 | 99 | 69 | 0 | 303 |  | 0 | 370 | 290 | 7 | 80 | 35 | 295 | 0 | 0 | 0 | 100 | 93 | 82 | 0 | 0 | 0 | 47 | 53 | 55 | 17 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 82 | 70 | 110 | 0 | 0 | 164 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 91 | 50 | 18 | 27 | 0 | 80 | 0 | 270 | 230 | 215 | 8 | 90 | 10 | 5 | 0 | 51 | 0 | 50 | 43 | 21 | 8 | 25 | 18 | 130 | 142 | 72 | 20 | 0 | 88 | 30 | 50 | 48 | 163 | 202 | 62 | 85 | 0 | 50 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 286 | 0 | 0 | 193 | 0 | 131 | 0 | 100 | 0 | 80 | 0 | 115 | 17 | 0 | 0 | 233 | 0 | 0 | 0 | 47 | 100 | 0 | 30 |  | 914 | 0 | 345 | 0 | 113 | 160 | 0 | 0 | 0 | 0 | 40 | 89 | 32 | 0 | 0 | 0 | 0 | 50 | 0 | 90 | 0 | 0 | 44 | 52 | 25 | 18 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 172 | 0 | 77 | 30 | 215 | 0 | 402 | 53 | 0 | 57 | 0 | 107 | 0 | 0 | 109 | 540 |  | 6936 | 3905 | 10841 | 3411 | 914 | 2118 | 2926 | 689 | 152 | 501 | 130 | 0 | 0 | 94.1
2:00 | 28 | 0 | 0 | 110 | 0 | 99 | 69 | 0 | 303 |  | 0 | 370 | 300 | 7 | 80 | 0 | 298 | 0 | 0 | 0 | 100 | 93 | 64 | 0 | 0 | 0 | 47 | 53 | 55 | 0 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 82 | 70 | 110 | 0 | 0 | 164 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 91 | 0 | 18 | 27 | 0 | 80 | 0 | 265 | 230 | 181 | 8 | 92 | 10 | 5 | 0 | 51 | 0 | 0 | 43 | 21 | 8 | 25 | 18 | 126 | 158 | 72 | 20 | 0 | 88 | 30 | 50 | 48 | 163 | 200 | 62 | 85 | 0 | 50 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 280 | 0 | 0 | 194 | 0 | 131 | 0 | 100 | 0 | 80 | 0 | 115 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 47 | 100 | 0 | 17 |  | 914 | 0 | 345 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 89 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 174 | 0 | 77 | 0 | 215 | 0 | 408 | 17 | 0 | 57 | 0 | 107 | 0 | 0 | 109 | 520 |  | 6717 | 3616 | 10333 | 3393 | 914 | 2122 | 2683 | 669 | 152 | 274 | 126 | 0 | 0 | 94.09
3:00 | 28 | 0 | 0 | 110 | 0 | 99 | 67 | 0 | 303 |  | 0 | 370 | 300 | 7 | 80 | 0 | 301 | 0 | 0 | 0 | 100 | 93 | 48 | 0 | 0 | 0 | 0 | 53 | 55 | 0 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 82 | 70 | 110 | 0 | 0 | 164 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 25 | 0 | 18 | 27 | 0 | 80 | 0 | 270 | 235 | 183 | 8 | 92 | 10 | 5 | 0 | 51 | 0 | 0 | 20 | 21 | 8 | 25 | 21 | 122 | 157 | 72 | 20 | 0 | 88 | 30 | 50 | 48 | 163 | 197 | 62 | 85 | 0 | 50 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 270 | 0 | 0 | 195 | 0 | 131 | 0 | 100 | 0 | 80 | 0 | 75 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 47 | 100 | 0 | 17 |  | 914 | 0 | 345 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 174 | 0 | 77 | 0 | 215 | 0 | 414 | 0 | 0 | 57 | 0 | 106 | 0 | 0 | 109 | 518 |  | 6534 | 3553 | 10087 | 3407 | 914 | 2131 | 2440 | 667 | 152 | 254 | 122 | 0 | 0 | 94.08
4:00 | 28 | 0 | 0 | 110 | 0 | 99 | 65 | 0 | 303 |  | 0 | 370 | 300 | 7 | 80 | 0 | 298 | 0 | 0 | 0 | 100 | 93 | 32 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 83 | 70 | 110 | 0 | 0 | 164 | 0 | 101 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 27 | 0 | 80 | 0 | 270 | 230 | 182 | 8 | 92 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 25 | 21 | 116 | 158 | 72 | 20 | 0 | 88 | 30 | 50 | 48 | 163 | 196 | 62 | 85 | 0 | 50 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 270 | 0 | 0 | 195 | 0 | 131 | 0 | 100 | 0 | 10 | 0 | 75 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 53 | 100 | 0 | 17 |  | 914 | 0 | 345 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 152 | 0 | 76 | 0 | 215 | 0 | 410 | 0 | 0 | 0 | 0 | 107 | 0 | 0 | 109 | 500 |  | 6346 | 3382 | 9728 | 3377 | 914 | 2114 | 2237 | 649 | 153 | 168 | 116 | 0 | 0 | 94.07
5:00 | 28 | 0 | 0 | 110 | 0 | 99 | 64 | 0 | 303 |  | 0 | 370 | 295 | 7 | 80 | 0 | 307 | 0 | 0 | 0 | 90 | 58 | 32 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 85 | 70 | 110 | 0 | 0 | 164 | 0 | 102 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 33 | 0 | 80 | 0 | 265 | 235 | 185 | 8 | 95 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 25 | 21 | 112 | 158 | 72 | 20 | 0 | 88 | 30 | 50 | 48 | 163 | 204 | 62 | 85 | 0 | 50 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 215 | 0 | 0 | 195 | 0 | 131 | 0 | 100 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 56 | 100 | 0 | 17 |  | 913 | 0 | 345 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 153 | 0 | 78 | 0 | 215 | 0 | 403 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 70 | 500 |  | 6229 | 3326 | 9555 | 3397 | 913 | 2112 | 2049 | 649 | 155 | 168 | 112 | 0 | 0 | 94.06
6:00 | 28 | 0 | 0 | 110 | 0 | 99 | 67 | 0 | 303 |  | 0 | 370 | 295 | 7 | 70 | 0 | 300 | 0 | 0 | 0 | 40 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 85 | 70 | 110 | 0 | 0 | 164 | 0 | 99 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 33 | 0 | 80 | 0 | 265 | 240 | 181 | 8 | 95 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 25 | 19 | 106 | 158 | 50 | 20 | 0.1 | 88 | 30 | 50 | 48 | 130 | 200 | 62 | 85 | 0 | 50 | 18 | 0 | 10 | 275 | 24 | 8 | 0 | 110 | 0 | 0 | 200 | 0 | 118 | 0.4 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 125 | 0 | 0 | 0 | 56 | 100 | 0 | 17 |  | 914 | 0 | 345 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 152 | 0 | 77 | 0 | 216 | 0 | 333 | 0 | 0 | 0 | 0 | 44 | 0 | 0.1 | 35 | 488 |  | 5693.8 | 3083.1 | 8776.9 | 3379 | 914 | 1991 | 1474 | 637 | 155 | 120 | 106 | 0.9 | 0 | 94.05
7:00 | 28 | 0 | 0 | 110 | 0 | 99 | 66 | 0 | 303 |  | 0 | 340 | 310 | 7 | 48 | 0 | 314 | 0 | 0 | 0 | 40 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 86 | 70 | 110 | 0 | 0 | 164 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 28 | 0 | 80 | 0 | 290 | 240 | 197 | 8 | 95 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 25 | 14 | 96 | 157 | 24 | 20 | 0.2 | 88 | 30 | 50 | 48 | 110 | 206 | 67 | 85 | 0 | 50 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 110 | 0 | 0 | 200 | 0 | 102 | 2.2 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 87 | 0 | 0 | 0 | 56 | 100 | 0 | 17 |  | 914 | 0 | 365 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 158 | 0 | 33 | 0 | 150 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 35 | 470 |  | 5491.7 | 2962.8 | 8454.5 | 3286 | 914 | 1934 | 1326 | 619 | 156 | 120 | 96 | 3.5 | 0 | 94.04
8:00 | 28 | 0 | 0 | 110 | 0 | 98 | 60 | 0 | 352 |  | 0 | 340 | 290 | 7 | 48 | 0 | 288 | 0 | 0 | 0 | 45 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 87 | 70 | 110 | 0 | 0 | 164 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 2 | 0 | 80 | 0 | 270 | 250 | 182 | 8 | 90 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 25 | 14 | 98 | 157 | 24 | 20 | 0.3 | 88 | 30 | 50 | 48 | 130 | 200 | 67 | 83 | 0 | 50 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 110 | 0 | 0 | 200 | 0 | 102 | 5.27 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 87 | 0 | 0 | 0 | 57 | 100 | 0 | 17 |  | 914 | 0 | 345 | 0 | 73 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 32 | 0 | 150 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 35 | 472 |  | 5474.47 | 2935.4 | 8409.87 | 3206 | 914 | 1966 | 1319 | 622 | 157 | 120 | 98 | 7.87 | 0 | 94.03
9:00 | 28 | 0 | 0 | 110 | 0 | 98 | 60 | 0 | 354 |  | 0 | 340 | 295 | 8 | 55 | 0 | 306 | 0 | 0 | 0 | 80 | 32 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 19 | 25 | 26 | 33 | 33 | 0 | 0 | 87 | 70 | 110 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 2 | 0 | 80 | 0 | 270 | 260 | 184 | 8 | 91 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 25 | 14 | 106 | 157 | 24 | 20 | 0.9 | 88 | 30 | 50 | 48 | 130 | 202 | 64 | 83 | 0 | 50 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 124 | 0 | 0 | 200 | 0 | 127 | 6.39 | 100 | 0 | 13 | 0 | 0 | 0 | 0 | 0.3 | 123 | 0 | 0 | 0 | 47 | 100 | 0 | 17 |  | 917 | 0 | 345 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 162 | 0 | 32 | 0 | 150 | 0 | 397 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 35 | 472 |  | 5719.59 | 3020.4 | 8739.99 | 3307 | 917 | 2014 | 1488 | 621 | 157 | 120 | 106 | 9.99 | 0 | 94.02
10:00 | 28 | 0 | 0 | 110 | 0 | 93 | 60 | 0 | 350 |  | 0 | 340 | 305 | 7 | 80 | 22 | 308 | 0 | 0 | 0 | 91 | 58 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 25 | 19 | 25 | 26 | 33 | 33 | 0 | 0 | 89 | 70 | 110 | 0 | 0 | 231 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 2 | 0 | 80 | 0 | 275 | 285 | 192 | 8 | 95 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 25 | 14 | 110 | 154 | 26 | 20 | 1.5 | 88 | 30 | 50 | 48 | 130 | 209 | 63 | 83 | 0 | 50 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 227 | 0 | 0 | 200 | 0 | 130 | 6.25 | 100 | 0 | 43 | 0 | 2 | 52 | 0 | 1.9 | 195 | 0 | 0 | 0 | 52 | 100 | 0 | 17 |  | 917 | 0 | 345 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 167 | 0 | 32 | 0 | 150 | 0 | 411 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 70 | 468 |  | 6217.65 | 3072.6 | 9290.25 | 3367 | 917 | 2017 | 1971 | 617 | 159 | 120 | 110 | 12.25 | 0 | 94.01
11:00 | 28 | 0 | 0 | 110 | 0 | 93 | 60 | 0 | 350 |  | 0 | 340 | 270 | 7 | 80 | 45 | 279 | 0 | 0 | 0 | 91 | 93 | 0 | 5 | 0 | 0 | 0 | 53 | 55 | 35 | 19 | 25 | 6 | 33 | 33 | 0 | 0 | 88 | 70 | 110 | 0 | 0 | 230 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 17 | 0 | 18 | 2 | 0 | 80 | 0 | 270 | 275 | 215 | 8 | 85 | 10 | 5 | 0 | 10 | 0 | 0 | 0 | 21 | 5 | 25 | 18 | 116 | 154 | 41 | 20 | 1.3 | 87 | 30 | 50 | 45 | 110 | 195 | 64 | 84 | 0 | 50 | 18 | 0 | 10 | 290 | 24 | 2 | 0 | 269 | 0 | 0 | 193 | 0 | 133 | 11.37 | 90 | 0 | 60 | 0 | 16 | 53 | 0 | 2.8 | 179 | 0 | 0 | 0 | 47 | 100 | 0 | 17 |  | 917 | 0 | 345 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 187 | 0 | 31 | 0 | 150 | 0 | 386 | 0 | 0 | 0 | 0 | 39 | 0 | 1.8 | 109 | 465 |  | 6234.47 | 3166.8 | 9401.27 | 3318 | 917 | 1920 | 2212 | 615 | 158 | 128 | 116 | 17.27 | 0 | 94
12:00 | 28 | 0 | 0 | 110 | 0 | 94 | 69 | 0 | 347 |  | 0 | 350 | 300 | 7 | 80 | 40 | 204 | 0 | 0 | 0 | 91 | 93 | 0 | 20 | 0 | 0 | 1 | 53 | 55 | 50 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 87 | 70 | 110 | 0 | 0 | 230 | 0 | 50 | 0 |  | 0 | 0 | 0 | 0 | 72 | 16 | 18 | 2 | 0 | 80 | 0 | 290 | 300 | 192 | 8 | 96 | 10 | 5 | 0 | 10 | 0 | 0 | 0 | 21 | 5 | 25 | 18 | 112 | 138 | 56 | 17 | 2.5 | 86 | 30 | 50 | 45 | 130 | 205 | 63 | 85 | 0 | 50 | 18 | 0 | 10 | 290 | 24 | 5 | 0 | 267 | 0 | 0 | 200 | 0 | 131 | 17.86 | 90 | 0 | 30 | 0 | 16 | 89 | 0 | 2.9 | 179 | 0 | 0 | 0 | 47 | 90 | 0 | 17 |  | 917 | 0 | 355 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 171 | 0 | 43 | 0 | 150 | 0 | 403 | 0 | 0 | 23 | 0 | 100 | 0 | 3.5 | 109 | 465 |  | 6438.26 | 3267.5 | 9705.76 | 3334 | 917 | 1988 | 2437 | 614 | 157 | 120 | 112 | 26.76 | 0 | 93.99
13:00 | 28 | 0 | 0 | 110 | 0 | 94 | 68 | 0 | 345 |  | 0 | 350 | 280 | 7 | 80 | 55 | 209 | 0 | 0 | 0 | 91 | 93 | 0 | 34 | 0 | 0 | 47 | 53 | 55 | 35 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 81 | 70 | 110 | 0 | 0 | 231 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 90 | 32 | 18 | 3 | 0 | 80 | 0 | 270 | 275 | 183 | 8 | 85 | 10 | 5 | 0 | 25 | 0 | 0 | 0 | 21 | 8 | 25 | 18 | 114 | 124 | 72 | 20 | 1.8 | 88 | 30 | 47 | 48 | 130 | 195 | 64 | 84 | 0 | 80 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 267 | 0 | 0 | 200 | 0 | 131 | 8.91 | 100 | 0 | 30 | 0 | 8 | 89 | 0 | 1.5 | 179 | 0 | 0 | 0 | 47 | 90 | 0 | 17 |  | 917 | 0 | 345 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 157 | 0 | 43 | 0 | 150 | 0 | 404 | 0 | 0 | 51 | 0 | 108 | 0 | 7.9 | 109 | 464 |  | 6541.21 | 3284.9 | 9826.11 | 3324 | 917 | 2001 | 2565 | 614 | 151 | 120 | 114 | 20.11 | 0 | 93.98
14:00 | 28 | 0 | 0 | 110 | 0 | 95 | 68 | 0 | 304 |  | 0 | 320 | 295 | 7 | 80 | 55 | 210 | 0 | 0 | 0 | 91 | 93 | 0 | 40 | 0 | 0 | 47 | 40 | 55 | 35 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 81 | 70 | 110 | 0 | 0 | 191 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 90 | 0 | 18 | 3 | 0 | 80 | 0 | 270 | 325 | 183 | 8 | 91 | 10 | 5 | 0 | 31 | 0 | 0 | 0 | 21 | 8 | 25 | 18 | 122 | 122 | 72 | 20 | 0.2 | 88 | 30 | 50 | 49 | 110 | 210 | 64 | 85 | 0 | 80 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 267 | 0 | 0 | 200 | 0 | 131 | 10.5 | 100 | 0 | 30 | 0 | 8 | 51 | 0 | 1.7 | 179 | 0 | 0 | 0 | 47 | 98 | 0 | 17 |  | 917 | 0 | 345 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 17 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 156 | 0 | 43 | 0 | 185 | 0 | 402 | 0 | 0 | 56 | 0 | 113 | 0 | 2.2 | 109 | 464 |  | 6435.4 | 3369.2 | 9804.6 | 3388 | 917 | 1908 | 2521 | 614 | 151 | 169 | 122 | 14.6 | 0 | 93.97
15:00 | 28 | 0 | 0 | 110 | 0 | 93 | 67 | 0 | 304 |  | 0 | 360 | 315 | 7 | 80 | 55 | 210 | 0 | 0 | 0 | 91 | 16 | 0 | 40 | 0 | 0 | 47 | 53 | 55 | 35 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 81 | 70 | 110 | 0 | 0 | 165 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 2 | 0 | 80 | 0 | 285 | 295 | 198 | 8 | 94 | 10 | 5 | 0 | 31 | 0 | 0 | 0 | 21 | 8 | 25 | 18 | 120 | 122 | 72 | 20 | 0.2 | 88 | 30 | 50 | 49 | 110 | 211 | 61 | 85 | 0 | 80 | 18 | 0 | 10 | 310 | 24 | 11 | 0 | 269 | 0 | 0 | 188 | 0 | 133 | 15.5 | 100 | 0 | 30 | 0 | 8 | 70 | 0 | 2.7 | 179 | 0 | 0 | 0 | 48 | 100 | 0 | 17 |  | 917 | 0 | 375 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 17 | 11 | 10 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 170 | 0 | 43 | 0 | 150 | 0 | 400 | 0 | 0 | 56 | 0 | 108 | 0 | 1.9 | 109 | 465 |  | 6435.4 | 3370.9 | 9806.3 | 3359 | 917 | 1970 | 2486 | 614 | 151 | 169 | 120 | 20.3 | 0 | 93.96
16:00 | 28 | 0 | 0 | 110 | 0 | 93 | 68 | 0 | 304 |  | 0 | 400 | 285 | 7 | 80 | 55 | 182 | 0 | 0 | 0 | 93 | 16 | 0 | 25 | 0 | 0 | 47 | 53 | 55 | 35 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 82 | 70 | 110 | 0 | 0 | 164 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 60 | 0 | 18 | 2 | 0 | 80 | 0 | 270 | 275 | 182 | 8 | 92 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 25 | 18 | 116 | 124 | 72 | 20 | 1.4 | 88 | 30 | 50 | 46 | 130 | 200 | 62 | 85 | 0 | 80 | 18 | 0 | 10 | 285 | 24 | 11 | 0 | 267 | 0 | 0 | 200 | 0 | 132 | 0 | 100 | 0 | 30 | 0 | 8 | 48 | 0 | 0.6 | 179 | 0 | 0 | 0 | 52 | 100 | 0 | 17 |  | 916 | 0 | 345 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 17 | 11 | 10 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 175 | 0 | 41 | 0 | 175 | 0 | 392 | 0 | 0 | 56 | 0 | 107 | 0 | 1.8 | 35 | 465 |  | 6307 | 3284.8 | 9591.8 | 3286 | 916 | 2006 | 2329 | 614 | 152 | 169 | 116 | 3.8 | 0 | 93.95
17:00 | 28 | 0 | 0 | 110 | 0 | 98 | 68 | 0 | 304 |  | 0 | 400 | 290 | 7 | 80 | 30 | 177 | 0 | 0 | 0 | 60 | 16 | 0 | 10 | 0 | 0 | 24 | 53 | 55 | 35 | 19 | 25 | 29 | 33 | 33 | 0 | 0 | 82 | 70 | 110 | 0 | 0 | 164 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 51 | 0 | 18 | 8 | 0 | 80 | 0 | 270 | 275 | 182 | 16 | 85 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 25 | 18 | 112 | 124 | 32 | 20 | 0.3 | 88 | 30 | 50 | 40 | 130 | 196 | 62 | 85 | 0 | 80 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 180 | 0 | 0 | 200 | 0 | 133 | 0.9 | 100 | 0 | 30 | 0 | 8 | 35 | 0 | 0.1 | 124 | 0 | 0 | 0 | 51 | 100 | 0 | 25 |  | 916 | 0 | 345 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 17 | 11 | 10 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 181 | 0 | 43 | 0 | 180 | 0 | 356 | 0 | 0 | 35 | 0 | 75 | 0 | 1.7 | 35 | 450 |  | 6015.3 | 3194.7 | 9210 | 3280 | 916 | 1990 | 1989 | 599 | 152 | 169 | 112 | 3 | 0 | 93.94
18:00 | 28 | 0 | 0 | 110 | 0 | 99 | 68 | 0 | 262 |  | 0 | 320 | 295 | 7 | 80 | 30 | 153 | 0 | 0 | 0 | 50 | 16 | 0 | 10 | 0 | 0 | 24 | 53 | 55 | 35 | 22 | 25 | 29 | 33 | 33 | 8 | 0 | 84 | 70 | 110 | 0 | 0 | 164 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 51 | 0 | 18 | 4 | 0 | 80 | 0 | 270 | 275 | 183 | 16 | 95 | 10 | 5 | 0 | 43 | 0 | 0 | 1 | 21 | 8 | 25 | 18 | 114 | 124 | 16 | 20 | 0 | 88 | 30 | 47 | 49 | 130 | 199 | 40 | 40 | 0 | 80 | 18 | 0 | 10 | 270 | 24 | 8 | 0 | 180 | 0 | 0 | 200 | 0 | 132 | 0 | 100 | 0 | 33 | 0 | 8 | 35 | 0 | 0 | 125 | 0 | 0 | 17 | 57 | 60 | 0 | 28 |  | 917 | 0 | 343 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 20 | 8 | 0 | 0 | 0 | 0 | 5 | 49 | 0 | 8 | 0 | 1 | 0 | 17 | 11 | 10 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 159 | 0 | 42 | 0 | 150 | 0 | 345 | 0 | 0 | 35 | 0 | 70 | 0 | 0.5 | 35 | 450 |  | 5782 | 3149.5 | 8931.5 | 3197 | 917 | 1798 | 1978 | 599 | 154 | 174 | 114 | 0.5 | 0 | 93.94
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 28 | 0 | 0 | 110 | 0 | 99 | 69 | 0 | 287 |  | 0 | 370 | 305 | 7 | 92 | 45 | 154 | 0 | 0 | 0 | 70 | 16 | 149 | 60 | 0 | 0 | 31 | 53 | 55 | 35 | 22 | 25 | 20 | 33 | 33 | 34 | 0 | 86 | 70 | 110 | 0 | 7 | 164 | 0 | 104 | 0 |  | 0 | 0 | 68 | 0 | 68 | 21 | 18 | 10 | 0 | 100 | 0 | 275 | 285 | 193 | 16 | 95 | 20 | 5 | 0 | 43 | 0 | 50 | 19 | 21 | 8 | 25 | 20 | 136 | 123 | 46 | 20 | 0 | 88 | 30 | 47 | 49 | 130 | 203 | 62 | 85 | 0 | 80 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 219 | 0 | 0 | 200 | 0 | 133 | 0 | 100 | 35 | 72 | 0 | 43 | 56 | 0 | 0 | 230 | 0 | 0 | 114 | 56 | 100 | 0 | 17 |  | 915 | 0 | 350 | 0 | 115 | 165 | 0 | 0 | 0 | 0 | 40 | 90 | 25 | 80 | 0 | 0 | 0 | 50 | 35 | 90 | 0 | 16 | 42 | 36 | 18 | 17 | 11 | 10 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 159 | 0 | 77 | 4 | 150 | 0 | 383 | 90 | 0 | 62 | 0 | 84 | 0 | 0 | 95 | 468 |  | 6920 | 3826 | 10746 | 3281 | 915 | 2013 | 2961 | 617 | 156 | 667 | 136 | 0 | 0 | 93.93
19:30 | 28 | 0 | 0 | 110 | 0 | 99 | 69 | 0 | 303 |  | 0 | 370 | 300 | 7 | 96 | 55 | 180 | 0 | 0 | 0 | 100 | 16 | 149 | 90 | 0 | 0 | 47 | 53 | 55 | 35 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 86 | 70 | 110 | 0 | 8 | 164 | 0 | 104 | 0 |  | 0 | 0 | 68 | 0 | 91 | 50 | 18 | 15 | 0 | 100 | 0 | 270 | 275 | 189 | 16 | 95 | 25 | 5 | 0 | 43 | 0 | 50 | 24 | 21 | 11 | 25 | 20 | 126 | 123 | 71 | 20 | 0 | 88 | 30 | 47 | 49 | 130 | 203 | 62 | 85 | 0 | 80 | 18 | 0 | 10 | 305 | 24 | 11 | 0 | 286 | 0 | 0 | 200 | 0 | 133 | 0 | 100 | 50 | 100 | 0 | 112 | 105 | 0 | 0 | 231 | 0 | 0 | 114 | 57 | 100 | 0 | 17 |  | 916 | 0 | 345 | 0 | 115 | 170 | 0 | 0 | 0 | 0 | 40 | 90 | 28 | 80 | 0 | 0 | 0 | 50 | 35 | 100 | 0 | 25 | 45 | 52 | 26 | 17 | 11 | 10 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 172 | 0 | 76 | 50 | 180 | 0 | 382 | 90 | 0 | 96 | 0 | 113 | 0 | 0 | 109 | 605 |  | 7397 | 4177 | 11574 | 3344 | 916 | 2060 | 3525 | 754 | 156 | 693 | 126 | 0 | 0 | 0
20:00 | 28 | 0 | 0 | 110 | 0 | 99 | 69 | 0 | 303 |  | 0 | 370 | 280 | 7 | 96 | 55 | 180 | 0 | 0 | 0 | 100 | 16 | 149 | 92 | 0 | 0 | 48 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 86 | 70 | 110 | 0 | 8 | 164 | 0 | 104 | 0 |  | 0 | 0 | 68 | 0 | 91 | 50 | 18 | 24 | 0 | 100 | 0 | 270 | 275 | 182 | 16 | 87 | 25 | 5 | 0 | 51 | 0 | 50 | 43 | 21 | 11 | 25 | 20 | 140 | 124 | 71 | 20 | 0 | 88 | 30 | 47 | 49 | 130 | 194 | 62 | 85 | 0 | 80 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 286 | 0 | 0 | 200 | 0 | 132 | 0 | 100 | 102 | 100 | 0 | 115 | 105 | 0 | 0 | 233 | 0 | 0 | 114 | 57 | 100 | 0 | 17 |  | 917 | 0 | 345 | 0 | 115 | 190 | 0 | 0 | 0 | 0 | 40 | 90 | 29 | 80 | 0 | 0 | 0 | 50 | 35 | 100 | 0 | 25 | 47 | 52 | 27 | 17 | 11 | 10 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 176 | 0 | 75 | 75 | 180 | 0 | 371 | 90 | 0 | 94 | 0 | 112 | 0 | 0 | 109 | 580 |  | 7458 | 4191 | 11649 | 3325 | 917 | 2041 | 3625 | 729 | 156 | 716 | 140 | 0 | 0 | 93.93
21:00 | 28 | 0 | 0 | 110 | 0 | 99 | 66 | 0 | 355 |  | 0 | 400 | 280 | 7 | 96 | 55 | 180 | 0 | 0 | 0 | 100 | 16 | 149 | 100 | 0 | 0 | 47 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 8 | 0 | 88 | 70 | 110 | 0 | 8 | 164 | 0 | 104 | 0 |  | 0 | 0 | 37 | 0 | 91 | 50 | 18 | 28 | 0 | 100 | 0 | 300 | 275 | 216 | 16 | 87 | 25 | 5 | 0 | 51 | 0 | 0 | 43 | 21 | 11 | 25 | 20 | 142 | 124 | 72 | 20 | 0 | 88 | 30 | 50 | 49 | 130 | 198 | 63 | 85 | 0 | 80 | 18 | 0 | 10 | 270 | 24 | 11 | 0 | 286 | 0 | 0 | 200 | 0 | 133 | 0 | 100 | 0 | 100 | 0 | 115 | 70 | 0 | 0 | 234 | 0 | 0 | 114 | 57 | 100 | 0 | 17 |  | 916 | 0 | 340 | 0 | 115 | 230 | 0 | 0 | 0 | 0 | 40 | 89 | 30 | 64 | 0 | 70 | 0 | 50 | 35 | 96 | 0 | 25 | 44 | 52 | 26 | 18 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 177 | 0 | 78 | 100 | 180 | 0 | 388 | 55 | 0 | 94 | 0 | 113 | 0 | 0 | 109 | 622 |  | 7355 | 4327 | 11682 | 3460 | 916 | 2139 | 3429 | 771 | 158 | 667 | 142 | 0 | 0 | 93.92
22:00 | 28 | 0 | 0 | 110 | 0 | 99 | 62 | 0 | 355 |  | 0 | 400 | 280 | 7 | 96 | 55 | 218 | 0 | 0 | 0 | 100 | 16 | 149 | 54 | 0 | 0 | 47 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 88 | 70 | 110 | 0 | 8 | 165 | 0 | 105 | 0 |  | 0 | 0 | 34 | 0 | 91 | 50 | 18 | 33 | 0 | 100 | 0 | 295 | 275 | 217 | 16 | 86 | 25 | 5 | 0 | 51 | 0 | 0 | 43 | 21 | 11 | 25 | 20 | 140 | 124 | 72 | 20 | 0 | 88 | 30 | 50 | 49 | 130 | 193 | 63 | 85 | 0 | 80 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 290 | 0 | 0 | 200 | 0 | 132 | 0 | 100 | 0 | 100 | 0 | 115 | 35 | 0 | 0 | 234 | 0 | 0 | 114 | 56 | 100 | 0 | 17 |  | 916 | 0 | 345 | 0 | 99 | 230 | 0 | 0 | 0 | 0 | 40 | 89 | 31 | 48 | 0 | 70 | 0 | 50 | 35 | 96 | 0 | 25 | 44 | 52 | 26 | 18 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 179 | 0 | 78 | 100 | 180 | 0 | 386 | 90 | 0 | 94 | 0 | 113 | 0 | 0 | 109 | 622 |  | 7314 | 4336 | 11650 | 3497 | 916 | 2159 | 3345 | 771 | 158 | 664 | 140 | 0 | 0 | 93.92
23:00 | 28 | 0 | 0 | 110 | 0 | 98 | 67 | 0 | 356 |  | 0 | 400 | 280 | 7 | 96 | 55 | 214 | 0 | 0 | 0 | 100 | 16 | 149 | 10 | 0 | 0 | 18 | 53 | 55 | 17 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 88 | 70 | 110 | 0 | 8 | 164 | 0 | 104 | 0 |  | 0 | 0 | 17 | 0 | 91 | 50 | 18 | 33 | 0 | 100 | 0 | 300 | 270 | 217 | 16 | 85 | 36 | 5 | 0 | 51 | 0 | 0 | 43 | 21 | 11 | 25 | 20 | 138 | 124 | 72 | 20 | 0 | 88 | 30 | 50 | 49 | 130 | 200 | 63 | 85 | 0 | 80 | 18 | 0 | 10 | 275 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 131 | 0 | 100 | 0 | 60 | 0 | 115 | 35 | 0 | 0 | 235 | 0 | 0 | 114 | 56 | 100 | 0 | 17 |  | 917 | 0 | 345 | 0 | 99 | 215 | 0 | 0 | 0 | 0 | 40 | 89 | 31 | 48 | 0 | 70 | 0 | 50 | 6 | 96 | 0 | 25 | 44 | 52 | 25 | 18 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 177 | 0 | 79 | 100 | 180 | 0 | 377 | 90 | 0 | 94 | 0 | 114 | 0 | 0 | 109 | 590 |  | 7155 | 4251 | 11406 | 3506 | 917 | 2141 | 3205 | 739 | 158 | 602 | 138 | 0 | 0 | 93.91
24:00 | 28 | 0 | 0 | 110 | 0 | 99 | 64 | 0 | 356 |  | 0 | 400 | 270 | 7 | 95 | 55 | 214 | 0 | 0 | 0 | 100 | 16 | 98 | 10 | 0 | 0 | 18 | 53 | 55 | 17 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 86 | 70 | 110 | 0 | 8 | 164 | 0 | 103 | 0 |  | 0 | 0 | 8 | 0 | 91 | 50 | 18 | 33 | 0 | 100 | 0 | 300 | 270 | 175 | 16 | 86 | 35 | 5 | 0 | 51 | 0 | 0 | 43 | 21 | 11 | 25 | 21 | 134 | 158 | 72 | 20 | 0 | 88 | 30 | 50 | 49 | 163 | 198 | 63 | 85 | 0 | 80 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 131 | 0 | 100 | 0 | 60 | 0 | 115 | 35 | 0 | 0 | 235 | 0 | 0 | 114 | 56 | 100 | 0 | 17 |  | 916 | 0 | 345 | 0 | 99 | 200 | 0 | 0 | 0 | 0 | 40 | 89 | 30 | 48 | 0 | 70 | 0 | 50 | 0 | 96 | 0 | 25 | 44 | 44 | 25 | 18 | 8 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 178 | 0 | 77 | 100 | 180 | 0 | 382 | 70 | 0 | 57 | 0 | 113 | 0 | 0 | 109 | 580 |  | 7104 | 4153 | 11257 | 3497 | 916 | 2176 | 3128 | 729 | 156 | 521 | 134 | 0 | 0 | 93.91
KWH | 571000 | 0 | 0 | 2709000 | 0 | 2300000 | 1549184 | 0 | 7605000 |  | 0 | 8739500 | 7006051 | 200640 | 1922352 | 781124 | 5955957 | 0 | 0 | 0 | 2081280 | 1203408 | 1119360 | 551108 | 0 | 0 | 600192 | 1060920 | 1022869 | 581665 | 429588 | 600000 | 642780 | 817800 | 817300 | 116292 | 0 | 2012296 | 1700000 | 2600000 | 0 | 57965 | 4215941 | 0 | 1851780 | 0 |  | 0 | 0 | 256040 | 0 | 1325760 | 391200 | 426720 | 377760 | 0 | 2018580 | 0 | 6757000 | 6453000 | 4687000 | 301090 | 2167820 | 355536 | 139680 | 0 | 1095533 | 0 | 83560 | 350126 | 474048 | 185220 | 615100 | 484020 | 2877120 | 3288200 | 1392000 | 434124 | 9500 | 2073000 | 720480 | 1192200 | 1146960 | 3387273 | 4586000 | 1483584 | 1988160 | 0 | 1539790 | 420000 | 0 | 246780 | 7172300 | 575400 | 208224 | 0 | 5851197 | 0 | 0 | 4704000 | 0 | 3110400 | 75870 | 2391360 | 180960 | 1254545 | 0 | 1213200 | 948792 | 0 | 16800 | 4554000 | 0 | 0 | 670320 | 1260000 | 2351040 | 0 | 468480 |  | 21969455 | 0 | 8615808 | 0 | 2547840 | 3507012 | 0 | 0 | 0 | 0 | 304875 | 2173196 | 528528 | 355776 | 0 | 264000 | 0 | 316704 | 155771 | 1090368 | 0 | 137502 | 301490 | 357120 | 182940 | 406560 | 261648 | 225684 | 0 | 0 | 3651600 | 0 | 0 | 0 | 0 | 4247727 | 0 | 1388406 | 551040 | 4648200 | 0 | 9371900 | 540000 | 0 | 1043040 | 0 | 1979520 | 0 | 32110 | 2049888 | 12983900 |  | 156159204 | 86189608 | 242348812 | 81338607 | 21969455 | 49198462 | 59469847 | 16635500 | 3712296 | 7013245 | 2877120 | 134280 | 0
Fuel Cost | 936440 | 0 | 0 | 3982230 | 0 | 3036000 | 2633612.8 | 0 | 7833150 |  | 0 | 9526055 | 7776716.61 | 1522857.6 | 13245005.28 | 6608309.04 | 6194195.28 | 0 | 0 | 0 | 15672038.4 | 10975080.96 | 11014502.4 | 5081215.76 | 0 | 0 | 5455745.28 | 7744716 | 7906777.37 | 5735216.9 | 322191 | 450000 | 0 | 0 | 0 | 1124543.64 | 0 | 543319.92 | 459000 | 4706000 | 0 | 538494.85 | 4595375.69 | 0 | 3148026 | 0 |  | 0 | 0 | 2483588 | 0 | 11534112 | 3098304 | 537667.2 | 1121947.2 | 0 | 2987498.4 | 0 | 5000180 | 6453000 | 4312040 | 388406.1 | 2492993 | 401755.68 | 195552 | 0 | 1873361.43 | 0 | 843956 | 3343703.3 | 602040.96 | 138915 | 1076425 | 363015 | 21578400 | 3485492 | 12639360 | 551337.48 | 151430 | 3399720 | 1152768 | 2122116 | 1789257.6 | 3861491.22 | 4769440 | 2922660.48 | 3797385.6 | 0 | 2663836.7 | 919800 | 0 | 503431.2 | 7244023 | 431550 | 158250.24 | 0 | 44235049.32 | 0 | 0 | 24460800 | 0 | 30606336 | 886920.3 | 19489584 | 1963416 | 8844542.25 | 0 | 11064384 | 8966084.4 | 0 | 0 | 34428240 | 0 | 0 | 6689793.6 | 10798200 | 15657926.4 | 0 | 0 |  | 126544060.8 | 0 | 9046598.4 | 0 | 20026022.4 | 48607186.32 | 0 | 0 | 0 | 0 | 3176797.5 | 2455711.48 | 819218.4 | 3472373.76 | 0 | 541200 | 0 | 3116367.36 | 1582633.36 | 9649756.8 | 0 | 1859027.04 | 2921438.1 | 3460492.8 | 1774518 | 780595.2 | 405554.4 | 170842.788 | 0 | 0 | 19791672 | 0 | 0 | 0 | 0 | 5606999.64 | 0 | 2082609 | 9373190.4 | 5438394 | 0 | 9278181 | 5637600 | 0 | 9898449.6 | 0 | 15361075.2 | 0 | 354815.5 | 15148672.32 | 56999321 |  | 490248301.84 | 395381374.568 | 885629676.408 | 92414589.418 | 126544060.8 | 59291947.15 | 424620253.98 | 76790993 | 1002319.92 | 81993946.34 | 21578400 | 1393165.8 | 0
Yesterday Day Peak | 28 | 0 | 0 | 110 | 0 | 94 | 69 | 0 | 347 |  | 0 | 350 | 300 | 7 | 80 | 40 | 204 | 0 | 0 | 0 | 91 | 93 | 0 | 20 | 0 | 0 | 1 | 53 | 55 | 50 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 87 | 70 | 110 | 0 | 0 | 230 | 0 | 50 | 0 |  | 0 | 0 | 0 | 0 | 72 | 16 | 18 | 2 | 0 | 80 | 0 | 290 | 300 | 192 | 8 | 96 | 10 | 5 | 0 | 10 | 0 | 0 | 0 | 21 | 5 | 25 | 18 | 112 | 138 | 56 | 17 | 2.5 | 86 | 30 | 50 | 45 | 130 | 205 | 63 | 85 | 0 | 50 | 18 | 0 | 10 | 290 | 24 | 5 | 0 | 267 | 0 | 0 | 200 | 0 | 131 | 17.86 | 90 | 0 | 30 | 0 | 16 | 89 | 0 | 2.9 | 179 | 0 | 0 | 0 | 47 | 90 | 0 | 17 |  | 917 | 0 | 355 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 171 | 0 | 43 | 0 | 150 | 0 | 403 | 0 | 0 | 23 | 0 | 100 | 0 | 3.5 | 109 | 465 |  | 9705.76 | DayPeak
Yesterday Evening Peak | 28 | 0 | 0 | 110 | 0 | 99 | 66 | 0 | 355 | 0 | 0 | 400 | 280 | 7 | 96 | 55 | 180 | 0 | 0 | 0 | 100 | 16 | 149 | 100 | 0 | 0 | 47 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 8 | 0 | 88 | 70 | 110 | 0 | 8 | 164 | 0 | 104 | 0 | 0 | 0 | 0 | 37 | 0 | 91 | 50 | 18 | 28 | 0 | 100 | 0 | 300 | 275 | 216 | 16 | 87 | 25 | 5 | 0 | 51 | 0 | 0 | 43 | 21 | 11 | 25 | 20 | 142 | 124 | 72 | 20 | 0 | 88 | 30 | 50 | 49 | 130 | 198 | 63 | 85 | 0 | 80 | 18 | 0 | 10 | 270 | 24 | 11 | 0 | 286 | 0 | 0 | 200 | 0 | 133 | 0 | 100 | 0 | 100 | 0 | 115 | 70 | 0 | 0 | 234 | 0 | 0 | 114 | 57 | 100 | 0 | 17 |  | 916 | 0 | 340 | 0 | 115 | 230 | 0 | 0 | 0 | 0 | 40 | 89 | 30 | 64 | 0 | 70 | 0 | 50 | 35 | 96 | 0 | 25 | 44 | 52 | 26 | 18 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 177 | 0 | 78 | 100 | 180 | 0 | 388 | 55 | 0 | 94 | 0 | 113 | 0 | 0 | 109 | 622 |  | 11682 | EvPeak
Forecast for Evening | 28 | 0 | 0 | 110 | 0 | 100 | 78 | 0 | 360 | 0 | 0 | 450 | 305 | 100 | 100 | 55 | 210 | 0 | 0 | 0 | 100 | 93 | 149 | 100 | 0 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 50 | 0 | 88 | 70 | 110 | 0 | 25 | 165 | 0 | 105 | 0 | 0 | 0 |  | 100 | 100 | 97 | 50 | 18 | 25 | 0 | 129 | 0 | 360 | 360 | 220 | 16 | 96 | 38 | 20 | 0 | 51 | 0 | 42 | 43 | 22 | 11 | 25 | 20 | 173 | 157 | 72 | 20 | 0 | 88 | 30 | 51 | 49 | 163 | 210 | 66 | 86 | 0 | 80 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 131 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 0 | 300 | 54 | 110 | 114 | 60 | 100 | 0 | 104 |  | 928 | 16 | 410 | 0 | 115 | 225 | 0 | 0 | 30 | 60 | 40 | 89 | 33 | 110 | 0 | 70 | 0 | 43 | 40 | 100 | 0 | 50 | 45 | 52 | 35 | 22 | 10 | 10 | 0 | 0 | 150 | 0 | 10 | 0 | 0 | 220 | 0 | 76 | 100 | 220 | 0 | 414 | 90 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 660
Forecast for Day | 28 | 0 | 0 | 110 | 0 | 100 | 78 | 0 | 360 | 0 | 0 | 450 | 305 | 100 | 100 | 55 | 210 | 0 | 0 | 0 | 100 | 85 | 149 | 100 | 0 | 0 | 49 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 35 | 0 | 88 | 70 | 110 | 0 | 25 | 165 | 0 | 105 | 0 | 0 | 0 |  | 100 | 100 | 97 | 50 | 18 | 10 | 0 | 129 | 0 | 360 | 360 | 220 | 16 | 92 | 38 | 20 | 0 | 51 | 0 | 0 | 43 | 22 | 11 | 25 | 20 | 163 | 157 | 72 | 20 | 1.6 | 88 | 30 | 51 | 49 | 163 | 210 | 61 | 86 | 0 | 80 | 18 | 0 | 10 | 341 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 80 | 131 | 20 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 5 | 300 | 50 | 50 | 114 | 60 | 100 | 0 | 104 |  | 928 | 0 | 410 | 0 | 115 | 180 | 0 | 0 | 0 | 0 | 40 | 89 | 33 | 110 | 0 | 70 | 0 | 0 | 0 | 100 | 0 | 50 | 0 | 52 | 0 | 22 | 10 | 10 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 |  | 76 | 60 | 220 | 0 | 414 | 90 | 0 | 113 | 100 | 113 | 0 | 8 | 113 | 470
Generation at 08:00(Today) | 28 | 0 | 0 | 110 | 0 | 99 | 30 | 0 | 243 | 0 | 0 | 350 | 295 |  | 94 | 15 | 150 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 84 | 70 | 110 | 0 | 0 | 164 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 5 | 0 | 80 | 0 | 333 | 290 | 184 | 16 | 92 | 32 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 25 | 0 | 100 | 155 | 24 | 20 | 0.1 | 60 | 30 | 50 | 49 | 100 | 204 | 40 | 40 | 0 | 80 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 145 | 0 | 0 | 140 | 0 | 132 | 0.6 | 100 | 0 | 0 | 0 | 7 | 0 | 0 | 0.7 | 160 | 0 | 0 | 0 | 56 | 40 | 0 | 17 | 0 | 918 | 0 | 360 | 0 | 73 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 17 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 152 | 0 | 32 | 0 | 150 | 0 | 370 | 0 | 0 | 0 | 0 | 34 | 0 | 0.6 | 35 | 450 | 0
199
| Minimum Generation |  | 8409.87 | 8:00
| Highest Generation |  | 11682 | 21:00
| Day Peak Generation |  | 9705.76 | 12:00
| Evening Peak Generation |  | 11682 | 21:00
| HVDC Max Flow |  | 917 | 9:00
| HVDC EvPeak Flow |  | 916 | 21:00
| Load factor L.F |  | 86.44%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-08-18
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-08-17 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9705.76 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 8485 | MW
Evening Peak Generation : |  | 11682 | MW Hour : | 21:00 | Available Max Generation : |  | 14851 | MW
E.P. Demand (at gen end) : |  | 11682 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 11900 | MW
Maximum Generation : |  | 11682 | MW Hour : | 21:00 | Reserve(Generation end) |  | 2951 | MW
Total Gen. (MKWH) : |  | 242.3488 | System Load Factor : | 86.44% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 63 | MW at | 4:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-08-18
Actual : | 93.89 | Ft.(MSL) , | Rule curve : | 94.44 | Ft.( MSL )
Gas Consumed : | Total = | 1138.05 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 151706536.568
: |  | Coal : | 76790993 | Oil : | 506614200.32 | Total : | 735111729.888
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4229.3189 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1440.2425 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1290.773 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1166.4514 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1054.0341 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 850.5733 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 472.9736 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 218.9303 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 656.0169 |  |  | 0 | 0%
Total | 0 |  | 11379.3141 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down | 10) Haripur-412 MW.
1) Barapukuria ST: Unit-1,2
2) Bibiyana #3
3) Ghorasal Unit-2,3,4,7
4) Ashuganj unit-3,5
5) Bhola-225 MW GT-2 & ST
|  |  |  | 6) Kaptai-2 |  | 6
7) Raozan #1,2
8) Sirajganj #1
9) Baghabari-70 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Mirpur 132/33 kV T1 transformer was under shut down from 09:25 to 16:29 for C/M.
b) Hasnabad-Aurahati 132 kV Ckt was under shut down from 09:24 to 16:51 for C/M.
c) Siddhirganj 335 MW ST tripped at 11:23 due to hydraulic line fault.
d) Sikalbaha 150 MW GT was synchronized at 11:49.
e) Narail 132/33 kV T1 transformer was under shut down from 09:22 to 12:35 for C/M.
f) Narail 132/33 kV T2 transformer was under shut down from 12:38 to 17:25 for C/M.
g) Tongi-Bashundhara 132 kV Ckt-1 was under shut down from 13:10 to 15:33 for D/W.
h) Kulaura 132/33 kV T1 transformer was shut down from 11:31 to 12:31 due to R/H at 33 kV bus isolator. |  |  |  |  | About 29 MW power interruption occurred under Kulaura S/S area
from 11:31 to 12:31.
i) After maintenance Barapukuria 132/33 kV T4 transformer was switched on at 20:35
j) Baghabari 100 MW was synchronized at 20:09.
k) Cumilla(N) 132/33 kV T3 transformers tripped at 05:02(18-8-2020) due 33 kV Balutupa feeder fault and |  |  |  |  | About 20 MW power interruption occurred under Cumilla(N) S/S area
was switched on at 05:33. |  |  |  |  | from 05:02 to 05:33.
l) Natore 33 kV bus of 132/33 kV T1 & T2 transformers was under shut down from 07:04 to 08:31 due to |  |  |  |  | About 58 MW power interruption occurred under Natore S/S area
red hot maintenance work by PBS. |  |  |  |  | from 07:04 to 08:31.
m) Sylhet-Chattak 132 kV Ckt was under shut down from 07:42 to 10:13 for C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-08-17 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 28 | 571000 | Unit-2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 110 | 2709000 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 66 | 1549184 | Engine problem
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 99 | 2300000 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 355 | 7605000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 8739500 | Frequency control.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 7 | 200640 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 280 | 7006051 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 96 | 1922352
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 781124
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 100 | 551108
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 429588
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 2081280
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 180 | 5955957 | STG under maintenance
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 16 | 1203408 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 47 | 600192
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 1060920
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 1119360
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1022869
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 581665
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1242780 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 817800
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 817300
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 8 | 116292 | Low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 286 | 5851197 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 133 | 3110400 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 70 | 948792 | Low demand
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 468480 | Fuel shortage
| Dhaka area Total |  |  |  | 5895 | 2908 | 61363239
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 110 | 2600000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 8 | 57965 | Low demand
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 75870
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 391200
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 158 | 3712296 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 164 | 4215941
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 104 | 1851780
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 37 | 256040
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2391360
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 426720 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 28 | 377760
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 91 | 1325760 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 16800
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 234 | 4554000 | Transformer over load
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2351040
| Chattogram area Total |  |  |  | 2266 | 1202 | 24604532
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 100 | 2018580 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 216 | 4687000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 300 | 6757000 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 275 | 6453000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 25 | 355536 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 139680 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 16 | 301090 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1095533
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 100 | 1254545 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 83560 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 87 | 2167820 | ST under maint.
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 180960 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 474048
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 185220
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 142 | 2877120
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 615100 | Engine problem
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 350126 | Engine problem
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 484020 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 670320
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 57 | 1260000 | Engine problem
| Cumilla Area Total |  |  |  | 2980 | 1608 | 32410258
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 124 | 3288200 | Engine problem
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 434124
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 72 | 1392000 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9500
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 4704000
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1213200 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 531 | 11041024
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 88 | 2073000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 720480 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3387273 | Frequency control.
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 198 | 4586000
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1192200
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 49 | 1146960
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 208224
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 63 | 1483584 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1988160
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 80 | 1539790 | Engine problem
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 420000 | Engine problem
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 575400
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 270 | 7172300 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 246780
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1106 | 26740151
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 916 | 21969455
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 2547840
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 230 | 3507012
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 340 | 8615808 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 304875
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 551040 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 55 | 540000 | Low demand
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Reserve
| Khulna Area Total |  |  |  | 2284 | 1796 | 38036030
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 64 | 355776 | Line over load
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 30 | 528528 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 89 | 2173196 | GT-2 Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 78 | 1388406 | Engine problem
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 622 | 12983900
| Barisal Area Total |  |  |  | 1054 | 883 | 17429806
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 70 | 264000 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 316704
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 35 | 155771
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 25 | 137502 | Low demand
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 44 | 301490
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage.
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 177 | 4247727 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 180 | 4648200 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 388 | 9371900 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 26 | 182940
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 18 | 406560 | Engine problem
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 11 | 261648
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 225684
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 357120
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 96 | 1090368
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 94 | 1043040 | Low demand
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 2049888
| Rajshahi Area Total |  |  |  | 2183 | 1386 | 25060542
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 149 | 3651600 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1979520
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 32110
| Rangpur Area Total |  |  |  | 605 | 262 | 5663230
| Total |  |  |  | 19892 | 11682 | 242348812
| Eastern Grid Total |  |  |  | 13766 | 7355 | 156159204
| Western Grid Total |  |  |  | 6126 | 4327 | 86189608
| National Grid Total |  |  |  | 19892 | 11682 | 242348812
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-08-17
(a) ENTIRE EASTERN GRID : |  | 7336 | MW | (b) ENTIRE WESTERN GRID : |  | 3825 | MW
i) Dhaka area |  | 3804 | MW | i) Khulna area |  | 1454 | MW
ii) Chittagong area |  | 1034 | MW | ii) Rajshahi area |  | 1274 | MW
iii) Comilla area |  | 1043 | MW | iii) Barisal area |  | 315 | MW
iv) Mymensingh area |  | 975 | MW | iv) Rangpur area |  | 782 | MW
v) Sylhet area |  | 480 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11161 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 124 | 13:00 | Sherpur | 106 | 22:00 | Jhenida | 108 | 19:30
Munsiganj | 112 | 23:00 | Srimongal | 46 | 1:00 | Bottail | 132 | 19:30
Sonargaon | 84 | 20:00 | Shahjibazar | 115 | 21:00 | G.K Project | 56 | 20:00
Shyampur | 184 | 10:00 | Fenchuganj | 44 | 21:00 | Faridpur | 187 | 0.91667
Bhulta | 191 | 24:00 | Kulawara | 45 | 19:00 | Madaripur | 98 | 0.95833
Madanganj | 44 | 6:00 | Sylhet | 116 | 19:00 | Sariatpur | 62 | 22:00
Shitalakhya | 101 | 12:00 | Chatak | 27 | 20:00 | Gopalganj | 91 | 19:30
Rahim steel | 11 | 18:00 | Sunamganj | 42 | 20:00 | Bagerhat | 85 | 19:00
Matuail | 78 | 10:00 | Biani Bazar | 56 | 20:00 | Mongla | 48 | 12:00
Ghorasal | 77 | 22:00 | Comilla (S) | 142 | 21:00 | Satkhira | 103 | 0.83333
Narsingdi | 157 | 21:00 | Comilla(N) | 103 | 20:00 | Gallamari | 46 | 13:00
Haripur (SBU) | 100 | 10:00 | Chandpur | 97 | 21:00 | Magura | 54 | 0.8125
Ullon | 54 | 19:00 | Feni | 110 | 19:00 | Norail | 39 | 19:00
Hasnabad | 190 | 20:00 | Chowmuhani | 152 | 21:00 | Chuadanga | 89 | 21:00
Magbazar | 97 | 12:00 | Ashuganj | 52 | 23:00 | Barisal(N) | 42 | 0.875
Maniknagar | 92 | 11:00 | Daudkandi | 132 | 20:00 | Barisal (S) | 90 | 0.79167
Bangabhaban | 36 | 10:00 | B.Baria | 144 | 21:00 | Patuakhali | 107 | 0.91667
Narinda | 84 | 11:00 | Ramganj | 106 | 20:00 | Bhandaria | 53 | 0.91667
Dhanmondi | 173 | 12:00 | Chaddagram | 34 | 19:30 | Borhan Uddin | 39 | 19:00
Lalbag | 85 | 13:00 | PHP | 8 | 23:00 | Ishurdi | 66 | 19:30
Madartek | 64 | 22:00 | Madunaghat | 53 | 11:00 | Ruppur Paromanobik | 2 | 1:00
Dhaka University |  |  | Hathazari | 89 | 0.79167 | Natore | 125 | 21:00
Fatullah | 31 | 0.875 | Khulshi | 185 | 0.54167 | Bogra | 165 | 21:00
Mirpur | 95 | 19:00 | Halishahar | 125 | 0.625 | Noagaon | 124 | 21:00
Kalyanpur | 96 | 19:00 | Baraulia | 134 | 0.20833 | Rajshahi | 147 | 20:00
Gulshan | 124 | 13:00 | Sikalbaha | 24 | 0.625 | Rajshahi New | 11 | 20:00
Uttara | 80 | 13:00 | Dohazari | 76 | 0.83333 | C.Nawabganj | 71 | 22:00
Uttara New | 27 | 19:00 | Cox'sbazar | 91 | 0.79167 | Amnura | 50 | 21:00
Kamrangirchar | 83 | 19:00 | Chandraghona | 26 | 0.83333 | Pabna | 122 | 21:00
Savar | 128 | 15:00 | Kaptai | 4 | 0.79167 | Shahjadpur | 97 | 20:00
Bhasantec | 143 | 13:00 | A. Khaer Stl. | 0 | 0.041667 | Serajganj | 98 | 20:00
Agargaon | 67 | 13:00 | Bakulia | 89 | 0.5 | Niyamatpur | 61 | 21:00
Satmosjid | 83 | 13:00 | Julda | 21 | 0.625 | Joypurhat | 54 | 21:00
Tongi | 126 | 0.45833 | TK chemical | 26 | 0.91667 | Sherpur(Bogura) | 50 | 22:00
Kabirpur | 226 | 12:00 | Modern Steel | 0 | 0.041667 | Mohastangor | 48 | 19:30
Basundhara | 124 | 19:00 | Shahmirpur | 22 | 0.083333 | Rangpur | 156 | 19:30
Manikganj | 70 | 0.875 | Khagrachhari | 22 | 0.8125 | Lalmonirhat | 59 | 20:00
Joydevpur | 161 | 21:00 | Matarbari | 26.5 | 0.77083 | Saidpur | 108 | 19:00
New Tongi | 99 | 12:00 | Baroiar Hat | 32 | 0.79167 | Purbasadipur | 105 | 21:00
Korda | 218 | 11:00 | Rangamati | 10 | 0.77083 | Thakurgaon | 78 | 21:00
Dhamrai | 94 | 21:00 | Abul Khair 230 | 139 | 0.5 | Palashbari | 130 | 19:30
Rajendrapur | 98 | 19:30 | BSRM | 101 | 0 | Barapukuria | 51 | 21:00
Valuka | 92 | 19:30 | GPH Ispat | 78 | 0.77083 | Panchagar | 48 | 20:00
Tangail | 171 | 20:00 | Goalpara | 23 | 0.91667 | Joldhaka | 29 | 21:00
Mymensing | 223 | 21:00 | Central s/s | 87 | 19:30 | Kurigram | 59 | 19:30
Kishorganj | 144 | 22:00 | Noapara | 61 | 19:30
Netrokona | 107 | 21:00 | Jessore | 106 | 19:00
Jamalpur | 140 | 21:00 | Benapol | 48 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-08-17 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 396 | 4:00 | 387 | 11:00 | Kaliakoir | 379 | 0.16667 | 368 | 0.66667
| Bheramara | 403 | 7:00 | 391 | 21:00 | Bhulta | 390 | 0.16667 | 378 | 0.45833
| Ashuganj(N) | 395 | 3:00 | 385 | 10:00 | Gopalganj | 414 | 0.25 | 389 | 0.875
| Payra | 415 | 6:00 | 401 | 19:30
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 232 | 1:00 | 230 | 7:00 | Comilla (N) | 234 | 19:00 | 229 | 12:00
| Ishurdi | 236 | 18:30 | 227 | 21:00 | Hathazari | 226 | 19:00 | 222 | 14:00
| Ashuganj | 237 | 3:00 | 232 | 10:00 | Megnaghat | 233 | 6:00 | 225 | 11:00
| Serajganj | 231 | 18:30 | 227 | 23:00 | Fenchuganj | 238 | 6:00 | 233 | 14:00
| Baghabari | 243 | 18:30 | 237 | 22:00 | Siddhirganj | 230 | 3:00 | 224 | 10:00
| Barapukuria | 234 | 11:00 | 224 | 20:00 | Maniknagar | 229 | 2:00 | 221 | 12:00
| Bogra | 223 | 18:00 | 214 | 22:00 | Agargaon | 228 | 3:00 | 218 | 16:00
| Rajshahi | 230 | 18:00 | 222 | 22:00 | Barisal | 246 | 6:00 | 235 | 21:00
| Khulna South | 238 | 18:30 | 227 | 4:00 | AKSML | 223 | 19:00 | 219 | 6:00
| Rampura | 228 | 1:00 | 221 | 15:00 | BSRM | 225 | 20:00 | 220 | 10:00
| Haripur | 229 | 4:00 | 222 | 12:00 | Bibiyana | 236 | 3:00 | 231 | 13:00
| Hasnabad | 230 | 1:00 | 222 | 9:00 | Bhulta | 231 | 19:00 | 224 | 17:00
| Shyampur | 227 | 4:00 | 219 | 10:00 | Ashuganj (S) | 232 | 4:00 | 222 | 16:00
| Aminbazar | 227 | 1:00 | 220 | 9:00 | Kaliakoir | 236 | 2:00 | 232 | 9:00
| Tongi | 226 | 19:00 | 219 | 9:00 | GPH | 223 | 2:00 | 219 | 7:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 130 | 1:00 | 126 | 11:00 | Hathazari | 134 | 0.79167 | 132 | 0.16667
| Munsiganj | 134 | 19:00 | 127 | 9:00 | Khulshi | 133 | 0.125 | 129 | 0.625
| Sonargaon | 132 | 1:00 | 124 | 10:00 | Halishahar | 136 | 0.54167 | 132 | 0.625
| Shyampur | 133 | 20:00 | 127 | 10:00 | Baraulia | 133 | 0.041667 | 130 | 0.625
| Bhulta | 125 | 19:00 | 119 | 10:00 | Sikalbaha | 136 | 19:00 | 132 | 0.20833
| Madanganj | 130 | 4:00 | 125 | 9:00 | Dohazari | 133 | 13:00 | 129 | 0.75
| Shitalakhya | 139 | 1:00 | 131 | 9:00 | Cox'sbazar | 130 | 0.54167 | 122 | 0.16667
| Rahim steal | 130 | 1:00 | 126 | 10:00 | Chandraghona | 135 | 0.83333 | 133 | 0.25
| Matuail | 130 | 1:00 | 126 | 11:00 | Kaptai | 135 | 1:00 | 130 | 0.125
| Ghorasal | 136 | 1:00 | 136 | 1:00 | A. Khaer Stl. | 133 | 0.83333 | 130 | 3:00
| Narsinghdi | 128 | 4:00 | 124 | 1:00 | Bakulia | 135 | 0.79167 | 131 | 0.29167
| Haripur (SBU) | 131 | 3:00 | 126 | 9:00 | Julda | 136 | 0.79167 | 132 | 0.41667
| Ullon | 133 | 2:00 | 127 | 11:00 | TK Chemical | 135 | 0.77083 | 132 | 18:00
| Hasnabad | 135 | 1:00 | 130 | 8:00 | Modern Steel | 135 | 0.83333 | 131 | 0.58333
| Magbazar | 133 | 3:00 | 127 | 11:00 | Shahmirpur | 136 | 0.77083 | 132 | 0.29167
| Maniknagar | 132 | 1:00 | 126 | 12:00 | Khagrachhari | 134 | 0.8125 | 132 | 0.125
| Bangabhaban | 132 | 1:00 | 126 | 12:00 | Matarbari | 130 | 0.20833 | 126 | 0.041667
| Narinda | 132 | 1:00 | 126 | 12:00 | Baroiar Hat | 130 | 0.625 | 128 | 0.041667
| Dhanmondi | 133 | 2:00 | 127 | 11:00 | Rangamati | 134 | 0.54167 | 132 | 6:00
| Lalbag | 135 | 4:00 | 126 | 10:00 | Goalpara S/S | 137 | 18:00 | 133 | 4:00
| Madartek | 133 | 2:00 | 127 | 10:00 | Khulna Central S/S | 138 | 0.77083 | 134 | 3:00
| Dhaka University |  |  |  |  | Noapara | 134 | 18:30 | 130 | 3:00
| Fatuiiah | 133 | 0.083333 | 127 | 10:00 | Jessore | 130 | 9:00 | 122 | 2:00
| Mirpur | 134 | 3:00 | 124 | 16:00 | Benapol | 132 | 18:30 | 121 | 2:00
| Kalyanpur | 133 | 3:00 | 125 | 12:00 | Jhenida | 127 | 0.75 | 114 | 21:00
| Gulshan | 133 | 4:00 | 126 | 12:00 | Bottail | 133 | 18:30 | 124 | 19:30
| Uttara | 132 | 4:00 | 124 | 12:00 | G.K Project | 138 | 0.75 | 134 | 1:00
| Uttara New | 134 | 18:30 | 128 | 16:00 | Faridpur | 134 | 6:00 | 122 | 19:30
| Kamrangirchar | 133 | 3:00 | 122 | 15:00 | Madaripur | 139 | 0.25 | 130 | 19:00
| Savar | 133 | 3:00 | 125 | 12:00 | Shariyatpur S/S | 138 | 0.25 | 127 | 21:00
| Bhasantec | 133 | 3:00 | 126 | 12:00 | Gopalganj | 139 | 6:00 | 124 | 19:30
| Agargaon | 134 | 3:00 | 127 | 12:00 | Bagerhat | 134 | 6:00 | 127 | 2:00
| Satmosjid | 134 | 3:00 | 127 | 12:00 | Mongla | 130 | 0.77083 | 125 | 3:00
| Tongi | 136 | 0.79167 | 130 | 17:00 | Satkhira | 136 | 0.77083 | 129 | 2:00
| Kabirpur | 135 | 7:00 | 129 | 21:00 | Gallamari | 138 | 18:30 | 132 | 3:00
| Basundhara | 133 | 3:00 | 126 | 13:00 | Magura | 126 | 18:00 | 113 | 21:00
| Manikganj | 134 | 18:30 | 130 | 9:00 | Norail | 124 | 0.33333 | 109 | 19:30
| Joydevpur | 140 | 2:00 | 133 | 15:00 | Chuadanga | 123 | 18:00 | 104 | 21:00
| New Tongi | 135 | 0.77083 | 126 | 21:00 | Barisal(N) | 140 | 6:00 | 132 | 21:00
| Kodda | 135 | 264:00 | 123 | 0.375 | Barisal (S) | 139 | 0.25 | 131 | 21:00
| Dhamrai | 135 | 5:00 | 128 | 21:00 | Patuakhali(S) | 136 | 0.66667 | 126 | 22:00
| Rajendrapur | 133 | 18:30 | 121 | 9:00 | Bhandaria | 132 | 18:30 | 124 | 19:30
| Valuka | 127 | 6:00 | 115 | 21:00 | Ishurdi | 137 | 18:30 | 132 | 19:30
| Tangail | 135 | 7:00 | 128 | 22:00 | Ruppur Paromanobik | 134 | 5:00 | 132 | 2:00
| Mymensing | 130 | 6:00 | 117 | 22:00 | Natore | 136 | 18:30 | 129 | 2:00
| Kishorganj | 129 | 9:00 | 118 | 22:00 | Bogra | 135 | 17:00 | 128 | 20:00
| Netrokona | 128 | 7:00 | 113 | 22:00 | Noagaon | 130 | 18:30 | 119 | 22:00
| Jamalpur | 138 | 3:00 | 131 | 23:00 | Rajshahi | 133 | 18:30 | 126 | 2:00
| Sherpur | 138 | 7:00 | 130 | 22:00 | Rajshahi New | 133 | 18:30 | 126 | 5:00
| Srimongal | 136 | 7:00 | 131 | 0.875 | C.Nawabganj | 131 | 18:30 | 131 | 5:00
| Shahjibazar | 133 | 5:00 | 129 | 0.041667 | Amnura | 132 | 18:30 | 124 | 5:00
| Fenchuganj | 135 | 6:00 | 131 | 0.041667 | Pabna | 134 | 18:00 | 130 | 20:00
| Khulawara | 133 | 5:00 | 129 | 0.91667 | Shahjadpur | 140 | 18:00 | 134 | 11:00
| Sylhet | 130 | 9:00 | 127 | 0.041667 | Serajganj | 134 | 18:00 | 128 | 20:00
| Chatak | 129 | 6:00 | 126 | 1:00 | Niyamatpur | 126 | 6:00 | 114 | 19:00
| Sunamganj | 128 | 6:00 | 123 | 0.041667 | Joypurhat | 130 | 18:30 | 117 | 22:00
| Biani Bazar | 129 | 7:00 | 124 | 0.041667 | Sherpur(Bogura) | 135 | 18:30 | 127 | 22:00
| Comilla(s) | 127 | 5:00 | 121 | 20:00 | Mohastangor | 133 | 18:00 | 124 | 22:00
| Comilla(n) | 136 | 20:00 | 132 | 15:00 | Rangpur | 128 | 13:00 | 114 | 20:00
| Chandpur | 131 | 19:00 | 126 | 10:00 | Lalmonirhat | 123 | 11:00 | 112 | 20:00
| Feni | 132 | 20:00 | 127 | 15:00 | Saidpur | 129 | 16:00 | 115 | 20:00
| Chowmuhani | 126 | 11:00 | 124 | 22:00 | Purbasadipur | 127 | 17:00 | 108 | 20:00
| Ashuganj | 135 | 8:00 | 129 | 22:00 | Thakurgaon | 126 | 17:00 | 108 | 23:00
| Daudkandi | 131 | 19:00 | 125 | 12:00 | Palashbari | 126 | 18:00 | 115 | 20:00
| B.Baria | 130 | 7:00 | 123 | 22:00 | Barapukuria | 134 | 17:00 | 124 | 20:00
| Ramganj | 123 | 10:00 | 120 | 21:00 | Panchagar | 123 | 17:00 | 104 | 20:00
| Chaddagram | 133 | 19:00 | 128 | 10:00 | Joldhaka | 128 | 11:00 | 110 | 20:00
| PHP | 132 | 20:00 | 127 | 15:00 | Kurigram | 127 | 16:00 | 113 | 22:00
| Madanhat | 136 | 18:30 | 134 | 10:00

## L-Curve
Date | 2020-08-17
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 275 | 7104 | 4153 | 11257 |  |  |  | QF-LDC-12
0:30 | 227.5 | 7020 | 4029 | 11049 | Date: | 2020-08-17
1:00 | 180 | 6936 | 3905 | 10841
1:30 | 152 | 6826.5 | 3760.5 | 10587
2:00 | 124 | 6717 | 3616 | 10333
2:30 | 111 | 6625.5 | 3584.5 | 10210 | [5 empty] | Gen. at Eve. Peak | 11682 | 11682 MW (21:00 )
3:00 | 98 | 6534 | 3553 | 10087 | [6 empty] | 21:00
3:30 | 80.5 | 6440 | 3467.5 | 9907.5 | [5 empty] | Gen. at Day Peak | 9705.76 | 9705.76 MW (12:00 )
4:00 | 63 | 6346 | 3382 | 9728 | [6 empty] | 12:00
4:30 | 80 | 6287.5 | 3354 | 9641.5 | [5 empty] | Highest Generation | 11682
5:00 | 97 | 6229 | 3326 | 9555 | [6 empty] | 21:00
5:30 | 184 | 5961.4 | 3204.55 | 9165.95
6:00 | 271 | 5693.8 | 3083.1 | 8776.9
6:30 | 274.5 | 5592.75 | 3022.95 | 8615.7
7:00 | 278 | 5491.7 | 2962.8 | 8454.5
7:30 | 286 | 5483.085 | 2949.1 | 8432.185
8:00 | 294 | 5474.47 | 2935.4 | 8409.87
8:30 | 344.5 | 5597.03 | 2977.9 | 8574.93
9:00 | 395 | 5719.59 | 3020.4 | 8739.99
9:30 | 409.5 | 5968.62 | 3046.5 | 9015.12
10:00 | 424 | 6217.65 | 3072.6 | 9290.25
10:30 | 436 | 6226.06 | 3119.7 | 9345.76
11:00 | 448 | 6234.47 | 3166.8 | 9401.27
11:30 | 426 | 6336.365 | 3217.15 | 9553.515
12:00 | 404 | 6438.26 | 3267.5 | 9705.76
12:30 | 369 | 6489.735 | 3276.2 | 9765.935
13:00 | 334 | 6541.21 | 3284.9 | 9826.11
13:30 | 383 | 6488.305 | 3327.05 | 9815.355
14:00 | 432 | 6435.4 | 3369.2 | 9804.6
14:30 | 428.5 | 6435.4 | 3370.05 | 9805.45
15:00 | 425 | 6435.4 | 3370.9 | 9806.3
15:30 | 440 | 6371.2 | 3327.85 | 9699.05
16:00 | 455 | 6307 | 3284.8 | 9591.8
16:30 | 473.5 | 6161.15 | 3239.75 | 9400.9
17:00 | 492 | 6015.3 | 3194.7 | 9210
17:30 | 491 | 5898.65 | 3172.1 | 9070.75
18:00 | 490 | 5782 | 3149.5 | 8931.5
18:30 | 308.5 | 6351 | 3487.75 | 9838.75
19:00 | 127 | 6920 | 3826 | 10746
19:30 | 128 | 7397 | 4177 | 11574
20:00 | 162 | 7458 | 4191 | 11649 |  |  |  | Executive Engineer
20:30 | 216 | 7406.5 | 4259 | 11665.5 |  |  |  | Network Operation Division
21:00 | 270 | 7355 | 4327 | 11682
21:30 | 285 | 7334.5 | 4331.5 | 11666
22:00 | 300 | 7314 | 4336 | 11650 |  |  |  |  | Page 6 of 7
22:30 | 290 | 7234.5 | 4293.5 | 11528
23:00 | 280 | 7155 | 4251 | 11406
23:30 | 277.5 | 7129.5 | 4202 | 11331.5
24:00 | 275 | 7104 | 4153 | 11257
11682 MW (21:00 )
9705.76 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-08-17 |  | Energy | 242348812
[10 empty] | 2020-08-17 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3497 | 916 | 2176 | 3205 | 729 | 156 | 521 | 0 | 134
0:30 | 3454 | 915 | 2147 | 3065.5 | 709 | 154 | 511 | 0 | 132 | Date: | 2020-08-17
1:00 | 3411 | 914 | 2118 | 2926 | 689 | 152 | 501 | 0 | 130
1:30 | 3402 | 914 | 2120 | 2804.5 | 679 | 152 | 387.5 | 0 | 128 | [7 empty] | Total Energy | 242.3488 | Total Energy Gen 242.349 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 242.349 MKWHr
2:00 | 3393 | 914 | 2122 | 2683 | 669 | 152 | 274 | 0 | 126 | [7 empty] | Energy not Served | 0
2:30 | 3400 | 914 | 2126.5 | 2561.5 | 668 | 152 | 264 | 0 | 124 | [7 empty] | Energy Requirement | 242.3488
3:00 | 3407 | 914 | 2131 | 2440 | 667 | 152 | 254 | 0 | 122
3:30 | 3392 | 914 | 2122.5 | 2338.5 | 658 | 152.5 | 211 | 0 | 119 | [6 empty] | Shortage
4:00 | 3377 | 914 | 2114 | 2237 | 649 | 153 | 168 | 0 | 116
4:30 | 3387 | 913.5 | 2113 | 2143 | 649 | 154 | 168 | 0 | 114
5:00 | 3397 | 913 | 2112 | 2049 | 649 | 155 | 168 | 0 | 112
5:30 | 3388 | 913.5 | 2051.5 | 1761.5 | 643 | 155 | 144 | 0 | 109
6:00 | 3379 | 914 | 1991 | 1474 | 637 | 155 | 120 | 0 | 106
6:30 | 3332.5 | 914 | 1962.5 | 1400 | 628 | 155.5 | 120 | 0 | 101 |  |  |  |  | Coal
7:00 | 3286 | 914 | 1934 | 1326 | 619 | 156 | 120 | 0 | 96
7:30 | 3246 | 914 | 1950 | 1322.5 | 620.5 | 156.5 | 120 | 0 | 97 |  |  |  | Oil |  |  |  | ,
8:00 | 3206 | 914 | 1966 | 1319 | 622 | 157 | 120 | 0 | 98
8:30 | 3256.5 | 915.5 | 1990 | 1403.5 | 621.5 | 157 | 120 | 0 | 102
9:00 | 3307 | 917 | 2014 | 1488 | 621 | 157 | 120 | 0 | 106
9:30 | 3337 | 917 | 2015.5 | 1729.5 | 619 | 158 | 120 | 0 | 108
10:00 | 3367 | 917 | 2017 | 1971 | 617 | 159 | 120 | 0 | 110
10:30 | 3342.5 | 917 | 1968.5 | 2091.5 | 616 | 158.5 | 124 | 0 | 113
11:00 | 3318 | 917 | 1920 | 2212 | 615 | 158 | 128 | 0 | 116
11:30 | 3326 | 917 | 1954 | 2324.5 | 614.5 | 157.5 | 124 | 0 | 114
12:00 | 3334 | 917 | 1988 | 2437 | 614 | 157 | 120 | 0 | 112
12:30 | 3329 | 917 | 1994.5 | 2501 | 614 | 154 | 120 | 0 | 113
13:00 | 3324 | 917 | 2001 | 2565 | 614 | 151 | 120 | 0 | 114
13:30 | 3324 | 917 | 2001 | 2565 | 614 | 151 | 120 | 0 | 114
14:00 | 3324 | 917 | 2001 | 2565 | 614 | 151 | 120 | 0 | 114
14:30 | 3341.5 | 917 | 1985.5 | 2525.5 | 614 | 151 | 144.5 | 0 | 117
15:00 | 3359 | 917 | 1970 | 2486 | 614 | 151 | 169 | 0 | 120
15:30 | 3322.5 | 916.5 | 1988 | 2407.5 | 614 | 151.5 | 169 | 0 | 118
16:00 | 3286 | 916 | 2006 | 2329 | 614 | 152 | 169 | 0 | 116
16:30 | 3283 | 916 | 1998 | 2159 | 606.5 | 152 | 169 | 0 | 114
17:00 | 3280 | 916 | 1990 | 1989 | 599 | 152 | 169 | 0 | 112
17:30 | 3238.5 | 916.5 | 1894 | 1983.5 | 599 | 153 | 171.5 | 0 | 113
18:00 | 3197 | 917 | 1798 | 1978 | 599 | 154 | 174 | 0 | 114
18:30 | 3239 | 916 | 1905.5 | 2469.5 | 608 | 155 | 420.5 | 0 | 125
19:00 | 3281 | 915 | 2013 | 2961 | 617 | 156 | 667 | 0 | 136
19:30 | 3344 | 916 | 2060 | 3525 | 754 | 156 | 693 | 0 | 126
20:00 | 3325 | 917 | 2041 | 3625 | 729 | 156 | 716 | 0 | 140
20:30 | 3392.5 | 916.5 | 2090 | 3527 | 750 | 157 | 691.5 | 0 | 141
21:00 | 3460 | 916 | 2139 | 3429 | 771 | 158 | 667 | 0 | 142
21:30 | 3478.5 | 916 | 2149 | 3387 | 771 | 158 | 665.5 | 0 | 141
22:00 | 3497 | 916 | 2159 | 3345 | 771 | 158 | 664 | 0 | 140
22:30 | 3501.5 | 916.5 | 2150 | 3275 | 755 | 158 | 633 | 0 | 139
23:00 | 3506 | 917 | 2141 | 3205 | 739 | 158 | 602 | 0 | 138
23:30 | 3501.5 | 916.5 | 2158.5 | 3205 | 734 | 157 | 561.5 | 0 | 136 | Max Temp. in Dhaka |  | 31.5° C
24:00 | 3497 | 916 | 2176 | 3205 | 729 | 156 | 521 | 0 | 134
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 242.349 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 242.349 MKWHr
Note on W13: Author:

## Generation
g | 2020-08-17
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 82 | 82 | 82 | 83 | 85 | 85 | 86 | 87 | 87 | 89 | 88 | 87 | 81 | 81 | 81 | 82 | 82 | 84 |  | 86 | 86 | 86 | 88 | 88 | 88 | 86 | 2012296
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1700000
3 | Chattogram TPP-1 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2600000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [19 empty] | 7 | 8 | 8 | 8 | 8 | 8 | 8 | 57965
| Teknaf 20MW PP (Solartech) | [5 empty] | 0.4 | 2.2 | 5.27 | 6.39 | 6.25 | 11.37 | 17.86 | 8.91 | 10.5 | 15.5 |  | 0.9 | [9 empty] | 75870
6 | Sikalbaha 225MW CCPP (Gas) | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 227 | 231 | 230 | 230 | 231 | 191 | 165 | 164 | 164 | 164 |  | 164 | 164 | 164 | 164 | 165 | 164 | 164 | 4215941
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 100 | 100 | 100 | 101 | 102 | 99 | [5 empty] | 50 | 105 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 105 | 104 | 103 | 1851780
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 68 | 68 | 68 | 37 | 34 | 17 | 8 | 256040
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | 50 | 0 | [17 empty] | 50 | 50 | 50 |  |  |  | 0 | 83560
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 295 | 298 | 301 | 298 | 307 | 300 | 314 | 288 | 306 | 308 | 279 | 204 | 209 | 210 | 210 | 182 | 177 | 153 |  | 154 | 180 | 180 | 180 | 218 | 214 | 214 | 5955957
18 | Kodda 300 MW PP Unit-2 (Summit) | 286 | 280 | 270 | 270 | 215 | 110 | 110 | 110 | 124 | 227 | 269 | 267 | 267 | 267 | 269 | 267 | 180 | 180 |  | 219 | 286 | 286 | 286 | 290 | 300 | 300 | 5851197
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 301090
20 | Ghorasal TPP (Unit-1&2) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 571000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2709000
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2018580
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 20 | 25 | 25 | 25 | 25 | 36 | 35 | 355536
33 | Ashuganj 225 MW CCPP | 215 | 181 | 183 | 182 | 185 | 181 | 197 | 182 | 184 | 192 | 215 | 192 | 183 | 183 | 198 | 182 | 182 | 183 |  | 193 | 189 | 182 | 216 | 217 | 217 | 175 | 4687000
34 | Ashuganj 450 MW CCPP(South) | 230 | 230 | 235 | 230 | 235 | 240 | 240 | 250 | 260 | 285 | 275 | 300 | 275 | 325 | 295 | 275 | 275 | 275 |  | 285 | 275 | 275 | 275 | 275 | 270 | 270 | 6453000
| Ashuganj 450 MW CCPP(North) | 270 | 265 | 270 | 270 | 265 | 265 | 290 | 270 | 270 | 275 | 270 | 290 | 270 | 270 | 285 | 270 | 270 | 270 |  | 275 | 270 | 270 | 300 | 295 | 300 | 300 | 6757000
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 139680
36 | Chandpur 150 MW CCPP | 90 | 92 | 92 | 92 | 95 | 95 | 95 | 90 | 91 | 95 | 85 | 96 | 85 | 91 | 94 | 92 | 85 | 95 |  | 95 | 95 | 87 | 87 | 86 | 85 | 86 | 2167820
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 370 | 370 | 370 | 370 | 370 | 370 | 340 | 340 | 340 | 340 | 340 | 350 | 350 | 320 | 360 | 400 | 400 | 320 |  | 370 | 370 | 370 | 400 | 400 | 400 | 400 | 8739500
41 | Haripur 360MW CCPP(HPL) | 303 | 303 | 303 | 303 | 303 | 303 | 303 | 352 | 354 | 350 | 350 | 347 | 345 | 304 | 304 | 304 | 304 | 262 |  | 287 | 303 | 303 | 355 | 355 | 356 | 356 | 7605000
42 | RPCL 210MW CCPP | 142 | 158 | 157 | 158 | 158 | 158 | 157 | 157 | 157 | 154 | 154 | 138 | 124 | 122 | 122 | 124 | 124 | 124 |  | 123 | 123 | 124 | 124 | 124 | 124 | 158 | 3288200
43
44 | Fenchugonj CCPP Phase-1 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 87 | 86 | 88 | 88 | 88 | 88 | 88 | 88 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 2073000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720480
46 | Shajibazar 330 MW CCPP | 202 | 200 | 197 | 196 | 204 | 200 | 206 | 200 | 202 | 209 | 195 | 205 | 195 | 210 | 211 | 200 | 196 | 199 |  | 203 | 203 | 194 | 198 | 193 | 200 | 198 | 4586000
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 62 | 62 | 62 | 62 | 62 | 67 | 67 | 64 | 63 | 64 | 63 | 64 | 64 | 61 | 62 | 62 | 40 |  | 62 | 62 | 62 | 63 | 63 | 63 | 63 | 1483584
48 | Shahjibazar 86MW PP (Shahjibazar) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 83 | 83 | 83 | 84 | 85 | 84 | 85 | 85 | 85 | 85 | 40 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1988160
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1539790
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 420000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 246780
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 2 | 5 | 8 | 8 | 11 | 11 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 208224
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 50 | 50 | 50 | 50 | 47 |  | 47 | 47 | 47 | 50 | 50 | 50 | 50 | 1192200
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 575400
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 290 | 300 | 290 | 290 | 275 | 290 | 300 | 300 | 300 | 290 | 290 | 290 | 280 | 310 | 285 | 290 | 270 |  | 280 | 305 | 280 | 270 | 290 | 275 | 280 | 7172300
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 17 | 0 | [7 empty] | 25 | 35 | 50 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 55 | 55 | 55 | 17 | 17 | 581665
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 426720
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 429588
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 434124
63 | Impoprt (Tripura) | 130 | 126 | 122 | 116 | 112 | 106 | 96 | 98 | 106 | 110 | 116 | 112 | 114 | 122 | 120 | 116 | 112 | 114 |  | 136 | 126 | 140 | 142 | 140 | 138 | 134 | 2877120
64 | Malancha, Ctg. EPZ (United) | 27 | 27 | 27 | 27 | 33 | 33 | 28 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 2 | 2 | 8 | 4 |  | 10 | 15 | 24 | 28 | 33 | 33 | 33 | 377760
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 18 | 18 | 18 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 474048
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 185220
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 615100
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 21 | 21 | 21 | 19 | 14 | 14 | 14 | 14 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 484020
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 28 | 28 | 28 | 28 | 26 | 26 | 6 | 28 | 28 | 28 | 28 | 28 | 29 | 29 |  | 20 | 30 | 30 | 30 | 30 | 30 | 30 | 642780
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 817800
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 817300
73 | Ghorashal 108MW PP (Regent) | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 98 | 98 | 93 | 93 | 94 | 94 | 95 | 93 | 93 | 98 | 99 |  | 99 | 99 | 99 | 99 | 99 | 98 | 99 | 2300000
| Feni Lanka Power | [17 empty] | 17 |  | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 670320
| Chowmuhani 113 MW | 47 | 47 | 47 | 53 | 56 | 56 | 56 | 57 | 47 | 52 | 47 | 47 | 47 | 47 | 48 | 52 | 51 | 57 |  | 56 | 57 | 57 | 57 | 56 | 56 | 56 | 1260000
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 100 | 100 | 100 | 90 | 40 | 40 | 45 | 80 | 91 | 91 | 91 | 91 | 91 | 91 | 93 | 60 | 50 |  | 70 | 100 | 100 | 100 | 100 | 100 | 100 | 2081280
78 | Gazipur 52 MW PP | [17 empty] | 8 |  | 34 | 52 | 52 | 8 |  |  | 0 | 116292
79 | Kodda 150MW PP | 82 | 64 | 48 | 32 | 32 | 0 | [13 empty] | 149 | 149 | 149 | 149 | 149 | 149 | 98 | 1119360
80 | Jamalpur 95 MW PP(Powerpac) | 72 | 72 | 72 | 72 | 72 | 50 | 24 | 24 | 24 | 26 | 41 | 56 | 72 | 72 | 72 | 72 | 32 | 16 |  | 46 | 71 | 71 | 72 | 72 | 72 | 72 | 1392000
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 20 | 0 | [13 empty] | 1 |  | 19 | 24 | 43 | 43 | 43 | 43 | 43 | 350126
| Gazipur 100 MW PP | 17 | 0 | [7 empty] | 52 | 53 | 89 | 89 | 51 | 70 | 48 | 35 | 35 |  | 56 | 105 | 105 | 70 | 35 | 35 | 35 | 948792
| Kaptai 7 MW Solar PP | [5 empty] | 0.3 | 0.3 | 0.9 | 0.3 | 1.9 | 2.8 | 2.9 | 1.5 | 1.7 | 2.7 | 0.6 | 0.1 | [9 empty] | 16800
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | 80 | 80 | 80 | 80 | 80 | 70 | 48 | 48 | 55 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 92 | 96 | 96 | 96 | 96 | 96 | 95 | 1922352
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [10 empty] | 5 | 20 | 34 | 40 | 40 | 25 | 10 | 10 |  | 60 | 90 | 92 | 100 | 54 | 10 | 10 | 551108
86 | Meghnaghat CCPP(Summit) | 290 | 300 | 300 | 300 | 295 | 295 | 310 | 290 | 295 | 305 | 270 | 300 | 280 | 295 | 315 | 285 | 290 | 295 |  | 305 | 300 | 280 | 280 | 280 | 280 | 270 | 7006051
87 | Meghnaghat 100 MW(IEL) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 200640
| Meghnaghat 104 MW PP (OPCL) | 30 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 25 | 28 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 468480
88 | Ghorashal 78.5 MW PP(MAX) | 69 | 69 | 67 | 65 | 64 | 67 | 66 | 60 | 60 | 60 | 60 | 69 | 68 | 68 | 67 | 68 | 68 | 68 |  | 69 | 69 | 69 | 66 | 62 | 67 | 64 | 1549184
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44MW (Energyprima) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 45 | 45 | 48 | 49 | 49 | 46 | 40 | 49 |  | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1146960
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 10 | 10 | 25 | 31 | 31 | 43 | 43 | 43 |  | 43 | 43 | 51 | 51 | 51 | 51 | 51 | 1095533
94 | Gagnagar 102 MW PP (Digital Power) | 93 | 93 | 93 | 93 | 58 | 24 | 24 | 24 | 32 | 58 | 93 | 93 | 93 | 93 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 1203408
95 | Patenga 50MW PP (Baraka) | 50 | 0 | [9 empty] | 16 | 32 | [6 empty] | 21 | 50 | 50 | 50 | 50 | 50 | 50 | 391200
96 | Chattogram 108 MW PP (ECPV) | 91 | 91 | 25 | 0 | [6 empty] | 17 | 72 | 90 | 90 | 90 | 60 | 51 | 51 |  | 68 | 91 | 91 | 91 | 91 | 91 | 91 | 1325760
97 | Katpotti 52 MW PP (Sinha) | 47 | 47 | 0 | [8 empty] | 1 | 47 | 47 | 47 | 47 | 24 | 24 |  | 31 | 47 | 48 | 47 | 47 | 18 | 18 | 600192
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | 35 | 0 | [7 empty] | 22 | 45 | 40 | 55 | 55 | 55 | 55 | 30 | 30 |  | 45 | 55 | 55 | 55 | 55 | 55 | 55 | 781124
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 17 | 17 | 0 |  |  |  | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1022869
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 130 | 110 | 130 | 130 | 130 | 110 | 130 | 130 | 110 | 110 | 130 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 163 | 3387273
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0.1 | 0.2 | 0.3 | 0.9 | 1.5 | 1.3 | 2.5 | 1.8 | 0.2 | 0.2 | 1.4 | 0.3 | [9 empty] | 9500
103 | Kamalaghat 54 MW PP(Banco Energy) | 53 | 53 | 53 | 53 | 53 | 17 |  |  | 9 | 53 | 53 | 53 | 53 | 40 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1060920
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 193 | 194 | 195 | 195 | 195 | 200 | 200 | 200 | 200 | 200 | 193 | 200 | 200 | 200 | 188 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4704000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 131 | 131 | 131 | 131 | 131 | 118 | 102 | 102 | 127 | 130 | 133 | 131 | 131 | 131 | 133 | 132 | 133 | 132 |  | 133 | 133 | 132 | 133 | 132 | 131 | 131 | 3110400
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2391360
116 | Chandpur 200MW (Desh energy) | [19 empty] | 35 | 50 | 102 |  |  |  | 0 | 180960
117 | Ashuganj 150MW PP (Midland) | 80 | 80 | 80 | 10 | 0 |  |  |  | 13 | 43 | 60 | 30 | 30 | 30 | 30 | 30 | 30 | 33 |  | 72 | 100 | 100 | 100 | 100 | 60 | 60 | 1254545
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 115 | 115 | 75 | 75 | 45 | 0 |  |  |  | 2 | 16 | 16 | 8 | 8 | 8 | 8 | 8 | 8 |  | 43 | 112 | 115 | 115 | 115 | 115 | 115 | 1213200
| Anwara 300 MW PP (United) | 233 | 233 | 233 | 233 | 233 | 125 | 87 | 87 | 123 | 195 | 179 | 179 | 179 | 179 | 179 | 179 | 124 | 125 |  | 230 | 231 | 233 | 234 | 234 | 235 | 235 | 4554000
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 98 | 100 | 100 | 100 | 60 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2351040
120 | Eastern Zone Total | 6936 | 6717 | 6534 | 6346 | 6229 | 5693.8 | 5491.7 | 5474.47 | 5719.59 | 6217.65 | 6234.47 | 6438.26 | 6541.21 | 6435.4 | 6435.4 | 6307 | 6015.3 | 5782 |  | 6920 | 7397 | 7458 | 7355 | 7314 | 7155 | 7104 | 156159204
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 113 | 115 | 115 | 115 | 115 | 66 | 66 | 73 | 99 | 99 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 99 | 99 | 99 | 2547840
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
| Khulna 225 MW CCPP | 160 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 165 | 170 | 190 | 230 | 230 | 215 | 200 | 3507012
129 | Rupsha 105 MW PP (Orion rupsha) | 53 | 17 | 0 | [16 empty] | 90 | 90 | 90 | 55 | 90 | 90 | 70 | 540000
130
131
132
133
| Barisal 110 MW PP (Summit ) | [17 empty] | 8 |  | 80 | 80 | 80 | 64 | 48 | 48 | 48 | 355776
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 77 | 77 | 77 | 76 | 78 | 77 | 33 | 32 | 32 | 32 | 31 | 43 | 43 | 43 | 43 | 41 | 43 | 42 |  | 77 | 76 | 75 | 78 | 78 | 79 | 77 | 1388406
| Bhola 225 MW CCPP | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 90 | 89 | 89 | 89 | 90 | 90 | 89 | 90 | 90 |  | 90 | 90 | 90 | 89 | 89 | 89 | 89 | 2173196
140 | Bhola 33 MW PP (Venture) | 32 | 30 | 25 | 25 | 23 | 18 | 19 | 17 | 17 | 15 | 18 | 19 | 19 | 17 | 15 | 16 | 16 | 20 |  | 25 | 28 | 29 | 30 | 31 | 31 | 30 | 528528
141 | Noapara 100 MW PP (Bangla Trac) | 30 | 0 | [17 empty] | 4 | 50 | 75 | 100 | 100 | 100 | 100 | 551040
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 0 | [16 empty] | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 304875
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 914 | 914 | 914 | 914 | 913 | 914 | 914 | 914 | 917 | 917 | 917 | 917 | 917 | 917 | 917 | 916 | 916 | 917 |  | 915 | 916 | 917 | 916 | 916 | 917 | 916 | 21969455
147 | Bheramara 410 MW CCPP | 345 | 345 | 345 | 345 | 345 | 345 | 365 | 345 | 345 | 345 | 345 | 355 | 345 | 345 | 375 | 345 | 345 | 343 |  | 350 | 345 | 345 | 340 | 345 | 345 | 345 | 8615808
148 | Payra 1320 MW | 540 | 520 | 518 | 500 | 500 | 488 | 470 | 472 | 472 | 468 | 465 | 465 | 464 | 464 | 465 | 465 | 450 | 450 |  | 468 | 605 | 580 | 622 | 622 | 590 | 580 | 12983900
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 150 | 149 | 149 | 150 | 149 | 150 | 150 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3651600
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP | [22 empty] | 70 | 70 | 70 | 70 | 264000
| Baghabari 50 MW Peaking PP | 50 | 0 | [17 empty] | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 316704
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 172 | 174 | 174 | 152 | 153 | 152 | 158 | 152 | 162 | 167 | 187 | 171 | 157 | 156 | 170 | 175 | 181 | 159 |  | 159 | 172 | 176 | 177 | 179 | 177 | 178 | 4247727
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 215 | 215 | 215 | 215 | 215 | 216 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 185 | 150 | 175 | 180 | 150 |  | 150 | 180 | 180 | 180 | 180 | 180 | 180 | 4648200
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 402 | 408 | 414 | 410 | 403 | 333 | 360 | 351 | 397 | 411 | 386 | 403 | 404 | 402 | 400 | 392 | 356 | 345 |  | 383 | 382 | 371 | 388 | 386 | 377 | 382 | 9371900
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 5 |  | 35 | 35 | 35 | 35 | 35 | 6 |  | 155771
162 | Bogra 22 MW PP (GBB) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 18 | 18 | 18 | 18 | 406560
163 | Bogura 20 MW PP (Energyprima) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 261648
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 8 | 8 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 225684
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 8 |  | 16 | 25 | 25 | 25 | 25 | 25 | 25 | 137502
167 | Katakhali 50 MW Peaking PP | 44 | 0 | [17 empty] | 42 | 45 | 47 | 44 | 44 | 44 | 44 | 301490
168 | Santahar 50 MW Peaking PP | 25 | 0 | [17 empty] | 18 | 26 | 27 | 26 | 26 | 25 | 25 | 182940
169 | Natore 52 MW PP (Rajlanka) | 52 | 0 | [15 empty] | 1 |  | 36 | 52 | 52 | 52 | 52 | 52 | 44 | 357120
170 | Chapainawabganj 100 MW Peaking PP | 90 | 90 | 86 | 16 | 16 | 0 |  |  |  |  | 8 |  |  | 49 | 49 | 49 | 49 | 49 |  | 90 | 100 | 100 | 96 | 96 | 96 | 96 | 1090368
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 57 | 57 | 57 | 0 | [7 empty] | 23 | 51 | 56 | 56 | 56 | 35 | 35 |  | 62 | 96 | 94 | 94 | 94 | 94 | 57 | 1043040
172 | Confidence Power Bogura Unit-1 113 MW | 109 | 109 | 109 | 109 | 70 | 35 | 35 | 35 | 35 | 70 | 109 | 109 | 109 | 109 | 109 | 35 | 35 | 35 |  | 95 | 109 | 109 | 109 | 109 | 109 | 109 | 2049888
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 107 | 107 | 106 | 107 | 100 | 44 |  |  |  |  | 39 | 100 | 108 | 113 | 108 | 107 | 75 | 70 |  | 84 | 113 | 112 | 113 | 113 | 114 | 113 | 1979520
177 | Sympa Solar Power 8MW | [5 empty] | 0.1 | 0.8 | 1.4 | 2.4 | 2.6 | 1.8 | 3.5 | 7.9 | 2.2 | 1.9 | 1.8 | 1.7 | 0.5 | [8 empty] | 32110
178
178