## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:July 2020
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | July 2020 |  | June 2020 |  | July 2019
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 12552 | 26/07/20 | 12070 | 24/06/20 | 12436 | 21/07/19 | 12893 | 29/05/19
|  |  | 22:00 |  | 22:00 |  | 21:00 |  | 21:00
2 | Minimum Generation (MW) | 7092.1 | 31/07/20 | 6656.5 | 05/06/20 | 6202 | 14/07/19 | - | -
|  |  | 8:00 |  | 7:00 |  | 6:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 12536 | 26/07/20 | 12070 | 24/06/20 | 12436 | 21/07/19 | 12893 | 29/05/19
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 10525.4 | 26/07/20 | 10183.6 | 24/06/20 | 10285.4 | 22/07/19 | 10636.2 | 01/09/19
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 12536 | 26/07/20 | 12070 | 24/06/20 | 12436 | 21/07/19 | 12893 | 29/05/19
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 11474.9032 |  | 10925.7667 |  | 11518.3226 |  | 11679.07 | 2019-09-19
7 | Average Generation (MW) at Day Peak | 9424.8087 |  | 9156.325 |  | 9293.471 |  | 9378.1933 | 2019-09-19
8 | Maximum Power Import from India, HVDC (MW) | 951 | 13/07/2020 | 950 | 04/06/2020 | 936 | 26/07/19 | 956 | 27/3/2019
|  |  | 2:30 |  | 2:30 |  | 5:30 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 174 | 27/07/2020 | 182 | 09/06/2020 | 194 | 21/07/19 | 194 | 12/06/19
|  |  | 23:00 |  | 21:00 |  | 22:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 2010-05-04
20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 3707.5 | 05/04/10
20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 3547.5075 |  | 3156.9465 |  | 3406.3279 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 100.2925 |  | 79.8302 |  | 125.0884
22 | Net Generation of BPDB (MKWH) | 3447.2149 |  | 3077.1163 |  | 3281.2394
23 | Net Generation of IPP & RPCL (MKWH) | 2424.5663 |  | 2233.4592 |  | 2468.1236
24 | Net Generation of REB (MKWH) | 150.4311 |  | 148.3631 |  | 143.6788
24 | Net Generation of Rental Power Plant (MKWH) | 531.8624 |  | 560.7517 |  | 572.3521
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 6554.0747 |  | 6019.6903 |  | 6465.3939 |  | 6554.0747 | July-20
26 | Energy Generation by Gas (MKWH) | 4349.8373 |  | 4101.8172 |  | 4492.67 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 314.162 |  | 302.7603 |  | 279.0809 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1406.9164 |  | 1221.1035 |  | 1524.0229 |  | 1524.02 | July-19
29 | Energy Generation by Hydro (MKWH) | 90.7677 |  | 62.4299 |  | 102.8917 |  | 151.4 | August-19
30 | Energy Generation by Solar (MKWH) | 4.1688 |  | 4.9313 |  | 3.1773 |  | 22.56 | 2019-09-16
31 | Energy Generation by Coal (MKWH) | 488.515 |  | 406.4783 |  | 189.3114 |  | 488.515 | July-20
32 | Enegry Import from India (HVDC & AC) (MKWH) | 769.1694 |  | 736.3907 |  | 736.9925 |  | 769.1694 | July-20
33 | Monthly Load Factor (%) | 79.4923 |  | 78.6605 |  | 79.2028 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:July' 2020
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 12552 | 26/07/20 | 22:00
Generation Period
| Dhaka | MW | 4054
| Chattogram | MW | 1100
| Cumilla | MW | 1222
| Mymensingh | MW | 963
| Sylhet | MW | 501
a) | Total supply in East zone | MW | 7840
| Khulna | MW | 1598
| Barisal | MW | 369
| Rajshahi | MW | 1332
| Rangpur | MW | 768
b) | Total supply in West zone | MW | 4067
c) | Total supply in both zone ( a+b) | MW | 11907
Ref: | 27.21.0000.603.16.087.20.305 | Date: 16/08/2020
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:July' 2020
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 325 | 04/07/20 | 21:00
| b) Ishurdi end | MW | 233 | 23/07/20 | 10:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 565 | 23/07/20 | 10:00
| b) Ishurdi end | MW | 125 | 04/07/20 | 21:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | 0.9936 | 02/07/20
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | 0.99 | 02/07/20
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 5.9509
| b) Ishurdi end | MKWH | 50.6201
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 49.1015
| b) Ishurdi end | MKWH | 5.7776
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 360 | 04/07/20 | 17:00
| b)Serajganj end | MW | 540 | 10/07/20 | 17:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 520 | 10/07/20 | 17:00
| b)Sirajganj end | MW | 350 | 04/07/20 | 17:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 2.696 | 15/07/20
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 2.66 | 15/07/20
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 21.18
| b)Sirajganj end | MKWH | 83.196
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 81.716
| b)Sirajganj end | MKWH | 21.028
30 | Transmission loss of EWI /NO-2 | % | 2.308
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishwardi.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: July 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kabirpur | 132/33 kV Transformer-T2 | 2020-07-02 05:26 | 2020-07-02 06:44 | 1:18 | E/O | Due to 33 kV Breaker maintenance | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformers-T1 & T2 | 2020-07-05 06:35 | 2020-07-05 07:58 | 1:23 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Kishorganj | 132/33 kV Transformers-T1 & T2 | 2020-07-11 05:58 | 2020-07-11 06:30 | 0:32 | T | Tripped showing 33 kV feeder fault | 90 | 48 | Power interruption
Manikganj | 132/33 kV Transformer-T2 | 2020-07-18 09:36 | 2020-07-18 11:10 | 1:34 | E/O | Due to red-hot maintenance at 33 kV side | 5 | 7.8333 | Power interruption
Mymensingh | 132/33 kV Transformers-T1 & T2 | 2020-07-19 09:48 | 2020-07-19 09:57 | 0:09 | T | Tripped showing 33 kV feeder fault | 55 | 8.25 | Power interruption
Savar | 132/33 kV Transformer-T1 | 2020-07-18 08:44 | 2020-07-18 08:48 | 0:04 | T | Tripped showing 33 kV feeder fault | 100 | 6.6667 | Power interruption
Mirpur | 132/33 kV Transformer-T1 | 2020-07-19 20:20 | 2020-07-19 20:20 | 0:00 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Kishorganj | 132/33 kV Transformers-T1 | 2020-07-20 12:03 | 2020-07-20 12:53 | 0:50 | T | Tripped showing 33 kV feeder fault | 55 | 45.8333 | Power interruption
| 132/33 kV Transformers-T2 | 2020-07-20 12:03 | 2020-07-20 12:57 | 0:54 | T
Tangail | 132/33 kV Transformer-T3 | 2020-07-30 22:36 | 2020-07-30 23:59 | 1:23 | E/O | Due to red-hot maintenance at 33 kV side | 39 | 156 | Power interruption 22:23 to 23:59
|  |  | Total : | 8:07 |  | Unserved Energy: |  | 272.5833
Dhaka (South) Grid Circle :
Madanganj | 132/33 kV Transformer-GT1 | 2020-07-01 04:53 | 2020-07-01 05:07 | 0:14 | T | Tripped showing backup protection relay | 0 | 0 | No interruption
Fatulla | 132/33 kV Transformer-T-2 | 2020-07-01 07:05 | 2020-07-01 10:00 | 2:55 | T | Tripped showing no relay | 0 | 0 | No interruption
| 132/33 kV Transformer-T-1 | 2020-07-03 09:07 | 2020-07-03 11:32 | 2:25 | T | Tripped showing protection block | 0 | 0 | No interruption
Madanganj | 132/33 kV Transformer-T-1 | 2020-07-05 09:03 | 2020-07-05 20:06 | 11:03 | T | Tripped showing E/F relay at 33 kV side | 0 | 0 | No interruption
Madanganj | 132/33 kV Transformer-T-1 | 2020-07-11 13:20 | 2020-07-11 22:50 | 9:30 | T | Tripped showing protection block | 21 | 199.5 | Power interruption
|  |  | Total : | 26:07 |  | Unserved Energy: |  | 199.5
Chattogram Grid Circle :
Halishahar | 132/33 kV Transformer-T2 | 2020-07-02 12:31 | 2020-07-02 13:54 | 1:23 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Hathazari | 132/33 kV Transformer-T-1 | 2020-07-07 20:40 | 2020-07-08 02:00 | 5:20 | T | Tripped showing XLPE 33 kV cable fault | 35 | 186.6667 | Power interruption
Khulshi | 132/33 kV Transformer-T-1 & 33 kV Bus | 2020-07-13 00:24 | 2020-07-13 01:53 | 1:29 | E/O | Due to red-hot maintenance 33 kV side | 50 | 74.1667 | Power interruption
Madunaghat | 132/33 kV Transformer-T-1 | 2020-07-13 06:32 | 2020-07-13 08:14 | 1:42 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Bakulia | 132/33 kV Transformer-T-3 | 2020-07-14 19:52 | 2020-07-14 21:52 | 2:00 | T | Tripped showing O/C relay at 33 kV side | 0 | 0 | No interruption
Dohazari | 132/33 kV Transformer-T-1 | 2020-07-15 18:19 | 2020-07-15 21:48 | 3:29 | T | Tripped showing O/C& E/F relay at 33 kV feeder fault | 20 | 65.8333 | Power interruption 18:19 to 19:48
Khulshi | 132/33 kV Transformer-T1 | 2020-07-21 01:40 | 2020-07-21 02:46 | 1:06 | E/O | Due to red-hot maintenance 33 kV side | 25 | 27.5 | Power interruption
Modern | 132/33 kV Transformer-T1 | 2020-07-24 10:29 | 2020-07-24 11:08 | 0:39 | E/O | Due to red-hot maintenance at 11 kV side | 0 | 0 | No interruption
Halishahar | 132/33 kV Transformer-T2 & 33 kV Bus | 2020-07-25 05:11 | 2020-07-25 05:19 | 0:08 | T | Due to Baraka Patenga feeder fault | 18 | 2.4 | Power interruption
| 132/33 kV Transformers-T-1 & T3 | 2020-07-25 22:29 | 2020-07-25 23:49 | 1:20 | E/O | Due to red-hot maintenance 33 kV side | 52 | 69.3333 | Power interruption
|  |  | Total : | 18:36 |  | Unserved Energy: |  | 425.9
Cumilla Grid Circle :
Chowmuhani | 132/33 kV Transformer-T1 | 2020-07-03 06:20 | 2020-07-03 07:35 | 1:15 | E/O | Due to red-hot maintenance | 40 | 50 | Power interruption
Cumilla | 132/33 kV Transformer-T4 | 2020-07-07 11:20 | 2020-07-07 14:56 | 3:36 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Chatak | 132/33 kV Transformer-T2 | 2020-07-10 00:49 | 2020-07-10 01:50 | 1:01 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Baroirhat | 132/33 kV Transformer-T2 | 2020-07-12 11:22 | 2020-07-12 12:50 | 1:28 | E/O | Due to red-hot maintenance 33 kV side | 0 | 0 | No interruption
Sreemongal | 132/33 kV Transformer-T3 | 2020-07-14 18:25 | 2020-07-14 18:44 | 0:19 | T | Tripped showing E/F relay at 33 kV side | 0 | 0 | No interruption
Cumilla (S) | 132/33 kV Transformer-T3 | 2020-07-21 19:38 | 2020-07-22 13:31 | 17:53 | T | Due to 33 kV CB pole(R-phase) burst | 0 | 0 | No interruption
Chowmuhani | 132/33 kV Transformer-T3 | 2020-07-22 08:50 | 2020-07-22 10:50 | 2:00 | E/O | Due to red-hot maintenance | 10 | 20 | Power interruption
Sreemongal | 132/33 kV Transformers-T2 & T3 | 2020-07-22 10:20 | 2020-07-22 11:20 | 1:00 | E/O | Due to red-hot maintenance 33 kV side | 10 | 10 | Power interruption
Shahjibazar | 132/33 kV Transformer-T1 | 2020-07-22 10:16 | 2020-07-22 13:52 | 3:36 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Baroirhat | 132/33 kV Transformers-T1 & T2 | 2020-07-23 15:00 | 2020-07-23 16:05 | 1:05 | T | Tripped showing Dist. relay at 33 kV side | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV Transformer-T3 | 2020-07-25 10:23 | 2020-07-25 15:26 | 5:03 | E/O | Due to SF6 gas low | 0 | 0 | No interruption
Sylhet | 132/33 kV Transformer-T4 | 2020-07-26 00:22 | 2020-07-26 04:32 | 4:10 | E/O | Due to SF6 gas leakage at 33 kV CB incoming | 0 | 0 | No interruption
Chowmuhani | 132/33 kV Transformers-T2 | 2020-07-27 14:25 | 2020-07-27 14:25 | 0:00 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
| 132/33 kV Transformers-T3 | 2020-07-27 14:25 | 2020-07-27 15:00 | 0:35 | T |  | 0 | 0 | No interruption
Ramganj | 132/33 kV Transformers-T1 | 2020-07-29 15:30 | 2020-07-29 16:02 | 0:32 | T | Tripped showing winding temperature & O/C relay | 82 | 43.7333 | Power interruption
| 132/33 kV Transformers-T2 | 2020-07-29 15:30 | 2020-07-29 16:25 | 0:55 | T
Chowmuhani | 132/33 kV Transformers-T1 & T3 | 2020-07-31 00:40 | 2020-07-31 00:46 | 0:06 | T | Tripped showing E/F relay at 33 kV side | 172 | 17.2 | Power interruption
|  |  |  | 44:34 |  | Unserved Energy: |  | 140.9333
Page: 2/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: July 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Faridpur | 132/33 kV Transformer-T1 | 2020-07-07 22:28 | 2020-07-07 22:53 | 0:25 | T | Tripped showing E/F relay | 160 | 66.6667 | Power interruption
| 132/33 kV Transformer-T2 | 2020-07-07 22:28 | 2020-07-07 22:54 | 0:26 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-07-08 15:35 | 2020-07-08 16:04 | 0:29 | E/O | Due to red-hot maintenance 33 kV side | 60 | 29 | Power interruption
Mongla | 132/33 kV Transformer-T1 | 2020-07-10 10:01 | 2020-07-10 11:56 | 1:55 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Satkhira | 132/33 kV Transformer-T2 | 2020-07-11 07:20 | 2020-07-11 10:38 | 3:18 | E/O | Due to Oil leakage | 10 | 33 | Power interruption
Bagerhat | 132/33 kV Transformer-T1 | 2020-07-15 07:25 | 2020-07-15 08:56 | 1:31 | E/O | Due to red-hot maintenance 33 kV side | 15 | 22.75 | Power interruption
Chuadanga | 132/33 kV Transformer-T1 & 33 kV Bus-1 & 2 | 2020-07-18 07:19 | 2020-07-18 09:06 | 1:47 | E/O | Due to red-hot maintenance 33 kV side | 20 | 35.6667 | Power interruption
Patuakhali | 132/33 kV Transformer-T2 | 2020-07-19 13:26 | 2020-07-19 19:27 | 6:01 | T | Tripped showing winding temperature high | 0 | 0 | No interruption
| 132/33 kV Transformers-T1 | 2020-07-23 03:19 | 2020-07-23 04:02 | 0:43 | T | Tripped showing E/F relay at 33 kV side | 70 | 50.1667 | Power interruption
| 132/33 kV Transformers-T2 | 2020-07-23 03:19 | 2020-07-23 04:02 | 0:43 | T
Barisal(S) | 132/33 kV Transformers-T1 & T2 | 2020-07-23 17:16 | 2020-07-23 17:26 | 0:10 | T | Tripped showing inst.O/C & E/F relay at 33 kV side | 64 | 10.6667 | Power interruption
Patuakhali | 132/33 kV Transformer-T1 | 2020-07-23 17:12 | 2020-07-23 17:35 | 0:23 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformers-T1 & T3 | 2020-07-24 16:58 | 2020-07-24 17:24 | 0:26 | T | Due to 33 kV feeder fault | 17 | 7.3667 | Power interruption
Satkhira | 132/33 kV Transformer-T1 | 2020-07-28 17:03 | 2020-07-28 18:23 | 1:20 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Gopalganj(O) | 132/33 kV Transformers-T1 | 2020-07-29 11:41 | 2020-07-29 12:37 | 0:56 | T | Tripped showing E/F relay at 33 kV side
| 132/33 kV Transformers-T2 | 2020-07-29 11:41 | 2020-07-29 12:20 | 0:39 | T |  | 50 | 32.5 | Power interruption
Chuadanga | 132/33 kV Transformer-T2 | 2020-07-29 14:45 | 2020-07-29 16:26 | 1:41 | T | Tripped showing SF6 block | 29 | 48.8167 | Power interruption
| 132/33 kV Transformer-T1 | 2020-07-29 19:58 | 2020-07-29 21:57 | 1:59 | T | Tripped showing O/C relay | 80 | 158.6667 | Power interruption
|  |  | Total : | 24:52 |  | Unserved Energy: |  | 495.2667
HVDC Grid Circle :
Bheramara HVDC | Bheramara HVDC Pole -1 | 2020-07-09 10:19 | 2020-07-09 14:28 | 4:09 | T | Tripped showing no check back signal | 0 | 0 | No interruption
Ishurdi | 230/132 kV Transformer-T02 | 2020-07-12 20:01 | 2020-07-12 23:31 | 3:30 | T | Tripped showing winding temperature high | 0 | 0 | No interruption
| 230/132 kV Transformer-T03 | 2020-07-14 13:50 | 2020-07-14 17:41 | 3:51 | E/O | Due to Breaker problem | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-07-22 22:25 | 2020-07-22 23:01 | 0:36 | E/O | Due to red-hot maintenance | 27 | 16.2 | Power interruption
Bottail | 132/33 kV Transformer-T1 | 2020-07-24 07:02 | 2020-07-24 09:21 | 2:19 | E/O | Due to red-hot maintenance 33 kV side | 25 | 57.9167 | Power interruption
Ishurdi | 132/33 kV Transformer-T3 | 2020-07-24 13:55 | 2020-07-24 14:15 | 0:20 | T | Tripped showing E/F relay at 33 kV side | 18 | 6 | Power interruption
|  |  | Total : | 14:45 |  |  |  | 80.1167
Bogura Grid Circle:
Sherpur | 132/33 kV Transformer-T3 | 2020-07-03 07:21 | 2020-07-03 08:42 | 1:21 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Mohastanghor | 132/33 kV Transformer-T2 | 2020-07-04 16:28 | 2020-07-04 17:25 | 0:57 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Kurigram | 132 kV main Bus | 2020-07-07 21:00 | 2020-07-07 21:46 | 0:46 | E/O | Due to red-hot maintenance | 45 | 34.5 | Power interruption
Barapukuria | 132/33 kV Transformer-T2 | 2020-07-08 11:35 | 2020-07-08 12:10 | 0:35 | T | Tripped showing main protection & Lockout relay
| 132/33 kV Transformer-T3 | 2020-07-08 11:35 | 2020-07-08 12:02 | 0:27 | T
| 132/33 kV Transformer-T5 | 2020-07-08 11:35 | 2020-07-08 12:48 | 1:13 | T
| 132/33 kV Transformer-T6 | 2020-07-08 11:35 | 2020-07-08 11:56 | 0:21 | T |  | 35 | 12.25 | Power interruption
C,nawabganj | 132/33 kV Transformer-T2 | 2020-07-09 10:19 | 2020-07-09 12:17 | 1:58 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Purbasadipur | 132/33 kV Transformer-T1 | 2020-07-09 15:24 | 2020-07-09 16:22 | 0:58 | E/O | Due to red-hot maintenance at 33 kV side | 30 | 29 | Power interruption
Mohastanghor | 132/33 kV Transformer-T1 | 2020-07-11 20:20 | 2020-07-11 20:20 | 0:00 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformer-T3 | 2020-07-13 23:09 | 2020-07-14 01:03 | 1:54 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Bogura | 132/33 kV Transformer-T3 | 2020-07-14 15:20 | 2020-07-14 17:38 | 2:18 | E/O | Due to red-hot maintenance at 33 kV side | 30 | 69 | Power interruption
| 132/33 kV Transformer-T1 | 2020-07-24 07:46 | 2020-07-24 09:15 | 1:29 | E/O | Due to red-hot maintenance at 33 kV side | 40 | 59.3333 | Power interruption
Sirajganj | 132/33 kV Transformer-T3 | 2020-07-26 09:42 | 2020-07-26 11:55 | 2:13 | E/O | Due to red-hot maintenance at 33 kV CB | 0 | 0 | No interruption
Barapukuria | 132/33 kV Transformer-T5 | 2020-07-26 10:19 | 2020-07-26 11:50 | 1:31 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
| 230/132 kV Transformer-T01 | 2020-07-27 00:46 | 2020-07-27 00:56 | 0:10 | T | Tripped showing diff.& O/C relay | 640 | 106.6667 | Power interruption
Rangpur | 132/33 kV Transformer-T2 | 2020-07-27 00:52 | 2020-07-28 16:35 | 39:43 | T | Tripped showing PRD & buchholz relay | 0 | 0 | No interruption
Barapukuria | 132/33 kV Transformer-T5 | 2020-07-29 11:10 | 2020-07-29 12:13 | 1:03 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 58:57 |  |  |  | 310.75
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 195:58 | Hours
T = Tripping | [7 empty] | Executive Engineer
E/O = Emergency Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: July 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar | Aminbazar-Savar 132 kV line-1 | 2020-07-03 03:50 | 2020-07-03 04:53 | 1:03 | T | Tripped showing dist.(Z1) relay | 0 | 0 | No interruption
| Aminbazar-Savar 132 kV line-2 | 2020-07-03 03:50 | 2020-07-03 04:57 | 1:07 | T | Tripped showing differential. relay | 0 | 0 | No interruption
Tangail | Tangail-Mymensingh RPCL 132 kV line-2 | 2020-07-11 02:26 | 2020-07-11 03:05 | 0:39 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Mymensingh RPCL | Mymensingh RPCL-Tangail RPCL 132 kV line-2 | 2020-07-23 17:56 | 2020-07-23 18:25 | 0:29 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Mymensingh RPCL-Tangail 132 kV line-1 | 2020-07-23 17:56 | 2020-07-23 18:13 | 0:17 | T | Tripped showing dist.R-phase relay | 0 | 0 | No interruption
Sherpur | Sherpur-united Mymensingh Power 132 kV line-1 & 2 | 2020-07-29 08:07 | 2020-07-29 08:20 | 0:13 | T | Tripped showing dist. relay | 45 | 9.75 | Power interruption
|  |  | Total : | 3:48 |  | Unserved Energy: |  | 9.75
Dhaka (South) Grid Circle :
Meghnaghat | Meghnaghat-Shyampur 230 kV line-2 | 2020-07-02 06:17 | 2020-07-02 06:28 | 0:11 | T | Tripped showing auto reclose relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj 132 kV line-1 | 2020-07-06 14:30 | 2020-07-06 14:44 | 0:14 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ghorashal-Ashuganj 230 kV line-1 & 2 | 2020-07-08 20:15 | 2020-07-08 21:24 | 1:09 | T | Tripped showing dist. (L1,L2 & L3) relay | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV line-1 | 2020-07-10 12:49 | 2020-07-10 12:59 | 0:10 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hasnabad | Hasnabad-Sitalakyha 132 kV line | 2020-07-17 09:01 | 2020-07-17 09:11 | 0:10 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Madanganj | Madanganj-Sitalakhya 132 kV line | 2020-07-17 09:01 | 2020-07-17 09:15 | 0:14 | T | Tripped showing main protection relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj 132 kV line-1 | 2020-07-17 09:57 | 2020-07-17 09:57 | 0:00 | T | Tripped showing dist.(C-phase) relay | 0 | 0 | No interruption
| Ghorashal-Joydevpur 132 kV line | 2020-07-26 10:43 | 2020-07-26 11:02 | 0:19 | T | Tripped showing remote protection relay | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 132 kV line-2 | 2020-07-30 11:56 | 2020-07-30 14:45 | 2:49 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 5:16 |  | Unserved Energy: |  | 0
Chittagong Grid Circle :
Hathazari | Hathazari-Baroierhat 132 kV line-2 | 2020-07-04 17:34 | 2020-07-04 17:44 | 0:10 | T | Tripped showing E/F & dist. relay | 24 | 4 | Power interruption
Khulshi | Khulshi-Rampur 132 kV line | 2020-07-05 12:42 | 2020-07-05 12:55 | 0:13 | T | Tripped showing dist.(Z3) relay | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Dohazari 132 kV line-1 | 2020-07-06 13:23 | 2020-07-06 13:43 | 0:20 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Sikalbaha-Dohazari 132 kV line | 2020-07-18 09:51 | 2020-07-18 10:44 | 0:53 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
Halishahar | Halishahar-Rampur 132 kV line-1 | 2020-07-31 08:03 | 2020-07-31 11:16 | 3:13 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 4:49 |  | Unserved Energy: |  | 4
Cumilla Grid Circle :
Fenchuganj | Fenchuganj-Sylhet 132 kV line | 2020-07-01 23:59 | 2020-07-02 00:12 | 0:13 | T | Tripped showing dist.& E/F relay | 210 | 45.5 | Power interruption
Cumilla(N) | Cumilla(N)-Chandpur 132 kV line-1 | 2020-07-03 03:04 | 2020-07-03 03:17 | 0:13 | T | Tripped showing dist.& Dire O/C relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2020-07-04 12:48 | 2020-07-04 15:54 | 3:06 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV line-1 | 2020-07-05 20:21 | 2020-07-05 21:06 | 0:45 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Chandraghona 132 kV line-1 | 2020-07-05 16:36 | 2020-07-05 16:45 | 0:09 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorashal 132 kV line-1 | 2020-07-06 21:55 | 2020-07-06 22:47 | 0:52 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-2 | 2020-07-06 21:14 | 2020-07-06 21:14 |  | T | Tripped showing dist. relay | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Tripura 132 kV line | 2020-07-08 11:06 | 2020-07-08 11:27 | 0:21 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorashal 132 kV line-2 | 2020-07-09 18:52 | 2020-07-09 19:08 | 0:16 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Choddagram 132 kV line-1 | 2020-07-10 00:42 | 2020-07-10 00:54 | 0:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj(S) | Ashuganj(S)-Ghorashal 230 kV line-2 | 2020-07-11 07:28 | 2020-07-11 09:05 | 1:37 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2020-07-15 06:38 | 2020-07-15 06:48 | 0:10 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV line-2 | 2020-07-17 11:11 | 2020-07-17 12:26 | 1:15 | T | Tripped showing dist.& O/C relay | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Tripura 132 kV line-2 | 2020-07-21 14:30 | 2020-07-21 14:51 | 0:21 | T | Tripped showing pole discrepancy | 0 | 0 | No interruption
| Cumilla(S)-Tripura 132 kV line-2 | 2020-07-21 14:55 | 2020-07-21 17:18 | 2:23 | T |  | 0 | 0 | No interruption
Ashuganj | Ashuganj-Cumilla(N) 132 kV line-1 | 2020-07-25 14:59 | 2020-07-25 15:26 | 0:27 | T | Tripped showing dist.C-phase relay | 0 | 0 | No interruption
| Ashuganj-Shahjibazar 132 kV line-3 | 2020-07-25 20:06 | 2020-07-25 20:06 | 0:00 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
| Ashuganj-Ghorashal 230 kV line-1 | 2020-07-28 10:48 | 2020-07-28 14:35 | 3:47 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-Ghorashal 230 kV line-1 | 2020-07-28 11:27 | 2020-07-28 14:38 | 3:11 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Tripura 132 kV line-1 | 2020-07-31 14:35 | 2020-07-31 15:04 | 0:29 | T | Tripped showing master protection .relay | 0 | 0 | No interruption
|  |  | Total : | 19:47 |  | Unserved Energy: |  | 45.5
Page: 2/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: July 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Faridpur | Faridpur-Bheramara 132 kV line-1 | 2020-07-04 13:50 | 2020-07-04 14:28 | 0:38 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Faridpur-Bheramara 132 kV line-2 | 2020-07-04 13:50 | 2020-07-04 14:36 | 0:46 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Gopalganj(N) | Gopalganj(N)-Gopalganj (O) 132 kV line | 2020-07-04 13:50 | 2020-07-04 14:34 | 0:44 | T | Tripped showing dist. relay | 435 | 319 | Power interruption
| Gopalganj(N)-Madaripur 132 kV line-3 | 2020-07-04 13:50 | 2020-07-04 15:01 | 1:11 | T | Tripped showing dist. relay
Bhola | Bhola-Barisal 230 kV line-2 | 2020-07-04 16:05 | 2020-07-04 16:28 | 0:23 | T | Tripped showing O/V. relay | 0 | 0 | No interruption
Faridpur | Faridpur-Bheramara 132 kV line-2 | 2020-07-07 14:00 | 2020-07-07 14:46 | 0:46 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Faridpur-Gopalganj (N) 132 kV line-1 | 2020-07-07 14:00 | 2020-07-07 14:44 | 0:44 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Faridpur-Bheramara 132 kV line-1 | 2020-07-07 19:53 | 2020-07-07 20:12 | 0:19 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Khulna (S) | Khulna (S)-Satkhira 132 kV line-1 | 2020-07-12 19:36 | 2020-07-12 19:56 | 0:20 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Faridpur | Faridpur-Bheramara 132 kV line-2 | 2020-07-13 10:19 | 2020-07-13 10:40 | 0:21 | T | Tripped showing dist.& O/C relay | 409 | 143.15 | Power interruption
Goalpara | Goalpara-Khulna 225MW 132 kV line | 2020-07-20 08:47 | 2020-07-20 14:41 | 5:54 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Faridpur | Faridpur-Gopalganj 132 kV line-2 | 2020-07-23 11:33 | 2020-07-23 11:41 | 0:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bhandaria | Bhandaria-Barishal 132 kV line | 2020-07-30 14:17 | 2020-07-30 15:07 | 0:50 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 13:04 |  | Unserved Energy: |  | 462.15
HVDC Grid Circle :
Bottail | Bottail-Jhenidah 132 kV line-2 | 2020-07-02 09:59 | 2020-07-02 13:32 | 3:33 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bheramara | Bheramara-Bahrampur 400 kV line-1 | 2020-07-02 20:58 | 2020-07-02 21:21 | 0:23 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Jessore | Jessore-Benapole 132 kV line-2 | 2020-07-11 13:26 | 2020-07-11 13:54 | 0:28 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
Baghabari | Baghabari-Shahjadpur 132 kV line-1 & 2 | 2020-07-11 17:47 | 2020-07-11 18:48 | 1:01 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bharamara | Bharamara-Faridpur 132 kV line-1 | 2020-07-13 10:18 | 2020-07-14 02:27 | 16:09 | T | Tripped showing dist.& /OC relay | 0 | 0 | No interruption
Benapole | Benapole-Jessore 132 kV line-1 | 2020-07-17 09:45 | 2020-07-17 10:58 | 1:13 | T | Tripped showing main protcetion relay | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ghorashal 230 kV line-2 | 2020-07-19 08:12 | 2020-07-19 10:32 | 2:20 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Jhenidah | Jhenidah-Magura 132 kV line-2 | 2020-07-27 13:04 | 2020-07-27 13:34 | 0:30 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bharamara | Bharamara-Ishurdi 230 kV line-3 | 2020-07-27 17:03 | 2020-07-27 18:16 | 1:13 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 26:50 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Thaurgaon | Thakurgaon-Purbasadipur 132 kV line-1 | 2020-07-02 04:58 | 2020-07-02 05:23 | 0:25 | T | Tripped showing O/C. relay | 80 | 33.3333 | Power interruption
| Thakurgaon-Purbasadipur 132 kV line-2 | 2020-07-02 04:58 | 2020-07-02 05:30 | 0:32 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rangpur | Rangpur-Saidpur 132 kV line-2 | 2020-07-02 12:52 | 2020-07-02 16:07 | 3:15 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Naogaon | Naogaon-Niyamatpur 132 kV line | 2020-07-03 03:42 | 2020-07-03 04:05 | 0:23 | T | Tripped showing dist. relay | 42 | 16.1 | Power interruption
| Naogaon-Joypurhat 132 kV line | 2020-07-03 19:01 | 2020-07-03 19:24 | 0:23 | T | Tripped showing dist. relay | 25 | 9.5833 | Power interruption
Rampur | Rampur-Agrabad 132 kV line-1 | 2020-07-05 12:40 | 2020-07-05 13:03 | 0:23 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rangpur | Rangpur-Saidpur 132 kV line-2 | 2020-07-08 11:32 | 2020-07-08 11:53 | 0:21 | T | Tripped showing dist. relay | 295 | 103.25 | Power interruption
Sirajganj | Sirajganj-Baghabari 230 kV line-1 | 2020-07-08 15:20 | 2020-07-08 15:51 | 0:31 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Purbasadipur | Purbasadipur-Thaurgaon 132 kV line-2 | 2020-07-09 09:01 | 2020-07-09 10:22 | 1:21 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sirajganj | Sirajganj-Baghabari 230 kV line-1 | 2020-07-10 06:07 | 2020-07-10 09:36 | 3:29 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Barapukuria | Barapukuria-saidpur 132 kV line-1 | 2020-07-09 05:25 | 2020-07-09 05:34 | 0:09 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rangpur | Rangpur-Ranpur confidence P.P 132 kV line-1 | 2020-07-18 05:31 | 2020-07-20 05:26 | 47:55 | T | Tripped showing dist. relay | 0 | 0 | No interruption
C.nawabganj | C.nawabganj-Amnura 132 kV line-1 | 2020-07-19 17:22 | 2020-07-19 17:55 | 0:33 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rangpur | Rangpur-Saidpur 132 kV line-1 | 2020-07-26 11:02 | 2020-07-26 16:20 | 5:18 | T | Tripped showing dist.& O/C relay | 0 | 0 | No interruption
Barapukuria | Barapukuria-Saidpur 132 kV line-2 | 2020-07-27 00:45 | 2020-07-27 00:50 | 0:05 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Barapukuria-Saidpur 132 kV line-1 | 2020-07-27 00:45 | 2020-07-27 00:54 | 0:09 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Palashbari | Palashbari-Mohasthangarth 132 kV line-1 & 2 | 2020-07-27 00:45 | 2020-07-27 01:02 | 0:17 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Purbasadipur | Purbasadipur-Thaurgaon 132 kV line-2 | 2020-07-29 22:10 | 2020-07-29 23:03 | 0:53 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sherpur | Sherpur-Sirajganj 132 kV line-2 | 2020-07-31 14:15 | 2020-07-31 14:45 | 0:30 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 66:52 |  | Unserved Energy: |  | 162.2667
Others :
Maniknagar | Maniknagar-Bangabhaban 132 kV line-1 | 2020-07-06 17:31 | 2020-07-06 18:36 | 1:05 | T | Tripped showing main protection. relay | 0 | 0 | No interruption
|  |  | Total : | 1:05 |  |  |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 168:21 | Hours
T = Tripping | [7 empty] | Executive Engineer
E/O = Emergency Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/3 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:July 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kabirpur | 132/33 kV Transformers-T2 & T3 | 2020-07-03 07:03 | 2020-07-03 11:19 | 4:16 | S/O | Due to C/M work | 70 | 298.6667 | Power interruption
| 132/33 kV Transformer-T1 | 2020-07-03 09:57 | 2020-07-03 11:16 | 1:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T1 | 2020-07-04 09:18 | 2020-07-04 11:27 | 2:09 | S/O | Due to C/M work | 0 | 0 | No interruption
Saver | 132/33 kV Transformer-T1 | 2020-07-05 06:16 | 2020-07-05 09:03 | 2:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T2 | 2020-07-06 05:42 | 2020-07-06 07:38 | 1:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T2 | 2020-07-07 10:55 | 2020-07-07 11:58 | 1:03 | S/O | Due to maintenance work | 0 | 0 | No interruption
Tongi | 132/33 kV Transformers-T1 & T2 & 33 kV Bus | 2020-07-07 13:05 | 2020-07-07 14:50 | 1:45 | S/O | Due to isolator maintenance | 70 | 122.5 | Power interruption
Kabirpur | 132/33 kV Transformer-T2 | 2020-07-08 05:10 | 2020-07-08 05:10 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T01 | 2020-07-09 09:51 | 2020-07-09 19:40 | 9:49 | S/O | Due to D/W work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T3 | 2020-07-12 09:10 | 2020-07-12 11:28 | 2:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T3 | 2020-07-15 05:05 | 2020-07-15 07:18 | 2:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhaluka | 132/33 kV Transformer-T1 & 132 kV Bus-1 | 2020-07-15 08:15 | 2020-07-15 12:47 | 4:32 | S/O | Due to replacement By CB | 15 | 68 | Power interruption
Saver | 132/33 kV Transformer-T1 | 2020-07-17 06:01 | 2020-07-17 10:07 | 4:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 33 kV Bus | 2020-07-17 06:10 | 2020-07-17 08:25 | 2:15 | S/O | Due to PBS work | 50 | 112.5 | Power interruption
Mymensingh | 132/33 kV Transformer-T3 | 2020-07-17 07:18 | 2020-07-17 07:18 | 0:00 | S/O | Due to 33 kV Bus maintenance | 0 | 0 | No interruption
Dhamrai | 132/33 kV Transformer-T2 | 2020-07-17 08:27 | 2020-07-17 12:21 | 3:54 | S/O | Due to C/M work | 30 | 117 | Power interruption
| 132/33 kV Transformer-T1 | 2020-07-17 14:10 | 2020-07-17 16:28 | 2:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Saver | 132/33 kV Transformer-T2 | 2020-07-18 06:33 | 2020-07-18 10:25 | 3:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T3 | 2020-07-18 08:22 | 2020-07-18 12:20 | 3:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T1 | 2020-07-18 09:17 | 2020-07-18 12:01 | 2:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Saver | 132/33 kV Transformer-T3 | 2020-07-21 13:02 | 2020-07-21 16:42 | 3:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 33 kV Bus | 2020-07-23 07:05 | 2020-07-23 08:20 | 1:15 | S/O | Due to C/M work | 70 | 87.5 | Power interruption
Jamalpur | 132/33 kV Transformer-T2 | 2020-07-24 06:50 | 2020-07-24 08:17 | 1:27 | S/O | Due to PBS feeder maintenance | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T1 | 2020-07-25 06:04 | 2020-07-25 06:48 | 0:44 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-07-25 08:45 | 2020-07-27 17:02 | 56:17 | S/O | Due to changing work | 0 | 0 | No interruption
Saver | 33 kV Bus-A & Capacitor Bank | 2020-07-26 09:47 | 2020-07-26 10:12 | 0:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T4 & 33 kV Bus | 2020-07-27 06:05 | 2020-07-27 08:44 | 2:39 | S/O | Due to C/M work | 20 | 53 | Power interruption
Saver | 132/33 kV Transformer-T2 | 2020-07-28 06:07 | 2020-07-28 10:20 | 4:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaliakoir | 400/132 kV Transformer-T1 | 2020-07-29 06:15 | 2020-07-29 07:32 | 1:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T2 | 2020-07-29 07:12 | 2020-07-29 10:19 | 3:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Saver | 132/33 kV Transformer-T2 | 2020-07-29 09:34 | 2020-07-29 13:35 | 4:01 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 136:19 |  | Unserved Energy: |  | 859.1667
Dhaka (South) Grid Circle :
Hasnabad | 132 kV reserve Bus | 2020-07-05 09:50 | 2020-07-05 09:50 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T5 | 2020-07-05 09:56 | 2020-07-05 17:42 | 7:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Meghnaghat | 230 kV Bus -1 | 2020-07-07 07:45 | 2020-07-07 16:47 | 9:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | 132/33 kV Transformer-T2 | 2020-07-07 08:30 | 2020-07-07 08:30 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | 132/33 kV Transformer-T2 | 2020-07-07 11:34 | 2020-07-07 12:30 | 0:56 | S/O | Due to earth resistance measurement | 0 | 0 | No interruption
Hasnabad | 132/33 kV Transformer-T1 | 2020-07-08 09:38 | 2020-07-08 17:19 | 7:41 | S/O | Due to painting work | 0 | 0 | No interruption
| 230/132 kV Transformer-T1 | 2020-07-09 09:24 | 2020-07-09 13:55 | 4:31 | S/O | Due to D/W work | 0 | 0 | No interruption
| 230/132 kV Transformer-T1 | 2020-07-13 10:12 | 2020-07-13 16:31 | 6:19 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T5 | 2020-07-14 11:30 | 2020-07-14 18:31 | 7:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Sonargaon | 132/33 kV Transformer-T1 | 2020-07-14 08:30 | 2020-07-14 11:38 | 3:08 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-07-15 09:18 | 2020-07-15 10:48 | 1:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Agrabad | 132/33 kV Transformers-T1 |  | 2020-07-15 15:16 |  | S/O | After maintenance work | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 |  | 2020-07-15 15:56
Hasnabad | 230/132 kV Transformer-T2 | 2020-07-20 12:32 | 2020-07-20 16:42 | 4:10 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-07-21 07:36 | 2020-07-21 18:43 | 11:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Madanganj | 132/33 kV Transformer-T-1 |  | 2020-07-23 14:12 |  |  | After maintenance work | 0 | 0 | No interruption
Hasnabad | 230/132 kV Transformer-T03 | 2020-07-26 13:42 | 2020-07-26 20:45 | 7:03 |  | Due to maintenance work | 0 | 0 | No interruption
Rampura | 230/132 kV Transformer-T01 | 2020-07-27 11:15 | 2020-07-27 13:55 | 2:40 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 72:54 |  | Unserved Energy: |  | 0
Page: 2/3 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:July 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Chattogram Grid Circle :
Rangamati | 132/33 kV Transformer-T1 | 2020-07-08 10:06 | 2020-07-08 12:17 | 2:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahjibazar | 132/33 kV Transformer-T2 | 2020-07-10 08:46 | 2020-07-10 10:06 | 1:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Botail | 132/33 kV Transformer-T1 | 2020-07-16 07:05 | 2020-07-16 08:05 | 1:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Halishahar | 132 kV Bus | 2020-07-17 06:15 | 2020-07-17 09:04 | 2:49 | S/O | Due to C/M work | 45 | 126.75 | Power interruption
| 132/33 kV Transformer-T2 | 2020-07-18 14:19 | 2020-07-18 15:14 | 0:55 | S/O | Due to loop 33 kV loop changing work | 17 | 15.5833 | Power interruption
Hathazari | 132/33 kV Transformer-T2 | 2020-07-25 08:15 | 2020-07-25 10:16 | 2:01 | S/O | Due to temperature high | 0 | 0 | No interruption
Dohazari | 132/33 kV Transformer-T2 | 2020-07-26 09:28 | 2020-07-26 11:47 | 2:19 | S/O | Due to working of earthing system | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-07-26 11:51 | 2020-07-26 16:23 | 4:32 | S/O |  | 0 | 0 | No interruption
Hathazari | 132/33 kV Transformer-T1 | 2020-07-28 07:07 | 2020-07-28 11:08 | 4:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Chandraghona | 132/33 kV Transformer-T2 | 2020-07-29 07:02 | 2020-07-29 08:20 | 1:18 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 22:26 |  | Unserved Energy : |  | 142.3333
Cumilla Grid Circle :
Cumilla(S) | 132/33 kV Transformers-T1 & T2 | 2020-07-02 07:33 | 2020-07-02 08:54 | 1:21 | S/O | Due to 33 kV feeder maintenance | 0 | 0 | No interruption
Daudkandi | 132/33 kV Transformer-T1 | 2020-07-03 08:06 | 2020-07-03 09:58 | 1:52 | S/O | Due to C/M work | 0 | 0 | No interruption
B.Baria | 132/33 kV Transformer-T2 | 2020-07-06 10:10 | 2020-07-06 17:06 | 6:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Sylhet | 132/33 kV Transformer-T1 | 2020-07-07 05:44 | 2020-07-07 06:48 | 1:04 | S/O | Due to C/M work | 25 | 26.6667 | Power interruption
Fenchuganj | 230 kV CB#202 52 & 203-52 | 2020-07-18 10:30 | 2020-07-18 10:30 |  | S/O | Due to D/W work | 0 | 0 | No interruption
| 230/132 kV Transformer-AT-2 | 2020-07-21 10:02 | 2020-07-21 17:05 | 7:03 | S/O | Due to D/W work | 0 | 0 | No interruption
| 230/132 kV Transformer-T-01 |  | 2020-07-21 23:18 |  |  | New connection | 0 | 0 | No interruption
Daudkandi | 132/33 kV Transformer-T3 | 2020-07-23 18:25 | 2020-07-23 20:03 | 1:38 | S/O | Due to maintenance work | 0 | 0 | No interruption
Baroierhat | 132/33 kV Transformer-T1 | 2020-07-26 09:38 | 2020-07-26 12:08 | 2:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Sylhet | 132/33 kV Transformer-T4 | 2020-07-26 14:30 | 2020-07-26 17:03 | 2:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Bibiyana | 230/132 kV Transformer-T02 | 2020-07-28 09:35 | 2020-07-28 10:13 | 0:38 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-T01 | 2020-07-28 10:18 | 2020-07-28 10:53 | 0:35 | S/O | Due to C/M work | 0 | 0 | No interruption
B.Baria | 132/33 kV Transformer-T1 | 2020-07-28 10:08 | 2020-07-28 11:45 | 1:37 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2020-07-28 11:52 | 2020-07-28 12:54 | 1:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Sreemongal | 132/33 kV Transformers-T1 & T3 | 2020-07-29 08:56 | 2020-07-29 09:56 | 1:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-07-29 10:09 | 2020-07-29 10:25 | 0:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla (S) | 132/33 kV Transformer-T3 | 2020-07-29 14:53 | 2020-07-29 15:13 | 0:20 | S/O | Due to replacement work | 8 | 2.6667 | Power interruption
Shahjibazar | 132/33 kV Transformers-T4 | 2020-07-31 06:35 | 2020-07-31 09:00 | 2:25 | S/O | Due to C/M work | 25 | 60.4167 | Power interruption
| 132/33 kV Transformers-T6 | 2020-07-31 06:35 | 2020-07-31 12:26 | 5:51 | S/O |  | 0 | 0
Chowmuhani | 132/33 kV Transformer-T1 with 33 kV Bus | 2020-07-31 06:12 | 2020-07-31 08:34 | 2:22 | S/O | Due to C/M work | 60 | 142 | Power interruption
| 132/33 kV Transformer-T3 | 2020-07-31 09:17 | 2020-07-31 11:08 | 1:51 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 42:54 |  | Unserved Energy : |  | 231.75
Khulna Grid Circle :
Bagerhat | 132/33 kV Transformer-T1 | 2020-07-03 08:19 | 2020-07-03 10:06 | 1:47 | S/O | Due to high temperarure of 33 kV bushing | 0 | 0 | No interruption
Satkhira | 132/33 kV Transformers-T1 & T2 | 2020-07-09 07:07 | 2020-07-10 13:50 | 30:43 | S/O | Due to D/W work | 0 | 0 | No interruption
Bagerhat | 33 kV Bus section-3 | 2020-07-10 08:05 | 2020-07-10 11:34 | 3:29 | S/O | Due to C/M work | 28 | 97.5333 | Power interruption
Faridpur | 33 kV Bus section-4 | 2020-07-17 06:12 | 2020-07-17 08:25 | 2:13 | S/O | Due to PBS work | 0 | 0 | No interruption
Barisal(N) | 33 kV Bus | 2020-07-18 08:15 | 2020-07-18 18:01 | 9:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T3 |  | 2020-07-23 09:05 |  |  | After maintenance work | 0 | 0 | No interruption
Barisal | 132/33 kV Transformer-T1 | 2020-07-24 07:16 | 2020-07-24 11:45 | 4:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Noapara | 132 kV Bus-1 | 2020-07-28 07:42 | 2020-07-28 09:55 | 2:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Chuadanga | 132/33 kV Transformer-T2 | 2020-07-29 08:39 | 2020-07-29 20:03 | 11:24 | S/O | Due to CB maintenance at 33 kV side | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-07-29 20:40 | 2020-07-29 21:55 | 1:15 | S/O | Due to 33 kV insulator removing | 0 | 0 | No interruption
Bhandaria | 132/33 kV Transformer-T2 | 2020-07-30 07:10 | 2020-07-30 13:37 | 6:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Norail | 132/33 kV Transformer-T2 | 2020-07-30 13:41 | 2020-07-30 13:59 | 0:18 | S/O | Due to high temperature at connector of 33 kV(Y-phase) CT | 0 | 0 | No interruption
|  |  | Total : | 74:04 |  | Unserved Energy : |  | 97.5333
HVDC Grid Circle :
Kustia | 132/33 kV Transformer-T2 | 2020-07-03 08:03 | 2020-07-03 16:19 | 8:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Ishurdi | 132 kV Bus-2 | 2020-07-11 15:10 | 2020-07-11 16:50 | 1:40 | S/O | Due to chaning work | 0 | 0 | No interruption
Shahjibazar | 132/33 kV Transformer-T4 | 2020-07-13 10:40 | 2020-07-13 15:14 | 4:34 | S/O | Due to D/W work | 0 | 0 | No interruption
Ishurdi | 132 kV Bus-1 | 2020-07-13 08:15 | 2020-07-13 11:50 | 3:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Jashore | 132/33 kV Transformer-T3 | 2020-07-20 07:21 | 2020-07-20 09:11 | 1:50 | S/O | Due to D/W work | 0 | 0 | No interruption
Ishurdi | 132/33 kV Transformer-T2 | 2020-07-20 10:11 | 2020-07-20 13:42 | 3:31 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV Bus-1 | 2020-07-23 08:20 | 2020-07-23 10:49 | 2:29 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-07-30 10:27 | 2020-07-30 12:14 | 1:47 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 27:42 |  | Unserved Energy : |  | 0
Page: 3/3 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:July 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle:
Niyamatpur | 132/33 kV Transformer-T3 | 2020-07-02 12:02 | 2020-07-23 15:44 | 507:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformer-T2 | 2020-07-03 07:10 | 2020-07-03 17:24 | 10:14 | S/O | Due to changing work | 5 | 51.1667 | Power interruption
| 132/33 kV Transformer-T3 | 2020-07-04 07:02 | 2020-07-04 18:03 | 11:01 | S/O | Due to C/M work | 25 | 275.4167 | Power interruption
Baghabari | 132 kV Bus-1 | 2020-07-06 10:35 |  |  |  |  | 0 | 0 | No interruption
Mohastangar | 132/33 kV Transformer-T1 | 2020-07-12 10:52 | 2020-07-12 14:24 | 0:35 | S/O | Due to PBS work | 10 | 5.8333 | Power interruption
Natore | 132/33 kV Transformer-T1 | 2020-07-14 11:34 | 2020-07-14 17:41 | 6:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer-T1 | 2020-07-16 10:13 | 2020-07-16 16:43 | 6:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV Transformer-T2 | 2020-07-20 11:25 | 2020-07-20 17:04 | 5:39 | S/O | Due to C/M work | 0 | 0 | No interruption
Niyamatpur | 132/33 kV Transformer-T2 | 2020-07-24 11:12 | 2020-07-26 18:17 | 55:05 | S/O | Due to replacement work | 0 | 0 | No interruption
Natore | 132 kV Bus | 2020-07-26 05:28 | 2020-07-26 10:10 | 4:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformer-T3 | 2020-07-27 06:41 | 2020-07-27 07:53 | 1:12 | S/O | Due to C/M work by NESCO | 40 | 48 | Power interruption
Rangpur | 132/33 kV Transformer-T2 |  | 2020-07-27 16:40 |  |  | After maintenance work | 0 | 0 | No interruption
Naogaon | 132 kV main Bus | 2020-07-30 06:20 | 2020-07-30 10:05 | 3:45 | S/O | Due to C/M work | 70 | 262.5 | Power interruption
|  |  | Total : | 612:32 |  | Unserved Energy : |  | 642.9167
Others :
Ullon | 132/33 kV Transformer-T1 | 2020-07-10 10:18 | 2020-07-10 13:58 | 3:40 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total | 3:40 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 379:59 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/3 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:July 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar | Aminbazar-Hasnabad 230 kV line-2 | 2020-07-04 07:04 | 2020-07-04 10:09 | 3:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Aminbazar 132 kV line-1 | 2020-07-05 07:52 | 2020-07-05 18:13 | 10:21 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV line-2 | 2020-07-06 08:14 | 2020-07-06 16:16 | 8:02 | S/O | Due to D/W work | 0 | 0 | No interruption
| Aminbazar-Kallyanpur 132 kV line-1 | 2020-07-07 08:25 | 2020-07-07 18:33 | 10:08 | S/O | Due to D/W work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh line-1 | 2020-07-07 08:27 | 2020-07-07 13:00 | 4:33 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-2 | 2020-07-07 10:16 | 2020-07-07 13:54 | 3:38 | S/O | Due to C/M work | 0 | 0 | No interruption
| Mymensingh-Netrakona 132 kV line-1 | 2020-07-07 13:36 | 2020-07-07 16:31 | 2:55 | S/O | Due to C/M work | 0 | 0 | No interruption
| Mymensingh-Jamalpur 132 kV line-2 | 2020-07-07 13:10 | 2020-07-07 16:49 | 3:39 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV line-2 | 2020-07-08 09:26 | 2020-07-08 22:12 | 12:46 | S/O | Due to D/W work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 3rd phase 132 kV line | 2020-07-12 08:25 | 2020-07-12 16:50 | 8:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj P/S 132 kV line-1 | 2020-07-12 13:23 | 2020-07-12 18:48 | 5:25 | S/O | Due to maintenance work | 0 | 0 | No interruption
| Aminbazar-Manikganj P/S 132 kV line-2 | 2020-07-13 10:11 | 2020-07-13 13:48 | 3:37 | S/O | Due to D/W work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV line-2 | 2020-07-14 05:10 | 2020-07-14 07:50 | 2:40 | S/O | Due to C/M work | 0 | 0 | No interruption
| Kabirpur-Tongi 132 kV line-1 | 2020-07-15 06:28 | 2020-07-15 08:28 | 2:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-1 | 2020-07-18 09:34 | 2020-07-18 13:25 | 3:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | Savar-Aminbazar (Manikganj PP) 132 kV line-2 | 2020-07-19 05:56 | 2020-07-19 10:08 | 4:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV line-2 | 2020-07-21 06:35 | 2020-07-21 09:26 | 2:51 | S/O | Due to C/M work | 0 | 0 | No interruption
| Kabirpur-Kaliakoir 132 kV line | 2020-07-22 06:19 | 2020-07-22 08:39 | 2:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-2 | 2020-07-27 07:05 | 2020-07-27 10:51 | 3:46 | S/O | Due to proection work | 0 | 0 | No interruption
| Mymensingh-Jamalpur 132 kV line-1 | 2020-07-27 10:58 | 2020-07-27 12:12 | 1:14 | S/O | Due to C/M work | 0 | 0 | No interruption
| Mymensingh-Kishoreganj 132 kV line-2 | 2020-07-27 12:16 | 2020-07-27 12:54 | 0:38 | S/O | Due to C/M work | 0 | 0 | No interruption
| Mymensingh-Kishoreganj 132 kV line-1 | 2020-07-27 12:58 | 2020-07-27 13:58 | 1:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Tangail 132 kV line-1 | 2020-07-28 10:20 | 2020-07-28 12:07 | 1:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Sherpur | Sherpur-united Mymensingh Power 132 kV line-1 | 2020-07-30 14:34 | 2020-07-30 16:21 | 1:47 | S/O | Due to relay test | 0 | 0 | No interruption
|  |  | Total : | 104:40 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Bhulta | Bhulta-Haripur 230 kV line-1 | 2020-07-02 14:45 | 2020-07-02 16:16 | 1:31 | S/O | Due to kite removing | 0 | 0 | No interruption
Aurahati | Aurahati-Kamrangirchar 132 kV lne | 2020-07-05 07:19 | 2020-07-05 07:19 |  | S/O | Due to maintenance work by DPDC | 0 | 0 | No interruption
Meghanghat | Meghanghat-Shyampur 230 kV line-2 | 2020-07-05 08:06 | 2020-07-05 17:24 | 9:18 | S/O | Due to D/W work | 0 | 0 | No interruption
Rampura | Rampura-Moghbazar 132 kV line-1 | 2020-07-05 16:44 | 2020-07-06 05:35 | 12:51 | S/O | Due to replacement work | 0 | 0 | No interruption
Meghna | Meghna-Shyampur 230 kV line-2 | 2020-07-06 09:12 | 2020-07-06 16:50 | 7:38 | S/O | Due to D/W work | 0 | 0 | No interruption
| Meghnaghat-Shyampur 230 kV line-1 | 2020-07-08 08:12 | 2020-07-08 15:38 | 7:26 | S/O | Due to C/M work | 0 | 0 | No interruption
| Meghna-Shyampur 230 kV line-1 | 2020-07-09 08:50 | 2020-07-09 15:38 | 6:48 | S/O | Due to D/W work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kVline-1 & 2 | 2020-07-10 07:54 | 2020-07-10 07:54 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Meghna | Meghna-Haripur 230 kV line-1 | 2020-07-12 09:10 | 2020-07-12 14:33 | 5:23 | S/O | Due to high temperature | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Siddhirganj GT(1& 2) 132 kV line | 2020-07-12 11:42 | 2020-07-12 11:50 | 0:08 | S/O | Due to auxiliary supply checking | 0 | 0 | No interruption
Sonargaon | Sonargaon-Daudkandi 132 kV line-1 | 2020-07-14 12:05 | 2020-07-14 13:38 | 1:33 | S/O | Due to C/M work | 0 | 0 | No interruption
| Sonargaon-Daudkandi 132 kV line-2 | 2020-07-14 13:41 | 2020-07-14 15:27 | 1:46 | S/O | Due to C/M work | 0 | 0 | No interruption
| Sonargaon-Haripur 132 kV line-1 | 2020-07-14 15:32 | 2020-07-14 16:14 | 0:42 | S/O | Due to CB test | 0 | 0 | No interruption
| Sonargaon-Meghnaghat IEL 132 kV line-1 | 2020-07-15 11:02 | 2020-07-15 11:31 | 0:29 | S/O | Due to D/W work | 0 | 0 | No interruption
| Sonargaon-Haripur 132 kV line-2 | 2020-07-15 11:58 | 2020-07-15 13:34 | 1:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Sonargaon P/S | Sonargaon P/S-Sonargaon S/S 132 kV line | 2020-07-26 12:52 | 2020-07-26 17:23 | 4:31 | S/O | Due to protection work | 0 | 0 | No interruption
|  |  | Total : | 61:40 |  | Unserved Energy: |  | 0
Page: 2/3 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:July 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Chattogram Grid Circle :
Hathazari | Hathazari-Madunaghat-Khulshi 132 kV line | 2020-07-04 08:28 | 2020-07-04 15:35 | 7:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'xbazar 132 kV line-2 | 2020-07-06 08:05 | 2020-07-06 17:50 | 9:45 | S/O | Due to D/W work | 0 | 0 | No interruption
| Dohazari-Cox'xbazar 132 kV line-2 | 2020-07-09 09:07 | 2020-07-09 19:48 | 10:41 | S/O | Due to D/W work | 0 | 0 | No interruption
Rangamati | Rangamati-Chandraghona 132 kV line-1 | 2020-07-08 10:15 | 2020-07-08 11:35 | 1:20 | S/O | Due to D/W work | 0 | 0 | No interruption
| Rangamati-Khagrachari 132 kV line-2 | 2020-07-08 11:38 | 2020-07-08 12:20 | 0:42 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'xbazar 132 kV line-1 | 2020-07-10 06:56 | 2020-07-10 16:26 | 9:30 | S/O | Due to D/W work | 0 | 0 | No interruption
| Dohazari-Cox'xbazar 132 kV line-1 | 2020-07-11 06:53 | 2020-07-11 18:23 | 11:30 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV line-2 | 2020-07-11 10:24 | 2020-07-11 10:57 | 0:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'xbazar 132 kV line-1 | 2020-07-12 08:18 | 2020-07-12 19:33 | 11:15 | S/O | Due to D/W work | 0 | 0 | No interruption
| Dohazari-Cox'xbazar 132 kV line-1 | 2020-07-13 08:18 | 2020-07-13 15:52 | 7:34 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari S/S | Hathazari S/S-Hathazari P/S 132 kV line | 2020-07-15 10:49 | 2020-07-15 13:00 | 2:11 | S/O | Due to maintenance work | 0 | 0 | No interruption
Kulshi | Kulshi-Baraulia 132 kV line-2 | 2020-07-15 11:15 | 2020-07-15 14:06 | 2:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'xbazar 132 kV line-2 | 2020-07-17 06:49 | 2020-07-17 18:20 | 11:31 | S/O | Due to D/W work | 0 | 0 | No interruption
| Dohazari-Cox'xbazar 132 kV line-2 | 2020-07-18 09:22 | 2020-07-18 18:57 | 9:35 | S/O | Due to D/W work | 0 | 0 | No interruption
| Dohazari-Cox'xbazar 132 kV line-2 | 2020-07-19 12:23 | 2020-07-19 13:39 | 1:16 | S/O | Due to D/W work | 0 | 0 | No interruption
| Dohazari-Cox'xbazar 132 kV line-2 | 2020-07-19 18:13 | 2020-07-19 18:37 | 0:24 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-Raozan 230 kV line-1 | 2020-07-20 09:10 | 2020-07-20 12:27 | 3:17 | S/O | Due to C/M work | 0 | 0 | No interruption
| Hathazari-Baroierhat 132 kV line-2 |  | 2020-07-20 15:04 |  |  | After maintenance work | 0 | 0 | No interruption
|  |  | Total : | 101:02 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Ashuganj | Ashuganj-Sirajganj 230 kV line-2 | 2020-07-08 08:19 | 2020-07-08 19:32 | 11:13 | S/O | Due to changing work | 0 | 0 | No interruption
B.Baria | B.Baria-Shahjibazar 132 kV line-2 | 2020-07-12 09:42 | 2020-07-12 14:23 | 4:41 | S/O | Due to C/M work | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Chowmuhani P/P 132 kV line | 2020-07-14 08:30 | 2020-07-14 12:10 | 3:40 | S/O | Due to C/M work | 0 | 0 | No interruption
| Chowmuhani-Chowmuhani P/P 132 kV line | 2020-07-16 07:18 | 2020-07-16 15:30 | 8:12 | S/O | Due to D/W work | 0 | 0 | No interruption
| Chowmuhani-Chowmuhani P/P 132 kV line | 2020-07-17 06:47 | 2020-07-17 15:04 |  | S/O | Due to D/W work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-BSRM 230 kV line-1 | 2020-07-17 08:25 | 2020-07-17 12:08 | 3:43 | S/O | Due to D/W work | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Chowmuhani P/P 132 kV line | 2020-07-18 06:59 | 2020-07-18 06:59 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-2 | 2020-07-18 06:23 | 2020-07-18 07:44 | 1:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-B.Baria 132 kV line | 2020-07-26 10:07 | 2020-07-26 12:22 | 2:15 | S/O | Due to C/M work | 0 | 0 | No interruption
B.Baria | B.Baria-Ashuganj 132 kV line-1 | 2020-07-30 09:42 | 2020-07-30 11:24 | 1:42 | S/O | Due to C/M work | 0 | 0 | No interruption
| B.Baria-Ashuganj 132 kV line-2 | 2020-07-30 11:25 | 2020-07-30 12:01 | 0:36 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 37:23 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Barishal(N) | Barishal(N)-Barishal(S) 132 kV line-2 | 2020-07-02 06:06 | 2020-07-02 17:02 | 10:56 | S/O | Due to replacement work | 0 | 0 | No interruption
Khulna(C) | Khulna©-KPCL-2 132 kV line | 2020-07-11 07:02 | 2020-07-11 09:48 | 2:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Orion P/P 132 kV line-1 | 2020-07-14 12:28 | 2020-07-14 13:19 | 0:51 | S/O | Due to C/M work | 0 | 0
| Bagerhat-Mongla 132 kV line | 2020-07-25 08:03 | 2020-07-25 13:57 | 5:54 | S/O | Due to D/W work | 9 | 53.1 | Power interruption
Gopalganj | Gopalganj-Madaripur 132 kV line-2 | 2020-07-28 06:47 | 2020-07-28 09:38 | 2:51 | S/O | Due to temperature high | 0 | 0 | No interruption
|  |  | Total : | 23:18 |  | Unserved Energy: |  | 53.1
HVDC Grid Circle :
Ishurdi | Ishurdi-Baghabari 132 kV line | 2020-07-03 09:30 | 2020-07-03 17:00 | 0:23 | S/O | Due to D/W work | 0 | 0 | No interruption
Shahjadpur | Shahjadpur-Baghabari 132 kV line-1 | 2020-07-03 09:40 | 2020-07-03 16:33 | 6:53 | S/O | Due to D/W work | 0 | 0 | No interruption
Bheramara | Bheramara-Bherampur 400 kV ine-2 | 2020-07-04 10:47 | 2020-07-04 16:51 | 6:04 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bheramara-Faridpur 132 kV line-2 | 2020-07-08 13:12 | 2020-07-08 13:54 | 0:42 | S/O | Due to removing kite | 0 | 0 | No interruption
Sirajganj | Sirajganj -Baghabari 230 kV ine-2 | 2020-07-08 15:10 | 2020-07-08 17:01 | 1:51 | S/O | Due to testing work | 0 | 0 | No interruption
Bheramara | Bheramara-Faridpur 132 kV line-1 | 2020-07-12 10:12 | 2020-07-12 11:02 | 0:50 | S/O | Due to removing kite | 0 | 0 | No interruption
Baghabari | Baghabari-Sirajganj 230 kV line-2 | 2020-07-19 08:36 | 2020-07-19 17:46 | 9:10 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 25:53 |  | Unserved Energy: |  | 0
Page: 3/3 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:July 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle :
Rangpur | Rangpur-Saidpur 132 kV line-1 | 2020-07-01 07:20 | 2020-07-01 07:20 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Palashbari | Palashbari-Mohastanghor 132 kV line-1 | 2020-07-03 08:09 | 2020-07-03 09:12 | 1:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangpur | Rangpur-Rangpur confidence power 132 kV line | 2020-07-10 08:50 | 2020-07-10 13:58 | 5:08 | S/O | Due to D/W work | 0 | 0 | No interruption
Purbasadipur | Purbasadipur-Thaurgaon 132 kV line-1 | 2020-07-20 10:20 | 2020-07-20 14:02 | 3:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Palashbari | Palashbari-Mohastanghor 132 kV line-2 | 2020-07-23 14:29 | 2020-07-23 14:43 | 0:14 | S/O | Due to removing kite | 0 | 0 | No interruption
Rangpur | Rangpur-Saidpur 132 kV line-2 |  | 2020-07-28 15:15 |  |  | After maintenance work | 0 | 0 | No interruption
|  |  | Total : | 10:07 |  | Unserved Energy: |  | 0
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 302:23 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:July' 2020
| Area | Previous Month (June 2020) |  |  |  | Current Month (July 2020)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 20 | 7 | 66 | 93 | 11 | 5 | 55 | 71
2 | Dhaka (South) Grid Circle. | 17 | 8 | 31 | 56 | 13 | 1 | 31 | 45
3 | Chattogram Grid Circle. | 13 | 4 | 22 | 39 | 8 | 7 | 28 | 43
4 | Cumilla Grid Circle. | 50 | 9 | 23 | 82 | 28 | 9 | 31 | 68
5 | Khulna Grid Circle. | 15 | 9 | 27 | 51 | 23 | 8 | 16 | 47
6 | Bheramara HVDC Grid Circle | 26 | 4 | 21 | 51 | 11 | 4 | 15 | 30
7 | Bogura Grid Circle. | 5 | 15 | 21 | 41 | 23 | 15 | 16 | 54
8 | Others | 6 | 3 | 1 | 10 | 1 |  | 1 | 2
9 | Total | 152 | 59 | 212 | 423 | 118 | 49 | 193 | 360
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:July' 2020
| Area | Previous Month (June 2020) |  |  |  | Current Month (July 2020)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 636.07 | 296.13 | 309.7 | 1241.9 | 118.5 | 163.83 | 859.17 | 1141.5
2 | Dhaka (South) Grid Circle. | 313.12 | 112.5 | 7.25 | 432.87 | 199.5 |  |  | 199.5
3 | Chattogram Grid Circle. | 64.33 | 119.25 | 208.17 | 391.75 | 258.9 | 171 | 142.3333 | 572.2333
4 | Cumilla Grid Circle. | 541.6 |  | 209.75 | 751.35 | 106.43 | 80 | 231.75 | 418.18
5 | Khulna Grid Circle. | 21.17 | 323.92 | 26.48 | 371.57 | 837 | 120.42 | 150.63 | 1108.05
6 | Bheramara HVDC Grid Circle | 482.88 | 80.8 | 103.6 | 667.28 | 6 | 74.12 |  | 80.12
7 | Bogura Grid Circle. | 38.63 | 531.95 | 2248.12 | 2818.7 | 281.19 | 191.83 | 642.92 | 1115.94
8 | Others | Energy unserved ( MWH ) due to T: 14.3; Energy unserved ( MWH ) due to Total: 14.3; Energy unserved ( MWH ) due to Total: 0
9 | Total | 2112.1 | 1464.55 | 3113.07 | 6689.72 | 1807.52 | 801.2 | 2026.8033 | 4635.5233
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:July' 2020
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 6 | 7 | 13 | 2 | 2 | 9 | 1131.75
2 | Dhaka (South) | 5031.6 | 1 |  | 1 |  |  | 1 | 199.5
3 | Chattogram | 2042 | 6 | 2 | 8 | 1 | 1 | 6 | 568.23
4 | Khulna | 2434 | 11 | 1 | 12 | 4 | 2 | 6 | 592.8
5 | Bheramara (HVDC) | 5913.3 | 3 |  | 3 | 1 | 1 | 1 | 80.12
6 | Bogura | 3145.6 | 6 | 4 | 11 | 2 | 2 | 7 | 953.67
7 | Cumilla | 2981 | 5 | 4 | 9 | 3 | 1 | 5 | 372.68
8 | Others | -
| Total | 30349.1 | [6 empty] | 3898.75
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.98%
3 | Chattogram | 99.88%
4 | Khulna | 99.9%
5 | Bheramara (HVDC) | 99.94% | [6 empty] | Executive Engineer
6 | Bogura | 99.74% | [6 empty] | Information Management Division
7 | Cumilla | 99.8% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:July' 2020
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 1 |  | 1 | 1 |  |  | 9.75
2 | Dhaka (South) | 990.29 |  | - | - | - | - | - | - | -
3 | Chattogram | 917 | - | 1 |  | 1 | 1 |  |  | 4
4 | Khulna | 1238.4 | - | 2 | 1 | 3 | 1 | 1 | 1 | 515.25
5 | Bheramara (HVDC) | 1324 | 501 | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | - | 4 | - | 4 | 4 | - | - | 162.27
7 | Cumilla | 1648.16 | - | 1 |  | 1 | 1 |  |  | 45.5
7 | Others | - |  | - | - | - | - | - | - | -
| Total | 10175.6215 | 501 | [6 empty] | 736.77
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 99.99%
4 | Khulna | 99.97%
5 | Bheramara (HVDC) | 99.76% | [7 empty] | Executive Engineer
6 | Bogura | 100% | [7 empty] | Information Management Division
7 | Cumilla | 99.91% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:July' 2020
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2020-07-18 | 15 | - | 2 | 3hour 54 min | - | - | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:July' 2020
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Kishorganj | 1 | 0:32 | 90 | 48 | Due to tripping of 132/33 kV Transformers-T1 & T2
Manikganj |  | 1:34 | 5 | 7.8333 | Due to red-hot maintenance of 132/33 kV Transformer T2
Mymensingh | 1 | 0:09 | 55 | 8.25 | Due to tripping of 132/33 kV Transformers-T1 & T2
Savar | 1 | 0:04 | 100 | 6.6667 | Due to tripping of 33 kV feeder fault
Kishorganj | 1 | 0:50 | 55 | 45.8333
Tangail | 1 | 1:36 | 39 | 156 | Due to red-hot maintenance of 132/33 kV Transformer T3
Sherpur | 1 | 0:13 | 45 | 9.75 | Due to tripping of Sherpur -Mymensingh P/S 132 kV line-1 & 2
Kabirpur | 1 | 4:16 | 70 | 298.6667 | Due to S/D of132/33 kV Transformers-T1 & T3
Tongi | 1 | 1:45 | 70 | 122.5 | Due to S/D of132/33 kV Transformers-T1 & T2 & 33 kV bus
Bhaluka | 1 | 4:32 | 15 | 68 | Due to S/D of132/33 kV Transformers-T1 & 132 kV Bus-1
Kabirpur | 1 | 2:15 | 50 | 112.5 | Due to S/D of 33 kV Bus
Dhamrai | 1 | 3:54 | 30 | 117 | Due to S/D of 132/33 kV Transformer-T2
Mymensingh | 1 | 1:27 | 70 | 87.5 | Due to S/D of 33 kV Bus
Tangail | 1 | 2:39 | 20 | 53 | Due to S/D of132/33 kV Transformer-T4 & 33 kV Bus
Madanganj | 1 | 9:30 | 21 | 199.5 | Due to S/D of 132/33 kV Transformer-T1
Hathazari |  | 5:20 | 35 | 186.6667 | Due to tripping of 132/33 kV Transformer-T1
Khulshi |  | 1:29 | 50 | 74.1667 | Due to red-hot maintenance of 132/33 kV Transformer T1
Dohazari | 1 | 3:29 | 20 | 65.8333 | Due to tripping of 132/33 kV Transformer-T1
Khulshi | 1 | 1:06 | 25 | 27.5 | Due to red-hot maintenance of 132/33 kV Transformer T1
Halishahar | 2 | 0:08 | 18 | 2.4 | Due to tripping of 33 kV feeder fault
|  | 1:20 | 52 | 69.3333 | Due to red-hot maintenance of 132/33 kV Transformer T1 & T3
Hathazari | 1 | 0:10 | 24 | 4 | Due to tripping of Hathazari-Baroierhat 132 kV line-2
Halishahar | 2 | 2:49 | 45 | 126.75 | Due to S/D of 132 kV Bus
|  | 0:55 | 17 | 15.5833 | Due to S/D of 132/33 kV Transformer-T2
Chowmuhani | 2 | 1:15 | 40 | 50 | Due to red-hot maintenance of 132/33 kV Transformer T1
|  | 2:00 | 10 | 20 | Due to red-hot maintenance of 132/33 kV Transformer T3
Sreemongal | 1 | 1:00 | 10 | 10 | Due to red-hot maintenance of 132/33 kV Transformers T2 & T3
Ramganj |  | 0:32 | 82 | 43.7333 | Due to tripping of 132/33 kV Transformers-T1 & T2
Chowmuhani | 1 | 0:06 | 172 | 17.2 | Due to tripping of 132/33 kV Transformers-T1 & T3
Fenchuganj | 1 | 0:13 | 210 | 45.5 | Due to tripping of Fenchuganj-Sylhet 132 kV line
Sylhet |  | 1:04 | 25 | 26.6667 | Due to S/D of 132/33 kV Transformer T1
Cumilla (S) |  | 0:20 | 8 | 2.6667 | Due to S/D of 132/33 kV Transformer T3
Shahjibazar |  | 2:25 | 25 | 60.4167 | Due to S/D of 132/33 kV Transformer T4
Chowmuhani |  | 2:22 | 60 | 142 | Due to S/D of 132/33 kV Transformer T1
Faridpur |  | 0:25 | 160 | 66.6667 | Due to tripping of 132/33 kV Transformers-T1 & T2
|  | 0:29 | 60 | 29 | Due to red-hot maintenance of 132/33 kV Transformer T2
Satkhira |  | 3:18 | 10 | 33 | Due to Oil leakage of of 132/33 kV Transformer T2
Bagerhat |  | 1:31 | 15 | 22.75 | Due to red-hot maintenance of 132/33 kV Transformer T1
Chuadanga |  | 1:47 | 20 | 35.6667
Patuakhali |  | 0:43 | 70 | 50.1667 | Due to tripping of 132/33 kV Transformer-T1
Barisal(S) |  | 0:10 | 64 | 10.6667 | Due to tripping of 132/33 kV Transformers-T1 & T2
Bagerhat |  | 0:26 | 17 | 7.3667
Gopalganj(O) |  | 0:39 | 50 | 32.5 | Due to tripping of 132/33 kV Transformer-T2
Chuadanga | 2 | 1:41 | 29 | 48.8167 | Due to tripping of 132/33 kV Transformer-T1
|  | 1:59 | 80 | 158.6667 | Due to tripping of 132/33 kV Transformer-T2
Gopalganj(N) | ! | 0:44 | 435 | 319 | Due to tripping of Gopalganj(N)-Gopalganj (S) 132 kV line
Faridpur | ! | 0:21 | 409 | 143.15 | Due to tripping of Faridpur-Bheramara 132 kV line
Bagerhat | 2 | 3:29 | 28 | 97.5333 | Due to S/D of 33 kV Bus
|  | 5:54 | 9 | 53.1 | Due to S/D of Bagerhat-Mongla 132 kV line
Ishurdi | ! | 0:36 | 27 | 16.2 | Due to red-hot maintenance of 132/33 kV Transformer T1
Bottail | ! | 2:19 | 25 | 57.9167 | Due to red-hot maintenance of 132/33 kV Transformer T1
Ishurdi | ! | 0:20 | 18 | 6 | Due to tripping of 132/33 kV Transformer-T3
Kurigram |  | 0:46 | 45 | 34.5 | Due to red-hot maintenance of 132 kV main Bus
Barapukuria |  | 0:21 | 35 | 12.25 | Due to tripping of 132/33 kV Transformer-T6
Purbasadipur |  | 0:58 | 30 | 29 | Due to red-hot maintenance of 132/33 kV Transformer T1
Bogura | 2 | 2:18 | 30 | 69 | Due to red-hot maintenance of 132/33 kV Transformer T3
|  | 1:29 | 40 | 59.3333 | Due to red-hot maintenance of 132/33 kV Transformer T1
Barapukuria |  | 0:10 | 640 | 106.6667 | Due to tripping of 230/132 kV Transformer-T01
Thaurgaon |  | 0:25 | 80 | 33.3333 | Due to tripping of Thakurgaon-Purbasadipur 132 kV line-1 & 2
Naogaon | 2 | 0:23 | 42 | 16.1 | Due to tripping of Naogaon-Niamatpur 132 kV line
|  | 0:23 | 25 | 9.5833 | Due to tripping of Naogaon-Joypurhat 132 kV line
Rangpur | 1 | 0:21 | 295 | 103.25 | Due to tripping of Rangpur-Saidpur 132 kV line
Rajshahi |  | 10:14 | 5 | 51.1667 | Due to S/D of 132/33 kV Transformer T2
Rajshahi |  | 11:01 | 25 | 275.4167 | Due to S/D of 132/33 kV Transformer T3
Mohastangar |  | 0:35 | 10 | 5.8333 | Due to S/D of 132/33 kV Transformer T1
Rajshahi |  | 1:12 | 40 | 48 | Due to S/D of 132/33 kV Transformer T3
Naogaon |  | 3:45 | 70 | 262.5 | Due to S/D of 132 kV Bus
| Total Unserved energy : |  |  | 4635.5167 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:July'2020
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 138 | 9 | 2020-07-01 | 14:00
2 | Munsiganj | 128 | 15 | 2020-07-01 | 22:00
3 | Sonargaon | 90 | 28 | 2020-07-01 | 21:00
4 | Shyampur | 204 | 4 | 2020-07-01 | 11:00
5 | Bhulta | 214 | 26 | 2020-07-01 | 0:00
6 | Madanganj | 69 | 9 | 2020-07-01 | 21:00
7 | Shitalakhya | 127 | 16 | 2020-07-01 | 11:00
8 | Rahim steel | 28 | 16 | 2020-07-01 | 9:00
9 | Matuail | 90 | 17 | 2020-07-01 | 10:00
10 | Ghorasal | 89 | 23 | 2020-07-01 | 21:00
11 | Narsingdi | 170 | 18 | 2020-07-01 | 22:00
12 | Haripur (SBU) | 105 | 1 | 2020-07-01 | 12:00
13 | Ullon | 70 | 12 | 2020-07-01 | 14:00
14 | Hasnabad | 205 | 1 | 2020-07-01 | 21:00
15 | Magbazar | 135 | 11 | 2020-07-01 | 3:00
16 | Maniknagar | 112 | 2 | 2020-07-01 | 15:00
17 | Bangabhaban | 32 | 5 | 2020-07-01 | 11:00
18 | Narinda | 96 | 1 | 2020-07-01 | 12:00
19 | Dhanmondi | 188 | 26 | 2020-07-01 | 12:00
20 | Lalbag | 133 | 24 | 2020-07-01 | 18:30
21 | Madartek | 72 | 3 | 2020-07-01 | 23:00
22 | Dhaka University | - | - | - | -
23 | Fatullah | 29 | 16 | 2020-07-01 | 12:00
24 | Mirpur | 106 | 26 | 2020-07-01 | 19:00
25 | Kalyanpur | 98 | 4 | 2020-07-01 | 12:00
26 | Gulshan | 132 | 2 | 2020-07-01 | 13:00
27 | Uttara | 110 | 4 | 2020-07-01 | 13:00
28 | Uttara(new) | 73 | 4 | 2020-07-01 | 12:00
29 | Kamrangirchar | 91 | 8 | 2020-07-01 | 13:00
30 | Savar | 139 | 2 | 2020-07-01 | 14:00
31 | Bhasantec | 168 | 25 | 2020-07-01 | 19:30
32 | Agargaon | 144 | 4 | 2020-07-01 | 13:00
33 | Satmosjid | 103 | 1 | 2020-07-01 | 14:00
34 | Tongi | 138 | 27 | 2020-07-01 | 11:00
35 | Kabirpur | 233 | 1 | 2020-07-01 | 12:00
36 | Basundhara | 226 | 4 | 2020-07-01 | 15:00
37 | Manikganj | 125 | 4 | 2020-07-01 | 12:00
38 | Joydevpur | 187 | 26 | 2020-07-01 | 21:00
39 | New Tongi | 173 | 4 | 2020-07-01 | 20:00
40 | Kodda | 228 | 14 | 2020-07-01 | 16:00
41 | Dhamrai | 102 | 19 | 2020-07-01 | 20:00
42 | Rajendrapur | 100 | 8 | 2020-07-01 | 19:30
43 | Valuka | 118 | 19 | 2020-07-01 | 16:00
44 | Tangail | 209 | 2 | 2020-07-01 | 21:00
45 | Mymensing | 230 | 8 | 2020-07-01 | 20:00
46 | Kishorganj | 225 | 4 | 2020-07-01 | 19:30
47 | Netrokona | 150 | 4 | 2020-07-01 | 21:00
48 | Jamalpur | 147 | 18 | 2020-07-01 | 22:00
49 | Sherpur | 116 | 26 | 2020-07-01 | 19:30
50 | Srimongal | 55 | 31 | 2020-07-01 | 19:00
51 | Shahjibazar | 120 | 26 | 2020-07-01 | 21:00
52 | Fenchuganj | 53 | 23 | 2020-07-01 | 21:00
53 | Kulawara | 50 | 14 | 2020-07-01 | 19:30
54 | Sylhet | 133 | 28 | 2020-07-01 | 21:00
55 | Chatak | 33 | 26 | 2020-07-01 | 21:00
56 | Sunamganj | 47 | 7 | 2020-07-01 | 21:00
57 | Bianibazar | 126 | 21 | 2020-07-01 | 8:00
58 | Cumilla (S) | 174 | 27 | 2020-07-01 | 23:00
59 | Cumilla(N) | 141 | 21 | 2020-07-01 | 20:00
60 | Chandpur | 109 | 8 | 2020-07-01 | 22:00
61 | Feni | 125 | 25 | 2020-07-01 | 21:00
62 | Chowmuhani | 185 | 2 | 2020-07-01 | 22:00
63 | Ashuganj | 65 | 13 | 2020-07-01 | 23:00
64 | Daudkandi | 157 | 8 | 2020-07-01 | 23:00
65 | B.Baria | 164 | 26 | 2020-07-01 | 21:00
66 | Ramganj | 124 | 26 | 2020-07-01 | 21:00
67 | Chaddagram | 52 | 24 | 2020-07-01 | 22:00
68 | PHP | 39 | 1 | 2020-07-01 | 21:00
69 | Madanhat | 70 | 7 | 2020-07-01 | 22:00
70 | Hathazari | 105 | 25 | 2020-07-01 | 20:00
71 | Khulshi | 207 | 28 | 2020-07-01 | 14:00
Page: 2/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:July'2020
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
72 | Halishahar | 140 | 16 | 2020-07-01 | 10:00
73 | Baraulia | 167 | 13 | 2020-07-01 | 0:00
74 | Sikalbaha | 28 | 26 | 2020-07-01 | 14:00
75 | Dohazari | 100 | 4 | 2020-07-01 | 23:00
76 | Cox'sbazar | 105 | 27 | 2020-07-01 | 19:00
77 | Chandraghona | 32 | 1 | 2020-07-01 | 20:00
78 | Kaptai | 5 | 23 | 2020-07-01 | 16:00
79 | A. Khaer Stl. | 12 | 2 | 2020-07-01 | 10:00
80 | Bakulia | 107 | 26 | 2020-07-01 | 14:00
81 | Julda | 25 | 27 | 2020-07-01 | 19:00
82 | TK chemical | 28.5 | 25 | 2020-07-01 | 21:00
83 | Modern Steel | 17 | 12 | 2020-07-01 | 9:00
84 | Shahmirpur | 30 | 1 | 2020-07-01 | 15:00
85 | Khagrachhari | 26 | 1 | 2020-07-01 | 21:00
86 | Matarbari | 41 | 11 | 2020-07-01 | 19:00
87 | Baroiar Hat | 42 | 7 | 2020-07-01 | 19:30
88 | Rangamati | 12 | 1 | 2020-07-01 | 20:00
89 | Abul Khair 230 | 215 | 6 | 2020-07-01 | 12:00
90 | BSRM | 160 | 2 | 2020-07-01 | 8:00
91 | GPH Ispat | 79 | 8 | 2020-07-01 | 7:00
92 | Goalpara | 35 | 14 | 2020-07-01 | 1:00
93 | Central s/s | 99 | 26 | 2020-07-01 | 23:00
94 | Noapara | 69 | 16 | 2020-07-01 | 21:00
95 | Jashore | 132 | 26 | 2020-07-01 | 20:00
96 | Benapol | 54 | 19 | 2020-07-01 | 21:00
97 | Jhenidah | 116 | 18 | 2020-07-01 | 19:30
98 | Bottail | 139 | 29 | 2020-07-01 | 21:00
99 | G.K Project | 64 | 28 | 2020-07-01 | 19:30
100 | Faridpur | 202 | 26 | 2020-07-01 | 22:00
101 | Madaripur | 107 | 26 | 2020-07-01 | 23:00
102 | Sariatpur | 72 | 31 | 2020-07-01 | 22:00
103 | Gopalganj | 101 | 26 | 2020-07-01 | 20:00
104 | Bagerhat | 104 | 25 | 2020-07-01 | 20:00
105 | Mongla | 54 | 14 | 2020-07-01 | 11:00
106 | Satkhira | 114 | 18 | 2020-07-01 | 22:00
107 | Gallamari | 48 | 1 | 2020-07-01 | 23:00
108 | Magura | 60 | 13 | 2020-07-01 | 21:00
109 | Norail | 43 | 31 | 2020-07-01 | 19:30
110 | Chuadanga | 94 | 26 | 2020-07-01 | 24:00
111 | Barsal(N) | 50 | 26 | 2020-07-01 | 21:00
112 | Barsal(S) | 104 | 26 | 2020-07-01 | 19:30
113 | Patuakhali | 129 | 31 | 2020-07-01 | 22:00
114 | Bhandaria | 58 | 2 | 2020-07-01 | 19:30
115 | Borhan Uddin | 48 | 18 | 2020-07-01 | 19:30
116 | Ishurdi | 69 | 26 | 2020-07-01 | 19:30
117 | Ruppur Paromanobik | 3 | 9 | 2020-07-01 | 11:00
118 | Natore | 152 | 26 | 2020-07-01 | 22:00
119 | Bogura | 173 | 26 | 2020-07-01 | 19:30
120 | Naogaon | 135 | 1 | 2020-07-01 | 22:00
121 | Rajshahi | 166 | 16 | 2020-07-01 | 21:00
122 | Rajshahi New | 12 | 1 | 2020-07-01 | 21:00
123 | C.Nawabganj | 78 | 26 | 2020-07-01 | 21:00
124 | Amnura | 50 | 8 | 2020-07-01 | 21:00
125 | Pabna | 134 | 1 | 2020-07-01 | 21:0
126 | Shahjadpur | 120 | 26 | 2020-07-01 | 21:00
127 | Serajganj | 115 | 26 | 2020-07-01 | 20:00
128 | Niyamatpur | 68 | 11 | 2020-07-01 | 21:00
129 | Joypurhat | 58 | 27 | 2020-07-01 | 1:00
130 | Sherpur(Bogura) | 52 | 26 | 2020-07-01 | 24:00
131 | Mohastangar | 62 | 8 | 2020-07-01 | 21:00
132 | Rangpur | 163 | 26 | 2020-07-01 | 20:00
133 | Lalmonirhat | 65 | 26 | 2020-07-01 | 21:00
134 | Saidpur | 113 | 8 | 2020-07-01 | 21:00
135 | Purbasadipur | 109 | 15 | 2020-07-01 | 19:30
136 | Thakurgaon | 84 | 27 | 2020-07-01 | 21:00
137 | Palshbari | 128 | 26 | 2020-07-01 | 19:30
138 | Barapukuria | 52 | 26 | 2020-07-01 | 21:00
139 | Panchugar | 52 | 21 | 2020-07-01 | 21:00
140 | Joldhaka | 33 | 17 | 2020-07-01 | 1:00
141 | Kurigram | 58 | 8 | 2020-07-01 | 19:30
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:July' 2020
Area | MW | Date | Hour | Remarks
Dhaka | 4228 | 26.07.2020 | 15:00
Chattogram | 1342 | 27.07.2020 | 01:00
Khulna | 1598 | 26.07.2020 | 22:00
Rajshahi | 1363 | 26.07.2020 | 21:00
Cumilla | 1222 | 26.07.2020 | 22:00
Mymensingh | 1029 | 18.07.2020 | 22:00
Sylhet | 523 | 26.07.2020 | 21:00
Barisal | 412 | 11.07.2020 | 22:00
Rangpur | 811 | 26.07.2020 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: July'2020
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 398 | 12 | 2020-07-01 | 20:00 | 383 | 2 | 2020-07-01 | 12:00
2 | Bheramara | 400 | 411 | 9 | 2020-07-01 | 11:00 | 382 | 2 | 2020-07-01 | 24:00
3 | Ashuganj(N) | 400 | 399 | 12 | 2020-07-01 | 19:30 | 381 | 23 | 2020-07-01 | 10:00
4 | Payra | 400 | 423 | 13 | 2020-07-01 | 12:00 | 370 | 14 | 2020-07-01 | 5:00
5 | Kaliakoir | 400 | 382 | 13 | 2020-07-01 | 1:00 | 358 | 2 | 2020-07-01 | 12:00
6 | Bhulta | 400 | 394 | 11 | 2020-07-01 | 20:00 | 373 | 2 | 2020-07-01 | 12:00
7 | Gopalganj | 400 | 430 | 4 | 2020-07-01 | 19:30 | 344 | 4 | 2020-07-01 | 19:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 236 | 6 | 2020-07-01 | 1:00 | 230 | 1 | 2020-07-01 | 12:00
2 | Ishurdi | 230 | 239 | 11 | 2020-07-01 | 18:30 | 223 | 1 | 2020-07-01 | 22:00
3 | Ashuganj | 230 | 240 | 11 | 2020-07-01 | 20:00 | 229 | 27 | 2020-07-01 | 10:00
4 | Serajganj | 230 | 234 | 15 | 2020-07-01 | 19:00 | 220 | 8 | 2020-07-01 | 10:00
5 | Baghabari | 230 | 243 | 9 | 2020-07-01 | 15:00 | 230 | 22 | 2020-07-01 | 21:00
6 | Barapukuria | 230 | 237 | 10 | 2020-07-01 | 17:00 | 220 | 26 | 2020-07-01 | 19:30
7 | Bogura | 230 | 234 | 19 | 2020-07-01 | 19:00 | 213 | 1 | 2020-07-01 | 22:00
8 | Rajshahi | 230 | 235 | 11 | 2020-07-01 | 18:00 | 217 | 26 | 2020-07-01 | 20:00
9 | Khulna South | 230 | 237 | 22 | 2020-07-01 | 14:00 | 206 | 20 | 2020-07-01 | 22:00
10 | Rampura | 230 | 230 | 14 | 2020-07-01 | 20:00 | 210 | 14 | 2020-07-01 | 5:00
11 | Haripur | 230 | 232 | 12 | 2020-07-01 | 24:00 | 218 | 28 | 2020-07-01 | 11:00
12 | Hasnabad | 230 | 231 | 12 | 2020-07-01 | 20:00 | 212 | 19 | 2020-07-01 | 12:00
13 | Shyampur | 230 | 229 | 31 | 2020-07-01 | 19:30 | 213 | 19 | 2020-07-01 | 12:00
14 | Aminbazar | 230 | 231 | 13 | 2020-07-01 | 1:00 | 214 | 11 | 2020-07-01 | 8:00
15 | Tongi | 230 | 230 | 5 | 2020-07-01 | 4:00 | 212 | 19 | 2020-07-01 | 15:00
16 | Comilla (N) | 230 | 237 | 15 | 2020-07-01 | 24:00 | 223 | 27 | 2020-07-01 | 2:00
17 | Hathazari | 230 | 231 | 23 | 2020-07-01 | 20:00 | 210 | 18 | 2020-07-01 | 10:00
18 | Megnaghat | 230 | 235 | 31 | 2020-07-01 | 16:00 | 220 | 19 | 2020-07-01 | 12:00
19 | Fenchuganj | 230 | 239 | 12 | 2020-07-01 | 20:00 | 230 | 2 | 2020-07-01 | 16:00
20 | Siddhirganj | 230 | 239 | 1 | 2020-07-01 | 23:00 | 220 | 28 | 2020-07-01 | 12:00
21 | Maniknagar | 230 | 233 | 16 | 2020-07-01 | 16:00 | 218 | 23 | 2020-07-01 | 10:00
22 | Old Airport | 230 | 229 | 12 | 2020-07-01 | 19:30 | 213 | 2 | 2020-07-01 | 12:00
23 | Barisal | 230 | 249 | 13 | 2020-07-01 | 17:00 | 227 | 10 | 2020-07-01 | 22:00
24 | AKSML | 230 | 228 | 15 | 2020-07-01 | 20:00 | 207 | 24 | 2020-07-01 | 10:00
25 | BSRM | 230 | 229 | 15 | 2020-07-01 | 20:00 | 210 | 18 | 2020-07-01 | 10:00
26 | Bibiyana | 230 | 239 | 25 | 2020-07-01 | 10:00 | 227 | 11 | 2020-07-01 | 11:00
27 | Bhulta | 230 | 233 | 11 | 2020-07-01 | 20:00 | 219 | 28 | 2020-07-01 | 12:00
28 | Ashuganj (S) | 230 | 238 | 11 | 2020-07-01 | 19:00 | 222 | 27 | 2020-07-01 | 11:00
29 | Kaliakoir | 230 | 237 | 31 | 2020-07-01 | 6:00 | 217 | 2 | 2020-07-01 | 10:00
30 | GPH | 230 | 229 | 2 | 2020-07-01 | 1:00 | 209 | 24 | 2020-07-01 | 10:00
132 kV Substation
1 | Siddhirganj | 132 | 135 | 31 | 2020-07-01 | 0.8125 | 125 | 19 | 2020-07-01 | 0.41667
2 | Munsiganj | 132 | 137 | 11 | 2020-07-01 | 0.79167 | 125 | 19 | 2020-07-01 | 0.70833
3 | Sonargaon | 132 | 136 | 31 | 2020-07-01 | 0.8125 | 124 | 8 | 2020-07-01 | 0.45833
4 | Shyampur | 132 | 140 | 30 | 2020-07-01 | 0.8125 | 128 | 2 | 2020-07-01 | 0.5
5 | Bhulta | 132 | 127 | 11 | 2020-07-01 | 0.79167 | 117 | 19 | 2020-07-01 | 0.45833
6 | Madanganj | 132 | 133 | 21 | 2020-07-01 | 0.95833 | 122 | 29 | 2020-07-01 | 0.41667
7 | Shitalakhya | 132 | 142 | 4 | 2020-07-01 | 0.79167 | 124 | 12 | 2020-07-01 | 0.25
8 | Rahim Steal | 132 | 134 | 12 | 2020-07-01 | 0.79167 | 125 | 19 | 2020-07-01 | 0.70833
9 | Matuail | 132 | 135 | 31 | 2020-07-01 | 0.8125 | 125 | 19 | 2020-07-01 | 0.41667
10 | Ghorasal | 132 | 140 | 10 | 2020-07-01 | 0.29167 | 130 | 2 | 2020-07-01 | 0.375
11 | Narsinghdi | 132 | 131 | 12 | 2020-07-01 | 0.79167 | 120 | 18 | 2020-07-01 | 0.95833
12 | Haripur (SBU) | 132 | 135 | 3 | 2020-07-01 | 0.75 | 125 | 9 | 2020-07-01 | 0.66667
13 | Ullon | 132 | 135 | 5 | 2020-07-01 | 0.125 | 125 | 19 | 2020-07-01 | 0.41667
14 | Hasnabad | 132 | 140 | 4 | 2020-07-01 | 0.83333 | 125 | 19 | 2020-07-01 | 0.41667
15 | Magbazar | 132 | 136 | 6 | 2020-07-01 | 0.8125 | 124 | 28 | 2020-07-01 | 0.5
16 | Maniknagar | 132 | 135 | 5 | 2020-07-01 | 0.125 | 124 | 27 | 2020-07-01 | 0.5
17 | Bangabhaban | 132 | 135 | 5 | 2020-07-01 | 0.125 | 124 | 27 | 2020-07-01 | 0.5
18 | Narinda | 132 | 135 | 5 | 2020-07-01 | 0.125 | 124 | 27 | 2020-07-01 | 0.5
19 | Dhanmondi | 132 | 135 | 5 | 2020-07-01 | 0.125 | 125 | 19 | 2020-07-01 | 0.41667
20 | Lalbag | 132 | 140 | 30 | 2020-07-01 | 0.8125 | 120 | 19 | 2020-07-01 | 0.5
21 | Madartek | 132 | 135 | 13 | 2020-07-01 | 0.083333 | 123 | 28 | 2020-07-01 | 0.5
22 | Dhaka University | 132 | - | - | - | - | - | - | - | -
23 | Fatullah | 132 | 139 | 30 | 2020-07-01 | 0.79167 | 128 | 19 | 2020-07-01 | 0.5
24 | Mirpur | 132 | 137 | 16 | 2020-07-01 | 0.083333 | 122 | 2 | 2020-07-01 | 0.5
25 | Kalyanpur | 132 | 135 | 13 | 2020-07-01 | 0.083333 | 124 | 2 | 2020-07-01 | 0.5
26 | Gulshan | 132 | 136 | 26 | 2020-07-01 | 0.20833 | 124 | 27 | 2020-07-01 | 0.41667
27 | Uttara | 132 | 138 | 30 | 2020-07-01 | 0.79167 | 122 | 2 | 2020-07-01 | 0.5
28 | Uttara(New) | 132 | 137 | 30 | 2020-07-01 | 0.83333 | 120 | 2 | 2020-07-01 | 0.5
29 | Kamrangirchar | 132 | 139 | 8 | 2020-07-01 | 0.91667 | 122 | 28 | 2020-07-01 | 0.5
30 | Savar | 132 | 134 | 13 | 2020-07-01 | 0.041667 | 122 | 2 | 2020-07-01 | 0.5
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: July'2020
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
31 | Bhasantec | 132 | 134 | 14 | 2020-07-01 | 0.25 | 122 | 2 | 2020-07-01 | 0.5
32 | Agargaon | 132 | 135 | 13 | 2020-07-01 | 0.125 | 123 | 2 | 2020-07-01 | 0.5
33 | Satmosjid | 132 | 134 | 13 | 2020-07-01 | 0.125 | 123 | 2 | 2020-07-01 | 0.5
34 | Tongi | 132 | 139 | 11 | 2020-07-01 | 0.875 | 125 | 27 | 2020-07-01 | 0.41667
35 | Kabirpur | 132 | 138 | 20 | 2020-07-01 | 0.29167 | 121 | 2 | 2020-07-01 | 0.5
36 | Basundhara | 132 | 135 | 12 | 2020-07-01 | 0.83333 | 123 | 28 | 2020-07-01 | 0.5
37 | Manikganj | 132 | 142 | 30 | 2020-07-01 | 0.79167 | 125 | 18 | 2020-07-01 | 0.41667
38 | Joydevpur | 132 | 144 | 27 | 2020-07-01 | 0.083333 | 124 | 4 | 2020-07-01 | 0.66667
39 | New Tongi | 132 | 139 | 30 | 2020-07-01 | 0.8125 | 124 | 2 | 2020-07-01 | 0.5
40 | Kodda | 132 | 142 | 30 | 2020-07-01 | 0.8125 | 118 | 2 | 2020-07-01 | 0.5
41 | Dhamrai | 132 | 138 | 20 | 2020-07-01 | 0.29167 | 121 | 2 | 2020-07-01 | 0.5
42 | Rajendrapur | 132 | 140 | 30 | 2020-07-01 | 0.8125 | 116 | 2 | 2020-07-01 | 0.5
43 | Valuka | 132 | 133 | 11 | 2020-07-01 | 0.25 | 110 | 1 | 2020-07-01 | 0.95833
44 | Tangail | 132 | 139 | 20 | 2020-07-01 | 0.58333 | 122 | 1 | 2020-07-01 | 0.91667
45 | Mymensing | 132 | 134 | 11 | 2020-07-01 | 0.25 | 112 | 18 | 2020-07-01 | 0.91667
46 | Kishorganj | 132 | 136 | 11 | 2020-07-01 | 0.25 | 115 | 18 | 2020-07-01 | 0.91667
47 | Netrokona | 132 | 134 | 11 | 2020-07-01 | 0.20833 | 108 | 18 | 2020-07-01 | 0.875
48 | Jamalpur | 132 | 139 | 8 | 2020-07-01 | 0.25 | 119 | 10 | 2020-07-01 | 0.41667
49 | Sherpur | 132 | 139 | 8 | 2020-07-01 | 0.33333 | 117 | 10 | 2020-07-01 | 0.45833
50 | Srimongal | 132 | 138 | 11 | 2020-07-01 | 0.20833 | 129 | 3 | 2020-07-01 | 0.91667
51 | Shahjibazar | 132 | 137 | 11 | 2020-07-01 | 0.29167 | 127 | 26 | 2020-07-01 | 0.79167
52 | Fenchuganj | 132 | 138 | 21 | 2020-07-01 | 0.45833 | 128 | 16 | 2020-07-01 | 0.79167
53 | Khulawara | 132 | 138 | 21 | 2020-07-01 | 0.54167 | 126 | 17 | 2020-07-01 | 0.91667
54 | Sylhet | 132 | 134 | 1 | 2020-07-01 | 0.29167 | 120 | 3 | 2020-07-01 | 0.41667
55 | Chattak | 132 | 134 | 10 | 2020-07-01 | 0.33333 | 121 | 17 | 2020-07-01 | 0.95833
56 | Sunamganj | 132 | 134 | 1 | 2020-07-01 | 0.33333 | 117 | 17 | 2020-07-01 | 0.95833
57 | Biani Bazar | 132 | 135 | 21 | 2020-07-01 | 0.54167 | 118 | 18 | 2020-07-01 | 0.041667
58 | Comilla(South) | 132 | 130 | 2 | 2020-07-01 | 0.33333 | 118 | 3 | 2020-07-01 | 0.8125
59 | Comilla (North) | 132 | 139 | 8 | 2020-07-01 | 0.91667 | 129 | 2 | 2020-07-01 | 0.625
60 | Chandpur | 132 | 138 | 14 | 2020-07-01 | 0.77083 | 120 | 7 | 2020-07-01 | 0.77083
61 | Feni | 132 | 138 | 14 | 2020-07-01 | 0.91667 | 124 | 3 | 2020-07-01 | 0.5
62 | Chowmuhani | 132 | 136 | 15 | 2020-07-01 | 0.8125 | 116 | 17 | 2020-07-01 | 0.625
63 | Ashuganj | 132 | 138 | 11 | 2020-07-01 | 0.29167 | 130 | 1 | 2020-07-01 | 0.875
64 | Daudkandi | 132 | 136 | 8 | 2020-07-01 | 0.91667 | 123 | 27 | 2020-07-01 | 0.41667
65 | Brahminbaria | 132 | 135 | 20 | 2020-07-01 | 0.375 | 123 | 15 | 2020-07-01 | 0.875
66 | Ramganj | 132 | 132 | 15 | 2020-07-01 | 0.95833 | 112 | 2 | 2020-07-01 | 0.625
67 | Chaddagram | 132 | 137 | 2 | 2020-07-01 | 0.83333 | 124 | 6 | 2020-07-01 | 0.66667
68 | PHP | 132 | 138 | 15 | 2020-07-01 | 0.8125 | 122 | 18 | 2020-07-01 | 0.41667
69 | Madanhat | 132 | 141 | 23 | 2020-07-01 | 0.83333 | 128 | 18 | 2020-07-01 | 0.41667
70 | Hathazari | 132 | 138 | 23 | 2020-07-01 | 0.83333 | 125 | 18 | 2020-07-01 | 0.41667
71 | Khulshi | 132 | 140 | 4 | 2020-07-01 | 0.75 | 124 | 18 | 2020-07-01 | 0.41667
72 | Halishahar | 132 | 140 | 14 | 2020-07-01 | 0.875 | 125 | 18 | 2020-07-01 | 0.41667
73 | Baraulia | 132 | 138 | 14 | 2020-07-01 | 0.875 | 123 | 18 | 2020-07-01 | 0.41667
74 | Sikalbaha | 132 | 141 | 22 | 2020-07-01 | 0.91667 | 126 | 18 | 2020-07-01 | 0.41667
75 | Dohazari | 132 | 138 | 15 | 2020-07-01 | 0.8125 | 123 | 31 | 2020-07-01 | 0.54167
76 | Cox'sbazar | 132 | 131 | 14 | 2020-07-01 | 0.66667 | 112 | 8 | 2020-07-01 | 0.77083
77 | Chandraghona | 132 | 138 | 15 | 2020-07-01 | 0.83333 | 127 | 24 | 2020-07-01 | 0.41667
78 | Kaptai | 132 | 136 | 14 | 2020-07-01 | 0.79167 | 129 | 24 | 2020-07-01 | 0.29167
79 | A. Khaer Stl. | 132 | 136 | 23 | 2020-07-01 | 0.79167 | 125 | 18 | 2020-07-01 | 0.41667
80 | Bakulia | 132 | 139 | 22 | 2020-07-01 | 0.91667 | 113 | 9 | 2020-07-01 | 0.45833
81 | Julda | 132 | 139 | 14 | 2020-07-01 | 0.77083 | 126 | 24 | 2020-07-01 | 0.375
82 | TK Chemical | 132 | 140 | 23 | 2020-07-01 | 0.83333 | 113 | 21 | 2020-07-01 | 0.375
83 | Modern Steel | 132 | 138 | 15 | 2020-07-01 | 0.8125 | 126 | 24 | 2020-07-01 | 0.33333
84 | Shahmirpur | 132 | 140 | 23 | 2020-07-01 | 0.83333 | 126 | 24 | 2020-07-01 | 0.375
85 | Khagrachhari | 132 | 137 | 22 | 2020-07-01 | 0.91667 | 126 | 24 | 2020-07-01 | 0.41667
86 | Matarbari | 132 | 133 | 4 | 2020-07-01 | 0.70833 | 115 | 12 | 2020-07-01 | 0.625
87 | Baroiar Hat | 132 | 137 | 8 | 2020-07-01 | 0.91667 | 124 | 6 | 2020-07-01 | 0.58333
88 | Rangamati | 132 | 137 | 14 | 2020-07-01 | 0.8125 | 127 | 24 | 2020-07-01 | 0.41667
89 | Goalpara | 132 | 140 | 11 | 2020-07-01 | 0.77083 | 121 | 30 | 2020-07-01 | 0.625
90 | Khulna Central | 132 | 140 | 23 | 2020-07-01 | 0.29167 | 121 | 25 | 2020-07-01 | 0.79167
91 | Noapara | 132 | 139 | 23 | 2020-07-01 | 0.25 | 121 | 2 | 2020-07-01 | 0.41667
92 | Jessore | 132 | 134 | 11 | 2020-07-01 | 0.77083 | 111 | 25 | 2020-07-01 | 0.8125
93 | Benapol | 132 | 136 | 11 | 2020-07-01 | 0.77083 | 111 | 25 | 2020-07-01 | 0.8125
94 | Jhenida | 132 | 132 | 11 | 2020-07-01 | 0.77083 | 105 | 25 | 2020-07-01 | 0.8125
95 | Bottail | 132 | 138 | 19 | 2020-07-01 | 0.875 | 120 | 2 | 2020-07-01 | 0.875
96 | G.K Project | 132 | 140 | 9 | 2020-07-01 | 0.75 | 129 | 2 | 2020-07-01 | 0.66667
97 | Faridpur | 132 | 137 | 31 | 2020-07-01 | 0.33333 | 122 | 4 | 2020-07-01 | 0.83333
98 | Madaripur | 132 | 141 | 7 | 2020-07-01 | 0.29167 | 120 | 4 | 2020-07-01 | 0.625
99 | Sariatpur | 132 | 142 | 13 | 2020-07-01 | 0.5 | 123 | 16 | 2020-07-01 | 0.875
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: July'2020
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
100 | Gopalganj | 132 | 144 | 14 | 2020-07-01 | 0.625 | 122 | 3 | 2020-07-01 | 0.875
101 | Bagerhat | 132 | 138 | 9 | 2020-07-01 | 0.58333 | 118 | 1 | 2020-07-01 | 0.45833
102 | Mongla | 132 | 135 | 9 | 2020-07-01 | 0.58333 | 110 | 30 | 2020-07-01 | 0.625
103 | Satkhira | 132 | 139 | 11 | 2020-07-01 | 0.77083 | 119 | 30 | 2020-07-01 | 0.625
104 | Gallamari | 132 | 141 | 11 | 2020-07-01 | 0.77083 | 122 | 25 | 2020-07-01 | 0.8125
105 | Magura | 132 | 132 | 11 | 2020-07-01 | 0.77083 | 104 | 25 | 2020-07-01 | 0.8125
106 | Norail | 132 | 128 | 6 | 2020-07-01 | 0.75 | 101 | 25 | 2020-07-01 | 0.8125
107 | Chuadanga | 132 | 130 | 11 | 2020-07-01 | 0.77083 | 96 | 26 | 2020-07-01 | 0.875
108 | Barisal(N) | 132 | 145 | 4 | 2020-07-01 | 0.8125 | 121 | 4 | 2020-07-01 | 0.58333
109 | Barisal(S) | 132 | 141 | 4 | 2020-07-01 | 0.8125 | 119 | 4 | 2020-07-01 | 0.79167
110 | Patuakhali | 132 | 141 | 4 | 2020-07-01 | 0.16667 | 110 | 4 | 2020-07-01 | 0.79167
111 | Bhandaria | 132 | 138 | 28 | 2020-07-01 | 0.54167 | 115 | 4 | 2020-07-01 | 0.8125
112 | Ishurdi | 132 | 138 | 10 | 2020-07-01 | 0.75 | 129 | 1 | 2020-07-01 | 0.875
113 | Ruppur paromanobik | 132 | 137 | 9 | 2020-07-01 | 0.70833 | 128 | 7 | 2020-07-01 | 0.83333
114 | Natore | 132 | 137 | 9 | 2020-07-01 | 0.79167 | 124 | 3 | 2020-07-01 | 0.83333
115 | Bogra | 132 | 137 | 13 | 2020-07-01 | 0.54167 | 123 | 1 | 2020-07-01 | 0.875
116 | Noagaon | 132 | 133 | 19 | 2020-07-01 | 0.79167 | 116 | 26 | 2020-07-01 | 0.875
117 | Rajshahi | 132 | 135 | 9 | 2020-07-01 | 0.77083 | 123 | 3 | 2020-07-01 | 0.875
118 | Rajshahi New | 132 | 136 | 9 | 2020-07-01 | 0.75 | 122 | 31 | 2020-07-01 | 0.875
119 | C.Nawabganj | 132 | 134 | 9 | 2020-07-01 | 0.77083 | 120 | 18 | 2020-07-01 | 0.625
120 | Amnura | 132 | 136 | 16 | 2020-07-01 | 0.77083 | 118 | 31 | 2020-07-01 | 0.083333
121 | Pabna | 132 | 136 | 10 | 2020-07-01 | 0.77083 | 125 | 1 | 2020-07-01 | 0.875
122 | Shahjadpur | 132 | 140 | 2 | 2020-07-01 | 0.79167 | 118 | 13 | 2020-07-01 | 0.083333
123 | Serajganj | 132 | 136 | 19 | 2020-07-01 | 0.79167 | 125 | 1 | 2020-07-01 | 0.875
124 | Niyamatpur | 132 | 132 | 10 | 2020-07-01 | 0.77083 | 113 | 1 | 2020-07-01 | 0.875
125 | Joypurhat | 132 | 135 | 10 | 2020-07-01 | 0.77083 | 114 | 17 | 2020-07-01 | 0.875
126 | Sherpur(Bogura) | 132 | 136 | 13 | 2020-07-01 | 0.58333 | 123 | 1 | 2020-07-01 | 0.91667
127 | Mohastangor | 132 | 136 | 13 | 2020-07-01 | 0.54167 | 120 | 5 | 2020-07-01 | 0.875
128 | Rangpur | 132 | 137 | 9 | 2020-07-01 | 0.5 | 114 | 18 | 2020-07-01 | 0.83333
129 | Lalmonirhat | 132 | 138 | 27 | 2020-07-01 | 0.041667 | 107 | 16 | 2020-07-01 | 0.875
130 | Saidpur | 132 | 140 | 27 | 2020-07-01 | 0.041667 | 109 | 28 | 2020-07-01 | 0.875
131 | Purbasadipur | 132 | 134 | 3 | 2020-07-01 | 0.29167 | 102 | 18 | 2020-07-01 | 0.83333
132 | Thakurgaon | 132 | 136 | 8 | 2020-07-01 | 0.5 | 100 | 18 | 2020-07-01 | 0.875
133 | Palashbari | 132 | 134 | 27 | 2020-07-01 | 0.041667 | 104 | 6 | 2020-07-01 | 0.875
134 | Barapukuria | 132 | 137 | 3 | 2020-07-01 | 0.25 | 110 | 19 | 2020-07-01 | 0.041667
135 | Panchagar | 132 | 135 | 8 | 2020-07-01 | 0.5 | 93 | 5 | 2020-07-01 | 0.875
136 | Joldhaka | 132 | 138 | 8 | 2020-07-01 | 0.5 | 106 | 16 | 2020-07-01 | 0.875
137 | Kurigram | 132 | 135 | 9 | 2020-07-01 | 0.5 | 106 | 16 | 2020-07-01 | 0.875
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:July' 2020
Name of the | Auto transofrmer |  | Recorded maximum load
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kV side ) | Date | Time | Remarks
| TR1 | 225 | 145 | 370
Hasnabad | TR2 | 225 | 135 | 370 | 19.07.2020 | 11:00
| TR3 | 225 | 132 | 370
| TR1 | 225 | 190 | 540
Tongi | TR2 | 225 | 190 | 540 | 05.07.2020 | 12:00
| TR3 | 225 | 190 | 540
Haripur | TR1 | 225 | 136 | 380 | 30.07.2020 | 07:00
| TR3 | 225 | 136 | 380
| TR1 | 225 | 165 | 460
Rampura | TR2 | 225 | 165 | 460 | 19.07.2020 | 12:00
| TR3 | 225 | 165 | 460
| TR1 | 225 | 132 | 367
Aminbazar | TR2 | 225 | 132 | 367 | 02.07.2020 | 18:00
| TR3 | 225 | 137 | 386
Maniknagar | TR1 | 300 | 114 | 340 | 08.07.2020 | 13:00
| TR2 | 300 | 114 | 340
Cumilla (N) | TR1 | 225 | 181 | 542 | 30.07.2020 | 23:00
| TR2 | 225 | 178 | 542
Fenchuganj | AT2 | 300 | 195 | 486 | 11.07.2020 | 9:00
| MT1 | 150 | 73 | 210
Hathazari | MT2 | 150 | 73 | 210 | 31.07.2020 | 18:30
| MT3 | 150 | 73 | 210
| MT4 | 150 | 73 | 210
| TR1 | 225 | 135 | 375
Ishurdi | TR2 | 225 | 135 | 375 | 14.07.2020 | 20:00
| TR3 | 225 | 135 | 375
Khulna(S) | TR1 | 225 | 127 | 338
| TR2 | 225 | 127 | 338 | 13.07.2020 | 19:00
| TR3 | 300 | 163 | 437
Bogra | TR1 | 225 | 120 | 344 | 04.07.2020 | 21:00
| TR2 | 225 | 120 | 344
| TR3 | 225 | 162 | 450
Baghabari | TR1 | 300 | 180 | 495 | 01.07.2020 | 23:00
| TR2 | 225 | 130 | 360
Barapukuria | TR1 | 225 | 167 | 750 | 19.07.2020 | 20:00 | Due to unavailability of 230 kV side meters
| TR2 | 225 | 144 | 670 |  |  | 132 kV current is being provided
| TR6 | 300 | 186 | 863
Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:July' 2020
Name of the | Transofrmer |  | Recorded maximum load |  |  |  | Remarks
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 400 kV side ) | Date | Time
Kaliakoir | TR1(400/230 kV) | 520 | 104.6 | 238.7 | 21.07.2020 | 8:30
| TR2(400/230 kV) | 520 | 106.9 | 245
| TR1(400/132 kV) | 325 | 253.8 | 430.6 | 14.07.2020 | 19:15
| TR2(400/132 kV) | 325 | 253.5 | 432.6
Bibiyana | ICT1(400/230 kV) | 520 | 156 | 269 | 24.06.2020 | 15:00
| ICT2(400/230kV) | 520 | 156 | 269
Bhulta | ATR1(400/230 kV) | 520 | 259 | 460 | 28.07.2020 | 12:15
| ATR2(400/230kV) | 520 | 259 | 460
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:July' 2020 | [6 empty] | (For Evening Peak) | [7 empty] | Month:July' 2020 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-07-20 | 12112 | 12112 | - | - | - | - | - | - | - | - | - | - | - | - | 01-07-20 | 10212.8 | 10212.8 | - | - | - | - | - | - | - | - | - | - | - | -
02-07-20 | 12032 | 12032 | - | - | - | - | - | - | - | - | - | - | - | - | 02-07-20 | 10368.1 | 10368.1 | - | - | - | - | - | - | - | - | - | - | - | -
03-07-20 | 11491 | 11491 | - | - | - | - | - | - | - | - | - | - | - | - | 03-07-20 | 8841.66 | 8841.66 | - | - | - | - | - | - | - | - | - | - | - | -
04-07-20 | 11743 | 11743 | - | - | - | - | - | - | - | - | - | - | - | - | 04-07-20 | 9795.9 | 9795.9 | - | - | - | - | - | - | - | - | - | - | - | -
05-07-20 | 11415 | 11415 | - | - | - | - | - | - | - | - | - | - | - | - | 05-07-20 | 9726.9 | 9726.9 | - | - | - | - | - | - | - | - | - | - | - | -
06-07-20 | 10677 | 10677 | - | - | - | - | - | - | - | - | - | - | - | - | 06-07-20 | 8998.5 | 8998.5 | - | - | - | - | - | - | - | - | - | - | - | -
07-07-20 | 11843 | 11843 | - | - | - | - | - | - | - | - | - | - | - | - | 07-07-20 | 9863 | 9863 | - | - | - | - | - | - | - | - | - | - | - | -
08-07-20 | 11838 | 11838 | - | - | - | - | - | - | - | - | - | - | - | - | 08-07-20 | 9872.1 | 9872.1 | - | - | - | - | - | - | - | - | - | - | - | -
09-07-20 | 11305 | 11305 | - | - | - | - | - | - | - | - | - | - | - | - | 09-07-20 | 9901.8 | 9901.8 | - | - | - | - | - | - | - | - | - | - | - | -
10-07-20 | 10640 | 10640 | - | - | - | - | - | - | - | - | - | - | - | - | 10-07-20 | 8329.2 | 8329.2 | - | - | - | - | - | - | - | - | - | - | - | -
11-07-20 | 10538 | 10538 | - | - | - | - | - | - | - | - | - | - | - | - | 11-07-20 | 9120.3 | 9120.3 | - | - | - | - | - | - | - | - | - | - | - | -
12-07-20 | 10886 | 10886 | - | - | - | - | - | - | - | - | - | - | - | - | 12-07-20 | 9400.9 | 9400.9 | - | - | - | - | - | - | - | - | - | - | - | -
13-07-20 | 11407 | 11407 | - | - | - | - | - | - | - | - | - | - | - | - | 13-07-20 | 9516.7 | 9516.7 | - | - | - | - | - | - | - | - | - | - | - | -
14-07-20 | 11783 | 11783 | - | - | - | - | - | - | - | - | - | - | - | - | 14-07-20 | 9794.3 | 9794.3 | - | - | - | - | - | - | - | - | - | - | - | -
15-07-20 | 11903 | 11903 | - | - | - | - | - | - | - | - | - | - | - | - | 15-07-20 | 9895.1 | 9895.1 | - | - | - | - | - | - | - | - | - | - | - | -
16-07-20 | 11962 | 11962 | - | - | - | - | - | - | - | - | - | - | - | - | 16-07-20 | 10082.6 | 10082.6 | - | - | - | - | - | - | - | - | - | - | - | -
17-07-20 | 11543 | 11543 | - | - | - | - | - | - | - | - | - | - | - | - | 17-07-20 | 8814.5 | 8814.5 | - | - | - | - | - | - | - | - | - | - | - | -
18-07-20 | 12103 | 12103 | - | - | - | - | - | - | - | - | - | - | - | - | 18-07-20 | 9760.7 | 9760.7 | - | - | - | - | - | - | - | - | - | - | - | -
19-07-20 | 11331 | 11331 | - | - | - | - | - | - | - | - | - | - | - | - | 19-07-20 | 9731.9 | 9731.9 | - | - | - | - | - | - | - | - | - | - | - | -
20-07-20 | 10787 | 10787 | - | - | - | - | - | - | - | - | - | - | - | - | 20-07-20 | 9311.6 | 9311.6 | - | - | - | - | - | - | - | - | - | - | - | -
21-07-20 | 10747 | 10747 | - | - | - | - | - | - | - | - | - | - | - | - | 21-07-20 | 8782.3 | 8782.3 | - | - | - | - | - | - | - | - | - | - | - | -
22-07-20 | 11483 | 11483 | - | - | - | - | - | - | - | - | - | - | - | - | 22-07-20 | 9143.5 | 9143.5 | - | - | - | - | - | - | - | - | - | - | - | -
23-07-20 | 11580 | 11580 | - | - | - | - | - | - | - | - | - | - | - | - | 23-07-20 | 9474.2 | 9474.2 | - | - | - | - | - | - | - | - | - | - | - | -
24-07-20 | 10998 | 10998 | - | - | - | - | - | - | - | - | - | - | - | - | 24-07-20 | 8224.7 | 8224.7 | - | - | - | - | - | - | - | - | - | - | - | -
25-07-20 | 12225 | 12225 | - | - | - | - | - | - | - | - | - | - | - | - | 25-07-20 | 9099.3 | 9099.3 | - | - | - | - | - | - | - | - | - | - | - | -
26-07-20 | 12536 | 12536 | - | - | - | - | - | - | - | - | - | - | - | - | 26-07-20 | 10525.4 | 10525.4 | - | - | - | - | - | - | - | - | - | - | - | -
27-07-20 | 11885 | 11885 | - | - | - | - | - | - | - | - | - | - | - | - | 27-07-20 | 10052.3 | 10052.3 | - | - | - | - | - | - | - | - | - | - | - | -
28-07-20 | 11797 | 11797 | - | - | - | - | - | - | - | - | - | - | - | - | 28-07-20 | 10012.9 | 10012.9 | - | - | - | - | - | - | - | - | - | - | - | -
29-07-20 | 11548 | 11548 | - | - | - | - | - | - | - | - | - | - | - | - | 29-07-20 | 9259.7 | 9259.7 | - | - | - | - | - | - | - | - | - | - | - | -
30-07-20 | 11169 | 11169 | - | - | - | - | - | - | - | - | - | - | - | - | 30-07-20 | 9204 | 9204
31-07-20 | 10415 | 10415 | - | - | - | - | - | - | - | - | - | - | - | - | 31-07-20 | 7640.3 | 7640.3

## QF-LDC-38
page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:July' 2020
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 12552 | 26/07/20 | 22:00
2 | Maximum Day Peak Genaration | MW | 10525.4 | 26/07/20 | 12:00
3 | Maximum Evening Peak Demand | MW | 12536 | 26/07/20 | 21:00
4 | Minimum Generation | MW | 7092.1 | 31/07/20 | 8:00
5 | Average of the daily evening peak Genaration | MW | 11474.9032
6 | Average of the daily day peak Genaration | MW | 9424.8087
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW | -
11 | Total Generation | MKWH | 7423.5366
12 | Total Generation by BPDB | MKWH | 3547.5075 | % of total Gen. | 47.79%
13 | Total Generation by IPP | MKWH | 2298.0033 | '' | 30.96%
14 | A) Total Generation by RPCL | MKWH | 126.563 | '' | 1.705%
| B) Total Generation by REB | MKWH | 150.4311 | " | 2.026%
| C) Total Generation by RENTAL | MKWH | 531.8624 | " | 7.165%
| D) Total Imported from India (HVDC) | MKWH | 672.1047 | " | 9.054%
| E) Total Imported from Tripura, India (A.C) | MKWH | 97.0646 | " | 1.308%
15 | Fuel wise Generation.
| A) Gas | MKWH | 4349.8373 | % of total Gen. | 58.6%
| B) Oil | MKWH | 1721.0784 | '' | 23.18%
| C) Hydro | MKWH | 90.7677 | '' | 1.223%
| D) Solar | MKWH | 4.1688 | '' | 0.05616%
| E) Coal | MKWH | 488.515 | '' | 6.581%
| F) HVDC (Import from India) | MKWH | 672.1047 | '' | 9.054%
| G) A.C (Import from Tripura, India) | MKWH | 97.0646 | '' | 1.308%
16 | Maximun of the daily total Generation . | MKWH | 263.5347 | 26-07-2020
17 | Monthly Load factor | % | 79.4923
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 21023.794
| A) Gas | M.Taka | 4875.6997
| B) Liquid fuel | M.Taka | 13886.369
| C) Coal | M.Taka | 2261.7254
| D) HVDC (Import from India) | M.Taka | 3427.7341
| E) Tripura(Import from India) | M.Taka | 727.9848
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 883.5385 | 24/07/2020
| A) Gas | M.Taka | 171.3384 | 01/07/2020
| B) Liquid fuel | M.Taka | 647.3859 | 26/07/2020
| C) Coal | M.Taka | 86.2404 | 03/07/2020
| D) HVDC (Import from India) | M.Taka | 116.1316 | 12-07-2020
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 3.1379
| B) Excluding Hydro & Solar | Taka/KWHR | 3.1782
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 88.83 | 31/07/2020 | 06:00
b) | Actual | FT (MSL) | 89.7 | 31/07/2020 | 06:00
22 | Peak Genaration of July 2019 | MW | 12436 | 21/07/19 | 21:00
23 | Peak Demand of July 2019 | MW | 12436 | 21/07/19 | 21:00
24 | Maximum peak Generation recorded upto 31/07/2020 | MW | 12893 | 29/05/19 | 21:00
25 | Maximum peak Demand recorded upto 31/07/2020 | MW | 12893 | 29/05/19 | 21:00
26 | Maximum load shed recorded upto 31/07/2020 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.