## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-08-22 | Saturday
|  |  | Date (day): | 2020-08-22 |  | Saturday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13117.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14759 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-08-21 | 2020-08-22 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 28 | 28 | 28 | 28 |  | 57 | Unit-2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 110 | 110 | 110 | 110
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 68 | 72 | 70 | 70 |  | 8 | Engine problem
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 88 | 98 | 100 | 100
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 84 | 335 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 300 | 358 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 360 | 420 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 100 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 150 | 140 | 150 | 150 |  |  | GT-1 S/D for gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 15 | 80 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 10 | 30 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 19 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 7 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 208 | 146 | 210 | 210 |  |  | ST under shut down
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 94 | 90 | 94 |  | 8 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 49 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 22 | 53 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 64 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 46 | 55 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 35 | 50
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 65 | 286 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 80 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 106 | 133 | 115 | 115 |  | 34 | Engine problem
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 29 | 90 | 104 | 104
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 1768 | 2810 | 3824 | 4114 | 423 | 982
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 7.5 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 123 | 119 | 119 | 119 | 111 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 164 | 164 | 165 | 165 | 60 |  | Gas shortage
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 116 | 107 | 105 | 105 | 45 |  | Gas shortage
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 100 | 100
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 16 | 18 | 18 |  | 4 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 22 | 42 | 30 | 30
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 21 | 97 | 97 |  | 11 | Engine problem
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3.7 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 160 | 234 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 50 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 70 | 100 | 100 | 100
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 784.2 | 971 | 1534 | 1573 | 576 | 113
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 80 | 80 | 80 | 80 | 49 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 184 | 216 | 220 | 220
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 245 | 260 | 20 | 360
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 220 | 220 | 250 | 360
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 6 | 26 | 26 | 19 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 8 | 8 | 187 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 95 | 93 | 90 | 90 |  | 73 | ST under shut down
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 200 | 200
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 18 | 18 |  | 4 | Engine problem
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 84 | 136 | 163 | 173
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 25 | 43 | 43 |  | 9 | Engine problem
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 12 | 21 | 21 | 21
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 1 | 56 | 60 | 60 | 53 |  | Fuel shortage.
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1006 | 1175 | 1555 | 2265 | 627 | 94
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 139 | 158 | 160 | 160 | 42 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 17 | 17 |  | 5 | Engine problem
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 91 | 80 | 80 |  | 15 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0.7 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 168 | 200 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 45 | 115 | 115
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 332.7 | 511 | 573.6 | 572 | 42 | 20
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 60 | 60 | 60
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  |  | unit-4 under shut down
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 163 | 163 | 163
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 215 | 197 | 210 | 210 |  |  | ST under shut down
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 44 | 47 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 46 | 46 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 64 | 61 | 66
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 83 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 80 | 79 | 80 | 80 |  | 151 | Engine problem
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 16 | 25 | 25
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 290 | 341 | 341
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1054 | 1111 | 1190 | 1195 | 0 | 551
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 931 | 930 | 941 | 941
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 49 | 83 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 150 | 150 | 220
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 260 | 345 | 350 | 410
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 30 | 60 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 90 | 90 |  | 15 | Engine problem
| 108 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1360 | 1578 | 1846 | 2122 | 0 | 15
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 32 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 17 | 29 | 33 | 33
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 90 | 90 | 90 | 90 |  | 104 | GT-2 & ST Under maint.
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 33 | 80 | 80 | 80 |  | 15 | Engine problem
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 420 | 510 | 500 | 660
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 560 | 741 | 813 | 973 | 0 | 119
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 44 | 0 | 40
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | S/D for ST Under maint.
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 155 | 199 | 220 | 220 |  |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 200 | 220 | 220 | 220 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 381 | 383 | 414 | 414 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 26 | 0 | 30
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 22 | 18 | 18 |  | 4 | Engine problem
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 11 | 11 | 10 | 10
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 10 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 25 | 43 | 43 |  | 9 | Engine problem
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 100 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 70 | 113 | 113
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 5 | 109 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 775 | 1270 | 1511 | 1672 | 431 | 13
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 149 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 85 | 113 | 113
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 0 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 150 | 234 | 271 | 273 | 294 | 30
|  | Total |  |  |  |  | 20383 | 19892 | 7789.9 | 10401 | 13117.6 | 14759 | 2393 | 1937
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7459.61 | 9960 | 12561.4168 | 14133.2218
| A. |  | 2020-08-21 | (Yesterday) |  |  |  |  | Friday
| 1 | Highest Generation : |  |  | 10401 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 7337.1 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10401 | MW
| 3 | Day peak Generation : |  |  | 7789.9 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9960 | MW
| 4 | Evening peak Generation : |  |  | 10401 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 211.2418 | MKWHr | By Solar | 0.12975 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 124.2544 | MKWHr |  | By Oil: | 43.8096 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 15.2248 | MKWHr |  | By Hydro: | 2.7873 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2393 | MW | Dhaka | 3172 | 3172 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 1937 | MW | Chittagong | 1043 | 1043 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4330 | MW | Khulna | 1251 | 1251 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1047.39 | MMCFD |  |  | Rajshahi | 1086 | 1086 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 143031361.488 | ii) Oil : | Taka | 329984980.38 | Comilla | 995 | 995 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 70589677 | Total | Taka | 543606018.868 | Mymensingh | 889 | 889 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | #VALUE! | MKWHr. | Sylhet | 497 | 497 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 269 | MW (E to W) at | 21:00 | hrs | Barisal | 288 | 288 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 103 | MW at | 1:00 | hrs | Rangpur | 739 | 739 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 30° C |  |  | Total | 9960 | 9960 |  | 0
| B. |  | 2020-08-22 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 31.9° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 11500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14759 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 9200 | MW
| 4 | Reserve(Generation end) |  |  |  | 3259 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 233.5622 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7618 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.3164 | MKWHr. | ii) HVDC Flow at Peak Time |  | 930 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.7197 | MKWHr. | iii) Maximum HVDC Flow : |  | 931 | MW at | 9:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 93.41 |  | (b) Today: | 93.26 |  | (c) Rule Curve: |  | 95.72
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-08-21
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 28 | 0 | 0 | 110 | 0 | 95 | 69 | 137 | 354 |  | 0 | 420 | 138 | 93 | 94 | 55 | 178 | 0 | 0 | 0 | 100 | 7 | 16 | 39 | 0 | 0 | 41 | 53 | 55 | 35 | 19 | 25 | 27 | 25 | 33 | 0 | 0 | 88 | 35 | 0 | 0 | 0 | 164 | 0 | 103 | 0 |  | 0 | 0 | 0 | 0 | 97 | 50 | 18 | 28 | 0 | 80 | 0 | 255 | 250 | 196 | 8 | 86 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 25 | 21 | 128 | 124 | 81 | 17 | 0 | 60 | 30 | 47 | 46 | 130 | 207 | 64 | 83 | 0 | 80 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 300 | 0 | 0 | 193 | 0 | 131 | 0 | 100 | 0 | 0 | 0 | 115 | 70 | 0 | 0 | 234 | 0 | 0 | 0 | 57 | 100 | 0 | 90 |  | 930 | 0 | 155 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 0 | 89 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 157 | 0 | 79 | 0 | 150 | 0 | 413 | 0 | 0 | 35 | 0 | 113 | 0 | 0 | 109 | 480 |  | 6705 | 3342 | 10047 | 3026 | 930 | 2194 | 2700 | 630 | 123 | 316 | 128 | 0 | 0 | 93.42
2:00 | 28 | 0 | 0 | 110 | 0 | 95 | 69 | 137 | 338 |  | 0 | 390 | 140 | 93 | 94 | 55 | 184 | 0 | 0 | 0 | 100 | 7 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 0 | 19 | 25 | 27 | 25 | 33 | 0 | 0 | 88 | 35 | 0 | 0 | 0 | 164 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 64 | 0 | 18 | 28 | 0 | 80 | 0 | 255 | 250 | 195 | 8 | 92 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 25 | 18 | 128 | 142 | 81 | 17 | 0 | 60 | 30 | 47 | 46 | 130 | 208 | 64 | 83 | 0 | 80 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 300 | 0 | 0 | 193 | 0 | 131 | 0 | 100 | 0 | 0 | 0 | 95 | 52 | 0 | 0 | 234 | 0 | 0 | 0 | 56 | 100 | 0 | 90 |  | 930 | 0 | 200 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 0 | 89 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 148 | 0 | 79 | 0 | 150 | 0 | 415 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 109 | 470 |  | 6427 | 3250 | 9677 | 3088 | 930 | 2138 | 2419 | 619 | 123 | 232 | 128 | 0 | 0 | 93.42
3:00 | 28 | 0 | 0 | 110 | 0 | 95 | 69 | 137 | 355 |  | 0 | 420 | 150 | 93 | 94 | 0 | 198 | 0 | 0 | 0 | 100 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 27 | 25 | 33 | 0 | 0 | 88 | 35 | 0 | 0 | 0 | 164 | 0 | 110 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 29 | 0 | 80 | 0 | 255 | 250 | 201 | 8 | 80 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 25 | 18 | 128 | 142 | 81 | 17 | 0 | 60 | 30 | 47 | 46 | 130 | 214 | 64 | 83 | 0 | 80 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 200 | 0 | 0 | 202 | 0 | 131 | 0 | 100 | 0 | 0 | 0 | 65 | 52 | 0 | 0 | 234 | 0 | 0 | 0 | 18 | 100 | 0 | 90 |  | 930 | 0 | 225 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 0 | 90 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 163 | 0 | 78 | 0 | 166 | 0 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 450 |  | 6145 | 3097 | 9242 | 3164 | 930 | 2188 | 1919 | 590 | 123 | 200 | 128 | 0 | 0 | 93.42
4:00 | 28 | 0 | 0 | 110 | 0 | 95 | 69 | 137 | 336 |  | 0 | 360 | 143 | 94 | 94 | 0 | 168 | 0 | 0 | 0 | 100 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 27 | 25 | 33 | 0 | 0 | 80 | 35 | 0 | 0 | 0 | 164 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 29 | 0 | 80 | 0 | 255 | 250 | 208 | 8 | 90 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 25 | 18 | 128 | 142 | 81 | 17 | 0 | 60 | 30 | 47 | 46 | 130 | 205 | 64 | 83 | 0 | 80 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 200 | 0 | 0 | 202 | 0 | 133 | 0 | 100 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 0 | 100 | 0 | 90 |  | 930 | 0 | 225 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 0 | 89 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 166 | 0 | 78 | 0 | 150 | 0 | 403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 440 |  | 5908 | 3041 | 8949 | 3122 | 930 | 2103 | 1762 | 589 | 115 | 200 | 128 | 0 | 0 | 93.41
5:00 | 28 | 0 | 0 | 110 | 0 | 95 | 69 | 137 | 309 |  | 0 | 360 | 150 | 100 | 94 | 0 | 198 | 0 | 0 | 0 | 90 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 27 | 25 | 33 | 0 | 0 | 80 | 35 | 0 | 0 | 0 | 164 | 0 | 103 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 34 | 0 | 80 | 0 | 255 | 250 | 208 | 8 | 90 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 25 | 18 | 120 | 142 | 81 | 17 | 0 | 60 | 30 | 47 | 46 | 130 | 209 | 64 | 83 | 0 | 80 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 95 | 0 | 0 | 200 | 0 | 133 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 0 | 0 | 0 | 100 | 0 | 90 |  | 930 | 0 | 225 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 0 | 89 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 159 | 0 | 77 | 0 | 150 | 0 | 417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440 |  | 5727 | 3008 | 8735 | 3148 | 930 | 2080 | 1553 | 589 | 115 | 200 | 120 | 0 | 0 | 93.41
6:00 | 28 | 0 | 0 | 110 | 0 | 95 | 69 | 137 | 310 |  | 0 | 360 | 145 | 70 | 30 | 0 | 177 | 0 | 0 | 0 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 80 | 35 | 0 | 0 | 0 | 164 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 35 | 0 | 80 | 0 | 255 | 250 | 211 | 8 | 86 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 25 | 18 | 106 | 158 | 24 | 17 | 0.1 | 60 | 30 | 47 | 46 | 130 | 202 | 65 | 83 | 0 | 80 | 18 | 0 | 10 | 295 | 24 | 8 | 0 | 0 | 0 | 0 | 170 | 0 | 131 | 0.1 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 160 | 0 | 0 | 0 | 0 | 100 | 0 | 35 |  | 930 | 0 | 235 | 0 | 16 | 160 | 0 | 0 | 0 | 0 | 0 | 89 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 149 | 0 | 77 | 0 | 150 | 0 | 368 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 400 |  | 5283.2 | 2772.1 | 8055.3 | 3138 | 930 | 2033 | 1023 | 549 | 115 | 160 | 106 | 1.3 | 0 | 93.41
7:00 | 28 | 0 | 0 | 110 | 0 | 95 | 69 | 137 | 274 |  | 0 | 360 | 152 | 0 | 15 | 0 | 191 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 30 | 25 | 33 | 0 | 0 | 82 | 35 | 0 | 0 | 0 | 164 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 36 | 0 | 80 | 0 | 255 | 250 | 211 | 8 | 90 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 25 | 9 | 98 | 158 | 0 | 17 | 0.1 | 60 | 30 | 47 | 46 | 130 | 207 | 40 | 83 | 0 | 80 | 18 | 0 | 10 | 290 | 16 | 8 | 0 | 0 | 0 | 0 | 80 | 0 | 93 | 1.3 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 124 | 0 | 0 | 0 | 0 | 70 | 0 | 0 |  | 930 | 0 | 250 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 147 | 0 | 32 | 0 | 150 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 400 |  | 4833 | 2670.7 | 7503.7 | 3112 | 930 | 1934 | 641 | 549 | 117 | 120 | 98 | 2.7 | 0 | 93.4
8:00 | 28 | 0 | 0 | 110 | 0 | 95 | 68 | 137 | 274 |  | 0 | 360 | 140 | 0 | 15 | 0 | 174 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 30 | 25 | 33 | 0 | 0 | 84 | 35 | 0 | 0 | 0 | 164 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 34 | 0 | 80 | 0 | 255 | 250 | 211 | 8 | 81 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 25 | 9 | 94 | 160 | 0 | 17 | 0.3 | 60 | 30 | 47 | 46 | 130 | 201 | 40 | 30 | 0 | 80 | 18 | 0 | 10 | 290 | 16 | 8 | 0 | 0 | 0 | 0 | 80 | 0 | 71 | 4.4 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 124 | 0 | 0 | 0 | 0 | 70 | 0 | 0 |  | 930 | 0 | 250 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 150 | 0 | 33 | 0 | 150 | 0 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 400 |  | 4716.5 | 2651.2 | 7367.7 | 3086 | 930 | 1853 | 607 | 550 | 119 | 120 | 94 | 8.7 | 0 | 93.4
9:00 | 28 | 0 | 0 | 110 | 0 | 92 | 68 | 137 | 270 |  | 0 | 360 | 145 | 0 | 15 | 0 | 183 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 85 | 35 | 0 | 0 | 0 | 164 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 36 | 0 | 80 | 0 | 255 | 250 | 207 | 8 | 90 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 16 | 5 | 25 | 9 | 74 | 142 | 0 | 17 | 0.6 | 60 | 30 | 47 | 46 | 110 | 200 | 40 | 30 | 0 | 80 | 18 | 0 | 10 | 280 | 16 | 5 | 0 | 0 | 0 | 0 | 80 | 0 | 72 | 9.4 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 124 | 0 | 0 | 0 | 0 | 70 | 0 | 0 |  | 931 | 0 | 250 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 145 | 0 | 33 | 0 | 150 | 0 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 400 |  | 4669.7 | 2667.4 | 7337.1 | 3086 | 931 | 1839 | 603 | 550 | 120 | 120 | 74 | 14.1 | 0 | 93.4
10:00 | 28 | 0 | 0 | 110 | 0 | 86 | 68 | 137 | 300 |  | 0 | 360 | 135 | 0 | 15 | 0 | 183 | 0 | 0 | 0 | 1 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 25 | 33 | 0 | 0 | 87 | 35 | 0 | 0 | 0 | 164 | 0 | 106 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 27 | 0 | 80 | 0 | 245 | 240 | 192 | 8 | 86 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 16 | 5 | 25 | 15 | 70 | 142 | 0 | 17 | 0.8 | 60 | 30 | 47 | 43 | 110 | 196 | 40 | 60 | 0 | 80 | 18 | 0 | 10 | 295 | 16 | 5 | 0 | 0 | 0 | 0 | 96 | 0 | 80 | 11.9 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 156 | 0 | 0 | 0 | 0 | 70 | 0 | 10 |  | 929 | 0 | 250 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 149 | 0 | 33 | 0 | 165 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1 | 0 | 400 |  | 4749.5 | 2669.1 | 7418.6 | 3068 | 929 | 1878 | 660 | 550 | 122 | 120 | 70 | 21.6 | 0 | 93.39
11:00 | 28 | 0 | 0 | 110 | 0 | 85 | 67 | 135 | 300 |  | 0 | 360 | 140 | 7 | 15 | 0 | 183 | 0 | 0 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 21 | 25 | 33 | 0 | 0 | 88 | 35 | 0 | 0 | 0 | 164 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 26 | 0 | 80 | 0 | 245 | 235 | 193 | 8 | 92 | 25 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 0 | 25 | 15 | 84 | 141 | 0 | 17 | 0.7 | 60 | 30 | 44 | 42 | 110 | 196 | 40 | 83 | 0 | 80 | 18 | 0 | 10 | 280 | 8 | 5 | 0 | 25 | 0 | 0 | 120 | 0 | 104 | 8.9 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 159 | 0 | 0 | 0 | 0 | 70 | 0 | 17 |  | 930 | 0 | 250 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 145 | 0 | 33 | 0 | 200 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 400 |  | 4824.6 | 2728.8 | 7553.4 | 3061 | 930 | 1892 | 777 | 550 | 123 | 120 | 84 | 16.4 | 0 | 93.39
12:00 | 28 | 0 | 0 | 110 | 0 | 88 | 68 | 84 | 300 |  | 0 | 360 | 150 | 7 | 15 | 10 | 208 | 0 | 0 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 25 | 21 | 25 | 33 | 0 | 0 | 88 | 35 | 0 | 0 | 0 | 164 | 0 | 116 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 80 | 0 | 245 | 220 | 184 | 0 | 95 | 26 | 5 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 25 | 12 | 84 | 139 | 8 | 17 | 0.7 | 60 | 30 | 44 | 46 | 110 | 215 | 40 | 83 | 0 | 80 | 18 | 0 | 10 | 305 | 8 | 5 | 0 | 65 | 0 | 0 | 168 | 0 | 106 | 7.5 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 160 | 0 | 0 | 0 | 1 | 70 | 0 | 29 |  | 931 | 0 | 260 | 0 | 49 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 155 | 0 | 33 | 0 | 200 | 0 | 381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 420 |  | 4944.9 | 2845 | 7789.9 | 3070 | 931 | 1901 | 979 | 570 | 123 | 120 | 84 | 11.9 | 0 | 93.39
13:00 | 28 | 0 | 0 | 110 | 0 | 89 | 67 | 28 | 320 |  | 0 | 400 | 135 | 7 | 38 | 27 | 178 | 0 | 0 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 0 | 25 | 16 | 25 | 33 | 0 | 0 | 89 | 35 | 0 | 0 | 0 | 164 | 0 | 106 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 35 | 0 | 80 | 0 | 235 | 220 | 180 | 0 | 83 | 26 | 5 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 25 | 15 | 106 | 124 | 13 | 0 | 1.4 | 60 | 30 | 47 | 46 | 163 | 196 | 67 | 85 | 0 | 80 | 18 | 0 | 10 | 310 | 8 | 5 | 0 | 120 | 0 | 0 | 200 | 0 | 130 | 11.3 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 197 | 0 | 0 | 0 | 20 | 100 | 0 | 72 |  | 930 | 0 | 260 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 159 | 0 | 54 | 0 | 205 | 0 | 338 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 40 | 460 |  | 5267.4 | 2947 | 8214.4 | 2930 | 930 | 2017 | 1362 | 610 | 124 | 120 | 106 | 15.4 | 0 | 93.38
14:00 | 28 | 0 | 0 | 110 | 0 | 92 | 50 | 29 | 300 |  | 0 | 380 | 150 | 7 | 64 | 40 | 196 | 0 | 0 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 0 | 25 | 16 | 25 | 33 | 0 | 0 | 85 | 35 | 0 | 0 | 0 | 164 | 0 | 107 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 37 | 0 | 80 | 0 | 235 | 215 | 178 | 0 | 96 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 25 | 15 | 106 | 122 | 24 | 0 | 1.1 | 59 | 30 | 47 | 42 | 110 | 214 | 40 | 85 | 0 | 80 | 18 | 0 | 10 | 285 | 8 | 5 | 0 | 165 | 0 | 0 | 200 | 0 | 88 | 12.23 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 198 | 0 | 0 | 0 | 34 | 100 | 0 | 72 |  | 929 | 0 | 145 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 146 | 0 | 53 | 0 | 200 | 0 | 377 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 50 | 470 |  | 5192.03 | 2857 | 8049.03 | 2805 | 929 | 1920 | 1412 | 620 | 120 | 120 | 106 | 17.03 | 0 | 93.37
15:00 | 28 | 0 | 0 | 110 | 0 | 91 | 30 | 38 | 352 |  | 0 | 420 | 130 | 7 | 64 | 40 | 172 | 0 | 0 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 19 | 25 | 8 | 25 | 33 | 0 | 0 | 83 | 35 | 0 | 0 | 0 | 166 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 31 | 0 | 80 | 0 | 235 | 210 | 186 | 0 | 86 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 25 | 18 | 108 | 140 | 24 | 0 | 0.6 | 60 | 30 | 47 | 42 | 163 | 198 | 63 | 85 | 0 | 80 | 18 | 0 | 10 | 300 | 8 | 5 | 0 | 165 | 0 | 0 | 200 | 0 | 90 | 4.5 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | 198 | 0 | 0 | 0 | 34 | 100 | 0 | 72 |  | 930 | 0 | 145 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 171 | 0 | 33 | 0 | 204 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 470 |  | 5305.4 | 2872 | 8177.4 | 2842 | 930 | 2048 | 1384 | 620 | 118 | 120 | 108 | 7.4 | 0 | 93.36
16:00 | 28 | 0 | 0 | 110 | 0 | 85 | 30 | 143 | 353 |  | 0 | 420 | 135 | 51 | 64 | 40 | 164 | 0 | 0 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 19 | 25 | 7 | 25 | 33 | 0 | 0 | 80 | 35 | 0 | 0 | 0 | 164 | 0 | 103 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 35 | 0 | 80 | 0 | 235 | 210 | 181 | 0 | 86 | 3 | 5 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 16 | 18 | 106 | 155 | 24 | 0 | 0.8 | 60 | 30 | 47 | 20 | 130 | 198 | 64 | 40 | 0 | 80 | 18 | 0 | 10 | 270 | 16 | 2 | 0 | 132 | 0 | 0 | 130 | 0 | 122 | 4.39 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 105 | 0 | 0 | 0 | 17 | 70 | 0 | 70 |  | 930 | 0 | 75 | 0 | 35 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 179 | 0 | 35 | 0 | 180 | 0 | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 |  | 5060.29 | 2672 | 7732.29 | 2848 | 930 | 1902 | 1103 | 599 | 115 | 123 | 106 | 6.29 | 0 | 93.35
17:00 | 28 | 0 | 0 | 110 | 0 | 43 | 30 | 260 | 270 |  | 0 | 340 | 135 | 75 | 64 | 40 | 145 | 0 | 0 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 16 | 25 | 33 | 0 | 0 | 80 | 35 | 0 | 0 | 0 | 164 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 35 | 0 | 80 | 0 | 235 | 220 | 181 | 0 | 86 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 25 | 18 | 100 | 156 | 24 | 0 | 0.5 | 60 | 30 | 22 | 20 | 110 | 198 | 40 | 20 | 0 | 80 | 18 | 0 | 10 | 275 | 16 | 2 | 0 | 115 | 0 | 0 | 130 | 0 | 99 | 4.4 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 86 | 0 | 0 | 0 | 17 | 70 | 0 | 54 |  | 930 | 0 | 75 | 0 | 32 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 151 | 0 | 35 | 0 | 150 | 0 | 392 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 410 |  | 4793.1 | 2592.5 | 7385.6 | 2863 | 930 | 1653 | 1032 | 559 | 115 | 128 | 100 | 5.6 | 0 | 93.34
18:00 | 28 | 0 | 0 | 110 | 0 | 43 | 30 | 330 | 270 |  | 0 | 340 | 130 | 75 | 64 | 40 | 145 | 0 | 0 | 0 | 7 | 7 | 0 | 1 | 0 | 0 | 0 | 17 | 0 | 15 | 19 | 25 | 16 | 25 | 33 | 0 | 0 | 81 | 35 | 0 | 0 | 0 | 164 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 2 | 0 | 18 | 39 | 0 | 80 | 0 | 235 | 220 | 202 | 0 | 85 | 6 | 5 | 0 | 0 | 0 | 0 | 1 | 21 | 8 | 25 | 18 | 104 | 154 | 24 | 0 | 0 | 60 | 30 | 22 | 20 | 110 | 196 | 40 | 20 | 0 | 80 | 18 | 0 | 10 | 270 | 16 | 5 | 0 | 115 | 0 | 0 | 130 | 0 | 100 | 0.35 | 80 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 19 | 50 | 0 | 54 |  | 930 | 0 | 305 | 0 | 32 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 19 | 16 | 0 | 0 | 0 | 0 | 5 | 8 | 0 | 0 | 0 | 0 | 12 | 21 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 152 | 0 | 34 | 0 | 150 | 0 | 274 | 0 | 0 | 0 | 0 | 8 | 0 | 0.1 | 15 | 400 |  | 4901.35 | 2755.1 | 7656.45 | 3183 | 930 | 1538 | 1091 | 549 | 116 | 145 | 104 | 0.45 | 0 | 93.33
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 28 | 0 | 0 | 110 | 0 | 86 | 30 | 351 | 356 |  | 0 | 400 | 120 | 75 | 70 | 43 | 146 | 0 | 0 | 0 | 7 | 94 | 36 | 20 | 0 | 0 | 6 | 20 | 17 | 17 | 19 | 25 | 16 | 25 | 33 | 0 | 0 | 82 | 35 | 0 | 0 | 4 | 164 | 0 | 105 | 0 |  | 0 | 0 | 85 | 0 | 31 | 10 | 18 | 39 | 0 | 80 | 0 | 235 | 220 | 211 | 0 | 85 | 6 | 5 | 0 | 0 | 0 | 50 | 20 | 21 | 8 | 25 | 21 | 136 | 158 | 64 | 0 | 0 | 60 | 30 | 47 | 30 | 163 | 197 | 65 | 83 | 0 | 80 | 18 | 0 | 10 | 275 | 24 | 8 | 0 | 225 | 0 | 0 | 156 | 0 | 123 | 0 | 100 | 0 | 0 | 0 | 34 | 17 | 0 | 0 | 215 | 0 | 0 | 17 | 55 | 100 | 0 | 76 |  | 930 | 0 | 365 | 0 | 115 | 130 | 0 | 0 | 0 | 0 | 40 | 89 | 25 | 64 | 0 | 0 | 0 | 50 | 35 | 91 | 0 | 0 | 31 | 26 | 32 | 21 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 158 | 0 | 63 | 0 | 163 | 0 | 343 | 0 | 0 | 16 | 0 | 50 | 0 | 0 | 70 | 420 |  | 6276 | 3498 | 9774 | 3378 | 930 | 1987 | 2117 | 569 | 117 | 540 | 136 | 0 | 0 | 93.32
19:30 | 28 | 0 | 0 | 110 | 0 | 92 | 70 | 342 | 358 |  | 0 | 370 | 135 | 100 | 80 | 30 | 145 | 0 | 0 | 0 | 7 | 94 | 64 | 0 | 0 | 0 | 0 | 53 | 35 | 17 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 82 | 35 | 0 | 0 | 0 | 164 | 0 | 104 | 0 |  | 0 | 0 | 85 | 0 | 26 | 10 | 18 | 40 | 0 | 80 | 0 | 240 | 220 | 216 | 0 | 85 | 6 | 5 | 0 | 0 | 0 | 0 | 25 | 21 | 11 | 25 | 21 | 138 | 156 | 90 | 0 | 0 | 60 | 30 | 47 | 46 | 163 | 199 | 65 | 83 | 0 | 80 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 285 | 0 | 0 | 200 | 0 | 133 | 0 | 100 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 56 | 100 | 0 | 91 |  | 931 | 0 | 345 | 0 | 16 | 150 | 0 | 0 | 0 | 0 | 40 | 89 | 25 | 48 | 0 | 0 | 0 | 50 | 35 | 100 | 0 | 0 | 38 | 25 | 32 | 21 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 198 | 0 | 76 | 30 | 212 | 0 | 380 | 0 | 0 | 50 | 0 | 101 | 0 | 0 | 90 | 470 |  | 6551 | 3717 | 10268 | 3457 | 931 | 2087 | 2365 | 619 | 117 | 554 | 138 | 0 | 0 | 0
20:00 | 28 | 0 | 0 | 110 | 0 | 96 | 68 | 338 | 358 |  | 0 | 370 | 130 | 93 | 77 | 30 | 146 | 0 | 0 | 0 | 7 | 94 | 64 | 0 | 0 | 0 | 0 | 53 | 17 | 17 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 84 | 35 | 0 | 0 | 0 | 164 | 0 | 103 | 0 |  | 0 | 0 | 68 | 0 | 26 | 0 | 18 | 39 | 0 | 80 | 0 | 250 | 220 | 216 | 0 | 86 | 6 | 5 | 0 | 0 | 0 | 0 | 25 | 21 | 11 | 25 | 21 | 136 | 158 | 91 | 17 | 0 | 60 | 30 | 47 | 46 | 163 | 194 | 65 | 85 | 0 | 80 | 18 | 0 | 10 | 275 | 16 | 8 | 0 | 285 | 0 | 0 | 200 | 0 | 133 | 0 | 100 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 56 | 100 | 0 | 91 |  | 930 | 0 | 345 | 0 | 49 | 150 | 0 | 0 | 0 | 0 | 40 | 89 | 27 | 48 | 0 | 0 | 0 | 50 | 35 | 100 | 0 | 0 | 47 | 25 | 26 | 21 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 199 | 0 | 79 | 22 | 215 | 0 | 345 | 0 | 0 | 68 | 0 | 94 | 0 | 0 | 109 | 480 |  | 6494 | 3764 | 10258 | 3480 | 930 | 2045 | 2379 | 629 | 119 | 540 | 136 | 0 | 0 | 93.32
21:00 | 28 | 0 | 0 | 110 | 0 | 98 | 72 | 335 | 358 |  | 0 | 420 | 140 | 100 | 80 | 30 | 146 | 0 | 0 | 0 | 7 | 94 | 64 | 0 | 0 | 0 | 0 | 53 | 17 | 17 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 84 | 35 | 0 | 0 | 0 | 164 | 0 | 107 | 0 |  | 0 | 0 | 68 | 0 | 21 | 0 | 16 | 42 | 0 | 80 | 0 | 260 | 220 | 216 | 0 | 93 | 6 | 5 | 0 | 0 | 0 | 0 | 25 | 21 | 11 | 25 | 21 | 136 | 158 | 91 | 17 | 0 | 60 | 30 | 47 | 46 | 163 | 197 | 64 | 83 | 0 | 79 | 18 | 0 | 10 | 290 | 16 | 8 | 0 | 286 | 0 | 0 | 200 | 0 | 133 | 0 | 100 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 56 | 100 | 0 | 90 |  | 930 | 0 | 345 | 0 | 83 | 150 | 0 | 0 | 0 | 0 | 40 | 90 | 29 | 32 | 0 | 0 | 0 | 50 | 0 | 100 | 0 | 0 | 44 | 25 | 26 | 22 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 199 | 0 | 80 | 30 | 220 | 0 | 383 | 0 | 0 | 70 | 0 | 85 | 0 | 0 | 109 | 510 |  | 6578 | 3823 | 10401 | 3503 | 930 | 2159 | 2393 | 659 | 119 | 502 | 136 | 0 | 0 | 93.31
22:00 | 28 | 0 | 0 | 110 | 0 | 98 | 72 | 333 | 358 |  | 0 | 420 | 130 | 100 | 80 | 30 | 145 | 0 | 0 | 0 | 7 | 94 | 64 | 0 | 0 | 0 | 0 | 53 | 17 | 17 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 85 | 35 | 0 | 0 | 0 | 164 | 0 | 103 | 0 |  | 0 | 0 | 68 | 0 | 25 | 0 | 18 | 42 | 0 | 80 | 0 | 260 | 220 | 216 | 8 | 87 | 6 | 5 | 0 | 0 | 0 | 0 | 25 | 21 | 11 | 25 | 21 | 134 | 104 | 91 | 17 | 0 | 60 | 30 | 47 | 46 | 130 | 197 | 64 | 85 | 0 | 80 | 18 | 0 | 10 | 290 | 16 | 8 | 0 | 286 | 0 | 0 | 200 | 0 | 132 | 0 | 90 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 56 | 100 | 0 | 90 |  | 929 | 0 | 340 | 0 | 115 | 150 | 0 | 0 | 0 | 0 | 40 | 90 | 29 | 16 | 0 | 0 | 0 | 50 | 0 | 100 | 0 | 0 | 44 | 25 | 25 | 22 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 182 | 0 | 80 | 30 | 216 | 0 | 366 | 0 | 0 | 70 | 0 | 84 | 0 | 0 | 109 | 510 |  | 6473 | 3793 | 10266 | 3413 | 929 | 2119 | 2391 | 659 | 120 | 501 | 134 | 0 | 0 | 93.3
23:00 | 28 | 0 | 0 | 110 | 0 | 98 | 72 | 333 | 356 |  | 0 | 390 | 135 | 100 | 91 | 30 | 145 | 0 | 0 | 0 | 7 | 7 | 64 | 0 | 0 | 0 | 0 | 53 | 17 | 17 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 88 | 35 | 0 | 0 | 0 | 164 | 0 | 104 | 0 |  | 0 | 0 | 68 | 0 | 20 | 0 | 18 | 32 | 0 | 80 | 0 | 260 | 225 | 215 | 8 | 96 | 6 | 5 | 0 | 10 | 0 | 0 | 25 | 21 | 11 | 25 | 21 | 134 | 105 | 91 | 17 | 0 | 60 | 30 | 47 | 46 | 130 | 206 | 64 | 85 | 0 | 80 | 18 | 0 | 10 | 290 | 16 | 8 | 0 | 286 | 0 | 0 | 200 | 0 | 131 | 0 | 90 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 57 | 100 | 0 | 90 |  | 930 | 0 | 345 | 0 | 99 | 130 | 0 | 0 | 0 | 0 | 40 | 90 | 29 | 16 | 0 | 0 | 0 | 50 | 0 | 100 | 0 | 0 | 38 | 25 | 25 | 22 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 164 | 0 | 79 | 0 | 160 | 0 | 401 | 0 | 0 | 70 | 0 | 85 | 0 | 0 | 109 | 480 |  | 6392 | 3659 | 10051 | 3368 | 930 | 2121 | 2270 | 630 | 123 | 475 | 134 | 0 | 0 | 93.29
24:00 | 28 | 0 | 0 | 110 | 0 | 98 | 71 | 338 | 358 |  | 0 | 390 | 125 | 100 | 94 | 30 | 145 | 0 | 0 | 0 | 7 | 7 | 48 | 0 | 0 | 0 | 0 | 53 | 17 | 17 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 88 | 35 | 0 | 0 | 0 | 164 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 21 | 0 | 18 | 32 | 0 | 80 | 0 | 260 | 225 | 214 | 8 | 87 | 6 | 5 | 0 | 15 | 0 | 0 | 25 | 21 | 11 | 25 | 21 | 134 | 105 | 91 | 17 | 0 | 60 | 30 | 47 | 46 | 130 | 200 | 65 | 85 | 0 | 80 | 18 | 0 | 10 | 290 | 16 | 8 | 0 | 286 | 0 | 0 | 200 | 0 | 132 | 0 | 100 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 56 | 100 | 0 | 90 |  | 931 | 0 | 345 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 90 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 37 | 25 | 25 | 22 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 163 | 0 | 78 | 0 | 160 | 0 | 358 | 0 | 0 | 70 | 0 | 88 | 0 | 0 | 109 | 480 |  | 6308 | 3572 | 9880 | 3357 | 931 | 2082 | 2293 | 630 | 123 | 330 | 134 | 0 | 0 | 93.28
KWH | 597000 | 0 | 0 | 2709000 | 0 | 2073136 | 1422176 | 4607952 | 7674000 |  | 0 | 9145000 | 3386269 | 1415040 | 1500456 | 585388 | 4262529 | 0 | 0 | 0 | 657600 | 495648 | 375360 | 73359 | 0 | 0 | 82608 | 705600 | 322972 | 178380 | 277308 | 600000 | 553500 | 705400 | 819700 | 0 | 0 | 1979290 | 808000 | 0 | 0 | 6435 | 3910618 | 0 | 2435973 | 0 |  | 0 | 0 | 356575 | 0 | 318720 | 76800 | 436032 | 686000 | 0 | 1919630 | 0 | 6089300 | 5674000 | 4847000 | 117090 | 2113620 | 423288 | 138240 | 0 | 638673 | 0 | 37048 | 156634 | 456480 | 196200 | 604200 | 436290 | 2719680 | 3293760 | 1151040 | 266472 | 9050 | 1428000 | 726360 | 1065000 | 1022904 | 3310118 | 4654000 | 1346016 | 1703040 | 0 | 1941110 | 429000 | 0 | 246600 | 7218000 | 393888 | 150000 | 0 | 3843926 | 0 | 0 | 4063200 | 0 | 2767680 | 81135 | 2163840 | 0 | 0 | 0 | 651600 | 245460 | 0 | 27601 | 4458655 | 0 | 0 | 18240 | 655200 | 2148480 | 0 | 1480320 |  | 22316364 | 0 | 5909760 | 0 | 1458240 | 3562560 | 0 | 0 | 0 | 0 | 223875 | 2186777 | 475524 | 212160 | 0 | 0 | 0 | 241403 | 75316 | 728120 | 0 | 0 | 190110 | 139200 | 145423 | 438000 | 272088 | 177714 | 0 | 0 | 3643500 | 0 | 0 | 0 | 0 | 4080273 | 0 | 1362068 | 100800 | 4635273 | 0 | 8953272 | 14400 | 0 | 467040 | 0 | 754560 | 0 | 11966 | 1117824 | 11581300 |  | 135766892 | 75474910 | 211241802 | 76293423 | 22316364 | 47960929 | 38097649 | 15224800 | 2787290 | 5711915 | 2719680 | 129752 | 0
Fuel Cost | 979080 | 0 | 0 | 3982230 | 0 | 2736539.52 | 2417699.2 | 4654031.52 | 7904220 |  | 0 | 9968050 | 3758758.59 | 10740153.6 | 10338141.84 | 4952382.48 | 4433030.16 | 0 | 0 | 0 | 4951728 | 4520309.76 | 3693542.4 | 676369.98 | 0 | 0 | 750906.72 | 5150880 | 2496573.56 | 1758826.8 | 207981 | 450000 | 0 | 0 | 0 | 0 | 0 | 534408.3 | 218160 | 0 | 0 | 59781.15 | 4262573.62 | 0 | 4141154.1 | 0 |  | 0 | 0 | 3458777.5 | 0 | 2772864 | 608256 | 549400.32 | 2037420 | 0 | 2841052.4 | 0 | 4506082 | 5674000 | 4459240 | 151046.1 | 2430663 | 478315.44 | 193536 | 0 | 1092130.83 | 0 | 374184.8 | 1495854.7 | 579729.6 | 147150 | 1057350 | 327217.5 | 20397600 | 3491385.6 | 10451443.2 | 338419.44 | 144257 | 2341920 | 1162176 | 1895700 | 1595730.24 | 3773534.52 | 4840160 | 2651651.52 | 3252806.4 | 0 | 3358120.3 | 939510 | 0 | 503064 | 7290180 | 295416 | 114000 | 0 | 29060080.56 | 0 | 0 | 21128640 | 0 | 27233971.2 | 948468.15 | 17635296 | 0 | 0 | 0 | 5942592 | 2319597 | 0 | 0 | 33707431.8 | 0 | 0 | 182035.2 | 5615064 | 14308876.8 | 0 | 0 |  | 128542256.64 | 0 | 6205248 | 0 | 11461766.4 | 49377081.6 | 0 | 0 | 0 | 0 | 2332777.5 | 2471058.01 | 737062.2 | 2070681.6 | 0 | 0 | 0 | 2375405.52 | 765210.56 | 6443862 | 0 | 0 | 1842165.9 | 1348848 | 1410603.1 | 840960 | 421736.4 | 134529.498 | 0 | 0 | 19747770 | 0 | 0 | 0 | 0 | 5385960.36 | 0 | 2043102 | 1714608 | 5423269.41 | 0 | 8863739.28 | 150336 | 0 | 4432209.6 | 0 | 5855385.6 | 0 | 132224.3 | 8260719.36 | 50841907 |  | 362890909.42 | 331632483.838 | 694523393.258 | 85313104.798 | 128542256.64 | 57718256.69 | 260244147 | 70589677 | 752568.3 | 69740833.38 | 20397600 | 1224949.45 | 0
Yesterday Day Peak | 28 | 0 | 0 | 110 | 0 | 88 | 68 | 84 | 300 |  | 0 | 360 | 150 | 7 | 15 | 10 | 208 | 0 | 0 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 25 | 21 | 25 | 33 | 0 | 0 | 88 | 35 | 0 | 0 | 0 | 164 | 0 | 116 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 80 | 0 | 245 | 220 | 184 | 0 | 95 | 26 | 5 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 25 | 12 | 84 | 139 | 8 | 17 | 0.7 | 60 | 30 | 44 | 46 | 110 | 215 | 40 | 83 | 0 | 80 | 18 | 0 | 10 | 305 | 8 | 5 | 0 | 65 | 0 | 0 | 168 | 0 | 106 | 7.5 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 160 | 0 | 0 | 0 | 1 | 70 | 0 | 29 |  | 931 | 0 | 260 | 0 | 49 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 155 | 0 | 33 | 0 | 200 | 0 | 381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 420 |  | 7789.9 | DayPeak
Yesterday Evening Peak | 28 | 0 | 0 | 110 | 0 | 98 | 72 | 335 | 358 | 0 | 0 | 420 | 140 | 100 | 80 | 30 | 146 | 0 | 0 | 0 | 7 | 94 | 64 | 0 | 0 | 0 | 0 | 53 | 17 | 17 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 84 | 35 | 0 | 0 | 0 | 164 | 0 | 107 | 0 | 0 | 0 | 0 | 68 | 0 | 21 | 0 | 16 | 42 | 0 | 80 | 0 | 260 | 220 | 216 | 0 | 93 | 6 | 5 | 0 | 0 | 0 | 0 | 25 | 21 | 11 | 25 | 21 | 136 | 158 | 91 | 17 | 0 | 60 | 30 | 47 | 46 | 163 | 197 | 64 | 83 | 0 | 79 | 18 | 0 | 10 | 290 | 16 | 8 | 0 | 286 | 0 | 0 | 200 | 0 | 133 | 0 | 100 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 56 | 100 | 0 | 90 |  | 930 | 0 | 345 | 0 | 83 | 150 | 0 | 0 | 0 | 0 | 40 | 90 | 29 | 32 | 0 | 0 | 0 | 50 | 0 | 100 | 0 | 0 | 44 | 25 | 26 | 22 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 199 | 0 | 80 | 30 | 220 | 0 | 383 | 0 | 0 | 70 | 0 | 85 | 0 | 0 | 109 | 510 |  | 10401 | EvPeak
Forecast for Evening | 28 | 0 | 0 | 110 | 0 | 100 | 70 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 210 | 0 | 0 | 0 | 100 | 94 | 149 | 100 | 0 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 50 | 0 | 84 | 35 | 0 | 0 | 25 | 165 | 0 | 105 | 0 | 0 | 0 |  | 100 | 100 | 97 | 50 | 18 | 30 | 0 | 80 | 0 | 360 | 360 | 220 | 8 | 90 | 26 | 5 | 0 | 51 | 0 | 50 | 43 | 18 | 11 | 25 | 21 | 173 | 160 | 80 | 17 | 0 | 60 | 30 | 51 | 44 | 163 | 210 | 66 | 86 | 0 | 80 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 115 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 0 | 300 | 54 | 110 | 114 | 60 | 100 | 0 | 104 |  | 941 | 16 | 410 | 0 | 115 | 220 | 0 | 0 | 30 | 60 | 40 | 90 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 0 | 50 | 40 | 43 | 30 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 10 | 0 | 0 | 220 | 0 | 80 | 100 | 220 | 0 | 414 | 90 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 660
Forecast for Day | 28 | 0 | 0 | 110 | 0 | 100 | 70 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 210 | 0 | 0 | 0 | 100 | 90 | 149 | 100 | 0 | 0 | 49 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 35 | 0 | 84 | 35 | 0 | 0 | 25 | 165 | 0 | 105 | 0 | 0 | 0 |  | 100 | 100 | 97 | 50 | 18 | 30 | 0 | 80 | 0 | 20 | 250 | 220 | 8 | 90 | 26 | 5 | 0 | 51 | 0 | 0 | 43 | 18 | 11 | 25 | 21 | 163 | 160 | 80 | 17 | 1.6 | 60 | 30 | 51 | 44 | 163 | 210 | 61 | 86 | 0 | 80 | 18 | 0 | 10 | 341 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 80 | 115 | 20 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 5 | 300 | 50 | 50 | 114 | 60 | 100 | 0 | 104 |  | 941 | 0 | 350 | 0 | 115 | 150 | 0 | 0 | 0 | 0 | 40 | 90 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 50 | 0 | 43 | 0 | 18 | 10 | 10 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 |  | 80 | 60 | 220 | 0 | 414 | 90 | 0 | 113 | 100 | 113 | 0 | 8 | 113 | 500
Generation at 08:00(Today) | 28 | 0 | 0 | 110 | 0 | 98 | 70 | 341 | 311 | 0 | 0 | 320 | 150 |  | 60 | 0 | 132 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 28 | 25 | 33 | 0 | 0 | 87 | 35 | 0 | 0 | 0 | 164 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 0 | 80 | 0 | 245 | 0 | 200 | 80 | 94 | 29 | 45 | 0 | 32 | 0 | 0 | 0 | 21 | 8 | 25 | 15 | 102 | 105 | 0 | 17 | 0.3 | 60 | 30 | 44 | 46 | 130 | 196 | 64 | 20 | 0 | 80 | 18 | 0 | 10 | 305 | 24 | 0 | 0 | 145 | 0 | 0 | 200 | 0 | 81 | 4.9 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 52 | 0 | 0 | 0 | 36 | 10 | 0 | 90 | 0 | 931 | 0 | 295 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 160 | 0 | 54 | 0 | 130 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 400 | 0
199
| Minimum Generation |  | 7337.1 | 9:00
| Highest Generation |  | 10401 | 21:00
| Day Peak Generation |  | 7789.9 | 12:00
| Evening Peak Generation |  | 10401 | 21:00
| HVDC Max Flow |  | 931 | 9:00
| HVDC EvPeak Flow |  | 930 | 21:00
| Load factor L.F |  | 84.62%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-08-22
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-08-21 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7789.9 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 7618 | MW
Evening Peak Generation : |  | 10401 | MW Hour : | 21:00 | Available Max Generation : |  | 14759 | MW
E.P. Demand (at gen end) : |  | 10401 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 11500 | MW
Maximum Generation : |  | 10401 | MW Hour : | 21:00 | Reserve(Generation end) |  | 3259 | MW
Total Gen. (MKWH) : |  | 211.2418 | System Load Factor : | 84.62% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 103 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-08-22
Actual : | 93.26 | Ft.(MSL) , | Rule curve : | 95.72 | Ft.( MSL )
Gas Consumed : | Total = | 1047.39 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 143031361.488
: |  | Coal : | 70589677 | Oil : | 329984980.38 | Total : | 543606018.868
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4098.0012 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1394.6351 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1249.7407 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1129.315 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1020.5076 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 823.5163 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 459.0698 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 211.9963 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 635.1434 |  |  | 0 | 0%
Total | 0 |  | 11021.9253 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Bibiyana #3
3) Ghorasal Unit-2,3,4,7
4) Ashuganj unit-3,5
5) Bhola-225 MW GT-2 & ST
6) Kaptai-2
7) Raozan #1,2
8) Sirajganj #1
9) Baghabari-71 & 100 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Sylhet 132/33 kV T1 transformer & its associated 33 kV breaker were under shut down from 07:58 to 11:58 |  |  |  |  | About 30 MW power interruption occurred under Sylhet S/S area
for C/M. |  |  |  |  | from 07:58 to 11:58.
b) Bhulta 132/33 kV T1 transformer was under shut down from 08:11 to17:12 for C/M.
c) Kaptai Unit-4 was force shut down at 09:08 due to Oil leakage.
d) Kaptai Unit-5 was synchronized at 09:58.
e) Rangpur-Rangpur Confidence 132 MW kV Ckt-2 was under shut down from 10:33 to 12:37 for C/M.
f) Midland 51 MW, Modular 195 MW & Midland 150 MW 230 kV line were isolated from 12:30 to 21:16 for
230 kV loop from AIS-GIS Y-phase R/H maintenance.
g) Haripur-Bhulta 132 kV Ckt was released at 12:06 to attend R/H at Haripur Bay at Bhulta S/S and was closed at 13:50.
h) Rangpur-Rangpur Confidence 132 MW kV Ckt-2 was under shut down from 20:08 to 23:29 due to Oil leakage |  |  |  |  | About 05 MW power interruption occurred under Rangpur S/S area
at CT(Y-Phase) of Rangpur S/S end. |  |  |  |  | from 20:08 to 23:29.
i) Haripur 412 MW CCPP ST was synchronized at 14:50.
j) Bheramara 410 MW CCPP ST was synchronized at 17:08.
k) Rangpur 132/33 kV T1 transformer was under shut down from 14:20 to15:45 for C/M.
l) Barapukuria 132/33 kV T4 transformer tripped at 21:34 showing lock out.
m) Barishal-Patuakhali 132 kV Ckt tripped at 21:47 from Barishal end showing Dist. Z2, L-3, E/F and was
switched on at 22:30
n) Ashuganj-Sirajganj 230 kV Ckt-1 tripped at 22:56 from both ends showing Dist. R, ST, Z1 at both ends.
o) Ashuganj North, Ashuganj South, Ashuganj Unit-4, Midland 51, Ashuganj Modular, Ashuganj TSK tripped |  |  |  |  | Total 408 MW(Ashuganj North-260 MW, Ashuganj South ST-45, Midland-
at 00:20(22/08/2020) as Ashuganj 230 kV Bus-2, Ashuganj OAT12 transformer, Ashuganj South-Ashuganj |  |  |  |  | 15 MW, Modular-8 MW, Ashuganj unit-4 80MW) Generation Out.
230 kV Ckt-1, Ashuganj-Cumilla(N) 230 kV Ckt-1 tripped.
p) Ashuganj 230 kV Bus-2 tripped at 00:20(22/08/2020) showing general Protection trip and was | [6 empty] | 408
switched on at 03:05(22/08/2020).
q) Ashuganj AOT12 transformer tripped at 00:20(22/08/2020) showing Master trip, Protection trip.
r) Ashuganj South-Ashuganj 230 kv Ckt-1 tripped at 00:20(22/08/2020).
s) Ashuganj-Cumilla(N) 230 kv Ckt-1 tripped at 00:20(22/08/2020).
t) Ashuganj South GT tripped at 00:56(22/08/2020).
u) Ashuganj North GT was synchronized at 02:39(22/08/2020).
v) Rangamati-Chandraghona 132 kV Ckt-1 tripped at 03:38(22/08/2020) from Rangamati end showing Dist.
Y-phase, Z1 and was switched on at 03:49(22/08/2020).
w) Hathazari-Kaptai 132 kV Ckt-1&2 tripped at 03:36(22/08/2020) from both ends showing Dist. 3-phase
and were switched on at 04:30(22/08/2020).
x) Ghorashal-Ashuganj(S) 230 kV Ckt-2 tripped at 03:46(22/08/2020) from both ends showing Dist. Z1 at Ghorashal
end & Dist Z1, E/F at Ashuganj(S) end and was switched on at 05:04(22/08/2020) & again tripped.
y) Ashuganj unit-4 was synchronized at 06:29(22/08/2020).
z) Khulshi 132 kV main Bus was under shut down from 03:56(22/08/2020) to 09:50(22/08/2020) for project work. |  |  |  |  | About 60 MW power interruption occurred under Khulshi S/S area
from 03:56(22/8/2020) to 09:50(22/08/2020).
aa) Polashbari 132/33 kV T2 transformer was under shut down from 07:08(22/08/2020) to 09:36(22/08/2020). |  |  |  |  | About 18 MW power interruption occurred under Polashbari S/S area
from 07:08(22/8/2020) to 09:36(22/08/2020).
ab) Shahjibazar 132/33 kV T2 transformer was shut down at 07:27(22/08/2020) for C/M. |  |  |  |  | About 20 MW power interruption has been occurring under Shahjibazar S/S
area since 07:27(22/08/2020).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-08-21 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 28 | 597000 | Unit-1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 110 | 2709000 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 72 | 1422176 | Engine problem
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 98 | 2073136 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 335 | 4607952 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 358 | 7674000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9145000 | Frequency control.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 1415040
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 140 | 3386269 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 80 | 1500456 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 30 | 585388 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 73359 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 277308
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 7 | 657600 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 146 | 4262529 | STG under maintenance
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 94 | 495648
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 82608 | Reserve
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 705600
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 64 | 375360 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 322972 | Low demand
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 178380 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1153500 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 705400 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 819700
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 286 | 3843926
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 133 | 2767680 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 245460 | Reserve
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 1480320 | Engine problem
| Dhaka area Total |  |  |  | 5895 | 2810 | 53562767
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 6435 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 81135
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 76800 | Reserve
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 119 | 2787290 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 164 | 3910618
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 107 | 2435973 | Gas shortage.
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 356575
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2163840
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 436032 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 686000
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 21 | 318720 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27601
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 234 | 4458655 | Transformer over load
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2148480
| Chattogram area Total |  |  |  | 2266 | 971 | 19894154
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 80 | 1919630 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 216 | 4847000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 260 | 6089300 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 220 | 5674000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 6 | 423288 | Gas shortage.
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 138240 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 117090 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 638673 | Line problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Reserve
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 37048 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 93 | 2113620 | ST under maint.
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 456480
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 196200
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 136 | 2719680
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 604200 | Engine problem
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 25 | 156634 | Low demand
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 436290
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 18240 | Reserve
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 56 | 655200 | Engine problem
| Cumilla Area Total |  |  |  | 2980 | 1175 | 27240813
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 158 | 3293760 | Engine problem
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 266472 | Engine problem
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 91 | 1151040
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9050
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 4063200 | Low demand
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 45 | 651600 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 511 | 9435122
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1428000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 726360 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3310118
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 197 | 4654000 | ST under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 47 | 1065000
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 46 | 1022904
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 150000 | Engine problem
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 64 | 1346016 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1703040
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 79 | 1941110 | Engine problem
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 429000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 393888
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7218000 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 246600
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1111 | 25634036
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 930 | 22316364
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 83 | 1458240 | Engine problem
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 150 | 3562560 | Low demand
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 345 | 5909760 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 223875
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 30 | 100800 | Low demand
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 14400 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Engine problem
| Khulna Area Total |  |  |  | 2284 | 1578 | 33585999
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 212160 | Low demand
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 29 | 475524
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 90 | 2186777 | GT-2 Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 80 | 1362068 | Engine problem
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 510 | 11581300 | Over load
| Barisal Area Total |  |  |  | 1054 | 741 | 15817829
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 241403
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 75316
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 44 | 190110
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage.
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 199 | 4080273 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 220 | 4635273 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 383 | 8953272 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 26 | 145423
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 438000
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 11 | 272088
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 177714
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 25 | 139200 | Low demand
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 728120
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 70 | 467040 | Low demand
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 1117824
| Rajshahi Area Total |  |  |  | 2183 | 1270 | 21661056
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 149 | 3643500 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 85 | 754560 | Low demand
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 11966
| Rangpur Area Total |  |  |  | 605 | 234 | 4410026
| Total |  |  |  | 19892 | 10401 | 211241802
| Eastern Grid Total |  |  |  | 13766 | 6578 | 135766892
| Western Grid Total |  |  |  | 6126 | 3823 | 75474910
| National Grid Total |  |  |  | 19892 | 10401 | 211241802
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-08-21
| (a) ENTIRE EASTERN GRID : |  | 6596 | MW | (b) ENTIRE WESTERN GRID : |  | 3364 | MW
| i) Dhaka area |  | 3172 | MW | i) Khulna area |  | 1251 | MW
| ii) Chittagong area |  | 1043 | MW | ii) Rajshahi area |  | 1086 | MW
| iii) Comilla area |  | 995 | MW | iii) Barisal area |  | 288 | MW
| iv) Mymensingh area |  | 889 | MW | iv) Rangpur area |  | 739 | MW
| v) Sylhet area |  | 497 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 9960 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 98 | 23:00 | Sherpur | 104 | 19:30 | Jhenida | 94 | 19:00
| Munsiganj | 102 | 21:00 | Srimongal | 54 | 20:00 | Bottail | 104 | 1:00
| Sonargaon | 74 | 1:00 | Shahjibazar | 115 | 21:00 | G.K Project | 50 | 20:00
| Shyampur | 198 | 9:00 | Fenchuganj | 43 | 19:00 | Faridpur | 165 | 0.875
| Bhulta | 176 | 1:00 | Kulawara | 35 | 19:30 | Madaripur | 83 | 0.91667
| Madanganj | 43 | 1:00 | Sylhet | 123 | 20:00 | Sariatpur | 56 | 22:00
| Shitalakhya | 74 | 1:00 | Chatak | 28 | 21:00 | Gopalganj | 85 | 20:00
| Rahim steel | 8 | 1:00 | Sunamganj | 42 | 19:30 | Bagerhat | 78 | 21:00
| Matuail | 68 | 1:00 | Biani Bazar | 60 | 21:00 | Mongla | 36 | 1:00
| Ghorasal | 70 | 1:00 | Comilla (S) | 138 | 19:30 | Satkhira | 85 | 0.875
| Narsingdi | 154 | 12:00 | Comilla(N) | 95 | 20:00 | Gallamari | 38 | 21:00
| Haripur (SBU) | 87 | 1:00 | Chandpur | 88 | 22:00 | Magura | 44 | 0.83333
| Ullon | 46 | 18:30 | Feni | 110 | 22:00 | Norail | 35 | 19:30
| Hasnabad | 155 | 19:00 | Chowmuhani | 144 | 21:00 | Chuadanga | 82 | 19:30
| Magbazar | 71 | 19:00 | Ashuganj | 52 | 21:00 | Barisal(N) | 35 | 0.91667
| Maniknagar | 72 | 19:00 | Daudkandi | 120 | 20:00 | Barisal (S) | 78 | 0.91667
| Bangabhaban | 14 | 1:00 | B.Baria | 157 | 22:00 | Patuakhali | 90 | 0.79167
| Narinda | 66 | 13:00 | Ramganj | 92 | 22:00 | Bhandaria | 46 | 0.83333
| Dhanmondi | 110 | 12:00 | Chaddagram | 32 | 19:00 | Borhan Uddin | 36 | 23:00
| Lalbag | 68 | 1:00 | PHP | 9 | 9:00 | Ishurdi | 54 | 19:30
| Madartek | 61 | 22:00 | Madunaghat | 49 | 20:00 | Ruppur Paromanobik | 2 | 7:00
| Dhaka University |  |  | Hathazari | 87 | 0.875 | Natore | 106 | 19:30
| Fatullah | 28 | 0.041667 | Khulshi | 164 | 0.875 | Bogra | 148 | 1:00
| Mirpur | 84 | 19:00 | Halishahar | 109 | 0.8125 | Noagaon | 118 | 21:00
| Kalyanpur | 87 | 19:00 | Baraulia | 155 | 0.041667 | Rajshahi | 126 | 20:00
| Gulshan | 82 | 19:00 | Sikalbaha | 26 | 0.79167 | Rajshahi New | 10 | 19:30
| Uttara | 66 | 19:00 | Dohazari | 92 | 0.79167 | C.Nawabganj | 66 | 21:00
| Uttara New | 21 | 20:00 | Cox'sbazar | 93 | 0.79167 | Amnura | 46 | 21:00
| Kamrangirchar | 68 | 21:00 | Chandraghona | 30 | 0.54167 | Pabna | 101 | 21:00
| Savar | 97 | 1:00 | Kaptai | 4.4 | 0.79167 | Shahjadpur | 84 | 20:00
| Bhasantec | 119 | 19:00 | A. Khaer Stl. | 0 | 0.041667 | Serajganj | 74 | 20:00
| Agargaon | 52 | 19:00 | Bakulia | 79 | 0.91667 | Niyamatpur | 53 | 21:00
| Satmosjid | 70 | 19:00 | Julda | 22 | 0.041667 | Joypurhat | 48 | 19:00
| Tongi | 96 | 0.041667 | TK chemical | 26.5 | 0.83333 | Sherpur(Bogura) | 42 | 19:30
| Kabirpur | 153 | 20:00 | Modern Steel | 0 | 0.041667 | Mohastangor | 42 | 19:00
| Basundhara | 106 | 19:00 | Shahmirpur | 18 | 0.041667 | Rangpur | 146 | 19:30
| Manikganj | 62 | 0.875 | Khagrachhari | 24 | 0.77083 | Lalmonirhat | 57 | 21:00
| Joydevpur | 117 | 19:00 | Matarbari | 30 | 0.8125 | Saidpur | 101 | 21:00
| New Tongi | 74 | 1:00 | Baroiar Hat | 34 | 0.77083 | Purbasadipur | 100 | 21:00
| Korda | 180 | 21:00 | Rangamati | 12 | 0.79167 | Thakurgaon | 78 | 20:00
| Dhamrai | 68 | 1:00 | Abul Khair 230 | 124 | 0.041667 | Palashbari | 122 | 20:00
| Rajendrapur | 78 | 1:00 | BSRM | 108 | 0.125 | Barapukuria | 45 | 19:30
| Valuka | 90 | 1:00 | GPH Ispat | 82 | 0.8125 | Panchagar | 50 | 19:30
| Tangail | 145 | 21:00 | Goalpara | 18 | 0.041667 | Joldhaka | 28 | 19:30
| Mymensing | 217 | 21:00 | Central s/s | 84 | 19:30 | Kurigram | 56 | 19:00
| Kishorganj | 140 | 20:00 | Noapara | 45 | 22:00
| Netrokona | 108 | 21:00 | Jessore | 88 | 21:00
| Jamalpur | 116 | 23:00 | Benapol | 40 | 21:00
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-08-21 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 398 | 18:30 | 390 | 11:00 | Kaliakoir | 380 | 0.041667 | 371 | 0.41667
| Bheramara | 405 | 5:00 | 392 | 21:00 | Bhulta | 394 | 0.77083 | 378 | 0.45833
| Ashuganj(N) | 394 | 1:00 | 385 | 12:00 | Gopalganj | 411 | 0.25 | 397 | 0.83333
| Payra | 414 | 7:00 | 407 | 21:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 232 | 1:00 | 230 | 13:00 | Comilla (N) | 235 | 18:30 | 228 | 12:00
| Ishurdi | 234 | 18:30 | 226 | 2:00 | Hathazari | 224 | 5:00 | 218 | 11:00
| Ashuganj | 236 | 18:30 | 232 | 10:00 | Megnaghat | 233 | 19:30 | 225 | 12:00
| Serajganj | 232 | 18:30 | 228 | 4:00 | Fenchuganj | 238 | 13:00 | 235 | 1:00
| Baghabari | 245 | 18:30 | 234 | 3:00 | Siddhirganj | 232 | 19:00 | 225 | 10:00
| Barapukuria | 236 | 18:00 | 225 | 21:00 | Maniknagar | 230 | 18:30 | 223 | 12:00
| Bogra | 225 | 18:00 | 217 | 20:00 | Agargaon | 229 | 19:00 | 220 | 12:00
| Rajshahi | 233 | 18:30 | 221 | 5:00 | Barisal | 244 | 5:00 | 237 | 23:00
| Khulna South | 235 | 18:30 | 225 | 19:30 | AKSML | 221 | 7:00 | 213 | 3:00
| Rampura | 229 | 1:00 | 224 | 12:00 | BSRM | 226 | 18:30 | 217 | 12:00
| Haripur | 228 | 18:00 | 224 | 10:00 | Bibiyana | 237 | 13:00 | 232 | 1:00
| Hasnabad | 230 | 19:00 | 222 | 12:00 | Bhulta | 231 | 19:00 | 224 | 17:00
| Shyampur | 227 | 19:00 | 220 | 10:00 | Ashuganj (S) | 231 | 18:30 | 224 | 15:00
| Aminbazar | 228 | 1:00 | 220 | 10:00 | Kaliakoir | 235 | 1:00 | 230 | 15:00
| Tongi | 228 | 1:00 | 220 | 11:00 | GPH | 229 | 1:00 | 214 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 133 | 19:00 | 127 | 11:00 | Hathazari | 133 | 0.75 | 130 | 0.083333
| Munsiganj | 135 | 18:30 | 126 | 7:00 | Khulshi | 132 | 0.77083 | 128 | 0.45833
| Sonargaon | 133 | 19:00 | 127 | 9:00 | Halishahar | 135 | 0.33333 | 130 | 0.70833
| Shyampur | 135 | 19:00 | 130 | 7:00 | Baraulia | 135 | 0.77083 | 129 | 0.20833
| Bhulta | 124 | 18:00 | 120 | 12:00 | Sikalbaha | 134 | 1:00 | 131 | 0.125
| Madanganj | 134 | 20:00 | 128 | 5:00 | Dohazari | 130 | 18:00 | 126 | 0.66667
| Shitalakhya | 141 | 19:00 | 131 | 10:00 | Cox'sbazar | 126 | 0.33333 | 117 | 0
| Rahim steal | 133 | 20:00 | 128 | 5:00 | Chandraghona | 134 | 0.77083 | 131 | 0.20833
| Matuail | 133 | 19:00 | 127 | 11:00 | Kaptai | 133 | 19:00 | 130 | 0.29167
| Ghorasal | 136 | 1:00 | 136 | 1:00 | A. Khaer Stl. | 131 | 0.041667 | 129 | 14:00
| Narsinghdi | 130 | 18:00 | 123 | 8:00 | Bakulia | 133 | 0.77083 | 130 | 0.20833
| Haripur (SBU) | 133 | 19:00 | 128 | 7:00 | Julda | 134 | 0.77083 | 132 | 0.041667
| Ullon | 134 | 19:30 | 130 | 11:00 | TK Chemical | 133 | 0.041667 | 130 | 15:00
| Hasnabad | 135 | 1:00 | 130 | 10:00 | Modern Steel | 133 | 0.79167 | 130 | 0.20833
| Magbazar | 135 | 4:00 | 130 | 10:00 | Shahmirpur | 134 | 0.041667 | 131 | 0.625
| Maniknagar | 132 | 2:00 | 129 | 12:00 | Khagrachhari | 132 | 0.77083 | 130 | 0.083333
| Bangabhaban | 132 | 2:00 | 129 | 12:00 | Matarbari | 130 | 0.33333 | 120 | 0
| Narinda | 132 | 2:00 | 129 | 12:00 | Baroiar Hat | 129 | 0.375 | 126 | 0.041667
| Dhanmondi | 134 | 19:30 | 130 | 11:00 | Rangamati | 132 | 0.041667 | 130 | 3:00
| Lalbag | 138 | 19:00 | 129 | 12:00 | Goalpara S/S | 137 | 15:00 | 131 | 19:30
| Madartek | 133 | 1:00 | 129 | 12:00 | Khulna Central S/S | 137 | 0.625 | 131 | 19:00
| Dhaka University |  |  |  |  | Noapara | 135 | 14:00 | 129 | 1:00
| Fatuiiah | 135 | 0.77083 | 130 | 5:00 | Jessore | 133 | 15:00 | 124 | 19:00
| Mirpur | 134 | 2:00 | 127 | 12:00 | Benapol | 134 | 15:00 | 125 | 1:00
| Kalyanpur | 133 | 18:30 | 129 | 12:00 | Jhenida | 130 | 0.625 | 119 | 19:30
| Gulshan | 133 | 1:00 | 128 | 12:00 | Bottail | 133 | 15:00 | 127 | 19:30
| Uttara | 132 | 1:00 | 129 | 12:00 | G.K Project | 138 | 0.77083 | 135 | 1:00
| Uttara New | 135 | 1:00 | 130 | 12:00 | Faridpur | 133 | 7:00 | 126 | 20:00
| Kamrangirchar | 135 | 19:30 | 128 | 12:00 | Madaripur | 137 | 0.45833 | 132 | 1:00
| Savar | 133 | 1:00 | 128 | 12:00 | Shariyatpur S/S | 138 | 0.29167 | 131 | 1:00
| Bhasantec | 133 | 1:00 | 128 | 12:00 | Gopalganj | 137 | 6:00 | 127 | 19:30
| Agargaon | 134 | 1:00 | 129 | 12:00 | Bagerhat | 136 | 15:00 | 126 | 19:00
| Satmosjid | 134 | 18:30 | 129 | 12:00 | Mongla | 133 | 0.625 | 124 | 19:00
| Tongi | 137 | 0.875 | 132 | 10:00 | Satkhira | 135 | 0.625 | 127 | 19:30
| Kabirpur | 136 | 18:00 | 134 | 21:00 | Gallamari | 137 | 15:00 | 130 | 19:30
| Basundhara | 133 | 21:00 | 129 | 11:00 | Magura | 130 | 10:00 | 118 | 19:30
| Manikganj | 138 | 18:30 | 132 | 8:00 | Norail | 128 | 0.625 | 115 | 19:30
| Joydevpur | 141 | 19:30 | 136 | 12:00 | Chuadanga | 127 | 15:00 | 111 | 19:30
| New Tongi | 136 | 0.875 | 130 | 9:00 | Barisal(N) | 140 | 6:00 | 134 | 1:00
| Kodda | 136 | 1:00 | 125 | 0.375 | Barisal (S) | 138 | 0.75 | 129 | 4:00
| Dhamrai | 137 | 18:30 | 133 | 11:00 | Patuakhali(S) | 135 | 0.29167 | 127 | 1:00
| Rajendrapur | 134 | 2:00 | 125 | 9:00 | Bhandaria | 134 | 15:00 | 121 | 19:30
| Valuka | 127 | 6:00 | 118 | 21:00 | Ishurdi | 137 | 18:00 | 132 | 3:00
| Tangail | 138 | 18:00 | 131 | 22:00 | Ruppur Paromanobik | 137 | 18:00 | 133 | 13:00
| Mymensing | 130 | 18:00 | 121 | 22:00 | Natore | 135 | 18:30 | 126 | 2:00
| Kishorganj | 129 | 10:00 | 121 | 21:00 | Bogra | 135 | 18:00 | 127 | 4:00
| Netrokona | 128 | 18:00 | 117 | 21:00 | Noagaon | 131 | 18:00 | 123 | 5:00
| Jamalpur | 139 | 20:00 | 126 | 7:00 | Rajshahi | 133 | 18:30 | 125 | 3:00
| Sherpur | 138 | 20:00 | 124 | 7:00 | Rajshahi New | 133 | 18:30 | 125 | 3:00
| Srimongal | 136 | 10:00 | 131 | 0.041667 | C.Nawabganj | 132 | 18:30 | 123 | 1:00
| Shahjibazar | 134 | 7:00 | 130 | 0.875 | Amnura | 133 | 18:30 | 125 | 12:00
| Fenchuganj | 134 | 8:00 | 131 | 0.041667 | Pabna | 135 | 17:00 | 129 | 3:00
| Khulawara | 133 | 7:00 | 131 | 0.041667 | Shahjadpur | 137 | 7:00 | 134 | 3:00
| Sylhet | 132 | 8:00 | 129 | 0.041667 | Serajganj | 135 | 18:00 | 130 | 4:00
| Chatak | 132 | 10:00 | 126 | 1:00 | Niyamatpur | 131 | 18:30 | 121 | 3:00
| Sunamganj | 130 | 9:00 | 124 | 0.041667 | Joypurhat | 134 | 18:30 | 124 | 1:00
| Biani Bazar | 130 | 10:00 | 125 | 0.041667 | Sherpur(Bogura) | 136 | 18:30 | 125 | 3:00
| Comilla(s) | 129 | 9:00 | 121 | 19:00 | Mohastangor | 135 | 18:00 | 125 | 3:00
| Comilla(n) | 136 | 18:30 | 132 | 15:00 | Rangpur | 128 | 18:30 | 117 | 21:00
| Chandpur | 130 | 13:00 | 127 | 19:00 | Lalmonirhat | 125 | 18:30 | 112 | 21:00
| Feni | 130 | 7:00 | 125 | 23:00 | Saidpur | 130 | 18:30 | 117 | 21:00
| Chowmuhani | 125 | 7:00 | 120 | 22:00 | Purbasadipur | 128 | 18:30 | 108 | 20:00
| Ashuganj | 135 | 6:00 | 131 | 22:00 | Thakurgaon | 126 | 6:00 | 110 | 19:30
| Daudkandi | 133 | 18:30 | 127 | 11:00 | Palashbari | 130 | 18:00 | 120 | 2:00
| B.Baria | 131 | 9:00 | 126 | 22:00 | Barapukuria | 136 | 18:00 | 125 | 21:00
| Ramganj | 123 | 8:00 | 119 | 23:00 | Panchagar | 127 | 6:00 | 108 | 21:00
| Chaddagram | 130 | 15:00 | 127 | 21:00 | Joldhaka | 128 | 18:00 | 111 | 21:00
| PHP | 130 | 18:30 | 124 | 23:00 | Kurigram | 126 | 18:30 | 108 | 21:00
| Madanhat | 135 | 1:00 | 131 | 11:00

## L-Curve
Date | 2020-08-21
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 306 | 6308 | 3572 | 9880 |  |  |  | QF-LDC-12
0:30 | 204.5 | 6506.5 | 3457 | 9963.5 | Date: | 2020-08-21
1:00 | 103 | 6705 | 3342 | 10047
1:30 | 126.5 | 6566 | 3296 | 9862
2:00 | 150 | 6427 | 3250 | 9677
2:30 | 166.5 | 6286 | 3173.5 | 9459.5 | [5 empty] | Gen. at Eve. Peak | 10401 | 10401 MW (21:00 )
3:00 | 183 | 6145 | 3097 | 9242 | [6 empty] | 21:00
3:30 | 201.5 | 6026.5 | 3069 | 9095.5 | [5 empty] | Gen. at Day Peak | 7789.9 | 7789.9 MW (12:00 )
4:00 | 220 | 5908 | 3041 | 8949 | [6 empty] | 12:00
4:30 | 246 | 5817.5 | 3024.5 | 8842 | [5 empty] | Highest Generation | 10401
5:00 | 272 | 5727 | 3008 | 8735 | [6 empty] | 21:00
5:30 | 308 | 5505.1 | 2890.05 | 8395.15
6:00 | 344 | 5283.2 | 2772.1 | 8055.3
6:30 | 372 | 5058.1 | 2721.4 | 7779.5
7:00 | 400 | 4833 | 2670.7 | 7503.7
7:30 | 380.5 | 4774.75 | 2660.95 | 7435.7
8:00 | 361 | 4716.5 | 2651.2 | 7367.7
8:30 | 410.5 | 4693.1 | 2659.3 | 7352.4
9:00 | 460 | 4669.7 | 2667.4 | 7337.1
9:30 | 488 | 4709.6 | 2668.25 | 7377.85
10:00 | 516 | 4749.5 | 2669.1 | 7418.6
10:30 | 547 | 4787.05 | 2698.95 | 7486
11:00 | 578 | 4824.6 | 2728.8 | 7553.4
11:30 | 561.5 | 4884.75 | 2786.9 | 7671.65
12:00 | 545 | 4944.9 | 2845 | 7789.9
12:30 | 502.5 | 5106.15 | 2896 | 8002.15
13:00 | 460 | 5267.4 | 2947 | 8214.4
13:30 | 475 | 5229.715 | 2902 | 8131.715
14:00 | 490 | 5192.03 | 2857 | 8049.03
14:30 | 523 | 5248.715 | 2864.5 | 8113.215
15:00 | 556 | 5305.4 | 2872 | 8177.4
15:30 | 515 | 5182.845 | 2772 | 7954.845
16:00 | 474 | 5060.29 | 2672 | 7732.29
16:30 | 487 | 4926.695 | 2632.25 | 7558.945
17:00 | 500 | 4793.1 | 2592.5 | 7385.6
17:30 | 505 | 4847.225 | 2673.8 | 7521.025
18:00 | 510 | 4901.35 | 2755.1 | 7656.45
18:30 | 355 | 5588.675 | 3126.55 | 8715.225
19:00 | 200 | 6276 | 3498 | 9774
19:30 | 242 | 6551 | 3717 | 10268
20:00 | 211 | 6494 | 3764 | 10258 |  |  |  | Executive Engineer
20:30 | 240 | 6536 | 3793.5 | 10329.5 |  |  |  | Network Operation Division
21:00 | 269 | 6578 | 3823 | 10401
21:30 | 297 | 6525.5 | 3808 | 10333.5
22:00 | 325 | 6473 | 3793 | 10266 |  |  |  |  | Page 6 of 7
22:30 | 322.5 | 6432.5 | 3726 | 10158.5
23:00 | 320 | 6392 | 3659 | 10051
23:30 | 313 | 6350 | 3615.5 | 9965.5
24:00 | 306 | 6308 | 3572 | 9880
10401 MW (21:00 )
7789.9 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-08-21 |  | Energy | 211241802
[10 empty] | 2020-08-21 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3357 | 931 | 2082 | 2270 | 630 | 123 | 330 | 0 | 134
0:30 | 3191.5 | 930.5 | 2138 | 2485 | 630 | 123 | 323 | 0 | 131 | Date: | 2020-08-21
1:00 | 3026 | 930 | 2194 | 2700 | 630 | 123 | 316 | 0 | 128
1:30 | 3057 | 930 | 2166 | 2559.5 | 624.5 | 123 | 274 | 0 | 128 | [7 empty] | Total Energy | 211.2418 | Total Energy Gen 211.242 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 211.242 MKWHr
2:00 | 3088 | 930 | 2138 | 2419 | 619 | 123 | 232 | 0 | 128 | [7 empty] | Energy not Served | 0
2:30 | 3126 | 930 | 2163 | 2169 | 604.5 | 123 | 216 | 0 | 128 | [7 empty] | Energy Requirement | 211.2418
3:00 | 3164 | 930 | 2188 | 1919 | 590 | 123 | 200 | 0 | 128
3:30 | 3143 | 930 | 2145.5 | 1840.5 | 589.5 | 119 | 200 | 0 | 128 | [6 empty] | Shortage
4:00 | 3122 | 930 | 2103 | 1762 | 589 | 115 | 200 | 0 | 128
4:30 | 3135 | 930 | 2091.5 | 1657.5 | 589 | 115 | 200 | 0 | 124
5:00 | 3148 | 930 | 2080 | 1553 | 589 | 115 | 200 | 0 | 120
5:30 | 3143 | 930 | 2056.5 | 1288 | 569 | 115 | 180 | 0 | 113
6:00 | 3138 | 930 | 2033 | 1023 | 549 | 115 | 160 | 0 | 106
6:30 | 3125 | 930 | 1983.5 | 832 | 549 | 116 | 140 | 0 | 102 |  |  |  |  | Coal
7:00 | 3112 | 930 | 1934 | 641 | 549 | 117 | 120 | 0 | 98
7:30 | 3099 | 930 | 1893.5 | 624 | 549.5 | 118 | 120 | 0 | 96 |  |  |  | Oil |  |  |  | ,
8:00 | 3086 | 930 | 1853 | 607 | 550 | 119 | 120 | 0 | 94
8:30 | 3086 | 930.5 | 1846 | 605 | 550 | 119.5 | 120 | 0 | 84
9:00 | 3086 | 931 | 1839 | 603 | 550 | 120 | 120 | 0 | 74
9:30 | 3077 | 930 | 1858.5 | 631.5 | 550 | 121 | 120 | 0 | 72
10:00 | 3068 | 929 | 1878 | 660 | 550 | 122 | 120 | 0 | 70
10:30 | 3064.5 | 929.5 | 1885 | 718.5 | 550 | 122.5 | 120 | 0 | 77
11:00 | 3061 | 930 | 1892 | 777 | 550 | 123 | 120 | 0 | 84
11:30 | 3065.5 | 930.5 | 1896.5 | 878 | 560 | 123 | 120 | 0 | 84
12:00 | 3070 | 931 | 1901 | 979 | 570 | 123 | 120 | 0 | 84
12:30 | 3000 | 930.5 | 1959 | 1170.5 | 590 | 123.5 | 120 | 0 | 95
13:00 | 2930 | 930 | 2017 | 1362 | 610 | 124 | 120 | 0 | 106
13:30 | 2930 | 930 | 2017 | 1362 | 610 | 124 | 120 | 0 | 106
14:00 | 2930 | 930 | 2017 | 1362 | 610 | 124 | 120 | 0 | 106
14:30 | 2886 | 930 | 2032.5 | 1373 | 615 | 121 | 120 | 0 | 107
15:00 | 2842 | 930 | 2048 | 1384 | 620 | 118 | 120 | 0 | 108
15:30 | 2845 | 930 | 1975 | 1243.5 | 609.5 | 116.5 | 121.5 | 0 | 107
16:00 | 2848 | 930 | 1902 | 1103 | 599 | 115 | 123 | 0 | 106
16:30 | 2855.5 | 930 | 1777.5 | 1067.5 | 579 | 115 | 125.5 | 0 | 103
17:00 | 2863 | 930 | 1653 | 1032 | 559 | 115 | 128 | 0 | 100
17:30 | 3023 | 930 | 1595.5 | 1061.5 | 554 | 115.5 | 136.5 | 0 | 102
18:00 | 3183 | 930 | 1538 | 1091 | 549 | 116 | 145 | 0 | 104
18:30 | 3280.5 | 930 | 1762.5 | 1604 | 559 | 116.5 | 342.5 | 0 | 120
19:00 | 3378 | 930 | 1987 | 2117 | 569 | 117 | 540 | 0 | 136
19:30 | 3457 | 931 | 2087 | 2365 | 619 | 117 | 554 | 0 | 138
20:00 | 3480 | 930 | 2045 | 2379 | 629 | 119 | 540 | 0 | 136
20:30 | 3491.5 | 930 | 2102 | 2386 | 644 | 119 | 521 | 0 | 136
21:00 | 3503 | 930 | 2159 | 2393 | 659 | 119 | 502 | 0 | 136
21:30 | 3458 | 929.5 | 2139 | 2392 | 659 | 119.5 | 501.5 | 0 | 135
22:00 | 3413 | 929 | 2119 | 2391 | 659 | 120 | 501 | 0 | 134
22:30 | 3390.5 | 929.5 | 2120 | 2330.5 | 644.5 | 121.5 | 488 | 0 | 134
23:00 | 3368 | 930 | 2121 | 2270 | 630 | 123 | 475 | 0 | 134
23:30 | 3362.5 | 930.5 | 2101.5 | 2270 | 630 | 123 | 402.5 | 0 | 134 | Max Temp. in Dhaka |  | 30° C
24:00 | 3357 | 931 | 2082 | 2270 | 630 | 123 | 330 | 0 | 134
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 211.242 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 211.242 MKWHr
Note on W13: Author:

## Generation
g | 2020-08-21
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 88 | 88 | 88 | 80 | 80 | 80 | 82 | 84 | 85 | 87 | 88 | 88 | 89 | 85 | 83 | 80 | 80 | 81 |  | 82 | 82 | 84 | 84 | 85 | 88 | 88 | 1979290
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 808000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [19 empty] | 4 | [5 empty] | 0 | 6435
| Teknaf 20MW PP (Solartech) | [5 empty] | 0.1 | 1.3 | 4.4 | 9.4 | 11.9 | 8.9 | 7.5 | 11.3 | 12.23 | 4.5 | 4.39 | 4.4 | 0.35 | [8 empty] | 81135
6 | Sikalbaha 225MW CCPP (Gas) | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 166 | 164 | 164 | 164 |  | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 3910618
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 103 | 105 | 110 | 104 | 103 | 105 | 104 | 105 | 104 | 106 | 104 | 116 | 106 | 107 | 105 | 103 | 70 | 70 |  | 105 | 104 | 103 | 107 | 103 | 104 | 104 | 2435973
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 85 | 85 | 68 | 68 | 68 | 68 | 0 | 356575
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [19 empty] | 50 | [6 empty] | 37048
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 178 | 184 | 198 | 168 | 198 | 177 | 191 | 174 | 183 | 183 | 183 | 208 | 178 | 196 | 172 | 164 | 145 | 145 |  | 146 | 145 | 146 | 146 | 145 | 145 | 145 | 4262529
18 | Kodda 300 MW PP Unit-2 (Summit) | 300 | 300 | 200 | 200 | 95 | [5 empty] | 25 | 65 | 120 | 165 | 165 | 132 | 115 | 115 |  | 225 | 285 | 285 | 286 | 286 | 286 | 286 | 3843926
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 8 | 8 | 8 | 117090
20 | Ghorasal TPP (Unit-1&2) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 597000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2709000
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1919630
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 25 | 26 | 26 | 20 | 10 | 3 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 423288
33 | Ashuganj 225 MW CCPP | 196 | 195 | 201 | 208 | 208 | 211 | 211 | 211 | 207 | 192 | 193 | 184 | 180 | 178 | 186 | 181 | 181 | 202 |  | 211 | 216 | 216 | 216 | 216 | 215 | 214 | 4847000
34 | Ashuganj 450 MW CCPP(South) | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 240 | 235 | 220 | 220 | 215 | 210 | 210 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 225 | 225 | 5674000
| Ashuganj 450 MW CCPP(North) | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 245 | 245 | 245 | 235 | 235 | 235 | 235 | 235 | 235 |  | 235 | 240 | 250 | 260 | 260 | 260 | 260 | 6089300
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 138240
36 | Chandpur 150 MW CCPP | 86 | 92 | 80 | 90 | 90 | 86 | 90 | 81 | 90 | 86 | 92 | 95 | 83 | 96 | 86 | 86 | 86 | 85 |  | 85 | 85 | 86 | 93 | 87 | 96 | 87 | 2113620
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 135 | 84 | 28 | 29 | 38 | 143 | 260 | 330 |  | 351 | 342 | 338 | 335 | 333 | 333 | 338 | 4607952
40 | Meghnaghat 450 MW CCPP(MPL) | 420 | 390 | 420 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 400 | 380 | 420 | 420 | 340 | 340 |  | 400 | 370 | 370 | 420 | 420 | 390 | 390 | 9145000
41 | Haripur 360MW CCPP(HPL) | 354 | 338 | 355 | 336 | 309 | 310 | 274 | 274 | 270 | 300 | 300 | 300 | 320 | 300 | 352 | 353 | 270 | 270 |  | 356 | 358 | 358 | 358 | 358 | 356 | 358 | 7674000
42 | RPCL 210MW CCPP | 124 | 142 | 142 | 142 | 142 | 158 | 158 | 160 | 142 | 142 | 141 | 139 | 124 | 122 | 140 | 155 | 156 | 154 |  | 158 | 156 | 158 | 158 | 104 | 105 | 105 | 3293760
43
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 59 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1428000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 726360
46 | Shajibazar 330 MW CCPP | 207 | 208 | 214 | 205 | 209 | 202 | 207 | 201 | 200 | 196 | 196 | 215 | 196 | 214 | 198 | 198 | 198 | 196 |  | 197 | 199 | 194 | 197 | 197 | 206 | 200 | 4654000
47 | Shahjibazar GTPP Unit- 8 & 9 | 64 | 64 | 64 | 64 | 64 | 65 | 40 | 40 | 40 | 40 | 40 | 40 | 67 | 40 | 63 | 64 | 40 | 40 |  | 65 | 65 | 65 | 64 | 64 | 64 | 65 | 1346016
48 | Shahjibazar 86MW PP (Shahjibazar) | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 30 | 30 | 60 | 83 | 83 | 85 | 85 | 85 | 40 | 20 | 20 |  | 83 | 83 | 85 | 83 | 85 | 85 | 85 | 1703040
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 79 | 80 | 80 | 80 | 1941110
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 429000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 246600
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 2 | 2 | 5 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 150000
55 | Fenchugonj 51 MW PP (Barakatullah) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 44 | 44 | 47 | 47 | 47 | 47 | 22 | 22 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 1065000
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 16 | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 16 |  | 24 | 24 | 16 | 16 | 16 | 16 | 16 | 393888
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 290 | 300 | 300 | 290 | 295 | 290 | 290 | 280 | 295 | 280 | 305 | 310 | 285 | 300 | 270 | 275 | 270 |  | 275 | 290 | 275 | 290 | 290 | 290 | 290 | 7218000
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 35 | [16 empty] | 15 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 178380
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 16 | 18 | 18 | 18 | 436032
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 |  |  | 19 | 19 |  |  |  |  | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 277308
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [9 empty] | 17 | 17 | 17 | 17 | 17 | 266472
63 | Impoprt (Tripura) | 128 | 128 | 128 | 128 | 120 | 106 | 98 | 94 | 74 | 70 | 84 | 84 | 106 | 106 | 108 | 106 | 100 | 104 |  | 136 | 138 | 136 | 136 | 134 | 134 | 134 | 2719680
64 | Malancha, Ctg. EPZ (United) | 28 | 28 | 29 | 29 | 34 | 35 | 36 | 34 | 36 | 27 | 26 | 22 | 35 | 37 | 31 | 35 | 35 | 39 |  | 39 | 40 | 39 | 42 | 42 | 32 | 32 | 686000
65 | Feni 22MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 456480
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 196200
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 16 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 604200
68 | Cumilla 25 MW PP (Summit) | 21 | 18 | 18 | 18 | 18 | 18 | 9 | 9 | 9 | 15 | 15 | 12 | 15 | 15 | 18 | 18 | 18 | 18 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 436290
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 27 | 27 | 27 | 27 | 27 | 30 | 30 | 30 | 30 | 28 | 21 | 21 | 16 | 16 | 8 | 7 | 16 | 16 |  | 16 | 30 | 30 | 30 | 30 | 30 | 30 | 553500
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 705400
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 819700
73 | Ghorashal 108MW PP (Regent) | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 92 | 86 | 85 | 88 | 89 | 92 | 91 | 85 | 43 | 43 |  | 86 | 92 | 96 | 98 | 98 | 98 | 98 | 2073136
| Feni Lanka Power | [19 empty] | 17 | [5 empty] | 0 | 18240
| Chowmuhani 113 MW | 57 | 56 | 18 | [8 empty] | 1 | 20 | 34 | 34 | 17 | 17 | 19 |  | 55 | 56 | 56 | 56 | 56 | 57 | 56 | 655200
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 100 | 100 | 100 | 90 | 35 |  |  |  | 1 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 657600
78 | Gazipur 52 MW PP
79 | Kodda 150MW PP | 16 | [18 empty] | 36 | 64 | 64 | 64 | 64 | 64 | 48 | 375360
80 | Jamalpur 95 MW PP(Powerpac) | 81 | 81 | 81 | 81 | 81 | 24 | [5 empty] | 8 | 13 | 24 | 24 | 24 | 24 | 24 |  | 64 | 90 | 91 | 91 | 91 | 91 | 91 | 1151040
81 | Jangalia 52 MW PP (Lakdanavi) | [17 empty] | 1 |  | 20 | 25 | 25 | 25 | 25 | 25 | 25 | 156634
| Gazipur 100 MW PP | 70 | 52 | 52 | [16 empty] | 17 | [5 empty] | 0 | 245460
| Kaptai 7 MW Solar PP | [5 empty] | 1 | 0.6 | 1.8 | 2.7 | 4.8 | 4 | 3.7 | 2.7 | 3.7 | 2.3 | 1.1 | 0.2 | [9 empty] | 27601
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | 94 | 94 | 94 | 94 | 94 | 30 | 15 | 15 | 15 | 15 | 15 | 15 | 38 | 64 | 64 | 64 | 64 | 64 |  | 70 | 80 | 77 | 80 | 80 | 91 | 94 | 1500456
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 39 | [16 empty] | 1 |  | 20 | [5 empty] | 0 | 73359
86 | Meghnaghat CCPP(Summit) | 138 | 140 | 150 | 143 | 150 | 145 | 152 | 140 | 145 | 135 | 140 | 150 | 135 | 150 | 130 | 135 | 135 | 130 |  | 120 | 135 | 130 | 140 | 130 | 135 | 125 | 3386269
87 | Meghnaghat 100 MW(IEL) | 93 | 93 | 93 | 94 | 100 | 70 |  |  |  |  | 7 | 7 | 7 | 7 | 7 | 51 | 75 | 75 |  | 75 | 100 | 93 | 100 | 100 | 100 | 100 | 1415040
| Meghnaghat 104 MW PP (OPCL) | 90 | 90 | 90 | 90 | 90 | 35 |  |  |  | 10 | 17 | 29 | 72 | 72 | 72 | 70 | 54 | 54 |  | 76 | 91 | 91 | 90 | 90 | 90 | 90 | 1480320
88 | Ghorashal 78.5 MW PP(MAX) | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 68 | 68 | 68 | 67 | 68 | 67 | 50 | 30 | 30 | 30 | 30 |  | 30 | 70 | 68 | 72 | 72 | 72 | 71 | 1422176
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0
92 | Fenchuganj 44MW (Energyprima) | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 43 | 42 | 46 | 46 | 42 | 42 | 20 | 20 | 20 |  | 30 | 46 | 46 | 46 | 46 | 46 | 46 | 1022904
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | [13 empty] | 10 | 15 | 638673
94 | Gagnagar 102 MW PP (Digital Power) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 94 | 94 | 94 | 94 | 94 | 7 | 7 | 495648
95 | Patenga 50MW PP (Baraka) | 50 | [18 empty] | 10 | 10 |  |  |  |  | 0 | 76800
96 | Chattogram 108 MW PP (ECPV) | 97 | 64 | [15 empty] | 2 |  | 31 | 26 | 26 | 21 | 25 | 20 | 21 | 318720
97 | Katpotti 52 MW PP (Sinha) | 41 | [18 empty] | 6 | [5 empty] | 0 | 82608
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | [9 empty] | 10 | 27 | 40 | 40 | 40 | 40 | 40 |  | 43 | 30 | 30 | 30 | 30 | 30 | 30 | 585388
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | [10 empty] | 17 | 17 | 17 | 17 |  |  |  | 17 | 35 | 17 | 17 | 17 | 17 | 17 | 322972
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 110 | 110 | 110 | 110 | 163 | 110 | 163 | 130 | 110 | 110 |  | 163 | 163 | 163 | 163 | 130 | 130 | 130 | 3310118
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0.1 | 0.1 | 0.3 | 0.6 | 0.8 | 0.7 | 0.7 | 1.4 | 1.1 | 0.6 | 0.8 | 0.5 | [9 empty] | 9050
103 | Kamalaghat 54 MW PP(Banco Energy) | 53 | 53 | 17 | [8 empty] | 22 | 53 | 53 | 53 | 17 | 17 | 17 |  | 20 | 53 | 53 | 53 | 53 | 53 | 53 | 705600
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 193 | 193 | 202 | 202 | 200 | 170 | 80 | 80 | 80 | 96 | 120 | 168 | 200 | 200 | 200 | 130 | 130 | 130 |  | 156 | 200 | 200 | 200 | 200 | 200 | 200 | 4063200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 131 | 131 | 131 | 133 | 133 | 131 | 93 | 71 | 72 | 80 | 104 | 106 | 130 | 88 | 90 | 122 | 99 | 100 |  | 123 | 133 | 133 | 133 | 132 | 131 | 132 | 2767680
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 90 | 100 | 90 | 60 | 60 | 60 | 60 | 80 |  | 100 | 100 | 100 | 100 | 90 | 90 | 100 | 2163840
116 | Chandpur 200MW (Desh energy) | [25 empty] | 0 | 0
117 | Ashuganj 150MW PP (Midland) | [25 empty] | 0 | 0
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 115 | 95 | 65 | 35 | [13 empty] | 3 |  | 34 | 65 | 65 | 45 | 45 | 45 | 45 | 651600
| Anwara 300 MW PP (United) | 234 | 234 | 234 | 233 | 198 | 160 | 124 | 124 | 124 | 156 | 159 | 160 | 197 | 198 | 198 | 105 | 86 | 86 |  | 215 | 233 | 234 | 234 | 234 | 234 | 234 | 4458655
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 70 | 70 | 70 | 70 | 70 | 70 | 100 | 100 | 100 | 70 | 70 | 50 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2148480
120 | Eastern Zone Total | 6705 | 6427 | 6145 | 5908 | 5727 | 5283.2 | 4833 | 4716.5 | 4669.7 | 4749.5 | 4824.6 | 4944.9 | 5267.4 | 5192.03 | 5305.4 | 5060.29 | 4793.1 | 4901.35 |  | 6276 | 6551 | 6494 | 6578 | 6473 | 6392 | 6308 | 135766892
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 115 | 115 | 115 | 115 | 115 | 16 |  |  |  |  | 16 | 49 | 66 | 66 | 66 | 35 | 32 | 32 |  | 115 | 16 | 49 | 83 | 115 | 99 | 115 | 1458240
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
| Khulna 225 MW CCPP | 200 | 200 | 200 | 200 | 200 | 160 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 130 | 150 | 150 | 150 | 150 | 130 | 120 | 3562560
129 | Rupsha 105 MW PP (Orion rupsha) | [25 empty] | 0 | 14400
130
131
132
133
| Barisal 110 MW PP (Summit ) | [17 empty] | 16 |  | 64 | 48 | 48 | 32 | 16 | 16 | 16 | 212160
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 79 | 79 | 78 | 78 | 77 | 77 | 32 | 33 | 33 | 33 | 33 | 33 | 54 | 53 | 33 | 35 | 35 | 34 |  | 63 | 76 | 79 | 80 | 80 | 79 | 78 | 1362068
| Bhola 225 MW CCPP | 89 | 89 | 90 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 90 | 89 | 89 | 89 | 89 | 89 | 89 |  | 89 | 89 | 89 | 90 | 90 | 90 | 90 | 2186777
140 | Bhola 33 MW PP (Venture) | 27 | 25 | 25 | 24 | 20 | 15 | 14 | 16 | 8 | 15 | 15 | 17 | 19 | 18 | 15 | 16 | 17 | 19 |  | 25 | 25 | 27 | 29 | 29 | 29 | 28 | 475524
141 | Noapara 100 MW PP (Bangla Trac) | [20 empty] | 30 | 22 | 30 | 30 |  | 0 | 100800
142 | Noapara 40 MW PP (Khanjahan Ali) | [19 empty] | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 223875
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 930 | 930 | 930 | 930 | 930 | 930 | 930 | 930 | 931 | 929 | 930 | 931 | 930 | 929 | 930 | 930 | 930 | 930 |  | 930 | 931 | 930 | 930 | 929 | 930 | 931 | 22316364
147 | Bheramara 410 MW CCPP | 155 | 200 | 225 | 225 | 225 | 235 | 250 | 250 | 250 | 250 | 250 | 260 | 260 | 145 | 145 | 75 | 75 | 305 |  | 365 | 345 | 345 | 345 | 340 | 345 | 345 | 5909760
148 | Payra 1320 MW | 480 | 470 | 450 | 440 | 440 | 400 | 400 | 400 | 400 | 400 | 400 | 420 | 460 | 470 | 470 | 450 | 410 | 400 |  | 420 | 470 | 480 | 510 | 510 | 480 | 480 | 11581300
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 149 | 140 | 149 | 149 | 149 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 150 | 150 | 3643500
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 50 | 50 | 50 | 50 | 50 | 50 |  | 241403
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 157 | 148 | 163 | 166 | 159 | 149 | 147 | 150 | 145 | 149 | 145 | 155 | 159 | 146 | 171 | 179 | 151 | 152 |  | 158 | 198 | 199 | 199 | 182 | 164 | 163 | 4080273
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 150 | 150 | 166 | 150 | 150 | 150 | 150 | 150 | 150 | 165 | 200 | 200 | 205 | 200 | 204 | 180 | 150 | 150 |  | 163 | 212 | 215 | 220 | 216 | 160 | 160 | 4635273
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 413 | 415 | 408 | 403 | 417 | 368 | 355 | 327 | 356 | 331 | 344 | 381 | 338 | 377 | 395 | 377 | 392 | 274 |  | 343 | 380 | 345 | 383 | 366 | 401 | 358 | 8953272
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 5 |  | 35 | 35 | 35 |  |  |  |  | 75316
162 | Bogra 22 MW PP (GBB) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 21 |  | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 438000
163 | Bogura 20 MW PP (Energyprima) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 272088
164 | Ullapara 11 MW PP (Summit) | 11 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 11 | 5 | 11 | 11 | 11 | 11 | 11 | 177714
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern) | [25 empty] | 0 | 0
167 | Katakhali 50 MW Peaking PP | [19 empty] | 31 | 38 | 47 | 44 | 44 | 38 | 37 | 190110
168 | Santahar 50 MW Peaking PP | [17 empty] | 12 |  | 32 | 32 | 26 | 26 | 25 | 25 | 25 | 145423
169 | Natore 52 MW PP (Rajlanka) | [19 empty] | 26 | 25 | 25 | 25 | 25 | 25 | 25 | 139200
170 | Chapainawabganj 100 MW Peaking PP | 100 | 32 | [13 empty] | 3 | 8 | 8 |  | 91 | 100 | 100 | 100 | 100 | 100 | 100 | 728120
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | [18 empty] | 16 | 50 | 68 | 70 | 70 | 70 | 70 | 467040
172 | Confidence Power Bogura Unit-1 113 MW | 109 | 109 | 70 | 35 | [7 empty] | 5 | 40 | 50 | 50 |  |  | 15 |  | 70 | 90 | 109 | 109 | 109 | 109 | 109 | 1117824
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 113 | 102 | [10 empty] | 23 | 10 |  |  |  | 8 |  | 50 | 101 | 94 | 85 | 84 | 85 | 88 | 754560
177 | Sympa Solar Power 8MW | [5 empty] | 0.1 | 0.7 | 2.2 | 1.4 | 4.1 | 2.8 | [5 empty] | 0.5 | 0.1 | [8 empty] | 11966
178
178