## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-08-24 | Monday
|  |  | Date (day): | 2020-08-24 |  | Monday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13580.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14576 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-08-23 | 2020-08-24 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 28 | 28 | 28 | 28 |  | 57 | Unit-2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 110 | 110 | 110 | 110
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 66 | 67 | 70 | 70 |  | 8 | Engine problem
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 93 | 97 | 100 | 100
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 389 | 389 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 350 | 353 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 400 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 10 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 135 | 135 | 150 | 150 |  |  | GT-1 S/D for gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 80 | 97 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 41 | 30 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 52 | 100 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 98 | 98 | 100 |  |  | Fuel Shortage.
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 94 | 102 | 102 | 102 |  | 0 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 48 | 46 | 49 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 53 | 53 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 149 | 149 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 46 | 55 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 52 | 52 | 35 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 286 | 286 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 300 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 80 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 109 | 133 | 133 | 133 |  | 16 | Engine problem
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 63 | 102 | 100 | 100
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 17 | 104 | 104
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 2875 | 3404 | 3642 | 3932 | 423 | 956
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19.1 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 77 | 78 | 78 | 78 | 152 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 231 | 0 | 165 | 165 | 60 |  | Gas shortage
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 139 | 140 | 110 | 140 | 10 |  | Gas shortage
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 34 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 100 | 100
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 10 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 100 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 18 | 18 | 18 |  | 4 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 34 | 30 | 30
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 91 | 97 | 97 | 97 |  | 11 | Engine problem
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2.3 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 179 | 253 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 54 | 50 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 1022.4 | 1095 | 1498 | 1567 | 582 | 113
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 70 | 70 | 80 | 80 | 49 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 144 | 126 | 220 | 220
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 270 | 360 | 360
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 200 | 220 | 360 | 360
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 5 | 5 | 5 | 40 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 5 | 5 | 50 |  | Gas shortage
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 46 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 16 | 100 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 50 | 50 | 0 | 50
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 85 | 96 | 96 | 96 |  | 67 | ST under shut down
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 118 | 114 | 200 | 200
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 21 | 21 | 21
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 118 | 132 | 163 | 173
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 43 | 43 | 43 |  | 9 | Engine problem
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 21 | 21 | 21
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 114 | 114 | 114 | 114
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 56 | 57 | 60 | 60 | 53 |  | Fuel shortage.
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1414 | 1526 | 1993 | 2253 | 648 | 84
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 123 | 123 | 160 | 160 | 42 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 17 | 17 |  | 5 | Engine problem
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 73 | 90 | 80 | 80 |  | 15 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1.2 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 200 | 200 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 11 | 115 | 115 | 115
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 425.2 | 545 | 573.6 | 572 | 42 | 20
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 60 | 60 | 60
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  |  | unit-4 under shut down
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 193 | 192 | 210 | 210 |  |  | ST under shut down
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 44 | 49 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 43 | 43 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 62 | 64 | 66 | 66
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 85 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 80 | 80 | 80 | 80 |  | 151 | Machine problem.
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 290 | 341 | 341
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1137 | 1116 | 1195 | 1195 | 0 | 551
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 923 | 922 | 932 | 932
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 115 | 115 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 200 | 220 | 220
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 325 | 330 | 350 | 410
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 60 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 105 | 105 | 105 |  | 0 | Engine problem
| 108 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 15 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1483 | 1827 | 1922 | 2128 | 0 | 0
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 18 | 32 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 16 | 31 | 33 | 33
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 90 | 89 | 90 | 90 |  | 104 | GT-2 & ST Under maint.
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 78 | 77 | 80 | 80 |  | 15 | Engine problem
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 0 | 520 | 660 | 660
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 202 | 749 | 973 | 973 | 0 | 119
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 35 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 25 | 50 | 50
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 47 | 0 | 50
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | S/D for ST Under maint.
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 182 | 175 | 220 | 220 |  |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 180 | 185 | 220 | 220 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 409 | 411 | 414 | 414 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 0 | 30
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 11 | 11 | 11 | 11
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 43 | 43 | 43 |  | 9 | Engine problem
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 100 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 94 | 113 | 113
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 60 | 109 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 868 | 1339 | 1513 | 1683 | 431 | 13
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 149 | 149 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 37 | 54 | 113 | 113
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7.6 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 193.6 | 203 | 271 | 273 | 294 | 30
|  | Total |  |  |  |  | 20383 | 19892 | 9620.2 | 11804 | 13580.6 | 14576 | 2420 | 1886
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9227.3725 | 11322 | 13026.055 | 13980.8092
| A. |  | 2020-08-23 | (Yesterday) |  |  |  |  | Sunday
| 1 | Highest Generation : |  |  | 11804 | MW at | 20:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
| 2 | Minimum Generation : |  |  | 8032.8 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11804 | MW
| 3 | Day peak Generation : |  |  | 9620.2 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11322 | MW
| 4 | Evening peak Generation : |  |  | 11804 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 239.544 | MKWHr | By Solar | 0.17908 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 125.2014 | MKWHr |  | By Oil: | 75.979 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 12.7731 | MKWHr |  | By Hydro: | 1.8097 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2420 | MW | Dhaka | 3927 | 3927 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 1886 | MW | Chittagong | 1126 | 1126 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4306 | MW | Khulna | 1429 | 1429 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1056.37 | MMCFD |  |  | Rajshahi | 1243 | 1243 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 144329766.566 | ii) Oil : | Taka | 643968750 | Comilla | 1083 | 1083 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 59832276 | Total | Taka | 848130792.566 | Mymensingh | 957 | 957 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.016 | MKWHr. | Sylhet | 488 | 488 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 183 | MW (E to W) at | 20:00 | hrs | Barisal | 310 | 310 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -9 | MW at | 10:00 | hrs | Rangpur | 759 | 759 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 31.0° C |  |  | Total | 11322 | 11322 |  | 0
| B. |  | 2020-08-24 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 33.7° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 11900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14576 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 9900 | MW
| 4 | Reserve(Generation end) |  |  |  | 2676 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 241.4921 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8577 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 20.4625 | MKWHr. | ii) HVDC Flow at Peak Time |  | 922 | MW at | 20:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.1392 | MKWHr. | iii) Maximum HVDC Flow : |  | 929 | MW at | 14:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 93.25 |  | (b) Today: | 93.24 |  | (c) Rule Curve: |  | 96.36
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-08-23
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 28 | 0 | 0 | 110 | 0 | 98 | 69 | 340 | 358 |  | 0 | 390 | 130 | 7 | 80 | 55 | 0 | 0 | 0 | 0 | 7 | 85 | 116 | 0 | 0 | 0 | 47 | 53 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 45 | 35 | 0 | 0 | 0 | 164 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 55 | 0 | 17 | 42 | 0 | 70 | 0 | 310 | 100 | 154 | 8 | 85 | 5 | 0 | 0 | 51 | 0 | 0 | 43 | 18 | 11 | 0 | 21 | 138 | 125 | 90 | 17 | 0 | 60 | 30 | 47 | 44 | 163 | 200 | 67 | 85 | 0 | 80 | 18 | 0 | 10 | 285 | 24 | 8 | 0 | 300 | 0 | 0 | 194 | 0 | 133 | 0 | 100 | 0 | 60 | 0 | 85 | 105 | 0 | 0 | 234 | 0 | 0 | 48 | 56 | 100 | 0 | 17 |  | 924 | 0 | 355 | 0 | 115 | 150 | 0 | 0 | 0 | 0 | 40 | 89 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 179 | 0 | 77 | 0 | 219 | 0 | 356 | 35 | 0 | 70 | 0 | 113 | 0 | 0 | 109 | 530 |  | 6484 | 3679 | 10163 | 3156 | 924 | 2143 | 2676 | 680 | 80 | 366 | 138 | 0 | 0 | 93.25
2:00 | 28 | 0 | 0 | 110 | 0 | 98 | 69 | 338 | 356 |  | 0 | 390 | 145 | 7 | 96 | 55 | 0 | 0 | 0 | 0 | 7 | 94 | 98 | 0 | 0 | 0 | 47 | 53 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 45 | 35 | 0 | 0 | 0 | 164 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 51 | 0 | 17 | 42 | 0 | 70 | 0 | 300 | 80 | 161 | 8 | 92 | 5 | 0 | 0 | 51 | 0 | 0 | 43 | 18 | 11 | 0 | 21 | 134 | 125 | 90 | 17 | 0 | 60 | 30 | 47 | 44 | 163 | 196 | 67 | 85 | 0 | 80 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 300 | 0 | 0 | 194 | 0 | 132 | 0 | 100 | 0 | 60 | 0 | 85 | 70 | 0 | 0 | 234 | 0 | 0 | 34 | 56 | 100 | 0 | 17 |  | 728 | 0 | 355 | 0 | 115 | 150 | 0 | 0 | 0 | 0 | 40 | 89 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 182 | 0 | 78 | 0 | 215 | 0 | 387 | 35 | 0 | 70 | 0 | 113 | 0 | 0 | 109 | 530 |  | 6420 | 3510 | 9930 | 3134 | 728 | 2166 | 2662 | 680 | 80 | 346 | 134 | 0 | 0 | 93.25
3:00 | 28 | 0 | 0 | 110 | 0 | 98 | 69 | 339 | 355 |  | 0 | 390 | 140 | 7 | 96 | 55 | 0 | 0 | 0 | 0 | 7 | 94 | 98 | 0 | 0 | 0 | 47 | 53 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 42 | 35 | 0 | 0 | 0 | 164 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 51 | 0 | 16 | 42 | 0 | 70 | 0 | 300 | 25 | 174 | 8 | 92 | 5 | 0 | 0 | 51 | 0 | 0 | 43 | 18 | 11 | 0 | 21 | 130 | 143 | 90 | 17 | 0 | 60 | 30 | 47 | 44 | 163 | 194 | 67 | 85 | 0 | 80 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 133 | 0 | 100 | 0 | 60 | 0 | 65 | 70 | 0 | 0 | 234 | 0 | 0 | 17 | 57 | 100 | 0 | 17 |  | 728 | 0 | 345 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 89 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 182 | 0 | 78 | 0 | 206 | 0 | 384 | 17 | 0 | 70 | 0 | 113 | 0 | 0 | 109 | 510 |  | 6371 | 3421 | 9792 | 3088 | 728 | 2183 | 2610 | 660 | 77 | 316 | 130 | 0 | 0 | 93.25
4:00 | 28 | 0 | 0 | 110 | 0 | 98 | 69 | 338 | 357 |  | 0 | 390 | 135 | 7 | 96 | 30 | 0 | 0 | 0 | 0 | 7 | 94 | 64 | 0 | 0 | 0 | 47 | 53 | 55 | 17 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 42 | 35 | 0 | 0 | 0 | 164 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 51 | 0 | 16 | 42 | 0 | 70 | 0 | 300 | 55 | 182 | 8 | 96 | 5 | 0 | 0 | 51 | 0 | 0 | 43 | 18 | 11 | 0 | 21 | 130 | 145 | 90 | 17 | 0 | 60 | 30 | 47 | 44 | 163 | 192 | 67 | 85 | 0 | 80 | 18 | 0 | 10 | 285 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 132 | 0 | 100 | 0 | 60 | 0 | 65 | 35 | 0 | 0 | 234 | 0 | 0 | 0 | 56 | 100 | 0 | 17 |  | 728 | 0 | 345 | 0 | 107 | 120 | 0 | 0 | 0 | 0 | 40 | 89 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 183 | 0 | 78 | 0 | 203 | 0 | 355 | 0 | 0 | 70 | 0 | 113 | 0 | 0 | 109 | 510 |  | 6243 | 3352 | 9595 | 3127 | 728 | 2129 | 2463 | 659 | 77 | 282 | 130 | 0 | 0 | 93.25
5:00 | 28 | 0 | 0 | 110 | 0 | 98 | 69 | 338 | 356 |  | 0 | 390 | 145 | 7 | 95 | 30 | 0 | 0 | 0 | 0 | 0 | 94 | 64 | 0 | 0 | 0 | 0 | 53 | 55 | 17 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 42 | 35 | 0 | 0 | 0 | 164 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 16 | 42 | 0 | 70 | 0 | 300 | 65 | 188 | 8 | 95 | 5 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 0 | 21 | 122 | 145 | 81 | 17 | 0 | 60 | 30 | 47 | 44 | 163 | 195 | 67 | 85 | 0 | 80 | 18 | 0 | 10 | 275 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 133 | 0 | 100 | 0 | 60 | 0 | 24 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 55 | 100 | 0 | 17 |  | 728 | 0 | 345 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 184 | 0 | 78 | 0 | 202 | 0 | 403 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 109 | 480 |  | 6030 | 3226 | 9256 | 3145 | 728 | 2170 | 2135 | 629 | 77 | 250 | 122 | 0 | 0 | 93.25
6:00 | 28 | 0 | 0 | 110 | 0 | 98 | 68 | 338 | 357 |  | 0 | 390 | 135 | 7 | 64 | 15 | 0 | 0 | 0 | 0 | 0 | 48 | 30 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 19 | 25 | 29 | 33 | 33 | 0 | 0 | 42 | 35 | 0 | 0 | 0 | 164 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 16 | 40 | 0 | 70 | 0 | 300 | 95 | 172 | 8 | 85 | 5 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 0 | 12 | 114 | 161 | 8 | 17 | 0 | 60 | 30 | 47 | 44 | 163 | 195 | 68 | 85 | 0 | 80 | 18 | 0 | 10 | 285 | 24 | 8 | 0 | 170 | 0 | 0 | 200 | 0 | 123 | 0.2 | 100 | 0 | 10 | 0 | 8 | 0 | 0 | 0.1 | 190 | 0 | 0 | 0 | 8 | 100 | 0 | 17 |  | 729 | 0 | 345 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 183 | 0 | 76 | 0 | 201 | 0 | 361 | 0 | 0 | 0 | 0 | 61 | 0 | 0.1 | 35 | 430 |  | 5479.3 | 2959.1 | 8438.4 | 3154 | 729 | 2132 | 1495 | 579 | 77 | 158 | 114 | 0.4 | 0 | 93.25
7:00 | 28 | 0 | 0 | 110 | 0 | 98 | 68 | 338 | 289 |  | 0 | 390 | 130 | 7 | 64 | 15 | 0 | 0 | 0 | 0 | 0 | 48 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 19 | 25 | 0 | 33 | 0 | 0 | 0 | 42 | 35 | 0 | 0 | 0 | 164 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 11 | 0 | 16 | 38 | 0 | 70 | 0 | 300 | 95 | 159 | 8 | 94 | 5 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 0 | 15 | 100 | 161 | 8 | 17 | 0.1 | 60 | 30 | 47 | 44 | 110 | 206 | 40 | 85 | 0 | 80 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 170 | 0 | 0 | 200 | 0 | 100 | 1.7 | 100 | 0 | 10 | 0 | 8 | 0 | 0 | 0.8 | 162 | 0 | 0 | 0 | 8 | 100 | 0 | 17 |  | 729 | 0 | 350 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 181 | 0 | 79 | 0 | 150 | 0 | 346 | 0 | 0 | 0 | 0 | 34 | 0 | 0.2 | 35 | 430 |  | 5167.6 | 2865.2 | 8032.8 | 3023 | 729 | 1993 | 1393 | 579 | 77 | 136 | 100 | 2.8 | 0 | 93.25
8:00 | 28 | 0 | 0 | 110 | 0 | 95 | 68 | 346 | 289 |  | 0 | 390 | 130 | 7 | 64 | 15 | 0 | 0 | 0 | 0 | 0 | 48 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 25 | 9 | 33 | 25 | 0 | 0 | 43 | 35 | 0 | 0 | 0 | 164 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 11 | 0 | 16 | 8 | 0 | 70 | 0 | 300 | 140 | 168 | 8 | 90 | 5 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 0 | 15 | 102 | 158 | 8 | 17 | 0.3 | 60 | 30 | 47 | 44 | 163 | 201 | 40 | 85 | 0 | 80 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 188 | 0 | 0 | 200 | 0 | 100 | 7.4 | 100 | 0 | 10 | 0 | 8 | 4 | 0 | 4 | 162 | 0 | 0 | 0 | 8 | 100 | 0 | 17 |  | 728 | 0 | 360 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 149 | 0 | 79 | 0 | 150 | 0 | 402 | 0 | 0 | 0 | 0 | 35 | 0 | 1.2 | 35 | 430 |  | 5322.7 | 2896.2 | 8218.9 | 3063 | 728 | 2088 | 1416 | 579 | 78 | 152 | 102 | 12.9 | 0 | 93.25
9:00 | 28 | 0 | 0 | 110 | 0 | 95 | 68 | 338 | 290 |  | 0 | 390 | 140 | 7 | 80 | 55 | 0 | 0 | 0 | 0 | 0 | 94 | 32 | 0 | 0 | 0 | 0 | 53 | 35 | 55 | 0 | 25 | 9 | 33 | 25 | 0 | 0 | 43 | 35 | 0 | 0 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 51 | 0 | 16 | 4 | 0 | 70 | 0 | 285 | 200 | 147 | 8 | 75 | 5 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 0 | 15 | 108 | 142 | 8 | 17 | 0.7 | 60 | 30 | 47 | 44 | 163 | 203 | 40 | 85 | 0 | 80 | 18 | 0 | 10 | 295 | 24 | 8 | 0 | 288 | 0 | 0 | 200 | 0 | 130 | 8.6 | 100 | 0 | 10 | 0 | 8 | 17 | 0 | 3.2 | 162 | 0 | 0 | 0 | 10 | 100 | 0 | 17 |  | 729 | 0 | 360 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 146 | 0 | 77 | 0 | 150 | 0 | 404 | 0 | 0 | 0 | 0 | 38 | 0 | 1.8 | 35 | 370 |  | 5736.5 | 2849.8 | 8586.3 | 3086 | 729 | 2076 | 1824 | 519 | 78 | 152 | 108 | 14.3 | 0 | 93.25
10:00 | 28 | 0 | 0 | 110 | 0 | 95 | 68 | 345 | 291 |  | 0 | 300 | 130 | 7 | 80 | 41 | 0 | 0 | 0 | 0 | 0 | 94 | 149 | 10 | 0 | 0 | 5 | 53 | 55 | 55 | 19 | 25 | 18 | 33 | 25 | 0 | 0 | 44 | 35 | 0 | 0 | 10 | 224 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 91 | 24 | 16 | 4 | 0 | 70 | 0 | 270 | 200 | 139 | 8 | 70 | 5 | 0 | 0 | 51 | 0 | 0 | 6 | 18 | 8 | 0 | 15 | 112 | 141 | 16 | 17 | 0.6 | 60 | 30 | 44 | 44 | 110 | 194 | 40 | 85 | 0 | 80 | 18 | 0 | 10 | 285 | 24 | 5 | 0 | 300 | 0 | 0 | 200 | 0 | 95 | 13.1 | 90 | 60 | 10 | 0 | 8 | 0 | 0 | 2.9 | 162 | 0 | 0 | 114 | 41 | 100 | 0 | 17 |  | 729 | 0 | 325 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 15 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 150 | 0 | 78 | 0 | 150 | 0 | 354 | 0 | 0 | 0 | 0 | 37 | 0 | 6.6 | 35 | 270 |  | 6012.6 | 2675.6 | 8688.2 | 3109 | 729 | 1871 | 2077 | 419 | 79 | 269 | 112 | 23.2 | 0 | 93.25
11:00 | 28 | 0 | 0 | 110 | 0 | 95 | 67 | 357 | 348 |  | 0 | 420 | 130 | 7 | 80 | 41 | 0 | 0 | 0 | 0 | 0 | 94 | 149 | 27 | 0 | 0 | 45 | 53 | 55 | 35 | 19 | 25 | 20 | 33 | 25 | 13 | 0 | 45 | 35 | 0 | 0 | 25 | 231 | 0 | 141 | 0 |  | 0 | 0 | 0 | 0 | 91 | 50 | 16 | 2 | 0 | 70 | 0 | 270 | 200 | 141 | 8 | 74 | 0 | 0 | 0 | 51 | 0 | 0 | 42 | 18 | 8 | 0 | 15 | 120 | 121 | 40 | 17 | 1.2 | 58 | 30 | 44 | 44 | 163 | 211 | 52 | 85 | 0 | 80 | 18 | 0 | 10 | 285 | 24 | 5 | 0 | 300 | 0 | 0 | 200 | 0 | 25 | 3.7 | 90 | 102 | 10 | 0 | 8 | 0 | 0 | 2.9 | 162 | 0 | 0 | 114 | 56 | 100 | 0 | 17 |  | 923 | 0 | 330 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 154 | 0 | 78 | 0 | 150 | 0 | 394 | 0 | 0 | 0 | 0 | 37 | 0 | 7.9 | 35 | 0 |  | 6407.8 | 2650.9 | 9058.7 | 3148 | 923 | 2139 | 2215 | 149 | 80 | 269 | 120 | 15.7 | 0 | 93.25
12:00 | 28 | 0 | 0 | 110 | 0 | 93 | 66 | 389 | 350 |  | 0 | 420 | 135 | 7 | 80 | 41 | 0 | 0 | 0 | 0 | 0 | 94 | 149 | 52 | 0 | 0 | 48 | 53 | 55 | 55 | 19 | 25 | 21 | 33 | 25 | 52 | 0 | 42 | 35 | 0 | 0 | 25 | 231 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 91 | 50 | 16 | 3 | 0 | 70 | 0 | 270 | 200 | 144 | 8 | 85 | 5 | 0 | 0 | 51 | 0 | 50 | 43 | 18 | 8 | 25 | 15 | 118 | 123 | 73 | 17 | 1.2 | 60 | 30 | 44 | 43 | 163 | 193 | 62 | 85 | 0 | 80 | 18 | 0 | 10 | 320 | 24 | 5 | 0 | 286 | 0 | 0 | 200 | 0 | 109 | 19.1 | 90 | 118 | 16 | 0 | 11 | 63 | 0 | 2.3 | 179 | 0 | 0 | 114 | 56 | 100 | 0 | 17 |  | 923 | 0 | 325 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 16 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 182 | 0 | 78 | 0 | 180 | 0 | 409 | 0 | 0 | 0 | 0 | 37 | 0 | 7.6 | 60 | 0 |  | 6873.6 | 2746.6 | 9620.2 | 3273 | 923 | 2188 | 2543 | 149 | 77 | 319 | 118 | 30.2 | 0 | 93.25
13:00 | 28 | 0 | 0 | 110 | 0 | 95 | 66 | 412 | 330 |  | 0 | 330 | 135 | 7 | 97 | 41 | 0 | 0 | 0 | 0 | 0 | 94 | 149 | 51 | 0 | 0 | 48 | 53 | 55 | 55 | 19 | 25 | 21 | 33 | 25 | 52 | 0 | 43 | 35 | 0 | 0 | 25 | 231 | 0 | 103 | 0 |  | 0 | 0 | 0 | 20 | 96 | 50 | 17 | 8 | 0 | 70 | 0 | 270 | 200 | 131 | 8 | 85 | 5 | 0 | 0 | 51 | 0 | 50 | 43 | 21 | 8 | 25 | 21 | 120 | 118 | 81 | 14 | 1.9 | 60 | 30 | 44 | 43 | 110 | 195 | 61 | 85 | 0 | 80 | 18 | 0 | 10 | 295 | 24 | 5 | 0 | 288 | 0 | 0 | 200 | 0 | 130 | 7.3 | 100 | 145 | 50 | 0 | 8 | 88 | 0 | 5.7 | 179 | 0 | 0 | 114 | 56 | 100 | 0 | 17 |  | 923 | 0 | 325 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 32 | 90 | 18 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 18 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 183 | 0 | 77 | 0 | 182 | 0 | 412 | 0 | 0 | 35 | 0 | 106 | 0 | 7.9 | 100 | 0 |  | 6829.9 | 3038.9 | 9868.8 | 3253 | 923 | 2011 | 2993 | 149 | 78 | 319 | 120 | 22.8 | 0 | 93.25
14:00 | 28 | 0 | 0 | 110 | 0 | 96 | 65 | 413 | 300 |  | 0 | 300 | 135 | 7 | 97 | 30 | 0 | 0 | 0 | 0 | 4 | 94 | 149 | 52 | 0 | 0 | 48 | 53 | 55 | 35 | 19 | 25 | 20 | 33 | 33 | 0 | 0 | 43 | 35 | 0 | 0 | 25 | 231 | 0 | 105 | 0 |  | 0 | 0 | 0 | 20 | 97 | 50 | 18 | 6 | 0 | 70 | 0 | 270 | 200 | 129 | 8 | 84 | 5 | 0 | 0 | 51 | 0 | 0 | 25 | 21 | 8 | 25 | 21 | 134 | 100 | 70 | 14 | 0.2 | 60 | 30 | 47 | 42 | 110 | 217 | 64 | 85 | 0 | 80 | 18 | 0 | 10 | 280 | 16 | 5 | 0 | 288 | 304 | 0 | 200 | 0 | 130 | 14.15 | 100 | 0 | 50 | 0 | 8 | 88 | 0 | 5.4 | 162 | 0 | 0 | 50 | 56 | 100 | 0 | 17 |  | 929 | 0 | 310 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 32 | 89 | 18 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 18 | 10 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 180 | 0 | 77 | 0 | 177 | 0 | 398 | 0 | 0 | 50 | 0 | 113 | 0 | 6.8 | 109 | 0 |  | 6702.75 | 3021.8 | 9724.55 | 3236 | 929 | 1921 | 2982 | 149 | 78 | 269 | 134 | 26.55 | 0 | 93.25
15:00 | 28 | 0 | 0 | 110 | 0 | 97 | 65 | 402 | 345 |  | 0 | 450 | 140 | 7 | 97 | 30 | 0 | 0 | 0 | 0 | 14 | 96 | 149 | 52 | 0 | 0 | 48 | 53 | 55 | 35 | 19 | 25 | 20 | 33 | 33 | 12 | 0 | 42 | 35 | 0 | 0 | 25 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 20 | 97 | 50 | 18 | 3 | 0 | 70 | 0 | 270 | 200 | 136 | 8 | 95 | 5 | 0 | 0 | 51 | 0 | 0 | 28 | 21 | 8 | 25 | 21 | 140 | 101 | 89 | 14 | 1.4 | 60 | 30 | 44 | 42 | 163 | 200 | 64 | 85 | 0 | 80 | 18 | 0 | 10 | 320 | 16 | 5 | 0 | 283 | 300 | 0 | 200 | 92 | 131 | 6.61 | 100 | 5 | 60 | 0 | 20 | 88 | 0 | 1.3 | 233 | 0 | 0 | 114 | 54 | 100 | 0 | 17 |  | 923 | 0 | 290 | 0 | 115 | 145 | 0 | 0 | 0 | 0 | 32 | 89 | 21 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 18 | 11 | 10 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 176 | 0 | 77 | 0 | 171 | 0 | 403 | 8 | 0 | 59 | 0 | 113 | 0 | 6 | 109 | 0 |  | 7070.31 | 3065 | 10135.31 | 3003 | 923 | 2213 | 3321 | 149 | 77 | 294 | 140 | 15.31 | 0 | 93.25
16:00 | 28 | 0 | 0 | 110 | 0 | 96 | 65 | 400 | 340 |  | 0 | 420 | 130 | 7 | 97 | 30 | 0 | 0 | 0 | 0 | 28 | 96 | 98 | 52 | 0 | 0 | 48 | 53 | 55 | 35 | 19 | 25 | 25 | 33 | 25 | 0 | 0 | 42 | 35 | 0 | 0 | 25 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 95 | 50 | 18 | 5 | 0 | 70 | 0 | 270 | 200 | 138 | 8 | 97 | 5 | 0 | 0 | 51 | 0 | 0 | 16 | 21 | 11 | 25 | 21 | 138 | 101 | 89 | 17 | 1 | 60 | 30 | 44 | 42 | 130 | 195 | 64 | 85 | 0 | 80 | 18 | 0 | 10 | 270 | 24 | 5 | 0 | 286 | 308 | 0 | 200 | 0 | 131 | 5.21 | 100 | 0 | 70 | 0 | 8 | 52 | 0 | 3.9 | 304 | 0 | 0 | 17 | 56 | 100 | 0 | 27 |  | 924 | 0 | 285 | 0 | 115 | 150 | 0 | 0 | 0 | 0 | 0 | 89 | 19 | 64 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 10 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 179 | 0 | 77 | 0 | 170 | 0 | 389 | 0 | 0 | 35 | 0 | 113 | 0 | 5.2 | 109 | 110 |  | 6729.11 | 3078.2 | 9807.31 | 3008 | 924 | 2080 | 3001 | 259 | 77 | 305 | 138 | 15.31 | 0 | 93.25
17:00 | 28 | 0 | 0 | 110 | 0 | 96 | 40 | 385 | 340 |  | 0 | 370 | 140 | 7 | 97 | 30 | 0 | 0 | 0 | 0 | 70 | 98 | 98 | 52 | 0 | 0 | 30 | 53 | 35 | 17 | 19 | 25 | 29 | 33 | 25 | 0 | 0 | 42 | 35 | 0 | 0 | 0 | 0 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 72 | 12 | 18 | 7 | 0 | 70 | 0 | 270 | 220 | 141 | 8 | 96 | 5 | 0 | 0 | 10 | 0 | 0 | 16 | 21 | 8 | 25 | 21 | 128 | 104 | 56 | 17 | 0.6 | 60 | 30 | 46 | 40 | 110 | 197 | 63 | 10 | 0 | 80 | 18 | 0 | 10 | 290 | 24 | 5 | 0 | 283 | 308 | 0 | 200 | 0 | 133 | 3.93 | 100 | 0 | 30 | 0 | 8 | 52 | 0 | 1.3 | 304 | 0 | 0 | 0 | 57 | 100 | 0 | 17 |  | 922 | 0 | 285 | 0 | 115 | 150 | 0 | 0 | 0 | 0 | 0 | 89 | 18 | 48 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 10 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 178 | 0 | 78 | 0 | 170 | 0 | 374 | 0 | 0 | 0 | 0 | 106 | 0 | 0.2 | 70 | 250 |  | 6313.83 | 3098.2 | 9412.03 | 2983 | 922 | 1876 | 2716 | 399 | 77 | 305 | 128 | 6.03 | 0 | 93.25
18:00 | 28 | 0 | 0 | 110 | 0 | 53 | 40 | 393 | 300 |  | 0 | 320 | 130 | 7 | 97 | 30 | 0 | 0 | 0 | 0 | 100 | 98 | 120 | 27 | 0 | 0 | 30 | 53 | 35 | 17 | 19 | 25 | 29 | 33 | 33 | 0 | 0 | 40 | 35 | 0 | 0 | 0 | 0 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 71 | 12 | 18 | 7 | 0 | 70 | 0 | 270 | 220 | 130 | 8 | 97 | 5 | 0 | 0 | 10 | 0 | 0 | 16 | 21 | 5 | 25 | 21 | 122 | 123 | 56 | 17 | 0 | 60 | 30 | 13 | 10 | 110 | 192 | 40 | 10 | 0 | 80 | 18 | 0 | 10 | 290 | 24 | 5 | 0 | 286 | 307 | 0 | 200 | 0 | 132 | 0.3 | 100 | 0 | 35 | 0 | 8 | 52 | 0 | 0.1 | 265 | 0 | 0 | 50 | 55 | 100 | 0 | 17 |  | 922 | 0 | 245 | 0 | 115 | 150 | 0 | 0 | 0 | 0 | 0 | 89 | 19 | 32 | 0 | 0 | 0 | 0 | 5 | 57 | 0 | 8 | 0 | 0 | 0 | 18 | 11 | 10 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 150 | 0 | 78 | 0 | 140 | 0 | 250 | 0 | 0 | 0 | 0 | 55 | 0 | 0.2 | 70 | 350 |  | 6125.4 | 2923.2 | 9048.6 | 2875 | 922 | 1557 | 2666 | 499 | 75 | 332 | 122 | 0.6 | 0 | 93.25
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 28 | 0 | 0 | 110 | 0 | 98 | 66 | 391 | 351 |  | 0 | 360 | 130 | 7 | 97 | 30 | 0 | 0 | 0 | 0 | 98 | 100 | 149 | 45 | 0 | 0 | 43 | 53 | 35 | 55 | 19 | 25 | 22 | 33 | 31 | 35 | 0 | 42 | 35 | 0 | 0 | 14 | 0 | 0 | 140 | 0 |  | 0 | 0 | 100 | 10 | 97 | 25 | 18 | 25 | 0 | 70 | 0 | 270 | 220 | 129 | 8 | 95 | 5 | 0 | 0 | 28 | 0 | 50 | 34 | 21 | 8 | 25 | 21 | 148 | 122 | 90 | 17 | 0 | 60 | 30 | 49 | 33 | 130 | 193 | 67 | 85 | 0 | 80 | 18 | 0 | 10 | 280 | 24 | 8 | 80 | 283 | 307 | 0 | 200 | 0 | 133 | 0 | 100 | 36 | 70 | 0 | 16 | 88 | 11 | 0 | 253 | 25 | 0 | 114 | 56 | 100 | 0 | 17 |  | 922 | 0 | 345 | 0 | 115 | 190 | 0 | 0 | 0 | 0 | 40 | 89 | 30 | 52 | 0 | 0 | 0 | 50 | 35 | 100 | 0 | 25 | 43 | 43 | 5 | 18 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 143 | 0 | 77 | 47 | 160 | 0 | 396 | 105 | 100 | 70 | 0 | 49 | 0 | 0 | 100 | 440 |  | 7234 | 3960 | 11194 | 3048 | 922 | 2055 | 3633 | 589 | 77 | 722 | 148 | 0 | 0 | 93.25
19:30 | 28 | 0 | 0 | 110 | 0 | 98 | 67 | 388 | 353 |  | 0 | 360 | 130 | 7 | 97 | 30 | 0 | 0 | 0 | 0 | 98 | 98 | 149 | 100 | 0 | 0 | 42 | 53 | 55 | 55 | 19 | 25 | 28 | 33 | 33 | 52 | 0 | 43 | 35 | 0 | 0 | 25 | 0 | 0 | 140 | 0 |  | 0 | 0 | 102 | 10 | 97 | 50 | 18 | 29 | 0 | 70 | 0 | 270 | 220 | 129 | 8 | 96 | 5 | 0 | 0 | 35 | 0 | 50 | 43 | 21 | 8 | 25 | 21 | 138 | 123 | 90 | 17 | 0 | 60 | 30 | 49 | 43 | 130 | 190 | 67 | 85 | 0 | 80 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 285 | 303 | 0 | 200 | 0 | 133 | 0 | 100 | 150 | 100 | 0 | 115 | 93 | 34 | 0 | 253 | 54 | 0 | 114 | 56 | 100 | 0 | 17 |  | 922 | 0 | 330 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 89 | 30 | 64 | 0 | 0 | 0 | 50 | 35 | 100 | 0 | 25 | 43 | 43 | 10 | 18 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 174 | 0 | 77 | 100 | 186 | 0 | 407 | 105 | 0 | 94 | 15 | 49 | 0 | 0 | 109 | 520 |  | 7627 | 4121 | 11748 | 3094 | 922 | 2110 | 3998 | 669 | 78 | 739 | 138 | 0 | 0 | 0
20:00 | 28 | 0 | 0 | 110 | 0 | 97 | 67 | 389 | 353 |  | 0 | 400 | 135 | 10 | 97 | 30 | 0 | 0 | 0 | 0 | 98 | 102 | 149 | 100 | 0 | 0 | 46 | 53 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 52 | 0 | 43 | 35 | 0 | 0 | 25 | 0 | 0 | 140 | 0 |  | 0 | 0 | 102 | 10 | 97 | 50 | 18 | 34 | 0 | 70 | 0 | 270 | 220 | 126 | 8 | 96 | 5 | 0 | 0 | 46 | 0 | 50 | 43 | 21 | 8 | 25 | 21 | 132 | 123 | 90 | 17 | 0 | 60 | 30 | 49 | 43 | 163 | 192 | 64 | 85 | 0 | 80 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 286 | 300 | 0 | 200 | 0 | 133 | 0 | 100 | 114 | 100 | 0 | 115 | 102 | 34 | 0 | 253 | 54 | 0 | 114 | 57 | 100 | 0 | 17 |  | 922 | 0 | 330 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 89 | 31 | 32 | 0 | 0 | 0 | 50 | 35 | 100 | 0 | 25 | 47 | 43 | 25 | 18 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 175 | 0 | 77 | 100 | 185 | 0 | 411 | 105 | 0 | 94 | 15 | 54 | 0 | 0 | 109 | 520 |  | 7686 | 4118 | 11804 | 3093 | 922 | 2193 | 3959 | 669 | 78 | 758 | 132 | 0 | 0 | 93.25
21:00 | 28 | 0 | 0 | 110 | 0 | 98 | 67 | 389 | 355 |  | 0 | 420 | 142 | 7 | 97 | 30 | 0 | 0 | 0 | 0 | 98 | 102 | 149 | 100 | 0 | 0 | 41 | 53 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 52 | 0 | 44 | 35 | 0 | 0 | 25 | 0 | 0 | 140 | 0 |  | 0 | 0 | 102 | 10 | 97 | 50 | 0 | 35 | 0 | 70 | 0 | 270 | 220 | 129 | 8 | 96 | 5 | 0 | 0 | 51 | 0 | 48 | 43 | 21 | 8 | 25 | 21 | 154 | 121 | 90 | 17 | 0 | 60 | 30 | 50 | 43 | 163 | 193 | 64 | 85 | 0 | 80 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 286 | 200 | 0 | 200 | 0 | 133 | 0 | 100 | 114 | 100 | 0 | 115 | 105 | 34 | 0 | 253 | 54 | 0 | 114 | 56 | 100 | 0 | 17 |  | 923 | 0 | 320 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 89 | 29 | 32 | 0 | 0 | 0 | 50 | 35 | 98 | 0 | 25 | 43 | 43 | 33 | 18 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 177 | 0 | 77 | 100 | 185 | 0 | 404 | 105 | 0 | 94 | 15 | 95 | 0 | 0 | 109 | 520 |  | 7612 | 4145 | 11757 | 3069 | 923 | 2204 | 3901 | 669 | 79 | 758 | 154 | 0 | 0 | 93.25
22:00 | 28 | 0 | 0 | 110 | 0 | 96 | 67 | 395 | 354 |  | 0 | 420 | 135 | 7 | 95 | 55 | 0 | 0 | 0 | 0 | 99 | 102 | 149 | 29 | 0 | 0 | 41 | 53 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 52 | 0 | 45 | 35 | 0 | 0 | 25 | 76 | 0 | 139 | 0 |  | 0 | 0 | 102 | 10 | 97 | 50 | 11 | 38 | 0 | 70 | 0 | 270 | 220 | 134 | 8 | 96 | 5 | 0 | 0 | 51 | 0 | 50 | 43 | 21 | 8 | 25 | 21 | 156 | 121 | 90 | 17 | 0 | 60 | 30 | 50 | 43 | 163 | 193 | 64 | 85 | 0 | 80 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 286 | 97 | 0 | 200 | 0 | 132 | 0 | 100 | 114 | 100 | 0 | 115 | 105 | 0 | 0 | 252 | 17 | 0 | 114 | 56 | 100 | 0 | 17 |  | 923 | 0 | 310 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 89 | 30 | 32 | 0 | 0 | 0 | 50 | 35 | 98 | 0 | 25 | 43 | 43 | 32 | 18 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 177 | 0 | 77 | 100 | 179 | 0 | 387 | 105 | 0 | 94 | 15 | 113 | 0 | 0 | 109 | 520 |  | 7494 | 4130 | 11624 | 3150 | 923 | 2198 | 3689 | 669 | 80 | 759 | 156 | 0 | 0 | 93.25
23:00 | 28 | 0 | 0 | 110 | 0 | 96 | 68 | 350 | 353 |  | 0 | 420 | 147 | 7 | 95 | 55 | 0 | 0 | 0 | 0 | 99 | 102 | 149 | 26 | 0 | 0 | 41 | 53 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 52 | 0 | 45 | 35 | 0 | 0 | 25 | 75 | 0 | 139 | 0 |  | 0 | 0 | 102 | 10 | 97 | 50 | 11 | 42 | 0 | 70 | 0 | 270 | 220 | 141 | 8 | 96 | 5 | 0 | 0 | 51 | 0 | 0 | 43 | 21 | 8 | 25 | 21 | 154 | 123 | 90 | 17 | 0 | 60 | 30 | 50 | 43 | 163 | 203 | 64 | 85 | 0 | 80 | 18 | 0 | 9 | 290 | 24 | 8 | 0 | 286 | 0 | 0 | 200 | 0 | 132 | 0 | 100 | 50 | 100 | 0 | 115 | 105 | 0 | 0 | 252 | 17 | 0 | 114 | 56 | 100 | 0 | 17 |  | 924 | 0 | 310 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 89 | 31 | 32 | 0 | 0 | 0 | 50 | 35 | 96 | 0 | 25 | 43 | 43 | 32 | 18 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 156 | 0 | 78 | 70 | 176 | 0 | 413 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 109 | 520 |  | 7266 | 4088 | 11354 | 3099 | 924 | 2229 | 3492 | 669 | 80 | 707 | 154 | 0 | 0 | 93.25
24:00 | 28 | 0 | 0 | 110 | 0 | 96 | 68 | 344 | 357 |  | 0 | 420 | 143 | 7 | 95 | 55 | 0 | 0 | 0 | 0 | 99 | 102 | 149 | 26 | 0 | 0 | 41 | 53 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 52 | 0 | 45 | 35 | 0 | 0 | 25 | 85 | 0 | 139 | 0 |  | 0 | 0 | 68 | 10 | 97 | 50 | 14 | 42 | 0 | 70 | 0 | 270 | 220 | 145 | 8 | 96 | 5 | 0 | 0 | 51 | 0 | 0 | 43 | 21 | 8 | 25 | 21 | 148 | 126 | 90 | 17 | 0 | 60 | 30 | 50 | 43 | 163 | 195 | 64 | 85 | 0 | 80 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 286 | 0 | 0 | 200 | 0 | 132 | 0 | 100 | 0 | 100 | 0 | 115 | 105 | 0 | 0 | 252 | 17 | 0 | 114 | 57 | 100 | 0 | 17 |  | 924 | 0 | 310 | 0 | 115 | 170 | 0 | 0 | 0 | 0 | 40 | 89 | 30 | 32 | 0 | 0 | 0 | 50 | 35 | 96 | 0 | 0 | 43 | 43 | 32 | 18 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 152 | 0 | 78 | 0 | 174 | 0 | 402 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 109 | 520 |  | 7184 | 3945 | 11129 | 3099 | 924 | 2222 | 3344 | 669 | 80 | 643 | 148 | 0 | 0 | 93.25
KWH | 571000 | 0 | 0 | 2709000 | 0 | 2242500 | 1522528 | 8924160 | 8005000 |  | 0 | 8899500 | 3396975 | 204480 | 2172072 | 953073 | 0 | 0 | 0 | 0 | 854400 | 2199024 | 2666400 | 726317 | 0 | 0 | 860256 | 1211400 | 1122476 | 984869 | 355284 | 600000 | 537300 | 819700 | 691800 | 484812 | 0 | 973680 | 836000 | 0 | 0 | 311760 | 2970555 | 0 | 2838806 | 0 |  | 0 | 0 | 576414 | 142200 | 1728000 | 651360 | 369408 | 566400 | 0 | 1682150 | 0 | 7106900 | 4048000 | 3620000 | 200727 | 2107810 | 128448 | 0 | 0 | 1178515 | 0 | 318184 | 709608 | 458424 | 208260 | 327800 | 482120 | 3139200 | 2981920 | 1577280 | 317880 | 10350 | 1420000 | 716400 | 1085400 | 1003824 | 3552872 | 4546000 | 1400640 | 1930560 | 0 | 1925720 | 418000 | 0 | 246420 | 7173800 | 548376 | 159000 | 47424 | 6744434 | 2367463 | 0 | 4776000 | 54371 | 2952000 | 91125 | 2400000 | 1129440 | 1380000 | 0 | 1111200 | 1450728 | 101200 | 33000 | 5331818 | 203565 | 0 | 1496820 | 1176840 | 2437440 | 0 | 453120 |  | 20462545 | 0 | 8064000 | 0 | 2734080 | 3576497 | 0 | 0 | 0 | 0 | 534375 | 2083127 | 496274 | 754848 | 0 | 0 | 0 | 284607 | 189577 | 1123416 | 0 | 145435 | 228229 | 334080 | 143000 | 442080 | 256860 | 217008 | 0 | 0 | 3648900 | 0 | 0 | 0 | 0 | 4304900 | 0 | 1868052 | 472320 | 4580655 | 0 | 9289490 | 707040 | 60071 | 1118400 | 46800 | 2007360 | 0 | 44608 | 2053632 | 9124200 |  | 158147485 | 81396466 | 239543951 | 75240551 | 20462545 | 49960802 | 66872666 | 12773100 | 1809680 | 9106324 | 3139200 | 179083 | 0
Fuel Cost | 936440 | 0 | 0 | 3982230 | 0 | 2960100 | 2588297.6 | 9013401.6 | 8245150 |  | 0 | 9700455 | 3770642.25 | 1552003.2 | 14965576.08 | 8062997.58 | 0 | 0 | 0 | 0 | 6433632 | 20055098.88 | 26237376 | 6696642.74 | 0 | 0 | 7819727.04 | 8843220 | 8676739.48 | 9710808.34 | 266463 | 450000 | 0 | 0 | 0 | 4688132.04 | 0 | 262893.6 | 225720 | 0 | 0 | 2896250.4 | 3237904.95 | 0 | 4825970.2 | 0 |  | 0 | 0 | 5591215.8 | 1358010 | 15033600 | 5158771.2 | 465454.08 | 1682208 | 0 | 2489582 | 0 | 5259106 | 4048000 | 3330400 | 258937.83 | 2423981.5 | 145146.24 | 0 | 0 | 2015260.65 | 0 | 3213658.4 | 6776756.4 | 582198.48 | 156195 | 573650 | 361590 | 23544000 | 3160835.2 | 14321702.4 | 403707.6 | 164979 | 2328800 | 1146240 | 1932012 | 1565965.44 | 4050274.08 | 4727840 | 2759260.8 | 3687369.6 | 0 | 3331495.6 | 915420 | 0 | 502696.8 | 7245538 | 411282 | 120840 | 806682.24 | 50987921.04 | 40199521.74 | 0 | 24835200 | 909083.12 | 29047680 | 1065251.25 | 19560000 | 12254424 | 9729000 | 0 | 10134144 | 13709379.6 | 881452 | 0 | 40308544.08 | 1773051.15 | 0 | 14938263.6 | 10085518.8 | 16233350.4 | 0 | 0 |  | 117864259.2 | 0 | 8467200 | 0 | 21489868.8 | 49570248.42 | 0 | 0 | 0 | 0 | 5568187.5 | 2353933.51 | 769224.7 | 7367316.48 | 0 | 0 | 0 | 2800532.88 | 1926102.32 | 9942231.6 | 0 | 1966281.2 | 2211539.01 | 3237235.2 | 1387100 | 848793.6 | 398133 | 164275.056 | 0 | 0 | 19777038 | 0 | 0 | 0 | 0 | 5682468 | 0 | 2802078 | 8034163.2 | 5359366.35 | 0 | 9196595.1 | 7381497.6 | 1021807.71 | 10613616 | 441792 | 15577113.6 | 0 | 492918.4 | 15176340.48 | 40055238 |  | 611806319.1 | 379944494.916 | 991750814.016 | 83880677.166 | 117864259.2 | 60449089.4 | 541088745.57 | 59832276 | 488613.6 | 102880004.43 | 23544000 | 1723148.65 | 0
Yesterday Day Peak | 28 | 0 | 0 | 110 | 0 | 93 | 66 | 389 | 350 |  | 0 | 420 | 135 | 7 | 80 | 41 | 0 | 0 | 0 | 0 | 0 | 94 | 149 | 52 | 0 | 0 | 48 | 53 | 55 | 55 | 19 | 25 | 21 | 33 | 25 | 52 | 0 | 42 | 35 | 0 | 0 | 25 | 231 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 91 | 50 | 16 | 3 | 0 | 70 | 0 | 270 | 200 | 144 | 8 | 85 | 5 | 0 | 0 | 51 | 0 | 50 | 43 | 18 | 8 | 25 | 15 | 118 | 123 | 73 | 17 | 1.2 | 60 | 30 | 44 | 43 | 163 | 193 | 62 | 85 | 0 | 80 | 18 | 0 | 10 | 320 | 24 | 5 | 0 | 286 | 0 | 0 | 200 | 0 | 109 | 19.1 | 90 | 118 | 16 | 0 | 11 | 63 | 0 | 2.3 | 179 | 0 | 0 | 114 | 56 | 100 | 0 | 17 |  | 923 | 0 | 325 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 16 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 182 | 0 | 78 | 0 | 180 | 0 | 409 | 0 | 0 | 0 | 0 | 37 | 0 | 7.6 | 60 | 0 |  | 9620.2 | DayPeak
Yesterday Evening Peak | 28 | 0 | 0 | 110 | 0 | 97 | 67 | 389 | 353 | 0 | 0 | 400 | 135 | 10 | 97 | 30 | 0 | 0 | 0 | 0 | 98 | 102 | 149 | 100 | 0 | 0 | 46 | 53 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 52 | 0 | 43 | 35 | 0 | 0 | 25 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 102 | 10 | 97 | 50 | 18 | 34 | 0 | 70 | 0 | 270 | 220 | 126 | 8 | 96 | 5 | 0 | 0 | 46 | 0 | 50 | 43 | 21 | 8 | 25 | 21 | 132 | 123 | 90 | 17 | 0 | 60 | 30 | 49 | 43 | 163 | 192 | 64 | 85 | 0 | 80 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 286 | 300 | 0 | 200 | 0 | 133 | 0 | 100 | 114 | 100 | 0 | 115 | 102 | 34 | 0 | 253 | 54 | 0 | 114 | 57 | 100 | 0 | 17 |  | 922 | 0 | 330 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 89 | 31 | 32 | 0 | 0 | 0 | 50 | 35 | 100 | 0 | 25 | 47 | 43 | 25 | 18 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 175 | 0 | 77 | 100 | 185 | 0 | 411 | 105 | 0 | 94 | 15 | 54 | 0 | 0 | 109 | 520 |  | 11804 | EvPeak
Forecast for Evening | 28 | 0 | 0 | 110 | 0 | 100 | 70 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 0 | 0 | 0 | 0 | 100 | 102 | 149 | 100 | 0 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 43 | 35 | 0 | 0 | 25 | 165 | 0 | 140 | 0 | 0 | 0 |  | 100 | 100 | 97 | 50 | 18 | 30 | 0 | 80 | 0 | 360 | 360 | 220 | 8 | 96 | 5 | 5 | 0 | 51 | 0 | 50 | 43 | 21 | 11 | 25 | 21 | 173 | 160 | 80 | 17 | 0 | 60 | 30 | 51 | 44 | 163 | 210 | 66 | 86 | 0 | 80 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 133 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 0 | 300 | 54 | 110 | 114 | 60 | 100 | 0 | 104 |  | 932 | 16 | 410 | 0 | 115 | 220 | 0 | 0 | 30 | 60 | 40 | 90 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 0 | 50 | 50 | 43 | 30 | 18 | 11 | 11 | 0 | 0 | 150 | 0 | 10 | 0 | 0 | 220 | 0 | 80 | 100 | 220 | 0 | 414 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 660
Forecast for Day | 28 | 0 | 0 | 110 | 0 | 100 | 70 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 0 | 0 | 0 | 0 | 98 | 102 | 149 | 100 | 0 | 0 | 49 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 35 | 0 | 43 | 35 | 0 | 0 | 25 | 165 | 0 | 110 | 0 | 0 | 0 |  | 100 | 100 | 97 | 50 | 18 | 30 | 0 | 80 | 0 | 360 | 360 | 220 | 8 | 96 | 5 | 5 | 0 | 51 | 0 | 0 | 43 | 21 | 11 | 25 | 21 | 163 | 160 | 80 | 17 | 1.6 | 60 | 30 | 51 | 44 | 163 | 210 | 66 | 86 | 0 | 80 | 18 | 0 | 10 | 341 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 80 | 133 | 20 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 5 | 300 | 50 | 50 | 114 | 60 | 100 | 0 | 104 |  | 932 | 0 | 350 | 0 | 115 | 220 | 0 | 0 | 0 | 0 | 40 | 90 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 50 | 0 | 43 | 0 | 18 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 |  | 80 | 60 | 220 | 0 | 414 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 660
Generation at 08:00(Today) | 28 | 0 | 0 | 110 | 0 | 97 | 67 | 347 | 279 | 0 | 0 | 400 | 150 |  | 86 | 15 | 0 | 0 | 0 | 0 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 0 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 41 | 35 | 0 | 0 | 0 | 151 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 9 | 0 | 70 | 0 | 270 | 220 | 134 | 8 | 96 | 5 | 0 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 25 | 15 | 112 | 156 | 48 | 17 | 0.6 | 60 | 30 | 50 | 44 | 100 | 218 | 63 | 85 | 0 | 80 | 18 | 0 | 10 | 300 | 16 | 5 | 0 | 65 | 0 | 0 | 200 | 0 | 133 | 9.5 | 100 | 0 | 10 | 0 | 8 | 0 | 0 | 2.8 | 217 | 0 | 0 | 0 | 17 | 100 | 0 | 17 | 0 | 924 | 0 | 360 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 160 | 0 | 23 | 0 | 160 | 0 | 392 | 0 | 0 | 0 | 0 | 50 | 0 | 3.1 | 35 | 450 | 0
199
| Minimum Generation |  | 8032.8 | 7:00
| Highest Generation |  | 11804 | 20:00
| Day Peak Generation |  | 9620.2 | 12:00
| Evening Peak Generation |  | 11804 | 20:00
| HVDC Max Flow |  | 929 | 14:00
| HVDC EvPeak Flow |  | 922 | 20:00
| Load factor L.F |  | 84.56%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-08-24
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-08-23 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9620.2 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 8577 | MW
Evening Peak Generation : |  | 11804 | MW Hour : | 20:00 | Available Max Generation : |  | 14576 | MW
E.P. Demand (at gen end) : |  | 11804 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 11900 | MW
Maximum Generation : |  | 11804 | MW Hour : | 20:00 | Reserve(Generation end) |  | 2676 | MW
Total Gen. (MKWH) : |  | 239.544 | System Load Factor : | 84.56% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -9 | MW at | 10:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-08-24
Actual : | 93.24 | Ft.(MSL) , | Rule curve : | 96.36 | Ft.( MSL )
Gas Consumed : | Total = | 1056.37 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 144329766.566
: |  | Coal : | 59832276 | Oil : | 643968750 | Total : | 848130792.566
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4245.4335 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1445.8392 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1295.8083 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1171.0086 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1058.1482 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 853.8936 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 474.6798 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 219.7812 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 658.5784 |  |  | 0 | 0%
Total | 0 |  | 11423.1709 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Bibiyana #3
3) Ghorasal Unit-2,3,4,7
4) Ashuganj unit-3,5
5) Bhola-225 MW GT-2 & ST
6) Kaptai-2
7) Raozan #1,2
8) Sirajganj #1
9) Baghabari-71 & 100 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Tongi-Kabirpur 132 MW kV Ckt-1 & 2 tripped at 09:43 from Tongi end showing E/F, Dist. Z2 relay and |  |  |  |  | About 300 MW power interruption occurred under Kodda, Manikganj
were switched on at 10:10,10:05 respectively. |  |  |  |  | Rajendrapur S/S area from 09:43 to 10:05.
b) Kabirpur-Manikganj 132 MW kV Ckt-1 tripped at 09:43 from Kabirpur end showing E/F, Dist. Z2 relay and
was switched on at 10:10.
c) Kodda-Gazipur 100 MW 132 MW kV Ckt tripped at 09:43 from Kodda end showing O/C, Dist. Z2 relay and
was switched on at 10:08.
d) Barapukuria 132/33 kV T4 transformer tripped at 12:01 showing HV,L/O at 132 kV end & no relay at 33 kV
end and was switched on at 13:04.
e) Natore-Bogura 132 kV Ckt-1 was under shut down from 08:57 to 17:39 for C/M.
f) Purbasadipur-Thakurgaon 132 kV Ckt-1 was under shut down from 11:09 to 16:15 for C/M.
g) Kaliakoir-Tangail 132 kv Ckt-1 tripped at 10:06 from Tangail end showing Dist. R-phase relay and was
switched on at 10:19.
h) Aminbazar 230/132 kV T2 transformer was under shut down from 11:37 to 18:48 for D/W.
i) Tongi 132 kV Metro Rail Bay was shut down at 13:22 for D/W.
j) Mymensing-Bhaluka 132 kV Ckt-2 was under shut down from 13:31 to 14:18 due to red hot maintenance
CB clamp at at Bhaluka end.
k) Sikalbaha 225 MW tripped at 14:37 due to gas valve problem.
l) Payra 660 MW was synchronized at 15:12.
m) Ashuganj-Sirajganj 230 kV Ckt-1 tripped at 16:25 due to flashing Y-phase line DS at Ashuganj end and
n) Sikalbaha 225 MW GT was synchronized at 17:51
o) Sikalbaha 225 MW tripped at 17:57 due to gas valve problem.
p) Sikalbaha 225 MW GT was synchronized at 21:05.
q) Palashbari-Mohosthan 132 kV Ckt-1 & 2 tripped at 20:17 showing Dist.A-phase at Ckt-2 & O/C relay at
Ckt-1 and were switched on at 20:20, 20:55 respectively.
r) Dhamrai 132/33 kV T2 transformer tripped at 22:28 showing master relay, O/C relay at 33 kV end and was |  |  |  |  | About 38 MW power interruption occurred under Dhamrai S/S area
switched on at 22:47. |  |  |  |  | from 22:38 to 22:47.
s) Sherpur 132/33 kV T1 transformer tripped at 07:10(24/08/2020) showing search trip, oil Tc/gas at 33 kV end

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-08-23 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 28 | 571000 | Unit-1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 110 | 2709000
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 67 | 1522528 | Engine problem
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 97 | 2242500 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 389 | 8924160 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 353 | 8005000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 8899500 | Frequency control.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 10 | 204480 | Fuel Shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 135 | 3396975 | GT-1 Under S/D.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 97 | 2172072
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 30 | 953073 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 100 | 726317
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 355284
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 98 | 854400
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 2199024
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 46 | 860256
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 1211400
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 2666400
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1122476
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 984869
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1137300 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 819700
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 691800
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 52 | 484812
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 286 | 6744434
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 300 | 2367463
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 54371 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 133 | 2952000 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 102 | 1450728
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 453120 | Fuel Shortage
| Dhaka area Total |  |  |  | 5895 | 3404 | 67736442
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 311760
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 91125
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 651360
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 78 | 1809680 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 2970555 | Machine problem
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 140 | 2838806
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 34 | 101200 | Low demand
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 576414
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 142200 | Low demand
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2400000
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 369408
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 34 | 566400
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 97 | 1728000 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 33000
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 253 | 5331818 | Transformer O/L
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 203565
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2437440
| Chattogram area Total |  |  |  | 2266 | 1095 | 22562731
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 70 | 1682150 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 126 | 3620000 | Gas shortage
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 270 | 7106900 | Gas shortage
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 220 | 4048000 | Gas shortage
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 5 | 128448 | Gas shortage.
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 0 | 0 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 46 | 1178515
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 100 | 1380000 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 318184
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 96 | 2107810 | ST under maint.
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 114 | 1129440 | Low demand
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 458424
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 208260
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 132 | 3139200
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 327800 | Engine problem
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 709608 | Engine problem
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 482120
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 47424 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1496820
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 57 | 1176840 | Fuel shortage
| Cumilla Area Total |  |  |  | 2980 | 1526 | 30946670
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 123 | 2981920 | Engine problem
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 317880 | Engine problem
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 90 | 1577280
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10350
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 4776000
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1111200 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 545 | 10774630
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1420000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 716400 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3552872
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 192 | 4546000 | ST under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 49 | 1085400
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 43 | 1003824
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 159000 | Engine problem
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 64 | 1400640 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1930560
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 80 | 1925720 | Engine problem
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 418000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 548376
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7173800 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 246420
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1116 | 26127012
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 922 | 20462545
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 2734080
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 200 | 3576497
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 330 | 8064000 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 534375
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 472320
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 707040
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 15 | 46800 | Low demand
| Khulna Area Total |  |  |  | 2284 | 1827 | 36597657
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 754848 | Low demand
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 31 | 496274
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 89 | 2083127 | GT-2 Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 77 | 1868052 | Engine problem
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 520 | 9124200 | Low demand
| Barisal Area Total |  |  |  | 1054 | 749 | 14326501
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 284607
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 35 | 189577
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 25 | 145435 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 47 | 228229
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage.
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 175 | 4304900 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 185 | 4580655 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 411 | 9289490 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 143000
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 18 | 442080
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 11 | 256860
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 217008
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 334080
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 1123416
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 60071 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 94 | 1118400 | Engine problem
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 2053632
| Rajshahi Area Total |  |  |  | 2183 | 1339 | 24771440
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 149 | 3648900 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 54 | 2007360 | Engine problem
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 44608
| Rangpur Area Total |  |  |  | 605 | 203 | 5700868
| Total |  |  |  | 19892 | 11804 | 239543951
| Eastern Grid Total |  |  |  | 13766 | 7686 | 158147485
| Western Grid Total |  |  |  | 6126 | 4118 | 81396466
| National Grid Total |  |  |  | 19892 | 11804 | 239543951
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-08-23
| (a) ENTIRE EASTERN GRID : |  | 7581 | MW | (b) ENTIRE WESTERN GRID : |  | 3741 | MW
| i) Dhaka area |  | 3927 | MW | i) Khulna area |  | 1429 | MW
| ii) Chittagong area |  | 1126 | MW | ii) Rajshahi area |  | 1243 | MW
| iii) Comilla area |  | 1083 | MW | iii) Barisal area |  | 310 | MW
| iv) Mymensingh area |  | 957 | MW | iv) Rangpur area |  | 759 | MW
| v) Sylhet area |  | 488 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11322 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 132 | 12:00 | Sherpur | 114 | 20:00 | Jhenida | 108 | 19:00
| Munsiganj | 122 | 22:00 | Srimongal | 53 | 22:00 | Bottail | 126 | 19:00
| Sonargaon | 82 | 19:30 | Shahjibazar | 130 | 21:00 | G.K Project | 55 | 21:00
| Shyampur | 198 | 0:00 | Fenchuganj | 47 | 20:00 | Faridpur | 186 | 0.91667
| Bhulta | 202 | 12:00 | Kulawara | 35 | 19:00 | Madaripur | 94 | 0.875
| Madanganj | 44 | 23:00 | Sylhet | 130 | 19:00 | Sariatpur | 60 | 22:00
| Shitalakhya | 109 | 15:00 | Chatak | 31 | 21:00 | Gopalganj | 81 | 21:00
| Rahim steel | 17 | 17:00 | Sunamganj | 50 | 20:00 | Bagerhat | 90 | 19:30
| Matuail | 78 | 10:00 | Biani Bazar | 62 | 22:00 | Mongla | 40 | 9:00
| Ghorasal | 80 | 21:00 | Comilla (S) | 156 | 22:00 | Satkhira | 100 | 0.79167
| Narsingdi | 169 | 22:00 | Comilla(N) | 131 | 20:00 | Gallamari | 39 | 10:00
| Haripur (SBU) | 111 | 9:00 | Chandpur | 99 | 21:00 | Magura | 54 | 0.8125
| Ullon | 54 | 19:00 | Feni | 111 | 19:00 | Norail | 37 | 19:00
| Hasnabad | 190 | 19:00 | Chowmuhani | 162 | 23:00 | Chuadanga | 89 | 20:00
| Magbazar | 93 | 14:00 | Ashuganj | 56 | 24:00 | Barisal(N) | 38 | 0.8125
| Maniknagar | 94 | 13:00 | Daudkandi | 134 | 21:00 | Barisal (S) | 88 | 0.79167
| Bangabhaban | 34 | 11:00 | B.Baria | 152 | 21:00 | Patuakhali | 102 | 0.875
| Narinda | 80 | 14:00 | Ramganj | 102 | 21:00 | Bhandaria | 50 | 0.8125
| Dhanmondi | 151 | 12:00 | Chaddagram | 36 | 19:30 | Borhan Uddin | 40 | 22:00
| Lalbag | 87 | 14:00 | PHP | 10 | 8:00 | Ishurdi | 62 | 19:00
| Madartek | 66 | 22:00 | Madunaghat | 52 | 21:00 | Ruppur Paromanobik | 2 | 7:00
| Dhaka University |  |  | Hathazari | 98 | 0.8125 | Natore | 127 | 21:00
| Fatullah | 31 | 0.66667 | Khulshi | 186 | 0.58333 | Bogra | 162 | 21:00
| Mirpur | 93 | 13:00 | Halishahar | 124 | 0.625 | Noagaon | 126 | 21:00
| Kalyanpur | 81 | 19:00 | Baraulia | 150 | 0.041667 | Rajshahi | 139 | 21:00
| Gulshan | 114 | 13:00 | Sikalbaha | 26 | 0.77083 | Rajshahi New | 10 | 20:00
| Uttara | 75 | 19:00 | Dohazari | 90 | 0.875 | C.Nawabganj | 67 | 20:00
| Uttara New | 27 | 19:00 | Cox'sbazar | 95 | 0.79167 | Amnura | 46 | 20:00
| Kamrangirchar | 88 | 19:00 | Chandraghona | 30 | 0.91667 | Pabna | 118 | 20:00
| Savar | 146 | 12:00 | Kaptai | 4.5 | 0.79167 | Shahjadpur | 101 | 21:00
| Bhasantec | 136 | 13:00 | A. Khaer Stl. | 0 | 0.041667 | Serajganj | 108 | 21:00
| Agargaon | 64 | 13:00 | Bakulia | 97 | 0.77083 | Niyamatpur | 58 | 21:00
| Satmosjid | 80 | 14:00 | Julda | 17 | 0.041667 | Joypurhat | 55 | 21:00
| Tongi | 127 | 0.41667 | TK chemical | 21.4 | 0.041667 | Sherpur(Bogura) | 48 | 21:00
| Kabirpur | 217 | 15:00 | Modern Steel | 0 | 0.041667 | Mohastangor | 50 | 21:00
| Basundhara | 125 | 19:00 | Shahmirpur | 20.5 | 0.66667 | Rangpur | 138 | 19:30
| Manikganj | 72 | 22:00 | Khagrachhari | 24 | 0.77083 | Lalmonirhat | 51 | 1:00
| Joydevpur | 156 | 16:00 | Matarbari | 29 | 0.8125 | Saidpur | 110 | 19:30
| New Tongi | 101 | 12:00 | Baroiar Hat | 36 | 0.79167 | Purbasadipur | 104 | 23:00
| Korda | 228 | 16:00 | Rangamati | 12 | 0.79167 | Thakurgaon | 78 | 22:00
| Dhamrai | 100 | 20:00 | Abul Khair 230 | 49 | 0.45833 | Palashbari | 131 | 20:00
| Rajendrapur | 90 | 21:00 | BSRM | 102 | 0.16667 | Barapukuria | 50 | 21:00
| Valuka | 100 | 19:00 | GPH Ispat | 77 | 0.20833 | Panchagar | 51 | 21:00
| Tangail | 166 | 21:00 | Goalpara | 24 | 0.54167 | Joldhaka | 26 | 19:00
| Mymensing | 234 | 19:30 | Central s/s | 87 | 19:00 | Kurigram | 54 | 19:00
| Kishorganj | 143 | 24:00 | Noapara | 87 | 19:00
| Netrokona | 107 | 19:00 | Jessore | 112 | 19:30
| Jamalpur | 137 | 21:00 | Benapol | 19 | 19:30
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-08-23 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 398 | 20:00 | 392 | 19:00 | Kaliakoir | 382 | 0.20833 | 373 | 0.45833
| Bheramara | 410 | 7:00 | 389 | 1:00 | Bhulta | 390 | 0.16667 | 382 | 0.375
| Ashuganj(N) | 397 | 18:30 | 388 | 11:00 | Gopalganj | 418 | 0.375 | 384 | 0.5
| Payra | 420 | 9:00 | 380 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 236 | 1:00 | 235 | 24:00 | Comilla (N) | 238 | 19:00 | 232 | 1:00
| Ishurdi | 236 | 6:00 | 226 | 19:30 | Hathazari | 230 | 19:00 | 221 | 8:00
| Ashuganj | 237 | 12:00 | 235 | 9:00 | Megnaghat | 235 | 17:00 | 229 | 10:00
| Serajganj | 232 | 4:00 | 227 | 19:30 | Fenchuganj | 240 | 10:00 | 236 | 13:00
| Baghabari | 241 | 4:00 | 236 | 1:00 | Siddhirganj | 232 | 19:00 | 228 | 10:00
| Barapukuria | 234 | 4:00 | 223 | 19:00 | Maniknagar | 231 | 20:00 | 224 | 11:00
| Bogra | 226 | 18:30 | 214 | 19:30 | Agargaon | 230 | 4:00 | 223 | 11:00
| Rajshahi | 235 | 18:30 | 220 | 12:00 | Barisal | 247 | 7:00 | 235 | 1:00
| Khulna South | 239 | 18:30 | 207 | 17:00 | AKSML | 225 | 18:30 | 218 | 10:00
| Rampura | 229 | 20:00 | 223 | 11:00 | BSRM | 228 | 18:30 | 221 | 8:00
| Haripur | 230 | 18:00 | 225 | 1:00 | Bibiyana | 238 | 3:00 | 232 | 16:00
| Hasnabad | 231 | 20:00 | 225 | 9:00 | Bhulta | 232 | 19:00 | 226 | 17:00
| Shyampur | 229 | 14:00 | 221 | 11:00 | Ashuganj (S) | 238 | 19:00 | 233 | 11:00
| Aminbazar | 231 | 4:00 | 223 | 12:00 | Kaliakoir | 234 | 19:30 | 228 | 10:00
| Tongi | 230 | 19:00 | 224 | 15:00 | GPH | 225 | 19:30 | 219 | 3:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 134 | 18:30 | 127 | 11:00 | Hathazari | 138 | 0.79167 | 132 | 0.375
| Munsiganj | 139 | 18:30 | 131 | 9:00 | Khulshi | 136 | 0.79167 | 130 | 0.083333
| Sonargaon | 134 | 19:00 | 126 | 9:00 | Halishahar | 140 | 0.83333 | 131 | 0.375
| Shyampur | 135 | 14:00 | 130 | 11:00 | Baraulia | 138 | 0.79167 | 130 | 0.66667
| Bhulta | 124 | 18:30 | 116 | 11:00 | Sikalbaha | 139 | 19:00 | 133 | 0.29167
| Madanganj | 136 | 3:00 | 129 | 0:00 | Dohazari | 136 | 18:30 | 130 | 0.041667
| Shitalakhya | 142 | 2:00 | 133 | 13:00 | Cox'sbazar | 127 | 0.41667 | 123 | 0.041667
| Rahim steal | 135 | 18:00 | 129 | 9:00 | Chandraghona | 137 | 0.79167 | 132 | 0.375
| Matuail | 134 | 18:30 | 127 | 11:00 | Kaptai | 136 | 19:30 | 132 | 0.625
| Ghorasal | 138 | 19:30 | 130 | 15:00 | A. Khaer Stl. | 135 | 0.79167 | 131 | 3:00
| Narsinghdi | 130 | 18:00 | 122 | 1:00 | Bakulia | 138 | 0.79167 | 132 | 0.33333
| Haripur (SBU) | 136 | 18:00 | 128 | 11:00 | Julda | 139 | 0.79167 | 133 | 0.33333
| Ullon | 134 | 3:00 | 129 | 11:00 | TK Chemical | 138 | 0.8125 | 133 | 16:00
| Hasnabad | 138 | 15:00 | 135 | 4:00 | Modern Steel | 137 | 0.8125 | 131 | 0.33333
| Magbazar | 135 | 4:00 | 129 | 11:00 | Shahmirpur | 139 | 0.79167 | 134 | 0.041667
| Maniknagar | 132 | 3:00 | 128 | 11:00 | Khagrachhari | 135 | 0.77083 | 131 | 0.125
| Bangabhaban | 132 | 3:00 | 128 | 11:00 | Matarbari | 130 | 0.041667 | 128 | 0.16667
| Narinda | 132 | 3:00 | 128 | 11:00 | Baroiar Hat | 138 | 0.41667 | 131 | 0.041667
| Dhanmondi | 134 | 3:00 | 129 | 11:00 | Rangamati | 136 | 0.77083 | 132 | 2:00
| Lalbag | 138 | 20:00 | 131 | 11:00 | Goalpara S/S | 138 | 8:00 | 134 | 1:00
| Madartek | 134 | 3:00 | 129 | 11:00 | Khulna Central S/S | 139 | 0.77083 | 132 | 18:00
| Dhaka University |  |  |  |  | Noapara | 138 | 18:00 | 130 | 12:00
| Fatuiiah | 137 | 0.77083 | 130 | 11:00 | Jessore | 133 | 18:30 | 124 | 1:00
| Mirpur | 134 | 4:00 | 126 | 11:00 | Benapol | 134 | 18:30 | 123 | 1:00
| Kalyanpur | 134 | 4:00 | 128 | 11:00 | Jhenida | 129 | 0.77083 | 116 | 19:30
| Gulshan | 133 | 4:00 | 128 | 12:00 | Bottail | 133 | 7:00 | 125 | 19:30
| Uttara | 134 | 4:00 | 127 | 11:00 | G.K Project | 139 | 0.41667 | 133 | 1:00
| Uttara New | 136 | 4:00 | 131 | 11:00 | Faridpur | 135 | 9:00 | 125 | 19:00
| Kamrangirchar | 135 | 4:00 | 131 | 11:00 | Madaripur | 140 | 0.375 | 127 | 12:00
| Savar | 133 | 4:00 | 129 | 12:00 | Shariyatpur S/S | 140 | 0.375 | 127 | 20:00
| Bhasantec | 134 | 4:00 | 131 | 11:00 | Gopalganj | 139 | 9:00 | 125 | 19:00
| Agargaon | 136 | 4:00 | 130 | 11:00 | Bagerhat | 136 | 15:00 | 128 | 1:00
| Satmosjid | 135 | 4:00 | 129 | 11:00 | Mongla | 132 | 0.33333 | 125 | 3:00
| Tongi | 138 | 0.16667 | 133 | 15:00 | Satkhira | 136 | 0.77083 | 128 | 1:00
| Kabirpur | 136 | 10:00 | 131 | 16:00 | Gallamari | 138 | 15:00 | 132 | 1:00
| Basundhara | 134 | 3:00 | 128 | 13:00 | Magura | 130 | 18:30 | 115 | 19:30
| Manikganj | 140 | 20:00 | 134 | 9:00 | Norail | 125 | 0.29167 | 111 | 19:30
| Joydevpur | 142 | 18:30 | 134 | 3:00 | Chuadanga | 124 | 18:30 | 107 | 19:30
| New Tongi | 137 | 0.91667 | 132 | 16:00 | Barisal(N) | 141 | 7:00 | 131 | 19:00
| Kodda | 138 | 22:00 | 127 | 0.375 | Barisal (S) | 139 | 0.25 | 129 | 12:00
| Dhamrai | 136 | 10:00 | 131 | 19:00 | Patuakhali(S) | 138 | 0.29167 | 125 | 21:00
| Rajendrapur | 136 | 22:00 | 127 | 16:00 | Bhandaria | 135 | 15:00 | 124 | 1:00
| Valuka | 128 | 8:00 | 117 | 19:00 | Ishurdi | 137 | 06:0 | 132 | 19:00
| Tangail | 139 | 10:00 | 130 | 19:00 | Ruppur Paromanobik | 136 | 6:00 | 132 | 21:00
| Mymensing | 131 | 7:00 | 119 | 23:00 | Natore | 137 | 5:00 | 128 | 19:30
| Kishorganj | 131 | 8:00 | 120 | 19:00 | Bogra | 136 | 18:30 | 126 | 20:00
| Netrokona | 129 | 10:00 | 115 | 19:00 | Noagaon | 131 | 18:30 | 120 | 19:30
| Jamalpur | 139 | 16:00 | 134 | 22:00 | Rajshahi | 134 | 18:30 | 124 | 12:00
| Sherpur | 138 | 16:00 | 132 | 22:00 | Rajshahi New | 135 | 18:30 | 125 | 12:00
| Srimongal | 137 | 7:00 | 131 | 0.875 | C.Nawabganj | 134 | 18:30 | 121 | 12:00
| Shahjibazar | 135 | 6:00 | 128 | 0.95833 | Amnura | 132 | 18:00 | 121 | 11:00
| Fenchuganj | 136 | 10:00 | 132 | 0.041667 | Pabna | 135 | 18:30 | 128 | 20:00
| Khulawara | 134 | 5:00 | 131 | 0.79167 | Shahjadpur | 140 | 18:30 | 134 | 20:00
| Sylhet | 133 | 8:00 | 129 | 0.79167 | Serajganj | 134 | 7:00 | 128 | 19:00
| Chatak | 132 | 7:00 | 127 | 19:00 | Niyamatpur | 129 | 18:30 | 118 | 19:30
| Sunamganj | 130 | 4:00 | 123 | 0.8125 | Joypurhat | 133 | 18:30 | 119 | 19:30
| Biani Bazar | 131 | 7:00 | 125 | 0.77083 | Sherpur(Bogura) | 136 | 18:30 | 126 | 19:30
| Comilla(s) | 126 | 7:00 | 121 | 14:00 | Mohastangor | 134 | 14:00 | 124 | 19:00
| Comilla(n) | 140 | 19:00 | 133 | 8:00 | Rangpur | 129 | 13:00 | 113 | 19:30
| Chandpur | 140 | 11:00 | 125 | 1:00 | Lalmonirhat | 123 | 13:00 | 112 | 19:30
| Feni | 137 | 22:00 | 129 | 9:00 | Saidpur | 129 | 6:00 | 116 | 19:00
| Chowmuhani | 134 | 18:00 | 125 | 9:00 | Purbasadipur | 126 | 6:00 | 108 | 19:30
| Ashuganj | 136 | 7:00 | 130 | 23:00 | Thakurgaon | 127 | 5:00 | 108 | 19:00
| Daudkandi | 137 | 19:00 | 128 | 23:00 | Palashbari | 129 | 14:00 | 115 | 19:00
| B.Baria | 133 | 10:00 | 123 | 22:00 | Barapukuria | 134 | 4:00 | 123 | 19:00
| Ramganj | 137 | 10:00 | 126 | 23:00 | Panchagar | 123 | 6:00 | 102 | 19:00
| Chaddagram | 139 | 12:00 | 130 | 9:00 | Joldhaka | 126 | 5:00 | 110 | 19:00
| PHP | 138 | 13:00 | 128 | 1:00 | Kurigram | 124 | 7:00 | 107 | 19:00
| Madanhat | 138 | 19:30 | 133 | 7:00

## L-Curve
Date | 2020-08-23
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 274 | 7184 | 3945 | 11129 |  |  |  | QF-LDC-12
0:30 | 231.5 | 6834 | 3812 | 10646 | Date: | 2020-08-23
1:00 | 189 | 6484 | 3679 | 10163
1:30 | 167 | 6452 | 3594.5 | 10046.5
2:00 | 145 | 6420 | 3510 | 9930
2:30 | 108.5 | 6395.5 | 3465.5 | 9861 | [5 empty] | Gen. at Eve. Peak | 11804 | 11804 MW (20:00 )
3:00 | 72 | 6371 | 3421 | 9792 | [6 empty] | 20:00
3:30 | 100 | 6307 | 3386.5 | 9693.5 | [5 empty] | Gen. at Day Peak | 9620.2 | 9620.2 MW (12:00 )
4:00 | 128 | 6243 | 3352 | 9595 | [6 empty] | 12:00
4:30 | 116 | 6136.5 | 3289 | 9425.5 | [5 empty] | Highest Generation | 11804
5:00 | 104 | 6030 | 3226 | 9256 | [6 empty] | 20:00
5:30 | 127.5 | 5754.65 | 3092.55 | 8847.2
6:00 | 151 | 5479.3 | 2959.1 | 8438.4
6:30 | 160.5 | 5323.45 | 2912.15 | 8235.6
7:00 | 170 | 5167.6 | 2865.2 | 8032.8
7:30 | 204 | 5245.15 | 2880.7 | 8125.85
8:00 | 238 | 5322.7 | 2896.2 | 8218.9
8:30 | 245 | 5529.6 | 2873 | 8402.6
9:00 | 252 | 5736.5 | 2849.8 | 8586.3
9:30 | 130.5 | 5874.55 | 2762.7 | 8637.25
10:00 | 9 | 6012.6 | 2675.6 | 8688.2
10:30 | 5 | 6210.2 | 2663.25 | 8873.45
11:00 | 1 | 6407.8 | 2650.9 | 9058.7
11:30 | 2 | 6640.7 | 2698.75 | 9339.45
12:00 | 3 | 6873.6 | 2746.6 | 9620.2
12:30 | 67 | 6851.75 | 2892.75 | 9744.5
13:00 | 131 | 6829.9 | 3038.9 | 9868.8
13:30 | 150 | 6766.325 | 3030.35 | 9796.675
14:00 | 169 | 6702.75 | 3021.8 | 9724.55
14:30 | 194.5 | 6886.53 | 3043.4 | 9929.93
15:00 | 220 | 7070.31 | 3065 | 10135.31
15:30 | 314 | 6899.71 | 3071.6 | 9971.31
16:00 | 408 | 6729.11 | 3078.2 | 9807.31
16:30 | 444 | 6521.47 | 3088.2 | 9609.67
17:00 | 480 | 6313.83 | 3098.2 | 9412.03
17:30 | 411 | 6219.615 | 3010.7 | 9230.315
18:00 | 342 | 6125.4 | 2923.2 | 9048.6
18:30 | 292.5 | 6679.7 | 3441.6 | 10121.3
19:00 | 243 | 7234 | 3960 | 11194
19:30 | 179 | 7627 | 4121 | 11748
20:00 | 183 | 7686 | 4118 | 11804 |  |  |  | Executive Engineer
20:30 | 189 | 7649 | 4131.5 | 11780.5 |  |  |  | Network Operation Division
21:00 | 195 | 7612 | 4145 | 11757
21:30 | 220 | 7553 | 4137.5 | 11690.5
22:00 | 245 | 7494 | 4130 | 11624 |  |  |  |  | Page 6 of 7
22:30 | 268.5 | 7380 | 4109 | 11489
23:00 | 292 | 7266 | 4088 | 11354
23:30 | 283 | 7225 | 4016.5 | 11241.5
24:00 | 274 | 7184 | 3945 | 11129
11804 MW (20:00 )
9620.2 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-08-23 |  | Energy | 239543951
[10 empty] | 2020-08-23 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3099 | 924 | 2222 | 3492 | 669 | 80 | 643 | 0 | 148
0:30 | 3127.5 | 924 | 2182.5 | 3084 | 674.5 | 80 | 504.5 | 0 | 143 | Date: | 2020-08-23
1:00 | 3156 | 924 | 2143 | 2676 | 680 | 80 | 366 | 0 | 138
1:30 | 3145 | 826 | 2154.5 | 2669 | 680 | 80 | 356 | 0 | 136 | [7 empty] | Total Energy | 239.544 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 3134 | 728 | 2166 | 2662 | 680 | 80 | 346 | 0 | 134 | [7 empty] | Energy not Served | 0
2:30 | 3111 | 728 | 2174.5 | 2636 | 670 | 78.5 | 331 | 0 | 132 | [7 empty] | Energy Requirement | 239.544
3:00 | 3088 | 728 | 2183 | 2610 | 660 | 77 | 316 | 0 | 130
3:30 | 3107.5 | 728 | 2156 | 2536.5 | 659.5 | 77 | 299 | 0 | 130 | [6 empty] | Shortage
4:00 | 3127 | 728 | 2129 | 2463 | 659 | 77 | 282 | 0 | 130
4:30 | 3136 | 728 | 2149.5 | 2299 | 644 | 77 | 266 | 0 | 126
5:00 | 3145 | 728 | 2170 | 2135 | 629 | 77 | 250 | 0 | 122
5:30 | 3149.5 | 728.5 | 2151 | 1815 | 604 | 77 | 204 | 0 | 118
6:00 | 3154 | 729 | 2132 | 1495 | 579 | 77 | 158 | 0 | 114
6:30 | 3088.5 | 729 | 2062.5 | 1444 | 579 | 77 | 147 | 0 | 107 |  |  |  |  | Coal
7:00 | 3023 | 729 | 1993 | 1393 | 579 | 77 | 136 | 0 | 100
7:30 | 3043 | 728.5 | 2040.5 | 1404.5 | 579 | 77.5 | 144 | 0 | 101 |  |  |  | Oil |  |  |  | ,
8:00 | 3063 | 728 | 2088 | 1416 | 579 | 78 | 152 | 0 | 102
8:30 | 3074.5 | 728.5 | 2082 | 1620 | 549 | 78 | 152 | 0 | 105
9:00 | 3086 | 729 | 2076 | 1824 | 519 | 78 | 152 | 0 | 108
9:30 | 3097.5 | 729 | 1973.5 | 1950.5 | 469 | 78.5 | 210.5 | 0 | 110
10:00 | 3109 | 729 | 1871 | 2077 | 419 | 79 | 269 | 0 | 112
10:30 | 3128.5 | 826 | 2005 | 2146 | 284 | 79.5 | 269 | 0 | 116
11:00 | 3148 | 923 | 2139 | 2215 | 149 | 80 | 269 | 0 | 120
11:30 | 3210.5 | 923 | 2163.5 | 2379 | 149 | 78.5 | 294 | 0 | 119
12:00 | 3273 | 923 | 2188 | 2543 | 149 | 77 | 319 | 0 | 118
12:30 | 3263 | 923 | 2099.5 | 2768 | 149 | 77.5 | 319 | 0 | 119
13:00 | 3253 | 923 | 2011 | 2993 | 149 | 78 | 319 | 0 | 120
13:30 | 3253 | 923 | 2011 | 2993 | 149 | 78 | 319 | 0 | 120
14:00 | 3253 | 923 | 2011 | 2993 | 149 | 78 | 319 | 0 | 120
14:30 | 3128 | 923 | 2112 | 3157 | 149 | 77.5 | 306.5 | 0 | 130
15:00 | 3003 | 923 | 2213 | 3321 | 149 | 77 | 294 | 0 | 140
15:30 | 3005.5 | 923.5 | 2146.5 | 3161 | 204 | 77 | 299.5 | 0 | 139
16:00 | 3008 | 924 | 2080 | 3001 | 259 | 77 | 305 | 0 | 138
16:30 | 2995.5 | 923 | 1978 | 2858.5 | 329 | 77 | 305 | 0 | 133
17:00 | 2983 | 922 | 1876 | 2716 | 399 | 77 | 305 | 0 | 128
17:30 | 2929 | 922 | 1716.5 | 2691 | 449 | 76 | 318.5 | 0 | 125
18:00 | 2875 | 922 | 1557 | 2666 | 499 | 75 | 332 | 0 | 122
18:30 | 2961.5 | 922 | 1806 | 3149.5 | 544 | 76 | 527 | 0 | 135
19:00 | 3048 | 922 | 2055 | 3633 | 589 | 77 | 722 | 0 | 148
19:30 | 3094 | 922 | 2110 | 3998 | 669 | 78 | 739 | 0 | 138
20:00 | 3093 | 922 | 2193 | 3959 | 669 | 78 | 758 | 0 | 132
20:30 | 3081 | 922.5 | 2198.5 | 3930 | 669 | 78.5 | 758 | 0 | 143
21:00 | 3069 | 923 | 2204 | 3901 | 669 | 79 | 758 | 0 | 154
21:30 | 3109.5 | 923 | 2201 | 3795 | 669 | 79.5 | 758.5 | 0 | 155
22:00 | 3150 | 923 | 2198 | 3689 | 669 | 80 | 759 | 0 | 156
22:30 | 3124.5 | 923.5 | 2213.5 | 3590.5 | 669 | 80 | 733 | 0 | 155
23:00 | 3099 | 924 | 2229 | 3492 | 669 | 80 | 707 | 0 | 154
23:30 | 3099 | 924 | 2225.5 | 3492 | 669 | 80 | 675 | 0 | 151 | Max Temp. in Dhaka |  | 31.0° C
24:00 | 3099 | 924 | 2222 | 3492 | 669 | 80 | 643 | 0 | 148
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
Note on W13: Author:

## Generation
g | 2020-08-23
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 45 | 45 | 42 | 42 | 42 | 42 | 42 | 43 | 43 | 44 | 45 | 42 | 43 | 43 | 42 | 42 | 42 | 40 |  | 42 | 43 | 43 | 44 | 45 | 45 | 45 | 973680
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 836000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [9 empty] | 10 | 25 | 25 | 25 | 25 | 25 | 25 |  |  |  | 14 | 25 | 25 | 25 | 25 | 25 | 25 | 311760
| Teknaf 20MW PP (Solartech) | [5 empty] | 0.2 | 1.7 | 7.4 | 8.6 | 13.1 | 3.7 | 19.1 | 7.3 | 14.15 | 6.61 | 5.21 | 3.93 | 0.3 | [8 empty] | 91125
6 | Sikalbaha 225MW CCPP (Gas) | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 203 | 224 | 231 | 231 | 231 | 231 | [9 empty] | 76 | 75 | 85 | 2970555
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 104 | 105 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 140 | 141 | 139 | 103 | 105 | 140 | 140 | 104 | 100 |  | 140 | 140 | 140 | 140 | 139 | 139 | 139 | 2838806
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 100 | 102 | 102 | 102 | 102 | 102 | 68 | 576414
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [19 empty] | 11 | 34 | 34 | 34 |  |  | 0 | 101200
| Daudkandi 200 MW PP (B.Trac) | [19 empty] | 80 | [6 empty] | 47424
14 | Titas 50 MW Peaking PP | [11 empty] | 50 | 50 | [6 empty] | 50 | 50 | 50 | 48 | 50 |  | 0 | 318184
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | [25 empty] | 0 | 0
18 | Kodda 300 MW PP Unit-2 (Summit) | 300 | 300 | 300 | 300 | 300 | 170 | 170 | 188 | 288 | 300 | 300 | 286 | 288 | 288 | 283 | 286 | 283 | 286 |  | 283 | 285 | 286 | 286 | 286 | 286 | 286 | 6744434
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 571000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2709000
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1682150
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 128448
33 | Ashuganj 225 MW CCPP | 154 | 161 | 174 | 182 | 188 | 172 | 159 | 168 | 147 | 139 | 141 | 144 | 131 | 129 | 136 | 138 | 141 | 130 |  | 129 | 129 | 126 | 129 | 134 | 141 | 145 | 3620000
34 | Ashuganj 450 MW CCPP(South) | 100 | 80 | 25 | 55 | 65 | 95 | 95 | 140 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 4048000
| Ashuganj 450 MW CCPP(North) | 310 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 285 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 7106900
35 | Ashuganj 55 MW PP (Precision) | [20 empty] | 0 |  |  |  |  | 0 | 0
36 | Chandpur 150 MW CCPP | 85 | 92 | 92 | 96 | 95 | 85 | 94 | 90 | 75 | 70 | 74 | 85 | 85 | 84 | 95 | 97 | 96 | 97 |  | 95 | 96 | 96 | 96 | 96 | 96 | 96 | 2107810
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 340 | 338 | 339 | 338 | 338 | 338 | 338 | 346 | 338 | 345 | 357 | 389 | 412 | 413 | 402 | 400 | 385 | 393 |  | 391 | 388 | 389 | 389 | 395 | 350 | 344 | 8924160
40 | Meghnaghat 450 MW CCPP(MPL) | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 300 | 420 | 420 | 330 | 300 | 450 | 420 | 370 | 320 |  | 360 | 360 | 400 | 420 | 420 | 420 | 420 | 8899500
41 | Haripur 360MW CCPP(HPL) | 358 | 356 | 355 | 357 | 356 | 357 | 289 | 289 | 290 | 291 | 348 | 350 | 330 | 300 | 345 | 340 | 340 | 300 |  | 351 | 353 | 353 | 355 | 354 | 353 | 357 | 8005000
42 | RPCL 210MW CCPP | 125 | 125 | 143 | 145 | 145 | 161 | 161 | 158 | 142 | 141 | 121 | 123 | 118 | 100 | 101 | 101 | 104 | 123 |  | 122 | 123 | 123 | 121 | 121 | 123 | 126 | 2981920
43
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 58 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1420000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 716400
46 | Shajibazar 330 MW CCPP | 200 | 196 | 194 | 192 | 195 | 195 | 206 | 201 | 203 | 194 | 211 | 193 | 195 | 217 | 200 | 195 | 197 | 192 |  | 193 | 190 | 192 | 193 | 193 | 203 | 195 | 4546000
47 | Shahjibazar GTPP Unit- 8 & 9 | 67 | 67 | 67 | 67 | 67 | 68 | 40 | 40 | 40 | 40 | 52 | 62 | 61 | 64 | 64 | 64 | 63 | 40 |  | 67 | 67 | 64 | 64 | 64 | 64 | 64 | 1400640
48 | Shahjibazar 86MW PP (Shahjibazar) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 10 | 10 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1930560
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1925720
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 418000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 9 | 10 | 246420
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 159000
55 | Fenchugonj 51 MW PP (Barakatullah) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 44 | 44 | 44 | 44 | 47 | 44 | 44 | 46 | 13 |  | 49 | 49 | 49 | 50 | 50 | 50 | 50 | 1085400
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 548376
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 280 | 300 | 285 | 275 | 285 | 280 | 300 | 295 | 285 | 285 | 320 | 295 | 280 | 320 | 270 | 290 | 290 |  | 280 | 300 | 290 | 280 | 290 | 290 | 290 | 7173800
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 17 | 17 | 17 | 17 | 17 | 55 | 55 | 35 | 55 | 55 | 35 | 35 | 35 | 17 | 17 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 984869
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 17 | 17 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 17 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 |  | 11 | 11 | 14 | 369408
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 355284
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 14 | 14 | 14 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 317880
63 | Impoprt (Tripura) | 138 | 134 | 130 | 130 | 122 | 114 | 100 | 102 | 108 | 112 | 120 | 118 | 120 | 134 | 140 | 138 | 128 | 122 |  | 148 | 138 | 132 | 154 | 156 | 154 | 148 | 3139200
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 40 | 38 | 8 | 4 | 4 | 2 | 3 | 8 | 6 | 3 | 5 | 7 | 7 |  | 25 | 29 | 34 | 35 | 38 | 42 | 42 | 566400
65 | Feni 22MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 458424
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 8 | 5 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 208260
67 | Jangalia 33MW PP (Summit) | [11 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 327800
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 12 | 15 | 15 | 15 | 15 | 15 | 15 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 482120
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 29 | 0 | 9 | 9 | 18 | 20 | 21 | 21 | 20 | 20 | 25 | 29 | 29 |  | 22 | 28 | 30 | 30 | 30 | 30 | 30 | 537300
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 819700
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 |  | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 25 | 25 | 33 |  | 31 | 33 | 33 | 33 | 33 | 33 | 33 | 691800
73 | Ghorashal 108MW PP (Regent) | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 95 | 95 | 95 | 95 | 93 | 95 | 96 | 97 | 96 | 96 | 53 |  | 98 | 98 | 97 | 98 | 96 | 96 | 96 | 2242500
| Feni Lanka Power | 48 | 34 | 17 | [6 empty] | 114 | 114 | 114 | 114 | 50 | 114 | 17 |  | 50 |  | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 1496820
| Chowmuhani 113 MW | 56 | 56 | 57 | 56 | 55 | 8 | 8 | 8 | 10 | 41 | 56 | 56 | 56 | 56 | 54 | 56 | 57 | 55 |  | 56 | 56 | 57 | 56 | 56 | 56 | 57 | 1176840
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 7 | 7 | 7 | 7 | [9 empty] | 4 | 14 | 28 | 70 | 100 |  | 98 | 98 | 98 | 98 | 99 | 99 | 99 | 854400
78 | Gazipur 52 MW PP | [10 empty] | 13 | 52 | 52 |  | 12 |  |  |  |  | 35 | 52 | 52 | 52 | 52 | 52 | 52 | 484812
79 | Kodda 150MW PP | 116 | 98 | 98 | 64 | 64 | 30 | 16 | 32 | 32 | 149 | 149 | 149 | 149 | 149 | 149 | 98 | 98 | 120 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 2666400
80 | Jamalpur 95 MW PP(Powerpac) | 90 | 90 | 90 | 90 | 81 | 8 | 8 | 8 | 8 | 16 | 40 | 73 | 81 | 70 | 89 | 89 | 56 | 56 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1577280
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 43 | [5 empty] | 6 | 42 | 43 | 43 | 25 | 28 | 16 | 16 | 16 |  | 34 | 43 | 43 | 43 | 43 | 43 | 43 | 709608
| Gazipur 100 MW PP | 105 | 70 | 70 | 35 |  |  |  | 4 | 17 |  |  | 63 | 88 | 88 | 88 | 52 | 52 | 52 |  | 88 | 93 | 102 | 105 | 105 | 105 | 105 | 1450728
| Kaptai 7 MW Solar PP | [5 empty] | 0.1 | 0.8 | 4 | 3.2 | 2.9 | 2.9 | 2.3 | 5.7 | 5.4 | 1.3 | 3.9 | 1.3 | 0.1 | [8 empty] | 33000
| Jodiac Power | [19 empty] | 25 | 54 | 54 | 54 | 17 | 17 | 17 | 203565
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | 80 | 96 | 96 | 96 | 95 | 64 | 64 | 64 | 80 | 80 | 80 | 80 | 97 | 97 | 97 | 97 | 97 | 97 |  | 97 | 97 | 97 | 97 | 95 | 95 | 95 | 2172072
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [9 empty] | 10 | 27 | 52 | 51 | 52 | 52 | 52 | 52 | 27 |  | 45 | 100 | 100 | 100 | 29 | 26 | 26 | 726317
86 | Meghnaghat CCPP(Summit) | 130 | 145 | 140 | 135 | 145 | 135 | 130 | 130 | 140 | 130 | 130 | 135 | 135 | 135 | 140 | 130 | 140 | 130 |  | 130 | 130 | 135 | 142 | 135 | 147 | 143 | 3396975
87 | Meghnaghat 100 MW(IEL) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 10 | 7 | 7 | 7 | 7 | 204480
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 27 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 453120
88 | Ghorashal 78.5 MW PP(MAX) | 69 | 69 | 69 | 69 | 69 | 68 | 68 | 68 | 68 | 68 | 67 | 66 | 66 | 65 | 65 | 65 | 40 | 40 |  | 66 | 67 | 67 | 67 | 67 | 68 | 68 | 1522528
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [12 empty] | 20 | 20 | 20 |  |  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 142200
92 | Fenchuganj 44MW (Energyprima) | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 43 | 42 | 42 | 42 | 40 | 10 |  | 33 | 43 | 43 | 43 | 43 | 43 | 43 | 1003824
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 10 | 10 |  | 28 | 35 | 46 | 51 | 51 | 51 | 51 | 1178515
94 | Gagnagar 102 MW PP (Digital Power) | 85 | 94 | 94 | 94 | 94 | 48 | 48 | 48 | 94 | 94 | 94 | 94 | 94 | 94 | 96 | 96 | 98 | 98 |  | 100 | 98 | 102 | 102 | 102 | 102 | 102 | 2199024
95 | Patenga 50MW PP (Baraka) | [9 empty] | 24 | 50 | 50 | 50 | 50 | 50 | 50 | 12 | 12 |  | 25 | 50 | 50 | 50 | 50 | 50 | 50 | 651360
96 | Chattogram 108 MW PP (ECPV) | 55 | 51 | 51 | 51 | 12 | 12 | 11 | 11 | 51 | 91 | 91 | 91 | 96 | 97 | 97 | 95 | 72 | 71 |  | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 1728000
97 | Katpotti 52 MW PP (Sinha) | 47 | 47 | 47 | 47 | [5 empty] | 5 | 45 | 48 | 48 | 48 | 48 | 48 | 30 | 30 |  | 43 | 42 | 46 | 41 | 41 | 41 | 41 | 860256
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 30 | 30 | 15 | 15 | 15 | 55 | 41 | 41 | 41 | 41 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 55 | 55 | 55 | 953073
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 17 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 |  | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 1122476
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 163 | 110 | 163 | 163 | 110 | 163 | 163 | 110 | 110 | 163 | 130 | 110 | 110 |  | 130 | 130 | 163 | 163 | 163 | 163 | 163 | 3552872
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0.1 | 0.3 | 0.7 | 0.6 | 1.2 | 1.2 | 1.9 | 0.2 | 1.4 | 1 | 0.6 | [9 empty] | 10350
103 | Kamalaghat 54 MW PP(Banco Energy) | 53 | 53 | 53 | 53 | 53 | 35 | 17 | 17 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1211400
104 | Keranigonj 300 MW PP (APR) | [13 empty] | 304 | 300 | 308 | 308 | 307 |  | 307 | 303 | 300 | 200 | 97 |  | 0 | 2367463
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 194 | 194 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4776000
112 | Aurahati 100MW PP (Aggreko) | [14 empty] | 92 | [10 empty] | 0 | 54371
114 | Kodda 149 MW PP Unit-1 (Summit) | 133 | 132 | 133 | 132 | 133 | 123 | 100 | 100 | 130 | 95 | 25 | 109 | 130 | 130 | 131 | 131 | 133 | 132 |  | 133 | 133 | 133 | 133 | 132 | 132 | 132 | 2952000
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 90 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
116 | Chandpur 200MW (Desh energy) | [9 empty] | 60 | 102 | 118 | 145 |  | 5 |  |  |  |  | 36 | 150 | 114 | 114 | 114 | 50 | 0 | 1129440
117 | Ashuganj 150MW PP (Midland) | 60 | 60 | 60 | 60 | 60 | 10 | 10 | 10 | 10 | 10 | 10 | 16 | 50 | 50 | 60 | 70 | 30 | 35 |  | 70 | 100 | 100 | 100 | 100 | 100 | 100 | 1380000
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 85 | 85 | 65 | 65 | 24 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 8 | 8 | 20 | 8 | 8 | 8 |  | 16 | 115 | 115 | 115 | 115 | 115 | 115 | 1111200
| Anwara 300 MW PP (United) | 234 | 234 | 234 | 234 | 234 | 190 | 162 | 162 | 162 | 162 | 162 | 179 | 179 | 162 | 233 | 304 | 304 | 265 |  | 253 | 253 | 253 | 253 | 252 | 252 | 252 | 5331818
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2437440
120 | Eastern Zone Total | 6484 | 6420 | 6371 | 6243 | 6030 | 5479.3 | 5167.6 | 5322.7 | 5736.5 | 6012.6 | 6407.8 | 6873.6 | 6829.9 | 6702.75 | 7070.31 | 6729.11 | 6313.83 | 6125.4 |  | 7234 | 7627 | 7686 | 7612 | 7494 | 7266 | 7184 | 158147485
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 115 | 115 | 115 | 107 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2734080
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
| Khulna 225 MW CCPP | 150 | 150 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 145 | 150 | 150 | 150 |  | 190 | 200 | 200 | 200 | 200 | 200 | 170 | 3576497
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | 35 | 17 | [11 empty] | 8 |  |  |  |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 707040
130
131
132
133
| Barisal 110 MW PP (Summit ) | [8 empty] | 16 | 16 | 16 | 18 | 110 | 96 | 96 | 64 | 48 | 32 |  | 52 | 64 | 32 | 32 | 32 | 32 | 32 | 754848
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 77 | 78 | 78 | 78 | 78 | 76 | 79 | 79 | 77 | 78 | 78 | 78 | 77 | 77 | 77 | 77 | 78 | 78 |  | 77 | 77 | 77 | 77 | 77 | 78 | 78 | 1868052
| Bhola 225 MW CCPP | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 90 | 90 | 89 | 89 | 89 | 89 | 89 |  | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 2083127
140 | Bhola 33 MW PP (Venture) | 27 | 25 | 26 | 14 | 18 | 16 | 17 | 16 | 16 | 15 | 16 | 16 | 18 | 18 | 21 | 19 | 18 | 19 |  | 30 | 30 | 31 | 29 | 30 | 31 | 30 | 496274
141 | Noapara 100 MW PP (Bangla Trac) | [19 empty] | 47 | 100 | 100 | 100 | 100 | 70 | 0 | 472320
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 40 | 40 | [8 empty] | 32 | 32 | 32 |  |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 534375
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [20 empty] | 15 | 15 | 15 | 15 |  | 0 | 46800
146 | Bheramara HVDC | 924 | 728 | 728 | 728 | 728 | 729 | 729 | 728 | 729 | 729 | 923 | 923 | 923 | 929 | 923 | 924 | 922 | 922 |  | 922 | 922 | 922 | 923 | 923 | 924 | 924 | 20462545
147 | Bheramara 410 MW CCPP | 355 | 355 | 345 | 345 | 345 | 345 | 350 | 360 | 360 | 325 | 330 | 325 | 325 | 310 | 290 | 285 | 285 | 245 |  | 345 | 330 | 330 | 320 | 310 | 310 | 310 | 8064000
148 | Payra 1320 MW | 530 | 530 | 510 | 510 | 480 | 430 | 430 | 430 | 370 | 270 | [5 empty] | 110 | 250 | 350 |  | 440 | 520 | 520 | 520 | 520 | 520 | 520 | 9124200
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3648900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 284607
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 179 | 182 | 182 | 183 | 184 | 183 | 181 | 149 | 146 | 150 | 154 | 182 | 183 | 180 | 176 | 179 | 178 | 150 |  | 143 | 174 | 175 | 177 | 177 | 156 | 152 | 4304900
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 219 | 215 | 206 | 203 | 202 | 201 | 150 | 150 | 150 | 150 | 150 | 180 | 182 | 177 | 171 | 170 | 170 | 140 |  | 160 | 186 | 185 | 185 | 179 | 176 | 174 | 4580655
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 356 | 387 | 384 | 355 | 403 | 361 | 346 | 402 | 404 | 354 | 394 | 409 | 412 | 398 | 403 | 389 | 374 | 250 |  | 396 | 407 | 411 | 404 | 387 | 413 | 402 | 9289490
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 5 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 189577
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 442080
163 | Bogura 20 MW PP (Energyprima) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 10 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 256860
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 10 | 10 | 10 | 10 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 217008
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 8 |  | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 145435
167 | Katakhali 50 MW Peaking PP | [19 empty] | 43 | 43 | 47 | 43 | 43 | 43 | 43 | 228229
168 | Santahar 50 MW Peaking PP | [19 empty] | 5 | 10 | 25 | 33 | 32 | 32 | 32 | 143000
169 | Natore 52 MW PP (Rajlanka) | [12 empty] | 17 | 17 | 44 |  |  |  |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 334080
170 | Chapainawabganj 100 MW Peaking PP | 100 | 98 | 98 | 98 | 66 | 8 | [9 empty] | 57 | 57 | 57 |  | 100 | 100 | 100 | 98 | 98 | 96 | 96 | 1123416
171 | Baghabari 200 MW PP (Paramount) | [19 empty] | 100 | [5 empty] | 0 | 60071
| Bagura 113 MW PP (Confidence)-2 | 70 | 70 | 70 | 70 | [8 empty] | 35 | 50 | 59 | 35 |  |  |  | 70 | 94 | 94 | 94 | 94 | 94 | 94 | 1118400
172 | Confidence Power Bogura Unit-1 113 MW | 109 | 109 | 109 | 109 | 109 | 35 | 35 | 35 | 35 | 35 | 35 | 60 | 100 | 109 | 109 | 109 | 70 | 70 |  | 100 | 109 | 109 | 109 | 109 | 109 | 109 | 2053632
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 113 | 113 | 99 | 61 | 34 | 35 | 38 | 37 | 37 | 37 | 106 | 113 | 113 | 113 | 106 | 55 |  | 49 | 49 | 54 | 95 | 113 | 113 | 113 | 2007360
177 | Sympa Solar Power 8MW | [5 empty] | 0.1 | 0.2 | 1.2 | 1.8 | 6.6 | 7.9 | 7.6 | 7.9 | 6.8 | 6 | 5.2 | 0.2 | 0.2 | [8 empty] | 44608
178
178