## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-08-27 | Thursday
|  |  | Date (day): | 2020-08-27 |  | Thursday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13096.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14009 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-08-26 | 2020-08-27 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 28 | 28 | 28 | 28 |  | 57 | Unit-2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 110 | 110 | 110 | 110 | 80 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 63 | 65 | 65 | 65 |  | 13 | Engine problem
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 94 | 101 | 100 | 100 |  | 8 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 348 | 339 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 348 | 353 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 320 | 420 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 7 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 145 | 138 | 150 | 150 | 155 |  | GT-1 S/D for gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 80 | 0 | 96 | 96
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 40 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 25 | 100 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 7 | 7 | 7 | 93 |  | Fuel Shortage.
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 16 | 16 | 16 | 16 | 86 |  | Fuel Shortage.
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 41 | 18 | 41 | 41 |  | 10 | Engine problem
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 53 | 0 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 149 | 133 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 55 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 20 | 51 | 35 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 300 | 286 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 36 | 209 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 100 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 26 | 102 | 80 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 116 | 130 | 133 | 133 |  | 16 | Engine problem
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 88 | 88 | 100 | 100
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 2815 | 3198 | 3448 | 3735 | 1172 | 979
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 8 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 13.1 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 84 | 85 | 80 | 80 | 150 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 112 | 111 | 111 | 111 | 114 |  | Gas shortage
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 106 | 104 | 105 | 105 | 45 |  | Gas shortage
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 86 | 100 | 100
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 40 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 20 | 20
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 25 | 15 | 25
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 84 | 97 | 97 | 97 |  | 11 | Engine problem
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 1.8 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 307 | 305 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 50 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 1017.9 | 1132 | 1428 | 1477 | 669 | 109
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 80 | 80 | 80 | 80 | 49 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 168 | 173 | 170 | 170
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 265 | 265 | 360 | 360
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 180 | 180 | 360 | 360
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 5 | 5 | 5 | 40 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 5 | 5 | 50 |  | Gas shortage
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 8 | 8 | 187 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 36 | 49 | 0 | 42
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 96 | 86 | 96 | 96 |  | 67 | ST under shut down
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 50 | 120 | 200 | 200
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 21 | 21 | 21
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 118 | 156 | 157 | 173
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 39 | 43 | 43 | 43 |  | 9 | Engine problem
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 21 | 20 | 20 |  | 5 | Engine problem
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 70 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 114 | 114 | 114 | 114
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 113 | 113 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1338 | 1537 | 1997 | 2255 | 595 | 81
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 120 | 125 | 160 | 160 | 42 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 17 | 17 |  | 5 | Engine problem
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 66 | 74 | 72 | 72 |  | 23 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 200 | 193 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 8 | 115 | 115 | 115
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 412 | 524 | 565.6 | 564 | 42 | 28
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 59 | 60 | 60 | 60
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 28 | 30 | 30 |  | 35 | Unit-4 under shut down
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 130 | 163 | 163
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 162 | 116 | 210 | 210 | 120 |  | Gas Shortage
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 50 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 43 | 44 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 63 | 67 | 66 | 66
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 85 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 80 | 80 | 80 | 80 |  | 151 | Machine problem.
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 290 | 341 | 341
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1041 | 1013 | 1195 | 1195 | 120 | 586
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 932 | 932 | 942 | 942
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 99 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 180 | 220 | 220
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 350 | 375 | 380 | 380 | 30 |  | Gas Shortage
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 60 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 53 | 105 | 105
| 108 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1402 | 1779 | 1962 | 2108 | 30 | 0
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 64 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 14 | 29 | 33 | 33
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 90 | 90 | 90 | 90 |  | 104 | GT-2 & ST Under maint.
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 22 | 75 | 80 | 80 |  | 15 | Engine problem
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 400 | 370 | 422 | 422
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 526 | 628 | 735 | 735 | 0 | 119
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 35 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 8 | 50 | 50
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 0 | 50
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 140 | 187 | 220 | 220 |  |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 158 | 210 | 220 | 220 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 403 | 364 | 414 | 414 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 0 | 32
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 9 | 11 | 11 | 11
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 43 | 43 | 43 |  | 9 | Engine problem
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 98 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 90 | 95 | 95 |  | 18 | Engine problem
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 90 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 736 | 1278 | 1495 | 1667 | 431 | 31
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 149 | 150 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 113 | 113
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3.6 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 152.6 | 150 | 271 | 273 | 294 | 30
|  | Total |  |  |  |  | 20383 | 19892 | 9440.5 | 11239 | 13096.6 | 14009 | 3353 | 1963
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9216.2262 | 10972 | 12785.4698 | 13676.1943
| A. |  | 2020-08-26 | (Yesterday) |  |  |  |  | Wednesday
| 1 | Highest Generation : |  |  | 11302 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
| 2 | Minimum Generation : |  |  | 8421.4 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11239 | MW
| 3 | Day peak Generation : |  |  | 9440.5 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10972 | MW
| 4 | Evening peak Generation : |  |  | 11239 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 239.0201 | MKWHr | By Solar | 0.17295 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 122.4447 | MKWHr |  | By Oil: | 74.0219 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 14.8442 | MKWHr |  | By Hydro: | 1.9551 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3353 | MW | Dhaka | 3843 | 3843 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 1963 | MW | Chittagong | 1143 | 1143 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5316 | MW | Khulna | 1353 | 1353 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1036.56 | MMCFD |  |  | Rajshahi | 1182 | 1182 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 140731141.42 | ii) Oil : | Taka | 601436678.63 | Comilla | 1002 | 1002 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 68928422 | Total | Taka | 811096242.05 | Mymensingh | 945 | 945 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.003 | MKWHr. | Sylhet | 507 | 507 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 163 | MW (E to W) at | 19:30 | hrs | Barisal | 291 | 291 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 154 | MW at | 3:00 | hrs | Rangpur | 706 | 706 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 31.7° C |  |  | Total | 10972 | 10972 |  | 0
| B. |  | 2020-08-27 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 32.3° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 11800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14009 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 9800 | MW
| 4 | Reserve(Generation end) |  |  |  | 2209 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 249.552 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8491.6 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.4036 | MKWHr. | ii) HVDC Flow at Peak Time |  | 932 | MW at | 19:30 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.1776 | MKWHr. | iii) Maximum HVDC Flow : |  | 936 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 93.29 |  | (b) Today: | 93.3 |  | (c) Rule Curve: |  | 97.35
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-08-26
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 28 | 0 | 0 | 110 | 0 | 101 | 66 | 356 | 332 |  | 0 | 360 | 140 | 24 | 97 | 42 | 0 | 0 | 0 | 0 | 7 | 16 | 149 | 59 | 0 | 0 | 41 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 84 | 0 | 0 | 0 | 0 | 110 | 0 | 106 | 0 |  | 0 | 0 | 34 | 0 | 97 | 50 | 21 | 41 | 0 | 70 | 0 | 265 | 180 | 195 | 8 | 90 | 5 | 0 | 0 | 51 | 0 | 0 | 43 | 21 | 8 | 33 | 21 | 144 | 141 | 74 | 17 | 0 | 60 | 30 | 53 | 43 | 110 | 161 | 64 | 85 | 0 | 70 | 18 | 0 | 10 | 300 | 24 | 5 | 0 | 300 | 0 | 0 | 177 | 0 | 131 | 0 | 100 | 0 | 10 | 0 | 115 | 105 | 0 | 0 | 269 | 0 | 0 | 0 | 113 | 100 | 0 | 104 |  | 935 | 0 | 320 | 0 | 115 | 230 | 0 | 0 | 12 | 0 | 40 | 90 | 22 | 0 | 0 | 0 | 0 | 50 | 35 | 98 | 0 | 25 | 44 | 43 | 32 | 22 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 197 | 0 | 61 | 0 | 191 | 0 | 413 | 4 | 0 | 94 | 0 | 106 | 0 | 0 | 109 | 600 |  | 6751 | 4059 | 10810 | 3161 | 935 | 2089 | 2964 | 749 | 84 | 684 | 144 | 0 | 0 | 93.29
2:00 | 28 | 0 | 0 | 110 | 0 | 100 | 66 | 351 | 353 |  | 0 | 390 | 150 | 7 | 88 | 55 | 0 | 0 | 0 | 0 | 7 | 16 | 115 | 100 | 0 | 0 | 41 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 8 | 0 | 85 | 0 | 0 | 0 | 0 | 110 | 0 | 105 | 0 |  | 0 | 0 | 31 | 0 | 97 | 50 | 21 | 41 | 0 | 70 | 0 | 265 | 180 | 195 | 8 | 96 | 5 | 0 | 0 | 51 | 0 | 0 | 43 | 21 | 8 | 33 | 21 | 140 | 142 | 74 | 17 | 0 | 60 | 30 | 53 | 43 | 110 | 160 | 64 | 85 | 0 | 70 | 18 | 0 | 10 | 300 | 24 | 5 | 0 | 300 | 0 | 0 | 177 | 0 | 131 | 0 | 100 | 0 | 10 | 0 | 115 | 105 | 0 | 0 | 269 | 0 | 0 | 0 | 113 | 100 | 0 | 104 |  | 936 | 0 | 310 | 0 | 115 | 170 | 0 | 0 | 0 | 0 | 40 | 90 | 25 | 0 | 0 | 0 | 0 | 17 | 0 | 98 | 0 | 0 | 44 | 16 | 32 | 22 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 197 | 0 | 63 | 0 | 192 | 0 | 408 | 0 | 0 | 94 | 0 | 105 | 0 | 0 | 109 | 510 |  | 6756 | 3764 | 10520 | 3152 | 936 | 2139 | 2902 | 659 | 85 | 507 | 140 | 0 | 0 | 93.29
3:00 | 28 | 0 | 0 | 110 | 0 | 100 | 66 | 366 | 353 |  | 0 | 420 | 145 | 7 | 64 | 55 | 0 | 0 | 0 | 0 | 7 | 16 | 115 | 37 | 0 | 0 | 41 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 87 | 0 | 0 | 0 | 0 | 110 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 91 | 50 | 21 | 41 | 0 | 70 | 0 | 265 | 180 | 195 | 8 | 95 | 5 | 0 | 0 | 51 | 0 | 0 | 43 | 21 | 8 | 33 | 21 | 138 | 142 | 74 | 17 | 0 | 60 | 30 | 50 | 43 | 110 | 158 | 64 | 85 | 0 | 70 | 18 | 0 | 10 | 310 | 24 | 5 | 0 | 300 | 0 | 0 | 180 | 0 | 131 | 0 | 100 | 0 | 10 | 0 | 115 | 105 | 0 | 0 | 269 | 0 | 0 | 0 | 113 | 100 | 0 | 104 |  | 934 | 0 | 310 | 0 | 108 | 120 | 0 | 0 | 0 | 0 | 40 | 90 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 44 | 0 | 0 | 22 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 197 | 0 | 63 | 0 | 192 | 0 | 414 | 0 | 0 | 94 | 0 | 107 | 0 | 0 | 109 | 470 |  | 6671 | 3604 | 10275 | 3161 | 934 | 2181 | 2778 | 619 | 87 | 377 | 138 | 0 | 0 | 93.29
4:00 | 28 | 0 | 0 | 110 | 0 | 100 | 66 | 347 | 355 |  | 0 | 420 | 135 | 7 | 64 | 55 | 0 | 0 | 0 | 0 | 7 | 16 | 98 | 26 | 0 | 0 | 41 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 89 | 0 | 0 | 0 | 0 | 110 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 94 | 50 | 21 | 41 | 0 | 70 | 0 | 265 | 180 | 191 | 8 | 94 | 5 | 0 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 134 | 158 | 74 | 17 | 0 | 60 | 30 | 50 | 43 | 110 | 160 | 64 | 85 | 0 | 70 | 18 | 0 | 10 | 300 | 24 | 5 | 0 | 300 | 0 | 0 | 181 | 0 | 131 | 0 | 100 | 0 | 10 | 0 | 115 | 70 | 0 | 0 | 269 | 0 | 0 | 0 | 113 | 100 | 0 | 104 |  | 935 | 0 | 320 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 8 | 89 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 160 | 0 | 42 | 0 | 160 | 0 | 399 | 0 | 0 | 94 | 0 | 107 | 0 | 0 | 109 | 470 |  | 6543 | 3436 | 9979 | 3095 | 935 | 2133 | 2658 | 619 | 89 | 316 | 134 | 0 | 0 | 93.29
5:00 | 28 | 0 | 0 | 110 | 0 | 100 | 66 | 341 | 353 |  | 0 | 380 | 130 | 7 | 64 | 55 | 0 | 0 | 0 | 0 | 7 | 16 | 82 | 19 | 0 | 0 | 41 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 88 | 0 | 0 | 0 | 0 | 110 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 89 | 50 | 21 | 41 | 0 | 70 | 0 | 265 | 180 | 194 | 8 | 90 | 5 | 0 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 130 | 158 | 74 | 17 | 0 | 60 | 28 | 50 | 43 | 110 | 162 | 64 | 85 | 0 | 70 | 18 | 0 | 10 | 290 | 24 | 5 | 0 | 300 | 0 | 0 | 185 | 0 | 131 | 0 | 100 | 0 | 10 | 0 | 115 | 0 | 0 | 0 | 269 | 0 | 0 | 0 | 113 | 100 | 0 | 104 |  | 935 | 0 | 330 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 160 | 0 | 42 | 0 | 160 | 0 | 409 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | 109 | 470 |  | 6379 | 3349 | 9728 | 3098 | 935 | 2091 | 2472 | 620 | 88 | 294 | 130 | 0 | 0 | 93.29
6:00 | 28 | 0 | 0 | 110 | 0 | 100 | 66 | 348 | 302 |  | 0 | 350 | 145 | 7 | 64 | 55 | 0 | 0 | 0 | 0 | 7 | 16 | 48 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 88 | 0 | 0 | 0 | 0 | 110 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 23 | 0 | 21 | 41 | 0 | 70 | 0 | 265 | 180 | 194 | 8 | 93 | 5 | 0 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 116 | 156 | 48 | 17 | 0 | 60 | 30 | 50 | 43 | 110 | 160 | 64 | 85 | 0 | 70 | 18 | 0 | 10 | 280 | 24 | 5 | 0 | 300 | 0 | 0 | 189 | 0 | 131 | 0.1 | 0 | 0 | 10 | 0 | 45 | 0 | 0 | 0.1 | 269 | 0 | 0 | 0 | 55 | 100 | 0 | 104 |  | 936 | 0 | 355 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 160 | 0 | 42 | 0 | 160 | 0 | 355 | 0 | 0 | 0 | 0 | 78 | 0 | 0.1 | 0 | 470 |  | 5743.2 | 3083.1 | 8826.3 | 3131 | 936 | 1938 | 1830 | 619 | 88 | 168 | 116 | 0.3 | 0 | 93.29
7:00 | 28 | 0 | 0 | 110 | 0 | 100 | 66 | 346 | 303 |  | 0 | 350 | 135 | 7 | 64 | 55 | 0 | 0 | 0 | 0 | 7 | 16 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 81 | 0 | 0 | 0 | 0 | 110 | 0 | 103 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 21 | 32 | 0 | 80 | 0 | 265 | 185 | 194 | 8 | 94 | 5 | 0 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 15 | 110 | 156 | 48 | 17 | 0.7 | 60 | 30 | 50 | 44 | 110 | 161 | 64 | 85 | 0 | 70 | 18 | 0 | 10 | 305 | 24 | 5 | 0 | 300 | 0 | 0 | 194 | 0 | 131 | 1.7 | 90 | 0 | 10 | 0 | 16 | 0 | 0 | 0.3 | 269 | 0 | 0 | 0 | 26 | 100 | 0 | 104 |  | 935 | 0 | 320 | 0 | 21 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 148 | 0 | 22 | 0 | 130 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 400 |  | 5724.7 | 2725.2 | 8449.9 | 3061 | 935 | 1918 | 1656 | 549 | 81 | 136 | 110 | 3.9 | 0 | 93.29
8:00 | 28 | 0 | 0 | 110 | 0 | 100 | 65 | 351 | 332 |  | 0 | 350 | 140 | 7 | 64 | 55 | 0 | 0 | 0 | 0 | 7 | 16 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 111 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 7 | 0 | 80 | 0 | 265 | 180 | 179 | 8 | 96 | 5 | 0 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 15 | 106 | 154 | 48 | 17 | 1.9 | 60 | 30 | 50 | 44 | 110 | 164 | 64 | 85 | 0 | 70 | 18 | 0 | 10 | 300 | 24 | 5 | 0 | 300 | 0 | 0 | 194 | 0 | 131 | 1.4 | 90 | 0 | 10 | 0 | 16 | 0 | 0 | 0.6 | 269 | 0 | 0 | 0 | 26 | 100 | 0 | 104 |  | 936 | 0 | 345 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 130 | 0 | 22 | 0 | 130 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 400 |  | 5693.9 | 2727.5 | 8421.4 | 3039 | 936 | 1930 | 1640 | 549 | 80 | 136 | 106 | 5.4 | 0 | 93.29
9:00 | 28 | 0 | 0 | 110 | 0 | 100 | 64 | 375 | 352 |  | 0 | 320 | 140 | 7 | 64 | 55 | 0 | 0 | 0 | 0 | 7 | 16 | 16 | 4 | 0 | 0 | 0 | 53 | 55 | 55 | 0 | 25 | 29 | 33 | 33 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 110 | 0 | 106 | 0 |  | 0 | 0 | 0 | 0 | 21 | 0 | 21 | 5 | 0 | 80 | 0 | 265 | 180 | 171 | 0 | 95 | 5 | 0 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 15 | 108 | 153 | 66 | 17 | 1.8 | 60 | 30 | 47 | 44 | 130 | 160 | 65 | 85 | 0 | 81 | 18 | 0 | 10 | 310 | 24 | 5 | 0 | 300 | 0 | 0 | 200 | 0 | 131 | 5.2 | 100 | 0 | 0 | 0 | 16 | 16 | 0 | 2.2 | 285 | 0 | 0 | 0 | 51 | 100 | 0 | 104 |  | 935 | 0 | 340 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 130 | 0 | 22 | 0 | 130 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 35 | 400 |  | 5933.2 | 2752.2 | 8685.4 | 3054 | 935 | 1930 | 1881 | 549 | 80 | 136 | 108 | 12.4 | 0 | 93.29
10:00 | 28 | 0 | 0 | 110 | 0 | 98 | 64 | 378 | 350 |  | 0 | 320 | 150 | 7 | 64 | 55 | 0 | 0 | 0 | 0 | 7 | 16 | 106 | 25 | 0 | 0 | 10 | 53 | 55 | 55 | 22 | 25 | 29 | 33 | 33 | 22 | 0 | 82 | 0 | 0 | 0 | 1 | 112 | 0 | 105 | 0 |  | 0 | 0 | 0 | 10 | 60 | 0 | 21 | 3 | 0 | 80 | 0 | 265 | 180 | 155 | 0 | 86 | 5 | 0 | 0 | 0 | 0 | 0 | 12 | 18 | 8 | 33 | 15 | 114 | 137 | 72 | 17 | 2.3 | 60 | 28 | 44 | 43 | 130 | 161 | 63 | 85 | 0 | 81 | 18 | 0 | 10 | 310 | 24 | 5 | 0 | 300 | 34 | 0 | 145 | 14 | 117 | 16.6 | 100 | 2 | 0 | 0 | 20 | 70 | 0 | 4.4 | 289 | 0 | 0 | 90 | 113 | 100 | 0 | 104 |  | 935 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 82 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 9 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 130 | 0 | 22 | 0 | 130 | 0 | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8 | 35 | 400 |  | 6289.3 | 2779.8 | 9069.1 | 3040 | 935 | 1886 | 2207 | 549 | 82 | 226 | 114 | 30.1 | 0 | 93.29
11:00 | 28 | 0 | 0 | 110 | 0 | 97 | 63 | 339 | 350 |  | 0 | 320 | 145 | 7 | 80 | 55 | 0 | 0 | 0 | 0 | 7 | 16 | 149 | 25 | 0 | 0 | 41 | 53 | 55 | 55 | 0 | 25 | 29 | 33 | 33 | 42 | 0 | 82 | 0 | 0 | 0 | 25 | 112 | 0 | 104 | 0 |  | 0 | 0 | 0 | 10 | 80 | 34 | 21 | 3 | 0 | 80 | 0 | 270 | 180 | 160 | 0 | 94 | 5 | 0 | 0 | 0 | 0 | 0 | 32 | 18 | 8 | 33 | 15 | 112 | 122 | 66 | 17 | 2.4 | 60 | 30 | 44 | 43 | 130 | 162 | 63 | 82 | 0 | 80 | 18 | 0 | 9 | 280 | 24 | 5 | 0 | 300 | 34 | 0 | 143 | 26 | 115 | 5.4 | 100 | 45 | 0 | 0 | 24 | 70 | 0 | 4.8 | 305 | 0 | 0 | 114 | 113 | 100 | 0 | 104 |  | 935 | 0 | 330 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 83 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 9 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 130 | 0 | 22 | 0 | 130 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7 | 0 | 400 |  | 6475.6 | 2667.7 | 9143.3 | 2959 | 935 | 1797 | 2421 | 549 | 82 | 269 | 112 | 19.3 | 0 | 93.29
12:00 | 28 | 0 | 0 | 110 | 0 | 94 | 63 | 348 | 348 |  | 0 | 320 | 145 | 7 | 80 | 40 | 0 | 0 | 0 | 0 | 7 | 16 | 149 | 25 | 0 | 0 | 41 | 53 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 20 | 0 | 84 | 0 | 0 | 0 | 25 | 112 | 0 | 106 | 0 |  | 0 | 0 | 0 | 10 | 84 | 50 | 21 | 4 | 0 | 80 | 0 | 265 | 180 | 168 | 0 | 96 | 5 | 0 | 0 | 0 | 0 | 36 | 39 | 18 | 8 | 33 | 15 | 118 | 120 | 66 | 17 | 1 | 59 | 30 | 47 | 43 | 130 | 162 | 63 | 81 | 0 | 80 | 18 | 0 | 9 | 290 | 24 | 5 | 0 | 300 | 36 | 0 | 200 | 26 | 116 | 13.1 | 100 | 50 | 0 | 0 | 8 | 88 | 0 | 1.8 | 307 | 0 | 0 | 114 | 113 | 100 | 0 | 104 |  | 932 | 0 | 350 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 9 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 140 | 0 | 22 | 0 | 158 | 0 | 403 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 0 | 400 |  | 6623.9 | 2816.6 | 9440.5 | 3058 | 932 | 1895 | 2480 | 549 | 84 | 305 | 118 | 19.5 | 0 | 93.29
13:00 | 28 | 0 | 0 | 110 | 0 | 97 | 63 | 359 | 346 |  | 0 | 320 | 135 | 7 | 80 | 40 | 0 | 0 | 0 | 0 | 7 | 16 | 149 | 25 | 0 | 0 | 41 | 53 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 39 | 0 | 86 | 0 | 0 | 0 | 25 | 112 | 0 | 110 | 0 |  | 0 | 0 | 0 | 10 | 84 | 50 | 21 | 8 | 0 | 80 | 0 | 265 | 180 | 169 | 0 | 86 | 5 | 0 | 0 | 0 | 0 | 42 | 43 | 18 | 8 | 33 | 15 | 124 | 118 | 74 | 17 | 2.2 | 59 | 30 | 47 | 43 | 130 | 160 | 63 | 84 | 0 | 81 | 18 | 0 | 10 | 300 | 24 | 5 | 0 | 288 | 0 | 0 | 200 | 0 | 115 | 7.9 | 100 | 50 | 0 | 0 | 8 | 88 | 0 | 2.3 | 305 | 0 | 0 | 114 | 113 | 100 | 0 | 104 |  | 933 | 0 | 370 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 9 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 180 | 0 | 32 | 0 | 180 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9 | 0 | 410 |  | 6600.4 | 2933.9 | 9534.3 | 3143 | 933 | 1920 | 2440 | 560 | 86 | 311 | 124 | 17.3 | 0 | 93.3
14:00 | 28 | 0 | 0 | 110 | 0 | 100 | 63 | 352 | 323 |  | 0 | 320 | 135 | 7 | 84 | 40 | 0 | 0 | 0 | 0 | 8 | 16 | 139 | 27 | 0 | 0 | 41 | 53 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 51 | 0 | 86 | 0 | 0 | 0 | 25 | 112 | 0 | 106 | 0 |  | 0 | 0 | 0 | 10 | 91 | 50 | 21 | 5 | 0 | 80 | 0 | 265 | 180 | 160 | 0 | 88 | 5 | 0 | 0 | 0 | 0 | 50 | 43 | 18 | 8 | 33 | 15 | 132 | 118 | 74 | 17 | 2.4 | 59 | 30 | 47 | 43 | 130 | 105 | 63 | 84 | 0 | 81 | 18 | 0 | 10 | 290 | 24 | 5 | 0 | 286 | 0 | 0 | 200 | 0 | 115 | 11.8 | 100 | 60 | 0 | 0 | 8 | 88 | 0 | 2.8 | 305 | 0 | 0 | 114 | 113 | 100 | 0 | 102 |  | 933 | 0 | 385 | 0 | 49 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 193 | 0 | 47 | 0 | 180 | 0 | 385 | 0 | 0 | 0 | 0 | 8 | 0 | 5.2 | 30 | 420 |  | 6537 | 3045.2 | 9582.2 | 3098 | 933 | 1889 | 2543 | 570 | 86 | 309 | 132 | 22.2 | 0 | 93.3
15:00 | 28 | 0 | 0 | 110 | 0 | 97 | 63 | 355 | 353 |  | 0 | 320 | 145 | 7 | 96 | 40 | 0 | 0 | 0 | 0 | 7 | 16 | 136 | 26 | 0 | 0 | 41 | 53 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 51 | 0 | 86 | 0 | 0 | 0 | 25 | 112 | 0 | 104 | 0 |  | 0 | 0 | 0 | 50 | 91 | 50 | 21 | 4 | 0 | 80 | 0 | 265 | 180 | 156 | 0 | 84 | 5 | 0 | 0 | 0 | 0 | 48 | 43 | 18 | 8 | 33 | 19 | 134 | 118 | 66 | 17 | 0.4 | 60 | 28 | 47 | 44 | 130 | 105 | 63 | 83 | 0 | 81 | 18 | 0 | 10 | 290 | 24 | 5 | 0 | 286 | 58 | 50 | 200 | 52 | 124 | 6.6 | 100 | 109 | 0 | 0 | 8 | 88 | 0 | 3 | 305 | 0 | 0 | 114 | 113 | 100 | 0 | 104 |  | 933 | 0 | 370 | 0 | 49 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 191 | 0 | 52 | 0 | 199 | 0 | 380 | 0 | 0 | 0 | 0 | 34 | 0 | 4.2 | 35 | 420 |  | 6821 | 3080.2 | 9901.2 | 3096 | 933 | 1918 | 2846 | 570 | 86 | 304 | 134 | 14.2 | 0 | 93.3
16:00 | 28 | 0 | 0 | 110 | 0 | 96 | 63 | 339 | 347 |  | 0 | 320 | 150 | 7 | 96 | 40 | 0 | 0 | 0 | 0 | 7 | 16 | 115 | 26 | 0 | 0 | 41 | 53 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 8 | 0 | 82 | 0 | 0 | 0 | 8 | 112 | 0 | 103 | 0 |  | 0 | 0 | 0 | 50 | 92 | 50 | 21 | 4 | 0 | 80 | 0 | 265 | 180 | 144 | 0 | 95 | 5 | 0 | 0 | 0 | 0 | 48 | 43 | 21 | 8 | 33 | 20 | 132 | 117 | 66 | 17 | 1.2 | 60 | 30 | 47 | 44 | 130 | 104 | 63 | 83 | 0 | 80 | 18 | 0 | 10 | 270 | 24 | 0 | 0 | 286 | 0 | 0 | 200 | 0 | 106 | 4.7 | 100 | 135 | 0 | 0 | 8 | 88 | 0 | 1.7 | 305 | 0 | 0 | 70 | 113 | 100 | 0 | 104 |  | 934 | 0 | 355 | 0 | 49 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 184 | 0 | 34 | 0 | 180 | 0 | 400 | 0 | 0 | 0 | 0 | 35 | 0 | 4.3 | 35 | 400 |  | 6494.6 | 3023.3 | 9517.9 | 3035 | 934 | 1893 | 2597 | 550 | 82 | 283 | 132 | 11.9 | 0 | 93.3
17:00 | 28 | 0 | 0 | 110 | 0 | 97 | 63 | 341 | 353 |  | 0 | 320 | 140 | 7 | 96 | 40 | 0 | 0 | 0 | 0 | 7 | 18 | 64 | 26 | 0 | 0 | 41 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 8 | 0 | 86 | 0 | 0 | 0 | 8 | 111 | 0 | 104 | 0 |  | 0 | 0 | 0 | 20 | 92 | 50 | 21 | 15 | 0 | 80 | 0 | 265 | 180 | 158 | 0 | 86 | 5 | 0 | 0 | 0 | 0 | 40 | 43 | 21 | 0 | 33 | 20 | 126 | 118 | 74 | 17 | 0.5 | 60 | 28 | 50 | 44 | 130 | 111 | 65 | 83 | 0 | 80 | 18 | 0 | 10 | 270 | 24 | 2 | 0 | 286 | 0 | 0 | 200 | 0 | 112 | 1.8 | 100 | 32 | 0 | 0 | 8 | 88 | 0 | 0.6 | 305 | 0 | 0 | 34 | 113 | 100 | 0 | 104 |  | 933 | 0 | 320 | 0 | 27 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 159 | 0 | 32 | 0 | 150 | 0 | 315 | 0 | 0 | 0 | 0 | 38 | 0 | 1.8 | 35 | 400 |  | 6297.9 | 2822.8 | 9120.7 | 2955 | 933 | 1827 | 2415 | 550 | 86 | 224 | 126 | 4.7 | 0 | 93.3
18:00 | 28 | 0 | 0 | 110 | 0 | 101 | 40 | 352 | 303 |  | 0 | 320 | 150 | 7 | 0 | 40 | 0 | 0 | 0 | 0 | 7 | 16 | 64 | 26 | 0 | 0 | 0 | 0 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 8 | 0 | 85 | 0 | 0 | 0 | 8 | 111 | 0 | 104 | 0 |  | 0 | 0 | 0 | 20 | 92 | 50 | 21 | 6 | 0 | 80 | 0 | 265 | 180 | 165 | 0 | 94 | 5 | 0 | 0 | 0 | 0 | 40 | 43 | 21 | 8 | 33 | 15 | 130 | 120 | 74 | 17 | 0.1 | 60 | 30 | 34 | 30 | 110 | 113 | 67 | 50 | 0 | 80 | 18 | 0 | 10 | 290 | 24 | 3 | 0 | 286 | 0 | 0 | 200 | 0 | 100 | 0.1 | 100 | 32 | 0 | 0 | 8 | 80 | 0 | 0 | 252 | 0 | 0 | 34 | 76 | 100 | 0 | 87 |  | 932 | 0 | 270 | 0 | 32 | 120 | 0 | 0 | 0 | 0 | 8 | 90 | 17 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 160 | 0 | 32 | 0 | 150 | 0 | 270 | 0 | 0 | 0 | 0 | 39 | 0 | 0.2 | 35 | 350 |  | 5886.2 | 2701.2 | 8587.4 | 2945 | 932 | 1642 | 2120 | 500 | 85 | 233 | 130 | 0.4 | 0 | 93.3
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 28 | 0 | 0 | 110 | 0 | 101 | 65 | 359 | 355 |  | 0 | 420 | 135 | 7 | 0 | 40 | 0 | 0 | 0 | 0 | 7 | 16 | 133 | 53 | 0 | 0 | 0 | 0 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 36 | 0 | 85 | 0 | 0 | 0 | 8 | 111 | 0 | 104 | 0 |  | 0 | 0 | 86 | 40 | 97 | 50 | 21 | 13 | 0 | 80 | 0 | 265 | 180 | 173 | 0 | 86 | 5 | 0 | 0 | 0 | 0 | 44 | 43 | 21 | 8 | 33 | 21 | 158 | 124 | 74 | 17 | 0 | 60 | 31 | 50 | 44 | 130 | 115 | 67 | 83 | 0 | 80 | 18 | 0 | 10 | 290 | 24 | 5 | 70 | 286 | 227 | 96 | 200 | 102 | 128 | 0 | 100 | 80 | 0 | 0 | 36 | 88 | 0 | 0 | 305 | 0 | 0 | 114 | 113 | 100 | 0 | 100 |  | 932 | 0 | 375 | 0 | 115 | 160 | 0 | 0 | 0 | 0 | 40 | 87 | 27 | 64 | 0 | 0 | 0 | 50 | 35 | 87 | 0 | 8 | 33 | 28 | 15 | 18 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 173 | 0 | 67 | 23 | 181 | 0 | 350 | 25 | 0 | 45 | 0 | 74 | 0 | 0 | 70 | 360 |  | 7217 | 3614 | 10831 | 3116 | 932 | 2034 | 3353 | 510 | 85 | 643 | 158 | 0 | 0 | 93.3
19:30 | 28 | 0 | 0 | 110 | 0 | 101 | 65 | 339 | 353 |  | 0 | 420 | 138 | 7 | 0 | 40 | 0 | 0 | 0 | 0 | 7 | 16 | 133 | 100 | 0 | 0 | 18 | 0 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 85 | 0 | 0 | 0 | 8 | 111 | 0 | 104 | 0 |  | 0 | 0 | 86 | 40 | 97 | 50 | 21 | 25 | 0 | 80 | 0 | 265 | 180 | 173 | 0 | 86 | 5 | 0 | 0 | 0 | 0 | 49 | 43 | 21 | 8 | 33 | 21 | 156 | 125 | 74 | 17 | 0 | 60 | 28 | 50 | 44 | 130 | 116 | 67 | 85 | 0 | 80 | 18 | 0 | 10 | 290 | 24 | 11 | 70 | 286 | 209 | 100 | 193 | 102 | 130 | 0 | 100 | 120 | 0 | 0 | 115 | 88 | 0 | 0 | 305 | 0 | 0 | 114 | 113 | 100 | 0 | 104 |  | 932 | 0 | 375 | 0 | 99 | 180 | 0 | 0 | 0 | 0 | 40 | 90 | 29 | 64 | 0 | 0 | 0 | 50 | 35 | 98 | 0 | 8 | 35 | 43 | 28 | 18 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 187 | 0 | 75 | 100 | 210 | 0 | 364 | 53 | 0 | 90 | 0 | 0 | 0 | 0 | 90 | 370 |  | 7404 | 3835 | 11239 | 3147 | 932 | 2070 | 3635 | 520 | 85 | 694 | 156 | 0 | 0 | 0
20:00 | 28 | 0 | 0 | 110 | 0 | 101 | 65 | 338 | 354 |  | 0 | 420 | 150 | 7 | 1 | 40 | 0 | 0 | 0 | 0 | 7 | 16 | 133 | 100 | 0 | 0 | 30 | 0 | 55 | 55 | 22 | 25 | 30 | 0 | 33 | 51 | 0 | 84 | 0 | 0 | 0 | 8 | 111 | 0 | 103 | 0 |  | 0 | 0 | 85 | 40 | 97 | 50 | 21 | 32 | 0 | 80 | 0 | 265 | 180 | 174 | 0 | 86 | 5 | 0 | 0 | 0 | 0 | 49 | 43 | 21 | 11 | 33 | 21 | 150 | 124 | 74 | 17 | 0 | 60 | 31 | 50 | 44 | 130 | 82 | 67 | 85 | 0 | 80 | 18 | 0 | 10 | 275 | 24 | 11 | 50 | 286 | 56 | 70 | 193 | 57 | 131 | 0 | 100 | 200 | 0 | 0 | 115 | 88 | 0 | 0 | 305 | 0 | 0 | 114 | 113 | 100 | 0 | 104 |  | 932 | 0 | 370 | 0 | 99 | 180 | 0 | 0 | 0 | 0 | 40 | 89 | 30 | 64 | 0 | 0 | 0 | 50 | 35 | 100 | 0 | 8 | 45 | 43 | 32 | 18 | 9 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 187 | 0 | 76 | 100 | 209 | 0 | 350 | 53 | 0 | 90 | 0 | 35 | 0 | 0 | 100 | 370 |  | 7184 | 3875 | 11059 | 3077 | 932 | 2049 | 3538 | 520 | 84 | 709 | 150 | 0 | 0 | 93.3
21:00 | 28 | 0 | 0 | 110 | 0 | 101 | 65 | 354 | 355 |  | 0 | 450 | 145 | 7 | 38 | 40 | 0 | 0 | 0 | 0 | 7 | 16 | 133 | 100 | 0 | 0 | 41 | 30 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 43 | 0 | 84 | 0 | 0 | 0 | 8 | 112 | 0 | 104 | 0 |  | 0 | 0 | 78 | 40 | 97 | 50 | 21 | 35 | 0 | 80 | 0 | 300 | 180 | 159 | 8 | 96 | 5 | 0 | 0 | 0 | 0 | 49 | 43 | 21 | 11 | 33 | 21 | 154 | 123 | 75 | 17 | 0 | 59 | 30 | 50 | 44 | 130 | 142 | 67 | 85 | 0 | 80 | 18 | 0 | 10 | 295 | 24 | 11 | 0 | 286 | 38 | 25 | 193 | 26 | 131 | 0 | 100 | 150 | 0 | 0 | 115 | 88 | 0 | 0 | 305 | 0 | 0 | 114 | 113 | 100 | 0 | 104 |  | 932 | 0 | 350 | 0 | 99 | 180 | 0 | 0 | 0 | 0 | 40 | 89 | 30 | 64 | 0 | 0 | 0 | 43 | 35 | 100 | 0 | 8 | 47 | 43 | 32 | 18 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 185 | 0 | 79 | 100 | 213 | 0 | 402 | 53 | 0 | 94 | 15 | 66 | 0 | 0 | 109 | 380 |  | 7253 | 3978 | 11231 | 3197 | 932 | 2168 | 3469 | 530 | 84 | 697 | 154 | 0 | 0 | 93.3
22:00 | 28 | 0 | 0 | 110 | 0 | 101 | 65 | 349 | 352 |  | 0 | 450 | 145 | 7 | 78 | 40 | 0 | 0 | 0 | 0 | 7 | 16 | 133 | 30 | 0 | 0 | 41 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 43 | 0 | 84 | 0 | 0 | 0 | 8 | 112 | 0 | 105 | 0 |  | 0 | 0 | 85 | 40 | 97 | 50 | 21 | 40 | 0 | 80 | 0 | 270 | 180 | 159 | 8 | 94 | 5 | 0 | 0 | 0 | 0 | 49 | 43 | 21 | 11 | 33 | 21 | 156 | 123 | 75 | 17 | 0 | 60 | 30 | 50 | 44 | 130 | 192 | 67 | 85 | 0 | 80 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 286 | 39 | 25 | 200 | 26 | 131 | 0 | 100 | 150 | 0 | 0 | 115 | 88 | 0 | 0 | 307 | 0 | 0 | 114 | 113 | 100 | 0 | 104 |  | 931 | 0 | 335 | 0 | 99 | 180 | 0 | 0 | 0 | 0 | 40 | 90 | 30 | 64 | 0 | 0 | 0 | 50 | 35 | 100 | 0 | 8 | 45 | 43 | 30 | 18 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 185 | 0 | 77 | 100 | 204 | 0 | 409 | 53 | 0 | 94 | 15 | 109 | 0 | 0 | 109 | 400 |  | 7277 | 4025 | 11302 | 3189 | 931 | 2170 | 3515 | 550 | 84 | 707 | 156 | 0 | 0 | 93.3
23:00 | 28 | 0 | 0 | 110 | 0 | 101 | 65 | 344 | 353 |  | 0 | 450 | 150 | 7 | 97 | 40 | 0 | 0 | 0 | 0 | 7 | 16 | 133 | 26 | 0 | 0 | 41 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 47 | 0 | 83 | 0 | 0 | 0 | 0 | 111 | 0 | 107 | 0 |  | 0 | 0 | 68 | 20 | 97 | 50 | 21 | 41 | 0 | 80 | 0 | 270 | 185 | 160 | 8 | 95 | 5 | 0 | 0 | 0 | 0 | 50 | 43 | 21 | 11 | 33 | 21 | 154 | 126 | 75 | 17 | 0 | 60 | 30 | 50 | 44 | 130 | 230 | 63 | 85 | 0 | 81 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 286 | 33 | 0 | 200 | 25 | 132 | 0 | 100 | 150 | 0 | 0 | 115 | 88 | 0 | 0 | 306 | 0 | 0 | 114 | 113 | 100 | 0 | 104 |  | 931 | 0 | 325 | 0 | 99 | 180 | 0 | 0 | 0 | 0 | 40 | 90 | 31 | 64 | 0 | 0 | 0 | 50 | 35 | 100 | 0 | 8 | 44 | 43 | 30 | 18 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 186 | 0 | 77 | 10 | 204 | 0 | 408 | 53 | 0 | 94 | 15 | 113 | 0 | 0 | 109 | 440 |  | 7265 | 3968 | 11233 | 3221 | 931 | 2172 | 3393 | 589 | 83 | 690 | 154 | 0 | 0 | 93.3
24:00 | 28 | 0 | 0 | 110 | 0 | 102 | 65 | 355 | 354 |  | 0 | 450 | 130 | 7 | 97 | 55 | 0 | 0 | 0 | 0 | 7 | 16 | 133 | 25 | 0 | 0 | 41 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 43 | 0 | 85 | 0 | 0 | 0 | 0 | 111 | 0 | 105 | 0 |  | 0 | 0 | 68 | 20 | 97 | 50 | 21 | 41 | 0 | 80 | 0 | 270 | 180 | 160 | 8 | 85 | 5 | 0 | 0 | 0 | 0 | 50 | 43 | 21 | 11 | 33 | 21 | 148 | 144 | 75 | 17 | 0 | 60 | 30 | 50 | 43 | 130 | 239 | 64 | 85 | 0 | 80 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 286 | 56 | 0 | 200 | 0 | 132 | 0 | 100 | 150 | 0 | 0 | 115 | 88 | 0 | 0 | 306 | 0 | 0 | 114 | 113 | 100 | 0 | 104 |  | 932 | 0 | 325 | 0 | 99 | 180 | 0 | 0 | 0 | 0 | 40 | 89 | 30 | 32 | 0 | 0 | 0 | 50 | 35 | 100 | 0 | 8 | 44 | 43 | 30 | 18 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 191 | 0 | 77 | 0 | 201 | 0 | 398 | 53 | 0 | 94 | 0 | 107 | 0 | 0 | 109 | 510 |  | 7263 | 3966 | 11229 | 3225 | 932 | 2172 | 3318 | 659 | 85 | 690 | 148 | 0 | 0 | 93.3
KWH | 554000 | 0 | 0 | 2693250 | 0 | 2335545 | 1492736 | 8561660 | 8149000 |  | 0 | 7938000 | 3450502 | 216000 | 1732224 | 1130930 | 0 | 0 | 0 | 0 | 199680 | 400896 | 2547840 | 848817 | 0 | 0 | 756912 | 1057320 | 1194741 | 1215291 | 403164 | 600000 | 667980 | 784200 | 804900 | 636696 | 0 | 1955095 | 0 | 0 | 0 | 224787 | 2600211 | 0 | 2537854 | 0 |  | 0 | 0 | 541631 | 407880 | 1893120 | 963360 | 472080 | 555360 | 0 | 1830575 | 0 | 6750400 | 4409000 | 4201000 | 117090 | 2192850 | 130608 | 0 | 0 | 480681 | 0 | 566288 | 779501 | 471060 | 195300 | 809200 | 447860 | 3177600 | 3127000 | 1674240 | 351396 | 14750 | 1420000 | 705840 | 1161600 | 1038816 | 3129463 | 3320000 | 1521696 | 1993920 | 0 | 1847920 | 415000 | 0 | 241920 | 7247500 | 573768 | 138144 | 82944 | 7075633 | 606387 | 260885 | 4476000 | 370810 | 3006720 | 86940 | 2334720 | 1461120 | 97018 | 0 | 1473600 | 1718460 | 0 | 26040 | 6945164 | 0 | 0 | 1517340 | 2444400 | 2425920 | 0 | 2579520 |  | 22403636 | 0 | 8349120 | 0 | 1494720 | 3481920 | 0 | 0 | 19200 | 0 | 383250 | 2157669 | 437275 | 344640 | 0 | 0 | 0 | 354096 | 246453 | 1026504 | 0 | 77696 | 357500 | 294240 | 228740 | 444240 | 238572 | 216900 | 0 | 0 | 3652800 | 0 | 0 | 0 | 0 | 4344273 | 0 | 1136075 | 406080 | 4592982 | 0 | 9108000 | 308640 | 0 | 934656 | 50112 | 1284480 | 0 | 45216 | 1413696 | 11191400 |  | 157995269 | 81024781 | 239020050 | 75198860 | 22403636 | 47245793 | 64651748 | 14844200 | 1955095 | 9370172 | 3177600 | 172946 | 0
Fuel Cost | 908560 | 0 | 0 | 3959077.5 | 0 | 3082919.4 | 2537651.2 | 8647276.6 | 8393470 |  | 0 | 8652420 | 3830057.22 | 1639440 | 11935023.36 | 9567667.8 | 0 | 0 | 0 | 0 | 1503590.4 | 3656171.52 | 25070745.6 | 7826092.74 | 0 | 0 | 6880330.08 | 7718436 | 9235347.93 | 11982769.26 | 302373 | 450000 | 0 | 0 | 0 | 6156850.32 | 0 | 527875.65 | 0 | 0 | 0 | 2088271.23 | 2834229.99 | 0 | 4314351.8 | 0 |  | 0 | 0 | 5253820.7 | 3895254 | 16470144 | 7629811.2 | 594820.8 | 1649419.2 | 0 | 2709251 | 0 | 4995296 | 4409000 | 3864920 | 151046.1 | 2521777.5 | 147587.04 | 0 | 0 | 821964.51 | 0 | 5719508.8 | 7444234.55 | 598246.2 | 146475 | 1416100 | 335895 | 23832000 | 3314620 | 15202099.2 | 446272.92 | 235115 | 2328800 | 1129344 | 2067648 | 1620552.96 | 3567587.82 | 3452800 | 2997741.12 | 3808387.2 | 0 | 3196901.6 | 908850 | 0 | 493516.8 | 7319975 | 430326 | 104989.44 | 1410877.44 | 53491785.48 | 10296451.26 | 4361997.2 | 23275200 | 6199943.2 | 29586124.8 | 1016328.6 | 19027968 | 15853152 | 683976.9 | 0 | 13439232 | 16239447 | 0 | 0 | 52505439.84 | 0 | 0 | 15143053.2 | 20948508 | 16156627.2 | 0 | 0 |  | 129044943.36 | 0 | 8766576 | 0 | 11748499.2 | 48259411.2 | 0 | 0 | 201408 | 0 | 3993465 | 2438165.97 | 677776.25 | 3363686.4 | 0 | 0 | 0 | 3484304.64 | 2503962.48 | 9084560.4 | 0 | 1050449.92 | 3464175 | 2851185.6 | 2218778 | 852940.8 | 369786.6 | 164193.3 | 0 | 0 | 19798176 | 0 | 0 | 0 | 0 | 5734440.36 | 0 | 1704112.5 | 6907420.8 | 5373788.94 | 0 | 9016920 | 3222201.6 | 0 | 8869885.44 | 473057.28 | 9967564.8 | 0 | 499636.8 | 10447213.44 | 49130246 |  | 600569209.38 | 365682932.08 | 966252141.46 | 83943047.08 | 129044943.36 | 56788094.34 | 496176003.81 | 68928422 | 527875.65 | 105260674.82 | 23832000 | 1751080.4 | 0
Yesterday Day Peak | 28 | 0 | 0 | 110 | 0 | 94 | 63 | 348 | 348 |  | 0 | 320 | 145 | 7 | 80 | 40 | 0 | 0 | 0 | 0 | 7 | 16 | 149 | 25 | 0 | 0 | 41 | 53 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 20 | 0 | 84 | 0 | 0 | 0 | 25 | 112 | 0 | 106 | 0 |  | 0 | 0 | 0 | 10 | 84 | 50 | 21 | 4 | 0 | 80 | 0 | 265 | 180 | 168 | 0 | 96 | 5 | 0 | 0 | 0 | 0 | 36 | 39 | 18 | 8 | 33 | 15 | 118 | 120 | 66 | 17 | 1 | 59 | 30 | 47 | 43 | 130 | 162 | 63 | 81 | 0 | 80 | 18 | 0 | 9 | 290 | 24 | 5 | 0 | 300 | 36 | 0 | 200 | 26 | 116 | 13.1 | 100 | 50 | 0 | 0 | 8 | 88 | 0 | 1.8 | 307 | 0 | 0 | 114 | 113 | 100 | 0 | 104 |  | 932 | 0 | 350 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 9 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 140 | 0 | 22 | 0 | 158 | 0 | 403 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 0 | 400 |  | 9440.5 | DayPeak
Yesterday Evening Peak | 28 | 0 | 0 | 110 | 0 | 101 | 65 | 339 | 353 | 0 | 0 | 420 | 138 | 7 | 0 | 40 | 0 | 0 | 0 | 0 | 7 | 16 | 133 | 100 | 0 | 0 | 18 | 0 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 85 | 0 | 0 | 0 | 8 | 111 | 0 | 104 | 0 | 0 | 0 | 0 | 86 | 40 | 97 | 50 | 21 | 25 | 0 | 80 | 0 | 265 | 180 | 173 | 0 | 86 | 5 | 0 | 0 | 0 | 0 | 49 | 43 | 21 | 8 | 33 | 21 | 156 | 125 | 74 | 17 | 0 | 60 | 28 | 50 | 44 | 130 | 116 | 67 | 85 | 0 | 80 | 18 | 0 | 10 | 290 | 24 | 11 | 70 | 286 | 209 | 100 | 193 | 102 | 130 | 0 | 100 | 120 | 0 | 0 | 115 | 88 | 0 | 0 | 305 | 0 | 0 | 114 | 113 | 100 | 0 | 104 |  | 932 | 0 | 375 | 0 | 99 | 180 | 0 | 0 | 0 | 0 | 40 | 90 | 29 | 64 | 0 | 0 | 0 | 50 | 35 | 98 | 0 | 8 | 35 | 43 | 28 | 18 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 187 | 0 | 75 | 100 | 210 | 0 | 364 | 53 | 0 | 90 | 0 | 0 | 0 | 0 | 90 | 370 |  | 11239 | EvPeak
Forecast for Evening | 28 | 0 | 0 | 110 | 0 | 100 | 65 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 96 | 55 | 0 | 0 | 0 | 0 | 7 | 16 | 149 | 100 | 0 | 0 | 41 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 80 | 0 | 0 | 0 | 25 | 111 | 0 | 105 | 0 | 0 | 0 |  | 100 | 100 | 97 | 50 | 20 | 25 | 0 | 80 | 0 | 360 | 360 | 170 | 8 | 96 | 5 | 5 | 0 | 51 | 0 | 42 | 43 | 21 | 11 | 33 | 20 | 173 | 160 | 72 | 17 | 0 | 60 | 30 | 51 | 44 | 163 | 210 | 66 | 86 | 0 | 80 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 133 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 104 |  | 942 | 16 | 380 | 0 | 115 | 220 | 0 | 0 | 30 | 60 | 40 | 90 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 0 | 50 | 50 | 43 | 32 | 18 | 11 | 11 | 0 | 0 | 150 | 0 | 10 | 0 | 0 | 220 | 0 | 80 | 100 | 220 | 0 | 414 | 105 | 200 | 95 | 100 | 113 | 0 | 0 | 113 | 422
Forecast for Day | 28 | 0 | 0 | 110 | 0 | 100 | 65 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 96 | 55 | 0 | 0 | 0 | 0 | 7 | 16 | 149 | 100 | 0 | 0 | 41 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 35 | 0 | 80 | 0 | 0 | 0 | 25 | 111 | 0 | 105 | 0 | 0 | 0 |  | 100 | 100 | 97 | 50 | 20 | 15 | 0 | 80 | 0 | 360 | 360 | 170 | 8 | 96 | 5 | 5 | 0 | 51 | 0 | 0 | 43 | 21 | 11 | 33 | 20 | 157 | 160 | 72 | 17 | 1.6 | 60 | 30 | 51 | 44 | 163 | 210 | 66 | 86 | 0 | 80 | 18 | 0 | 10 | 341 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 80 | 133 | 20 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 5 | 300 | 50 | 50 | 114 | 113 | 100 | 0 | 104 |  | 942 | 0 | 380 | 0 | 115 | 220 | 0 | 0 | 0 | 0 | 40 | 90 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 50 | 0 | 43 | 0 | 18 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 |  | 80 | 60 | 220 | 0 | 414 | 105 | 100 | 95 | 100 | 113 | 0 | 8 | 113 | 422
Generation at 08:00(Today) | 28 | 0 | 0 | 110 | 0 | 102 | 64 | 360 | 303 | 0 | 0 | 340 | 130 |  | 96 | 23 | 0 | 0 | 0 | 0 | 7 | 16 | 16 | 11 | 0 | 0 | 0 | 53 | 17 | 17 | 19 | 25 | 27 | 33 | 33 | 0 | 0 | 84 | 0 | 0 | 0 | 0 | 111 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 21 | 2 | 0 | 80 | 0 | 290 | 180 | 171 | 8 | 96 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 33 | 15 | 112 | 157 | 75 | 17 | 0.7 | 60 | 30 | 50 | 44 | 130 | 212 | 64 | 83 | 0 | 80 | 0 | 0 | 10 | 300 | 24 | 5 | 0 | 200 | 0 | 0 | 200 | 0 | 95 | 1.1 | 100 | 0 | 0 | 0 | 8 | 50 | 0 | 1.4 | 237 | 0 | 0 | 0 | 99 | 100 | 0 | 104 | 0 | 931 | 0 | 340 | 0 | 83 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 175 | 0 | 77 | 0 | 150 | 0 | 306 | 0 | 0 | 4 | 0 | 38 | 0 | 2.4 | 90 | 240 | 0
199
| Minimum Generation |  | 8421.4 | 8:00
| Highest Generation |  | 11302 | 22:00
| Day Peak Generation |  | 9440.5 | 12:00
| Evening Peak Generation |  | 11239 | 19:30
| HVDC Max Flow |  | 936 | 2:00
| HVDC EvPeak Flow |  | 932 | 19:30
| Load factor L.F |  | 88.12%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-08-27
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-08-26 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9440.5 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 8491.6 | MW
Evening Peak Generation : |  | 11239 | MW Hour : | 19:30 | Available Max Generation : |  | 14009 | MW
E.P. Demand (at gen end) : |  | 11239 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 11800 | MW
Maximum Generation : |  | 11302 | MW Hour : | 22:00 | Reserve(Generation end) |  | 2209 | MW
Total Gen. (MKWH) : |  | 239.0201 | System Load Factor : | 88.12% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 154 | MW at | 3:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-08-27
Actual : | 93.3 | Ft.(MSL) , | Rule curve : | 97.35 | Ft.( MSL )
Gas Consumed : | Total = | 1036.56 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 140731141.42
: |  | Coal : | 68928422 | Oil : | 601436678.63 | Total : | 811096242.05
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4282.6597 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1458.7681 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1307.4402 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1181.5361 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1067.6524 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 861.5638 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 478.6213 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 221.7469 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 664.4957 |  |  | 0 | 0%
Total | 0 |  | 11524.4841 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Bibiyana #3
3) Ghorasal Unit-2,3,4,7
4) Ashuganj unit-3,5
5) Bhola-225 MW GT-2 & ST
6) Kaptai-2,4,5
7) Raozan #1,2
8) Sirajganj #1
9) Baghabari-71 & 100 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Hathazari-Raozan P.P. 230 Ckt-1 was shut down at 10:39 due to oil leakage.
b) Ishwardi 132/33 kV T1 transformer was under shut down from 11:55 to 15:08 to attend R/H at 33 kV
Bushing clamp.
c) Ashuganj 230 kV Bus-1 was under shut down from 10:44 to 18:22 due to Y-phase loop maintenance of
Ashuganj-Sirajganj 230 kV Ckt-1. Midland 51 MW, Midland 150 MW, Ashuganj Modular were under S/D
for above maintenance work.
d) Bagerhat 132/33 kV T1&T2 transformers tripped at 10:17 due to 33 kV feeder fault and were switched on at |  |  |  |  | About 26 MW power interruption occurred under Bagerhat S/S area
10:23. |  |  |  |  | from 10:17 to 10:23.
e) Ashuganj 230/132 kV OAT12 transformer was switched on at 16:16.
f) Payra Unit-2 was synchronized for the first time at 17:35 and shut down at 22:55 and again synchronized
at 02:09(27/08/2020).
g) Hathazari-Baroaulia 132 kV Ckt-1 tripped at 16:11 from both ends showing E/F, B-phase at Hathazari end
& Dist. C-phase, E/F at Baroaulia end.
h) Haripur-Madanganj 132 kV Ckt tripped at 17:55 showing O/C due to Munshiganj 33/11 kV auxiliary |  |  |  |  | About 25 MW power interruption occurred under Madanganj S/S area from
transformer fault and was switched on at 19:05. At the same time Madanganj 100 MW, Banco & |  |  |  |  | 17:55 to 18:06.
Katpotti were trip.
i) Munshiganj 132/33 kV T1&T2 transformers 33 kV incoming tripped at 17:55 and was switched on at |  |  |  |  | About 82 MW power interruption occurred under Munshiganj S/S area from
18:26 & 20:30 respectively. |  |  |  |  | 17:55 to 18:26.
j) Ashuganj 230 kV Bus CB was closed at 21:06.
k) Cumilla(N) 132/33 kV T3 transformer tripped at 23:42 showing O/C due to 33 kV Moinamoti feeder fault |  |  |  |  | About 15 MW power interruption occurred under Cumilla(N) S/S area from
and was switched on at 00:14(27/08/2020). |  |  |  |  | 23:42 to 00:14(27/08/2020).
l) Cumilla(N) 132/33 kV T3 transformer's 33 kV side was under shut down from 04:07(27/08/2020) to
04:57(27/08/2020) due to R/H at 33 kV Moinamoti feeder Bus DS.
m) Kabirpur 132/33 kV T-3 transformer was shut down at 06:10(27/08/2020) for C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-08-26 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 28 | 554000 | Unit-1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 110 | 2693250
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 65 | 1492736 | Engine problem
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 101 | 2335545
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 339 | 8561660 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 353 | 8149000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 7938000 | Frequency control.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 7 | 216000 | Fuel Shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 138 | 3450502 | GT-1 Under S/D.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 1732224 | Grid line fault
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 40 | 1130930 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 100 | 848817
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 403164
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 7 | 199680 | Fuel Shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 16 | 400896 | Fuel Shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 18 | 756912 | Engine problem
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 1057320
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 133 | 2547840 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1194741
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1215291
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1267980 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 784200
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 804900
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 636696
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 286 | 7075633
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 209 | 606387 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 100 | 260885
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 102 | 370810
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 130 | 3006720 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 88 | 1718460 | Engine problem
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2579520
| Dhaka area Total |  |  |  | 5895 | 3198 | 65990699
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 8 | 224787 | Low demand
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 86940
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 963360
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 85 | 1955095 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 111 | 2600211 | Machine problem
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 104 | 2537854 | Gas shortage.
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 86 | 541631
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 40 | 407880 | Low demand
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2334720
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 472080
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 25 | 555360
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 97 | 1893120
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26040
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 305 | 6945164
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2425920
| Chattogram area Total |  |  |  | 2266 | 1132 | 23970162
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 80 | 1830575 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 173 | 4201000 | Gas shortage
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 265 | 6750400 | Gas shortage
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 180 | 4409000 | Gas shortage
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 5 | 130608 | Gas shortage.
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 0 | 0 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 117090 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 480681 | Gas shortage
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 97018 | Line over load
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 49 | 566288
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 86 | 2192850 | ST under maint.
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 120 | 1461120
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 471060
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 195300 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 156 | 3177600
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 809200
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 779501 | Engine problem
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 447860
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 70 | 82944 | Low demand
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1517340
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 2444400
| Cumilla Area Total |  |  |  | 2980 | 1537 | 32161835
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 125 | 3127000 | Engine problem
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 351396 | Engine problem
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 74 | 1674240 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14750
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 193 | 4476000
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1473600 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 524 | 11116986
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1420000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 28 | 705840 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3129463 | Frequency control.
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 116 | 3320000 | ST under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1161600
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 44 | 1038816
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 138144
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 67 | 1521696 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1993920
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 80 | 1847920 | Machine problem
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 415000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 573768
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7247500 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 241920
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1013 | 24755587
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 932 | 22403636
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 1494720 | Engine problem
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 19200 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 180 | 3481920
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 375 | 8349120 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 383250
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 406080
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 308640 | Low demand
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 50112 | Reserve
| Khulna Area Total |  |  |  | 2284 | 1779 | 36896678
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 64 | 344640 | Low demand
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 29 | 437275 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 90 | 2157669 | GT-2 Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 75 | 1136075 | Engine problem
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 370 | 11191400
| Barisal Area Total |  |  |  | 1054 | 628 | 15267059
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 354096
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 35 | 246453
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 8 | 77696 | Low demand
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 357500
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage.
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 187 | 4344273 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 210 | 4592982 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 364 | 9108000 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 228740
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 18 | 444240
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 11 | 238572
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 216900
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 294240 | Engine problem
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 98 | 1026504
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 90 | 934656 | Engine problem
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 90 | 1413696 | Engine problem
| Rajshahi Area Total |  |  |  | 2183 | 1278 | 23878548
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3652800 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Machine problem
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 0 | 1284480
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 45216
| Rangpur Area Total |  |  |  | 605 | 150 | 4982496
| Total |  |  |  | 19892 | 11239 | 239020050
| Eastern Grid Total |  |  |  | 13766 | 7404 | 157995269
| Western Grid Total |  |  |  | 6126 | 3835 | 81024781
| National Grid Total |  |  |  | 19892 | 11239 | 239020050
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-08-26
| (a) ENTIRE EASTERN GRID : |  | 7440 | MW | (b) ENTIRE WESTERN GRID : |  | 3532 | MW
| i) Dhaka area |  | 3843 | MW | i) Khulna area |  | 1353 | MW
| ii) Chittagong area |  | 1143 | MW | ii) Rajshahi area |  | 1182 | MW
| iii) Comilla area |  | 1002 | MW | iii) Barisal area |  | 291 | MW
| iv) Mymensingh area |  | 945 | MW | iv) Rangpur area |  | 706 | MW
| v) Sylhet area |  | 507 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 10972 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 114 | 15:00 | Sherpur | 112 | 22:00 | Jhenida | 104 | 19:30
| Munsiganj | 104 | 22:00 | Srimongal | 51 | 19:30 | Bottail | 123 | 19:00
| Sonargaon | 87 | 23:00 | Shahjibazar | 121 | 22:00 | G.K Project | 53 | 1:00
| Shyampur | 194 | 9:00 | Fenchuganj | 45 | 19:00 | Faridpur | 180 | 0.875
| Bhulta | 203 | 23:00 | Kulawara | 48 | 19:00 | Madaripur | 89 | 0.91667
| Madanganj | 56 | 0:00 | Sylhet | 126 | 20:00 | Sariatpur | 58 | 21:00
| Shitalakhya | 111 | 12:00 | Chatak | 31 | 22:00 | Gopalganj | 77 | 19:30
| Rahim steel | 12 | 6:00 | Sunamganj | 48 | 21:00 | Bagerhat | 86 | 19:30
| Matuail | 80 | 12:00 | Biani Bazar | 59 | 21:00 | Mongla | 48 | 10:00
| Ghorasal | 76 | 22:00 | Comilla (S) | 158 | 19:00 | Satkhira | 92 | 0.875
| Narsingdi | 162 | 22:00 | Comilla(N) | 99 | 23:00 | Gallamari | 38 | 13:00
| Haripur (SBU) | 100 | 15:00 | Chandpur | 87 | 23:00 | Magura | 50 | 0.8125
| Ullon | 54 | 18:30 | Feni | 107 | 21:00 | Norail | 36 | 20:00
| Hasnabad | 184 | 22:00 | Chowmuhani | 161 | 22:00 | Chuadanga | 86 | 1:00
| Magbazar | 97 | 14:00 | Ashuganj | 55 | 24:00 | Barisal(N) | 38 | 0.95833
| Maniknagar | 92 | 11:00 | Daudkandi | 135 | 0:00 | Barisal (S) | 92 | 0.79167
| Bangabhaban | 36 | 11:00 | B.Baria | 140 | 19:00 | Patuakhali | 104 | 0.91667
| Narinda | 86 | 11:00 | Ramganj | 100 | 21:00 | Bhandaria | 50 | 0.83333
| Dhanmondi | 158 | 12:00 | Chaddagram | 34 | 22:00 | Borhan Uddin | 42 | 22:00
| Lalbag | 86 | 12:00 | PHP | 4 | 19:00 | Ishurdi | 58 | 19:30
| Madartek | 64 | 22:00 | Madunaghat | 53 | 10:00 | Ruppur Paromanobik | 2 | 1:00
| Dhaka University |  |  | Hathazari | 96 | 0.8125 | Natore | 116 | 21:00
| Fatullah | 35 | 0.625 | Khulshi | 181 | 0.5 | Bogra | 170 | 20:00
| Mirpur | 97 | 19:00 | Halishahar | 123 | 0.45833 | Noagaon | 123 | 21:00
| Kalyanpur | 96 | 19:00 | Baraulia | 154 | 0.29167 | Rajshahi | 138 | 20:00
| Gulshan | 122 | 13:00 | Sikalbaha | 27 | 0.77083 | Rajshahi New | 11 | 19:30
| Uttara | 75 | 13:00 | Dohazari | 78 | 0.83333 | C.Nawabganj | 71 | 1:00
| Uttara New | 27 | 15:00 | Cox'sbazar | 90 | 0.8125 | Amnura | 48 | 21:00
| Kamrangirchar | 88 | 19:00 | Chandraghona | 30 | 0.5 | Pabna | 111 | 20:00
| Savar | 143 | 13:00 | Kaptai | 4.2 | 0.375 | Shahjadpur | 94 | 20:00
| Bhasantec | 138 | 13:00 | A. Khaer Stl. | 0 | 0.041667 | Serajganj | 102 | 19:30
| Agargaon | 65 | 13:00 | Bakulia | 95 | 0.625 | Niyamatpur | 57 | 1:00
| Satmosjid | 79 | 13:00 | Julda | 20 | 0.041667 | Joypurhat | 54 | 20:00
| Tongi | 122 | 0.625 | TK chemical | 28 | 0.79167 | Sherpur(Bogura) | 48 | 21:00
| Kabirpur | 222 | 15:00 | Modern Steel | 16 | 0.125 | Mohastangor | 50 | 20:00
| Basundhara | 117 | 19:00 | Shahmirpur | 30 | 0.83333 | Rangpur | 140 | 19:00
| Manikganj | 64 | 0.875 | Khagrachhari | 22 | 0.70833 | Lalmonirhat | 61 | 1:00
| Joydevpur | 180 | 15:00 | Matarbari | 29 | 0.83333 | Saidpur | 102 | 1:00
| New Tongi | 103 | 15:00 | Baroiar Hat | 34 | 0.79167 | Purbasadipur | 100 | 19:30
| Korda | 206 | 11:00 | Rangamati | 12 | 0.77083 | Thakurgaon | 82 | 21:00
| Dhamrai | 88 | 21:00 | Abul Khair 230 | 130 | 0.54167 | Palashbari | 125 | 1:00
| Rajendrapur | 96 | 19:00 | BSRM | 104 | 0.54167 | Barapukuria | 53 | 20:00
| Valuka | 98 | 19:00 | GPH Ispat | 79 | 0.41667 | Panchagar | 51 | 21:00
| Tangail | 174 | 21:00 | Goalpara | 22 | 0.54167 | Joldhaka | 30 | 21:00
| Mymensing | 218 | 1:00 | Central s/s | 81 | 19:00 | Kurigram | 56 | 19:00
| Kishorganj | 136 | 1:00 | Noapara | 49 | 19:00
| Netrokona | 113 | 19:30 | Jessore | 104 | 19:30
| Jamalpur | 135 | 1:00 | Benapol | 46 | 19:00
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-08-26 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 396 | 10:00 | 388 | 18:30 | Kaliakoir | 380 | 0.20833 | 371 | 0.66667
| Bheramara | 400 | 8:00 | 392 | 1:00 | Bhulta | 389 | 0.16667 | 379 | 0.66667
| Ashuganj(N) | 395 | 4:00 | 386 | 16:00 | Gopalganj | 419 | 0.29167 | 396 | 24:00
| Payra | 418 | 7:00 | 407 | 23:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 232 | 23:00 | 230 | 1:00 | Comilla (N) | 235 | 5:00 | 232 | 23:00
| Ishurdi | 234 | 17:00 | 228 | 13:00 | Hathazari | 229 | 20:00 | 219 | 8:00
| Ashuganj | 240 | 3:00 | 232 | 14:00 | Megnaghat | 232 | 11:00 | 230 | 1:00
| Serajganj | 231 | 18:00 | 226 | 1:00 | Fenchuganj | 239 | 8:00 | 235 | 5:00
| Baghabari | 241 | 18:30 | 238 | 1:00 | Siddhirganj | 231 | 4:00 | 224 | 13:00
| Barapukuria | 233 | 18:00 | 222 | 19:00 | Maniknagar | 229 | 4:00 | 222 | 16:00
| Bogra | 223 | 18:30 | 213 | 13:00 | Agargaon | 228 | 4:00 | 221 | 16:00
| Rajshahi | 231 | 18:30 | 221 | 13:00 | Barisal | 245 | 3:00 | 236 | 24:00
| Khulna South | 236 | 20:00 | 226 | 12:00 | AKSML | 228 | 20:00 | 218 | 6:00
| Rampura | 229 | 5:00 | 222 | 12:00 | BSRM | 228 | 20:00 | 220 | 6:00
| Haripur | 228 | 5:00 | 222 | 12:00 | Bibiyana | 236 | 5:00 | 231 | 22:00
| Hasnabad | 230 | 5:00 | 224 | 11:00 | Bhulta | 231 | 19:00 | 224 | 17:00
| Shyampur | 226 | 4:00 | 220 | 12:00 | Ashuganj (S) | 236 | 4:00 | 231 | 16:00
| Aminbazar | 228 | 8:00 | 220 | 17:00 | Kaliakoir | 233 | 5:00 | 226 | 12:00
| Tongi | 227 | 18:00 | 225 | 1:00 | GPH | 225 | 5:00 | 220 | 4:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 131 | 2:00 | 128 | 12:00 | Hathazari | 136 | 0.45833 | 131 | 0.33333
| Munsiganj | 140 | 19:00 | 131 | 7:00 | Khulshi | 135 | 0.041667 | 131 | 0.29167
| Sonargaon | 132 | 19:00 | 130 | 10:00 | Halishahar | 138 | 0.70833 | 133 | 0.25
| Shyampur | 133 | 4:00 | 129 | 12:00 | Baraulia | 134 | 0.041667 | 130 | 0.29167
| Bhulta | 124 | 4:00 | 120 | 1:00 | Sikalbaha | 138 | 17:00 | 133 | 0.33333
| Madanganj | 134 | 4:00 | 0 | 18:00 | Dohazari | 135 | 17:00 | 130 | 0.16667
| Shitalakhya | 140 | 19:00 | 132 | 12:00 | Cox'sbazar | 129 | 0.45833 | 121 | 0.95833
| Rahim steal | 131 | 3:00 | 128 | 12:00 | Chandraghona | 136 | 0.16667 | 132 | 0.25
| Matuail | 131 | 2:00 | 128 | 12:00 | Kaptai | 135 | 18:00 | 134 | 0.041667
| Ghorasal | 138 | 11:00 | 136 | 1:00 | A. Khaer Stl. | 134 | 0.041667 | 130 | 8:00
| Narsinghdi | 127 | 5:00 | 122 | 23:00 | Bakulia | 137 | 0.83333 | 132 | 0.29167
| Haripur (SBU) | 132 | 2:00 | 126 | 5:00 | Julda | 138 | 0.70833 | 132 | 0.29167
| Ullon | 133 | 2:00 | 128 | 12:00 | TK Chemical | 137 | 0.70833 | 134 | 5:00
| Hasnabad | 137 | 2:00 | 134 | 8:00 | Modern Steel | 136 | 0.66667 | 132 | 0.20833
| Magbazar | 135 | 5:00 | 127 | 13:00 | Shahmirpur | 137 | 0.125 | 134 | 0.375
| Maniknagar | 134 | 4:00 | 128 | 16:00 | Khagrachhari | 135 | 0.70833 | 131 | 0.25
| Bangabhaban | 134 | 4:00 | 128 | 16:00 | Matarbari | 131 | 0.70833 | 125 | 0.95833
| Narinda | 134 | 4:00 | 128 | 16:00 | Baroiar Hat | 136 | 0.41667 | 131 | 0.041667
| Dhanmondi | 133 | 2:00 | 128 | 12:00 | Rangamati | 136 | 0.58333 | 132 | 6:00
| Lalbag | 138 | 19:00 | 129 | 12:00 | Goalpara S/S | 137 | 6:00 | 132 | 12:00
| Madartek | 133 | 2:00 | 128 | 12:00 | Khulna Central S/S | 137 | 0.25 | 131 | 12:00
| Dhaka University |  |  |  |  | Noapara | 135 | 20:00 | 129 | 13:00
| Fatuiiah | 134 | 0.25 | 129 | 9:00 | Jessore | 132 | 6:00 | 126 | 1:00
| Mirpur | 131 | 3:00 | 128 | 11:00 | Benapol | 131 | 6:00 | 125 | 1:00
| Kalyanpur | 133 | 7:00 | 128 | 13:00 | Jhenida | 130 | 0.70833 | 120 | 1:00
| Gulshan | 133 | 3:00 | 128 | 12:00 | Bottail | 134 | 17:00 | 127 | 1:00
| Uttara | 132 | 7:00 | 125 | 16:00 | G.K Project | 138 | 0.375 | 134 | 1:00
| Uttara New | 137 | 3:00 | 131 | 8:00 | Faridpur | 134 | 7:00 | 127 | 1:00
| Kamrangirchar | 137 | 19:30 | 129 | 13:00 | Madaripur | 140 | 0.125 | 131 | 23:00
| Savar | 132 | 7:00 | 126 | 16:00 | Shariyatpur S/S | 140 | 0.29167 | 129 | 23:00
| Bhasantec | 133 | 3:00 | 127 | 13:00 | Gopalganj | 141 | 7:00 | 132 | 1:00
| Agargaon | 134 | 3:00 | 129 | 13:00 | Bagerhat | 135 | 17:00 | 126 | 12:00
| Satmosjid | 134 | 4:00 | 128 | 13:00 | Mongla | 131 | 0.70833 | 122 | 12:00
| Tongi | 137 | 0.95833 | 134 | 15:00 | Satkhira | 136 | 0.70833 | 131 | 1:00
| Kabirpur | 136 | 11:00 | 132 | 21:00 | Gallamari | 137 | 6:00 | 132 | 12:00
| Basundhara | 133 | 3:00 | 127 | 13:00 | Magura | 128 | 6:00 | 116 | 1:00
| Manikganj | 140 | 24:00 | 135 | 8:00 | Norail | 127 | 0.75 | 115 | 1:00
| Joydevpur | 139 | 21:00 | 135 | 9:00 | Chuadanga | 125 | 17:00 | 110 | 1:00
| New Tongi | 136 | 1904-01-02 | 131 | 16:00 | Barisal(N) | 139 | 6:00 | 133 | 22:00
| Kodda | 137 | 24:00 | 131 | 0.375 | Barisal (S) | 139 | 0.33333 | 132 | 22:00
| Dhamrai | 136 | 7:00 | 130 | 19:30 | Patuakhali(S) | 139 | 0.375 | 125 | 22:00
| Rajendrapur | 136 | 1:00 | 127 | 8:00 | Bhandaria | 131 | 17:00 | 124 | 12:00
| Valuka | 127 | 12:00 | 115 | 1:00 | Ishurdi | 136 | 6:00 | 133 | 1:00
| Tangail | 136 | 8:00 | 127 | 10:00 | Ruppur Paromanobik | 136 | 18:30 | 132 | 13:00
| Mymensing | 130 | 12:00 | 117 | 1:00 | Natore | 134 | 18:30 | 128 | 13:00
| Kishorganj | 129 | 7:00 | 117 | 1:00 | Bogra | 132 | 17:00 | 126 | 13:00
| Netrokona | 127 | 10:00 | 114 | 1:00 | Noagaon | 131 | 18:00 | 122 | 19:30
| Jamalpur | 139 | 10:00 | 132 | 1:00 | Rajshahi | 132 | 18:30 | 125 | 13:00
| Sherpur | 138 | 9:00 | 128 | 1:00 | Rajshahi New | 132 | 19:30 | 126 | 13:00
| Srimongal | 136 | 8:00 | 130 | 0.041667 | C.Nawabganj | 130 | 18:30 | 123 | 11:00
| Shahjibazar | 135 | 10:00 | 128 | 0.041667 | Amnura | 130 | 20:00 | 123 | 11:00
| Fenchuganj | 135 | 15:00 | 130 | 1904-01-02 | Pabna | 133 | 7:00 | 129 | 19:30
| Khulawara | 133 | 8:00 | 129 | 0.041667 | Shahjadpur | 136 | 4:00 | 133 | 12:00
| Sylhet | 132 | 15:00 | 127 | 0.041667 | Serajganj | 133 | 18:00 | 128 | 12:00
| Chatak | 130 | 15:00 | 125 | 22:00 | Niyamatpur | 129 | 17:00 | 120 | 19:00
| Sunamganj | 129 | 16:00 | 121 | 0.91667 | Joypurhat | 131 | 18:30 | 121 | 1:00
| Biani Bazar | 130 | 15:00 | 124 | 0.91667 | Sherpur(Bogura) | 134 | 18:00 | 126 | 13:00
| Comilla(s) | 126 | 7:00 | 122 | 23:00 | Mohastangor | 131 | 18:00 | 124 | 13:00
| Comilla(n) | 138 | 9:00 | 135 | 23:00 | Rangpur | 127 | 18:00 | 116 | 19:00
| Chandpur | 140 | 7:00 | 136 | 18:30 | Lalmonirhat | 122 | 6:00 | 112 | 1:00
| Feni | 138 | 10:00 | 131 | 8:00 | Saidpur | 126 | 18:00 | 112 | 19:30
| Chowmuhani | 136 | 7:00 | 131 | 22:00 | Purbasadipur | 122 | 18:00 | 104 | 19:30
| Ashuganj | 135 | 14:00 | 130 | 1:00 | Thakurgaon | 124 | 18:00 | 108 | 19:00
| Daudkandi | 135 | 15:00 | 125 | 9:00 | Palashbari | 126 | 18:30 | 114 | 19:30
| B.Baria | 132 | 6:00 | 127 | 22:00 | Barapukuria | 133 | 18:00 | 122 | 19:00
| Ramganj | 135 | 15:00 | 125 | 9:00 | Panchagar | 123 | 18:00 | 99 | 19:30
| Chaddagram | 138 | 10:00 | 131 | 1:00 | Joldhaka | 124 | 17:00 | 108 | 19:30
| PHP | 137 | 10:00 | 130 | 1:00 | Kurigram | 122 | 18:00 | 108 | 19:00
| Madanhat | 139 | 17:00 | 134 | 8:00

## L-Curve
Date | 2020-08-26
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 336 | 7263 | 3966 | 11229 |  |  |  | QF-LDC-12
0:30 | 330 | 7007 | 4012.5 | 11019.5 | Date: | 2020-08-26
1:00 | 324 | 6751 | 4059 | 10810
1:30 | 253 | 6753.5 | 3911.5 | 10665
2:00 | 182 | 6756 | 3764 | 10520
2:30 | 168 | 6713.5 | 3684 | 10397.5 | [5 empty] | Gen. at Eve. Peak | 11239 | 11239 MW (19:30 )
3:00 | 154 | 6671 | 3604 | 10275 | [6 empty] | 19:30
3:30 | 154.5 | 6607 | 3520 | 10127 | [5 empty] | Gen. at Day Peak | 9440.5 | 9440.5 MW (12:00 )
4:00 | 155 | 6543 | 3436 | 9979 | [6 empty] | 12:00
4:30 | 162.5 | 6461 | 3392.5 | 9853.5 | [5 empty] | Highest Generation | 11302
5:00 | 170 | 6379 | 3349 | 9728 | [6 empty] | 22:00
5:30 | 261 | 6061.1 | 3216.05 | 9277.15
6:00 | 352 | 5743.2 | 3083.1 | 8826.3
6:30 | 267 | 5733.95 | 2904.15 | 8638.1
7:00 | 182 | 5724.7 | 2725.2 | 8449.9
7:30 | 241 | 5709.3 | 2726.35 | 8435.65
8:00 | 300 | 5693.9 | 2727.5 | 8421.4
8:30 | 335 | 5813.55 | 2739.85 | 8553.4
9:00 | 370 | 5933.2 | 2752.2 | 8685.4
9:30 | 340 | 6111.25 | 2766 | 8877.25
10:00 | 310 | 6289.3 | 2779.8 | 9069.1
10:30 | 258.5 | 6382.45 | 2723.75 | 9106.2
11:00 | 207 | 6475.6 | 2667.7 | 9143.3
11:30 | 205 | 6549.75 | 2742.15 | 9291.9
12:00 | 203 | 6623.9 | 2816.6 | 9440.5
12:30 | 231.5 | 6612.15 | 2875.25 | 9487.4
13:00 | 260 | 6600.4 | 2933.9 | 9534.3
13:30 | 303.5 | 6568.7 | 2989.55 | 9558.25
14:00 | 347 | 6537 | 3045.2 | 9582.2
14:30 | 361 | 6679 | 3062.7 | 9741.7
15:00 | 375 | 6821 | 3080.2 | 9901.2
15:30 | 372 | 6657.8 | 3051.75 | 9709.55
16:00 | 369 | 6494.6 | 3023.3 | 9517.9
16:30 | 364.5 | 6396.25 | 2923.05 | 9319.3
17:00 | 360 | 6297.9 | 2822.8 | 9120.7
17:30 | 352.5 | 6092.05 | 2762 | 8854.05
18:00 | 345 | 5886.2 | 2701.2 | 8587.4
18:30 | 258.5 | 6551.6 | 3157.6 | 9709.2
19:00 | 172 | 7217 | 3614 | 10831
19:30 | 163 | 7404 | 3835 | 11239
20:00 | 197 | 7184 | 3875 | 11059 |  |  |  | Executive Engineer
20:30 | 239.5 | 7218.5 | 3926.5 | 11145 |  |  |  | Network Operation Division
21:00 | 282 | 7253 | 3978 | 11231
21:30 | 308 | 7265 | 4001.5 | 11266.5
22:00 | 334 | 7277 | 4025 | 11302 |  |  |  |  | Page 6 of 7
22:30 | 311 | 7271 | 3996.5 | 11267.5
23:00 | 288 | 7265 | 3968 | 11233
23:30 | 312 | 7264 | 3967 | 11231
24:00 | 336 | 7263 | 3966 | 11229
11239 MW (19:30 )
9440.5 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-08-26 |  | Energy | 239020050
[10 empty] | 2020-08-26 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3225 | 932 | 2172 | 3393 | 659 | 85 | 690 | 0 | 148
0:30 | 3193 | 933.5 | 2130.5 | 3178.5 | 704 | 84.5 | 687 | 0 | 146 | Date: | 2020-08-26
1:00 | 3161 | 935 | 2089 | 2964 | 749 | 84 | 684 | 0 | 144
1:30 | 3156.5 | 935.5 | 2114 | 2933 | 704 | 84.5 | 595.5 | 0 | 142 | [7 empty] | Total Energy | 239.02 | Total Energy Gen 239.020 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 239.020 MKWHr
2:00 | 3152 | 936 | 2139 | 2902 | 659 | 85 | 507 | 0 | 140 | [7 empty] | Energy not Served | 0
2:30 | 3156.5 | 935 | 2160 | 2840 | 639 | 86 | 442 | 0 | 139 | [7 empty] | Energy Requirement | 239.02
3:00 | 3161 | 934 | 2181 | 2778 | 619 | 87 | 377 | 0 | 138
3:30 | 3128 | 934.5 | 2157 | 2718 | 619 | 88 | 346.5 | 0 | 136 | [6 empty] | Shortage
4:00 | 3095 | 935 | 2133 | 2658 | 619 | 89 | 316 | 0 | 134
4:30 | 3096.5 | 935 | 2112 | 2565 | 619.5 | 88.5 | 305 | 0 | 132
5:00 | 3098 | 935 | 2091 | 2472 | 620 | 88 | 294 | 0 | 130
5:30 | 3114.5 | 935.5 | 2014.5 | 2151 | 619.5 | 88 | 231 | 0 | 123
6:00 | 3131 | 936 | 1938 | 1830 | 619 | 88 | 168 | 0 | 116
6:30 | 3096 | 935.5 | 1928 | 1743 | 584 | 84.5 | 152 | 0 | 113 |  |  |  |  | Coal
7:00 | 3061 | 935 | 1918 | 1656 | 549 | 81 | 136 | 0 | 110
7:30 | 3050 | 935.5 | 1924 | 1648 | 549 | 80.5 | 136 | 0 | 108 |  |  |  | Oil |  |  |  | ,
8:00 | 3039 | 936 | 1930 | 1640 | 549 | 80 | 136 | 0 | 106
8:30 | 3046.5 | 935.5 | 1930 | 1760.5 | 549 | 80 | 136 | 0 | 107
9:00 | 3054 | 935 | 1930 | 1881 | 549 | 80 | 136 | 0 | 108
9:30 | 3047 | 935 | 1908 | 2044 | 549 | 81 | 181 | 0 | 111
10:00 | 3040 | 935 | 1886 | 2207 | 549 | 82 | 226 | 0 | 114
10:30 | 2999.5 | 935 | 1841.5 | 2314 | 549 | 82 | 247.5 | 0 | 113
11:00 | 2959 | 935 | 1797 | 2421 | 549 | 82 | 269 | 0 | 112
11:30 | 3008.5 | 933.5 | 1846 | 2450.5 | 549 | 83 | 287 | 0 | 115
12:00 | 3058 | 932 | 1895 | 2480 | 549 | 84 | 305 | 0 | 118
12:30 | 3100.5 | 932.5 | 1907.5 | 2460 | 554.5 | 85 | 308 | 0 | 121
13:00 | 3143 | 933 | 1920 | 2440 | 560 | 86 | 311 | 0 | 124
13:30 | 3143 | 933 | 1920 | 2440 | 560 | 86 | 311 | 0 | 124
14:00 | 3143 | 933 | 1920 | 2440 | 560 | 86 | 311 | 0 | 124
14:30 | 3119.5 | 933 | 1919 | 2643 | 565 | 86 | 307.5 | 0 | 129
15:00 | 3096 | 933 | 1918 | 2846 | 570 | 86 | 304 | 0 | 134
15:30 | 3065.5 | 933.5 | 1905.5 | 2721.5 | 560 | 84 | 293.5 | 0 | 133
16:00 | 3035 | 934 | 1893 | 2597 | 550 | 82 | 283 | 0 | 132
16:30 | 2995 | 933.5 | 1860 | 2506 | 550 | 84 | 253.5 | 0 | 129
17:00 | 2955 | 933 | 1827 | 2415 | 550 | 86 | 224 | 0 | 126
17:30 | 2950 | 932.5 | 1734.5 | 2267.5 | 525 | 85.5 | 228.5 | 0 | 128
18:00 | 2945 | 932 | 1642 | 2120 | 500 | 85 | 233 | 0 | 130
18:30 | 3030.5 | 932 | 1838 | 2736.5 | 505 | 85 | 438 | 0 | 144
19:00 | 3116 | 932 | 2034 | 3353 | 510 | 85 | 643 | 0 | 158
19:30 | 3147 | 932 | 2070 | 3635 | 520 | 85 | 694 | 0 | 156
20:00 | 3077 | 932 | 2049 | 3538 | 520 | 84 | 709 | 0 | 150
20:30 | 3137 | 932 | 2108.5 | 3503.5 | 525 | 84 | 703 | 0 | 152
21:00 | 3197 | 932 | 2168 | 3469 | 530 | 84 | 697 | 0 | 154
21:30 | 3193 | 931.5 | 2169 | 3492 | 540 | 84 | 702 | 0 | 155
22:00 | 3189 | 931 | 2170 | 3515 | 550 | 84 | 707 | 0 | 156
22:30 | 3205 | 931 | 2171 | 3454 | 569.5 | 83.5 | 698.5 | 0 | 155
23:00 | 3221 | 931 | 2172 | 3393 | 589 | 83 | 690 | 0 | 154
23:30 | 3223 | 931.5 | 2172 | 3393 | 624 | 84 | 690 | 0 | 151 | Max Temp. in Dhaka |  | 31.7° C
24:00 | 3225 | 932 | 2172 | 3393 | 659 | 85 | 690 | 0 | 148
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 239.020 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 239.020 MKWHr
Note on W13: Author:

## Generation
g | 2020-08-26
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 84 | 85 | 87 | 89 | 88 | 88 | 81 | 80 | 80 | 82 | 82 | 84 | 86 | 86 | 86 | 82 | 86 | 85 |  | 85 | 85 | 84 | 84 | 84 | 83 | 85 | 1955095
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [9 empty] | 1 | 25 | 25 | 25 | 25 | 25 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 |  | 0 | 224787
| Teknaf 20MW PP (Solartech) | [5 empty] | 0.1 | 1.7 | 1.4 | 5.2 | 16.6 | 5.4 | 13.1 | 7.9 | 11.8 | 6.6 | 4.7 | 1.8 | 0.1 | [8 empty] | 86940
6 | Sikalbaha 225MW CCPP (Gas) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 111 | 110 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 111 | 111 |  | 111 | 111 | 111 | 112 | 112 | 111 | 111 | 2600211
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 106 | 105 | 105 | 105 | 104 | 104 | 103 | 105 | 106 | 105 | 104 | 106 | 110 | 106 | 104 | 103 | 104 | 104 |  | 104 | 104 | 103 | 104 | 105 | 107 | 105 | 2537854
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 34 | 31 | [17 empty] | 86 | 86 | 85 | 78 | 85 | 68 | 68 | 541631
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [19 empty] | 70 | 70 | 50 |  |  |  |  | 82944
14 | Titas 50 MW Peaking PP | [11 empty] | 36 | 42 | 50 | 48 | 48 | 40 | 40 |  | 44 | 49 | 49 | 49 | 49 | 50 | 50 | 566288
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 288 | 286 | 286 | 286 | 286 | 286 |  | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 7075633
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 8 | 8 | 8 | 8 | 117090
20 | Ghorasal TPP (Unit-1&2) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 554000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2693250
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 70 | 70 | 70 | 70 | 70 | 70 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1830575
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 130608
33 | Ashuganj 225 MW CCPP | 195 | 195 | 195 | 191 | 194 | 194 | 194 | 179 | 171 | 155 | 160 | 168 | 169 | 160 | 156 | 144 | 158 | 165 |  | 173 | 173 | 174 | 159 | 159 | 160 | 160 | 4201000
34 | Ashuganj 450 MW CCPP(South) | 180 | 180 | 180 | 180 | 180 | 180 | 185 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 185 | 180 | 4409000
| Ashuganj 450 MW CCPP(North) | 265 | 265 | 265 | 265 | 265 | 265 | 265 | 265 | 265 | 265 | 270 | 265 | 265 | 265 | 265 | 265 | 265 | 265 |  | 265 | 265 | 265 | 300 | 270 | 270 | 270 | 6750400
35 | Ashuganj 55 MW PP (Precision) | [25 empty] | 0 | 0
36 | Chandpur 150 MW CCPP | 90 | 96 | 95 | 94 | 90 | 93 | 94 | 96 | 95 | 86 | 94 | 96 | 86 | 88 | 84 | 95 | 86 | 94 |  | 86 | 86 | 86 | 96 | 94 | 95 | 85 | 2192850
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 356 | 351 | 366 | 347 | 341 | 348 | 346 | 351 | 375 | 378 | 339 | 348 | 359 | 352 | 355 | 339 | 341 | 352 |  | 359 | 339 | 338 | 354 | 349 | 344 | 355 | 8561660
40 | Meghnaghat 450 MW CCPP(MPL) | 360 | 390 | 420 | 420 | 380 | 350 | 350 | 350 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  | 420 | 420 | 420 | 450 | 450 | 450 | 450 | 7938000
41 | Haripur 360MW CCPP(HPL) | 332 | 353 | 353 | 355 | 353 | 302 | 303 | 332 | 352 | 350 | 350 | 348 | 346 | 323 | 353 | 347 | 353 | 303 |  | 355 | 353 | 354 | 355 | 352 | 353 | 354 | 8149000
42 | RPCL 210MW CCPP | 141 | 142 | 142 | 158 | 158 | 156 | 156 | 154 | 153 | 137 | 122 | 120 | 118 | 118 | 118 | 117 | 118 | 120 |  | 124 | 125 | 124 | 123 | 123 | 126 | 144 | 3127000
43
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 59 | 59 | 59 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 59 | 60 | 60 | 60 | 1420000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 28 | 30 | 30 | 30 | 30 | 28 | 30 | 30 | 30 | 30 | 28 | 30 | 28 | 30 |  | 31 | 28 | 31 | 30 | 30 | 30 | 30 | 705840
46 | Shajibazar 330 MW CCPP | 161 | 160 | 158 | 160 | 162 | 160 | 161 | 164 | 160 | 161 | 162 | 162 | 160 | 105 | 105 | 104 | 111 | 113 |  | 115 | 116 | 82 | 142 | 192 | 230 | 239 | 3320000
47 | Shahjibazar GTPP Unit- 8 & 9 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 65 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 65 | 67 |  | 67 | 67 | 67 | 67 | 67 | 63 | 64 | 1521696
48 | Shahjibazar 86MW PP (Shahjibazar) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 82 | 81 | 84 | 84 | 83 | 83 | 83 | 50 |  | 83 | 85 | 85 | 85 | 85 | 85 | 85 | 1993920
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 81 | 81 | 80 | 80 | 81 | 81 | 81 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 81 | 80 | 1847920
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 0 | 415000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 241920
54 | Hobiganj 11MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 2 | 3 |  | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 138144
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 44 | 44 | 47 | 47 | 47 | 47 | 47 | 50 | 34 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1161600
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 573768
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 300 | 310 | 300 | 290 | 280 | 305 | 300 | 310 | 310 | 280 | 290 | 300 | 290 | 290 | 270 | 270 | 290 |  | 290 | 290 | 275 | 295 | 290 | 290 | 300 | 7247500
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1215291
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 472080
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 403164
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 351396
63 | Impoprt (Tripura) | 144 | 140 | 138 | 134 | 130 | 116 | 110 | 106 | 108 | 114 | 112 | 118 | 124 | 132 | 134 | 132 | 126 | 130 |  | 158 | 156 | 150 | 154 | 156 | 154 | 148 | 3177600
64 | Malancha, Ctg. EPZ (United) | 41 | 41 | 41 | 41 | 41 | 41 | 32 | 7 | 5 | 3 | 3 | 4 | 8 | 5 | 4 | 4 | 15 | 6 |  | 13 | 25 | 32 | 35 | 40 | 41 | 41 | 555360
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 18 | 18 | 18 | 18 | 18 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 471060
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 |  | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 195300
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 809200
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 19 | 20 | 20 | 15 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 447860
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 29 | 29 | 28 | 28 | 28 | 28 | 28 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 667980
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 |  | 33 | 33 | 33 | 33 | 784200
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 804900
73 | Ghorashal 108MW PP (Regent) | 101 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 98 | 97 | 94 | 97 | 100 | 97 | 96 | 97 | 101 |  | 101 | 101 | 101 | 101 | 101 | 101 | 102 | 2335545
| Feni Lanka Power | [9 empty] | 90 | 114 | 114 | 114 | 114 | 114 | 70 | 34 | 34 |  | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 1517340
| Chowmuhani 113 MW | 113 | 113 | 113 | 113 | 113 | 55 | 26 | 26 | 51 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 76 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2444400
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 199680
78 | Gazipur 52 MW PP | 51 | 8 | [7 empty] | 22 | 42 | 20 | 39 | 51 | 51 | 8 | 8 | 8 |  | 36 | 51 | 51 | 43 | 43 | 47 | 43 | 636696
79 | Kodda 150MW PP | 149 | 115 | 115 | 98 | 82 | 48 | 16 | 16 | 16 | 106 | 149 | 149 | 149 | 139 | 136 | 115 | 64 | 64 |  | 133 | 133 | 133 | 133 | 133 | 133 | 133 | 2547840
80 | Jamalpur 95 MW PP(Powerpac) | 74 | 74 | 74 | 74 | 74 | 48 | 48 | 48 | 66 | 72 | 66 | 66 | 74 | 74 | 66 | 66 | 74 | 74 |  | 74 | 74 | 74 | 75 | 75 | 75 | 75 | 1674240
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | [6 empty] | 12 | 32 | 39 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 779501
| Gazipur 100 MW PP | 105 | 105 | 105 | 70 |  |  |  |  | 16 | 70 | 70 | 88 | 88 | 88 | 88 | 88 | 88 | 80 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 1718460
| Kaptai 7 MW Solar PP | [5 empty] | 0.1 | 0.3 | 0.6 | 2.2 | 4.4 | 4.8 | 1.8 | 2.3 | 2.8 | 3 | 1.7 | 0.6 | [9 empty] | 26040
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | 97 | 88 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 80 | 80 | 80 | 84 | 96 | 96 | 96 |  |  |  |  | 1 | 38 | 78 | 97 | 97 | 1732224
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 59 | 100 | 37 | 26 | 19 |  |  |  | 4 | 25 | 25 | 25 | 25 | 27 | 26 | 26 | 26 | 26 |  | 53 | 100 | 100 | 100 | 30 | 26 | 25 | 848817
86 | Meghnaghat CCPP(Summit) | 140 | 150 | 145 | 135 | 130 | 145 | 135 | 140 | 140 | 150 | 145 | 145 | 135 | 135 | 145 | 150 | 140 | 150 |  | 135 | 138 | 150 | 145 | 145 | 150 | 130 | 3450502
87 | Meghnaghat 100 MW(IEL) | 24 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 216000
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 102 | 104 | 104 | 104 | 87 |  | 100 | 104 | 104 | 104 | 104 | 104 | 104 | 2579520
88 | Ghorashal 78.5 MW PP(MAX) | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 65 | 64 | 64 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 40 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1492736
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [9 empty] | 10 | 10 | 10 | 10 | 10 | 50 | 50 | 20 | 20 |  | 40 | 40 | 40 | 40 | 40 | 20 | 20 | 407880
92 | Fenchuganj 44MW (Energyprima) | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 44 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 44 | 30 |  | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 1038816
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | [16 empty] | 0 | 480681
94 | Gagnagar 102 MW PP (Digital Power) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 18 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 400896
95 | Patenga 50MW PP (Baraka) | 50 | 50 | 50 | 50 | 50 | [5 empty] | 34 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 963360
96 | Chattogram 108 MW PP (ECPV) | 97 | 97 | 91 | 94 | 89 | 23 | 12 | 12 | 21 | 60 | 80 | 84 | 84 | 91 | 91 | 92 | 92 | 92 |  | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 1893120
97 | Katpotti 52 MW PP (Sinha) | 41 | 41 | 41 | 41 | 41 |  |  |  |  | 10 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  |  |  | 18 | 30 | 41 | 41 | 41 | 41 | 756912
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | 42 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 55 | 1130930
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1194741
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 110 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3129463
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0.7 | 1.9 | 1.8 | 2.3 | 2.4 | 1 | 2.2 | 2.4 | 0.4 | 1.2 | 0.5 | 0.1 | [8 empty] | 14750
103 | Kamalaghat 54 MW PP(Banco Energy) | 53 | 53 | 53 | 53 | 53 | 35 | 17 | 17 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | [5 empty] | 30 | 53 | 53 | 53 | 1057320
104 | Keranigonj 300 MW PP (APR) | [9 empty] | 34 | 34 | 36 |  |  | 58 |  |  |  |  | 227 | 209 | 56 | 38 | 39 | 33 | 56 | 606387
105 | Bramhangoan 100 MW PP (Aggreko) | [14 empty] | 50 |  |  |  |  | 96 | 100 | 70 | 25 | 25 |  |  | 260885
106 | Mymensingh 200 MW PP (United) | 177 | 177 | 180 | 181 | 185 | 189 | 194 | 194 | 200 | 145 | 143 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 193 | 193 | 193 | 200 | 200 | 200 | 4476000
112 | Aurahati 100MW PP (Aggreko) | [9 empty] | 14 | 26 | 26 |  |  | 52 |  |  |  |  | 102 | 102 | 57 | 26 | 26 | 25 | 0 | 370810
114 | Kodda 149 MW PP Unit-1 (Summit) | 131 | 131 | 131 | 131 | 131 | 131 | 131 | 131 | 131 | 117 | 115 | 116 | 115 | 115 | 124 | 106 | 112 | 100 |  | 128 | 130 | 131 | 131 | 131 | 132 | 132 | 3006720
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 |  | 90 | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2334720
116 | Chandpur 200MW (Desh energy) | [9 empty] | 2 | 45 | 50 | 50 | 60 | 109 | 135 | 32 | 32 |  | 80 | 120 | 200 | 150 | 150 | 150 | 150 | 1461120
117 | Ashuganj 150MW PP (Midland) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | [16 empty] | 0 | 97018
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 115 | 45 | 16 | 16 | 16 | 20 | 24 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 36 | 115 | 115 | 115 | 115 | 115 | 115 | 1473600
| Anwara 300 MW PP (United) | 269 | 269 | 269 | 269 | 269 | 269 | 269 | 269 | 285 | 289 | 305 | 307 | 305 | 305 | 305 | 305 | 305 | 252 |  | 305 | 305 | 305 | 305 | 307 | 306 | 306 | 6945164
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2425920
120 | Eastern Zone Total | 6751 | 6756 | 6671 | 6543 | 6379 | 5743.2 | 5724.7 | 5693.9 | 5933.2 | 6289.3 | 6475.6 | 6623.9 | 6600.4 | 6537 | 6821 | 6494.6 | 6297.9 | 5886.2 |  | 7217 | 7404 | 7184 | 7253 | 7277 | 7265 | 7263 | 157995269
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 115 | 115 | 108 | 115 | 115 | 115 | 21 | [5 empty] | 16 | 49 | 49 | 49 | 27 | 32 |  | 115 | 99 | 99 | 99 | 99 | 99 | 99 | 1494720
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 12 | [25 empty] | 19200
| Khulna 225 MW CCPP | 230 | 170 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 160 | 180 | 180 | 180 | 180 | 180 | 180 | 3481920
129 | Rupsha 105 MW PP (Orion rupsha) | 4 | [18 empty] | 25 | 53 | 53 | 53 | 53 | 53 | 53 | 308640
130
131
132
133
| Barisal 110 MW PP (Summit ) | [19 empty] | 64 | 64 | 64 | 64 | 64 | 64 | 32 | 344640
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 61 | 63 | 63 | 42 | 42 | 42 | 22 | 22 | 22 | 22 | 22 | 22 | 32 | 47 | 52 | 34 | 32 | 32 |  | 67 | 75 | 76 | 79 | 77 | 77 | 77 | 1136075
| Bhola 225 MW CCPP | 90 | 90 | 90 | 89 | 90 | 90 | 89 | 90 | 90 | 82 | 83 | 90 | 90 | 90 | 90 | 90 | 89 | 90 |  | 87 | 90 | 89 | 89 | 90 | 90 | 89 | 2157669
140 | Bhola 33 MW PP (Venture) | 22 | 25 | 24 | 20 | 20 | 12 | 11 | 10 | 6 | 6 | 12 | 14 | 13 | 13 | 16 | 16 | 16 | 17 |  | 27 | 29 | 30 | 30 | 30 | 31 | 30 | 437275
141 | Noapara 100 MW PP (Bangla Trac) | [19 empty] | 23 | 100 | 100 | 100 | 100 | 10 | 0 | 406080
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 40 | 8 | [13 empty] | 8 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 383250
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [22 empty] | 15 | 15 | 15 | 0 | 50112
146 | Bheramara HVDC | 935 | 936 | 934 | 935 | 935 | 936 | 935 | 936 | 935 | 935 | 935 | 932 | 933 | 933 | 933 | 934 | 933 | 932 |  | 932 | 932 | 932 | 932 | 931 | 931 | 932 | 22403636
147 | Bheramara 410 MW CCPP | 320 | 310 | 310 | 320 | 330 | 355 | 320 | 345 | 340 | 355 | 330 | 350 | 370 | 385 | 370 | 355 | 320 | 270 |  | 375 | 375 | 370 | 350 | 335 | 325 | 325 | 8349120
148 | Payra 1320 MW | 600 | 510 | 470 | 470 | 470 | 470 | 400 | 400 | 400 | 400 | 400 | 400 | 410 | 420 | 420 | 400 | 400 | 350 |  | 360 | 370 | 370 | 380 | 400 | 440 | 510 | 11191400
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 149 | 149 | 149 | 149 | 150 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 149 | 149 | 3652800
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 50 | 17 | [17 empty] | 50 | 50 | 50 | 43 | 50 | 50 | 50 | 354096
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 197 | 197 | 197 | 160 | 160 | 160 | 148 | 130 | 130 | 130 | 130 | 140 | 180 | 193 | 191 | 184 | 159 | 160 |  | 173 | 187 | 187 | 185 | 185 | 186 | 191 | 4344273
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 191 | 192 | 192 | 160 | 160 | 160 | 130 | 130 | 130 | 130 | 130 | 158 | 180 | 180 | 199 | 180 | 150 | 150 |  | 181 | 210 | 209 | 213 | 204 | 204 | 201 | 4592982
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 413 | 408 | 414 | 399 | 409 | 355 | 338 | 353 | 355 | 374 | 315 | 403 | 400 | 385 | 380 | 400 | 315 | 270 |  | 350 | 364 | 350 | 402 | 409 | 408 | 398 | 9108000
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 35 | [16 empty] | 9 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 246453
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 444240
163 | Bogura 20 MW PP (Energyprima) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 9 | 9 | 9 | 9 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 9 | 11 | 11 | 11 | 11 | 238572
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 216900
165 | Amnura 50 MW PP(Sinha) | [20 empty] | 0 |  |  |  |  | 0 | 0
166 | Katakhali 50 MW PP (Northern) | 25 | [18 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 77696
167 | Katakhali 50 MW Peaking PP | 44 | 44 | 44 | [16 empty] | 33 | 35 | 45 | 47 | 45 | 44 | 44 | 357500
168 | Santahar 50 MW Peaking PP | 32 | 32 | [17 empty] | 15 | 28 | 32 | 32 | 30 | 30 | 30 | 228740
169 | Natore 52 MW PP (Rajlanka) | 43 | 16 | [17 empty] | 28 | 43 | 43 | 43 | 43 | 43 | 43 | 294240
170 | Chapainawabganj 100 MW Peaking PP | 98 | 98 | 98 | 98 | 92 | [14 empty] | 87 | 98 | 100 | 100 | 100 | 100 | 100 | 1026504
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 94 | 94 | 94 | 94 | [15 empty] | 45 | 90 | 90 | 94 | 94 | 94 | 94 | 934656
172 | Confidence Power Bogura Unit-1 113 MW | 109 | 109 | 109 | 109 | 109 |  |  |  | 35 | 35 |  |  |  | 30 | 35 | 35 | 35 | 35 |  | 70 | 90 | 100 | 109 | 109 | 109 | 109 | 1413696
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 106 | 105 | 107 | 107 | 106 | 78 | [7 empty] | 8 | 34 | 35 | 38 | 39 |  | 74 |  | 35 | 66 | 109 | 113 | 107 | 1284480
177 | Sympa Solar Power 8MW | [5 empty] | 0.1 | 1.2 | 1.5 | 3.2 | 6.8 | 6.7 | 3.6 | 4.9 | 5.2 | 4.2 | 4.3 | 1.8 | 0.2 | [8 empty] | 45216
178
178