## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-09-02 | Wednesday
|  |  | Date (day): | 2020-09-02 |  | Wednesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13480.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14508 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-09-01 | 2020-09-02 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 28 | 28 | 28 | 28 |  | 57 | Unit-2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 102 | 100 | 150 | 150 | 30 |  | Gas shortage
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 110 | 110 | 110 | 110 | 80 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 73 | 72 | 90 | 90 | 18 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 340 | 341 | 412 | 412 |  |  | DCT
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 302 | 351 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 370 | 420 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 100 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 140 | 140 | 150 | 150 | 155 |  | GT-1 S/D for gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 96 | 96
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 12 | 18 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 100 | 100 | 110 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 93 | 93 | 85 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 53 | 53 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 149 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 0 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 55 | 55 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 16 | 51 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 281 | 268 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 112 | 111 | 133 | 133 |  | 16 | Engine problem
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 97 | 105 | 100 | 100
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 95 | 104 | 104 | 104
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 2745 | 2967 | 3781 | 4048 | 1070 | 768
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 8 | 25 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 10.83 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 18 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 80 | 79 | 80 | 80 | 150 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 | 225 |  | Under maint.
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 147 | 147 | 150 | 150
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 17 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 102 | 100 | 100
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 10 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 18 | 21 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 29 | 15 | 30
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 70 | 89 | 95 | 95 |  | 13 | Engine problem
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2.3 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 307 | 305 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 34 | 54 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 915.13 | 1125 | 1365 | 1415 | 735 | 111
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 179 | 187 | 225 | 225
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 275 | 260 | 360 | 360
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 255 | 265 | 360 | 360
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 33 | 35 | 35 | 36 | 9 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 50 | 50 | 5 |  | Gas shortage
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 36 | 36 | 8 | 8 | 187 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 38 | 51 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 85 | 122 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 42 | 0 | 42
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 95 | 92 | 100 | 100 |  | 63 | ST under shut down
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 105 | 200 | 200
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 19 | 21 | 21
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 10 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 136 | 170 | 157 | 173
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 43 | 43 | 43 |  | 9 | Engine problem
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 21 | 20 | 20 |  | 5 | Engine problem
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 114 | 114 | 114
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 113 | 113 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1353 | 1723 | 2051 | 2310 | 599 | 77
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 124 | 126 | 157 | 160 | 42 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 21 | 20 | 20
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 16 | 75 | 72 | 72 |  | 23 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0.1 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 120 | 194 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 95 | 115 | 115
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 277.1 | 511 | 565.6 | 567 | 42 | 23
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 90 | 91 | 90 | 90
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Unit-4 under shut down
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 195 | 192 | 210 | 210 |  | 120 | Engine problem
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 47 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 44 | 47 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 5 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 67 | 64 | 66 | 66
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 84 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 100 | 100 | 100 |  | 131 | Machine problem
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 18 | 18 | 18
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 25 | 25
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 285 | 310 | 341 | 341
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1101 | 1185 | 1245 | 1245 | 0 | 711
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 931 | 920 | 942 | 942
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 66 | 99 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 120 | 225 | 225
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 370 | 315 | 410 | 410
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 30 | 60 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 90 | 105 | 105
| 108 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1487 | 1614 | 1997 | 2143 | 0 | 0
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 64 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 17 | 32 | 33 | 33
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 65 | 65 | 65 | 65 |  | 129 | GT-2 & ST Under maint.
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 22 | 76 | 80 | 80 |  | 15 | Engine problem
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 400 | 540 | 400 | 530 |  |  | Unit-2 Test. Unit-1 under S/D
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 504 | 777 | 688 | 818 | 0 | 144
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 35 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 44 | 0 | 50
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 148 | 187 | 220 | 220 |  |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 150 | 209 | 220 | 220 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 353 | 420 | 414 | 414 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 33 | 0 | 32
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 22 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 11 | 11 | 11 | 11
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 8 | 43 | 43 | 43 |  | 9 | Engine problem
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 96 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 35 | 89 | 113 | 113
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 72 | 90 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 806 | 1340 | 1517 | 1689 | 431 | 9
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 149 | 113 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 71 | 98 | 113 | 113
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7.4 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 227.4 | 211 | 271 | 273 | 294 | 30
|  | Total |  |  |  |  | 20383 | 19892 | 9415.63 | 11453 | 13480.6 | 14508 | 3171 | 1873
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9007.8633 | 10957 | 12896.7899 | 13879.6958
| A. |  | 2020-09-01 | (Yesterday) |  |  |  |  | Tuesday
| 1 | Highest Generation : |  |  | 11877 | MW at | 1:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
| 2 | Minimum Generation : |  |  | 9026.89 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11453 | MW
| 3 | Day peak Generation : |  |  | 9415.63 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10957 | MW
| 4 | Evening peak Generation : |  |  | 11453 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 241.8786 | MKWHr | By Solar | 0.14035 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 126.5219 | MKWHr |  | By Oil: | 79.0272 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 8.4966 | MKWHr |  | By Hydro: | 1.9392 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3171 | MW | Dhaka | 3755 | 3755 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 1873 | MW | Chittagong | 1205 | 1205 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5044 | MW | Khulna | 1369 | 1369 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1055.61 | MMCFD |  |  | Rajshahi | 1112 | 1112 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 145732054.17 | ii) Oil : | Taka | 627334924.38 | Comilla | 1102 | 1102 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 40848218 | Total | Taka | 813915196.55 | Mymensingh | 874 | 874 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.149 | MKWHr. | Sylhet | 482 | 482 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 115 | MW (E to W) at | 19:30 | hrs | Barisal | 332 | 332 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -78 | MW at | 2:00 | hrs | Rangpur | 726 | 726 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 31° C |  |  | Total | 10957 | 10957 |  | 0
| B. |  | 2020-09-02 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 34° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14508 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10000 | MW
| 4 | Reserve(Generation end) |  |  |  | 2008 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 254.5662 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8452.6 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.2975 | MKWHr. | ii) HVDC Flow at Peak Time |  | 920 | MW at | 19:30 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.456 | MKWHr. | iii) Maximum HVDC Flow : |  | 934 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 93.18 |  | (b) Today: | 93.18 |  | (c) Rule Curve: |  | 99
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-09-01
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 28 | 0 | 100 | 110 | 0 | 72 | 0 | 339 | 352 |  | 0 | 450 | 132 | 100 | 80 | 55 | 0 | 0 | 0 | 0 | 100 | 93 | 149 | 26 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 89 | 0 | 0 | 0 | 25 | 0 | 0 | 148 | 0 |  | 0 | 0 | 68 | 0 | 90 | 50 | 21 | 40 | 0 | 0 | 0 | 260 | 255 | 213 | 8 | 87 | 33 | 5 | 0 | 51 | 0 | 33 | 43 | 20 | 11 | 33 | 20 | 144 | 157 | 72 | 20 | 0 | 91 | 30 | 53 | 47 | 163 | 204 | 64 | 85 | 0 | 80 | 0 | 0 | 10 | 280 | 24 | 5 | 70 | 300 | 33 | 0 | 192 | 0 | 130 | 0 | 100 | 200 | 83 | 0 | 115 | 105 | 34 | 0 | 307 | 54 | 17 | 114 | 113 | 100 | 0 | 104 |  | 934 | 0 | 310 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 60 | 28 | 48 | 0 | 0 | 0 | 50 | 0 | 96 | 0 | 50 | 44 | 43 | 29 | 21 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 190 | 0 | 72 | 100 | 202 | 0 | 370 | 105 | 30 | 95 | 0 | 98 | 0 | 0 | 90 | 440 |  | 7846 | 4031 | 11877 | 3269 | 934 | 2118 | 4065 | 589 | 89 | 669 | 144 | 0 | 0 | 93.18
2:00 | 28 | 0 | 100 | 110 | 0 | 72 | 0 | 339 | 352 |  | 0 | 450 | 127 | 100 | 80 | 55 | 0 | 0 | 0 | 0 | 100 | 93 | 149 | 26 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 |  | 0 | 0 | 34 | 0 | 90 | 50 | 21 | 40 | 0 | 0 | 0 | 260 | 255 | 173 | 8 | 87 | 33 | 5 | 0 | 51 | 0 | 33 | 43 | 20 | 11 | 33 | 20 | 142 | 158 | 72 | 20 | 0 | 91 | 30 | 53 | 47 | 163 | 206 | 64 | 85 | 0 | 80 | 0 | 0 | 10 | 275 | 24 | 5 | 0 | 300 | 0 | 0 | 192 | 0 | 131 | 0 | 100 | 200 | 83 | 0 | 115 | 105 | 34 | 0 | 307 | 54 | 17 | 114 | 108 | 100 | 0 | 104 |  | 933 | 0 | 315 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 60 | 28 | 48 | 0 | 0 | 0 | 50 | 0 | 88 | 0 | 0 | 44 | 43 | 29 | 21 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 188 | 0 | 76 | 100 | 202 | 0 | 320 | 105 | 0 | 76 | 0 | 79 | 0 | 0 | 90 | 450 |  | 7627 | 3872 | 11499 | 3233 | 933 | 2067 | 3810 | 600 | 87 | 627 | 142 | 0 | 0 | 93.18
3:00 | 28 | 0 | 100 | 110 | 0 | 72 | 0 | 338 | 352 |  | 0 | 400 | 133 | 100 | 80 | 55 | 0 | 0 | 0 | 0 | 100 | 93 | 149 | 0 | 0 | 0 | 0 | 53 | 55 | 17 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 |  | 0 | 0 | 34 | 0 | 84 | 50 | 20 | 40 | 0 | 0 | 0 | 260 | 255 | 173 | 8 | 95 | 33 | 5 | 0 | 51 | 0 | 33 | 43 | 20 | 11 | 33 | 20 | 140 | 157 | 71 | 20 | 0 | 91 | 30 | 53 | 47 | 163 | 205 | 64 | 85 | 0 | 80 | 0 | 0 | 10 | 270 | 24 | 5 | 0 | 300 | 0 | 0 | 192 | 0 | 131 | 0 | 100 | 150 | 83 | 0 | 115 | 105 | 34 | 0 | 307 | 54 | 17 | 114 | 113 | 100 | 0 | 104 |  | 934 | 0 | 340 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 60 | 27 | 48 | 0 | 0 | 0 | 50 | 0 | 88 | 0 | 0 | 44 | 43 | 29 | 21 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 187 | 0 | 77 | 0 | 202 | 0 | 362 | 105 | 0 | 76 | 0 | 71 | 0 | 0 | 90 | 450 |  | 7464 | 3831 | 11295 | 3263 | 934 | 2054 | 3592 | 600 | 85 | 627 | 140 | 0 | 0 | 93.18
4:00 | 28 | 0 | 100 | 110 | 0 | 72 | 0 | 338 | 353 |  | 0 | 400 | 140 | 100 | 80 | 15 | 0 | 0 | 0 | 0 | 100 | 85 | 98 | 0 | 0 | 0 | 0 | 53 | 55 | 17 | 22 | 25 | 30 | 33 | 33 | 25 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 87 | 50 | 20 | 40 | 0 | 0 | 0 | 275 | 270 | 184 | 8 | 97 | 33 | 5 | 0 | 51 | 0 | 0 | 43 | 20 | 11 | 33 | 20 | 138 | 157 | 71 | 20 | 0 | 91 | 30 | 53 | 47 | 130 | 208 | 64 | 85 | 0 | 79 | 0 | 0 | 10 | 285 | 24 | 5 | 0 | 300 | 0 | 0 | 192 | 0 | 131 | 0 | 100 | 0 | 83 | 0 | 75 | 105 | 17 | 0 | 307 | 34 | 0 | 88 | 113 | 100 | 0 | 104 |  | 933 | 0 | 340 | 0 | 99 | 200 | 0 | 0 | 0 | 0 | 40 | 60 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 0 | 44 | 43 | 29 | 21 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 185 | 0 | 78 | 0 | 204 | 0 | 368 | 105 | 0 | 57 | 0 | 71 | 0 | 0 | 72 | 430 |  | 7034 | 3708 | 10742 | 3302 | 933 | 2042 | 3205 | 579 | 84 | 459 | 138 | 0 | 0 | 93.18
5:00 | 28 | 0 | 100 | 110 | 0 | 72 | 0 | 350 | 353 |  | 0 | 400 | 140 | 100 | 80 | 15 | 0 | 0 | 0 | 0 | 100 | 85 | 64 | 0 | 0 | 0 | 0 | 53 | 55 | 17 | 22 | 25 | 30 | 33 | 33 | 25 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 |  | 0 | 0 | 0 | 0 | 90 | 50 | 20 | 40 | 0 | 0 | 0 | 275 | 270 | 186 | 8 | 97 | 33 | 5 | 0 | 51 | 0 | 0 | 43 | 20 | 11 | 33 | 20 | 134 | 157 | 71 | 20 | 0 | 91 | 30 | 53 | 47 | 130 | 204 | 64 | 83 | 0 | 80 | 0 | 0 | 10 | 300 | 24 | 2 | 0 | 300 | 0 | 0 | 192 | 0 | 131 | 0 | 100 | 0 | 83 | 0 | 75 | 105 | 17 | 0 | 307 | 34 | 0 | 52 | 113 | 100 | 0 | 104 |  | 934 | 0 | 345 | 0 | 99 | 185 | 0 | 0 | 0 | 0 | 40 | 60 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 0 | 44 | 43 | 28 | 21 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 188 | 0 | 77 | 0 | 204 | 0 | 370 | 105 | 0 | 57 | 0 | 70 | 0 | 0 | 72 | 430 |  | 6986 | 3701 | 10687 | 3320 | 934 | 2056 | 3171 | 579 | 84 | 409 | 134 | 0 | 0 | 93.18
6:00 | 28 | 0 | 100 | 110 | 0 | 72 | 0 | 340 | 353 |  | 0 | 400 | 130 | 100 | 80 | 15 | 0 | 0 | 0 | 0 | 100 | 93 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 17 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 |  | 0 | 0 | 0 | 0 | 90 | 40 | 20 | 40 | 0 | 0 | 0 | 260 | 255 | 181 | 8 | 96 | 33 | 5 | 0 | 51 | 0 | 0 | 8 | 20 | 11 | 33 | 20 | 116 | 158 | 71 | 20 | 0 | 91 | 30 | 53 | 47 | 130 | 205 | 63 | 83 | 0 | 80 | 0 | 0 | 10 | 280 | 24 | 2 | 0 | 300 | 0 | 0 | 192 | 0 | 128 | 0.5 | 100 | 0 | 83 | 0 | 24 | 105 | 0 | 0.1 | 307 | 34 | 0 | 0 | 109 | 100 | 0 | 104 |  | 933 | 0 | 355 | 0 | 99 | 125 | 0 | 0 | 0 | 0 | 0 | 60 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 186 | 0 | 78 | 0 | 210 | 0 | 347 | 53 | 0 | 37 | 0 | 71 | 0 | 0 | 54 | 430 |  | 6644.6 | 3354 | 9998.6 | 3291 | 933 | 2012 | 2768 | 579 | 86 | 213 | 116 | 0.6 | 0 | 93.18
7:00 | 28 | 0 | 100 | 110 | 0 | 72 | 0 | 344 | 300 |  | 0 | 370 | 145 | 100 | 60 | 15 | 0 | 0 | 0 | 0 | 92 | 93 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 17 | 0 | 25 | 30 | 33 | 33 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 0 |  | 0 | 0 | 0 | 0 | 50 | 0 | 20 | 34 | 0 | 0 | 0 | 290 | 280 | 195 | 8 | 96 | 33 | 5 | 0 | 51 | 0 | 0 | 0 | 20 | 11 | 33 | 15 | 108 | 157 | 48 | 20 | 0.1 | 91 | 30 | 50 | 47 | 130 | 211 | 63 | 83 | 0 | 79 | 0 | 0 | 10 | 295 | 24 | 2 | 0 | 288 | 0 | 0 | 200 | 0 | 112 | 2.1 | 100 | 0 | 10 | 0 | 0 | 17 | 0 | 0.9 | 217 | 0 | 0 | 0 | 108 | 100 | 0 | 104 |  | 933 | 0 | 365 | 0 | 74 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 166 | 0 | 79 | 0 | 150 | 0 | 347 | 0 | 0 | 0 | 0 | 71 | 0 | 0.2 | 72 | 410 |  | 6115.1 | 3104.2 | 9219.3 | 3266 | 933 | 1933 | 2179 | 559 | 86 | 152 | 108 | 3.3 | 0 | 93.18
8:00 | 28 | 0 | 100 | 110 | 0 | 72 | 0 | 351 | 300 |  | 0 | 370 | 125 | 100 | 0 | 15 | 0 | 0 | 0 | 0 | 92 | 93 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 40 | 0 | 25 | 30 | 33 | 33 | 0 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 39 | 0 | 20 | 8 | 0 | 0 | 0 | 260 | 255 | 176 | 8 | 90 | 33 | 5 | 0 | 51 | 0 | 0 | 0 | 20 | 11 | 33 | 15 | 110 | 159 | 8 | 17 | 0.1 | 91 | 30 | 50 | 47 | 130 | 202 | 64 | 83 | 0 | 80 | 0 | 0 | 10 | 305 | 24 | 2 | 0 | 300 | 0 | 0 | 200 | 0 | 112 | 4.59 | 100 | 0 | 18 | 0 | 0 | 29 | 0 | 1.8 | 283 | 0 | 0 | 0 | 110 | 100 | 0 | 104 |  | 933 | 0 | 375 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 158 | 0 | 29 | 0 | 150 | 0 | 350 | 0 | 0 | 0 | 0 | 71 | 0 | 0.4 | 72 | 400 |  | 6001.49 | 3025.4 | 9026.89 | 3188 | 933 | 1870 | 2130 | 549 | 88 | 152 | 110 | 6.89 | 0 | 93.18
9:00 | 28 | 0 | 100 | 110 | 0 | 73 | 0 | 340 | 302 |  | 0 | 370 | 140 | 100 | 0 | 48 | 0 | 0 | 0 | 0 | 100 | 93 | 0 | 9 | 0 | 0 | 0 | 53 | 0 | 55 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 70 | 1 | 20 | 4 | 0 | 0 | 0 | 275 | 255 | 188 | 8 | 0 | 35 | 5 | 0 | 51 | 0 | 0 | 0 | 17 | 8 | 33 | 15 | 112 | 158 | 8 | 17 | 0.1 | 91 | 30 | 50 | 47 | 130 | 203 | 64 | 83 | 0 | 80 | 0 | 0 | 10 | 280 | 24 | 2 | 0 | 295 | 0 | 0 | 200 | 0 | 112 | 7.69 | 100 | 0 | 85 | 0 | 0 | 87 | 0 | 2.6 | 306 | 0 | 0 | 0 | 108 | 100 | 0 | 91 |  | 933 | 0 | 375 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 11 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 149 | 0 | 22 | 0 | 130 | 0 | 353 | 0 | 0 | 0 | 0 | 71 | 0 | 1.2 | 72 | 400 |  | 6164.39 | 2993.2 | 9157.59 | 3103 | 933 | 1838 | 2370 | 548 | 90 | 152 | 112 | 11.59 | 0 | 93.18
10:00 | 28 | 0 | 100 | 110 | 0 | 73 | 0 | 342 | 302 |  | 0 | 370 | 135 | 100 | 0 | 55 | 0 | 0 | 0 | 0 | 100 | 93 | 16 | 12 | 0 | 0 | 0 | 53 | 0 | 55 | 19 | 25 | 30 | 33 | 33 | 10 | 0 | 45 | 35 | 0 | 0 | 5 | 0 | 0 | 147 | 0 |  | 0 | 0 | 0 | 0 | 70 | 16 | 20 | 3 | 0 | 0 | 0 | 275 | 250 | 188 | 36 | 20 | 33 | 5 | 0 | 51 | 0 | 0 | 3 | 17 | 8 | 33 | 0 | 126 | 158 | 12 | 17 | 0.1 | 91 | 30 | 47 | 47 | 130 | 201 | 64 | 85 | 0 | 80 | 0 | 0 | 10 | 290 | 16 | 2 | 0 | 286 | 0 | 0 | 160 | 0 | 112 | 9.5 | 100 | 0 | 85 | 0 | 0 | 87 | 0 | 2.9 | 306 | 30 | 0 | 17 | 113 | 100 | 0 | 90 |  | 933 | 0 | 370 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 8 | 0 | 18 | 11 | 11 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 152 | 0 | 22 | 0 | 150 | 0 | 342 | 0 | 0 | 12 | 0 | 71 | 0 | 4.2 | 72 | 400 |  | 6258.5 | 2991.2 | 9249.7 | 3113 | 933 | 1857 | 2434 | 548 | 80 | 142 | 126 | 16.7 | 0 | 93.18
11:00 | 28 | 0 | 100 | 110 | 0 | 73 | 0 | 345 | 302 |  | 0 | 370 | 140 | 100 | 0 | 55 | 0 | 0 | 0 | 0 | 100 | 93 | 16 | 12 | 0 | 0 | 0 | 53 | 17 | 55 | 19 | 25 | 30 | 33 | 33 | 16 | 0 | 45 | 35 | 0 | 0 | 8 | 0 | 0 | 147 | 0 |  | 0 | 0 | 0 | 0 | 70 | 18 | 17 | 2 | 0 | 0 | 0 | 275 | 250 | 178 | 36 | 90 | 35 | 5 | 0 | 14 | 0 | 0 | 8 | 17 | 8 | 33 | 20 | 132 | 142 | 16 | 17 | 0.1 | 90 | 30 | 47 | 44 | 130 | 200 | 67 | 85 | 0 | 80 | 0 | 0 | 10 | 285 | 16 | 2 | 0 | 272 | 0 | 0 | 120 | 0 | 112 | 7.89 | 100 | 0 | 26 | 0 | 0 | 87 | 0 | 2.3 | 307 | 34 | 0 | 17 | 113 | 100 | 0 | 89 |  | 930 | 0 | 375 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 152 | 0 | 22 | 0 | 150 | 0 | 349 | 0 | 0 | 35 | 0 | 71 | 0 | 3.5 | 72 | 400 |  | 6216.29 | 3021.5 | 9237.79 | 3190 | 930 | 1817 | 2390 | 549 | 80 | 136 | 132 | 13.79 | 0 | 93.18
12:00 | 28 | 0 | 102 | 110 | 0 | 73 | 0 | 340 | 302 |  | 0 | 370 | 140 | 100 | 0 | 55 | 0 | 0 | 0 | 0 | 100 | 93 | 16 | 12 | 0 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 16 | 0 | 45 | 35 | 0 | 0 | 8 | 0 | 0 | 147 | 0 |  | 0 | 0 | 17 | 0 | 70 | 18 | 17 | 4 | 0 | 0 | 0 | 275 | 255 | 179 | 36 | 95 | 33 | 5 | 0 | 38 | 0 | 0 | 8 | 17 | 8 | 33 | 20 | 136 | 124 | 16 | 17 | 0.1 | 90 | 30 | 47 | 44 | 130 | 195 | 67 | 85 | 0 | 100 | 0 | 0 | 10 | 285 | 16 | 2 | 0 | 281 | 0 | 0 | 120 | 0 | 112 | 10.83 | 100 | 0 | 85 | 0 | 0 | 97 | 0 | 2.3 | 307 | 34 | 0 | 17 | 113 | 100 | 0 | 95 |  | 931 | 0 | 370 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 148 | 0 | 22 | 0 | 150 | 0 | 353 | 0 | 0 | 35 | 0 | 71 | 0 | 7.4 | 72 | 400 |  | 6391.23 | 3024.4 | 9415.63 | 3184 | 931 | 1850 | 2512 | 549 | 80 | 153 | 136 | 20.63 | 0 | 93.18
13:00 | 28 | 0 | 90 | 110 | 0 | 73 | 0 | 341 | 350 |  | 0 | 420 | 120 | 100 | 0 | 55 | 0 | 0 | 0 | 0 | 100 | 86 | 0 | 12 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 45 | 35 | 0 | 0 | 0 | 0 | 0 | 150 | 0 |  | 0 | 0 | 17 | 0 | 72 | 26 | 17 | 14 | 0 | 0 | 0 | 310 | 265 | 176 | 36 | 85 | 33 | 5 | 0 | 51 | 0 | 0 | 8 | 17 | 8 | 33 | 20 | 140 | 125 | 16 | 17 | 0 | 90 | 30 | 47 | 47 | 163 | 192 | 64 | 85 | 0 | 100 | 0 | 0 | 10 | 275 | 24 | 2 | 0 | 260 | 0 | 0 | 120 | 0 | 112 | 4 | 100 | 0 | 95 | 0 | 0 | 105 | 0 | 1 | 307 | 47 | 0 | 0 | 113 | 100 | 0 | 104 |  | 931 | 0 | 370 | 0 | 82 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 11 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 181 | 0 | 22 | 0 | 180 | 0 | 375 | 0 | 0 | 35 | 0 | 70 | 0 | 6.8 | 72 | 360 |  | 6509 | 3077.8 | 9586.8 | 3277 | 931 | 2022 | 2480 | 508 | 80 | 137 | 140 | 11.8 | 0 | 93.18
14:00 | 28 | 0 | 102 | 110 | 0 | 73 | 0 | 339 | 302 |  | 0 | 380 | 130 | 100 | 0 | 55 | 0 | 0 | 0 | 0 | 100 | 93 | 0 | 12 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 42 | 35 | 0 | 0 | 0 | 0 | 0 | 147 | 0 |  | 0 | 0 | 17 | 0 | 77 | 40 | 17 | 16 | 0 | 0 | 0 | 260 | 265 | 179 | 36 | 95 | 35 | 5 | 0 | 51 | 0 | 0 | 0 | 17 | 8 | 33 | 20 | 152 | 122 | 16 | 17 | 0 | 90 | 30 | 47 | 43 | 130 | 200 | 64 | 85 | 0 | 100 | 18 | 0 | 10 | 265 | 24 | 2 | 0 | 253 | 0 | 0 | 120 | 0 | 111 | 9.9 | 100 | 0 | 105 | 0 | 0 | 17 | 0 | 3.3 | 307 | 17 | 0 | 0 | 109 | 100 | 0 | 104 |  | 930 | 0 | 350 | 0 | 85 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 149 | 0 | 23 | 0 | 130 | 0 | 346 | 0 | 0 | 0 | 0 | 70 | 0 | 4.8 | 72 | 410 |  | 6296.2 | 2954.8 | 9251 | 3159 | 930 | 1863 | 2356 | 559 | 77 | 137 | 152 | 18 | 0 | 93.18
15:00 | 28 | 0 | 100 | 110 | 0 | 72 | 0 | 352 | 352 |  | 0 | 450 | 140 | 100 | 0 | 55 | 0 | 0 | 0 | 0 | 100 | 93 | 0 | 12 | 0 | 0 | 0 | 53 | 55 | 35 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 42 | 35 | 0 | 0 | 0 | 0 | 0 | 146 | 0 |  | 0 | 0 | 17 | 0 | 51 | 25 | 17 | 3 | 0 | 0 | 0 | 260 | 265 | 186 | 36 | 96 | 33 | 5 | 0 | 51 | 0 | 0 | 0 | 17 | 8 | 33 | 20 | 154 | 122 | 16 | 19 | 0.1 | 90 | 30 | 47 | 43 | 163 | 203 | 63 | 84 | 0 | 100 | 18 | 0 | 10 | 300 | 24 | 2 | 0 | 258 | 0 | 0 | 120 | 0 | 80 | 6.3 | 100 | 0 | 113 | 0 | 0 | 17 | 0 | 4.5 | 253 | 17 | 0 | 0 | 113 | 100 | 0 | 104 |  | 930 | 0 | 335 | 0 | 74 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 163 | 0 | 22 | 0 | 182 | 0 | 416 | 0 | 0 | 0 | 0 | 39 | 0 | 3.2 | 72 | 490 |  | 6369.9 | 3114.2 | 9484.1 | 3230 | 930 | 2108 | 2195 | 639 | 77 | 137 | 154 | 14.1 | 0 | 93.18
16:00 | 28 | 0 | 100 | 110 | 0 | 72 | 0 | 344 | 351 |  | 0 | 450 | 135 | 100 | 0 | 55 | 0 | 0 | 0 | 0 | 100 | 93 | 0 | 12 | 0 | 0 | 0 | 53 | 55 | 35 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 42 | 35 | 0 | 0 | 0 | 0 | 0 | 146 | 0 |  | 0 | 0 | 17 | 0 | 51 | 25 | 17 | 6 | 0 | 0 | 0 | 260 | 265 | 181 | 36 | 92 | 35 | 5 | 0 | 51 | 0 | 0 | 0 | 17 | 10 | 33 | 21 | 148 | 122 | 16 | 19 | 0.1 | 90 | 30 | 50 | 43 | 163 | 196 | 63 | 85 | 0 | 100 | 18 | 0 | 10 | 295 | 24 | 2 | 0 | 270 | 0 | 0 | 120 | 0 | 64 | 10.3 | 100 | 0 | 117 | 0 | 0 | 17 | 0 | 0.1 | 252 | 17 | 0 | 0 | 113 | 100 | 0 | 104 |  | 930 | 0 | 325 | 0 | 66 | 120 | 0 | 0 | 0 | 3 | 0 | 65 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 156 | 0 | 22 | 0 | 216 | 0 | 405 | 0 | 0 | 0 | 0 | 34 | 0 | 1.2 | 72 | 500 |  | 6338.5 | 3116.2 | 9454.7 | 3227 | 930 | 2096 | 2176 | 649 | 77 | 140 | 148 | 11.7 | 0 | 93.18
17:00 | 28 | 0 | 100 | 110 | 0 | 72 | 0 | 340 | 303 |  | 0 | 400 | 140 | 100 | 0 | 55 | 0 | 0 | 0 | 0 | 100 | 93 | 0 | 29 | 0 | 0 | 0 | 53 | 55 | 35 | 0 | 25 | 28 | 33 | 33 | 0 | 0 | 42 | 35 | 0 | 0 | 0 | 0 | 0 | 147 | 0 |  | 0 | 0 | 17 | 0 | 50 | 25 | 18 | 13 | 0 | 0 | 0 | 260 | 265 | 182 | 36 | 90 | 35 | 5 | 0 | 51 | 0 | 0 | 0 | 17 | 10 | 33 | 21 | 132 | 127 | 16 | 19 | 0.1 | 91 | 30 | 50 | 43 | 110 | 198 | 63 | 85 | 0 | 100 | 18 | 0 | 10 | 290 | 24 | 2 | 0 | 268 | 0 | 0 | 120 | 0 | 94 | 2.2 | 100 | 0 | 117 | 0 | 0 | 32 | 0 | 0 | 199 | 17 | 0 | 0 | 107 | 100 | 0 | 104 |  | 931 | 0 | 320 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 147 | 0 | 22 | 0 | 150 | 0 | 357 | 0 | 0 | 0 | 0 | 35 | 0 | 0.8 | 90 | 500 |  | 6152.3 | 3002.8 | 9155.1 | 3137 | 931 | 1898 | 2200 | 640 | 77 | 137 | 132 | 3.1 | 0 | 93.18
18:00 | 28 | 0 | 100 | 110 | 0 | 72 | 0 | 341 | 272 |  | 0 | 320 | 140 | 100 | 0 | 55 | 0 | 0 | 0 | 0 | 100 | 93 | 48 | 100 | 0 | 0 | 0 | 53 | 55 | 35 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 42 | 35 | 0 | 0 | 0 | 0 | 0 | 100 | 0 |  | 0 | 0 | 34 | 0 | 50 | 25 | 18 | 12 | 0 | 0 | 0 | 260 | 270 | 190 | 36 | 95 | 33 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 10 | 33 | 21 | 134 | 125 | 16 | 19 | 0 | 91 | 30 | 47 | 47 | 110 | 204 | 63 | 20 | 0 | 100 | 18 | 0 | 10 | 280 | 24 | 2 | 0 | 268 | 0 | 0 | 134 | 0 | 112 | 0.1 | 100 | 0 | 118 | 0 | 0 | 34 | 0 | 0 | 197 | 17 | 0 | 0 | 110 | 100 | 0 | 104 |  | 930 | 0 | 265 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 22 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 9 | 0 | 0 | 108 | 0 | 0 | 0 | 0 | 148 | 0 | 67 | 0 | 130 | 0 | 352 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 90 | 500 |  | 6137.1 | 2944 | 9081.1 | 3063 | 930 | 1756 | 2306 | 608 | 77 | 207 | 134 | 0.1 | 0 | 93.18
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 28 | 0 | 100 | 110 | 0 | 72 | 0 | 370 | 350 |  | 0 | 420 | 150 | 100 | 0 | 55 | 0 | 0 | 0 | 0 | 97 | 93 | 149 | 16 | 0 | 0 | 0 | 53 | 0 | 55 | 22 | 25 | 31 | 33 | 33 | 37 | 0 | 42 | 35 | 0 | 0 | 21 | 0 | 0 | 145 | 0 |  | 0 | 0 | 102 | 20 | 86 | 44 | 18 | 26 | 0 | 0 | 0 | 295 | 300 | 203 | 36 | 95 | 35 | 5 | 0 | 51 | 0 | 42 | 25 | 19 | 10 | 33 | 21 | 166 | 126 | 45 | 19 | 0 | 91 | 30 | 47 | 47 | 130 | 210 | 63 | 85 | 0 | 100 | 18 | 0 | 10 | 310 | 24 | 5 | 0 | 268 | 0 | 0 | 192 | 0 | 111 | 0 | 100 | 22 | 122 | 0 | 72 | 85 | 9 | 0 | 270 | 46 | 0 | 114 | 113 | 100 | 0 | 104 |  | 920 | 0 | 340 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 65 | 30 | 62 | 0 | 0 | 0 | 50 | 16 | 56 | 0 | 0 | 35 | 35 | 22 | 22 | 11 | 11 | 0 | 0 | 112 | 0 | 0 | 0 | 0 | 178 | 0 | 76 | 21 | 175 | 0 | 412 | 53 | 0 | 21 | 0 | 74 | 0 | 0 | 90 | 500 |  | 7362 | 3662 | 11024 | 3381 | 920 | 2140 | 3136 | 612 | 77 | 592 | 166 | 0 | 0 | 93.18
19:30 | 28 | 0 | 100 | 110 | 0 | 72 | 0 | 341 | 351 |  | 0 | 420 | 140 | 100 | 0 | 55 | 0 | 0 | 0 | 0 | 100 | 93 | 149 | 18 | 0 | 0 | 0 | 53 | 0 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 44 | 35 | 0 | 0 | 25 | 0 | 0 | 147 | 0 |  | 0 | 0 | 102 | 10 | 89 | 50 | 18 | 29 | 0 | 0 | 0 | 260 | 265 | 187 | 36 | 92 | 35 | 5 | 0 | 51 | 0 | 42 | 43 | 19 | 10 | 33 | 21 | 170 | 126 | 75 | 21 | 0 | 91 | 30 | 47 | 47 | 163 | 192 | 64 | 84 | 0 | 100 | 18 | 0 | 10 | 310 | 24 | 5 | 0 | 268 | 0 | 0 | 194 | 0 | 111 | 0 | 100 | 105 | 122 | 0 | 95 | 105 | 17 | 0 | 305 | 54 | 0 | 114 | 113 | 100 | 0 | 104 |  | 920 | 0 | 315 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 40 | 65 | 32 | 64 | 0 | 0 | 0 | 50 | 35 | 96 | 0 | 0 | 44 | 43 | 33 | 22 | 11 | 11 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 187 | 0 | 76 | 30 | 209 | 0 | 420 | 90 | 0 | 89 | 0 | 98 | 0 | 0 | 90 | 540 |  | 7511 | 3942 | 11453 | 3267 | 920 | 2186 | 3507 | 653 | 79 | 671 | 170 | 0 | 0 | 0
20:00 | 28 | 0 | 100 | 110 | 0 | 72 | 0 | 349 | 353 |  | 0 | 420 | 140 | 100 | 2 | 55 | 0 | 0 | 0 | 0 | 95 | 93 | 149 | 20 | 0 | 0 | 0 | 53 | 0 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 44 | 35 | 0 | 0 | 25 | 0 | 0 | 147 | 0 |  | 0 | 0 | 102 | 0 | 90 | 45 | 18 | 29 | 0 | 0 | 0 | 260 | 265 | 181 | 36 | 90 | 35 | 5 | 0 | 51 | 0 | 42 | 43 | 19 | 10 | 33 | 21 | 170 | 126 | 74 | 20 | 0 | 91 | 30 | 50 | 47 | 130 | 194 | 64 | 87 | 0 | 100 | 18 | 0 | 10 | 300 | 24 | 7 | 0 | 270 | 0 | 0 | 193 | 0 | 112 | 0 | 100 | 151 | 122 | 0 | 95 | 105 | 17 | 0 | 307 | 54 | 0 | 114 | 113 | 100 | 0 | 104 |  | 920 | 0 | 315 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 40 | 65 | 33 | 64 | 0 | 0 | 0 | 50 | 35 | 98 | 0 | 0 | 47 | 43 | 32 | 22 | 11 | 11 | 0 | 0 | 112 | 0 | 0 | 0 | 0 | 174 | 0 | 77 | 30 | 185 | 0 | 423 | 105 | 0 | 90 | 0 | 99 | 0 | 0 | 90 | 540 |  | 7513 | 3930 | 11443 | 3233 | 920 | 2156 | 3558 | 652 | 79 | 675 | 170 | 0 | 0 | 93.18
21:00 | 28 | 0 | 100 | 110 | 0 | 72 | 0 | 341 | 355 |  | 0 | 390 | 144 | 100 | 48 | 55 | 0 | 0 | 0 | 0 | 90 | 93 | 149 | 26 | 0 | 0 | 0 | 53 | 33 | 55 | 0 | 25 | 30 | 33 | 33 | 51 | 0 | 45 | 35 | 0 | 0 | 25 | 0 | 0 | 149 | 0 |  | 0 | 0 | 102 | 0 | 90 | 32 | 18 | 35 | 0 | 0 | 0 | 265 | 270 | 213 | 36 | 95 | 35 | 5 | 0 | 51 | 0 | 42 | 43 | 20 | 10 | 33 | 21 | 170 | 125 | 73 | 22 | 0 | 91 | 30 | 47 | 47 | 130 | 203 | 67 | 87 | 0 | 100 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 268 | 0 | 0 | 194 | 0 | 112 | 0 | 100 | 101 | 122 | 0 | 65 | 105 | 0 | 0 | 307 | 54 | 0 | 114 | 113 | 100 | 0 | 104 |  | 920 | 0 | 300 | 0 | 99 | 150 | 0 | 0 | 0 | 0 | 40 | 65 | 31 | 64 | 0 | 0 | 0 | 50 | 35 | 98 | 0 | 0 | 44 | 43 | 32 | 22 | 11 | 11 | 0 | 0 | 107 | 0 | 0 | 0 | 0 | 150 | 0 | 79 | 30 | 180 | 0 | 423 | 105 | 0 | 113 | 0 | 98 | 0 | 0 | 90 | 570 |  | 7485 | 3960 | 11445 | 3223 | 920 | 2121 | 3552 | 677 | 80 | 702 | 170 | 0 | 0 | 93.18
22:00 | 28 | 0 | 100 | 110 | 0 | 72 | 0 | 340 | 355 |  | 0 | 350 | 140 | 100 | 64 | 55 | 0 | 0 | 0 | 0 | 90 | 93 | 149 | 25 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 45 | 35 | 0 | 0 | 25 | 0 | 0 | 148 | 0 |  | 0 | 0 | 102 | 0 | 90 | 32 | 18 | 37 | 0 | 0 | 0 | 260 | 265 | 214 | 36 | 88 | 35 | 5 | 0 | 51 | 0 | 33 | 43 | 20 | 10 | 33 | 21 | 168 | 125 | 73 | 22 | 0 | 90 | 30 | 47 | 47 | 110 | 193 | 67 | 87 | 0 | 100 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 268 | 0 | 0 | 200 | 0 | 128 | 0 | 100 | 0 | 122 | 0 | 35 | 105 | 0 | 0 | 307 | 54 | 0 | 114 | 113 | 100 | 0 | 104 |  | 919 | 0 | 300 | 0 | 99 | 150 | 0 | 0 | 0 | 0 | 40 | 65 | 35 | 64 | 0 | 0 | 0 | 50 | 35 | 98 | 0 | 0 | 43 | 43 | 32 | 22 | 11 | 11 | 0 | 0 | 101 | 0 | 0 | 0 | 0 | 149 | 0 | 78 | 0 | 150 | 0 | 407 | 105 | 0 | 113 | 0 | 95 | 0 | 0 | 90 | 570 |  | 7333 | 3875 | 11208 | 3185 | 919 | 2050 | 3443 | 671 | 80 | 692 | 168 | 0 | 0 | 93.18
23:00 | 28 | 0 | 100 | 110 | 0 | 72 | 0 | 347 | 354 |  | 0 | 350 | 140 | 100 | 64 | 55 | 0 | 0 | 0 | 0 | 95 | 93 | 98 | 26 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 8 | 0 | 45 | 35 | 0 | 0 | 8 | 0 | 0 | 148 | 0 |  | 0 | 0 | 68 | 0 | 90 | 32 | 18 | 40 | 0 | 0 | 0 | 305 | 310 | 206 | 36 | 94 | 35 | 5 | 0 | 51 | 0 | 0 | 43 | 20 | 10 | 33 | 21 | 168 | 123 | 73 | 22 | 0 | 90 | 30 | 47 | 47 | 110 | 208 | 40 | 87 | 0 | 100 | 18 | 0 | 10 | 285 | 24 | 8 | 0 | 268 | 0 | 0 | 200 | 0 | 132 | 0 | 100 | 0 | 123 | 0 | 35 | 105 | 0 | 0 | 307 | 54 | 0 | 70 | 113 | 100 | 0 | 104 |  | 920 | 0 | 310 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 40 | 65 | 35 | 64 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 43 | 8 | 0 | 22 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 150 | 0 | 77 | 0 | 150 | 0 | 412 | 21 | 0 | 113 | 0 | 102 | 0 | 0 | 90 | 520 |  | 7200 | 3629 | 10829 | 3277 | 920 | 2051 | 3238 | 670 | 80 | 425 | 168 | 0 | 0 | 93.18
24:00 | 28 | 0 | 100 | 110 | 0 | 72 | 0 | 377 | 352 |  | 0 | 420 | 146 | 100 | 64 | 55 | 0 | 0 | 0 | 0 | 100 | 93 | 98 | 26 | 0 | 0 | 0 | 53 | 0 | 55 | 22 | 25 | 30 | 33 | 33 | 8 | 0 | 45 | 35 | 0 | 0 | 8 | 0 | 0 | 149 | 0 |  | 0 | 0 | 68 | 0 | 90 | 32 | 18 | 31 | 0 | 0 | 0 | 270 | 265 | 179 | 8 | 97 | 35 | 5 | 0 | 51 | 0 | 0 | 43 | 20 | 10 | 33 | 21 | 164 | 125 | 73 | 22 | 0 | 90 | 30 | 47 | 47 | 163 | 193 | 40 | 87 | 0 | 100 | 18 | 0 | 10 | 310 | 24 | 8 | 0 | 268 | 0 | 0 | 200 | 0 | 131 | 0 | 100 | 0 | 118 | 0 | 35 | 105 | 0 | 0 | 307 | 54 | 0 | 70 | 113 | 100 | 0 | 104 |  | 921 | 0 | 310 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 40 | 65 | 33 | 64 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 0 | 43 | 8 | 0 | 21 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 173 | 0 | 79 | 0 | 175 | 0 | 420 | 17 | 0 | 113 | 0 | 106 | 0 | 0 | 90 | 449 |  | 7169 | 3606 | 10775 | 3239 | 921 | 2167 | 3188 | 598 | 80 | 418 | 164 | 0 | 0 | 93.18
KWH | 570000 | 0 | 2398000 | 2677500 | 0 | 1716636 | 0 | 8400890 | 7939000 |  | 0 | 9124750 | 3357498 | 2451840 | 808396 | 1150776 | 0 | 0 | 0 | 0 | 2373120 | 2203920 | 1561440 | 447193 | 0 | 0 | 0 | 1313280 | 944057 | 1072940 | 385236 | 600000 | 687780 | 816800 | 798300 | 510552 | 0 | 1415198 | 524000 | 0 | 0 | 188020 | 0 | 0 | 3469144 | 0 |  | 0 | 0 | 868026 | 71160 | 1816320 | 744000 | 438864 | 587040 | 0 | 0 | 0 | 6848200 | 6437000 | 4594000 | 602181 | 2024200 | 780624 | 137760 | 0 | 1200453 | 0 | 282936 | 530054 | 436572 | 232920 | 818400 | 483210 | 3456000 | 3254160 | 1093440 | 433080 | 550 | 2134000 | 719280 | 1188600 | 1106280 | 3567927 | 4780000 | 1511904 | 1986240 | 0 | 2166030 | 179000 | 0 | 246600 | 7157800 | 536832 | 97392 | 97536 | 6746943 | 37902 | 0 | 4104000 | 0 | 2783520 | 85320 | 2441280 | 1033920 | 2274909 | 0 | 986400 | 1940856 | 204071 | 23761 | 6919320 | 874443 | 71090 | 1225500 | 2693880 | 2436480 | 0 | 2543040 |  | 22297454 | 0 | 8148672 | 0 | 2090880 | 3471360 | 0 | 0 | 0 | 768 | 450375 | 1513000 | 605440 | 655680 | 0 | 0 | 0 | 412488 | 124952 | 1165040 | 0 | 72018 | 448400 | 464160 | 292362 | 490320 | 254700 | 212220 | 0 | 0 | 3444800 | 0 | 0 | 0 | 0 | 4190055 | 0 | 1287950 | 334080 | 4655855 | 0 | 8893054 | 1052640 | 0 | 1143456 | 0 | 1753920 | 0 | 30715 | 1890528 | 5051800 |  | 164979472 | 76899142 | 241878614 | 78429120 | 22297454 | 48092731 | 70399393 | 8496600 | 1939198 | 8627772 | 3456000 | 140346 | 0
Fuel Cost | 934800 | 0 | 3501080 | 3935925 | 0 | 2265959.52 | 0 | 8484898.9 | 8177170 |  | 0 | 9945977.5 | 3726822.78 | 18609465.6 | 5569848.44 | 9735564.96 | 0 | 0 | 0 | 0 | 17869593.6 | 20099750.4 | 15364569.6 | 4123119.46 | 0 | 0 | 0 | 9586944 | 7297560.61 | 10579188.4 | 288927 | 450000 | 0 | 0 | 0 | 4937037.84 | 0 | 382103.46 | 141480 | 0 | 0 | 1746705.8 | 0 | 0 | 5897544.8 | 0 |  | 0 | 0 | 8419852.2 | 679578 | 15801984 | 5892480 | 552968.64 | 1743508.8 | 0 | 0 | 0 | 5067668 | 6437000 | 4226480 | 776813.49 | 2327830 | 882105.12 | 192864 | 0 | 2052774.63 | 0 | 2857653.6 | 5062015.7 | 554446.44 | 174690 | 1432200 | 362407.5 | 25920000 | 3449409.6 | 9928435.2 | 550011.6 | 8767 | 3499760 | 1150848 | 2115708 | 1725796.8 | 4067436.78 | 4971200 | 2978450.88 | 3793718.4 | 0 | 3747231.9 | 392010 | 0 | 503064 | 7229378 | 402624 | 74017.92 | 1659087.36 | 51006889.08 | 643575.96 | 0 | 21340800 | 0 | 27389836.8 | 997390.8 | 19896432 | 11218032 | 16038108.45 | 0 | 8995968 | 18341089.2 | 1777458.41 | 0 | 52310059.2 | 7616398.53 | 624881.1 | 12230490 | 23086551.6 | 16226956.8 | 0 | 0 |  | 128433335.04 | 0 | 8556105.6 | 0 | 16434316.8 | 48113049.6 | 0 | 0 | 0 | 8048.64 | 4692907.5 | 1709690 | 938432 | 6399436.8 | 0 | 0 | 0 | 4058881.92 | 1269512.32 | 10310604 | 0 | 973683.36 | 4344996 | 4497710.4 | 2835911.4 | 941414.4 | 394785 | 160650.54 | 0 | 0 | 18670816 | 0 | 0 | 0 | 0 | 5530872.6 | 0 | 1931925 | 5682700.8 | 5447350.35 | 0 | 8804123.46 | 10989561.6 | 0 | 10851397.44 | 0 | 13610419.2 | 0 | 339400.75 | 13971001.92 | 22177402 |  | 607057231.16 | 363080442.44 | 970137673.6 | 88131204.39 | 128433335.04 | 57600849.78 | 529751845.1 | 40848218 | 523583.46 | 97583079.28 | 25920000 | 1345558.55 | 0
Yesterday Day Peak | 28 | 0 | 102 | 110 | 0 | 73 | 0 | 340 | 302 |  | 0 | 370 | 140 | 100 | 0 | 55 | 0 | 0 | 0 | 0 | 100 | 93 | 16 | 12 | 0 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 16 | 0 | 45 | 35 | 0 | 0 | 8 | 0 | 0 | 147 | 0 |  | 0 | 0 | 17 | 0 | 70 | 18 | 17 | 4 | 0 | 0 | 0 | 275 | 255 | 179 | 36 | 95 | 33 | 5 | 0 | 38 | 0 | 0 | 8 | 17 | 8 | 33 | 20 | 136 | 124 | 16 | 17 | 0.1 | 90 | 30 | 47 | 44 | 130 | 195 | 67 | 85 | 0 | 100 | 0 | 0 | 10 | 285 | 16 | 2 | 0 | 281 | 0 | 0 | 120 | 0 | 112 | 10.83 | 100 | 0 | 85 | 0 | 0 | 97 | 0 | 2.3 | 307 | 34 | 0 | 17 | 113 | 100 | 0 | 95 |  | 931 | 0 | 370 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 148 | 0 | 22 | 0 | 150 | 0 | 353 | 0 | 0 | 35 | 0 | 71 | 0 | 7.4 | 72 | 400 |  | 9415.63 | DayPeak
Yesterday Evening Peak | 28 | 0 | 100 | 110 | 0 | 72 | 0 | 341 | 351 | 0 | 0 | 420 | 140 | 100 | 0 | 55 | 0 | 0 | 0 | 0 | 100 | 93 | 149 | 18 | 0 | 0 | 0 | 53 | 0 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 44 | 35 | 0 | 0 | 25 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 102 | 10 | 89 | 50 | 18 | 29 | 0 | 0 | 0 | 260 | 265 | 187 | 36 | 92 | 35 | 5 | 0 | 51 | 0 | 42 | 43 | 19 | 10 | 33 | 21 | 170 | 126 | 75 | 21 | 0 | 91 | 30 | 47 | 47 | 163 | 192 | 64 | 84 | 0 | 100 | 18 | 0 | 10 | 310 | 24 | 5 | 0 | 268 | 0 | 0 | 194 | 0 | 111 | 0 | 100 | 105 | 122 | 0 | 95 | 105 | 17 | 0 | 305 | 54 | 0 | 114 | 113 | 100 | 0 | 104 |  | 920 | 0 | 315 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 40 | 65 | 32 | 64 | 0 | 0 | 0 | 50 | 35 | 96 | 0 | 0 | 44 | 43 | 33 | 22 | 11 | 11 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 187 | 0 | 76 | 30 | 209 | 0 | 420 | 90 | 0 | 89 | 0 | 98 | 0 | 0 | 90 | 540 |  | 11453 | EvPeak
Forecast for Evening | 28 | 0 | 150 | 110 | 0 | 90 | 0 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 96 | 55 | 0 | 0 | 100 | 0 | 100 | 102 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 45 | 35 | 0 | 0 | 25 | 0 | 0 | 150 | 0 | 0 | 0 |  | 100 | 100 | 95 | 50 | 21 | 30 | 0 | 0 | 0 | 360 | 360 | 225 | 8 | 100 | 36 | 50 | 0 | 51 | 0 | 42 | 43 | 21 | 11 | 33 | 20 | 173 | 160 | 72 | 20 | 0 | 90 | 30 | 51 | 44 | 163 | 210 | 66 | 86 | 0 | 100 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 133 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 104 |  | 942 | 16 | 410 | 0 | 115 | 225 | 0 | 0 | 30 | 60 | 40 | 65 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 0 | 50 | 50 | 43 | 32 | 22 | 11 | 11 | 0 | 0 | 150 | 0 | 10 | 0 | 0 | 220 | 0 | 80 | 100 | 220 | 0 | 414 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 530
Forecast for Day | 28 | 0 | 150 | 110 | 0 | 90 | 0 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 96 | 55 | 0 | 0 | 100 | 0 | 100 | 85 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 45 | 35 | 0 | 0 | 25 | 0 | 0 | 150 | 0 | 0 | 0 |  | 100 | 100 | 95 | 50 | 21 | 15 | 0 | 0 | 0 | 360 | 360 | 225 | 8 | 100 | 35 | 50 | 0 | 51 | 0 | 0 | 43 | 21 | 11 | 33 | 20 | 157 | 157 | 72 | 20 | 1.6 | 90 | 30 | 51 | 44 | 163 | 210 | 66 | 86 | 0 | 100 | 18 | 0 | 10 | 341 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 100 | 133 | 20 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 5 | 300 | 54 | 50 | 114 | 113 | 100 | 0 | 104 |  | 942 | 0 | 410 | 0 | 115 | 225 | 0 | 0 | 0 | 0 | 40 | 65 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 50 | 0 | 43 | 0 | 22 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 |  | 80 | 60 | 220 | 0 | 414 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 400
Generation at 08:00(Today) | 28 | 0 | 100 | 110 | 0 | 73 | 0 | 346 | 284 | 0 | 0 | 370 | 150 |  | 30 | 15 | 0 | 0 | 0 | 0 | 30 | 32 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 30 | 15 | 33 | 0 | 0 | 43 | 35 | 0 | 0 | 4 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 18 | 8 | 0 | 0 | 0 | 285 | 285 | 209 | 8 | 95 | 32 | 5 | 0 | 51 | 0 | 0 | 8 | 20 | 8 | 33 | 20 | 118 | 156 | 8 | 22 | 0.9 | 90 | 30 | 47 | 47 | 163 | 210 | 40 | 87 | 0 | 100 | 18 | 0 | 10 | 300 | 24 | 5 | 0 | 45 | 0 | 0 | 150 | 0 | 95 | 6 | 100 | 0 | 0 | 0 | 0 | 7 | 0 | 3.3 | 307 | 34 | 0 | 0 | 105 | 100 | 0 | 50 | 0 | 933 | 0 | 345 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 153 | 0 | 52 | 0 | 180 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8 | 35 | 400 | 0
199
| Minimum Generation |  | 9026.89 | 8:00
| Highest Generation |  | 11877 | 1:00
| Day Peak Generation |  | 9415.63 | 12:00
| Evening Peak Generation |  | 11453 | 19:30
| HVDC Max Flow |  | 934 | 1:00
| HVDC EvPeak Flow |  | 920 | 19:30
| Load factor L.F |  | 84.86%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-09-02
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-09-01 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9415.63 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 8452.6 | MW
Evening Peak Generation : |  | 11453 | MW Hour : | 19:30 | Available Max Generation : |  | 14508 | MW
E.P. Demand (at gen end) : |  | 11453 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 12500 | MW
Maximum Generation : |  | 11877 | MW Hour : | 1:00 | Reserve(Generation end) |  | 2008 | MW
Total Gen. (MKWH) : |  | 241.8786 | System Load Factor : | 84.86% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -78 | MW at | 2:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-09-02
Actual : | 93.18 | Ft.(MSL) , | Rule curve : | 99 | Ft.( MSL )
Gas Consumed : | Total = | 1055.61 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 145732054.17
: |  | Coal : | 40848218 | Oil : | 627334924.38 | Total : | 813915196.55
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4445.7384 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1515.4062 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1358.3968 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1227.6544 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1109.2876 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 895.1649 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 495.8879 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 230.358 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 690.4179 |  |  | 0 | 0%
Total | 0 |  | 11968.312 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 10) Sikalbaha 225 MW
|  |  |  | 2) Bibiyana #3 | 11) Payra Unit-1
3) Ghorasal Unit-2,3,7
4) Ashuganj unit-3,5
5) Bhola-225 MW GT-2 & ST
6) Kaptai-1,2,5
7) Raozan #1,2
8) Sirajganj #1
9) Baghabari-71 & 100 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Faridpur-Gopalganj 132 kV Ckt-1 was under shut down from 08:11 to 10:21 to attend R/H of CB at
Faridpur.
b) Ashuganj-Sirajganj 230 kV Ckt-1 tripped at 10:16 from both ends showing Dist. Z1, RST
phases, A/R block and was switched on at 10:54.
c) Khulna(C)-Goalpara 132 kV Ckt-1 was under shut down from 08:08 to 09:08 for C/M.
d) Khulna(C)-Khulna 225 MW 132 kV Ckt-2 was under shut down from 09:24 to 11:34 for C/M.
e) Jamalpur 132/33 kV T2 transformer was under shut down from 09:08 to 15:55 for C/M.
f) Mymensingh-Jamalpur 132 kV Ckt-1 tripped at 12:05 from both ends showing Dist. Z2 at
Mymensingh end & Dist. Z1 at Jamalpur end and was switched on at 12:15.
g) Aminbazar-Savar 132 kV both Ckts was shut down at 09:30 due to 2 No Tower breakdown maintenance
work by Aminbazar.
h) Payra completed 50%(311 MW) rejection test of unit-2 at 12:18.
i) Payra unit-2 was synchronized at 12:30.
j) Chandpur 150 MW CCPP GT was synchronized at 09:59.
k) Bibiyana-Bibiyana(South) 230 kV Ckt was shut down at 11:56 by Bibiyana South for maintenance.
l) Payra unit-2 conducted AGC test at 14:30.
m) Aminbazar-Savar 132 kV Ckt-2 via Manikganj P.P charged at 18:49 and tripped at 18:50 by AR block
and broken conductor trip at Aminbazar end. Again tried at 19:28 and tripped at 19:42 from Aminbazar
end showing the same relay.
n) Manikganj 55 MW(Northern) was shut down at 18:59 for Savar grid operation and was synchronized at
20:40.
o) Aminbazar-Savar 132 kV Ckt-2 again closed at 21:39.
p) Aminbazar-Savar 132 kV Ckt-2 CB closed at 22:37 from Savar end.
q) Payra unit-1 was shut down at 23:36 for unit-2 test.
r) Hathazari 132 kV main Bus-2 was under shut down from 02:06(02/09/2020) to 08:53(02/09/2020) for C/M.
s) Ghorashal 230/132 kV AT02 was shut down at 07:22(02/09/2020) for C/M.
t) Rangpur 33 kV Bus section-2&3 was under shut down from 06:35(02/09/2020) to 07:42(02/09/2020) |  |  |  |  | About 70 MW power interruption occurred under Rangpur S/S area
for C/M. |  |  |  |  | from 06:35(02/09/2020) to 07:42(02/09/2020).
u) Kulaura 132/33 kV T1 transformer was under shut down from 07:15(02/09/2020) to 08:38(02/09/2020) |  |  |  |  | About 15 MW power interruption occurred under Kulaura S/S area
for C/M. |  |  |  |  | from 07:15(02/09/2020) to 07:48(02/09/2020).
v) Kulaura 132/33 kV T2 transformer was under shut down from 07:15(02/09/2020) to 07:48(02/09/2020)
for C/M.
w) Joydebpur 132/33 kV T3 transformer was under shut down from 05:51(02/09/2020) to 06:18(02/09/2020) |  |  |  |  | About 30 MW power interruption occurred under Joydebpur S/S area
for C/M. |  |  |  |  | from 05:51(02/09/2020) to 06:18(02/09/2020).
x) Chapainawabganj 132/33 kV T4 transformer tripped at 12:24(02/09/2020) from both sides showing O/C,
B-phase due to 33 kV feeder fault.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-09-01 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 28 | 570000 | Unit-1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 100 | 2398000 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 110 | 2677500 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 72 | 1716636 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 341 | 8400890 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 351 | 7939000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9124750 | Frequency control.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 2451840
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 140 | 3357498 | GT-1 Under S/D.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 808396 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1150776
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 18 | 447193 | Low demand
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 385236
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 2373120
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 2203920 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Machine problem
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 1313280
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 1561440
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 944057
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1072940
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1287780 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 816800
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 798300
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 510552
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 268 | 6746943 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 37902 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 111 | 2783520 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 1940856
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2543040
| Dhaka area Total |  |  |  | 5895 | 2967 | 68362165
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 188020
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 85320
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 744000
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 79 | 1939198 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 147 | 3469144
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 17 | 204071 | Low demand
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 868026
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 71160 | Low demand
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2441280
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 438864
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 29 | 587040
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 89 | 1816320 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 23761
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 305 | 6919320
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 874443
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 71090 | Reserve
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2436480
| Chattogram area Total |  |  |  | 2266 | 1125 | 23177537
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 187 | 4594000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 260 | 6848200 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 265 | 6437000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 35 | 780624 | Gas shortage.
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 137760 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 36 | 602181 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1200453
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 122 | 2274909 | Engine problem
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 42 | 282936 | Engine problem
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 92 | 2024200
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 105 | 1033920 | Low demand
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 436572
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 232920
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 170 | 3456000
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 818400
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 530054 | Engine problem
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 483210
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 97536 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1225500
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 2693880
| Cumilla Area Total |  |  |  | 2980 | 1723 | 36190255
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 126 | 3254160 | Engine problem
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 433080
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 75 | 1093440 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 550
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 194 | 4104000 | Low demand
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 95 | 986400 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 511 | 9871630
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 91 | 2134000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 719280 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3567927
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 192 | 4780000 | ST under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 47 | 1188600
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 47 | 1106280
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 97392
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 64 | 1511904 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1986240
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2166030 | Engine problem
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 179000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 536832
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7157800 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 246600
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1185 | 27377885
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 920 | 22297454
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 2090880 | Engine problem
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 120 | 3471360 | Low demand
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 768
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 315 | 8148672 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 450375
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 30 | 334080 | Low demand
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 90 | 1052640 | Low demand
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Reserve
| Khulna Area Total |  |  |  | 2284 | 1614 | 37846229
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 64 | 655680
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 32 | 605440
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 65 | 1513000 | GT-2 Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 76 | 1287950 | Engine problem
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 540 | 5051800
| Barisal Area Total |  |  |  | 1054 | 777 | 9113870
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 412488
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 35 | 124952
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 72018 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 44 | 448400 | Engine problem
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage.
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 187 | 4190055 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 209 | 4655855 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 420 | 8893054 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 33 | 292362
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 490320
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 11 | 254700
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 212220
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 464160 | Engine problem
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 96 | 1165040
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 89 | 1143456 | Low demand
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 90 | 1890528 | Engine problem
| Rajshahi Area Total |  |  |  | 2183 | 1340 | 24709608
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 113 | 3444800 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Machine problem
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 98 | 1753920 | Engine problem
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 30715
| Rangpur Area Total |  |  |  | 605 | 211 | 5229435
| Total |  |  |  | 19892 | 11453 | 241878614
| Eastern Grid Total |  |  |  | 13766 | 7511 | 164979472
| Western Grid Total |  |  |  | 6126 | 3942 | 76899142
| National Grid Total |  |  |  | 19892 | 11453 | 241878614
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-09-01
| (a) ENTIRE EASTERN GRID : |  | 7418 | MW | (b) ENTIRE WESTERN GRID : |  | 3539 | MW
| i) Dhaka area |  | 3755 | MW | i) Khulna area |  | 1369 | MW
| ii) Chittagong area |  | 1205 | MW | ii) Rajshahi area |  | 1112 | MW
| iii) Comilla area |  | 1102 | MW | iii) Barisal area |  | 332 | MW
| iv) Mymensingh area |  | 874 | MW | iv) Rangpur area |  | 726 | MW
| v) Sylhet area |  | 482 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 10957 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 118 | 5:00 | Sherpur | 86 | 1:00 | Jhenida | 108 | 1:00
| Munsiganj | 122 | 1:00 | Srimongal | 46 | 18:30 | Bottail | 125 | 1:00
| Sonargaon | 80 | 2:00 | Shahjibazar | 116 | 21:00 | G.K Project | 55 | 1:00
| Shyampur | 200 | 1:00 | Fenchuganj | 43 | 22:00 | Faridpur | 185 | 0.041667
| Bhulta | 203 | 1:00 | Kulawara | 47 | 20:00 | Madaripur | 91 | 0.91667
| Madanganj | 52 | 2:00 | Sylhet | 123 | 19:30 | Sariatpur | 60 | 21:00
| Shitalakhya | 99 | 13:00 | Chatak | 28 | 20:00 | Gopalganj | 83 | 19:30
| Rahim steel | 25 | 17:00 | Sunamganj | 44 | 21:30 | Bagerhat | 98 | 20:00
| Matuail | 78 | 10:00 | Biani Bazar | 58 | 21:00 | Mongla | 50 | 1:00
| Ghorasal | 74 | 23:00 | Comilla (S) | 170 | 19:30 | Satkhira | 105 | 0.041667
| Narsingdi | 167 | 21:00 | Comilla(N) | 101 | 20:00 | Gallamari | 48 | 13:00
| Haripur (SBU) | 94 | 17:00 | Chandpur | 103 | 22:00 | Magura | 52 | 0.041667
| Ullon | 52 | 19:00 | Feni | 125 | 20:00 | Norail | 38 | 1:00
| Hasnabad | 190 | 21:00 | Chowmuhani | 176 | 19:00 | Chuadanga | 93 | 1:00
| Magbazar | 100 | 13:00 | Ashuganj | 57 | 22:00 | Barisal(N) | 41 | 0.875
| Maniknagar | 98 | 13:00 | Daudkandi | 133 | 21:00 | Barisal (S) | 100 | 0.8125
| Bangabhaban | 37 | 10:00 | B.Baria | 145 | 21:00 | Patuakhali | 114 | 0.91667
| Narinda | 98 | 14:00 | Ramganj | 110 | 21:00 | Bhandaria | 54 | 0.875
| Dhanmondi | 166 | 13:00 | Chaddagram | 29 | 19:00 | Borhan Uddin | 39 | 1:00
| Lalbag | 90 | 13:00 | PHP | 2 | 7:00 | Ishurdi | 58 | 1:00
| Madartek | 68 | 1:00 | Madunaghat | 61 | 15:00 | Ruppur Paromanobik | 2 | 3:00
| Dhaka University |  |  | Hathazari | 103 | 0.8125 | Natore | 124 | 1:00
| Fatullah | 38 | 0.41667 | Khulshi | 202 | 0.77083 | Bogra | 169 | 1:00
| Mirpur | 101 | 12:00 | Halishahar | 132 | 0.45833 | Noagaon | 130 | 1:00
| Kalyanpur | 111 | 12:00 | Baraulia | 157 | 0 | Rajshahi | 153 | 1:00
| Gulshan | 132 | 13:00 | Sikalbaha | 27 | 0.79167 | Rajshahi New | 10 | 19:30
| Uttara | 79 | 12:00 | Dohazari | 84 | 0.875 | C.Nawabganj | 67 | 3:00
| Uttara New | 30 | 12:00 | Cox'sbazar | 98 | 0.8125 | Amnura | 50 | 2:00
| Kamrangirchar | 87 | 13:00 | Chandraghona | 28 | 0.041667 | Pabna | 115 | 1:00
| Savar | 107 | 1:00 | Kaptai | 4.5 | 0.79167 | Shahjadpur | 90 | 1:00
| Bhasantec | 151 | 13:00 | A. Khaer Stl. | 17 | 0.083333 | Serajganj | 88 | 21:00
| Agargaon | 70 | 13:00 | Bakulia | 101 | 0.77083 | Niyamatpur | 57 | 1:00
| Satmosjid | 80 | 14:00 | Julda | 20 | 0.041667 | Joypurhat | 52 | 1:00
| Tongi | 126 | 0.41667 | TK chemical | 28 | 0.041667 | Sherpur(Bogura) | 48 | 1:00
| Kabirpur | 256 | 9:00 | Modern Steel | 16 | 0.45833 | Mohastangor | 48 | 1:00
| Basundhara | 136 | 12:00 | Shahmirpur | 25 | 0.95833 | Rangpur | 150 | 1:00
| Manikganj | 68 | 0.875 | Khagrachhari | 24 | 0.79167 | Lalmonirhat | 53 | 2:00
| Joydevpur | 127 | 10:00 | Matarbari | 31 | 0.8125 | Saidpur | 106 | 19:30
| New Tongi | 98 | 9:00 | Baroiar Hat | 38 | 0.79167 | Purbasadipur | 100 | 19:30
| Korda | 228 | 19:30 | Rangamati | 12 | 0.83333 | Thakurgaon | 82 | 19:30
| Dhamrai | 96 | 12:00 | Abul Khair 230 | 108 | 0.20833 | Palashbari | 124 | 1:00
| Rajendrapur | 92 | 21:00 | BSRM | 109 | 0.125 | Barapukuria | 48 | 19:30
| Valuka | 108 | 19:30 | GPH Ispat | 88 | 0.125 | Panchagar | 50 | 21:00
| Tangail | 185 | 1:00 | Goalpara | 29 | 0.041667 | Joldhaka | 26 | 2:00
| Mymensing | 216 | 1:00 | Central s/s | 84 | 19:00 | Kurigram | 57 | 19:00
| Kishorganj | 135 | 23:00 | Noapara | 61 | 1:00
| Netrokona | 103 | 20:00 | Jessore | 98 | 1:00
| Jamalpur | 136 | 1:00 | Benapol | 46 | 1:00
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-09-01 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 397 | 2:00 | 387 | 16:00 | Kaliakoir | 383 | 0.25 | 369 | 0.625
| Bheramara | 392 | 7:00 | 385 | 1:00 | Bhulta | 393 | 0.20833 | 380 | 0.625
| Ashuganj(N) | 398 | 5:00 | 384 | 15:00 | Gopalganj | 419 | 0.54167 | 404 | 0.83333
| Payra | 419 | 5:00 | 408 | 19:30
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 1:00 | 232 | 14:00 | Comilla (N) | 236 | 1:00 | 229 | 15:00
| Ishurdi | 237 | 24:00 | 230 | 1:00 | Hathazari | 231 | 19:30 | 214 | 15:00
| Ashuganj | 240 | 4:00 | 232 | 14:00 | Megnaghat | 232 | 1:00 | 224 | 13:00
| Serajganj | 234 | 13:00 | 230 | 1:00 | Fenchuganj | 238 | 1:00 | 235 | 12:00
| Baghabari | 242 | 23:00 | 238 | 1:00 | Siddhirganj | 233 | 5:00 | 223 | 16:00
| Barapukuria | 236 | 8:00 | 228 | 1:00 | Maniknagar | 231 | 5:00 | 221 | 16:00
| Bogra | 227 | 11:00 | 216 | 1:00 | Agargaon | 230 | 6:00 | 219 | 16:00
| Rajshahi | 225 | 22:00 | 218 | 2:00 | Barisal | 247 | 7:00 | 235 | 22:00
| Khulna South | 237 | 13:00 | 230 | 7:00 | AKSML | 227 | 19:00 | 213 | 15:00
| Rampura | 229 | 4:00 | 222 | 11:00 | BSRM | 229 | 2:00 | 214 | 15:00
| Haripur | 230 | 3:00 | 223 | 10:00 | Bibiyana | 238 | 2:00 | 231 | 12:00
| Hasnabad | 230 | 1:00 | 222 | 11:00 | Bhulta | 233 | 19:00 | 223 | 17:00
| Shyampur | 228 | 2:00 | 219 | 15:00 | Ashuganj (S) | 238 | 4:00 | 228 | 12:00
| Aminbazar | 230 | 24:00 | 221 | 16:00 | Kaliakoir | 235 | 6:00 | 224 | 17:00
| Tongi | 228 | 1:00 | 215 | 15:00 | GPH | 226 | 6:00 | 217 | 15:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 134 | 4:00 | 129 | 12:00 | Hathazari | 138 | 0.25 | 130 | 0.625
| Munsiganj | 135 | 5:00 | 129 | 19:00 | Khulshi | 137 | 0.8125 | 128 | 0.625
| Sonargaon | 134 | 5:00 | 130 | 19:00 | Halishahar | 141 | 0.125 | 130 | 0.625
| Shyampur | 136 | 4:00 | 130 | 15:00 | Baraulia | 139 | 0.041667 | 127 | 0.58333
| Bhulta | 126 | 5:00 | 122 | 16:00 | Sikalbaha | 141 | 2:00 | 130 | 0.58333
| Madanganj | 131 | 12:00 | 127 | 15:00 | Dohazari | 137 | 19:00 | 127 | 0.625
| Shitalakhya | 143 | 2:00 | 130 | 15:00 | Cox'sbazar | 127 | 0.79167 | 121 | 0.625
| Rahim steal | 134 | 4:00 | 129 | 15:00 | Chandraghona | 137 | 0.041667 | 130 | 0.58333
| Matuail | 134 | 4:00 | 129 | 12:00 | Kaptai | 136 | 19:00 | 130 | 0.20833
| Ghorasal | 140 | 1:00 | 136 | 14:00 | A. Khaer Stl. | 135 | 0.125 | 128 | 15:00
| Narsinghdi | 129 | 6:00 | 125 | 1:00 | Bakulia | 139 | 0.8125 | 130 | 0.625
| Haripur (SBU) | 133 | 7:00 | 131 | 1:00 | Julda | 139 | 0.041667 | 131 | 0.625
| Ullon | 134 | 4:00 | 126 | 16:00 | TK Chemical | 140 | 0.041667 | 131 | 15:00
| Hasnabad | 139 | 1:00 | 128 | 14:00 | Modern Steel | 137 | 0.041667 | 129 | 0.625
| Magbazar | 137 | 17:00 | 125 | 12:00 | Shahmirpur | 139 | 0.083333 | 131 | 0.625
| Maniknagar | 135 | 4:00 | 127 | 15:00 | Khagrachhari | 136 | 0.79167 | 128 | 0.625
| Bangabhaban | 135 | 4:00 | 127 | 15:00 | Matarbari | 130 | 0.083333 | 124 | 0.625
| Narinda | 135 | 4:00 | 127 | 15:00 | Baroiar Hat | 137 | 0.83333 | 126 | 0.625
| Dhanmondi | 134 | 4:00 | 126 | 16:00 | Rangamati | 137 | 0.8125 | 130 | 15:00
| Lalbag | 138 | 2:00 | 126 | 16:00 | Goalpara S/S | 138 | 14:00 | 134 | 23:00
| Madartek | 134 | 4:00 | 125 | 12:00 | Khulna Central S/S | 135 | 0.083333 | 130 | 2:00
| Dhaka University |  |  |  |  | Noapara | 136 | 14:00 | 132 | 1:00
| Fatuiiah | 134 | 0.083333 | 129 | 16:00 | Jessore | 132 | 8:00 | 124 | 1:00
| Mirpur | 133 | 6:00 | 127 | 12:00 | Benapol | 135 | 9:00 | 125 | 2:00
| Kalyanpur | 132 | 6:00 | 128 | 12:00 | Jhenida | 131 | 0.58333 | 119 | 1:00
| Gulshan | 134 | 6:00 | 125 | 12:00 | Bottail | 135 | 13:00 | 128 | 1:00
| Uttara | 133 | 6:00 | 128 | 12:00 | G.K Project | 141 | 0.66667 | 137 | 1:00
| Uttara New | 136 | 5:00 | 127 | 15:00 | Faridpur | 135 | 13:00 | 127 | 1:00
| Kamrangirchar | 137 | 2:00 | 126 | 15:00 | Madaripur | 140 | 0.29167 | 131 | 20:00
| Savar | 133 | 6:00 | 129 | 9:00 | Shariyatpur S/S | 138 | 0.29167 | 130 | 1:00
| Bhasantec | 134 | 6:00 | 127 | 15:00 | Gopalganj | 140 | 8:00 | 128 | 20:00
| Agargaon | 135 | 6:00 | 128 | 12:00 | Bagerhat | 130 | 23:00 | 135 | 11:00
| Satmosjid | 134 | 6:00 | 128 | 12:00 | Mongla | 131 | 0.91667 | 125 | 6:00
| Tongi | 137 | 0.875 | 130 | 15:00 | Satkhira | 135 | 0.33333 | 131 | 19:00
| Kabirpur | 137 | 6:00 | 129 | 19:00 | Gallamari | 137 | 2:00 | 134 | 23:00
| Basundhara | 134 | 5:00 | 125 | 12:00 | Magura | 130 | 8:00 | 116 | 1:00
| Manikganj | 142 | 3:00 | 130 | 15:00 | Norail | 129 | 0.54167 | 112 | 1:00
| Joydevpur | 142 | 21:00 | 137 | 15:00 | Chuadanga | 127 | 14:00 | 109 | 1:00
| New Tongi | 137 | 0.875 | 129 | 15:00 | Barisal(N) | 140 | 5:00 | 133 | 22:00
| Kodda | 137 | 1:00 | 120 | 0.66667 | Barisal (S) | 139 | 0.29167 | 131 | 20:00
| Dhamrai | 136 | 6:00 | 130 | 16:00 | Patuakhali(S) | 138 | 0.58333 | 124 | 22:00
| Rajendrapur | 137 | 2:00 | 121 | 15:00 | Bhandaria | 131 | 14:00 | 124 | 23:00
| Valuka | 129 | 10:00 | 119 | 1:00 | Ishurdi | 139 | 13:00 | 135 | 1:00
| Tangail | 138 | 8:00 | 130 | 1:00 | Ruppur Paromanobik | 138 | 14:00 | 134 | 2:00
| Mymensing | 134 | 8:00 | 122 | 1:00 | Natore | 137 | 13:00 | 132 | 2:00
| Kishorganj | 133 | 10:00 | 123 | 1:00 | Bogra | 138 | 11:00 | 128 | 2:00
| Netrokona | 133 | 8:00 | 118 | 1:00 | Noagaon | 133 | 13:00 | 121 | 1:00
| Jamalpur | 139 | 20:00 | 132 | 18:00 | Rajshahi | 135 | 17:00 | 132 | 12:00
| Sherpur | 138 | 4:00 | 132 | 17:00 | Rajshahi New | 138 | 22:00 | 133 | 3:00
| Srimongal | 138 | 5:00 | 134 | 0.041667 | C.Nawabganj | 135 | 17:00 | 129 | 12:00
| Shahjibazar | 137 | 8:00 | 131 | 0.041667 | Amnura | 136 | 19:00 | 129 | 12:00
| Fenchuganj | 136 | 7:00 | 133 | 0.041667 | Pabna | 137 | 13:00 | 131 | 2:00
| Khulawara | 135 | 7:00 | 132 | 0.041667 | Shahjadpur | 140 | 18:00 | 135 | 2:00
| Sylhet | 133 | 13:00 | 128 | 0.041667 | Serajganj | 135 | 13:00 | 129 | 2:00
| Chatak | 131 | 8:00 | 126 | 1:00 | Niyamatpur | 131 | 11:00 | 117 | 1:00
| Sunamganj | 130 | 8:00 | 124 | 0.041667 | Joypurhat | 134 | 11:00 | 119 | 1:00
| Biani Bazar | 131 | 10:00 | 127 | 0.041667 | Sherpur(Bogura) | 137 | 13:00 | 129 | 2:00
| Comilla(s) | 128 | 7:00 | 120 | 14:00 | Mohastangor | 137 | 11:00 | 124 | 2:00
| Comilla(n) | 139 | 19:30 | 134 | 17:00 | Rangpur | 135 | 10:00 | 116 | 1:00
| Chandpur | 135 | 19:00 | 130 | 15:00 | Lalmonirhat | 130 | 11:00 | 121 | 19:00
| Feni | 138 | 20:00 | 130 | 16:00 | Saidpur | 131 | 10:00 | 117 | 1:00
| Chowmuhani | 137 | 19:00 | 129 | 23:00 | Purbasadipur | 129 | 10:00 | 112 | 1:00
| Ashuganj | 136 | 15:00 | 132 | 1:00 | Thakurgaon | 126 | 7:00 | 110 | 1:00
| Daudkandi | 134 | 18:30 | 128 | 15:00 | Palashbari | 134 | 10:00 | 115 | 2:00
| B.Baria | 135 | 8:00 | 128 | 21:00 | Barapukuria | 137 | 9:00 | 128 | 1:00
| Ramganj | 131 | 7:00 | 123 | 23:00 | Panchagar | 125 | 10:00 | 105 | 1:00
| Chaddagram | 138 | 19:00 | 129 | 15:00 | Joldhaka | 131 | 10:00 | 116 | 2:00
| PHP | 138 | 3:00 | 126 | 15:00 | Kurigram | 131 | 9:00 | 112 | 1:00
| Madanhat | 140 | 19:30 | 132 | 15:00

## L-Curve
Date | 2020-09-01
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 248 | 7169 | 3606 | 10775 |  |  |  | QF-LDC-11
0:30 | 135.5 | 7507.5 | 3818.5 | 11326 | Date: | 2020-09-01
1:00 | 23 | 7846 | 4031 | 11877
1:30 | 50.5 | 7736.5 | 3951.5 | 11688
2:00 | 78 | 7627 | 3872 | 11499
2:30 | 55 | 7545.5 | 3851.5 | 11397 | [5 empty] | Gen. at Eve. Peak | 11453 | 11453 MW (19:30 )
3:00 | 32 | 7464 | 3831 | 11295 | [6 empty] | 19:30
3:30 | 21 | 7249 | 3769.5 | 11018.5 | [5 empty] | Gen. at Day Peak | 9415.63 | 9415.63 MW (12:00 )
4:00 | 10 | 7034 | 3708 | 10742 | [6 empty] | 12:00
4:30 | 27 | 7010 | 3704.5 | 10714.5 | [5 empty] | Highest Generation | 11877
5:00 | 44 | 6986 | 3701 | 10687 | [6 empty] | 1:00
5:30 | 42.5 | 6815.3 | 3527.5 | 10342.8
6:00 | 41 | 6644.6 | 3354 | 9998.6
6:30 | 92.5 | 6379.85 | 3229.1 | 9608.95
7:00 | 144 | 6115.1 | 3104.2 | 9219.3
7:30 | 156 | 6058.295 | 3064.8 | 9123.095
8:00 | 168 | 6001.49 | 3025.4 | 9026.89
8:30 | 244.5 | 6082.94 | 3009.3 | 9092.24
9:00 | 321 | 6164.39 | 2993.2 | 9157.59
9:30 | 363 | 6211.445 | 2992.2 | 9203.645
10:00 | 405 | 6258.5 | 2991.2 | 9249.7
10:30 | 417.5 | 6237.395 | 3006.35 | 9243.745
11:00 | 430 | 6216.29 | 3021.5 | 9237.79
11:30 | 473 | 6303.76 | 3022.95 | 9326.71
12:00 | 516 | 6391.23 | 3024.4 | 9415.63
12:30 | 474 | 6450.115 | 3051.1 | 9501.215
13:00 | 432 | 6509 | 3077.8 | 9586.8
13:30 | 478 | 6402.6 | 3016.3 | 9418.9
14:00 | 524 | 6296.2 | 2954.8 | 9251
14:30 | 559.5 | 6333.05 | 3034.5 | 9367.55
15:00 | 595 | 6369.9 | 3114.2 | 9484.1
15:30 | 567 | 6354.2 | 3115.2 | 9469.4
16:00 | 539 | 6338.5 | 3116.2 | 9454.7
16:30 | 568 | 6245.4 | 3059.5 | 9304.9
17:00 | 597 | 6152.3 | 3002.8 | 9155.1
17:30 | 483.5 | 6144.7 | 2973.4 | 9118.1
18:00 | 370 | 6137.1 | 2944 | 9081.1
18:30 | 196 | 6749.55 | 3303 | 10052.55
19:00 | 22 | 7362 | 3662 | 11024
19:30 | 115 | 7511 | 3942 | 11453
20:00 | 151 | 7513 | 3930 | 11443 |  |  |  | Executive Engineer
20:30 | 177 | 7499 | 3945 | 11444 |  |  |  | Network Operation Division
21:00 | 203 | 7485 | 3960 | 11445
21:30 | 206.5 | 7409 | 3917.5 | 11326.5
22:00 | 210 | 7333 | 3875 | 11208 |  |  |  |  | Page 6 of 7
22:30 | 204 | 7266.5 | 3752 | 11018.5
23:00 | 198 | 7200 | 3629 | 10829
23:30 | 223 | 7184.5 | 3617.5 | 10802
24:00 | 248 | 7169 | 3606 | 10775
11453 MW (19:30 )
9415.63 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-09-01 |  | Energy | 241878614
[10 empty] | 2020-09-01 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3239 | 921 | 2167 | 3238 | 598 | 80 | 418 | 0 | 164
0:30 | 3254 | 927.5 | 2142.5 | 3651.5 | 593.5 | 84.5 | 543.5 | 0 | 154 | Date: | 2020-09-01
1:00 | 3269 | 934 | 2118 | 4065 | 589 | 89 | 669 | 0 | 144
1:30 | 3251 | 933.5 | 2092.5 | 3937.5 | 594.5 | 88 | 648 | 0 | 143 | [7 empty] | Total Energy | 241.8786 | Total Energy Gen 241.879 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 241.879 MKWHr
2:00 | 3233 | 933 | 2067 | 3810 | 600 | 87 | 627 | 0 | 142 | [7 empty] | Energy not Served | 0
2:30 | 3248 | 933.5 | 2060.5 | 3701 | 600 | 86 | 627 | 0 | 141 | [7 empty] | Energy Requirement | 241.8786
3:00 | 3263 | 934 | 2054 | 3592 | 600 | 85 | 627 | 0 | 140
3:30 | 3282.5 | 933.5 | 2048 | 3398.5 | 589.5 | 84.5 | 543 | 0 | 139 | [6 empty] | Shortage
4:00 | 3302 | 933 | 2042 | 3205 | 579 | 84 | 459 | 0 | 138
4:30 | 3311 | 933.5 | 2049 | 3188 | 579 | 84 | 434 | 0 | 136
5:00 | 3320 | 934 | 2056 | 3171 | 579 | 84 | 409 | 0 | 134
5:30 | 3305.5 | 933.5 | 2034 | 2969.5 | 579 | 85 | 311 | 0 | 125
6:00 | 3291 | 933 | 2012 | 2768 | 579 | 86 | 213 | 0 | 116
6:30 | 3278.5 | 933 | 1972.5 | 2473.5 | 569 | 86 | 182.5 | 0 | 112 |  |  |  |  | Coal
7:00 | 3266 | 933 | 1933 | 2179 | 559 | 86 | 152 | 0 | 108
7:30 | 3227 | 933 | 1901.5 | 2154.5 | 554 | 87 | 152 | 0 | 109 |  |  |  | Oil |  |  |  | ,
8:00 | 3188 | 933 | 1870 | 2130 | 549 | 88 | 152 | 0 | 110
8:30 | 3145.5 | 933 | 1854 | 2250 | 548.5 | 89 | 152 | 0 | 111
9:00 | 3103 | 933 | 1838 | 2370 | 548 | 90 | 152 | 0 | 112
9:30 | 3108 | 933 | 1847.5 | 2402 | 548 | 85 | 147 | 0 | 119
10:00 | 3113 | 933 | 1857 | 2434 | 548 | 80 | 142 | 0 | 126
10:30 | 3151.5 | 931.5 | 1837 | 2412 | 548.5 | 80 | 139 | 0 | 129
11:00 | 3190 | 930 | 1817 | 2390 | 549 | 80 | 136 | 0 | 132
11:30 | 3187 | 930.5 | 1833.5 | 2451 | 549 | 80 | 144.5 | 0 | 134
12:00 | 3184 | 931 | 1850 | 2512 | 549 | 80 | 153 | 0 | 136
12:30 | 3230.5 | 931 | 1936 | 2496 | 528.5 | 80 | 145 | 0 | 138
13:00 | 3277 | 931 | 2022 | 2480 | 508 | 80 | 137 | 0 | 140
13:30 | 3277 | 931 | 2022 | 2480 | 508 | 80 | 137 | 0 | 140
14:00 | 3277 | 931 | 2022 | 2480 | 508 | 80 | 137 | 0 | 140
14:30 | 3253.5 | 930.5 | 2065 | 2337.5 | 573.5 | 78.5 | 137 | 0 | 147
15:00 | 3230 | 930 | 2108 | 2195 | 639 | 77 | 137 | 0 | 154
15:30 | 3228.5 | 930 | 2102 | 2185.5 | 644 | 77 | 138.5 | 0 | 151
16:00 | 3227 | 930 | 2096 | 2176 | 649 | 77 | 140 | 0 | 148
16:30 | 3182 | 930.5 | 1997 | 2188 | 644.5 | 77 | 138.5 | 0 | 140
17:00 | 3137 | 931 | 1898 | 2200 | 640 | 77 | 137 | 0 | 132
17:30 | 3100 | 930.5 | 1827 | 2253 | 624 | 77 | 172 | 0 | 133
18:00 | 3063 | 930 | 1756 | 2306 | 608 | 77 | 207 | 0 | 134
18:30 | 3222 | 925 | 1948 | 2721 | 610 | 77 | 399.5 | 0 | 150
19:00 | 3381 | 920 | 2140 | 3136 | 612 | 77 | 592 | 0 | 166
19:30 | 3267 | 920 | 2186 | 3507 | 653 | 79 | 671 | 0 | 170
20:00 | 3233 | 920 | 2156 | 3558 | 652 | 79 | 675 | 0 | 170
20:30 | 3228 | 920 | 2138.5 | 3555 | 664.5 | 79.5 | 688.5 | 0 | 170
21:00 | 3223 | 920 | 2121 | 3552 | 677 | 80 | 702 | 0 | 170
21:30 | 3204 | 919.5 | 2085.5 | 3497.5 | 674 | 80 | 697 | 0 | 169
22:00 | 3185 | 919 | 2050 | 3443 | 671 | 80 | 692 | 0 | 168
22:30 | 3231 | 919.5 | 2050.5 | 3340.5 | 670.5 | 80 | 558.5 | 0 | 168
23:00 | 3277 | 920 | 2051 | 3238 | 670 | 80 | 425 | 0 | 168
23:30 | 3258 | 920.5 | 2109 | 3238 | 634 | 80 | 421.5 | 0 | 166 | Max Temp. in Dhaka |  | 31° C
24:00 | 3239 | 921 | 2167 | 3238 | 598 | 80 | 418 | 0 | 164
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 241.879 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 241.879 MKWHr
Note on W13: Author:

## Generation
g | 2020-09-01
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 89 | 87 | 85 | 84 | 84 | 86 | 86 | 88 | 90 | 45 | 45 | 45 | 45 | 42 | 42 | 42 | 42 | 42 |  | 42 | 44 | 44 | 45 | 45 | 45 | 45 | 1415198
2 | Karnaphuli Hydro PP Unit-4 & 5 | [9 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 524000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 0 | [7 empty] | 5 | 8 | 8 | [7 empty] | 21 | 25 | 25 | 25 | 25 | 8 | 8 | 188020
| Teknaf 20MW PP (Solartech) | [5 empty] | 0.5 | 2.1 | 4.59 | 7.69 | 9.5 | 7.89 | 10.83 | 4 | 9.9 | 6.3 | 10.3 | 2.2 | 0.1 | [8 empty] | 85320
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 148 | 146 | 148 | 145 | 147 | 149 | 144 | 145 | 145 | 147 | 147 | 147 | 150 | 147 | 146 | 146 | 147 | 100 |  | 145 | 147 | 147 | 149 | 148 | 148 | 149 | 3469144
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 68 | 34 | 34 | 0 | [7 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 34 |  | 102 | 102 | 102 | 102 | 102 | 68 | 68 | 868026
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 34 | 34 | 34 | 17 | 17 | 0 | [13 empty] | 9 | 17 | 17 |  |  |  |  | 204071
| Daudkandi 200 MW PP (B.Trac) | 70 | 0 | [24 empty] | 97536
14 | Titas 50 MW Peaking PP | 33 | 33 | 33 | [16 empty] | 42 | 42 | 42 | 42 | 33 |  |  | 282936
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 300 | 300 | 300 | 300 | 300 | 300 | 288 | 300 | 295 | 286 | 272 | 281 | 260 | 253 | 258 | 270 | 268 | 268 |  | 268 | 268 | 270 | 268 | 268 | 268 | 268 | 6746943
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 8 | 602181
20 | Ghorasal TPP (Unit-1&2) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 570000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 102 | 90 | 102 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2398000
23 | Ghorasal TPP Unit-5 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2677500
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 35 | 33 | 35 | 33 | 33 | 35 | 33 | 35 | 35 | 33 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 780624
33 | Ashuganj 225 MW CCPP | 213 | 173 | 173 | 184 | 186 | 181 | 195 | 176 | 188 | 188 | 178 | 179 | 176 | 179 | 186 | 181 | 182 | 190 |  | 203 | 187 | 181 | 213 | 214 | 206 | 179 | 4594000
34 | Ashuganj 450 MW CCPP(South) | 255 | 255 | 255 | 270 | 270 | 255 | 280 | 255 | 255 | 250 | 250 | 255 | 265 | 265 | 265 | 265 | 265 | 270 |  | 300 | 265 | 265 | 270 | 265 | 310 | 265 | 6437000
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 260 | 275 | 275 | 260 | 290 | 260 | 275 | 275 | 275 | 275 | 310 | 260 | 260 | 260 | 260 | 260 |  | 295 | 260 | 260 | 265 | 260 | 305 | 270 | 6848200
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 137760
36 | Chandpur 150 MW CCPP | 87 | 87 | 95 | 97 | 97 | 96 | 96 | 90 |  | 20 | 90 | 95 | 85 | 95 | 96 | 92 | 90 | 95 |  | 95 | 92 | 90 | 95 | 88 | 94 | 97 | 2024200
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 339 | 339 | 338 | 338 | 350 | 340 | 344 | 351 | 340 | 342 | 345 | 340 | 341 | 339 | 352 | 344 | 340 | 341 |  | 370 | 341 | 349 | 341 | 340 | 347 | 377 | 8400890
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 400 | 400 | 400 | 400 | 370 | 370 | 370 | 370 | 370 | 370 | 420 | 380 | 450 | 450 | 400 | 320 |  | 420 | 420 | 420 | 390 | 350 | 350 | 420 | 9124750
41 | Haripur 360MW CCPP(HPL) | 352 | 352 | 352 | 353 | 353 | 353 | 300 | 300 | 302 | 302 | 302 | 302 | 350 | 302 | 352 | 351 | 303 | 272 |  | 350 | 351 | 353 | 355 | 355 | 354 | 352 | 7939000
42 | RPCL 210MW CCPP | 157 | 158 | 157 | 157 | 157 | 158 | 157 | 159 | 158 | 158 | 142 | 124 | 125 | 122 | 122 | 122 | 127 | 125 |  | 126 | 126 | 126 | 125 | 125 | 123 | 125 | 3254160
43
44 | Fenchugonj CCPP Phase-1 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 90 | 90 | 90 | 90 | 90 | 90 | 91 | 91 |  | 91 | 91 | 91 | 91 | 90 | 90 | 90 | 2134000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 719280
46 | Shajibazar 330 MW CCPP | 204 | 206 | 205 | 208 | 204 | 205 | 211 | 202 | 203 | 201 | 200 | 195 | 192 | 200 | 203 | 196 | 198 | 204 |  | 210 | 192 | 194 | 203 | 193 | 208 | 193 | 4780000
47 | Shahjibazar GTPP Unit- 8 & 9 | 64 | 64 | 64 | 64 | 64 | 63 | 63 | 64 | 64 | 64 | 67 | 67 | 64 | 64 | 63 | 63 | 63 | 63 |  | 63 | 64 | 64 | 67 | 67 | 40 | 40 | 1511904
48 | Shahjibazar 86MW PP (Shahjibazar) | 85 | 85 | 85 | 85 | 83 | 83 | 83 | 83 | 83 | 85 | 85 | 85 | 85 | 85 | 84 | 85 | 85 | 20 |  | 85 | 84 | 87 | 87 | 87 | 87 | 87 | 1986240
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 80 | 80 | 80 | 79 | 80 | 80 | 79 | 80 | 80 | 80 | 80 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2166030
51 | Sylhet 20 MW GTPP | [13 empty] | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 179000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 246600
54 | Hobiganj 11MW PP Cofidence-E | 5 | 5 | 5 | 5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 5 | 5 | 7 | 8 | 8 | 8 | 8 | 97392
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 50 | 50 | 47 | 47 | 47 | 47 | 47 | 47 | 50 | 50 | 47 |  | 47 | 47 | 50 | 47 | 47 | 47 | 47 | 1188600
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 536832
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 275 | 270 | 285 | 300 | 280 | 295 | 305 | 280 | 290 | 285 | 285 | 275 | 265 | 300 | 295 | 290 | 280 |  | 310 | 310 | 300 | 290 | 290 | 285 | 310 | 7157800
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 17 | 17 | 17 | 17 | 17 | 40 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1072940
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 438864
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 |  |  | 19 | 19 | 19 | 19 | 22 | 22 | 22 | 22 |  | 22 |  | 22 | 22 | 22 |  | 22 | 22 | 22 | 385236
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 19 | 19 | 19 | 19 |  | 19 | 21 | 20 | 22 | 22 | 22 | 22 | 433080
63 | Impoprt (Tripura) | 144 | 142 | 140 | 138 | 134 | 116 | 108 | 110 | 112 | 126 | 132 | 136 | 140 | 152 | 154 | 148 | 132 | 134 |  | 166 | 170 | 170 | 170 | 168 | 168 | 164 | 3456000
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 40 | 40 | 40 | 40 | 34 | 8 | 4 | 3 | 2 | 4 | 14 | 16 | 3 | 6 | 13 | 12 |  | 26 | 29 | 29 | 35 | 37 | 40 | 31 | 587040
65 | Feni 22MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 19 |  | 19 | 19 | 19 | 20 | 20 | 20 | 20 | 436572
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 232920
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 818400
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 15 | 15 | 15 | 0 | 20 | 20 | 20 | 20 | 20 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 483210
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 28 | 29 |  | 31 | 30 | 30 | 30 | 30 | 30 | 30 | 687780
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 816800
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 798300
73 | Ghorashal 108MW PP (Regent) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 73 | 73 | 73 | 73 | 73 | 73 | 72 | 72 | 72 | 72 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 1716636
| Feni Lanka Power | 114 | 114 | 114 | 88 | 52 | 0 |  |  |  | 17 | 17 | 17 | [7 empty] | 114 | 114 | 114 | 114 | 114 | 70 | 70 | 1225500
| Chowmuhani 113 MW | 113 | 108 | 113 | 113 | 113 | 109 | 108 | 110 | 108 | 113 | 113 | 113 | 113 | 109 | 113 | 113 | 107 | 110 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2693880
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 100 | 100 | 100 | 100 | 100 | 92 | 92 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 97 | 100 | 95 | 90 | 90 | 95 | 100 | 2373120
78 | Gazipur 52 MW PP | 51 | 51 | 51 | 25 | 25 | 0 |  |  |  | 10 | 16 | 16 | [7 empty] | 37 | 51 | 51 | 51 | 51 | 8 | 8 | 510552
79 | Kodda 150MW PP | 149 | 149 | 149 | 98 | 64 | 0 |  |  |  | 16 | 16 | 16 | [5 empty] | 48 |  | 149 | 149 | 149 | 149 | 149 | 98 | 98 | 1561440
80 | Jamalpur 95 MW PP(Powerpac) | 72 | 72 | 71 | 71 | 71 | 71 | 48 | 8 | 8 | 12 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 45 | 75 | 74 | 73 | 73 | 73 | 73 | 1093440
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 43 | 43 | 8 |  |  |  | 3 | 8 | 8 | 8 | [6 empty] | 25 | 43 | 43 | 43 | 43 | 43 | 43 | 530054
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 17 | 29 | 87 | 87 | 87 | 97 | 105 | 17 | 17 | 17 | 32 | 34 |  | 85 | 105 | 105 | 105 | 105 | 105 | 105 | 1940856
| Kaptai 7 MW Solar PP | [5 empty] | 0.1 | 0.9 | 1.8 | 2.6 | 2.9 | 2.3 | 2.3 | 1 | 3.3 | 4.5 | 0.1 | [10 empty] | 23761
| Jodiac Power | 54 | 54 | 54 | 34 | 34 | 34 |  |  |  | 30 | 34 | 34 | 47 | 17 | 17 | 17 | 17 | 17 |  | 46 | 54 | 54 | 54 | 54 | 54 | 54 | 874443
| Karnaphuli Power Ltd. | 17 | 17 | 17 | 0 | [22 empty] | 71090
82 | Madanganj 102 PP(Summit) | 80 | 80 | 80 | 80 | 80 | 80 | 60 | [14 empty] | 2 | 48 | 64 | 64 | 64 | 808396
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 26 | 26 | [6 empty] | 9 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 29 | 100 |  | 16 | 18 | 20 | 26 | 25 | 26 | 26 | 447193
86 | Meghnaghat CCPP(Summit) | 132 | 127 | 133 | 140 | 140 | 130 | 145 | 125 | 140 | 135 | 140 | 140 | 120 | 130 | 140 | 135 | 140 | 140 |  | 150 | 140 | 140 | 144 | 140 | 140 | 146 | 3357498
87 | Meghnaghat 100 MW(IEL) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2451840
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 91 | 90 | 89 | 95 | 104 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 2543040
88 | Ghorashal 78.5 MW PP(MAX) | [26 empty] | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [19 empty] | 20 | 10 | [5 empty] | 71160
92 | Fenchuganj 44MW (Energyprima) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 44 | 44 | 47 | 43 | 43 | 43 | 43 | 47 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 1106280
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 14 | 38 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1200453
94 | Gagnagar 102 MW PP (Digital Power) | 93 | 93 | 93 | 85 | 85 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 86 | 93 | 93 | 93 | 93 | 93 |  | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 2203920
95 | Patenga 50MW PP (Baraka) | 50 | 50 | 50 | 50 | 50 | 40 |  |  | 1 | 16 | 18 | 18 | 26 | 40 | 25 | 25 | 25 | 25 |  | 44 | 50 | 45 | 32 | 32 | 32 | 32 | 744000
96 | Chattogram 108 MW PP (ECPV) | 90 | 90 | 84 | 87 | 90 | 90 | 50 | 39 | 70 | 70 | 70 | 70 | 72 | 77 | 51 | 51 | 50 | 50 |  | 86 | 89 | 90 | 90 | 90 | 90 | 90 | 1816320
97 | Katpotti 52 MW PP (Sinha)
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 15 | 15 | 15 | 15 | 15 | 48 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1150776
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 17 |  |  |  | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  |  |  |  | 33 | 55 | 55 |  | 944057
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 163 | 130 | 163 | 163 | 110 | 110 |  | 130 | 163 | 130 | 130 | 110 | 110 | 163 | 3567927
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  | 0.1 | 0.1 | 0.1 | [9 empty] | 550
103 | Kamalaghat 54 MW PP(Banco Energy) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1313280
104 | Keranigonj 300 MW PP (APR) | 33 | [25 empty] | 37902
105 | Bramhangoan 100 MW PP (Aggreko) | [26 empty] | 0
106 | Mymensingh 200 MW PP (United) | 192 | 192 | 192 | 192 | 192 | 192 | 200 | 200 | 200 | 160 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 134 |  | 192 | 194 | 193 | 194 | 200 | 200 | 200 | 4104000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 130 | 131 | 131 | 131 | 131 | 128 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 111 | 80 | 64 | 94 | 112 |  | 111 | 111 | 112 | 112 | 128 | 132 | 131 | 2783520
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2441280
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 150 | [16 empty] | 22 | 105 | 151 | 101 |  |  |  | 1033920
117 | Ashuganj 150MW PP (Midland) | 83 | 83 | 83 | 83 | 83 | 83 | 10 | 18 | 85 | 85 | 26 | 85 | 95 | 105 | 113 | 117 | 117 | 118 |  | 122 | 122 | 122 | 122 | 122 | 123 | 118 | 2274909
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 75 | 75 | 24 | [13 empty] | 72 | 95 | 95 | 65 | 35 | 35 | 35 | 986400
| Anwara 300 MW PP (United) | 307 | 307 | 307 | 307 | 307 | 307 | 217 | 283 | 306 | 306 | 307 | 307 | 307 | 307 | 253 | 252 | 199 | 197 |  | 270 | 305 | 307 | 307 | 307 | 307 | 307 | 6919320
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2436480
120 | Eastern Zone Total | 7846 | 7627 | 7464 | 7034 | 6986 | 6644.6 | 6115.1 | 6001.49 | 6164.39 | 6258.5 | 6216.29 | 6391.23 | 6509 | 6296.2 | 6369.9 | 6338.5 | 6152.3 | 6137.1 |  | 7362 | 7511 | 7513 | 7485 | 7333 | 7200 | 7169 | 164979472
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 115 | 115 | 115 | 99 | 99 | 99 | 74 | 66 | 66 | 66 | 66 | 66 | 82 | 85 | 74 | 66 | 66 | 66 |  | 115 | 99 | 99 | 99 | 99 | 99 | 99 | 2090880
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
| Khulna 225 MW CCPP | 200 | 200 | 200 | 200 | 185 | 125 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 150 | 150 | 120 | 120 | 3471360
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 105 | 105 | 105 | 53 | [13 empty] | 53 | 90 | 105 | 105 | 105 | 21 | 17 | 1052640
130
131
132
133
| Barisal 110 MW PP (Summit ) | 48 | 48 | 48 | 48 | 48 | 16 | 16 | [12 empty] | 62 | 64 | 64 | 64 | 64 | 64 | 64 | 655680
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 72 | 76 | 77 | 78 | 77 | 78 | 79 | 29 | 22 | 22 | 22 | 22 | 22 | 23 | 22 | 22 | 22 | 67 |  | 76 | 76 | 77 | 79 | 78 | 77 | 79 | 1287950
| Bhola 225 MW CCPP | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1513000
140 | Bhola 33 MW PP (Venture) | 28 | 28 | 27 | 25 | 25 | 23 | 20 | 19 | 17 | 15 | 14 | 17 | 17 | 18 | 21 | 19 | 18 | 22 |  | 30 | 32 | 33 | 31 | 35 | 35 | 33 | 605440
141 | Noapara 100 MW PP (Bangla Trac) | 100 | 100 | 0 | [16 empty] | 21 | 30 | 30 | 30 |  |  |  | 334080
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 40 | 40 | 40 | 0 | [13 empty] | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 450375
143 | Gopalganj 100 MW Peaking PP | [15 empty] | 3 | [10 empty] | 768
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 934 | 933 | 934 | 933 | 934 | 933 | 933 | 933 | 933 | 933 | 930 | 931 | 931 | 930 | 930 | 930 | 931 | 930 |  | 920 | 920 | 920 | 920 | 919 | 920 | 921 | 22297454
147 | Bheramara 410 MW CCPP | 310 | 315 | 340 | 340 | 345 | 355 | 365 | 375 | 375 | 370 | 375 | 370 | 370 | 350 | 335 | 325 | 320 | 265 |  | 340 | 315 | 315 | 300 | 300 | 310 | 310 | 8148672
148 | Payra 1320 MW | 440 | 450 | 450 | 430 | 430 | 430 | 410 | 400 | 400 | 400 | 400 | 400 | 360 | 410 | 490 | 500 | 500 | 500 |  | 500 | 540 | 540 | 570 | 570 | 520 | 449 | 5051800
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 149 | 150 | 150 | 149 | 149 | 149 | 149 | 149 | 148 | 148 | 149 | 149 | 148 | 149 | 149 | 149 | 140 | 108 |  | 112 | 113 | 112 | 107 | 101 | 150 | 149 | 3444800
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 50 | 50 | 50 | 0 | [15 empty] | 50 | 50 | 50 | 50 | 50 |  |  | 412488
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 190 | 188 | 187 | 185 | 188 | 186 | 166 | 158 | 149 | 152 | 152 | 148 | 181 | 149 | 163 | 156 | 147 | 148 |  | 178 | 187 | 174 | 150 | 149 | 150 | 173 | 4190055
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 202 | 202 | 202 | 204 | 204 | 210 | 150 | 150 | 130 | 150 | 150 | 150 | 180 | 130 | 182 | 216 | 150 | 130 |  | 175 | 209 | 185 | 180 | 150 | 150 | 175 | 4655855
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 370 | 320 | 362 | 368 | 370 | 347 | 347 | 350 | 353 | 342 | 349 | 353 | 375 | 346 | 416 | 405 | 357 | 352 |  | 412 | 420 | 423 | 423 | 407 | 412 | 420 | 8893054
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 5 |  | 16 | 35 | 35 | 35 | 35 |  |  | 124952
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 22 | 18 | 18 | 18 | 21 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 490320
163 | Bogura 20 MW PP (Energyprima) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 254700
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 |  |  |  | 8 | 9 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 212220
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 50 | 0 | [24 empty] | 72018
167 | Katakhali 50 MW Peaking PP | 44 | 44 | 44 | 44 | 44 | 0 | [13 empty] | 35 | 44 | 47 | 44 | 43 | 43 | 43 | 448400
168 | Santahar 50 MW Peaking PP | 29 | 29 | 29 | 29 | 28 | 0 | [13 empty] | 22 | 33 | 32 | 32 | 32 |  |  | 292362
169 | Natore 52 MW PP (Rajlanka) | 43 | 43 | 43 | 43 | 43 | 0 |  |  |  | 8 | 8 | 8 | [7 empty] | 35 | 43 | 43 | 43 | 43 | 8 | 8 | 464160
170 | Chapainawabganj 100 MW Peaking PP | 96 | 88 | 88 | 88 | 88 | 88 | 32 | 32 | 32 | 6 | [9 empty] | 56 | 96 | 98 | 98 | 98 | 96 | 89 | 1165040
171 | Baghabari 200 MW PP (Paramount) | 30 | 0
| Bagura 113 MW PP (Confidence)-2 | 95 | 76 | 76 | 57 | 57 | 37 |  |  |  | 12 | 35 | 35 | 35 | [6 empty] | 21 | 89 | 90 | 113 | 113 | 113 | 113 | 1143456
172 | Confidence Power Bogura Unit-1 113 MW | 90 | 90 | 90 | 72 | 72 | 54 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1890528
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 98 | 79 | 71 | 71 | 70 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 70 | 70 | 39 | 34 | 35 | 34 |  | 74 | 98 | 99 | 98 | 95 | 102 | 106 | 1753920
177 | Sympa Solar Power 8MW | [6 empty] | 0.2 | 0.4 | 1.2 | 4.2 | 3.5 | 7.4 | 6.8 | 4.8 | 3.2 | 1.2 | 0.8 | [9 empty] | 30715
178
178