## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-09-04 | Friday
|  |  | Date (day): | 2020-09-04 |  | Friday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14012.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14870 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-09-03 | 2020-09-04 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 28 | 28 | 28 | 28 |  | 57 | Unit-2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 110 | 110 | 110 | 110 | 80 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 71 | 73 | 90 | 90 | 18 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 341 | 342 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 303 | 348 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 420 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 100 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 140 | 148 | 150 | 150 | 155 |  | GT-1 S/D for gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 97 | 97 | 96 | 96
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 12 | 100 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 95 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 272 | 309 | 335 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 93 | 93 | 93 | 93
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 53 | 53 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 116 | 149 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 47 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 51 | 51 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 253 | 253 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 77 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 50 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 55 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 113 | 113 | 133 | 133 |  | 16 | Engine problem
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 85 | 103 | 100 | 100
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 3277 | 3676 | 3974 | 4224 | 885 | 768
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20.33 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 46 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 80 | 77 | 77 | 77 | 153 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 24 | 97 | 225 | 225 | 0
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Under maint.
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 66 | 102 | 100 | 100
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 65 | 60 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 20 | 21 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 28 | 30 | 40
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 78 | 85 | 95 | 95 |  | 13 | Engine problem
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5.5 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 307 | 235 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 1 | 0 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 938.83 | 979 | 1512 | 1497 | 513 | 111
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 100 | 80 | 100 | 134 |  | Gas shortage
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 140 | 114 | 225 | 225
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 280 | 360 | 360
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 275 | 255 | 360 | 360
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 14 | 34 | 35 | 36 | 9 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 44 | 50 | 50 | 5
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 97 | 106 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 41 | 48 | 0 | 44
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 95 | 100 | 100 |  | 63 | ST under shut down
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 58 | 100 | 200 | 200
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 20 | 21 | 21
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 10 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 138 | 170 | 157 | 173
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 17 | 33 | 33
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 43 | 43 | 43 |  | 9 | Engine problem
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 18 | 20 | 20 |  | 5 | Engine problem
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 80 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 114 | 108 | 114 | 114
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 113 | 113 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1535 | 1814 | 2131 | 2412 | 599 | 77
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 154 | 152 | 157 | 160 | 42 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 72 | 72 | 72 | 72 |  | 23 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.5 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 184 | 200 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 65 | 115 | 115 | 115
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 496.5 | 558 | 567.6 | 569 | 42 | 23
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 91 | 91 | 90 | 90
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Unit-4 under shut down
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 163 | 163 | 163
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 99 | 130 | 210 | 210 |  | 120 | Engine problem
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 53 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 48 | 49 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 65 | 66 | 66
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 87 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 130 | 140 | 140 | 140 |  | 91 | Machine problem
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 300 | 341 | 341
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1017 | 1171 | 1285 | 1285 | 0 | 671
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 895 | 889 | 942 | 942
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 99 | 115 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 2 | 0 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 135 | 190 | 225 | 225
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 410 | 405 | 410 | 410
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 40 | 40 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 80 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 90 | 105 | 105 | 105
| 108 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 80 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1751 | 1844 | 2017 | 2143 | 0 | 0
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 110 | 110 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 21 | 31 | 33 | 33
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 15 | 89 | 65 | 65 |  | 129 | GT-2 & ST Under maint.
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 78 | 77 | 80 | 80 |  | 15 | Engine problem
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 0 | 490 | 450 | 490 |  |  | Unit-2 Test. Unit-1 under S/D
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 224 | 797 | 738 | 778 | 0 | 144
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 50 | 50 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 35 | 34 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 44 | 0 | 50
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 190 | 191 | 220 | 220 |  |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 213 | 180 | 220 | 220 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 370 | 408 | 414 | 414 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 31 | 0 | 32
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 21 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 11 | 11 | 11 | 11
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 43 | 43 | 43 | 43 |  | 9 | Engine problem
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 48 | 98 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 95 | 113 | 113 | 113
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 90 | 103 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 1177 | 1338 | 1517 | 1689 | 431 | 9
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 70 | 100 | 113 | 113
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5.4 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 225.4 | 250 | 271 | 273 | 294 | 30
|  | Total |  |  |  |  | 20383 | 19892 | 10641.73 | 12427 | 14012.6 | 14870 | 2764 | 1833
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10239.2505 | 11957 | 13482.6312 | 14307.6036
| A. |  | 2020-09-03 | (Yesterday) |  |  |  |  | Thursday
| 1 | Highest Generation : |  |  | 12427 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
| 2 | Minimum Generation : |  |  | 9015.2 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12427 | MW
| 3 | Day peak Generation : |  |  | 10641.73 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11957 | MW
| 4 | Evening peak Generation : |  |  | 12427 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 261.423 | MKWHr | By Solar | 0.24385 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 132.8456 | MKWHr |  | By Oil: | 87.3989 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 13.8604 | MKWHr |  | By Hydro: | 1.9207 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2764 | MW | Dhaka | 4129 | 4129 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 1833 | MW | Chittagong | 1286 | 1286 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4597 | MW | Khulna | 1504 | 1504 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1084.28 | MMCFD |  |  | Rajshahi | 1289 | 1289 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 152252722.776 | ii) Oil : | Taka | 712799578.58 | Comilla | 1137 | 1137 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 64647650 | Total | Taka | 929699951.356 | Mymensingh | 978 | 978 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 529 | 529 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 55 | MW (E to W) at | 19:30 | hrs | Barisal | 346 | 346 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 20 | MW at | 20:00 | hrs | Rangpur | 759 | 759 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 35.4° C |  |  | Total | 11957 | 11957 |  | 0
| B. |  | 2020-09-04 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 33.5° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 11800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14870 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 9400 | MW
| 4 | Reserve(Generation end) |  |  |  | 3070 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 248.233 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8804.3 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.4633 | MKWHr. | ii) HVDC Flow at Peak Time |  | 889 | MW at | 19:30 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.6902 | MKWHr. | iii) Maximum HVDC Flow : |  | 904 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 93.23 |  | (b) Today: | 93.31 |  | (c) Rule Curve: |  | 99.69
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-09-03
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 28 | 0 | 100 | 110 | 0 | 72 | 0 | 341 | 353 |  | 0 | 400 | 140 | 100 | 97 | 55 | 288 | 0 | 0 | 0 | 100 | 93 | 149 | 12 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 28 | 33 | 51 | 0 | 46 | 35 | 0 | 0 | 25 | 107 | 0 | 150 | 0 |  | 0 | 0 | 51 | 0 | 87 | 50 | 18 | 42 | 0 | 0 | 0 | 310 | 285 | 0 | 8 | 0 | 35 | 42 | 0 | 5 | 0 | 0 | 43 | 20 | 11 | 33 | 21 | 166 | 155 | 72 | 22 | 0 | 90 | 30 | 50 | 49 | 163 | 202 | 62 | 85 | 0 | 120 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 268 | 0 | 0 | 193 | 0 | 96 | 0 | 100 | 70 | 0 | 0 | 109 | 104 | 0 | 0 | 288 | 0 | 17 | 114 | 113 | 100 | 0 | 104 |  | 904 | 0 | 360 | 0 | 115 | 160 | 0 | 0 | 0 | 0 | 40 | 65 | 37 | 64 | 0 | 0 | 0 | 50 | 0 | 96 | 0 | 0 | 42 | 43 | 31 | 21 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 176 | 0 | 78 | 0 | 201 | 0 | 346 | 105 | 0 | 113 | 0 | 88 | 0 | 0 | 90 | 540 |  | 7506 | 3936 | 11442 | 3539 | 904 | 2062 | 3422 | 689 | 81 | 579 | 166 | 0 | 0 | 93.22
2:00 | 28 | 0 | 100 | 110 | 0 | 72 | 0 | 342 | 356 |  | 0 | 400 | 130 | 100 | 88 | 55 | 268 | 0 | 0 | 0 | 100 | 93 | 149 | 12 | 0 | 0 | 0 | 53 | 55 | 17 | 22 | 25 | 30 | 28 | 33 | 51 | 0 | 42 | 35 | 0 | 0 | 0 | 146 | 0 | 140 | 0 |  | 0 | 0 | 17 | 0 | 89 | 50 | 18 | 42 | 0 | 0 | 0 | 310 | 285 | 0 | 8 | 0 | 35 | 46 | 0 | 5 | 0 | 0 | 43 | 20 | 11 | 33 | 21 | 162 | 157 | 72 | 22 | 0 | 90 | 30 | 50 | 49 | 163 | 206 | 62 | 85 | 0 | 120 | 18 | 0 | 10 | 275 | 24 | 8 | 0 | 253 | 0 | 0 | 193 | 0 | 110 | 0 | 100 | 0 | 0 | 0 | 109 | 104 | 0 | 0 | 232 | 0 | 17 | 70 | 106 | 100 | 0 | 104 |  | 894 | 0 | 370 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 65 | 37 | 64 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 42 | 43 | 31 | 21 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 164 | 0 | 78 | 0 | 204 | 0 | 304 | 50 | 0 | 95 | 0 | 74 | 0 | 0 | 90 | 540 |  | 7214 | 3709 | 10923 | 3556 | 894 | 2012 | 3077 | 690 | 77 | 455 | 162 | 0 | 0 | 93.22
3:00 | 28 | 0 | 100 | 110 | 0 | 72 | 0 | 343 | 354 |  | 0 | 400 | 140 | 100 | 84 | 55 | 300 | 0 | 0 | 0 | 100 | 93 | 149 | 13 | 0 | 0 | 0 | 53 | 55 | 0 | 22 | 25 | 30 | 28 | 33 | 8 | 0 | 40 | 35 | 0 | 0 | 0 | 145 | 0 | 140 | 0 |  | 0 | 0 | 17 | 0 | 75 | 19 | 18 | 42 | 0 | 0 | 0 | 315 | 290 | 0 | 8 | 0 | 35 | 46 | 0 | 5 | 0 | 0 | 43 | 20 | 11 | 33 | 21 | 160 | 157 | 72 | 22 | 0 | 90 | 30 | 50 | 46 | 163 | 203 | 62 | 85 | 0 | 120 | 18 | 0 | 10 | 315 | 24 | 8 | 0 | 253 | 0 | 0 | 193 | 0 | 114 | 0 | 100 | 0 | 0 | 0 | 109 | 104 | 0 | 0 | 216 | 0 | 17 | 0 | 113 | 100 | 0 | 104 |  | 894 | 0 | 380 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 34 | 32 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 165 | 0 | 77 | 0 | 210 | 0 | 344 | 0 | 0 | 95 | 0 | 71 | 0 | 0 | 90 | 540 |  | 7111 | 3499 | 10610 | 3612 | 894 | 2083 | 2736 | 689 | 75 | 361 | 160 | 0 | 0 | 93.22
4:00 | 28 | 0 | 100 | 110 | 0 | 72 | 0 | 354 | 355 |  | 0 | 400 | 140 | 100 | 97 | 55 | 310 | 0 | 0 | 0 | 100 | 93 | 149 | 12 | 0 | 0 | 0 | 53 | 55 | 0 | 22 | 25 | 30 | 28 | 33 | 0 | 0 | 40 | 35 | 0 | 0 | 0 | 147 | 0 | 139 | 0 |  | 0 | 0 | 6 | 0 | 44 | 0 | 18 | 42 | 0 | 0 | 0 | 325 | 300 | 0 | 8 | 0 | 35 | 47 | 0 | 5 | 0 | 0 | 0 | 20 | 11 | 33 | 21 | 156 | 157 | 72 | 22 | 0 | 90 | 30 | 50 | 49 | 163 | 211 | 62 | 85 | 0 | 120 | 18 | 0 | 10 | 315 | 24 | 5 | 0 | 250 | 0 | 0 | 193 | 0 | 113 | 0 | 100 | 0 | 0 | 0 | 109 | 0 | 0 | 0 | 216 | 0 | 17 | 0 | 113 | 100 | 0 | 104 |  | 894 | 0 | 395 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 33 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 166 | 0 | 77 | 0 | 214 | 0 | 347 | 0 | 0 | 50 | 0 | 71 | 0 | 0 | 90 | 520 |  | 6951 | 3378 | 10329 | 3676 | 894 | 2090 | 2494 | 669 | 75 | 275 | 156 | 0 | 0 | 93.23
5:00 | 28 | 0 | 100 | 110 | 0 | 72 | 0 | 350 | 354 |  | 0 | 400 | 140 | 100 | 97 | 55 | 306 | 0 | 0 | 0 | 100 | 93 | 82 | 13 | 0 | 0 | 0 | 53 | 55 | 0 | 22 | 25 | 30 | 28 | 33 | 0 | 0 | 41 | 35 | 0 | 0 | 0 | 146 | 0 | 141 | 0 |  | 0 | 0 | 0 | 0 | 44 | 0 | 18 | 42 | 0 | 0 | 0 | 325 | 300 | 0 | 8 | 0 | 35 | 46 | 0 | 5 | 0 | 0 | 0 | 20 | 11 | 33 | 21 | 150 | 157 | 72 | 22 | 0 | 90 | 30 | 50 | 49 | 163 | 210 | 62 | 85 | 0 | 120 | 18 | 0 | 10 | 305 | 24 | 8 | 0 | 250 | 0 | 0 | 194 | 0 | 113 | 0 | 100 | 0 | 0 | 0 | 109 | 0 | 0 | 0 | 216 | 0 | 17 | 0 | 113 | 100 | 0 | 104 |  | 894 | 0 | 400 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 34 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 165 | 0 | 76 | 0 | 216 | 0 | 347 | 0 | 0 | 50 | 0 | 71 | 0 | 0 | 90 | 520 |  | 6858 | 3384 | 10242 | 3677 | 894 | 2078 | 2496 | 669 | 76 | 202 | 150 | 0 | 0 | 93.23
6:00 | 28 | 0 | 100 | 110 | 0 | 72 | 0 | 341 | 316 |  | 0 | 400 | 125 | 100 | 97 | 15 | 255 | 0 | 0 | 0 | 100 | 93 | 32 | 12 | 0 | 0 | 0 | 17 | 17 | 0 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 42 | 35 | 0 | 0 | 0 | 146 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 11 | 0 | 18 | 28 | 0 | 0 | 0 | 310 | 285 | 90 | 8 | 0 | 35 | 47 | 0 | 5 | 0 | 0 | 0 | 20 | 11 | 33 | 21 | 138 | 160 | 72 | 22 | 0.1 | 90 | 30 | 50 | 49 | 163 | 202 | 63 | 85 | 0 | 120 | 18 | 0 | 10 | 285 | 24 | 8 | 0 | 195 | 0 | 0 | 194 | 0 | 113 | 0.5 | 100 | 0 | 0 | 0 | 8 | 0 | 0 | 0.1 | 216 | 0 | 17 | 0 | 113 | 100 | 0 | 104 |  | 893 | 0 | 310 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 147 | 0 | 76 | 0 | 218 | 0 | 294 | 0 | 0 | 0 | 0 | 71 | 0 | 0 | 90 | 500 |  | 6399.7 | 3067 | 9466.7 | 3563 | 893 | 1948 | 2046 | 649 | 77 | 152 | 138 | 0.7 | 0 | 93.23
7:00 | 28 | 0 | 100 | 110 | 0 | 72 | 0 | 339 | 304 |  | 0 | 340 | 140 | 100 | 64 | 15 | 293 | 0 | 0 | 0 | 96 | 93 | 0 | 12 | 0 | 0 | 0 | 53 | 17 | 0 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 42 | 35 | 0 | 0 | 0 | 85 | 0 | 110 | 0 |  | 0 | 0 | 0 | 0 | 11 | 0 | 18 | 6 | 0 | 0 | 22 | 260 | 270 | 132 | 8 | 0 | 35 | 47 | 0 | 5 | 0 | 0 | 0 | 20 | 11 | 33 | 18 | 128 | 159 | 16 | 22 | 0.5 | 90 | 30 | 50 | 49 | 130 | 212 | 62 | 83 | 0 | 120 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 195 | 0 | 0 | 200 | 0 | 113 | 5.1 | 100 | 0 | 0 | 0 | 8 | 0 | 0 | 1.1 | 216 | 0 | 17 | 0 | 113 | 100 | 0 | 104 |  | 893 | 0 | 295 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 144 | 0 | 77 | 0 | 150 | 0 | 342 | 0 | 0 | 0 | 0 | 71 | 0 | 0.4 | 90 | 460 |  | 6142.7 | 2938.4 | 9081.1 | 3426 | 893 | 1861 | 1960 | 609 | 77 | 120 | 128 | 7.1 | 0 | 93.24
8:00 | 28 | 0 | 100 | 110 | 0 | 72 | 0 | 357 | 352 |  | 0 | 340 | 130 | 100 | 0 | 15 | 285 | 0 | 0 | 0 | 100 | 93 | 0 | 12 | 0 | 0 | 0 | 53 | 36 | 0 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 42 | 35 | 0 | 0 | 0 | 57 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 30 | 0 | 18 | 7 | 0 | 0 | 30 | 260 | 280 | 62 | 8 | 0 | 35 | 5 | 0 | 5 | 0 | 0 | 0 | 17 | 8 | 33 | 18 | 128 | 158 | 25 | 22 | 1.2 | 90 | 30 | 50 | 49 | 130 | 200 | 61 | 83 | 0 | 120 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 215 | 0 | 0 | 200 | 0 | 112 | 10.6 | 100 | 0 | 5 | 0 | 8 | 5 | 0 | 2.6 | 252 | 0 | 17 | 0 | 113 | 100 | 0 | 104 |  | 894 | 0 | 330 | 0 | 68 | 120 | 0 | 0 | 0 | 0 | 0 | 15 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 157 | 0 | 83 | 0 | 159 | 0 | 333 | 0 | 0 | 0 | 0 | 70 | 0 | 1.8 | 90 | 460 |  | 6019.4 | 2995.8 | 9015.2 | 3233 | 894 | 1884 | 2053 | 610 | 77 | 120 | 128 | 16.2 | 0 | 93.24
9:00 | 28 | 0 | 100 | 110 | 0 | 72 | 0 | 349 | 351 |  | 0 | 340 | 140 | 100 | 0 | 32 | 303 | 0 | 0 | 0 | 100 | 93 | 32 | 13 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 25 | 33 | 2 | 0 | 43 | 35 | 0 | 0 | 2 | 58 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 73 | 15 | 18 | 6 | 0 | 0 | 60 | 255 | 260 | 79 | 8 | 0 | 5 | 5 | 0 | 28 | 0 | 0 | 5 | 17 | 8 | 33 | 18 | 128 | 155 | 64 | 22 | 1.9 | 91 | 30 | 50 | 49 | 130 | 105 | 40 | 83 | 0 | 120 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 253 | 0 | 0 | 200 | 0 | 113 | 15.7 | 100 | 0 | 30 | 0 | 25 | 69 | 0 | 4 | 252 | 0 | 0 | 0 | 108 | 100 | 0 | 104 |  | 894 | 0 | 310 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 40 | 15 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 83 | 0 | 210 | 0 | 382 | 0 | 0 | 18 | 0 | 70 | 0 | 1.6 | 90 | 480 |  | 6296.6 | 3190.6 | 9487.2 | 3147 | 894 | 1944 | 2491 | 630 | 78 | 152 | 128 | 23.2 | 0 | 93.24
10:00 | 28 | 0 | 100 | 110 | 0 | 72 | 0 | 357 | 350 |  | 0 | 450 | 138 | 100 | 22 | 55 | 266 | 0 | 0 | 0 | 100 | 93 | 84 | 12 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 25 | 33 | 41 | 0 | 44 | 35 | 0 | 0 | 12 | 58 | 0 | 0 | 0 |  | 0 | 0 | 0 | 65 | 75 | 44 | 18 | 4 | 0 | 0 | 80 | 265 | 260 | 121 | 8 | 0 | 5 | 5 | 0 | 43 | 0 | 0 | 32 | 17 | 8 | 33 | 18 | 134 | 155 | 64 | 0 | 0.9 | 91 | 30 | 50 | 46 | 130 | 98 | 65 | 83 | 0 | 120 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 253 | 150 | 0 | 185 | 46 | 113 | 18.7 | 90 | 17 | 82 | 0 | 42 | 70 | 0 | 4.7 | 304 | 0 | 0 | 114 | 113 | 90 | 0 | 104 |  | 893 | 0 | 310 | 0 | 115 | 130 | 0 | 0 | 0 | 0 | 40 | 15 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 20 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 171 | 0 | 81 | 0 | 207 | 0 | 383 | 35 | 0 | 57 | 0 | 70 | 0 | 6 | 90 | 0 |  | 7129.3 | 2872 | 10001.3 | 3202 | 893 | 2051 | 3248 | 150 | 79 | 214 | 134 | 30.3 | 0 | 93.25
11:00 | 28 | 0 | 100 | 110 | 0 | 71 | 0 | 341 | 318 |  | 0 | 450 | 140 | 100 | 88 | 55 | 271 | 0 | 0 | 0 | 96 | 93 | 84 | 12 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 29 | 25 | 33 | 51 | 0 | 44 | 35 | 0 | 0 | 25 | 57 | 0 | 0 | 0 |  | 0 | 0 | 68 | 65 | 75 | 47 | 18 | 3 | 0 | 0 | 80 | 265 | 260 | 141 | 8 | 0 | 8 | 5 | 0 | 51 | 0 | 0 | 32 | 17 | 8 | 33 | 20 | 138 | 153 | 64 | 0 | 2.4 | 91 | 30 | 47 | 46 | 163 | 98 | 40 | 82 | 0 | 120 | 18 | 0 | 10 | 270 | 24 | 8 | 0 | 250 | 0 | 0 | 184 | 27 | 113 | 16.6 | 90 | 51 | 100 | 0 | 65 | 85 | 0 | 5.3 | 307 | 0 | 0 | 114 | 110 | 90 | 0 | 104 |  | 896 | 0 | 355 | 0 | 99 | 135 | 0 | 0 | 0 | 0 | 40 | 15 | 26 | 110 | 0 | 0 | 0 | 50 | 17 | 24 | 0 | 0 | 0 | 43 | 0 | 20 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 214 | 0 | 362 | 53 | 0 | 81 | 20 | 70 | 0 | 6.8 | 90 | 0 |  | 7186.3 | 3156.8 | 10343.1 | 3248 | 896 | 2021 | 3402 | 150 | 79 | 378 | 138 | 31.1 | 0 | 93.25
12:00 | 28 | 0 | 100 | 110 | 0 | 71 | 0 | 341 | 303 |  | 0 | 450 | 140 | 100 | 97 | 55 | 272 | 0 | 0 | 0 | 95 | 93 | 116 | 12 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 28 | 25 | 25 | 51 | 0 | 45 | 35 | 0 | 0 | 25 | 24 | 0 | 0 | 0 |  | 0 | 0 | 66 | 65 | 78 | 46 | 18 | 3 | 0 | 0 | 80 | 280 | 275 | 140 | 8 | 0 | 14 | 5 | 0 | 51 | 0 | 41 | 43 | 17 | 8 | 33 | 20 | 138 | 154 | 72 | 19 | 2.5 | 91 | 30 | 47 | 48 | 110 | 99 | 40 | 82 | 0 | 130 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 253 | 0 | 0 | 184 | 0 | 113 | 20.33 | 100 | 58 | 97 | 0 | 65 | 85 | 0 | 5.5 | 307 | 1 | 0 | 114 | 113 | 100 | 0 | 104 |  | 895 | 0 | 410 | 0 | 99 | 135 | 0 | 0 | 2 | 0 | 40 | 15 | 21 | 110 | 0 | 0 | 0 | 50 | 35 | 48 | 0 | 0 | 0 | 43 | 0 | 21 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 190 | 0 | 78 | 0 | 213 | 0 | 370 | 90 | 0 | 95 | 80 | 70 | 0 | 5.4 | 90 | 0 |  | 7264.33 | 3377.4 | 10641.73 | 3337 | 895 | 1969 | 3546 | 150 | 80 | 493 | 138 | 33.73 | 0 | 93.25
13:00 | 28 | 0 | 100 | 110 | 0 | 71 | 0 | 345 | 273 |  | 0 | 450 | 138 | 93 | 97 | 55 | 272 | 0 | 0 | 0 | 96 | 93 | 116 | 12 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 28 | 33 | 25 | 51 | 0 | 45 | 35 | 0 | 0 | 25 | 25 | 0 | 0 | 0 |  | 0 | 0 | 68 | 65 | 80 | 48 | 17 | 7 | 0 | 0 | 80 | 280 | 330 | 139 | 8 | 0 | 14 | 5 | 0 | 51 | 0 | 42 | 43 | 17 | 8 | 33 | 20 | 130 | 151 | 72 | 19 | 2.5 | 90 | 30 | 50 | 48 | 110 | 98 | 40 | 84 | 0 | 130 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 253 | 0 | 0 | 183 | 0 | 112 | 20 | 100 | 85 | 100 | 0 | 45 | 85 | 0 | 5.2 | 307 | 24 | 0 | 114 | 106 | 100 | 0 | 104 |  | 896 | 0 | 410 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 40 | 90 | 19 | 110 | 0 | 0 | 0 | 50 | 35 | 48 | 0 | 0 | 0 | 43 | 0 | 21 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 165 | 0 | 54 | 0 | 211 | 0 | 340 | 90 | 0 | 95 | 89 | 70 | 0 | 5.2 | 90 | 0 |  | 7328.7 | 3362.2 | 10690.9 | 3446 | 896 | 1902 | 3575 | 150 | 80 | 479 | 130 | 32.9 | 0 | 93.26
14:00 | 28 | 0 | 100 | 110 | 0 | 72 | 0 | 342 | 303 |  | 0 | 450 | 140 | 98 | 97 | 55 | 293 | 0 | 0 | 0 | 96 | 93 | 116 | 12 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 51 | 0 | 44 | 35 | 0 | 0 | 25 | 25 | 0 | 0 | 0 |  | 0 | 0 | 68 | 65 | 78 | 50 | 17 | 7 | 0 | 0 | 100 | 280 | 280 | 30 | 8 | 0 | 25 | 5 | 0 | 51 | 0 | 42 | 43 | 17 | 8 | 33 | 0 | 148 | 136 | 72 | 19 | 1 | 90 | 30 | 53 | 48 | 130 | 102 | 40 | 84 | 0 | 130 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 253 | 0 | 0 | 183 | 0 | 113 | 17.7 | 100 | 85 | 98 | 0 | 45 | 69 | 0 | 4.7 | 307 | 35 | 0 | 114 | 109 | 100 | 0 | 104 |  | 896 | 0 | 345 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 90 | 18 | 110 | 0 | 0 | 0 | 50 | 34 | 48 | 0 | 0 | 0 | 43 | 0 | 21 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 148 | 0 | 33 | 0 | 211 | 0 | 396 | 53 | 0 | 100 | 0 | 70 | 0 | 5.3 | 90 | 200 |  | 7266.4 | 3408.3 | 10674.7 | 3231 | 896 | 1990 | 3474 | 350 | 79 | 478 | 148 | 28.7 | 0 | 93.26
15:00 | 28 | 0 | 100 | 110 | 0 | 73 | 0 | 359 | 304 |  | 0 | 450 | 150 | 100 | 97 | 55 | 303 | 0 | 0 | 0 | 96 | 93 | 116 | 12 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 20 | 33 | 33 | 51 | 0 | 44 | 35 | 0 | 0 | 25 | 27 | 0 | 0 | 0 |  | 0 | 0 | 66 | 65 | 80 | 50 | 17 | 5 | 0 | 0 | 100 | 310 | 305 | 43 | 8 | 0 | 25 | 39 | 0 | 51 | 0 | 42 | 43 | 17 | 8 | 33 | 20 | 156 | 135 | 72 | 19 | 1.7 | 90 | 30 | 50 | 48 | 130 | 106 | 40 | 84 | 0 | 130 | 18 | 0 | 10 | 310 | 24 | 8 | 0 | 248 | 0 | 0 | 182 | 0 | 115 | 14.4 | 100 | 85 | 98 | 0 | 45 | 68 | 0 | 3.6 | 307 | 34 | 0 | 114 | 108 | 100 | 0 | 104 |  | 896 | 0 | 370 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 89 | 25 | 110 | 0 | 0 | 0 | 50 | 34 | 48 | 0 | 0 | 0 | 43 | 0 | 21 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 163 | 0 | 33 | 0 | 209 | 0 | 401 | 53 | 0 | 113 | 0 | 70 | 0 | 6 | 90 | 300 |  | 7438.7 | 3571 | 11009.7 | 3380 | 896 | 2053 | 3494 | 450 | 79 | 476 | 156 | 25.7 | 0 | 93.26
16:00 | 28 | 0 | 100 | 110 | 0 | 73 | 0 | 353 | 303 |  | 0 | 450 | 145 | 100 | 97 | 55 | 298 | 0 | 0 | 0 | 98 | 93 | 82 | 12 | 0 | 0 | 0 | 42 | 55 | 55 | 22 | 25 | 20 | 33 | 25 | 51 | 0 | 42 | 35 | 0 | 0 | 25 | 40 | 0 | 0 | 0 |  | 0 | 0 | 66 | 65 | 80 | 50 | 20 | 8 | 0 | 0 | 100 | 280 | 280 | 46 | 8 | 0 | 30 | 39 | 0 | 51 | 0 | 41 | 43 | 17 | 8 | 33 | 20 | 154 | 135 | 72 | 19 | 1.2 | 88 | 30 | 53 | 48 | 130 | 98 | 40 | 84 | 0 | 130 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 252 | 0 | 0 | 182 | 0 | 115 | 9.4 | 90 | 48 | 102 | 0 | 45 | 68 | 0 | 2.5 | 307 | 34 | 0 | 70 | 105 | 100 | 0 | 104 |  | 895 | 0 | 345 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 89 | 24 | 110 | 0 | 0 | 0 | 50 | 34 | 48 | 0 | 0 | 0 | 43 | 0 | 0 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 163 | 0 | 33 | 0 | 209 | 0 | 402 | 35 | 0 | 113 | 0 | 69 | 0 | 2.2 | 95 | 350 |  | 7228.1 | 3556.2 | 10784.3 | 3295 | 895 | 2027 | 3380 | 500 | 77 | 441 | 154 | 15.3 | 0 | 93.27
17:00 | 28 | 0 | 100 | 110 | 0 | 73 | 0 | 344 | 302 |  | 0 | 450 | 138 | 75 | 97 | 55 | 287 | 0 | 0 | 0 | 72 | 93 | 82 | 17 | 0 | 0 | 0 | 17 | 55 | 55 | 22 | 25 | 28 | 0 | 25 | 8 | 0 | 42 | 35 | 0 | 0 | 8 | 40 | 0 | 0 | 0 |  | 0 | 0 | 51 | 20 | 80 | 50 | 20 | 16 | 0 | 0 | 100 | 280 | 280 | 48 | 8 | 0 | 30 | 42 | 0 | 51 | 0 | 41 | 43 | 17 | 11 | 17 | 20 | 148 | 137 | 72 | 19 | 0.4 | 89 | 30 | 53 | 48 | 163 | 100 | 40 | 85 | 0 | 140 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 250 | 0 | 0 | 182 | 0 | 113 | 3.6 | 70 | 32 | 103 | 0 | 45 | 68 | 0 | 0.6 | 252 | 34 | 0 | 50 | 65 | 100 | 0 | 104 |  | 887 | 0 | 345 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 8 | 89 | 20 | 80 | 0 | 0 | 0 | 50 | 34 | 48 | 0 | 0 | 0 | 25 | 0 | 20 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 157 | 0 | 33 | 0 | 208 | 0 | 396 | 35 | 0 | 35 | 0 | 70 | 0 | 0.8 | 70 | 440 |  | 6864.6 | 3457.8 | 10322.4 | 3247 | 887 | 2081 | 2861 | 590 | 77 | 426 | 148 | 5.4 | 0 | 93.27
18:00 | 28 | 0 | 100 | 110 | 0 | 52 | 0 | 340 | 251 |  | 0 | 300 | 125 | 75 | 97 | 55 | 257 | 0 | 0 | 0 | 72 | 93 | 82 | 25 | 0 | 0 | 0 | 17 | 55 | 55 | 22 | 25 | 28 | 0 | 33 | 8 | 0 | 42 | 35 | 0 | 0 | 8 | 58 | 0 | 0 | 0 |  | 0 | 0 | 66 | 20 | 84 | 50 | 20 | 10 | 0 | 0 | 100 | 280 | 280 | 94 | 8 | 0 | 35 | 42 | 0 | 51 | 0 | 48 | 43 | 20 | 11 | 17 | 20 | 134 | 136 | 72 | 19 | 0 | 91 | 30 | 11 | 10 | 110 | 75 | 40 | 10 | 0 | 140 | 18 | 0 | 10 | 270 | 24 | 8 | 0 | 250 | 0 | 25 | 150 | 0 | 113 | 0.3 | 70 | 32 | 100 | 0 | 45 | 68 | 0 | 0 | 212 | 17 | 0 | 50 | 65 | 100 | 0 | 104 |  | 890 | 0 | 295 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 8 | 89 | 21 | 80 | 0 | 0 | 0 | 50 | 34 | 48 | 0 | 0 | 35 | 25 | 32 | 20 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 151 | 0 | 33 | 0 | 140 | 0 | 289 | 35 | 0 | 35 | 0 | 78 | 0 | 0.2 | 70 | 400 |  | 6356.3 | 3265.2 | 9621.5 | 3145 | 890 | 1509 | 2801 | 550 | 77 | 515 | 134 | 0.5 | 0 | 93.27
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 28 | 0 | 100 | 110 | 0 | 73 | 0 | 353 | 347 |  | 0 | 380 | 145 | 85 | 97 | 55 | 307 | 0 | 0 | 0 | 90 | 93 | 149 | 53 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 36 | 0 | 42 | 35 | 0 | 0 | 15 | 81 | 0 | 0 | 0 |  | 0 | 0 | 102 | 60 | 77 | 50 | 20 | 26 | 0 | 0 | 100 | 285 | 255 | 114 | 8 | 90 | 34 | 43 | 0 | 51 | 0 | 48 | 43 | 20 | 10 | 17 | 0 | 170 | 153 | 72 | 19 | 0 | 91 | 30 | 53 | 35 | 163 | 109 | 65 | 87 | 0 | 140 | 18 | 0 | 10 | 280 | 24 | 11 | 80 | 253 | 77 | 50 | 170 | 55 | 113 | 0 | 100 | 65 | 100 | 0 | 70 | 104 | 0 | 0 | 235 | 0 | 0 | 108 | 95 | 100 | 0 | 104 |  | 889 | 0 | 405 | 0 | 115 | 180 | 0 | 0 | 0 | 0 | 40 | 89 | 31 | 80 | 0 | 0 | 0 | 50 | 34 | 96 | 0 | 0 | 43 | 28 | 31 | 21 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 173 | 0 | 78 | 40 | 171 | 0 | 410 | 105 | 0 | 68 | 0 | 87 | 0 | 0 | 90 | 460 |  | 7834 | 3986 | 11820 | 3568 | 889 | 2107 | 3666 | 610 | 77 | 733 | 170 | 0 | 0 | 93.28
19:30 | 28 | 0 | 100 | 110 | 0 | 73 | 0 | 342 | 348 |  | 0 | 420 | 148 | 100 | 97 | 55 | 309 | 0 | 0 | 0 | 100 | 93 | 149 | 100 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 51 | 0 | 42 | 35 | 0 | 0 | 25 | 97 | 0 | 0 | 0 |  | 0 | 0 | 102 | 60 | 85 | 50 | 20 | 28 | 0 | 0 | 100 | 280 | 255 | 114 | 8 | 95 | 34 | 44 | 0 | 51 | 0 | 48 | 43 | 20 | 10 | 17 | 18 | 170 | 152 | 72 | 19 | 0 | 91 | 30 | 53 | 49 | 163 | 130 | 65 | 87 | 0 | 140 | 18 | 0 | 10 | 300 | 24 | 11 | 80 | 253 | 77 | 50 | 200 | 55 | 113 | 0 | 100 | 100 | 106 | 0 | 115 | 103 | 0 | 0 | 235 | 0 | 0 | 108 | 113 | 100 | 0 | 104 |  | 889 | 0 | 405 | 0 | 115 | 190 | 0 | 0 | 0 | 0 | 40 | 89 | 31 | 110 | 0 | 0 | 0 | 50 | 34 | 98 | 0 | 0 | 44 | 43 | 31 | 21 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 191 | 0 | 77 | 100 | 180 | 0 | 408 | 105 | 0 | 113 | 0 | 100 | 0 | 0 | 103 | 490 |  | 8198 | 4229 | 12427 | 3640 | 889 | 2182 | 4083 | 640 | 77 | 746 | 170 | 0 | 0 | 0
20:00 | 28 | 0 | 100 | 110 | 0 | 73 | 0 | 342 | 351 |  | 0 | 420 | 120 | 100 | 97 | 55 | 242 | 0 | 0 | 0 | 98 | 93 | 149 | 100 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 42 | 35 | 0 | 0 | 25 | 112 | 0 | 0 | 0 |  | 0 | 0 | 102 | 60 | 85 | 50 | 20 | 30 | 0 | 0 | 100 | 280 | 250 | 195 | 8 | 90 | 34 | 25 | 0 | 51 | 0 | 50 | 43 | 20 | 10 | 17 | 18 | 168 | 154 | 72 | 19 | 0 | 91 | 30 | 53 | 49 | 163 | 167 | 64 | 87 | 0 | 140 | 18 | 0 | 10 | 280 | 24 | 11 | 60 | 250 | 76 | 50 | 200 | 56 | 113 | 0 | 100 | 100 | 107 | 0 | 115 | 103 | 0 | 0 | 234 | 0 | 0 | 108 | 113 | 100 | 0 | 104 |  | 889 | 0 | 410 | 0 | 115 | 190 | 0 | 0 | 0 | 0 | 40 | 79 | 32 | 110 | 0 | 0 | 0 | 50 | 34 | 96 | 0 | 0 | 47 | 43 | 31 | 21 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 184 | 0 | 77 | 100 | 180 | 0 | 358 | 105 | 50 | 113 | 15 | 99 | 0 | 0 | 108 | 490 |  | 8176 | 4238 | 12414 | 3693 | 889 | 2099 | 4099 | 640 | 77 | 749 | 168 | 0 | 0 | 93.28
21:00 | 28 | 0 | 100 | 110 | 0 | 73 | 0 | 340 | 354 |  | 0 | 420 | 130 | 100 | 97 | 55 | 282 | 0 | 0 | 0 | 100 | 93 | 149 | 100 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 0 | 33 | 51 | 0 | 42 | 35 | 0 | 0 | 25 | 173 | 0 | 0 | 0 |  | 0 | 0 | 102 | 60 | 83 | 50 | 20 | 36 | 0 | 0 | 80 | 280 | 255 | 212 | 8 | 85 | 34 | 10 | 0 | 51 | 0 | 50 | 43 | 20 | 10 | 17 | 21 | 172 | 155 | 72 | 20 | 0 | 91 | 30 | 53 | 49 | 163 | 160 | 62 | 87 | 0 | 140 | 18 | 0 | 10 | 270 | 24 | 11 | 0 | 250 | 31 | 0 | 200 | 0 | 113 | 0 | 100 | 50 | 105 | 0 | 115 | 103 | 0 | 0 | 234 | 0 | 0 | 114 | 113 | 100 | 0 | 104 |  | 898 | 0 | 410 | 0 | 115 | 190 | 0 | 0 | 0 | 0 | 40 | 90 | 33 | 110 | 0 | 0 | 0 | 50 | 34 | 96 | 0 | 0 | 44 | 43 | 31 | 21 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 177 | 0 | 77 | 100 | 180 | 0 | 388 | 105 | 50 | 113 | 15 | 106 | 0 | 0 | 108 | 500 |  | 7976 | 4296 | 12272 | 3756 | 898 | 2114 | 3859 | 650 | 77 | 746 | 172 | 0 | 0 | 93.28
22:00 | 28 | 0 | 98 | 110 | 0 | 73 | 0 | 340 | 304 |  | 0 | 370 | 135 | 100 | 97 | 55 | 310 | 0 | 0 | 0 | 100 | 93 | 149 | 29 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 0 | 33 | 51 | 0 | 42 | 35 | 0 | 0 | 25 | 213 | 0 | 0 | 0 |  | 0 | 0 | 102 | 60 | 81 | 50 | 20 | 36 | 0 | 0 | 80 | 280 | 255 | 210 | 8 | 95 | 35 | 10 | 0 | 51 | 0 | 50 | 43 | 20 | 10 | 33 | 21 | 176 | 140 | 72 | 20 | 0 | 91 | 30 | 53 | 49 | 130 | 223 | 61 | 87 | 0 | 140 | 18 | 0 | 10 | 275 | 24 | 11 | 0 | 253 | 35 | 0 | 200 | 0 | 113 | 0 | 100 | 50 | 105 | 0 | 115 | 103 | 0 | 0 | 215 | 0 | 0 | 114 | 113 | 100 | 0 | 104 |  | 898 | 0 | 390 | 0 | 115 | 190 | 0 | 0 | 0 | 0 | 40 | 90 | 35 | 110 | 0 | 0 | 0 | 50 | 34 | 96 | 0 | 0 | 43 | 43 | 31 | 21 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 178 | 0 | 77 | 100 | 204 | 0 | 414 | 105 | 10 | 113 | 15 | 106 | 0 | 0 | 109 | 510 |  | 7910 | 4299 | 12209 | 3899 | 898 | 2014 | 3740 | 660 | 77 | 745 | 176 | 0 | 0 | 93.29
23:00 | 28 | 0 | 100 | 110 | 0 | 73 | 0 | 346 | 302 |  | 0 | 370 | 150 | 100 | 97 | 55 | 310 | 0 | 0 | 0 | 100 | 84 | 149 | 25 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 43 | 35 | 0 | 0 | 25 | 216 | 0 | 0 | 0 |  | 0 | 0 | 102 | 60 | 85 | 50 | 20 | 41 | 0 | 0 | 80 | 300 | 270 | 194 | 8 | 96 | 35 | 10 | 0 | 51 | 0 | 50 | 43 | 20 | 10 | 33 | 20 | 178 | 140 | 72 | 20 | 0 | 91 | 30 | 53 | 49 | 130 | 178 | 61 | 87 | 0 | 140 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 253 | 33 | 0 | 200 | 0 | 113 | 0 | 100 | 50 | 108 | 0 | 115 | 103 | 0 | 0 | 216 | 0 | 0 | 114 | 113 | 100 | 0 | 104 |  | 898 | 0 | 370 | 0 | 115 | 190 | 0 | 0 | 0 | 0 | 40 | 90 | 36 | 110 | 0 | 0 | 0 | 50 | 34 | 96 | 0 | 0 | 43 | 43 | 31 | 22 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 193 | 0 | 78 | 100 | 212 | 0 | 406 | 70 | 0 | 113 | 15 | 106 | 0 | 0 | 90 | 520 |  | 7967 | 4243 | 12210 | 3920 | 898 | 2037 | 3684 | 670 | 78 | 745 | 178 | 0 | 0 | 93.29
24:00 | 28 | 0 | 100 | 110 | 0 | 72 | 0 | 361 | 352 |  | 0 | 370 | 135 | 100 | 97 | 55 | 291 | 0 | 0 | 0 | 100 | 84 | 149 | 25 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 45 | 35 | 0 | 0 | 25 | 216 | 0 | 0 | 0 |  | 0 | 0 | 102 | 60 | 88 | 50 | 20 | 42 | 0 | 0 | 80 | 280 | 250 | 176 | 8 | 89 | 35 | 10 | 0 | 51 | 0 | 50 | 43 | 20 | 10 | 33 | 21 | 172 | 140 | 72 | 20 | 0 | 91 | 30 | 53 | 49 | 130 | 188 | 61 | 87 | 0 | 140 | 18 | 0 | 10 | 310 | 24 | 11 | 0 | 253 | 0 | 0 | 200 | 0 | 113 | 0 | 100 | 50 | 107 | 0 | 115 | 103 | 0 | 0 | 216 | 0 | 0 | 114 | 113 | 100 | 0 | 104 |  | 898 | 0 | 345 | 0 | 115 | 190 | 0 | 0 | 0 | 0 | 40 | 90 | 34 | 110 | 0 | 0 | 0 | 50 | 34 | 96 | 0 | 0 | 43 | 43 | 31 | 22 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 196 | 0 | 77 | 100 | 213 | 0 | 415 | 70 | 0 | 113 | 0 | 106 | 0 | 0 | 90 | 520 |  | 7919 | 4213 | 12132 | 3841 | 898 | 2103 | 3623 | 670 | 80 | 745 | 172 | 0 | 0 | 93.29
KWH | 562000 | 0 | 2391000 | 2661750 | 0 | 1711409 | 0 | 8448950 | 7797000 |  | 0 | 9235750 | 3324044 | 2387520 | 2030544 | 1226669 | 7076894 | 0 | 0 | 0 | 2336640 | 2219184 | 2564640 | 605775 | 0 | 0 | 0 | 1189800 | 1236451 | 973225 | 477576 | 600000 | 647460 | 626000 | 759500 | 806268 | 0 | 1068742 | 852000 | 0 | 0 | 371966 | 2254147 | 0 | 1030111 | 0 |  | 0 | 0 | 1211728 | 858120 | 1704000 | 889440 | 436896 | 534720 | 0 | 0 | 1372466 | 7288000 | 6760000 | 2192000 | 200727 | 507070 | 649296 | 689280 | 0 | 814218 | 0 | 599920 | 809597 | 444312 | 225720 | 712700 | 468780 | 3690240 | 3493000 | 1632960 | 425412 | 15300 | 2123000 | 722160 | 1178400 | 1143000 | 3517118 | 3482000 | 1320672 | 1965120 | 0 | 3081300 | 413000 | 0 | 245880 | 7171700 | 571080 | 201264 | 122688 | 5991706 | 302034 | 103579 | 4557600 | 145122 | 2717280 | 151470 | 2334720 | 1099200 | 1552290 | 0 | 1788000 | 1704948 | 0 | 39721 | 6112145 | 191368 | 148036 | 1753320 | 2599800 | 2414400 | 0 | 2615040 |  | 21463273 | 0 | 8778816 | 0 | 2474880 | 3461760 | 0 | 0 | 0 | 0 | 660375 | 1872160 | 684552 | 1742016 | 0 | 0 | 0 | 773920 | 442074 | 1162392 | 0 | 0 | 349900 | 676320 | 275135 | 481920 | 253728 | 251838 | 0 | 0 | 3689800 | 0 | 0 | 0 | 0 | 4257418 | 0 | 1629747 | 552960 | 5154773 | 0 | 8850818 | 1232640 | 118742 | 1910112 | 242640 | 1919040 | 0 | 37358 | 2172192 | 10170600 |  | 173679078 | 87743899 | 261422977 | 84740521 | 21463273 | 48105087 | 76557396 | 13860400 | 1920742 | 10841469 | 3690240 | 243849 | 0
Fuel Cost | 921680 | 0 | 3490860 | 3912772.5 | 0 | 2259059.88 | 0 | 8533439.5 | 8030910 |  | 0 | 10066967.5 | 3689688.84 | 18121276.8 | 13990448.16 | 10377619.74 | 7359969.76 | 0 | 0 | 0 | 17594899.2 | 20238958.08 | 25236057.6 | 5585245.5 | 0 | 0 | 0 | 8685540 | 9557766.23 | 9595998.5 | 358182 | 450000 | 0 | 0 | 0 | 7796611.56 | 0 | 288560.34 | 230040 | 0 | 0 | 3455564.14 | 2457020.23 | 0 | 1751188.7 | 0 |  | 0 | 0 | 11753761.6 | 8195046 | 14824800 | 7044364.8 | 550488.96 | 1588118.4 | 0 | 0 | 2017525.02 | 5393120 | 6760000 | 2016640 | 258937.83 | 583130.5 | 733704.48 | 964992 | 0 | 1392312.78 | 0 | 6059192 | 7731651.35 | 564276.24 | 169290 | 1247225 | 351585 | 27676800 | 3702580 | 14827276.8 | 540273.24 | 243882 | 3481720 | 1155456 | 2097552 | 1783080 | 4009514.52 | 3621280 | 2601723.84 | 3753379.2 | 0 | 5330649 | 904470 | 0 | 501595.2 | 7243417 | 428310 | 152960.64 | 2086922.88 | 45297297.36 | 5128537.32 | 1731840.88 | 23699520 | 2426439.84 | 26738035.2 | 1770684.3 | 19027968 | 11926320 | 10943644.5 | 0 | 16306560 | 16111758.6 | 0 | 0 | 46207816.2 | 1666815.28 | 1301236.44 | 17498133.6 | 22280286 | 16079904 | 0 | 0 |  | 123628452.48 | 0 | 9217756.8 | 0 | 19452556.8 | 47979993.6 | 0 | 0 | 0 | 0 | 6881107.5 | 2115540.8 | 1061055.6 | 17002076.16 | 0 | 0 | 0 | 7615372.8 | 4491471.84 | 10287169.2 | 0 | 0 | 3390531 | 6553540.8 | 2668809.5 | 925286.4 | 393278.4 | 190641.366 | 0 | 0 | 19998716 | 0 | 0 | 0 | 0 | 5619791.76 | 0 | 2444620.5 | 9405849.6 | 6031084.41 | 0 | 8762309.82 | 12868761.6 | 2019801.42 | 18126962.88 | 2290521.6 | 14891750.4 | 0 | 412805.9 | 16052498.88 | 44648934 |  | 656522126.56 | 427429049.816 | 1083951176.376 | 94716335.746 | 123628452.48 | 57536387.03 | 593317219.44 | 64647650 | 518600.34 | 119482359.14 | 27676800 | 2427372.2 | 0
Yesterday Day Peak | 28 | 0 | 100 | 110 | 0 | 71 | 0 | 341 | 303 |  | 0 | 450 | 140 | 100 | 97 | 55 | 272 | 0 | 0 | 0 | 95 | 93 | 116 | 12 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 28 | 25 | 25 | 51 | 0 | 45 | 35 | 0 | 0 | 25 | 24 | 0 | 0 | 0 |  | 0 | 0 | 66 | 65 | 78 | 46 | 18 | 3 | 0 | 0 | 80 | 280 | 275 | 140 | 8 | 0 | 14 | 5 | 0 | 51 | 0 | 41 | 43 | 17 | 8 | 33 | 20 | 138 | 154 | 72 | 19 | 2.5 | 91 | 30 | 47 | 48 | 110 | 99 | 40 | 82 | 0 | 130 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 253 | 0 | 0 | 184 | 0 | 113 | 20.33 | 100 | 58 | 97 | 0 | 65 | 85 | 0 | 5.5 | 307 | 1 | 0 | 114 | 113 | 100 | 0 | 104 |  | 895 | 0 | 410 | 0 | 99 | 135 | 0 | 0 | 2 | 0 | 40 | 15 | 21 | 110 | 0 | 0 | 0 | 50 | 35 | 48 | 0 | 0 | 0 | 43 | 0 | 21 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 190 | 0 | 78 | 0 | 213 | 0 | 370 | 90 | 0 | 95 | 80 | 70 | 0 | 5.4 | 90 | 0 |  | 10641.73 | DayPeak
Yesterday Evening Peak | 28 | 0 | 100 | 110 | 0 | 73 | 0 | 342 | 348 | 0 | 0 | 420 | 148 | 100 | 97 | 55 | 309 | 0 | 0 | 0 | 100 | 93 | 149 | 100 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 51 | 0 | 42 | 35 | 0 | 0 | 25 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 60 | 85 | 50 | 20 | 28 | 0 | 0 | 100 | 280 | 255 | 114 | 8 | 95 | 34 | 44 | 0 | 51 | 0 | 48 | 43 | 20 | 10 | 17 | 18 | 170 | 152 | 72 | 19 | 0 | 91 | 30 | 53 | 49 | 163 | 130 | 65 | 87 | 0 | 140 | 18 | 0 | 10 | 300 | 24 | 11 | 80 | 253 | 77 | 50 | 200 | 55 | 113 | 0 | 100 | 100 | 106 | 0 | 115 | 103 | 0 | 0 | 235 | 0 | 0 | 108 | 113 | 100 | 0 | 104 |  | 889 | 0 | 405 | 0 | 115 | 190 | 0 | 0 | 0 | 0 | 40 | 89 | 31 | 110 | 0 | 0 | 0 | 50 | 34 | 98 | 0 | 0 | 44 | 43 | 31 | 21 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 191 | 0 | 77 | 100 | 180 | 0 | 408 | 105 | 0 | 113 | 0 | 100 | 0 | 0 | 103 | 490 |  | 12427 | EvPeak
Forecast for Evening | 28 | 0 | 100 | 110 | 0 | 90 | 0 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 96 | 55 | 335 | 0 | 0 | 0 | 100 | 93 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 42 | 35 | 0 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 0 |  | 100 | 100 | 95 | 50 | 21 | 40 | 0 | 0 | 100 | 360 | 360 | 225 | 8 | 100 | 36 | 50 | 0 | 51 | 0 | 44 | 43 | 21 | 11 | 33 | 20 | 173 | 160 | 72 | 22 | 0 | 90 | 30 | 51 | 44 | 163 | 210 | 66 | 86 | 0 | 140 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 133 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 104 |  | 942 | 16 | 410 | 0 | 115 | 225 | 0 | 0 | 30 | 60 | 40 | 65 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 0 | 50 | 50 | 43 | 32 | 22 | 11 | 11 | 0 | 0 | 150 | 0 | 10 | 0 | 0 | 220 | 0 | 80 | 100 | 220 | 0 | 414 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 490
Forecast for Day | 28 | 0 | 100 | 110 | 0 | 90 | 0 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 96 | 55 | 335 | 0 | 0 | 0 | 100 | 93 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 42 | 35 | 0 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 0 |  | 100 | 100 | 95 | 50 | 21 | 30 | 0 | 0 | 80 | 360 | 360 | 225 | 8 | 100 | 35 | 50 | 0 | 51 | 0 | 0 | 43 | 21 | 11 | 33 | 20 | 157 | 157 | 72 | 22 | 1.6 | 90 | 30 | 51 | 44 | 163 | 210 | 66 | 86 | 0 | 140 | 18 | 0 | 10 | 341 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 100 | 133 | 20 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 104 |  | 942 | 0 | 410 | 0 | 115 | 225 | 0 | 0 | 0 | 0 | 40 | 65 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 50 | 0 | 43 | 0 | 22 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 |  | 80 | 80 | 220 | 0 | 414 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 450
Generation at 08:00(Today) | 28 | 0 | 102 | 110 | 0 | 72 | 0 | 341 | 303 | 0 | 0 | 340 | 120 |  | 30 | 30 | 266 | 0 | 0 | 0 | 50 | 93 | 0 | 12 | 0 | 0 | 0 | 17 | 17 | 0 | 22 | 25 | 20 | 33 | 33 | 0 | 0 | 41 | 35 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 19 | 20 | 35 | 0 | 0 | 80 | 280 | 250 | 176 | 8 | 86 | 28 | 47 | 0 | 43 | 0 | 0 | 0 | 20 | 8 | 25 | 0 | 114 | 156 | 32 | 20 | 1.1 | 91 | 30 | 47 | 49 | 130 | 188 | 67 | 88 | 0 | 140 | 18 | 0 | 10 | 285 | 24 | 8 | 0 | 95 | 0 | 0 | 200 | 0 | 71 | 0 | 50 | 0 | 20 | 0 | 8 | 16 | 0 | 2.4 | 144 | 0 | 0 | 0 | 65 | 100 | 0 | 53 | 0 | 904 | 0 | 345 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 153 | 0 | 32 | 0 | 170 | 0 | 321 | 0 | 0 | 0 | 0 | 34 | 0 | 1.8 | 50 | 450 | 0
199
| Minimum Generation |  | 9015.2 | 8:00
| Highest Generation |  | 12427 | 19:30
| Day Peak Generation |  | 10641.73 | 12:00
| Evening Peak Generation |  | 12427 | 19:30
| HVDC Max Flow |  | 904 | 1:00
| HVDC EvPeak Flow |  | 889 | 19:30
| Load factor L.F |  | 87.65%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-09-04
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-09-03 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10641.73 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 8804.3 | MW
Evening Peak Generation : |  | 12427 | MW Hour : | 19:30 | Available Max Generation : |  | 14870 | MW
E.P. Demand (at gen end) : |  | 12427 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 11800 | MW
Maximum Generation : |  | 12427 | MW Hour : | 19:30 | Reserve(Generation end) |  | 3070 | MW
Total Gen. (MKWH) : |  | 261.423 | System Load Factor : | 87.65% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 20 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-09-04
Actual : | 93.31 | Ft.(MSL) , | Rule curve : | 99.69 | Ft.( MSL )
Gas Consumed : | Total = | 1084.28 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 152252722.776
: |  | Coal : | 64647650 | Oil : | 712799578.58 | Total : | 929699951.356
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4222.9783 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1438.0404 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1288.7918 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1164.6582 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1052.4152 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 849.2669 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 472.3023 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 218.5955 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 655.0091 |  |  | 0 | 0%
Total | 0 |  | 11362.0576 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 10) Sikalbaha 150 MW
|  |  |  | 2) Bibiyana #3 | 11) Payra Unit-1
3) Ghorasal Unit-2,3,7
4) Ashuganj unit-3,4
5) Bhola-225 MW GT-2 & ST
6) Kaptai-1,2,5
7) Raozan #1,2
8) Sirajganj #1
9) Baghabari-71 & 100 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Payra unit-2 tripped at 09:45 and was synchronized at 13:17.
b) Kabirpur-Manikganj 132 kV Ckt-2 was under shut down from 09:05 to 16:10 for C/M. |  |  |  |  | About 15 MW power interruption occurred under Kabirpur S/S area
from 09:05 to 16:10.
c) Hathazari-Kaptai 132 kV Ckt-1 tripped at 12:13 from both end showing Dist. Z1,Y,B phase
relays and was switched on at 12:27.
d) Baraulia 132/33 kV T1 transformer was under shut down from 10:10 to 11:45 due to DC System
up gradation.
e) Baraulia 132/33 kV T2 transformer was under shut down from 12:20 to 12:30 due to DC System
up gradation.
f) Bhola 225 MW ST was synchronized at 12:16.
g) Faridpur-Bheramara 132 kV Ckt-1 was under shut down from 15:04 to 15:59 for C/M.
h) Halishar-Rampur 132 kV Ckt-2 was under shut down from 15:34 to 19:25 for C/M.
i) Ashuganj 225 MW STG was synchronized at 17:33.
j) Chandpur 150 MW GT was synchronized at 18:08.
k) Sikalbaha 225 MW CCPP STG was synchronized at 17:54.
l) Shahzibazar 330 MW CCPP GT-1 was synchronized at 17:50.
m) Tongi 132/33 kV T1 & T2 transformers tripped at 20:04 due to 33 kV incoming CT, PT & CB of T1 |  |  |  |  | About 122 MW power interruption occurred under Tongi S/S area
transformer burn and T2 was switched on at 20:30. |  |  |  |  | from 20:04 to 20:30.
n) Bottail 132/33 kV T1 transformer was under shut down from 06:32(04/09/2020) to 06:57(04/06/2020) |  |  |  |  | About 50 MW power interruption occurred under Bottail S/S area
due to red hot maintenance at DS of 33 kV incoming bus. |  |  |  |  | from 06:32(04/09/2020) to 06:57(04/09/2020).
o) Faridpur 33 kV Bus section-4 was under shut down from 07:07(04/09/2020) to 08:17(04/09/2020) |  |  |  |  | About 30 MW power interruption occurred under Faridpur S/S area
due to 33 kV CB commissioning. |  |  |  |  | from 07:07(04/09/2020) to 08:17(04/09/2020).
p) Cumilla(N) 33 kV Bus was under shut down from 07:24(04/09/2020) to 08:42(04/09/2020) due to red |  |  |  |  | About 43 MW power interruption occurred under Cumilla(N) S/S area
hot maintenance at 33kv incomer. |  |  |  |  | from 07:24(04/09/2020) to 08:42(04/09/2020).
q) Joydevpur 132/33 kV T3 transformer was under shut down from 22:28 to 22:50 due to overheating |  |  |  |  | About 20 MW power interruption occurred under Joydevpur S/S area
of B-phase . |  |  |  |  | from 22:28 to 22:50.
r) Fenchuganj 132/33 kV T2 transformer tripped at 00:06(04/09/2020) showing E/F relay at 33 kV end |  |  |  |  | About 27 MW power interruption occurred under Fenchuganj S/S area
and was switched on at 01:05(041/09/2020). |  |  |  |  | from 06:06(04/09/2020) to 01:05(04/09/2020).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-09-03 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 28 | 562000 | Unit-1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 100 | 2391000 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 110 | 2661750 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 73 | 1711409 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 342 | 8448950 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 348 | 7797000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9235750 | frequency control.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 2387520
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 148 | 3324044 | GT-1 Under S/D due to gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 97 | 2030544
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1226669
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 100 | 605775
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 477576
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 2336640
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 309 | 7076894 | frequency control.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 2219184 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel Shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 1189800
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 2564640
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1236451
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 973225
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 47 | 1247460 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 626000
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 759500
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 806268
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 253 | 5991706 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 77 | 302034 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 50 | 103579 | Low demand
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 55 | 145122 | Low demand
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 113 | 2717280 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 103 | 1704948
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2615040
| Dhaka area Total |  |  |  | 5895 | 3676 | 77475758
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 371966
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 151470
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 889440
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 77 | 1920742 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 97 | 2254147 | ST sync process.
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 1030111
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 1211728
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 60 | 858120 | Low demand
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2334720
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 436896
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 28 | 534720
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 85 | 1704000 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 39721
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 235 | 6112145 | Low demand
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 191368 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 148036 | Reserve
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2414400
| Chattogram area Total |  |  |  | 2266 | 979 | 22603730
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 100 | 1372466 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 114 | 2192000 | Machine problem
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7288000 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 255 | 6760000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 34 | 649296 | Gas shortage.
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 44 | 689280 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 814218
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 106 | 1552290 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 48 | 599920
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 95 | 507070
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 100 | 1099200 | Low demand
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 444312
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 225720
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 170 | 3690240
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 17 | 712700 | Engine problem
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 809597 | Engine problem
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 18 | 468780
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 80 | 122688 | Low demand
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 108 | 1753320
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 2599800
| Cumilla Area Total |  |  |  | 2980 | 1814 | 34551624
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 152 | 3493000 | Machine problem
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 425412
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 72 | 1632960 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 15300
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 4557600
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1788000 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 558 | 11912272
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 91 | 2123000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 722160 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3517118
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 130 | 3482000 | ST under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1178400
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 49 | 1143000
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 201264
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 65 | 1320672 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 87 | 1965120
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 140 | 3081300
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 413000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 571080
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7171700 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 245880
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1171 | 27135694
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 889 | 21463273
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 2474880
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 190 | 3461760 | Low demand
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 405 | 8778816 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 660375
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 552960
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1232640
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 242640 | Reserve
| Khulna Area Total |  |  |  | 2284 | 1844 | 38867344
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1742016
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 31 | 684552
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 89 | 1872160 | GT-2 Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 77 | 1629747 | Engine problem
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 490 | 10170600
| Barisal Area Total |  |  |  | 1054 | 797 | 16099075
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 773920
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 34 | 442074
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 44 | 349900 | Engine problem
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage.
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 191 | 4257418 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 180 | 5154773 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 408 | 8850818 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 31 | 275135
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 481920
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 11 | 253728
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 251838
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 676320 | Engine problem
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 98 | 1162392
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 118742 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 1910112
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 103 | 2172192 | Engine problem
| Rajshahi Area Total |  |  |  | 2183 | 1338 | 27131282
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3689800 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Machine problem
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 100 | 1919040 | Engine problem
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 37358
| Rangpur Area Total |  |  |  | 605 | 250 | 5646198
| Total |  |  |  | 19892 | 12427 | 261422977
| Eastern Grid Total |  |  |  | 13766 | 8198 | 173679078
| Western Grid Total |  |  |  | 6126 | 4229 | 87743899
| National Grid Total |  |  |  | 19892 | 12427 | 261422977
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-09-03
| (a) ENTIRE EASTERN GRID : |  | 8059 | MW | (b) ENTIRE WESTERN GRID : |  | 3898 | MW
| i) Dhaka area |  | 4129 | MW | i) Khulna area |  | 1504 | MW
| ii) Chittagong area |  | 1286 | MW | ii) Rajshahi area |  | 1289 | MW
| iii) Comilla area |  | 1137 | MW | iii) Barisal area |  | 346 | MW
| iv) Mymensingh area |  | 978 | MW | iv) Rangpur area |  | 759 | MW
| v) Sylhet area |  | 529 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11957 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 134 | 10:00 | Sherpur | 110 | 20:00 | Jhenida | 112 | 19:00
| Munsiganj | 124 | 22:00 | Srimongal | 49 | 21:00 | Bottail | 132 | 19:30
| Sonargaon | 91 | 19:30 | Shahjibazar | 127 | 22:00 | G.K Project | 58 | 19:30
| Shyampur | 196 | 6:00 | Fenchuganj | 51 | 19:00 | Faridpur | 192 | 0.91667
| Bhulta | 203 | 24:00 | Kulawara | 48 | 21:00 | Madaripur | 106 | 0.91667
| Madanganj | 52 | 24:00 | Sylhet | 135 | 19:00 | Sariatpur | 68 | 22:00
| Shitalakhya | 111 | 17:00 | Chatak | 31 | 19:30 | Gopalganj | 89 | 19:00
| Rahim steel | 13 | 17:00 | Sunamganj | 48 | 20:00 | Bagerhat | 101 | 19:00
| Matuail | 82 | 10:00 | Biani Bazar | 64 | 20:00 | Mongla | 48 | 1:00
| Ghorasal | 80 | 23:00 | Comilla (S) | 178 | 23:00 | Satkhira | 111 | 0.95833
| Narsingdi | 288 | 20:00 | Comilla(N) | 109 | 20:00 | Gallamari | 49 | 13:00
| Haripur (SBU) | 100 | 19:30 | Chandpur | 106 | 22:00 | Magura | 52 | 0.875
| Ullon | 68 | 19:00 | Feni | 119 | 19:00 | Norail | 41 | 19:00
| Hasnabad | 205 | 19:30 | Chowmuhani | 180 | 20:00 | Chuadanga | 93 | 20:00
| Magbazar | 104 | 12:00 | Ashuganj | 65 | 24:00 | Barisal(N) | 45 | 0.91667
| Maniknagar | 102 | 12:00 | Daudkandi | 143 | 21:00 | Barisal (S) | 98 | 0.8125
| Bangabhaban | 38 | 10:00 | B.Baria | 161 | 20:00 | Patuakhali | 123 | 0.95833
| Narinda | 94 | 17:00 | Ramganj | 117 | 23:00 | Bhandaria | 56 | 0.875
| Dhanmondi | 172 | 12:00 | Chaddagram | 38 | 20:00 | Borhan Uddin | 45 | 22:00
| Lalbag | 89 | 13:00 | PHP | 3 | 18:30 | Ishurdi | 63 | 19:00
| Madartek | 73 | 23:00 | Madunaghat | 55 | 19:00 | Ruppur Paromanobik | 2 | 7:00
| Dhaka University |  |  | Hathazari | 102 | 0.83333 | Natore | 128 | 21:00
| Fatullah | 36 | 0.41667 | Khulshi | 210 | 0.5 | Bogra | 176 | 21:00
| Mirpur | 103 | 18:00 | Halishahar | 136 | 0.58333 | Noagaon | 132 | 21:00
| Kalyanpur | 114 | 19:30 | Baraulia | 142 | 0.041667 | Rajshahi | 150 | 21:00
| Gulshan | 132 | 15:00 | Sikalbaha | 26 | 0.8125 | Rajshahi New | 11 | 21:00
| Uttara | 90 | 21:00 | Dohazari | 92 | 0.83333 | C.Nawabganj | 74 | 21:00
| Uttara New | 302 | 18:30 | Cox'sbazar | 98 | 0.91667 | Amnura | 44 | 19:30
| Kamrangirchar | 94 | 19:00 | Chandraghona | 30 | 0.77083 | Pabna | 126 | 21:00
| Savar | 133 | 17:00 | Kaptai | 4.8 | 0.79167 | Shahjadpur | 105 | 20:00
| Bhasantec | 150 | 19:30 | A. Khaer Stl. | 18 | 0.45833 | Serajganj | 102 | 21:00
| Agargaon | 73 | 13:00 | Bakulia | 104 | 0.45833 | Niyamatpur | 60 | 21:00
| Satmosjid | 83 | 19:00 | Julda | 24 | 0.58333 | Joypurhat | 56 | 20:00
| Tongi | 127 | 0.625 | TK chemical | 29 | 0.83333 | Sherpur(Bogura) | 49 | 19:30
| Kabirpur | 222 | 15:00 | Modern Steel | 18 | 0.25 | Mohastangor | 52 | 21:00
| Basundhara | 136 | 14:00 | Shahmirpur | 23 | 0 | Rangpur | 147 | 1:00
| Manikganj | 74 | 0.91667 | Khagrachhari | 26 | 0.54167 | Lalmonirhat | 61 | 1:00
| Joydevpur | 115 | 23:00 | Matarbari | 33 | 0.8125 | Saidpur | 108 | 19:30
| New Tongi | 110 | 21:00 | Baroiar Hat | 38 | 0.77083 | Purbasadipur | 103 | 1:00
| Korda | 269 | 16:00 | Rangamati | 12 | 0.77083 | Thakurgaon | 90 | 20:00
| Dhamrai | 90 | 21:00 | Abul Khair 230 | 110 | 0.95833 | Palashbari | 127 | 1:00
| Rajendrapur | 98 | 21:00 | BSRM | 104 | 0.20833 | Barapukuria | 53 | 21:00
| Valuka | 118 | 15:00 | GPH Ispat | 75 | 0.8125 | Panchagar | 51 | 21:00
| Tangail | 208 | 21:00 | Goalpara | 29 | 0.79167 | Joldhaka | 30 | 19:30
| Mymensing | 232 | 21:00 | Central s/s | 90 | 20:00 | Kurigram | 53 | 19:30
| Kishorganj | 143 | 20:00 | Noapara | 60 | 21:00
| Netrokona | 115 | 19:30 | Jessore | 114 | 19:30
| Jamalpur | 141 | 21:00 | Benapol | 50 | 20:00
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-09-03 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 397 | 6:00 | 389 | 15:00 | Kaliakoir | 383 | #REF! | 369 | 0.625
| Bheramara | 395 | 7:00 | 388 | 20:00 | Bhulta | 392 | 0.25 | 381 | 0.70833
| Ashuganj(N) | 396 | 6:00 | 388 | 17:00 | Gopalganj | 415 | 0.33333 | 396 | 0.875
| Payra | 415 | 7:00 | 404 | 21:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 1:00 | 235 | 1:00 | Comilla (N) | 235 | 12:00 | 231 | 17:00
| Ishurdi | 235 | 18:00 | 225 | 4:00 | Hathazari | 231 | 11:00 | 221 | 8:00
| Ashuganj | 239 | 14:00 | 234 | 21:00 | Megnaghat | 233 | 5:00 | 229 | 12:00
| Serajganj | 232 | 18:00 | 226 | 19:30 | Fenchuganj | 239 | 5:00 | 234 | 18:30
| Baghabari | 242 | 18:00 | 229 | 11:00 | Siddhirganj | 232 | 3:00 | 227 | 16:00
| Barapukuria | 236 | 18:00 | 225 | 22:00 | Maniknagar | 231 | 6:00 | 225 | 16:00
| Bogra | 227 | 18:00 | 213 | 21:00 | Agargaon | 228 | 2:00 | 220 | 16:00
| Rajshahi | 227 | 18:00 | 215 | 4:00 | Barisal | 246 | 7:00 | 237 | 18:30
| Khulna South | 240 | 18:00 | 228 | 2:00 | AKSML | 229 | 11:00 | 214 | 5:00
| Rampura | 230 | 3:00 | 222 | 16:00 | BSRM | 227 | 11:00 | 216 | 5:00
| Haripur | 231 | 4:00 | 225 | 16:00 | Bibiyana | 238 | 6:00 | 232 | 11:00
| Hasnabad | 230 | 19:00 | 224 | 16:00 | Bhulta | 232 | 19:00 | 226 | 17:00
| Shyampur | 227 | 6:00 | 221 | 16:00 | Ashuganj (S) | 236 | 18:00 | 231 | 17:00
| Aminbazar | 228 | 3:00 | 222 | 16:00 | Kaliakoir | 232 | 10:00 | 225 | 6:00
| Tongi | 227 | 4:00 | 220 | 23:00 | GPH | 226 | 10:00 | 215 | 9:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 133 | 19:00 | 130 | 15:00 | Hathazari | 137 | 0.45833 | 131 | 0.16667
| Munsiganj | 135 | 19:00 | 130 | 8:00 | Khulshi | 136 | 0.54167 | 130 | 0.16667
| Sonargaon | 135 | 19:00 | 132 | 8:00 | Halishahar | 140 | 0.45833 | 133 | 0.29167
| Shyampur | 134 | 6:00 | 131 | 12:00 | Baraulia | 134 | 0.41667 | 130 | 0.20833
| Bhulta | 126 | 3:00 | 123 | 9:00 | Sikalbaha | 139 | 10:00 | 131 | 0.20833
| Madanganj | 132 | 2:00 | 130 | 7:00 | Dohazari | 136 | 13:00 | 128 | 0.20833
| Shitalakhya | 142 | 20:00 | 135 | 16:00 | Cox'sbazar | 130 | 0.54167 | 119 | 0.20833
| Rahim steal | 134 | 3:00 | 131 | 9:00 | Chandraghona | 136 | 0.41667 | 131 | 0.25
| Matuail | 133 | 19:00 | 130 | 15:00 | Kaptai | 135 | 11:00 | 132 | 0.041667
| Ghorasal | 138 | 7:00 | 136 | 1:00 | A. Khaer Stl. | 134 | 0.41667 | 130 | 4:00
| Narsinghdi | 129 | 6:00 | 125 | 1:00 | Bakulia | 137 | 0.45833 | 129 | 0.25
| Haripur (SBU) | 133 | 3:00 | 131 | 9:00 | Julda | 140 | 0.5 | 134 | 0.083333
| Ullon | 134 | 4:00 | 129 | 17:00 | TK Chemical | 138 | 0.5 | 132 | 4:00
| Hasnabad | 138 | 19:30 | 132 | 16:00 | Modern Steel | 136 | 0.41667 | 130 | 0.33333
| Magbazar | 134 | 6:00 | 128 | 12:00 | Shahmirpur | 139 | 0.5 | 132 | 0.20833
| Maniknagar | 135 | 2:00 | 129 | 17:00 | Khagrachhari | 135 | 0.54167 | 129 | 0.20833
| Bangabhaban | 135 | 2:00 | 129 | 17:00 | Matarbari | 132 | 0.54167 | 124 | 0.25
| Narinda | 135 | 2:00 | 129 | 17:00 | Baroiar Hat | 137 | 0.41667 | 130 | 0.66667
| Dhanmondi | 134 | 4:00 | 129 | 17:00 | Rangamati | 135 | 0.41667 | 130 | 5:00
| Lalbag | 138 | 20:00 | 129 | 16:00 | Goalpara S/S | 138 | 10:00 | 132 | 5:00
| Madartek | 134 | 6:00 | 128 | 15:00 | Khulna Central S/S | 138 | 0.41667 | 134 | 4:00
| Dhaka University |  |  |  |  | Noapara | 136 | 10:00 | 130 | 2:00
| Fatuiiah | 135 | 0.79167 | 131 | 9:00 | Jessore | 132 | 10:00 | 123 | 19:30
| Mirpur | 132 | 6:00 | 126 | 12:00 | Benapol | 132 | 11:00 | 121 | 22:00
| Kalyanpur | 132 | 6:00 | 128 | 12:00 | Jhenida | 129 | 0.41667 | 115 | 19:30
| Gulshan | 133 | 6:00 | 128 | 12:00 | Bottail | 134 | 10:00 | 125 | 19:30
| Uttara | 133 | 6:00 | 128 | 12:00 | G.K Project | 141 | 0.75 | 134 | 20:00
| Uttara New | 135 | 6:00 | 131 | 12:00 | Faridpur | 133 | 9:00 | 124 | 21:00
| Kamrangirchar | 134 | 5:00 | 129 | 12:00 | Madaripur | 138 | 0.29167 | 130 | 12:00
| Savar | 131 | 6:00 | 126 | 12:00 | Shariyatpur S/S | 137 | 0.29167 | 127 | 21:00
| Bhasantec | 133 | 6:00 | 127 | 17:00 | Gopalganj | 141 | 12:00 | 127 | 19:00
| Agargaon | 134 | 6:00 | 129 | 12:00 | Bagerhat | 136 | 12:00 | 129 | 7:00
| Satmosjid | 134 | 6:00 | 128 | 12:00 | Mongla | 132 | 0.5 | 124 | 6:00
| Tongi | 137 | 0.875 | 132 | 16:00 | Satkhira | 137 | 0.41667 | 129 | 22:00
| Kabirpur | 136 | 18:00 | 129 | 19:00 | Gallamari | 138 | 10:00 | 132 | 3:00
| Basundhara | 134 | 3:00 | 127 | 15:00 | Magura | 128 | 9:00 | 112 | 21:00
| Manikganj | 139 | 20:00 | 132 | 6:00 | Norail | 126 | 0.375 | 109 | 22:00
| Joydevpur | 143 | 10:00 | 132 | 12:00 | Chuadanga | 125 | 9:00 | 104 | 22:00
| New Tongi | 136 | 0.83333 | 131 | 15:00 | Barisal(N) | 139 | 6:00 | 133 | 18:30
| Kodda | 136 | 20:00 | 125 | 0.66667 | Barisal (S) | 138 | 0.29167 | 132 | 18:30
| Dhamrai | 135 | 18:00 | 128 | 21:00 | Patuakhali(S) | 134 | 0.29167 | 127 | 1:00
| Rajendrapur | 135 | 2:00 | 125 | 16:00 | Bhandaria | 131 | 12:00 | 121 | 22:00
| Valuka | 126 | 18:00 | 113 | 19:00 | Ishurdi | 137 | 11:00 | 132 | 21:00
| Tangail | 137 | 18:00 | 125 | 21:00 | Ruppur Paromanobik | 137 | 10:00 | 132 | 21:00
| Mymensing | 131 | 18:00 | 116 | 22:00 | Natore | 138 | 18:00 | 129 | 19:00
| Kishorganj | 129 | 10:00 | 119 | 20:00 | Bogra | 138 | 18:00 | 127 | 21:00
| Netrokona | 128 | 18:00 | 113 | 20:00 | Noagaon | 134 | 18:00 | 120 | 21:00
| Jamalpur | 139 | 9:00 | 130 | 18:30 | Rajshahi | 135 | 18:00 | 127 | 19:30
| Sherpur | 137 | 17:00 | 128 | 22:00 | Rajshahi New | 140 | 18:00 | 128 | 5:00
| Srimongal | 138 | 7:00 | 132 | 0.875 | C.Nawabganj | 136 | 18:30 | 125 | 19:30
| Shahjibazar | 136 | 7:00 | 129 | 0.91667 | Amnura | 137 | 18:00 | 125 | 5:00
| Fenchuganj | 136 | 6:00 | 132 | 0.041667 | Pabna | 134 | 10:00 | 125 | 5:00
| Khulawara | 134 | 7:00 | 131 | 0.77083 | Shahjadpur | 140 | 18:30 | 135 | 9:00
| Sylhet | 133 | 8:00 | 129 | 0.041667 | Serajganj | 136 | 18:00 | 127 | 21:00
| Chatak | 131 | 6:00 | 127 | 1:00 | Niyamatpur | 131 | 18:00 | 117 | 21:00
| Sunamganj | 131 | 8:00 | 124 | 0.79167 | Joypurhat | 134 | 18:00 | 119 | 21:00
| Biani Bazar | 131 | 8:00 | 125 | 0.041667 | Sherpur(Bogura) | 137 | 18:00 | 127 | 21:00
| Comilla(s) | 127 | 6:00 | 119 | 21:00 | Mohastangor | 135 | 18:00 | 124 | 19:00
| Comilla(n) | 140 | 12:00 | 136 | 7:00 | Rangpur | 129 | 18:00 | 114 | 21:00
| Chandpur | 138 | 13:00 | 127 | 6:00 | Lalmonirhat | 125 | 10:00 | 114 | 1:00
| Feni | 140 | 11:00 | 130 | 8:00 | Saidpur | 129 | 7:00 | 117 | 21:00
| Chowmuhani | 138 | 15:00 | 134 | 19:30 | Purbasadipur | 127 | 18:00 | 110 | 21:00
| Ashuganj | 137 | 7:00 | 130 | 1:00 | Thakurgaon | 126 | 18:00 | 109 | 21:00
| Daudkandi | 137 | 19:00 | 131 | 7:00 | Palashbari | 130 | 18:00 | 119 | 1:00
| B.Baria | 134 | 7:00 | 126 | 21:00 | Barapukuria | 136 | 18:00 | 126 | 1:00
| Ramganj | 136 | 13:00 | 125 | 24:00 | Panchagar | 125 | 18:00 | 105 | 21:00
| Chaddagram | 139 | 10:00 | 131 | 8:00 | Joldhaka | 128 | 18:00 | 111 | 21:00
| PHP | 138 | 10:00 | 127 | 3:00 | Kurigram | 129 | 18:00 | 110 | 21:00
| Madanhat | 139 | 11:00 | 132 | 2:00

## L-Curve
Date | 2020-09-03
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 182 | 7919 | 4213 | 12132 |  |  |  | QF-LDC-11
0:30 | 166 | 7712.5 | 4074.5 | 11787 | Date: | 2020-09-03
1:00 | 150 | 7506 | 3936 | 11442
1:30 | 117.5 | 7360 | 3822.5 | 11182.5
2:00 | 85 | 7214 | 3709 | 10923
2:30 | 97.5 | 7162.5 | 3604 | 10766.5 | [5 empty] | Gen. at Eve. Peak | 12427 | 12427 MW (19:30 )
3:00 | 110 | 7111 | 3499 | 10610 | [6 empty] | 19:30
3:30 | 95 | 7031 | 3438.5 | 10469.5 | [5 empty] | Gen. at Day Peak | 10641.73 | 10641.73 MW (12:00 )
4:00 | 80 | 6951 | 3378 | 10329 | [6 empty] | 12:00
4:30 | 95 | 6904.5 | 3381 | 10285.5 | [5 empty] | Highest Generation | 12427
5:00 | 110 | 6858 | 3384 | 10242 | [6 empty] | 19:30
5:30 | 141 | 6628.85 | 3225.5 | 9854.35
6:00 | 172 | 6399.7 | 3067 | 9466.7
6:30 | 157 | 6271.2 | 3002.7 | 9273.9
7:00 | 142 | 6142.7 | 2938.4 | 9081.1
7:30 | 241 | 6081.05 | 2967.1 | 9048.15
8:00 | 340 | 6019.4 | 2995.8 | 9015.2
8:30 | 406 | 6158 | 3093.2 | 9251.2
9:00 | 472 | 6296.6 | 3190.6 | 9487.2
9:30 | 302 | 6712.95 | 3031.3 | 9744.25
10:00 | 132 | 7129.3 | 2872 | 10001.3
10:30 | 183.5 | 7157.8 | 3014.4 | 10172.2
11:00 | 235 | 7186.3 | 3156.8 | 10343.1
11:30 | 271.5 | 7225.315 | 3267.1 | 10492.415
12:00 | 308 | 7264.33 | 3377.4 | 10641.73
12:30 | 233 | 7296.515 | 3369.8 | 10666.315
13:00 | 158 | 7328.7 | 3362.2 | 10690.9
13:30 | 204 | 7297.55 | 3385.25 | 10682.8
14:00 | 250 | 7266.4 | 3408.3 | 10674.7
14:30 | 312 | 7352.55 | 3489.65 | 10842.2
15:00 | 374 | 7438.7 | 3571 | 11009.7
15:30 | 404 | 7333.4 | 3563.6 | 10897
16:00 | 434 | 7228.1 | 3556.2 | 10784.3
16:30 | 479.5 | 7046.35 | 3507 | 10553.35
17:00 | 525 | 6864.6 | 3457.8 | 10322.4
17:30 | 521 | 6610.45 | 3361.5 | 9971.95
18:00 | 517 | 6356.3 | 3265.2 | 9621.5
18:30 | 292 | 7095.15 | 3625.6 | 10720.75
19:00 | 67 | 7834 | 3986 | 11820
19:30 | 55 | 8198 | 4229 | 12427
20:00 | 20 | 8176 | 4238 | 12414 |  |  |  | Executive Engineer
20:30 | 86 | 8076 | 4267 | 12343 |  |  |  | Network Operation Division
21:00 | 152 | 7976 | 4296 | 12272
21:30 | 152 | 7943 | 4297.5 | 12240.5
22:00 | 152 | 7910 | 4299 | 12209 |  |  |  |  | Page 6 of 7
22:30 | 152 | 7938.5 | 4271 | 12209.5
23:00 | 152 | 7967 | 4243 | 12210
23:30 | 167 | 7943 | 4228 | 12171
24:00 | 182 | 7919 | 4213 | 12132
12427 MW (19:30 )
10641.73 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-09-03 |  | Energy | 261422977
[10 empty] | 2020-09-03 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3841 | 898 | 2103 | 3684 | 670 | 80 | 745 | 0 | 172
0:30 | 3690 | 901 | 2082.5 | 3553 | 679.5 | 80.5 | 662 | 0 | 169 | Date: | 2020-09-03
1:00 | 3539 | 904 | 2062 | 3422 | 689 | 81 | 579 | 0 | 166
1:30 | 3547.5 | 899 | 2037 | 3249.5 | 689.5 | 79 | 517 | 0 | 164 | [7 empty] | Total Energy | 261.423 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 3556 | 894 | 2012 | 3077 | 690 | 77 | 455 | 0 | 162 | [7 empty] | Energy not Served | 0
2:30 | 3584 | 894 | 2047.5 | 2906.5 | 689.5 | 76 | 408 | 0 | 161 | [7 empty] | Energy Requirement | 261.423
3:00 | 3612 | 894 | 2083 | 2736 | 689 | 75 | 361 | 0 | 160
3:30 | 3644 | 894 | 2086.5 | 2615 | 679 | 75 | 318 | 0 | 158 | [6 empty] | Shortage
4:00 | 3676 | 894 | 2090 | 2494 | 669 | 75 | 275 | 0 | 156
4:30 | 3676.5 | 894 | 2084 | 2495 | 669 | 75.5 | 238.5 | 0 | 153
5:00 | 3677 | 894 | 2078 | 2496 | 669 | 76 | 202 | 0 | 150
5:30 | 3620 | 893.5 | 2013 | 2271 | 659 | 76.5 | 177 | 0 | 144
6:00 | 3563 | 893 | 1948 | 2046 | 649 | 77 | 152 | 0 | 138
6:30 | 3494.5 | 893 | 1904.5 | 2003 | 629 | 77 | 136 | 0 | 133 |  |  |  |  | Coal
7:00 | 3426 | 893 | 1861 | 1960 | 609 | 77 | 120 | 0 | 128
7:30 | 3329.5 | 893.5 | 1872.5 | 2006.5 | 609.5 | 77 | 120 | 0 | 128 |  |  |  | Oil |  |  |  | ,
8:00 | 3233 | 894 | 1884 | 2053 | 610 | 77 | 120 | 0 | 128
8:30 | 3190 | 894 | 1914 | 2272 | 620 | 77.5 | 136 | 0 | 128
9:00 | 3147 | 894 | 1944 | 2491 | 630 | 78 | 152 | 0 | 128
9:30 | 3174.5 | 893.5 | 1997.5 | 2869.5 | 390 | 78.5 | 183 | 0 | 131
10:00 | 3202 | 893 | 2051 | 3248 | 150 | 79 | 214 | 0 | 134
10:30 | 3225 | 894.5 | 2036 | 3325 | 150 | 79 | 296 | 0 | 136
11:00 | 3248 | 896 | 2021 | 3402 | 150 | 79 | 378 | 0 | 138
11:30 | 3292.5 | 895.5 | 1995 | 3474 | 150 | 79.5 | 435.5 | 0 | 138
12:00 | 3337 | 895 | 1969 | 3546 | 150 | 80 | 493 | 0 | 138
12:30 | 3391.5 | 895.5 | 1935.5 | 3560.5 | 150 | 80 | 486 | 0 | 134
13:00 | 3446 | 896 | 1902 | 3575 | 150 | 80 | 479 | 0 | 130
13:30 | 3446 | 896 | 1902 | 3575 | 150 | 80 | 479 | 0 | 130
14:00 | 3446 | 896 | 1902 | 3575 | 150 | 80 | 479 | 0 | 130
14:30 | 3413 | 896 | 1977.5 | 3534.5 | 300 | 79.5 | 477.5 | 0 | 143
15:00 | 3380 | 896 | 2053 | 3494 | 450 | 79 | 476 | 0 | 156
15:30 | 3337.5 | 895.5 | 2040 | 3437 | 475 | 78 | 458.5 | 0 | 155
16:00 | 3295 | 895 | 2027 | 3380 | 500 | 77 | 441 | 0 | 154
16:30 | 3271 | 891 | 2054 | 3120.5 | 545 | 77 | 433.5 | 0 | 151
17:00 | 3247 | 887 | 2081 | 2861 | 590 | 77 | 426 | 0 | 148
17:30 | 3196 | 888.5 | 1795 | 2831 | 570 | 77 | 470.5 | 0 | 141
18:00 | 3145 | 890 | 1509 | 2801 | 550 | 77 | 515 | 0 | 134
18:30 | 3356.5 | 889.5 | 1808 | 3233.5 | 580 | 77 | 624 | 0 | 152
19:00 | 3568 | 889 | 2107 | 3666 | 610 | 77 | 733 | 0 | 170
19:30 | 3640 | 889 | 2182 | 4083 | 640 | 77 | 746 | 0 | 170
20:00 | 3693 | 889 | 2099 | 4099 | 640 | 77 | 749 | 0 | 168
20:30 | 3724.5 | 893.5 | 2106.5 | 3979 | 645 | 77 | 747.5 | 0 | 170
21:00 | 3756 | 898 | 2114 | 3859 | 650 | 77 | 746 | 0 | 172
21:30 | 3827.5 | 898 | 2064 | 3799.5 | 655 | 77 | 745.5 | 0 | 174
22:00 | 3899 | 898 | 2014 | 3740 | 660 | 77 | 745 | 0 | 176
22:30 | 3909.5 | 898 | 2025.5 | 3712 | 665 | 77.5 | 745 | 0 | 177
23:00 | 3920 | 898 | 2037 | 3684 | 670 | 78 | 745 | 0 | 178
23:30 | 3880.5 | 898 | 2070 | 3684 | 670 | 79 | 745 | 0 | 175 | Max Temp. in Dhaka |  | 35.4° C
24:00 | 3841 | 898 | 2103 | 3684 | 670 | 80 | 745 | 0 | 172
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
Note on W13: Author:

## Generation
g | 2020-09-03
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 42 | 40 | 40 | 41 | 42 | 42 | 42 | 43 | 44 | 44 | 45 | 45 | 44 | 44 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 43 | 45 | 1068742
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 852000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 0 | [6 empty] | 2 | 12 | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 8 |  | 15 | 25 | 25 | 25 | 25 | 25 | 25 | 371966
| Teknaf 20MW PP (Solartech) | [5 empty] | 0.5 | 5.1 | 10.6 | 15.7 | 18.7 | 16.6 | 20.33 | 20 | 17.7 | 14.4 | 9.4 | 3.6 | 0.3 | [8 empty] | 151470
6 | Sikalbaha 225MW CCPP (Gas) | 107 | 146 | 145 | 147 | 146 | 146 | 85 | 57 | 58 | 58 | 57 | 24 | 25 | 25 | 27 | 40 | 40 | 58 |  | 81 | 97 | 112 | 173 | 213 | 216 | 216 | 2254147
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 150 | 140 | 140 | 139 | 141 | 140 | 110 | [19 empty] | 1030111
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 17 | 17 | 6 | 0 | [5 empty] | 68 | 66 | 68 | 68 | 66 | 66 | 51 | 66 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 1211728
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [19 empty] | 80 | 80 | 60 |  |  |  |  | 122688
14 | Titas 50 MW Peaking PP | [11 empty] | 41 | 42 | 42 | 42 | 41 | 41 | 48 |  | 48 | 48 | 50 | 50 | 50 | 50 | 50 | 599920
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 288 | 268 | 300 | 310 | 306 | 255 | 293 | 285 | 303 | 266 | 271 | 272 | 272 | 293 | 303 | 298 | 287 | 257 |  | 307 | 309 | 242 | 282 | 310 | 310 | 291 | 7076894
18 | Kodda 300 MW PP Unit-2 (Summit) | 268 | 253 | 253 | 250 | 250 | 195 | 195 | 215 | 253 | 253 | 250 | 253 | 253 | 253 | 248 | 252 | 250 | 250 |  | 253 | 253 | 250 | 250 | 253 | 253 | 253 | 5991706
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 562000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 98 | 100 | 100 | 2391000
23 | Ghorasal TPP Unit-5 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2661750
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | [6 empty] | 22 | 30 | 60 | 80 | 80 | 80 | 80 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 80 | 80 | 80 | 80 | 1372466
32 | Ashuganj 50 MW PP | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 5 | 5 | 8 | 14 | 14 | 25 | 25 | 30 | 30 | 35 |  | 34 | 34 | 34 | 34 | 35 | 35 | 35 | 649296
33 | Ashuganj 225 MW CCPP | [5 empty] | 90 | 132 | 62 | 79 | 121 | 141 | 140 | 139 | 30 | 43 | 46 | 48 | 94 |  | 114 | 114 | 195 | 212 | 210 | 194 | 176 | 2192000
34 | Ashuganj 450 MW CCPP(South) | 285 | 285 | 290 | 300 | 300 | 285 | 270 | 280 | 260 | 260 | 260 | 275 | 330 | 280 | 305 | 280 | 280 | 280 |  | 255 | 255 | 250 | 255 | 255 | 270 | 250 | 6760000
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 315 | 325 | 325 | 310 | 260 | 260 | 255 | 265 | 265 | 280 | 280 | 280 | 310 | 280 | 280 | 280 |  | 285 | 280 | 280 | 280 | 280 | 300 | 280 | 7288000
35 | Ashuganj 55 MW PP (Precision) | 42 | 46 | 46 | 47 | 46 | 47 | 47 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 39 | 39 | 42 | 42 |  | 43 | 44 | 25 | 10 | 10 | 10 | 10 | 689280
36 | Chandpur 150 MW CCPP | [19 empty] | 90 | 95 | 90 | 85 | 95 | 96 | 89 | 507070
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 341 | 342 | 343 | 354 | 350 | 341 | 339 | 357 | 349 | 357 | 341 | 341 | 345 | 342 | 359 | 353 | 344 | 340 |  | 353 | 342 | 342 | 340 | 340 | 346 | 361 | 8448950
40 | Meghnaghat 450 MW CCPP(MPL) | 400 | 400 | 400 | 400 | 400 | 400 | 340 | 340 | 340 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 300 |  | 380 | 420 | 420 | 420 | 370 | 370 | 370 | 9235750
41 | Haripur 360MW CCPP(HPL) | 353 | 356 | 354 | 355 | 354 | 316 | 304 | 352 | 351 | 350 | 318 | 303 | 273 | 303 | 304 | 303 | 302 | 251 |  | 347 | 348 | 351 | 354 | 304 | 302 | 352 | 7797000
42 | RPCL 210MW CCPP | 155 | 157 | 157 | 157 | 157 | 160 | 159 | 158 | 155 | 155 | 153 | 154 | 151 | 136 | 135 | 135 | 137 | 136 |  | 153 | 152 | 154 | 155 | 140 | 140 | 140 | 3493000
43
44 | Fenchugonj CCPP Phase-1 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 91 | 91 | 91 | 91 | 90 | 90 | 90 | 88 | 89 | 91 |  | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 2123000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 722160
46 | Shajibazar 330 MW CCPP | 202 | 206 | 203 | 211 | 210 | 202 | 212 | 200 | 105 | 98 | 98 | 99 | 98 | 102 | 106 | 98 | 100 | 75 |  | 109 | 130 | 167 | 160 | 223 | 178 | 188 | 3482000
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 62 | 62 | 62 | 62 | 63 | 62 | 61 | 40 | 65 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 65 | 65 | 64 | 62 | 61 | 61 | 61 | 1320672
48 | Shahjibazar 86MW PP (Shahjibazar) | 85 | 85 | 85 | 85 | 85 | 85 | 83 | 83 | 83 | 83 | 82 | 82 | 84 | 84 | 84 | 84 | 85 | 10 |  | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 1965120
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 130 | 130 | 130 | 130 | 130 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3081300
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 413000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 245880
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 201264
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 47 | 50 | 53 | 50 | 53 | 53 | 11 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1178400
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 571080
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 275 | 315 | 315 | 305 | 285 | 280 | 300 | 290 | 280 | 270 | 280 | 290 | 290 | 310 | 300 | 300 | 270 |  | 280 | 300 | 280 | 270 | 275 | 300 | 310 | 7171700
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 55 | 17 | 0 | [5 empty] | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 973225
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 436896
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 477576
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 20 | 20 | 20 | 20 | 425412
63 | Impoprt (Tripura) | 166 | 162 | 160 | 156 | 150 | 138 | 128 | 128 | 128 | 134 | 138 | 138 | 130 | 148 | 156 | 154 | 148 | 134 |  | 170 | 170 | 168 | 172 | 176 | 178 | 172 | 3690240
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 28 | 6 | 7 | 6 | 4 | 3 | 3 | 7 | 7 | 5 | 8 | 16 | 10 |  | 26 | 28 | 30 | 36 | 36 | 41 | 42 | 534720
65 | Feni 22MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 444312
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 225720
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 17 | 17 |  | 17 | 17 | 17 | 17 | 33 | 33 | 33 | 712700
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 18 | 18 | 18 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 |  |  | 18 | 18 | 21 | 21 | 20 | 21 | 468780
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 28 | 28 | 28 | 20 | 20 | 28 | 28 |  | 22 | 22 | 30 | 30 | 30 | 30 | 30 | 647460
71 | Maona 33 MW PP(Summit) | 28 | 28 | 28 | 28 | 28 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 |  |  |  | 33 | 33 | 33 |  |  | 33 | 33 | 626000
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 33 | 33 | 25 | 25 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 759500
73 | Ghorashal 108MW PP (Regent) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 71 | 71 | 71 | 72 | 73 | 73 | 73 | 52 |  | 73 | 73 | 73 | 73 | 73 | 73 | 72 | 1711409
| Feni Lanka Power | 114 | 70 | 0 | [6 empty] | 114 | 114 | 114 | 114 | 114 | 114 | 70 | 50 | 50 |  | 108 | 108 | 108 | 114 | 114 | 114 | 114 | 1753320
| Chowmuhani 113 MW | 113 | 106 | 113 | 113 | 113 | 113 | 113 | 113 | 108 | 113 | 110 | 113 | 106 | 109 | 108 | 105 | 65 | 65 |  | 95 | 113 | 113 | 113 | 113 | 113 | 113 | 2599800
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 100 | 100 | 100 | 100 | 100 | 96 | 100 | 100 | 100 | 96 | 95 | 96 | 96 | 96 | 98 | 72 | 72 |  | 90 | 100 | 98 | 100 | 100 | 100 | 100 | 2336640
78 | Gazipur 52 MW PP | 51 | 51 | 8 | 0 |  |  |  |  | 2 | 41 | 51 | 51 | 51 | 51 | 51 | 51 | 8 | 8 |  | 36 | 51 | 51 | 51 | 51 | 51 | 51 | 806268
79 | Kodda 150MW PP | 149 | 149 | 149 | 149 | 82 | 32 | 0 |  | 32 | 84 | 84 | 116 | 116 | 116 | 116 | 82 | 82 | 82 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 2564640
80 | Jamalpur 95 MW PP(Powerpac) | 72 | 72 | 72 | 72 | 72 | 72 | 16 | 25 | 64 | 64 | 64 | 72 | 72 | 72 | 72 | 72 | 72 | 72 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 1632960
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 0 |  |  |  |  | 5 | 32 | 32 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 809597
| Gazipur 100 MW PP | 104 | 104 | 104 | 0 |  |  |  | 5 | 69 | 70 | 85 | 85 | 85 | 69 | 68 | 68 | 68 | 68 |  | 104 | 103 | 103 | 103 | 103 | 103 | 103 | 1704948
| Kaptai 7 MW Solar PP | [5 empty] | 0.1 | 1.1 | 2.6 | 4 | 4.7 | 5.3 | 5.5 | 5.2 | 4.7 | 3.6 | 2.5 | 0.6 | [9 empty] | 39721
| Jodiac Power | [11 empty] | 1 | 24 | 35 | 34 | 34 | 34 | 17 | [7 empty] | 0 | 191368
| Karnaphuli Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [17 empty] | 0 | 148036
82 | Madanganj 102 PP(Summit) | 97 | 88 | 84 | 97 | 97 | 97 | 64 |  |  | 22 | 88 | 97 | 97 | 97 | 97 | 97 | 97 | 97 |  | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 2030544
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 12 | 12 | 13 | 12 | 13 | 12 | 12 | 12 | 13 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 17 | 25 |  | 53 | 100 | 100 | 100 | 29 | 25 | 25 | 605775
86 | Meghnaghat CCPP(Summit) | 140 | 130 | 140 | 140 | 140 | 125 | 140 | 130 | 140 | 138 | 140 | 140 | 138 | 140 | 150 | 145 | 138 | 125 |  | 145 | 148 | 120 | 130 | 135 | 150 | 135 | 3324044
87 | Meghnaghat 100 MW(IEL) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 93 | 98 | 100 | 100 | 75 | 75 |  | 85 | 100 | 100 | 100 | 100 | 100 | 100 | 2387520
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 2615040
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [8 empty] | 10 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 20 | 20 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 858120
92 | Fenchuganj 44MW (Energyprima) | 49 | 49 | 46 | 49 | 49 | 49 | 49 | 49 | 49 | 46 | 46 | 48 | 48 | 48 | 48 | 48 | 48 | 10 |  | 35 | 49 | 49 | 49 | 49 | 49 | 49 | 1143000
93 | Ashuganj 51 MW PP (Midland) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 28 | 43 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 814218
94 | Gagnagar 102 MW PP (Digital Power) | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 |  | 93 | 93 | 93 | 93 | 93 | 84 | 84 | 2219184
95 | Patenga 50MW PP (Baraka) | 50 | 50 | 19 | 0 |  |  |  |  | 15 | 44 | 47 | 46 | 48 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 889440
96 | Chattogram 108 MW PP (ECPV) | 87 | 89 | 75 | 44 | 44 | 11 | 11 | 30 | 73 | 75 | 75 | 78 | 80 | 78 | 80 | 80 | 80 | 84 |  | 77 | 85 | 85 | 83 | 81 | 85 | 88 | 1704000
97 | Katpotti 52 MW PP (Sinha)
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 15 | 15 | 15 | 32 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1226669
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 36 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1236451
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 163 | 130 | 130 | 130 | 130 | 163 | 110 | 110 | 130 | 130 | 130 | 163 | 110 |  | 163 | 163 | 163 | 163 | 130 | 130 | 130 | 3517118
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0.1 | 0.5 | 1.2 | 1.9 | 0.9 | 2.4 | 2.5 | 2.5 | 1 | 1.7 | 1.2 | 0.4 | [9 empty] | 15300
103 | Kamalaghat 54 MW PP(Banco Energy) | 53 | 53 | 53 | 53 | 53 | 17 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 42 | 17 | 17 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1189800
104 | Keranigonj 300 MW PP (APR) | [9 empty] | 150 | [9 empty] | 77 | 77 | 76 | 31 | 35 | 33 | 0 | 302034
105 | Bramhangoan 100 MW PP (Aggreko) | [17 empty] | 25 |  | 50 | 50 | 50 |  |  |  |  | 103579
106 | Mymensingh 200 MW PP (United) | 193 | 193 | 193 | 193 | 194 | 194 | 200 | 200 | 200 | 185 | 184 | 184 | 183 | 183 | 182 | 182 | 182 | 150 |  | 170 | 200 | 200 | 200 | 200 | 200 | 200 | 4557600
112 | Aurahati 100MW PP (Aggreko) | [9 empty] | 46 | 27 | [8 empty] | 55 | 55 | 56 |  |  |  | 0 | 145122
114 | Kodda 149 MW PP Unit-1 (Summit) | 96 | 110 | 114 | 113 | 113 | 113 | 113 | 112 | 113 | 113 | 113 | 113 | 112 | 113 | 115 | 115 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2717280
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 100 | 100 | 100 | 100 | 90 | 70 | 70 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2334720
116 | Chandpur 200MW (Desh energy) | 70 | 0 | [7 empty] | 17 | 51 | 58 | 85 | 85 | 85 | 48 | 32 | 32 |  | 65 | 100 | 100 | 50 | 50 | 50 | 50 | 1099200
117 | Ashuganj 150MW PP (Midland) | [7 empty] | 5 | 30 | 82 | 100 | 97 | 100 | 98 | 98 | 102 | 103 | 100 |  | 100 | 106 | 107 | 105 | 105 | 108 | 107 | 1552290
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 109 | 109 | 109 | 109 | 109 | 8 | 8 | 8 | 25 | 42 | 65 | 65 | 45 | 45 | 45 | 45 | 45 | 45 |  | 70 | 115 | 115 | 115 | 115 | 115 | 115 | 1788000
| Anwara 300 MW PP (United) | 288 | 232 | 216 | 216 | 216 | 216 | 216 | 252 | 252 | 304 | 307 | 307 | 307 | 307 | 307 | 307 | 252 | 212 |  | 235 | 235 | 234 | 234 | 215 | 216 | 216 | 6112145
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2414400
120 | Eastern Zone Total | 7506 | 7214 | 7111 | 6951 | 6858 | 6399.7 | 6142.7 | 6019.4 | 6296.6 | 7129.3 | 7186.3 | 7264.33 | 7328.7 | 7266.4 | 7438.7 | 7228.1 | 6864.6 | 6356.3 |  | 7834 | 8198 | 8176 | 7976 | 7910 | 7967 | 7919 | 173679078
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 115 | 115 | 115 | 115 | 115 | 66 | 16 | 68 | 99 | 115 | 99 | 99 | 99 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2474880
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [11 empty] | 2
| Khulna 225 MW CCPP | 160 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 130 | 135 | 135 | 120 | 120 | 120 | 120 | 120 | 120 |  | 180 | 190 | 190 | 190 | 190 | 190 | 190 | 3461760
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 50 | 0 | [6 empty] | 35 | 53 | 90 | 90 | 53 | 53 | 35 | 35 | 35 |  | 105 | 105 | 105 | 105 | 105 | 70 | 70 | 1232640
130
131
132
133
| Barisal 110 MW PP (Summit ) | 64 | 64 | 32 | 32 | 32 | 0 |  |  |  | 16 | 110 | 110 | 110 | 110 | 110 | 110 | 80 | 80 |  | 80 | 110 | 110 | 110 | 110 | 110 | 110 | 1742016
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 78 | 78 | 77 | 77 | 76 | 76 | 77 | 83 | 83 | 81 | 78 | 78 | 54 | 33 | 33 | 33 | 33 | 33 |  | 78 | 77 | 77 | 77 | 77 | 78 | 77 | 1629747
| Bhola 225 MW CCPP | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 15 | 15 | 15 | 15 | 15 | 90 | 90 | 89 | 89 | 89 | 89 |  | 89 | 89 | 79 | 90 | 90 | 90 | 90 | 1872160
140 | Bhola 33 MW PP (Venture) | 37 | 37 | 34 | 33 | 34 | 28 | 26 | 25 | 25 | 25 | 26 | 21 | 19 | 18 | 25 | 24 | 20 | 21 |  | 31 | 31 | 32 | 33 | 35 | 36 | 34 | 684552
141 | Noapara 100 MW PP (Bangla Trac) | [19 empty] | 40 | 100 | 100 | 100 | 100 | 100 | 100 | 552960
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 0 | [5 empty] | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 8 | 8 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 660375
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [10 empty] | 20 | 80 | 89 | [8 empty] | 15 | 15 | 15 | 15 | 0 | 242640
146 | Bheramara HVDC | 904 | 894 | 894 | 894 | 894 | 893 | 893 | 894 | 894 | 893 | 896 | 895 | 896 | 896 | 896 | 895 | 887 | 890 |  | 889 | 889 | 889 | 898 | 898 | 898 | 898 | 21463273
147 | Bheramara 410 MW CCPP | 360 | 370 | 380 | 395 | 400 | 310 | 295 | 330 | 310 | 310 | 355 | 410 | 410 | 345 | 370 | 345 | 345 | 295 |  | 405 | 405 | 410 | 410 | 390 | 370 | 345 | 8778816
148 | Payra 1320 MW | 540 | 540 | 540 | 520 | 520 | 500 | 460 | 460 | 480 |  |  |  |  | 200 | 300 | 350 | 440 | 400 |  | 460 | 490 | 490 | 500 | 510 | 520 | 520 | 10170600
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 149 | 150 | 149 | 149 | 149 | 149 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3689800
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 50 | 0 | [8 empty] | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 773920
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 176 | 164 | 165 | 166 | 165 | 147 | 144 | 157 | 152 | 171 | 180 | 190 | 165 | 148 | 163 | 163 | 157 | 151 |  | 173 | 191 | 184 | 177 | 178 | 193 | 196 | 4257418
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 201 | 204 | 210 | 214 | 216 | 218 | 150 | 159 | 210 | 207 | 214 | 213 | 211 | 211 | 209 | 209 | 208 | 140 |  | 171 | 180 | 180 | 180 | 204 | 212 | 213 | 5154773
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 346 | 304 | 344 | 347 | 347 | 294 | 342 | 333 | 382 | 383 | 362 | 370 | 340 | 396 | 401 | 402 | 396 | 289 |  | 410 | 408 | 358 | 388 | 414 | 406 | 415 | 8850818
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [10 empty] | 17 | 35 | 35 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 442074
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 21 | 21 | 21 | 21 | 0 | 20 | 20 |  | 21 | 21 | 21 | 21 | 21 | 22 | 22 | 481920
163 | Bogura 20 MW PP (Energyprima) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 253728
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 251838
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | 42 | 42 | 0 | [14 empty] | 35 |  | 43 | 44 | 47 | 44 | 43 | 43 | 43 | 349900
168 | Santahar 50 MW Peaking PP | 31 | 31 | 0 | [14 empty] | 32 |  | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 275135
169 | Natore 52 MW PP (Rajlanka) | 43 | 43 | 0 | [5 empty] | 8 | 36 | 43 | 43 | 43 | 43 | 43 | 43 | 25 | 25 |  | 28 | 43 | 43 | 43 | 43 | 43 | 43 | 676320
170 | Chapainawabganj 100 MW Peaking PP | 96 | 96 | 75 | 0 | [6 empty] | 24 | 48 | 48 | 48 | 48 | 48 | 48 | 48 |  | 96 | 98 | 96 | 96 | 96 | 96 | 96 | 1162392
171 | Baghabari 200 MW PP (Paramount) | [21 empty] | 50 | 50 | 10 |  | 0 | 118742
| Bagura 113 MW PP (Confidence)-2 | 113 | 95 | 95 | 50 | 50 | 0 |  |  | 18 | 57 | 81 | 95 | 95 | 100 | 113 | 113 | 35 | 35 |  | 68 | 113 | 113 | 113 | 113 | 113 | 113 | 1910112
172 | Confidence Power Bogura Unit-1 113 MW | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 95 | 70 | 70 |  | 90 | 103 | 108 | 108 | 109 | 90 | 90 | 2172192
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 88 | 74 | 71 | 71 | 71 | 71 | 71 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 69 | 70 | 78 |  | 87 | 100 | 99 | 106 | 106 | 106 | 106 | 1919040
177 | Sympa Solar Power 8MW | [6 empty] | 0.4 | 1.8 | 1.6 | 6 | 6.8 | 5.4 | 5.2 | 5.3 | 6 | 2.2 | 0.8 | 0.2 | [8 empty] | 37358
178
178