## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-09-05 | Saturday
|  |  | Date (day): | 2020-09-05 |  | Saturday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13938.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14876 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-09-04 | 2020-09-05 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 28 | 28 | 28 | 28 |  | 57 | Unit-2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 140 | 100 | 140 | 40 |  | Gas shortage
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 110 | 110 | 110 | 110 | 80 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 71 | 72 | 90 | 90 | 18 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 345 | 340 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 302 | 352 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 350 | 450 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 75 | 91 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 125 | 140 | 150 | 150 | 155 |  | GT-1 S/D for gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 52 | 97 | 96 | 96
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 46 | 45 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 9 | 87 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 90 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 300 | 335 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 50 | 93 | 93 | 93
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 53 | 53 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 32 | 149 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 40 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 38 | 54 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 28 | 28 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 25 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 22 | 51 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 155 | 253 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 96 | 113 | 133 | 133 |  | 16 | Engine problem
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 60 | 104 | 100 | 100
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 2471 | 3511 | 3974 | 4264 | 845 | 768
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 16 | 25 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 0 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 10 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 78 | 77 | 77 | 77 | 153 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 218 | 204 | 225 | 225 | 0
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Under maint.
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 100 | 100
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 20 | 20 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 21 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 23 | 42 | 20 | 30
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 32 | 85 | 95 | 95 |  | 13 | Engine problem
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5.2 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 180 | 216 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 792.2 | 1041 | 1502 | 1487 | 513 | 111
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 80 | 80 | 100 | 134 |  | Gas shortage
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 192 | 180 | 225 | 225
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 275 | 360 | 360
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 250 | 250 | 360 | 360
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 32 | 32 | 35 | 36 | 9 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 10 | 10 | 10 | 10 | 45
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 52 | 92 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 50 | 0 | 44
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 86 | 95 | 100 | 100 |  | 63 | ST under shut down
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 16 | 200 | 200
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 21 | 21
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 118 | 172 | 157 | 173
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 5 | 40 | 43 | 43 |  | 9 | Engine problem
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 20 | 20 | 20 |  | 5 | Engine problem
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 34 | 114 | 114 | 114
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 108 | 113 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1365 | 1657 | 2091 | 2372 | 639 | 77
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 153 | 154 | 157 | 160 | 42 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 20 | 22 | 22
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 64 | 72 | 72 | 72 |  | 23 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.3 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 200 | 200 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 35 | 115 | 115 | 115
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 476.3 | 561 | 567.6 | 569 | 42 | 23
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 91 | 86 | 90 | 90
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Unit-4 under shut down
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 199 | 180 | 210 | 210 |  | 120 | Engine problem
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 44 | 50 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 45 | 49 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 63 | 66 | 66
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 87 | 85 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 140 | 140 | 140 |  | 91 | Machine problem
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 18 | 18 | 18
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 260 | 290 | 341 | 341
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1085 | 1199 | 1285 | 1285 | 0 | 671
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 916 | 900 | 918 | 918
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 99 | 115 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 195 | 225 | 225
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 340 | 345 | 410 | 410
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 40 | 40 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 80 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 105 | 105 | 105
| 108 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 32 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1547 | 1800 | 1993 | 2119 | 0 | 0
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 110 | 80 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 20 | 35 | 33 | 33
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 90 | 90 | 0 | 90 |  | 104 | GT-2 & ST Under maint.
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 76 | 78 | 80 | 80 |  | 15 | Engine problem
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 0 | 535 | 450 | 490 |  |  | Unit-2 Test. Unit-1 under S/D
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 296 | 818 | 673 | 803 | 0 | 119
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 65 | 65 | 35 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 34 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 43 | 50 | 50
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 171 | 153 | 220 | 220 |  |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 150 | 210 | 220 | 220 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 356 | 348 | 414 | 414 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 0 | 32
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 21 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 11 | 11 | 11 | 11
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 35 | 43 | 43 | 43 |  | 9 | Engine problem
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 96 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 32 | 113 | 113 | 113
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 50 | 106 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 834 | 1269 | 1582 | 1704 | 366 | 9
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 52 | 95 | 113 | 113
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7.2 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 209.2 | 245 | 271 | 273 | 294 | 30
|  | Total |  |  |  |  | 20383 | 19892 | 9075.7 | 12101 | 13938.6 | 14876 | 2699 | 1808
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8711.952 | 11616 | 13379.9502 | 14279.7799
| A. |  | 2020-09-04 | (Yesterday) |  |  |  |  | Friday
| 1 | Highest Generation : |  |  | 12106 | MW at | 23:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 8634.4 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12101 | MW
| 3 | Day peak Generation : |  |  | 9075.7 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11616 | MW
| 4 | Evening peak Generation : |  |  | 12101 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 251.1791 | MKWHr | By Solar | 0.18152 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 137.4432 | MKWHr |  | By Oil: | 72.9999 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 13.4503 | MKWHr |  | By Hydro: | 1.853 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2699 | MW | Dhaka | 3766 | 3766 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 1808 | MW | Chittagong | 1284 | 1284 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4507 | MW | Khulna | 1513 | 1513 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1110.69 | MMCFD |  |  | Rajshahi | 1279 | 1279 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 157553205.078 | ii) Oil : | Taka | 579612671.67 | Comilla | 1228 | 1228 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 62839483 | Total | Taka | 800005359.748 | Mymensingh | 907 | 907 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.09 | MKWHr. | Sylhet | 505 | 505 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -48 | MW (E to W) at | 21:00 | hrs | Barisal | 356 | 356 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -86 | MW at | 19:30 | hrs | Rangpur | 778 | 778 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 35.8° C |  |  | Total | 11616 | 11616 |  | 0
| B. |  | 2020-09-05 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 34.6° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14876 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10300 | MW
| 4 | Reserve(Generation end) |  |  |  | 2376 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 259.3539 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9300.7 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.7011 | MKWHr. | ii) HVDC Flow at Peak Time |  | 900 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.5501 | MKWHr. | iii) Maximum HVDC Flow : |  | 917 | MW at | 10:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 93.31 |  | (b) Today: | 93.37 |  | (c) Rule Curve: |  | 99.92
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-09-04
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 28 | 0 | 99 | 110 | 0 | 73 | 0 | 340 | 354 |  | 0 | 370 | 135 | 100 | 97 | 44 | 268 | 0 | 0 | 0 | 100 | 93 | 149 | 13 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 28 | 33 | 51 | 0 | 45 | 35 | 0 | 0 | 25 | 217 | 0 | 0 | 0 |  | 0 | 0 | 102 | 60 | 84 | 50 | 20 | 42 | 0 | 0 | 80 | 280 | 250 | 176 | 8 | 86 | 35 | 10 | 0 | 51 | 0 | 0 | 43 | 20 | 10 | 33 | 21 | 166 | 141 | 71 | 22 | 0 | 91 | 30 | 50 | 49 | 130 | 197 | 62 | 87 | 0 | 140 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 253 | 0 | 0 | 200 | 0 | 113 | 0 | 100 | 0 | 107 | 0 | 115 | 103 | 0 | 0 | 216 | 0 | 0 | 114 | 108 | 100 | 0 | 104 |  | 898 | 0 | 345 | 0 | 115 | 190 | 0 | 0 | 0 | 0 | 40 | 90 | 33 | 96 | 0 | 0 | 0 | 50 | 0 | 96 | 0 | 0 | 42 | 43 | 31 | 22 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 184 | 0 | 77 | 99 | 216 | 0 | 382 | 35 | 0 | 113 | 0 | 106 | 0 | 0 | 90 | 520 |  | 7717 | 4085 | 11802 | 3790 | 898 | 2039 | 3499 | 670 | 80 | 660 | 166 | 0 | 0 | 93.3
2:00 | 28 | 0 | 103 | 110 | 0 | 73 | 0 | 340 | 355 |  | 0 | 370 | 135 | 100 | 97 | 55 | 305 | 0 | 0 | 0 | 100 | 93 | 32 | 12 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 28 | 33 | 51 | 0 | 45 | 35 | 0 | 0 | 25 | 217 | 0 | 0 | 0 |  | 0 | 0 | 102 | 60 | 85 | 50 | 20 | 42 | 0 | 0 | 80 | 280 | 250 | 176 | 8 | 95 | 35 | 10 | 0 | 51 | 0 | 0 | 43 | 20 | 10 | 20 | 21 | 162 | 155 | 71 | 22 | 0 | 91 | 30 | 50 | 49 | 130 | 198 | 62 | 87 | 0 | 140 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 253 | 0 | 0 | 200 | 0 | 113 | 0 | 100 | 0 | 105 | 0 | 95 | 103 | 0 | 0 | 216 | 0 | 0 | 0 | 107 | 100 | 0 | 104 |  | 898 | 0 | 345 | 0 | 115 | 170 | 0 | 0 | 0 | 0 | 40 | 90 | 31 | 96 | 0 | 0 | 0 | 50 | 0 | 96 | 0 | 0 | 42 | 43 | 31 | 22 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 185 | 0 | 78 | 0 | 216 | 0 | 409 | 35 | 0 | 113 | 0 | 107 | 0 | 0 | 90 | 520 |  | 7523 | 3994 | 11517 | 3843 | 898 | 2066 | 3275 | 670 | 80 | 523 | 162 | 0 | 0 | 93.3
3:00 | 28 | 0 | 101 | 110 | 0 | 73 | 0 | 340 | 354 |  | 0 | 370 | 135 | 100 | 97 | 55 | 310 | 0 | 0 | 0 | 100 | 93 | 32 | 12 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 28 | 33 | 0 | 0 | 44 | 35 | 0 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 89 | 50 | 20 | 42 | 0 | 0 | 80 | 280 | 250 | 179 | 8 | 95 | 32 | 30 | 0 | 51 | 0 | 0 | 43 | 20 | 10 | 25 | 21 | 158 | 155 | 71 | 20 | 0 | 91 | 30 | 50 | 49 | 130 | 198 | 62 | 87 | 0 | 140 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 253 | 0 | 0 | 200 | 0 | 113 | 0 | 100 | 0 | 107 | 0 | 95 | 103 | 0 | 0 | 216 | 0 | 0 | 0 | 108 | 100 | 0 | 104 |  | 902 | 0 | 340 | 0 | 115 | 135 | 0 | 0 | 0 | 0 | 40 | 90 | 30 | 48 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 42 | 43 | 31 | 22 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 185 | 0 | 78 | 0 | 217 | 0 | 413 | 17 | 0 | 113 | 0 | 80 | 0 | 0 | 90 | 520 |  | 7322 | 3819 | 11141 | 3845 | 902 | 2098 | 3053 | 670 | 79 | 336 | 158 | 0 | 0 | 93.3
4:00 | 28 | 0 | 99 | 110 | 0 | 73 | 0 | 341 | 354 |  | 0 | 370 | 135 | 100 | 97 | 55 | 298 | 0 | 0 | 0 | 100 | 93 | 16 | 12 | 0 | 0 | 0 | 53 | 55 | 0 | 22 | 25 | 30 | 28 | 33 | 0 | 0 | 44 | 35 | 0 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 89 | 50 | 20 | 42 | 0 | 0 | 80 | 280 | 250 | 175 | 8 | 89 | 32 | 43 | 0 | 51 | 0 | 0 | 43 | 20 | 10 | 25 | 21 | 156 | 155 | 71 | 20 | 0 | 91 | 30 | 50 | 49 | 130 | 195 | 62 | 87 | 0 | 140 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 250 | 0 | 0 | 200 | 0 | 113 | 0 | 100 | 0 | 105 | 0 | 95 | 103 | 0 | 0 | 216 | 0 | 0 | 0 | 113 | 100 | 0 | 104 |  | 901 | 0 | 345 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 90 | 27 | 48 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 0 | 42 | 0 | 0 | 22 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 190 | 0 | 77 | 0 | 216 | 0 | 409 | 0 | 0 | 113 | 0 | 72 | 0 | 0 | 90 | 520 |  | 7236 | 3696 | 10932 | 3828 | 901 | 2103 | 2930 | 669 | 79 | 266 | 156 | 0 | 0 | 93.31
5:00 | 28 | 0 | 101 | 110 | 0 | 73 | 0 | 341 | 354 |  | 0 | 370 | 135 | 100 | 97 | 55 | 302 | 0 | 0 | 0 | 100 | 93 | 0 | 12 | 0 | 0 | 0 | 53 | 55 | 0 | 22 | 25 | 30 | 28 | 33 | 0 | 0 | 42 | 35 | 0 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 89 | 50 | 20 | 42 | 0 | 0 | 80 | 280 | 250 | 176 | 8 | 91 | 32 | 43 | 0 | 51 | 0 | 0 | 0 | 20 | 10 | 25 | 21 | 158 | 156 | 71 | 20 | 0 | 91 | 30 | 50 | 49 | 130 | 192 | 62 | 87 | 0 | 140 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 253 | 0 | 0 | 200 | 0 | 113 | 0 | 100 | 0 | 107 | 0 | 45 | 103 | 0 | 0 | 216 | 0 | 0 | 0 | 113 | 100 | 0 | 104 |  | 902 | 0 | 345 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 40 | 90 | 26 | 48 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 189 | 0 | 77 | 0 | 217 | 0 | 412 | 0 | 0 | 50 | 0 | 70 | 0 | 0 | 90 | 510 |  | 7149 | 3567 | 10716 | 3835 | 902 | 2115 | 2761 | 660 | 77 | 208 | 158 | 0 | 0 | 93.31
6:00 | 28 | 0 | 101 | 110 | 0 | 73 | 0 | 340 | 357 |  | 0 | 370 | 120 | 100 | 30 | 55 | 265 | 0 | 0 | 0 | 100 | 93 | 0 | 12 | 0 | 0 | 0 | 17 | 17 | 0 | 22 | 25 | 30 | 28 | 33 | 0 | 0 | 42 | 35 | 0 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 45 | 22 | 20 | 42 | 0 | 0 | 80 | 280 | 250 | 175 | 8 | 85 | 32 | 43 | 0 | 51 | 0 | 0 | 0 | 20 | 8 | 25 | 21 | 138 | 158 | 71 | 22 | 0 | 91 | 30 | 50 | 49 | 130 | 198 | 62 | 87 | 0 | 140 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 145 | 0 | 0 | 200 | 0 | 101 | 0.6 | 100 | 0 | 20 | 0 | 8 | 16 | 0 | 0.19 | 216 | 0 | 0 | 0 | 113 | 100 | 0 | 104 |  | 902 | 0 | 345 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 186 | 0 | 76 | 0 | 220 | 0 | 377 | 0 | 0 | 0 | 0 | 65 | 0 | 0.1 | 90 | 470 |  | 6516.79 | 3352.1 | 9868.89 | 3795 | 902 | 2061 | 2107 | 620 | 77 | 168 | 138 | 0.89 | 0 | 93.31
7:00 | 28 | 0 | 100 | 110 | 0 | 73 | 0 | 340 | 302 |  | 0 | 340 | 140 | 78 | 30 | 30 | 310 | 0 | 0 | 0 | 50 | 93 | 0 | 12 | 0 | 0 | 0 | 17 | 17 | 0 | 22 | 25 | 30 | 0 | 33 | 0 | 0 | 40 | 35 | 0 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 12 | 19 | 20 | 42 | 0 | 0 | 80 | 290 | 260 | 187 | 8 | 95 | 28 | 45 | 0 | 51 | 0 | 0 | 0 | 20 | 8 | 25 | 21 | 126 | 155 | 32 | 22 | 0.3 | 91 | 30 | 50 | 49 | 130 | 200 | 61 | 88 | 0 | 140 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 95 | 0 | 0 | 200 | 0 | 71 | 0 | 50 | 0 | 20 | 0 | 8 | 16 | 0 | 1.1 | 144 | 0 | 0 | 0 | 65 | 100 | 0 | 85 |  | 902 | 0 | 350 | 0 | 24 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 177 | 0 | 31 | 0 | 170 | 0 | 374 | 0 | 0 | 0 | 0 | 41 | 0 | 0.6 | 50 | 450 |  | 6062.4 | 3030.6 | 9093 | 3793 | 902 | 1936 | 1515 | 600 | 75 | 144 | 126 | 2 | 0 | 93.32
8:00 | 28 | 0 | 102 | 110 | 0 | 72 | 0 | 341 | 303 |  | 0 | 340 | 120 | 53 | 30 | 30 | 266 | 0 | 0 | 0 | 50 | 93 | 0 | 12 | 0 | 0 | 0 | 17 | 17 | 0 | 22 | 25 | 20 | 33 | 33 | 0 | 0 | 41 | 35 | 0 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 12 | 19 | 20 | 35 | 0 | 0 | 80 | 280 | 250 | 176 | 8 | 86 | 28 | 47 | 0 | 43 | 0 | 0 | 0 | 20 | 8 | 25 | 0 | 114 | 156 | 32 | 20 | 1.1 | 91 | 30 | 47 | 49 | 130 | 188 | 67 | 88 | 0 | 140 | 18 | 0 | 10 | 285 | 24 | 8 | 0 | 95 | 0 | 0 | 200 | 0 | 71 | 0 | 50 | 0 | 20 | 0 | 8 | 16 | 0 | 2.4 | 144 | 0 | 0 | 0 | 65 | 100 | 0 | 53 |  | 904 | 0 | 345 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 153 | 0 | 32 | 0 | 170 | 0 | 321 | 0 | 0 | 0 | 0 | 34 | 0 | 1.8 | 50 | 450 |  | 5869.5 | 2934.8 | 8804.3 | 3677 | 904 | 1861 | 1423 | 600 | 76 | 144 | 114 | 5.3 | 0 | 93.32
9:00 | 28 | 0 | 100 | 110 | 0 | 72 | 0 | 341 | 273 |  | 0 | 340 | 140 | 50 | 30 | 30 | 310 | 0 | 0 | 0 | 50 | 58 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 22 | 25 | 24 | 33 | 17 | 0 | 0 | 41 | 35 | 0 | 0 | 7 | 219 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 20 | 30 | 0 | 0 | 80 | 280 | 260 | 192 | 8 | 96 | 28 | 47 | 0 | 43 | 0 | 0 | 0 | 17 | 8 | 33 | 0 | 116 | 154 | 32 | 20 | 1.4 | 89 | 30 | 47 | 49 | 130 | 215 | 40 | 40 | 0 | 140 | 18 | 0 | 10 | 260 | 24 | 8 | 0 | 95 | 0 | 0 | 200 | 0 | 71 | 15.6 | 50 | 0 | 20 | 0 | 8 | 16 | 0 | 3.3 | 89 | 0 | 0 | 0 | 36 | 60 | 0 | 53 |  | 903 | 0 | 355 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 154 | 0 | 32 | 0 | 170 | 0 | 374 | 0 | 0 | 0 | 0 | 35 | 0 | 3.1 | 35 | 440 |  | 5683.3 | 2951.1 | 8634.4 | 3758 | 903 | 1805 | 1243 | 590 | 76 | 120 | 116 | 23.4 | 0 | 93.32
10:00 | 28 | 0 | 100 | 110 | 0 | 72 | 0 | 363 | 303 |  | 0 | 340 | 145 | 50 | 30 | 30 | 305 | 0 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 22 | 25 | 24 | 25 | 33 | 0 | 0 | 41 | 35 | 0 | 0 | 5 | 217 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 20 | 30 | 0 | 0 | 80 | 285 | 300 | 192 | 8 | 97 | 28 | 46 | 0 | 43 | 0 | 0 | 0 | 17 | 8 | 33 | 0 | 118 | 151 | 48 | 22 | 2 | 89 | 30 | 47 | 49 | 163 | 213 | 40 | 40 | 0 | 140 | 17 | 0 | 10 | 310 | 24 | 2 | 0 | 95 | 0 | 0 | 200 | 0 | 70 | 19.1 | 50 | 0 | 20 | 0 | 35 | 16 | 0 | 4.8 | 88 | 0 | 0 | 0 | 36 | 60 | 0 | 53 |  | 917 | 0 | 365 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 19 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 187 | 0 | 48 | 0 | 170 | 0 | 405 | 0 | 0 | 0 | 0 | 35 | 0 | 4.6 | 35 | 280 |  | 5897.9 | 2945.6 | 8843.5 | 3860 | 917 | 1965 | 1327 | 430 | 76 | 120 | 118 | 30.5 | 0 | 93.32
11:00 | 28 | 0 | 101 | 110 | 0 | 72 | 0 | 377 | 315 |  | 0 | 420 | 140 | 51 | 30 | 30 | 306 | 0 | 0 | 0 | 58 | 50 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 22 | 25 | 17 | 25 | 33 | 0 | 0 | 42 | 35 | 0 | 0 | 8 | 220 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 10 | 0 | 20 | 29 | 0 | 0 | 80 | 315 | 345 | 153 | 8 | 95 | 26 | 10 | 0 | 43 | 0 | 0 | 0 | 17 | 5 | 25 | 18 | 120 | 150 | 48 | 22 | 2.4 | 89 | 30 | 44 | 45 | 163 | 202 | 62 | 87 | 0 | 140 | 17 | 0 | 10 | 315 | 24 | 2 | 0 | 95 | 0 | 0 | 200 | 0 | 76 | 0 | 76 | 0 | 23 | 0 | 40 | 50 | 0 | 5.2 | 154 | 0 | 0 | 0 | 50 | 80 | 0 | 60 |  | 917 | 0 | 370 | 0 | 21 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 19 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 196 | 0 | 76 | 0 | 170 | 0 | 401 | 0 | 0 | 0 | 0 | 35 | 0 | 5.6 | 50 | 0 |  | 6229.6 | 2770.6 | 9000.2 | 3935 | 917 | 2089 | 1579 | 150 | 77 | 120 | 120 | 13.2 | 0 | 93.33
12:00 | 28 | 0 | 100 | 110 | 0 | 71 | 0 | 345 | 302 |  | 0 | 350 | 125 | 75 | 52 | 46 | 0 | 0 | 0 | 0 | 90 | 50 | 32 | 9 | 0 | 0 | 0 | 53 | 35 | 40 | 22 | 25 | 13 | 28 | 33 | 22 | 0 | 43 | 35 | 0 | 0 | 16 | 218 | 0 | 0 | 0 |  | 0 | 0 | 0 | 20 | 32 | 10 | 20 | 23 | 0 | 0 | 80 | 270 | 250 | 192 | 8 | 86 | 32 | 10 | 0 | 51 | 0 | 0 | 5 | 18 | 0 | 33 | 18 | 118 | 153 | 64 | 22 | 2.3 | 91 | 30 | 44 | 45 | 130 | 199 | 40 | 87 | 0 | 100 | 17 | 0 | 10 | 260 | 24 | 8 | 0 | 155 | 0 | 0 | 200 | 0 | 96 | 0 | 100 | 0 | 52 | 0 | 35 | 60 | 0 | 5.2 | 180 | 0 | 0 | 34 | 108 | 90 | 0 | 104 |  | 916 | 0 | 340 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 40 | 90 | 20 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 21 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 171 | 0 | 76 | 0 | 150 | 0 | 356 | 0 | 0 | 32 | 32 | 52 | 0 | 7.2 | 50 | 0 |  | 6189.5 | 2886.2 | 9075.7 | 3364 | 916 | 1875 | 2408 | 150 | 78 | 152 | 118 | 14.7 | 0 | 93.33
13:00 | 28 | 0 | 100 | 110 | 0 | 71 | 0 | 349 | 302 |  | 0 | 350 | 140 | 83 | 80 | 55 | 0 | 0 | 0 | 0 | 100 | 50 | 32 | 12 | 0 | 0 | 0 | 53 | 35 | 55 | 0 | 25 | 13 | 28 | 33 | 16 | 0 | 45 | 35 | 0 | 0 | 25 | 219 | 0 | 0 | 0 |  | 0 | 0 | 0 | 20 | 37 | 47 | 20 | 34 | 0 | 0 | 80 | 295 | 250 | 182 | 8 | 96 | 34 | 10 | 0 | 51 | 0 | 0 | 34 | 18 | 5 | 33 | 18 | 136 | 149 | 64 | 22 | 2 | 86 | 30 | 44 | 45 | 130 | 197 | 40 | 84 | 0 | 100 | 18 | 0 | 10 | 285 | 24 | 8 | 0 | 240 | 0 | 0 | 192 | 0 | 95 | 0 | 100 | 0 | 83 | 0 | 35 | 87 | 0 | 5.1 | 180 | 0 | 0 | 34 | 110 | 90 | 0 | 104 |  | 917 | 0 | 345 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 90 | 22 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 20 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 159 | 0 | 76 | 0 | 150 | 0 | 396 | 0 | 0 | 54 | 50 | 71 | 0 | 7.6 | 50 | 0 |  | 6545.1 | 2996.6 | 9541.7 | 3362 | 917 | 1949 | 2781 | 150 | 80 | 152 | 136 | 14.7 | 0 | 93.33
14:00 | 28 | 0 | 100 | 110 | 0 | 71 | 0 | 342 | 302 |  | 0 | 350 | 145 | 84 | 87 | 55 | 0 | 0 | 0 | 0 | 99 | 85 | 32 | 12 | 0 | 0 | 0 | 53 | 35 | 55 | 0 | 25 | 13 | 28 | 33 | 16 | 0 | 45 | 35 | 0 | 0 | 25 | 218 | 0 | 0 | 0 |  | 0 | 0 | 0 | 20 | 38 | 50 | 20 | 29 | 0 | 0 | 80 | 295 | 250 | 189 | 8 | 96 | 33 | 10 | 0 | 51 | 0 | 0 | 34 | 18 | 8 | 33 | 18 | 140 | 150 | 64 | 22 | 2 | 89 | 30 | 47 | 41 | 130 | 199 | 40 | 84 | 0 | 100 | 18 | 0 | 10 | 275 | 24 | 8 | 0 | 245 | 0 | 0 | 192 | 0 | 95 | 17.4 | 100 | 0 | 88 | 0 | 35 | 87 | 0 | 2.9 | 180 | 0 | 0 | 17 | 113 | 90 | 0 | 104 |  | 909 | 0 | 370 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 8 | 90 | 23 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 20 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 154 | 0 | 75 | 0 | 150 | 0 | 403 | 0 | 0 | 55 | 32 | 83 | 0 | 6.2 | 0 | 90 |  | 6602.3 | 2989.2 | 9591.5 | 3389 | 909 | 1940 | 2714 | 239 | 80 | 152 | 140 | 28.5 | 0 | 93.33
15:00 | 28 | 0 | 100 | 110 | 0 | 71 | 0 | 361 | 302 |  | 0 | 350 | 145 | 84 | 95 | 55 | 0 | 0 | 0 | 0 | 99 | 93 | 32 | 12 | 0 | 0 | 0 | 53 | 35 | 55 | 22 | 25 | 13 | 25 | 33 | 16 | 0 | 43 | 35 | 0 | 0 | 25 | 219 | 0 | 0 | 0 |  | 0 | 0 | 0 | 20 | 52 | 50 | 20 | 27 | 0 | 0 | 80 | 310 | 260 | 197 | 8 | 96 | 33 | 10 | 0 | 51 | 0 | 0 | 34 | 18 | 5 | 25 | 18 | 144 | 149 | 64 | 22 | 1.8 | 86 | 30 | 50 | 45 | 130 | 192 | 40 | 86 | 0 | 100 | 18 | 0 | 9 | 310 | 24 | 8 | 0 | 245 | 0 | 0 | 192 | 0 | 105 | 13.8 | 100 | 0 | 83 | 0 | 35 | 87 | 0 | 2.6 | 180 | 0 | 0 | 17 | 113 | 100 | 0 | 104 |  | 908 | 0 | 365 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 8 | 89 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 20 | 11 | 8 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 171 | 0 | 75 | 0 | 150 | 0 | 401 | 0 | 0 | 55 | 0 | 79 | 0 | 3.6 | 0 | 200 |  | 6736.2 | 3072.6 | 9808.8 | 3450 | 908 | 1981 | 2723 | 351 | 78 | 152 | 144 | 21.8 | 0 | 93.34
16:00 | 28 | 0 | 140 | 110 | 0 | 72 | 0 | 347 | 302 |  | 0 | 350 | 130 | 91 | 96 | 55 | 0 | 0 | 0 | 0 | 99 | 93 | 16 | 12 | 0 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 17 | 28 | 33 | 0 | 0 | 43 | 35 | 0 | 0 | 25 | 218 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 43 | 37 | 20 | 27 | 0 | 0 | 80 | 295 | 250 | 181 | 8 | 86 | 34 | 10 | 0 | 51 | 0 | 0 | 16 | 17 | 8 | 25 | 19 | 140 | 152 | 56 | 20 | 0.8 | 86 | 30 | 50 | 48 | 130 | 183 | 40 | 86 | 0 | 100 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 245 | 0 | 0 | 200 | 0 | 113 | 8.9 | 100 | 0 | 40 | 0 | 8 | 50 | 0 | 2 | 180 | 0 | 0 | 0 | 105 | 100 | 0 | 104 |  | 908 | 0 | 345 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 21 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 161 | 0 | 75 | 0 | 150 | 0 | 367 | 0 | 0 | 35 | 0 | 76 | 0 | 3 | 50 | 260 |  | 6491.7 | 3075 | 9566.7 | 3395 | 908 | 1938 | 2547 | 410 | 78 | 136 | 140 | 14.7 | 0 | 93.34
17:00 | 28 | 0 | 140 | 110 | 0 | 72 | 0 | 345 | 302 |  | 0 | 350 | 140 | 92 | 96 | 30 | 27 | 0 | 0 | 0 | 70 | 93 | 0 | 12 | 0 | 0 | 0 | 17 | 35 | 17 | 0 | 25 | 17 | 28 | 33 | 0 | 0 | 42 | 35 | 0 | 0 | 8 | 205 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 18 | 19 | 20 | 27 | 0 | 0 | 80 | 295 | 250 | 181 | 8 | 92 | 35 | 10 | 0 | 15 | 0 | 0 | 8 | 17 | 8 | 25 | 18 | 132 | 150 | 64 | 20 | 0.4 | 86 | 30 | 50 | 10 | 130 | 188 | 40 | 20 | 0 | 100 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 170 | 0 | 0 | 200 | 0 | 113 | 3.6 | 100 | 0 | 20 | 0 | 8 | 16 | 0 | 0.9 | 128 | 0 | 0 | 0 | 84 | 100 | 0 | 104 |  | 901 | 0 | 345 | 0 | 49 | 120 | 0 | 0 | 0 | 10 | 0 | 90 | 21 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 161 | 0 | 75 | 0 | 150 | 0 | 404 | 0 | 0 | 0 | 0 | 81 | 0 | 1.4 | 65 | 350 |  | 5912.9 | 3044.4 | 8957.3 | 3397 | 901 | 1825 | 1989 | 500 | 77 | 130 | 132 | 6.3 | 0 | 93.35
18:00 | 28 | 0 | 140 | 110 | 0 | 72 | 0 | 340 | 252 |  | 0 | 300 | 125 | 92 | 97 | 30 | 25 | 0 | 0 | 0 | 70 | 93 | 48 | 12 | 0 | 0 | 0 | 38 | 35 | 17 | 0 | 25 | 17 | 0 | 33 | 0 | 0 | 42 | 35 | 0 | 0 | 8 | 222 | 0 | 0 | 0 |  | 0 | 0 | 31 | 0 | 26 | 18 | 20 | 36 | 0 | 0 | 80 | 275 | 250 | 180 | 8 | 86 | 35 | 10 | 0 | 15 | 0 | 0 | 25 | 18 | 10 | 25 | 18 | 130 | 154 | 64 | 20 | 0 | 86 | 30 | 11 | 10 | 110 | 197 | 40 | 20 | 0 | 70 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 155 | 0 | 0 | 200 | 0 | 113 | 0 | 100 | 0 | 38 | 0 | 8 | 50 | 0 | 0 | 88 | 0 | 0 | 45 | 93 | 100 | 0 | 104 |  | 900 | 0 | 270 | 0 | 49 | 120 | 0 | 0 | 0 | 0 | 0 | 83 | 31 | 32 | 0 | 0 | 0 | 0 | 5 | 15 | 0 | 0 | 10 | 0 | 3 | 20 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 78 | 0 | 130 | 0 | 240 | 0 | 0 | 4 | 0 | 85 | 0 | 0.2 | 70 | 340 |  | 5848 | 2794.2 | 8642.2 | 3215 | 900 | 1514 | 2084 | 490 | 77 | 232 | 130 | 0.2 | 0 | 93.35
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 28 | 0 | 140 | 110 | 0 | 72 | 0 | 348 | 346 |  | 0 | 450 | 130 | 92 | 97 | 31 | 34 | 0 | 0 | 0 | 100 | 93 | 149 | 43 | 0 | 0 | 0 | 53 | 55 | 52 | 22 | 25 | 17 | 28 | 33 | 36 | 0 | 42 | 35 | 0 | 0 | 14 | 205 | 0 | 0 | 0 |  | 0 | 0 | 102 | 10 | 79 | 32 | 20 | 36 | 0 | 0 | 80 | 325 | 275 | 181 | 8 | 90 | 35 | 10 | 0 | 25 | 0 | 50 | 25 | 18 | 8 | 33 | 20 | 162 | 154 | 72 | 20 | 0 | 86 | 30 | 50 | 38 | 163 | 185 | 65 | 87 | 0 | 140 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 225 | 87 | 0 | 192 | 29 | 113 | 0 | 100 | 7 | 75 | 0 | 55 | 105 | 0 | 0 | 215 | 0 | 0 | 114 | 113 | 100 | 0 | 104 |  | 899 | 0 | 345 | 0 | 115 | 140 | 0 | 0 | 0 | 0 | 40 | 90 | 32 | 64 | 0 | 0 | 0 | 25 | 34 | 90 | 0 | 0 | 43 | 43 | 25 | 21 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 165 | 0 | 79 | 50 | 170 | 0 | 396 | 53 | 0 | 57 | 0 | 84 | 0 | 0 | 106 | 463 |  | 7581 | 3801 | 11382 | 3589 | 899 | 2124 | 3260 | 613 | 77 | 658 | 162 | 0 | 0 | 93.35
19:30 | 28 | 0 | 140 | 110 | 0 | 72 | 0 | 342 | 346 |  | 0 | 450 | 140 | 93 | 97 | 45 | 150 | 0 | 0 | 0 | 100 | 93 | 149 | 100 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 28 | 28 | 33 | 51 | 0 | 42 | 35 | 0 | 0 | 25 | 204 | 0 | 0 | 0 |  | 0 | 0 | 102 | 20 | 89 | 50 | 20 | 36 | 0 | 0 | 80 | 300 | 265 | 189 | 8 | 96 | 35 | 10 | 0 | 45 | 0 | 50 | 34 | 18 | 10 | 33 | 20 | 170 | 151 | 72 | 20 | 0 | 86 | 30 | 50 | 49 | 163 | 182 | 65 | 87 | 0 | 140 | 18 | 0 | 10 | 310 | 24 | 11 | 0 | 225 | 0 | 0 | 192 | 0 | 113 | 0 | 100 | 16 | 96 | 0 | 115 | 105 | 0 | 0 | 215 | 0 | 0 | 114 | 113 | 100 | 0 | 104 |  | 899 | 0 | 345 | 0 | 115 | 155 | 0 | 0 | 0 | 0 | 40 | 90 | 33 | 80 | 0 | 0 | 0 | 50 | 34 | 96 | 0 | 0 | 43 | 43 | 32 | 21 | 11 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 171 | 0 | 79 | 100 | 210 | 0 | 372 | 70 | 0 | 102 | 0 | 84 | 0 | 0 | 106 | 500 |  | 7867 | 4032 | 11899 | 3719 | 899 | 2152 | 3520 | 651 | 77 | 711 | 170 | 0 | 0 | 0
20:00 | 28 | 0 | 140 | 110 | 0 | 72 | 0 | 341 | 345 |  | 0 | 450 | 145 | 91 | 97 | 45 | 159 | 0 | 0 | 0 | 100 | 93 | 149 | 89 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 29 | 28 | 33 | 51 | 0 | 42 | 35 | 0 | 0 | 25 | 204 | 0 | 0 | 0 |  | 0 | 0 | 102 | 20 | 89 | 50 | 20 | 36 | 0 | 0 | 80 | 275 | 250 | 189 | 8 | 96 | 35 | 10 | 0 | 45 | 0 | 48 | 34 | 18 | 10 | 33 | 20 | 174 | 152 | 72 | 20 | 0 | 86 | 30 | 50 | 49 | 163 | 185 | 63 | 85 | 0 | 140 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 243 | 0 | 0 | 192 | 0 | 113 | 0 | 100 | 16 | 95 | 0 | 115 | 104 | 0 | 0 | 216 | 0 | 0 | 114 | 113 | 100 | 0 | 104 |  | 900 | 0 | 345 | 0 | 115 | 170 | 0 | 0 | 0 | 0 | 40 | 90 | 35 | 80 | 0 | 0 | 0 | 50 | 34 | 98 | 0 | 0 | 47 | 43 | 31 | 21 | 11 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 164 | 0 | 78 | 100 | 210 | 0 | 378 | 90 | 0 | 107 | 0 | 84 | 0 | 0 | 106 | 500 |  | 7816 | 4077 | 11893 | 3683 | 900 | 2126 | 3554 | 650 | 77 | 729 | 174 | 0 | 0 | 93.36
21:00 | 28 | 0 | 140 | 110 | 0 | 72 | 0 | 340 | 352 |  | 0 | 450 | 140 | 91 | 97 | 45 | 300 | 0 | 0 | 0 | 100 | 93 | 149 | 87 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 29 | 28 | 25 | 51 | 0 | 42 | 35 | 0 | 0 | 25 | 204 | 0 | 0 | 0 |  | 0 | 0 | 102 | 20 | 85 | 50 | 20 | 42 | 0 | 0 | 80 | 275 | 250 | 180 | 8 | 95 | 32 | 10 | 0 | 51 | 0 | 50 | 40 | 18 | 8 | 33 | 20 | 172 | 154 | 72 | 20 | 0 | 86 | 30 | 50 | 49 | 163 | 180 | 63 | 85 | 0 | 140 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 253 | 0 | 0 | 200 | 0 | 113 | 0 | 100 | 16 | 92 | 0 | 115 | 104 | 0 | 0 | 216 | 0 | 0 | 114 | 113 | 100 | 0 | 104 |  | 900 | 0 | 345 | 0 | 115 | 195 | 0 | 0 | 0 | 0 | 40 | 90 | 35 | 80 | 0 | 0 | 0 | 50 | 34 | 96 | 0 | 0 | 43 | 43 | 30 | 21 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 153 | 0 | 78 | 100 | 210 | 0 | 348 | 105 | 0 | 113 | 0 | 95 | 0 | 0 | 106 | 535 |  | 7969 | 4132 | 12101 | 3797 | 900 | 2125 | 3596 | 685 | 77 | 749 | 172 | 0 | 0 | 93.36
22:00 | 28 | 0 | 140 | 110 | 0 | 72 | 0 | 343 | 350 |  | 0 | 450 | 145 | 93 | 97 | 45 | 304 | 0 | 0 | 0 | 100 | 93 | 149 | 17 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 29 | 25 | 33 | 51 | 0 | 44 | 35 | 0 | 0 | 25 | 209 | 0 | 0 | 0 |  | 0 | 0 | 102 | 20 | 85 | 50 | 20 | 42 | 0 | 0 | 80 | 275 | 250 | 185 | 8 | 96 | 32 | 10 | 0 | 51 | 0 | 50 | 43 | 18 | 8 | 33 | 20 | 176 | 153 | 72 | 20 | 0 | 86 | 30 | 50 | 49 | 163 | 180 | 63 | 85 | 0 | 140 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 250 | 0 | 0 | 200 | 0 | 113 | 0 | 100 | 0 | 98 | 0 | 115 | 104 | 0 | 0 | 216 | 0 | 0 | 114 | 113 | 100 | 0 | 104 |  | 901 | 0 | 345 | 0 | 115 | 195 | 0 | 0 | 0 | 0 | 40 | 90 | 36 | 80 | 0 | 0 | 0 | 50 | 0 | 96 | 0 | 0 | 43 | 43 | 30 | 22 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 157 | 0 | 78 | 100 | 210 | 0 | 371 | 105 | 0 | 113 | 0 | 105 | 0 | 0 | 106 | 530 |  | 7932 | 4133 | 12065 | 3823 | 901 | 2158 | 3533 | 680 | 79 | 715 | 176 | 0 | 0 | 93.36
23:00 | 28 | 0 | 140 | 110 | 0 | 72 | 0 | 349 | 350 |  | 0 | 450 | 150 | 93 | 97 | 45 | 308 | 0 | 0 | 0 | 100 | 93 | 149 | 12 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 29 | 25 | 33 | 51 | 0 | 44 | 35 | 0 | 0 | 25 | 214 | 0 | 0 | 0 |  | 0 | 0 | 102 | 20 | 85 | 50 | 20 | 42 | 0 | 0 | 80 | 290 | 265 | 193 | 8 | 96 | 29 | 10 | 0 | 51 | 0 | 50 | 43 | 18 | 8 | 33 | 20 | 174 | 100 | 72 | 22 | 0 | 91 | 30 | 50 | 49 | 163 | 198 | 62 | 85 | 0 | 140 | 18 | 0 | 10 | 305 | 24 | 11 | 0 | 250 | 0 | 0 | 200 | 0 | 114 | 0 | 100 | 0 | 97 | 0 | 115 | 104 | 0 | 0 | 216 | 0 | 0 | 114 | 113 | 100 | 0 | 104 |  | 901 | 0 | 350 | 0 | 115 | 195 | 0 | 0 | 0 | 0 | 40 | 90 | 37 | 80 | 0 | 0 | 0 | 50 | 0 | 96 | 0 | 0 | 43 | 43 | 30 | 22 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 163 | 0 | 79 | 100 | 212 | 0 | 371 | 105 | 0 | 113 | 0 | 107 | 0 | 0 | 106 | 530 |  | 7956 | 4150 | 12106 | 3857 | 901 | 2165 | 3535 | 680 | 79 | 715 | 174 | 0 | 0 | 93.37
24:00 | 28 | 0 | 140 | 110 | 0 | 72 | 0 | 349 | 350 |  | 0 | 450 | 140 | 93 | 97 | 45 | 298 | 0 | 0 | 0 | 100 | 93 | 149 | 12 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 29 | 25 | 33 | 51 | 0 | 45 | 35 | 0 | 0 | 25 | 204 | 0 | 0 | 0 |  | 0 | 0 | 102 | 20 | 89 | 50 | 20 | 42 | 0 | 0 | 80 | 275 | 250 | 177 | 8 | 96 | 32 | 10 | 0 | 51 | 0 | 50 | 43 | 18 | 8 | 33 | 20 | 168 | 101 | 72 | 22 | 0 | 91 | 30 | 50 | 49 | 130 | 198 | 63 | 85 | 0 | 140 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 250 | 0 | 0 | 200 | 0 | 113 | 0 | 100 | 0 | 98 | 0 | 115 | 104 | 0 | 0 | 216 | 0 | 0 | 114 | 113 | 100 | 0 | 104 |  | 900 | 0 | 345 | 0 | 115 | 195 | 0 | 0 | 0 | 0 | 40 | 89 | 35 | 80 | 0 | 60 | 0 | 50 | 0 | 96 | 0 | 0 | 43 | 43 | 30 | 22 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 163 | 0 | 77 | 100 | 213 | 0 | 341 | 105 | 0 | 113 | 0 | 106 | 0 | 0 | 106 | 530 |  | 7846 | 4169 | 12015 | 3851 | 900 | 2093 | 3528 | 680 | 80 | 715 | 168 | 0 | 0 | 93.37
KWH | 561000 | 0 | 2744000 | 2712150 | 0 | 1718727 | 0 | 8442960 | 7724000 |  | 0 | 8912500 | 3346793 | 2075520 | 1922376 | 1072404 | 4787138 | 0 | 0 | 0 | 2136960 | 2007216 | 1261440 | 472575 | 0 | 0 | 0 | 1050120 | 1013432 | 787756 | 408960 | 600000 | 556920 | 657200 | 767700 | 489240 | 0 | 1001018 | 852000 | 0 | 0 | 371610 | 5057508 | 0 | 0 | 0 |  | 0 | 0 | 824619 | 392640 | 1333440 | 848640 | 468048 | 855360 | 0 | 0 | 1933474 | 7213000 | 6376000 | 4437000 | 217454 | 2186110 | 736560 | 544320 | 0 | 1087504 | 0 | 287176 | 596957 | 428688 | 190980 | 701100 | 440160 | 3550080 | 3499760 | 1491840 | 469152 | 14850 | 2111000 | 720240 | 1117800 | 1111536 | 3432434 | 4378000 | 1307616 | 1858560 | 0 | 3090830 | 420000 | 0 | 245700 | 7204000 | 573672 | 198240 | 0 | 4978035 | 46498 | 0 | 4776000 | 21460 | 2453760 | 84915 | 2210880 | 88800 | 1761381 | 0 | 1496400 | 1678308 | 0 | 36119 | 4270473 | 0 | 0 | 927960 | 2367120 | 2294400 | 0 | 2369280 |  | 21701090 | 0 | 8432928 | 0 | 2063040 | 3490560 | 0 | 0 | 0 | 5760 | 537750 | 2150942 | 618745 | 1668480 | 0 | 19000 | 0 | 384944 | 124787 | 1739064 | 0 | 0 | 410400 | 457920 | 265065 | 491040 | 251352 | 209844 | 0 | 0 | 3682200 | 0 | 0 | 0 | 0 | 4297355 | 0 | 1708700 | 692160 | 4866582 | 0 | 9191636 | 612960 | 0 | 1451424 | 108576 | 1805760 | 0 | 45636 | 1657728 | 9768100 |  | 166267552 | 84911528 | 251179080 | 89151817 | 21701090 | 48291368 | 64206072 | 13450300 | 1853018 | 8793815 | 3550080 | 181520 | 0
Fuel Cost | 920040 | 0 | 4006240 | 3986860.5 | 0 | 2268719.64 | 0 | 8527389.6 | 7955720 |  | 0 | 9714625 | 3714940.23 | 15753196.8 | 13245170.64 | 9072537.84 | 4978623.52 | 0 | 0 | 0 | 16091308.8 | 18305809.92 | 12412569.6 | 4357141.5 | 0 | 0 | 0 | 7665876 | 7833829.36 | 7767274.16 | 306720 | 450000 | 0 | 0 | 0 | 4730950.8 | 0 | 270274.86 | 230040 | 0 | 0 | 3452256.9 | 5512683.72 | 0 | 0 | 0 |  | 0 | 0 | 7998804.3 | 3749712 | 11600928 | 6721228.8 | 589740.48 | 2540419.2 | 0 | 0 | 2842206.78 | 5337620 | 6376000 | 4082040 | 280515.66 | 2514026.5 | 832312.8 | 762048 | 0 | 1859631.84 | 0 | 2900477.6 | 5700939.35 | 544433.76 | 143235 | 1226925 | 330120 | 26625600 | 3709745.6 | 13545907.2 | 595823.04 | 236709 | 3462040 | 1152384 | 1989684 | 1733996.16 | 3912974.76 | 4553120 | 2576003.52 | 3549849.6 | 0 | 5347135.9 | 919800 | 0 | 501228 | 7276040 | 430254 | 150662.4 | 0 | 37633944.6 | 789536.04 | 0 | 24835200 | 358811.2 | 24144998.4 | 992656.35 | 18018672 | 963480 | 12417736.05 | 0 | 13647168 | 15860010.6 | 0 | 0 | 32284775.88 | 0 | 0 | 9261040.8 | 20286218.4 | 15280704 | 0 | 0 |  | 124998278.4 | 0 | 8854574.4 | 0 | 16215494.4 | 48379161.6 | 0 | 0 | 0 | 60364.8 | 5603355 | 2430564.46 | 959054.75 | 16284364.8 | 0 | 38950 | 0 | 3787848.96 | 1267835.92 | 15390716.4 | 0 | 0 | 3976776 | 4437244.8 | 2571130.5 | 942796.8 | 389595.6 | 158851.908 | 0 | 0 | 19957524 | 0 | 0 | 0 | 0 | 5672508.6 | 0 | 2563050 | 11773641.6 | 5693900.94 | 0 | 9099719.64 | 6399302.4 | 0 | 13774013.76 | 1024957.44 | 14012697.6 | 0 | 504277.8 | 12250609.92 | 42881959 |  | 551508073.96 | 402355122.198 | 953863196.158 | 99253536.428 | 124998278.4 | 58299668.65 | 480866985.99 | 62839483 | 500314.86 | 98745685.68 | 26625600 | 1733643.15 | 0
Yesterday Day Peak | 28 | 0 | 100 | 110 | 0 | 71 | 0 | 345 | 302 |  | 0 | 350 | 125 | 75 | 52 | 46 | 0 | 0 | 0 | 0 | 90 | 50 | 32 | 9 | 0 | 0 | 0 | 53 | 35 | 40 | 22 | 25 | 13 | 28 | 33 | 22 | 0 | 43 | 35 | 0 | 0 | 16 | 218 | 0 | 0 | 0 |  | 0 | 0 | 0 | 20 | 32 | 10 | 20 | 23 | 0 | 0 | 80 | 270 | 250 | 192 | 8 | 86 | 32 | 10 | 0 | 51 | 0 | 0 | 5 | 18 | 0 | 33 | 18 | 118 | 153 | 64 | 22 | 2.3 | 91 | 30 | 44 | 45 | 130 | 199 | 40 | 87 | 0 | 100 | 17 | 0 | 10 | 260 | 24 | 8 | 0 | 155 | 0 | 0 | 200 | 0 | 96 | 0 | 100 | 0 | 52 | 0 | 35 | 60 | 0 | 5.2 | 180 | 0 | 0 | 34 | 108 | 90 | 0 | 104 |  | 916 | 0 | 340 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 40 | 90 | 20 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 21 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 171 | 0 | 76 | 0 | 150 | 0 | 356 | 0 | 0 | 32 | 32 | 52 | 0 | 7.2 | 50 | 0 |  | 9075.7 | DayPeak
Yesterday Evening Peak | 28 | 0 | 140 | 110 | 0 | 72 | 0 | 340 | 352 | 0 | 0 | 450 | 140 | 91 | 97 | 45 | 300 | 0 | 0 | 0 | 100 | 93 | 149 | 87 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 29 | 28 | 25 | 51 | 0 | 42 | 35 | 0 | 0 | 25 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 20 | 85 | 50 | 20 | 42 | 0 | 0 | 80 | 275 | 250 | 180 | 8 | 95 | 32 | 10 | 0 | 51 | 0 | 50 | 40 | 18 | 8 | 33 | 20 | 172 | 154 | 72 | 20 | 0 | 86 | 30 | 50 | 49 | 163 | 180 | 63 | 85 | 0 | 140 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 253 | 0 | 0 | 200 | 0 | 113 | 0 | 100 | 16 | 92 | 0 | 115 | 104 | 0 | 0 | 216 | 0 | 0 | 114 | 113 | 100 | 0 | 104 |  | 900 | 0 | 345 | 0 | 115 | 195 | 0 | 0 | 0 | 0 | 40 | 90 | 35 | 80 | 0 | 0 | 0 | 50 | 34 | 96 | 0 | 0 | 43 | 43 | 30 | 21 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 153 | 0 | 78 | 100 | 210 | 0 | 348 | 105 | 0 | 113 | 0 | 95 | 0 | 0 | 106 | 535 |  | 12101 | EvPeak
Forecast for Evening | 28 | 0 | 140 | 110 | 0 | 90 | 0 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 96 | 55 | 335 | 0 | 0 | 0 | 100 | 93 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 42 | 35 | 0 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 0 |  | 100 | 100 | 95 | 50 | 21 | 30 | 0 | 0 | 100 | 360 | 360 | 225 | 8 | 100 | 36 | 10 | 0 | 51 | 0 | 44 | 43 | 21 | 11 | 33 | 20 | 173 | 160 | 72 | 22 | 0 | 90 | 30 | 51 | 44 | 163 | 210 | 66 | 86 | 0 | 140 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 133 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 104 |  | 918 | 16 | 410 | 0 | 115 | 225 | 0 | 0 | 30 | 60 | 40 | 90 | 33 | 110 | 0 | 65 | 0 | 50 | 40 | 100 | 0 | 0 | 50 | 43 | 32 | 22 | 11 | 11 | 0 | 0 | 150 | 0 | 10 | 0 | 0 | 220 | 0 | 80 | 100 | 220 | 0 | 414 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 490
Forecast for Day | 28 | 0 | 100 | 110 | 0 | 90 | 0 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 96 | 55 | 335 | 0 | 0 | 0 | 100 | 93 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 42 | 35 | 0 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 0 |  | 100 | 100 | 95 | 50 | 21 | 20 | 0 | 0 | 80 | 360 | 360 | 225 | 8 | 100 | 35 | 10 | 0 | 51 | 0 | 0 | 43 | 21 | 11 | 33 | 20 | 157 | 157 | 72 | 22 | 1.6 | 90 | 30 | 51 | 44 | 163 | 210 | 66 | 86 | 0 | 140 | 18 | 0 | 10 | 341 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 100 | 133 | 20 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 104 |  | 918 | 0 | 410 | 0 | 115 | 225 | 0 | 0 | 0 | 0 | 40 | 0 | 33 | 110 | 0 | 65 | 0 | 0 | 0 | 100 | 0 | 0 | 50 | 43 | 0 | 22 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 |  | 80 | 80 | 220 | 0 | 414 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 450
Generation at 08:00(Today) | 28 | 0 | 140 | 110 | 0 | 72 | 0 | 340 | 263 | 0 | 0 | 300 | 143 |  | 80 | 15 | 300 | 0 | 0 | 0 | 92 | 93 | 16 | 12 | 0 | 0 | 0 | 17 | 55 | 55 | 22 | 25 | 30 | 22 | 33 | 0 | 0 | 41 | 35 | 0 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 20 | 13 | 0 | 0 | 80 | 260 | 250 | 178 | 8 | 95 | 31 | 10 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 20 | 128 | 102 | 71 | 22 | 0.6 | 91 | 30 | 50 | 49 | 110 | 186 | 63 | 83 | 0 | 0 | 18 | 0 | 10 | 280 | 8 | 8 | 0 | 268 | 0 | 0 | 180 | 0 | 114 | 7 | 100 | 0 | 86 | 0 | 8 | 16 | 0 | 2.4 | 124 | 0 | 0 | 0 | 113 | 100 | 0 | 104 | 0 | 914 | 0 | 290 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 20 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 142 | 0 | 75 | 0 | 150 | 0 | 267 | 0 | 0 | 0 | 0 | 78 | 0 | 0.7 | 72 | 450 | 0
199
| Minimum Generation |  | 8634.4 | 9:00
| Highest Generation |  | 12106 | 23:00
| Day Peak Generation |  | 9075.7 | 12:00
| Evening Peak Generation |  | 12101 | 21:00
| HVDC Max Flow |  | 917 | 10:00
| HVDC EvPeak Flow |  | 900 | 21:00
| Load factor L.F |  | 86.45%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-09-05
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-09-04 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9075.7 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 9300.7 | MW
Evening Peak Generation : |  | 12101 | MW Hour : | 21:00 | Available Max Generation : |  | 14876 | MW
E.P. Demand (at gen end) : |  | 12101 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12500 | MW
Maximum Generation : |  | 12106 | MW Hour : | 23:00 | Reserve(Generation end) |  | 2376 | MW
Total Gen. (MKWH) : |  | 251.1791 | System Load Factor : | 86.45% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -86 | MW at | 19:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-09-05
Actual : | 93.37 | Ft.(MSL) , | Rule curve : | 99.92 | Ft.( MSL )
Gas Consumed : | Total = | 1110.69 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 157553205.078
: |  | Coal : | 62839483 | Oil : | 579612671.67 | Total : | 800005359.748
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4460.267 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1520.452 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1362.9364 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1231.763 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1112.9968 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 898.1584 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 497.4262 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 231.1251 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 692.7272 |  |  | 0 | 0%
Total | 0 |  | 12007.8523 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 10) Sikalbaha 150 MW
|  |  |  | 2) Bibiyana #3 | 11) Payra Unit-1
3) Ghorasal Unit-2,3,7
4) Ashuganj unit-3,4
5) Bhola-225 MW GT-2 & ST
6) Kaptai-1,2,5
7) Raozan #1,2
8) Sirajganj #1
9) Baghabari-71 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Chatak-Sunamganj 132 kV Ckt tripped at 10:34 from Chatak end showing Z2,Y-phase, REL-670 |  |  |  |  | About 26 MW power interruption occurred under Sunamganj S/S area
and was switched on at 10:50. |  |  |  |  | from 10:34 to 10:50.
b) Tongi 132/33 kV T2(both sides) & T3(33 kV side) transformers tripped at 11:42 due to 132 kV LA |  |  |  |  | About 80 MW power interruption occurred under Tongi S/S area
(R-phase) burst and T3 was switched on at 11:50. |  |  |  |  | from 11:42 to 11:50.
c) Payra unit-2 was shut down at 10:44 due to Gopalganj work.
d) Siddhirganj 335 MW CCPP was shut down at 11:50 due to R/H maintenance of GT line at 230 kV Grid
and was synchronized at GT(16:24) & ST(18:57).
e) Siddhirganj 230 kV S/S-Siddhirganj 335 MW P.P. 230 kV GT line was under shut down from 12:38 to
14:53 due to R/H maintenance at Grid.
f) Tangail-Kaliakoir 132 kV Ckt-1 was under shut down from 09:41 to 11:52 for C/M.
g) Barapukuria-Saidpur 132 kV Ckt-2 was under shut down from 08:57 to 11:08 for C/M.
h) Gopalganj-Payra 400 kV Ckt-2 was under shut down from 10:50 to 13:41 for C/M.
i) Gopalganj 400/132 kV T01 transformer was under shut down from 11:02 to 13:03 for C/M.
j) Bogura-Bogura Confidence P.P. 132 kV Ckt-1 was under shut down from 13:45 to 15:10 for C/M.
k) Madunaghat 132/33 kV T2 transformer was under shut down from 08:42 to 16:32 due to 33 kV Bus
upgradation work.
l) Sylhet-Chatak 132 kV Ckt-1 tripped at 20:08 from both ends showing Dist.C-phase trialed at 20:29 |  |  |  |  | About 20 MW power interruption occurred under Chatak S/S area
from Chatak end but showing SOTF. |  |  |  |  | from 20:08 to 23:00.
m) Bhulta 33 kV Capacitor bank was shut down at 21:21 due to R/H at Y-phase bushing.
upgradation work.
n) Baghabari 100 MW GT was synchronized at 23:37.
o) Mymensingh RPCL, GT-2 Force shut down at 22:22 due to AVR problem.
p) Sylhet-Fenchuganj P/S & Sylhet-Fenchuganj S/S both Ckts tripped at 05:14(05/09/2020) showing O/C |  |  |  |  | Full power interruption occurred under Sylhet, Chattak & Sunamganj S/S
due to Boroikandi & Uposhahar 33 kV feeder tripped and was switched on at 05:52(05/09/2020). |  |  |  |  | area from 05:14(05/09/2020) to 05:52(05/09/2020).
As a result Sylhet, Chatak & Sunamganj S/S were isolated from the Grid.
At the same time Sylhet 150 MW, Sylhet 20 MW & Sylhet 10 MW were tripped. .
q) Goalpara 33 kV Bus under T2 & T6 transformer was shut down at 06:24(05/09/2020) for C/M.
r) Sherpur 132/33 kV T2 & T3 transformer was shut down at 07:40(05/09/2020) for C/M.
s) Madunaghat 132/33 kV T1 transformer was shut down at 07:09(05/09/2020) for D/W.
t) Naogaon 132/33 kV T1 & T2 transformer 33 kV side were shut down at 07:19(05/09/2020)(T2) &
07:42(05/09/2020)(T1) to attend R/H.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-09-04 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 28 | 561000 | Unit-1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 140 | 2744000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 110 | 2712150 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 72 | 1718727 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 340 | 8442960 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 352 | 7724000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 8912500
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 91 | 2075520 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 140 | 3346793 | GT-1 Under S/D due to gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 97 | 1922376
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 45 | 1072404 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 87 | 472575 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 408960
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 2136960
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 4787138
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 2007216 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel Shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 1050120
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 1261440
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1013432
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 787756
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 54 | 1156920 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 28 | 657200 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 767700 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 489240
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 253 | 4978035 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 46498 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 21460 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 113 | 2453760 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 104 | 1678308
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2369280
| Dhaka area Total |  |  |  | 5895 | 3511 | 69776428
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 371610
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 84915
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 848640
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 77 | 1853018 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 5057508
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 824619
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 20 | 392640 | Low demand
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2210880
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 468048
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 855360
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 85 | 1333440 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 36119
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 216 | 4270473 | Low demand
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2294400
| Chattogram area Total |  |  |  | 2266 | 1041 | 20901670
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 1933474 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 180 | 4437000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 275 | 7213000 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 250 | 6376000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 32 | 736560 | Gas shortage.
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 10 | 544320 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1087504
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 92 | 1761381 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 287176
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 95 | 2186110
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 16 | 88800 | Low demand
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 428688 | Engine problem
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 190980 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 172 | 3550080
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 701100
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 40 | 596957 | Engine problem
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 440160 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 927960
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 2367120
| Cumilla Area Total |  |  |  | 2980 | 1657 | 36071824
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 154 | 3499760 | Machine problem
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 469152
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 72 | 1491840 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14850
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 4776000
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1496400 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 561 | 11748002
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 86 | 2111000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 720240 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3432434
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 180 | 4378000 | ST under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1117800
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 49 | 1111536
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 198240
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 63 | 1307616 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1858560
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 140 | 3090830
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 420000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 573672
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7204000 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 245700
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1199 | 27769628
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 900 | 21701090
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 2063040
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 195 | 3490560 | Low demand
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 5760 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 345 | 8432928 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 537750
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 692160
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 612960
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 108576 | Reserve
| Khulna Area Total |  |  |  | 2284 | 1800 | 37644824
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 80 | 1668480
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 35 | 618745
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 90 | 2150942 | GT-2 Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 78 | 1708700 | Engine problem
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 535 | 9768100
| Barisal Area Total |  |  |  | 1054 | 818 | 15914967
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 19000 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 384944
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 34 | 124787
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 43 | 410400
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage.
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 153 | 4297355 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 210 | 4866582 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 348 | 9191636 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 265065
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 491040
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 11 | 251352
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 209844
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 457920 | Engine problem
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 96 | 1739064
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 1451424
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 106 | 1657728
| Rajshahi Area Total |  |  |  | 2183 | 1269 | 25818141
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3682200 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Machine problem
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 95 | 1805760 | Engine problem
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 45636
| Rangpur Area Total |  |  |  | 605 | 245 | 5533596
| Total |  |  |  | 19892 | 12101 | 251179080
| Eastern Grid Total |  |  |  | 13766 | 7969 | 166267552
| Western Grid Total |  |  |  | 6126 | 4132 | 84911528
| National Grid Total |  |  |  | 19892 | 12101 | 251179080
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-09-04
| (a) ENTIRE EASTERN GRID : |  | 7690 | MW | (b) ENTIRE WESTERN GRID : |  | 3926 | MW
| i) Dhaka area |  | 3766 | MW | i) Khulna area |  | 1513 | MW
| ii) Chittagong area |  | 1284 | MW | ii) Rajshahi area |  | 1279 | MW
| iii) Comilla area |  | 1228 | MW | iii) Barisal area |  | 356 | MW
| iv) Mymensingh area |  | 907 | MW | iv) Rangpur area |  | 778 | MW
| v) Sylhet area |  | 505 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11616 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 120 | 1:00 | Sherpur | 114 | 22:00 | Jhenida | 116 | 19:00
| Munsiganj | 130 | 22:00 | Srimongal | 54 | 19:30 | Bottail | 118 | 19:30
| Sonargaon | 80 | 0:00 | Shahjibazar | 120 | 19:30 | G.K Project | 56 | 19:00
| Shyampur | 184 | 2:00 | Fenchuganj | 47 | 19:00 | Faridpur | 185 | 0.041667
| Bhulta | 201 | 1:00 | Kulawara | 48 | 21:00 | Madaripur | 105 | 0.91667
| Madanganj | 55 | 1:00 | Sylhet | 125 | 20:00 | Sariatpur | 68 | 21:00
| Shitalakhya | 90 | 0:00 | Chatak | 32 | 20:00 | Gopalganj | 91 | 22:00
| Rahim steel | 4 | 7:00 | Sunamganj | 48 | 19:30 | Bagerhat | 98 | 21:00
| Matuail | 72 | 1:00 | Biani Bazar | 64 | 20:00 | Mongla | 36 | 1:00
| Ghorasal | 78 | 23:00 | Comilla (S) | 176 | 22:00 | Satkhira | 114 | 0.875
| Narsingdi | 168 | 21:00 | Comilla(N) | 109 | 19:30 | Gallamari | 46 | 21:00
| Haripur (SBU) | 90 | 1:00 | Chandpur | 109 | 22:00 | Magura | 56 | 0.8125
| Ullon | 67 | 19:00 | Feni | 127 | 22:00 | Norail | 41 | 21:00
| Hasnabad | 196 | 21:00 | Chowmuhani | 177 | 0:00 | Chuadanga | 92 | 20:00
| Magbazar | 82 | 20:00 | Ashuganj | 65 | 0:00 | Barisal(N) | 41 | 0.79167
| Maniknagar | 82 | 23:00 | Daudkandi | 142 | 21:00 | Barisal (S) | 96 | 0.875
| Bangabhaban | 16 | 1:00 | B.Baria | 164 | 22:00 | Patuakhali | 123 | 0.95833
| Narinda | 76 | 15:00 | Ramganj | 112 | 20:00 | Bhandaria | 58 | 0.875
| Dhanmondi | 125 | 20:00 | Chaddagram | 38 | 21:00 | Borhan Uddin | 45 | 22:00
| Lalbag | 72 | 1:00 | PHP | 3 | 15:00 | Ishurdi | 61 | 21:00
| Madartek | 75 | 23:00 | Madunaghat | 52 | 19:00 | Ruppur Paromanobik | 2 | 21:00
| Dhaka University |  |  | Hathazari | 98 | 0.79167 | Natore | 123 | 21:00
| Fatullah | 34 | 0.041667 | Khulshi | 196 | 0.8125 | Bogra | 169 | 21:00
| Mirpur | 100 | 19:30 | Halishahar | 126 | 0.875 | Noagaon | 129 | 21:00
| Kalyanpur | 111 | 19:00 | Baraulia | 140 | 0.083333 | Rajshahi | 150 | 21:00
| Gulshan | 102 | 19:00 | Sikalbaha | 26 | 0.77083 | Rajshahi New | 12 | 21:00
| Uttara | 91 | 19:00 | Dohazari | 90 | 0.83333 | C.Nawabganj | 77 | 21:00
| Uttara New | 26 | 21:00 | Cox'sbazar | 104 | 0.8125 | Amnura | 46 | 21:00
| Kamrangirchar | 82 | 1l:00 | Chandraghona | 32 | 0.77083 | Pabna | 125 | 19:30
| Savar | 105 | 1:00 | Kaptai | 5 | 0.79167 | Shahjadpur | 94 | 19:00
| Bhasantec | 140 | 19:00 | A. Khaer Stl. | 18 | 0.083333 | Serajganj | 92 | 20:00
| Agargaon | 64 | 19:00 | Bakulia | 92 | 0 | Niyamatpur | 62 | 21:00
| Satmosjid | 84 | 19:00 | Julda | 20 | 0.041667 | Joypurhat | 56 | 21:00
| Tongi | 89 | 0.041667 | TK chemical | 30 | 0.875 | Sherpur(Bogura) | 50 | 20:00
| Kabirpur | 166 | 21:00 | Modern Steel | 12 | 0.041667 | Mohastangor | 52 | 21:00
| Basundhara | 125 | 19:00 | Shahmirpur | 21 | 0.041667 | Rangpur | 148 | 21:00
| Manikganj | 72 | 0.875 | Khagrachhari | 26 | 0.79167 | Lalmonirhat | 58 | 19:00
| Joydevpur | 110 | 21:00 | Matarbari | 34 | 0.95833 | Saidpur | 105 | 21:00
| New Tongi | 96 | 1:00 | Baroiar Hat | 38 | 0.79167 | Purbasadipur | 106 | 21:00
| Korda | 206 | 1:00 | Rangamati | 12 | 0.77083 | Thakurgaon | 88 | 19:30
| Dhamrai | 84 | 21:00 | Abul Khair 230 | 120 | 0.95833 | Palashbari | 124 | 2:00
| Rajendrapur | 96 | 21:00 | BSRM | 106 | 0.625 | Barapukuria | 50 | 21:00
| Valuka | 94 | 21:00 | GPH Ispat | 78 | 0.95833 | Panchagar | 51 | 20:00
| Tangail | 186 | 19:30 | Goalpara | 18 | 0.95833 | Joldhaka | 30 | 20:00
| Mymensing | 237 | 20:00 | Central s/s | 96 | 21:00 | Kurigram | 56 | 19:00
| Kishorganj | 150 | 24:00 | Noapara | 52 | 1:00
| Netrokona | 113 | 19:00 | Jessore | 114 | 20:00
| Jamalpur | 148 | 23:00 | Benapol | 50 | 21:00
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-09-04 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 400 | 12:00 | 391 | 22:00 | Kaliakoir | 383 | 0.75 | 372 | 0.41667
| Bheramara | 395 | 7:00 | 385 | 22:00 | Bhulta | 393 | 0.5 | 383 | 0.41667
| Ashuganj(N) | 400 | 18:00 | 390 | 9:00 | Gopalganj | 418 | 0.58333 | 391 | 0.5
| Payra | 420 | 14:00 | 0 | 11:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 1:00 | 235 | 1:00 | Comilla (N) | 236 | 12:00 | 229 | 10:00
| Ishurdi | 237 | 1:00 | 225 | 21:00 | Hathazari | 229 | 18:30 | 213 | 10:00
| Ashuganj | 240 | 14:00 | 235 | 11:00 | Megnaghat | 234 | 12:00 | 230 | 1:00
| Serajganj | 233 | 18:00 | 226 | 1:00 | Fenchuganj | 241 | 12:00 | 234 | 8:00
| Baghabari | 240 | 11:00 | 236 | 1:00 | Siddhirganj | 233 | 4:00 | 228 | 10:00
| Barapukuria | 237 | 18:00 | 217 | 1:00 | Maniknagar | 230 | 5:00 | 227 | 9:00
| Bogra | 227 | 18:00 | 214 | 21:00 | Agargaon | 229 | 18:00 | 222 | 10:00
| Rajshahi | 227 | 18:00 | 215 | 22:00 | Barisal | 249 | 16:00 | 235 | 22:00
| Khulna South | 238 | 18:00 | 228 | 5:00 | AKSML | 224 | 18:00 | 210 | 9:00
| Rampura | 229 | 5:00 | 226 | 10:00 | BSRM | 227 | 18:00 | 215 | 9:00
| Haripur | 230 | 12:00 | 225 | 10:00 | Bibiyana | 238 | 13:00 | 232 | 17:00
| Hasnabad | 230 | 7:00 | 227 | 10:00 | Bhulta | 232 | 19:00 | 228 | 17:00
| Shyampur | 229 | 18:00 | 221 | 11:00 | Ashuganj (S) | 238 | 4:00 | 232 | 9:00
| Aminbazar | 230 | 18:00 | 223 | 10:00 | Kaliakoir | 233 | 18:00 | 226 | 9:00
| Tongi | 231 | 12:00 | 221 | 9:00 | GPH | 225 | 18:00 | 211 | 10:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 135 | 12:00 | 130 | 10:00 | Hathazari | 136 | 0.75 | 127 | 0.41667
| Munsiganj | 138 | 12:00 | 128 | 10:00 | Khulshi | 135 | 0.79167 | 126 | 0.33333
| Sonargaon | 136 | 18:00 | 132 | 7:00 | Halishahar | 140 | 0.041667 | 128 | 0.41667
| Shyampur | 136 | 18:00 | 131 | 10:00 | Baraulia | 137 | 0.79167 | 127 | 0.375
| Bhulta | 130 | 14:00 | 124 | 1:00 | Sikalbaha | 138 | 19:00 | 129 | 0.375
| Madanganj | 136 | 13:00 | 126 | 10:00 | Dohazari | 135 | 19:00 | 126 | 0.375
| Shitalakhya | 142 | 18:00 | 132 | 11:00 | Cox'sbazar | 130 | 0.33333 | 116 | 0.77083
| Rahim steal | 135 | 12:00 | 131 | 10:00 | Chandraghona | 136 | 0.79167 | 127 | 0.41667
| Matuail | 135 | 12:00 | 130 | 10:00 | Kaptai | 135 | 18:00 | 127 | 0.41667
| Ghorasal | 138 | 12:00 | 136 | 1:00 | A. Khaer Stl. | 135 | 0.8125 | 128 | 8:00
| Narsinghdi | 132 | 12:00 | 125 | 21:00 | Bakulia | 137 | 0.875 | 127 | 0.41667
| Haripur (SBU) | 135 | 12:00 | 130 | 10:00 | Julda | 138 | 0.77083 | 127 | 0.41667
| Ullon | 133 | 12:00 | 131 | 1:00 | TK Chemical | 137 | 0.79167 | 128 | 10:00
| Hasnabad | 138 | 19:00 | 133 | 10:00 | Modern Steel | 137 | 0.79167 | 126 | 0.41667
| Magbazar | 134 | 5:00 | 131 | 10:00 | Shahmirpur | 138 | 0.79167 | 129 | 0.375
| Maniknagar | 135 | 3:00 | 132 | 10:00 | Khagrachhari | 134 | 0.79167 | 127 | 0.41667
| Bangabhaban | 135 | 3:00 | 132 | 10:00 | Matarbari | 130 | 0.5 | 120 | 0.375
| Narinda | 135 | 3:00 | 132 | 10:00 | Baroiar Hat | 136 | 0.75 | 128 | 0.29167
| Dhanmondi | 133 | 12:00 | 131 | 1:00 | Rangamati | 135 | 0.79167 | 127 | 10:00
| Lalbag | 139 | 19:00 | 130 | 11:00 | Goalpara S/S | 136 | 6:00 | 132 | 18:30
| Madartek | 133 | 3:00 | 130 | 10:00 | Khulna Central S/S | 137 | 0.75 | 133 | 20:00
| Dhaka University |  |  |  |  | Noapara | 136 | 18:00 | 128 | 3:00
| Fatuiiah | 136 | 0.54167 | 131 | 10:00 | Jessore | 133 | 18:00 | 121 | 21:00
| Mirpur | 134 | 6:00 | 127 | 10:00 | Benapol | 133 | 18:00 | 123 | 20:00
| Kalyanpur | 132 | 6:00 | 129 | 11:00 | Jhenida | 131 | 0.75 | 114 | 20:00
| Gulshan | 133 | 6:00 | 130 | 11:00 | Bottail | 136 | 18:00 | 125 | 21:00
| Uttara | 130 | 18:30 | 127 | 11:00 | G.K Project | 142 | 0.75 | 135 | 1:00
| Uttara New | 137 | 13:00 | 130 | 10:00 | Faridpur | 135 | 18:00 | 126 | 21:00
| Kamrangirchar | 137 | 19:00 | 130 | 10:00 | Madaripur | 138 | 0.75 | 130 | 21:00
| Savar | 133 | 18:00 | 126 | 11:00 | Shariyatpur S/S | 138 | 0.25 | 127 | 22:00
| Bhasantec | 133 | 18:00 | 129 | 11:00 | Gopalganj | 141 | 17:00 | 127 | 23:00
| Agargaon | 134 | 18:00 | 130 | 11:00 | Bagerhat | 131 | 13:00 | 125 | 20:00
| Satmosjid | 134 | 18:00 | 129 | 11:00 | Mongla | 130 | 0.5 | 122 | 4:00
| Tongi | 140 | 0.5 | 132 | 10:00 | Satkhira | 137 | 0.75 | 128 | 20:00
| Kabirpur | 138 | 18:00 | 131 | 21:00 | Gallamari | 138 | 12:00 | 132 | 2:00
| Basundhara | 133 | 8:00 | 130 | 10:00 | Magura | 130 | 18:00 | 112 | 21:00
| Manikganj | 140 | 21:00 | 133 | 9:00 | Norail | 126 | 0.70833 | 107 | 21:00
| Joydevpur | 143 | 12:00 | 138 | 17:00 | Chuadanga | 126 | 18:00 | 104 | 20:00
| New Tongi | 139 | 0.5 | 131 | 9:00 | Barisal(N) | 140 | 14:00 | 131 | 22:00
| Kodda | 137 | 18:00 | 126 | 0.41667 | Barisal (S) | 139 | 0.75 | 130 | 21:00
| Dhamrai | 137 | 18:00 | 130 | 21:00 | Patuakhali(S) | 136 | 0.75 | 121 | 22:00
| Rajendrapur | 136 | 20:00 | 124 | 10:00 | Bhandaria | 130 | 18:00 | 119 | 18:30
| Valuka | 127 | 18:00 | 113 | 22:00 | Ishurdi | 139 | 18:00 | 132 | 21:00
| Tangail | 138 | 18:00 | 126 | 22:00 | Ruppur Paromanobik | 138 | 18:00 | 132 | 21:00
| Mymensing | 130 | 18:00 | 115 | 23:00 | Natore | 138 | 18:00 | 129 | 21:00
| Kishorganj | 130 | 12:00 | 118 | 22:00 | Bogra | 138 | 18:00 | 128 | 21:00
| Netrokona | 128 | 18:00 | 111 | 21:00 | Noagaon | 133 | 18:00 | 120 | 21:00
| Jamalpur | 140 | 12:00 | 129 | 21:00 | Rajshahi | 136 | 18:00 | 128 | 21:00
| Sherpur | 139 | 12:00 | 127 | 21:00 | Rajshahi New | 136 | 18:00 | 129 | 21:00
| Srimongal | 136 | 7:00 | 133 | 0.041667 | C.Nawabganj | 133 | 18:00 | 126 | 21:00
| Shahjibazar | 135 | 12:00 | 130 | 0.041667 | Amnura | 135 | 18:00 | 126 | 15:00
| Fenchuganj | 135 | 9:00 | 132 | 0.041667 | Pabna | 136 | 18:00 | 130 | 21:00
| Khulawara | 134 | 9:00 | 131 | 0.041667 | Shahjadpur | 140 | 18:00 | 133 | 21:00
| Sylhet | 133 | 8:00 | 129 | 0.95833 | Serajganj | 136 | 18:00 | 128 | 19:30
| Chatak | 131 | 11:00 | 126 | 22:00 | Niyamatpur | 129 | 18:00 | 116 | 21:00
| Sunamganj | 130 | 11:00 | 121 | 0.8125 | Joypurhat | 133 | 18:00 | 119 | 21:00
| Biani Bazar | 131 | 10:00 | 120 | 1904-01-02 | Sherpur(Bogura) | 138 | 18:00 | 128 | 21:00
| Comilla(s) | 128 | 6:00 | 120 | 18:30 | Mohastangor | 137 | 18:00 | 124 | 21:00
| Comilla(n) | 140 | 18:00 | 132 | 10:00 | Rangpur | 130 | 18:00 | 115 | 21:00
| Chandpur | 135 | 19:00 | 128 | 23:00 | Lalmonirhat | 130 | 18:00 | 115 | 21:00
| Feni | 135 | 20:00 | 130 | 7:00 | Saidpur | 132 | 18:00 | 117 | 1:00
| Chowmuhani | 135 | 7:00 | 127 | 17:00 | Purbasadipur | 130 | 18:00 | 111 | 21:00
| Ashuganj | 136 | 12:00 | 130 | 7:00 | Thakurgaon | 128 | 18:00 | 110 | 21:00
| Daudkandi | 137 | 18:00 | 128 | 10:00 | Palashbari | 129 | 18:00 | 118 | 1:00
| B.Baria | 132 | 11:00 | 126 | 22:00 | Barapukuria | 137 | 18:00 | 117 | 1:00
| Ramganj | 131 | 19:30 | 123 | 18:00 | Panchagar | 128 | 18:00 | 107 | 21:00
| Chaddagram | 135 | 18:00 | 130 | 7:00 | Joldhaka | 130 | 18:00 | 112 | 21:00
| PHP | 136 | 18:00 | 126 | 10:00 | Kurigram | 132 | 18:00 | 112 | 21:00
| Madanhat | 139 | 19:00 | 128 | 10:00

## L-Curve
Date | 2020-09-04
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 68 | 7846 | 4169 | 12015 |  |  |  | QF-LDC-11
0:30 | 116.5 | 7781.5 | 4127 | 11908.5 | Date: | 2020-09-04
1:00 | 165 | 7717 | 4085 | 11802
1:30 | 152.5 | 7620 | 4039.5 | 11659.5
2:00 | 140 | 7523 | 3994 | 11517
2:30 | 129 | 7422.5 | 3906.5 | 11329 | [5 empty] | Gen. at Eve. Peak | 12101 | 12101 MW (21:00 )
3:00 | 118 | 7322 | 3819 | 11141 | [6 empty] | 21:00
3:30 | 115 | 7279 | 3757.5 | 11036.5 | [5 empty] | Gen. at Day Peak | 9075.7 | 9075.7 MW (12:00 )
4:00 | 112 | 7236 | 3696 | 10932 | [6 empty] | 12:00
4:30 | 117 | 7192.5 | 3631.5 | 10824 | [5 empty] | Highest Generation | 12106
5:00 | 122 | 7149 | 3567 | 10716 | [6 empty] | 23:00
5:30 | 214.5 | 6832.895 | 3459.55 | 10292.445
6:00 | 307 | 6516.79 | 3352.1 | 9868.89
6:30 | 284.5 | 6289.595 | 3191.35 | 9480.945
7:00 | 262 | 6062.4 | 3030.6 | 9093
7:30 | 250.5 | 5965.95 | 2982.7 | 8948.65
8:00 | 239 | 5869.5 | 2934.8 | 8804.3
8:30 | 296 | 5776.4 | 2942.95 | 8719.35
9:00 | 353 | 5683.3 | 2951.1 | 8634.4
9:30 | 366.5 | 5790.6 | 2948.35 | 8738.95
10:00 | 380 | 5897.9 | 2945.6 | 8843.5
10:30 | 247.5 | 6063.75 | 2858.1 | 8921.85
11:00 | 115 | 6229.6 | 2770.6 | 9000.2
11:30 | 82.5 | 6209.55 | 2828.4 | 9037.95
12:00 | 50 | 6189.5 | 2886.2 | 9075.7
12:30 | 40.5 | 6367.3 | 2941.4 | 9308.7
13:00 | 31 | 6545.1 | 2996.6 | 9541.7
13:30 | 34 | 6573.7 | 2992.9 | 9566.6
14:00 | 37 | 6602.3 | 2989.2 | 9591.5
14:30 | 46 | 6669.25 | 3030.9 | 9700.15
15:00 | 55 | 6736.2 | 3072.6 | 9808.8
15:30 | 106 | 6613.95 | 3073.8 | 9687.75
16:00 | 157 | 6491.7 | 3075 | 9566.7
16:30 | 254.5 | 6202.3 | 3059.7 | 9262
17:00 | 352 | 5912.9 | 3044.4 | 8957.3
17:30 | 303.5 | 5880.45 | 2919.3 | 8799.75
18:00 | 255 | 5848 | 2794.2 | 8642.2
18:30 | 168.5 | 6714.5 | 3297.6 | 10012.1
19:00 | 82 | 7581 | 3801 | 11382
19:30 | 86 | 7867 | 4032 | 11899
20:00 | 44 | 7816 | 4077 | 11893 |  |  |  | Executive Engineer
20:30 | 46 | 7892.5 | 4104.5 | 11997 |  |  |  | Network Operation Division
21:00 | 48 | 7969 | 4132 | 12101
21:30 | 37 | 7950.5 | 4132.5 | 12083
22:00 | 26 | 7932 | 4133 | 12065 |  |  |  |  | Page 6 of 7
22:30 | 50.5 | 7944 | 4141.5 | 12085.5
23:00 | 75 | 7956 | 4150 | 12106
23:30 | 71.5 | 7901 | 4159.5 | 12060.5
24:00 | 68 | 7846 | 4169 | 12015
12101 MW (21:00 )
9075.7 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-09-04 |  | Energy | 251179080
[10 empty] | 2020-09-04 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3851 | 900 | 2093 | 3535 | 680 | 80 | 715 | 0 | 168
0:30 | 3820.5 | 899 | 2066 | 3517 | 675 | 80 | 687.5 | 0 | 167 | Date: | 2020-09-04
1:00 | 3790 | 898 | 2039 | 3499 | 670 | 80 | 660 | 0 | 166
1:30 | 3816.5 | 898 | 2052.5 | 3387 | 670 | 80 | 591.5 | 0 | 164 | [7 empty] | Total Energy | 251.1791 | Total Energy Gen 251.179 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 251.179 MKWHr
2:00 | 3843 | 898 | 2066 | 3275 | 670 | 80 | 523 | 0 | 162 | [7 empty] | Energy not Served | 0
2:30 | 3844 | 900 | 2082 | 3164 | 670 | 79.5 | 429.5 | 0 | 160 | [7 empty] | Energy Requirement | 251.1791
3:00 | 3845 | 902 | 2098 | 3053 | 670 | 79 | 336 | 0 | 158
3:30 | 3836.5 | 901.5 | 2100.5 | 2991.5 | 669.5 | 79 | 301 | 0 | 157 | [6 empty] | Shortage
4:00 | 3828 | 901 | 2103 | 2930 | 669 | 79 | 266 | 0 | 156
4:30 | 3831.5 | 901.5 | 2109 | 2845.5 | 664.5 | 78 | 237 | 0 | 157
5:00 | 3835 | 902 | 2115 | 2761 | 660 | 77 | 208 | 0 | 158
5:30 | 3815 | 902 | 2088 | 2434 | 640 | 77 | 188 | 0 | 148
6:00 | 3795 | 902 | 2061 | 2107 | 620 | 77 | 168 | 0 | 138
6:30 | 3794 | 902 | 1998.5 | 1811 | 610 | 76 | 156 | 0 | 132 |  |  |  |  | Coal
7:00 | 3793 | 902 | 1936 | 1515 | 600 | 75 | 144 | 0 | 126
7:30 | 3735 | 903 | 1898.5 | 1469 | 600 | 75.5 | 144 | 0 | 120 |  |  |  | Oil |  |  |  | ,
8:00 | 3677 | 904 | 1861 | 1423 | 600 | 76 | 144 | 0 | 114
8:30 | 3717.5 | 903.5 | 1833 | 1333 | 595 | 76 | 132 | 0 | 115
9:00 | 3758 | 903 | 1805 | 1243 | 590 | 76 | 120 | 0 | 116
9:30 | 3809 | 910 | 1885 | 1285 | 510 | 76 | 120 | 0 | 117
10:00 | 3860 | 917 | 1965 | 1327 | 430 | 76 | 120 | 0 | 118
10:30 | 3897.5 | 917 | 2027 | 1453 | 290 | 76.5 | 120 | 0 | 119
11:00 | 3935 | 917 | 2089 | 1579 | 150 | 77 | 120 | 0 | 120
11:30 | 3649.5 | 916.5 | 1982 | 1993.5 | 150 | 77.5 | 136 | 0 | 119
12:00 | 3364 | 916 | 1875 | 2408 | 150 | 78 | 152 | 0 | 118
12:30 | 3363 | 916.5 | 1912 | 2594.5 | 150 | 79 | 152 | 0 | 127
13:00 | 3362 | 917 | 1949 | 2781 | 150 | 80 | 152 | 0 | 136
13:30 | 3362 | 917 | 1949 | 2781 | 150 | 80 | 152 | 0 | 136
14:00 | 3362 | 917 | 1949 | 2781 | 150 | 80 | 152 | 0 | 136
14:30 | 3406 | 912.5 | 1965 | 2752 | 250.5 | 79 | 152 | 0 | 140
15:00 | 3450 | 908 | 1981 | 2723 | 351 | 78 | 152 | 0 | 144
15:30 | 3422.5 | 908 | 1959.5 | 2635 | 380.5 | 78 | 144 | 0 | 142
16:00 | 3395 | 908 | 1938 | 2547 | 410 | 78 | 136 | 0 | 140
16:30 | 3396 | 904.5 | 1881.5 | 2268 | 455 | 77.5 | 133 | 0 | 136
17:00 | 3397 | 901 | 1825 | 1989 | 500 | 77 | 130 | 0 | 132
17:30 | 3306 | 900.5 | 1669.5 | 2036.5 | 495 | 77 | 181 | 0 | 131
18:00 | 3215 | 900 | 1514 | 2084 | 490 | 77 | 232 | 0 | 130
18:30 | 3402 | 899.5 | 1819 | 2672 | 551.5 | 77 | 445 | 0 | 146
19:00 | 3589 | 899 | 2124 | 3260 | 613 | 77 | 658 | 0 | 162
19:30 | 3719 | 899 | 2152 | 3520 | 651 | 77 | 711 | 0 | 170
20:00 | 3683 | 900 | 2126 | 3554 | 650 | 77 | 729 | 0 | 174
20:30 | 3740 | 900 | 2125.5 | 3575 | 667.5 | 77 | 739 | 0 | 173
21:00 | 3797 | 900 | 2125 | 3596 | 685 | 77 | 749 | 0 | 172
21:30 | 3810 | 900.5 | 2141.5 | 3564.5 | 682.5 | 78 | 732 | 0 | 174
22:00 | 3823 | 901 | 2158 | 3533 | 680 | 79 | 715 | 0 | 176
22:30 | 3840 | 901 | 2161.5 | 3534 | 680 | 79 | 715 | 0 | 175
23:00 | 3857 | 901 | 2165 | 3535 | 680 | 79 | 715 | 0 | 174
23:30 | 3854 | 900.5 | 2129 | 3535 | 680 | 79.5 | 715 | 0 | 171 | Max Temp. in Dhaka |  | 35.8° C
24:00 | 3851 | 900 | 2093 | 3535 | 680 | 80 | 715 | 0 | 168
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 251.179 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 251.179 MKWHr
Note on W13: Author:

## Generation
g | 2020-09-04
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 45 | 45 | 44 | 44 | 42 | 42 | 40 | 41 | 41 | 41 | 42 | 43 | 45 | 45 | 43 | 43 | 42 | 42 |  | 42 | 42 | 42 | 42 | 44 | 44 | 45 | 1001018
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 852000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | [6 empty] | 7 | 5 | 8 | 16 | 25 | 25 | 25 | 25 | 8 | 8 |  | 14 | 25 | 25 | 25 | 25 | 25 | 25 | 371610
| Teknaf 20MW PP (Solartech) | [5 empty] | 0.6 |  |  | 15.6 | 19.1 |  |  |  | 17.4 | 13.8 | 8.9 | 3.6 | [9 empty] | 84915
6 | Sikalbaha 225MW CCPP (Gas) | 217 | 217 | 217 | 217 | 217 | 217 | 217 | 217 | 219 | 217 | 220 | 218 | 219 | 218 | 219 | 218 | 205 | 222 |  | 205 | 204 | 204 | 204 | 209 | 214 | 204 | 5057508
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 102 | 102 | [15 empty] | 31 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 824619
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [19 empty] | 50 | 50 | 48 | 50 | 50 | 50 | 50 | 287176
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 268 | 305 | 310 | 298 | 302 | 265 | 310 | 266 | 310 | 305 | 306 | [5 empty] | 27 | 25 |  | 34 | 150 | 159 | 300 | 304 | 308 | 298 | 4787138
18 | Kodda 300 MW PP Unit-2 (Summit) | 253 | 253 | 253 | 250 | 253 | 145 | 95 | 95 | 95 | 95 | 95 | 155 | 240 | 245 | 245 | 245 | 170 | 155 |  | 225 | 225 | 243 | 253 | 250 | 250 | 250 | 4978035
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 561000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 99 | 103 | 101 | 99 | 101 | 101 | 100 | 102 | 100 | 100 | 101 | 100 | 100 | 100 | 100 | 140 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 2744000
23 | Ghorasal TPP Unit-5 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2712150
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1933474
32 | Ashuganj 50 MW PP | 35 | 35 | 32 | 32 | 32 | 32 | 28 | 28 | 28 | 28 | 26 | 32 | 34 | 33 | 33 | 34 | 35 | 35 |  | 35 | 35 | 35 | 32 | 32 | 29 | 32 | 736560
33 | Ashuganj 225 MW CCPP | 176 | 176 | 179 | 175 | 176 | 175 | 187 | 176 | 192 | 192 | 153 | 192 | 182 | 189 | 197 | 181 | 181 | 180 |  | 181 | 189 | 189 | 180 | 185 | 193 | 177 | 4437000
34 | Ashuganj 450 MW CCPP(South) | 250 | 250 | 250 | 250 | 250 | 250 | 260 | 250 | 260 | 300 | 345 | 250 | 250 | 250 | 260 | 250 | 250 | 250 |  | 275 | 265 | 250 | 250 | 250 | 265 | 250 | 6376000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 290 | 280 | 280 | 285 | 315 | 270 | 295 | 295 | 310 | 295 | 295 | 275 |  | 325 | 300 | 275 | 275 | 275 | 290 | 275 | 7213000
35 | Ashuganj 55 MW PP (Precision) | 10 | 10 | 30 | 43 | 43 | 43 | 45 | 47 | 47 | 46 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 544320
36 | Chandpur 150 MW CCPP | 86 | 95 | 95 | 89 | 91 | 85 | 95 | 86 | 96 | 97 | 95 | 86 | 96 | 96 | 96 | 86 | 92 | 86 |  | 90 | 96 | 96 | 95 | 96 | 96 | 96 | 2186110
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 340 | 340 | 340 | 341 | 341 | 340 | 340 | 341 | 341 | 363 | 377 | 345 | 349 | 342 | 361 | 347 | 345 | 340 |  | 348 | 342 | 341 | 340 | 343 | 349 | 349 | 8442960
40 | Meghnaghat 450 MW CCPP(MPL) | 370 | 370 | 370 | 370 | 370 | 370 | 340 | 340 | 340 | 340 | 420 | 350 | 350 | 350 | 350 | 350 | 350 | 300 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 8912500
41 | Haripur 360MW CCPP(HPL) | 354 | 355 | 354 | 354 | 354 | 357 | 302 | 303 | 273 | 303 | 315 | 302 | 302 | 302 | 302 | 302 | 302 | 252 |  | 346 | 346 | 345 | 352 | 350 | 350 | 350 | 7724000
42 | RPCL 210MW CCPP | 141 | 155 | 155 | 155 | 156 | 158 | 155 | 156 | 154 | 151 | 150 | 153 | 149 | 150 | 149 | 152 | 150 | 154 |  | 154 | 151 | 152 | 154 | 153 | 100 | 101 | 3499760
43
44 | Fenchugonj CCPP Phase-1 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 89 | 89 | 89 | 91 | 86 | 89 | 86 | 86 | 86 | 86 |  | 86 | 86 | 86 | 86 | 86 | 91 | 91 | 2111000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720240
46 | Shajibazar 330 MW CCPP | 197 | 198 | 198 | 195 | 192 | 198 | 200 | 188 | 215 | 213 | 202 | 199 | 197 | 199 | 192 | 183 | 188 | 197 |  | 185 | 182 | 185 | 180 | 180 | 198 | 198 | 4378000
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 62 | 62 | 62 | 62 | 62 | 61 | 67 | 40 | 40 | 62 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 65 | 65 | 63 | 63 | 63 | 62 | 63 | 1307616
48 | Shahjibazar 86MW PP (Shahjibazar) | 87 | 87 | 87 | 87 | 87 | 87 | 88 | 88 | 40 | 40 | 87 | 87 | 84 | 84 | 86 | 86 | 20 | 20 |  | 87 | 87 | 85 | 85 | 85 | 85 | 85 | 1858560
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 100 | 100 | 100 | 100 | 100 | 100 | 70 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3090830
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 420000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 245700
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 2 | 2 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 198240
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 47 | 47 | 44 | 44 | 44 | 47 | 50 | 50 | 50 | 11 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1117800
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 573672
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 280 | 290 | 290 | 300 | 280 | 290 | 285 | 260 | 310 | 315 | 260 | 285 | 275 | 310 | 300 | 290 | 280 |  | 290 | 310 | 280 | 290 | 300 | 305 | 300 | 7204000
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | [8 empty] | 40 | 55 | 55 | 55 | 55 | 17 | 17 |  | 52 | 55 | 55 | 55 | 55 | 55 | 55 | 787756
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 468048
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  |  | 22 | 19 |  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 408960
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 20 | 20 | 20 | 22 | 22 | 20 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 22 | 22 | 469152
63 | Impoprt (Tripura) | 166 | 162 | 158 | 156 | 158 | 138 | 126 | 114 | 116 | 118 | 120 | 118 | 136 | 140 | 144 | 140 | 132 | 130 |  | 162 | 170 | 174 | 172 | 176 | 174 | 168 | 3550080
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 35 | 30 | 30 | 29 | 23 | 34 | 29 | 27 | 27 | 27 | 36 |  | 36 | 36 | 36 | 42 | 42 | 42 | 42 | 855360
65 | Feni 22MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 17 | 18 | 18 | 18 | 18 | 17 | 17 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 428688
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 8 | 8 | 8 | 8 | 8 | 5 |  | 5 | 8 | 5 | 8 | 8 | 10 |  | 8 | 10 | 10 | 8 | 8 | 8 | 8 | 190980
67 | Jangalia 33MW PP (Summit) | 33 | 20 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 25 | 33 | 33 | 33 | 25 | 25 | 25 | 25 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 701100
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  |  |  | 18 | 18 | 18 | 18 | 18 | 19 | 18 | 18 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 440160
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 20 | 24 | 24 | 17 | 13 | 13 | 13 | 13 | 17 | 17 | 17 |  | 17 | 28 | 29 | 29 | 29 | 29 | 29 | 556920
71 | Maona 33 MW PP(Summit) | 28 | 28 | 28 | 28 | 28 | 28 |  | 33 | 33 | 25 | 25 | 28 | 28 | 28 | 25 | 28 | 28 |  |  | 28 | 28 | 28 | 28 | 25 | 25 | 25 | 657200
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 17 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 25 | 33 | 33 | 33 | 767700
73 | Ghorashal 108MW PP (Regent) | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 72 | 72 | 72 | 72 | 71 | 71 | 71 | 71 | 72 | 72 | 72 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 1718727
| Feni Lanka Power | 114 | [10 empty] | 34 | 34 | 17 | 17 |  |  | 45 |  | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 927960
| Chowmuhani 113 MW | 108 | 107 | 108 | 113 | 113 | 113 | 65 | 65 | 36 | 36 | 50 | 108 | 110 | 113 | 113 | 105 | 84 | 93 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2367120
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 50 | 50 | 58 | 90 | 100 | 99 | 99 | 99 | 70 | 70 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2136960
78 | Gazipur 52 MW PP | 51 | 51 | [9 empty] | 22 | 16 | 16 | 16 |  |  |  |  | 36 | 51 | 51 | 51 | 51 | 51 | 51 | 489240
79 | Kodda 150MW PP | 149 | 32 | 32 | 16 | [7 empty] | 32 | 32 | 32 | 32 | 16 |  | 48 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 1261440
80 | Jamalpur 95 MW PP(Powerpac) | 71 | 71 | 71 | 71 | 71 | 71 | 32 | 32 | 32 | 48 | 48 | 64 | 64 | 64 | 64 | 56 | 64 | 64 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 1491840
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 43 | [7 empty] | 5 | 34 | 34 | 34 | 16 | 8 | 25 |  | 25 | 34 | 34 | 40 | 43 | 43 | 43 | 596957
| Gazipur 100 MW PP | 103 | 103 | 103 | 103 | 103 | 16 | 16 | 16 | 16 | 16 | 50 | 60 | 87 | 87 | 87 | 50 | 16 | 50 |  | 105 | 105 | 104 | 104 | 104 | 104 | 104 | 1678308
| Kaptai 7 MW Solar PP | [5 empty] | 0.19 | 1.1 | 2.4 | 3.3 | 4.8 | 5.2 | 5.2 | 5.1 | 2.9 | 2.6 | 2 | 0.9 | [9 empty] | 36119
| Jodiac Power | [26 empty] | 0
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | 97 | 97 | 97 | 97 | 97 | 30 | 30 | 30 | 30 | 30 | 30 | 52 | 80 | 87 | 95 | 96 | 96 | 97 |  | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 1922376
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 13 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  |  |  | 9 | 12 | 12 | 12 | 12 | 12 | 12 |  | 43 | 100 | 89 | 87 | 17 | 12 | 12 | 472575
86 | Meghnaghat CCPP(Summit) | 135 | 135 | 135 | 135 | 135 | 120 | 140 | 120 | 140 | 145 | 140 | 125 | 140 | 145 | 145 | 130 | 140 | 125 |  | 130 | 140 | 145 | 140 | 145 | 150 | 140 | 3346793
87 | Meghnaghat 100 MW(IEL) | 100 | 100 | 100 | 100 | 100 | 100 | 78 | 53 | 50 | 50 | 51 | 75 | 83 | 84 | 84 | 91 | 92 | 92 |  | 92 | 93 | 91 | 91 | 93 | 93 | 93 | 2075520
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 104 | 104 | 104 | 85 | 53 | 53 | 53 | 60 | 104 | 104 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 2369280
88 | Ghorashal 78.5 MW PP(MAX) | [26 empty] | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 60 | 60 | [9 empty] | 20 | 20 | 20 | 20 |  |  |  |  | 10 | 20 | 20 | 20 | 20 | 20 | 20 | 392640
92 | Fenchuganj 44MW (Energyprima) | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 45 | 45 | 45 | 41 | 45 | 48 | 10 | 10 |  | 38 | 49 | 49 | 49 | 49 | 49 | 49 | 1111536
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 51 | 51 | 51 | 51 | 51 | 15 | 15 |  | 25 | 45 | 45 | 51 | 51 | 51 | 51 | 1087504
94 | Gagnagar 102 MW PP (Digital Power) | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 58 | 50 | 50 | 50 | 50 | 85 | 93 | 93 | 93 | 93 |  | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 2007216
95 | Patenga 50MW PP (Baraka) | 50 | 50 | 50 | 50 | 50 | 22 | 19 | 19 |  |  |  | 10 | 47 | 50 | 50 | 37 | 19 | 18 |  | 32 | 50 | 50 | 50 | 50 | 50 | 50 | 848640
96 | Chattogram 108 MW PP (ECPV) | 84 | 85 | 89 | 89 | 89 | 45 | 12 | 12 | 12 | 12 | 10 | 32 | 37 | 38 | 52 | 43 | 18 | 26 |  | 79 | 89 | 89 | 85 | 85 | 85 | 89 | 1333440
97 | Katpotti 52 MW PP (Sinha)
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | 44 | 55 | 55 | 55 | 55 | 55 | 30 | 30 | 30 | 30 | 30 | 46 | 55 | 55 | 55 | 55 | 30 | 30 |  | 31 | 45 | 45 | 45 | 45 | 45 | 45 | 1072404
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 55 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1013432
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 163 | 163 | 130 | 130 | 130 | 130 | 130 | 130 | 110 |  | 163 | 163 | 163 | 163 | 163 | 163 | 130 | 3432434
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0.3 | 1.1 | 1.4 | 2 | 2.4 | 2.3 | 2 | 2 | 1.8 | 0.8 | 0.4 | [9 empty] | 14850
103 | Kamalaghat 54 MW PP(Banco Energy) | 53 | 53 | 53 | 53 | 53 | 17 | 17 | 17 | 17 | 17 | 17 | 53 | 53 | 53 | 53 | 53 | 17 | 38 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1050120
104 | Keranigonj 300 MW PP (APR) | [19 empty] | 87 | [6 empty] | 46498
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 192 | 192 | 192 | 200 | 200 | 200 |  | 192 | 192 | 192 | 200 | 200 | 200 | 200 | 4776000
112 | Aurahati 100MW PP (Aggreko) | [19 empty] | 29 | [6 empty] | 21460
114 | Kodda 149 MW PP Unit-1 (Summit) | 113 | 113 | 113 | 113 | 113 | 101 | 71 | 71 | 71 | 70 | 76 | 96 | 95 | 95 | 105 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 114 | 113 | 2453760
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 50 | 50 | 76 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2210880
116 | Chandpur 200MW (Desh energy) | [19 empty] | 7 | 16 | 16 | 16 |  |  |  | 88800
117 | Ashuganj 150MW PP (Midland) | 107 | 105 | 107 | 105 | 107 | 20 | 20 | 20 | 20 | 20 | 23 | 52 | 83 | 88 | 83 | 40 | 20 | 38 |  | 75 | 96 | 95 | 92 | 98 | 97 | 98 | 1761381
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 115 | 95 | 95 | 95 | 45 | 8 | 8 | 8 | 8 | 35 | 40 | 35 | 35 | 35 | 35 | 8 | 8 | 8 |  | 55 | 115 | 115 | 115 | 115 | 115 | 115 | 1496400
| Anwara 300 MW PP (United) | 216 | 216 | 216 | 216 | 216 | 216 | 144 | 144 | 89 | 88 | 154 | 180 | 180 | 180 | 180 | 180 | 128 | 88 |  | 215 | 215 | 216 | 216 | 216 | 216 | 216 | 4270473
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 60 | 60 | 80 | 90 | 90 | 90 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2294400
120 | Eastern Zone Total | 7717 | 7523 | 7322 | 7236 | 7149 | 6516.79 | 6062.4 | 5869.5 | 5683.3 | 5897.9 | 6229.6 | 6189.5 | 6545.1 | 6602.3 | 6736.2 | 6491.7 | 5912.9 | 5848 |  | 7581 | 7867 | 7816 | 7969 | 7932 | 7956 | 7846 | 166267552
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 115 | 115 | 115 | 115 | 99 | 99 | 24 | 16 | 16 | 16 | 21 | 99 | 115 | 115 | 115 | 115 | 49 | 49 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2063040
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
| Khulna 225 MW CCPP | 190 | 170 | 135 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 140 | 155 | 170 | 195 | 195 | 195 | 195 | 3490560
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | 35 | 17 | [16 empty] | 53 | 70 | 90 | 105 | 105 | 105 | 105 | 612960
130
131
132
133
| Barisal 110 MW PP (Summit ) | 96 | 96 | 48 | 48 | 48 | 48 | 16 | 16 | 16 | 64 | 110 | 110 | 110 | 110 | 110 | 110 | 32 | 32 |  | 64 | 80 | 80 | 80 | 80 | 80 | 80 | 1668480
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 77 | 78 | 78 | 77 | 77 | 76 | 31 | 32 | 32 | 48 | 76 | 76 | 76 | 75 | 75 | 75 | 75 | 78 |  | 79 | 79 | 78 | 78 | 78 | 79 | 77 | 1708700
| Bhola 225 MW CCPP | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 89 | 90 | 90 | 90 | 90 | 90 | 90 | 89 | 90 | 90 | 83 |  | 90 | 90 | 90 | 90 | 90 | 90 | 89 | 2150942
140 | Bhola 33 MW PP (Venture) | 33 | 31 | 30 | 27 | 26 | 25 | 20 | 18 | 18 | 19 | 19 | 20 | 22 | 23 | 25 | 21 | 21 | 31 |  | 32 | 33 | 35 | 35 | 36 | 37 | 35 | 618745
141 | Noapara 100 MW PP (Bangla Trac) | 99 | [18 empty] | 50 | 100 | 100 | 100 | 100 | 100 | 100 | 692160
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 40 | 40 | 40 | [6 empty] | 40 | 40 | 8 | 8 |  |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 537750
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 10 | [9 empty] | 5760
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [11 empty] | 32 | 50 | 32 | [12 empty] | 108576
146 | Bheramara HVDC | 898 | 898 | 902 | 901 | 902 | 902 | 902 | 904 | 903 | 917 | 917 | 916 | 917 | 909 | 908 | 908 | 901 | 900 |  | 899 | 899 | 900 | 900 | 901 | 901 | 900 | 21701090
147 | Bheramara 410 MW CCPP | 345 | 345 | 340 | 345 | 345 | 345 | 350 | 345 | 355 | 365 | 370 | 340 | 345 | 370 | 365 | 345 | 345 | 270 |  | 345 | 345 | 345 | 345 | 345 | 350 | 345 | 8432928
148 | Payra 1320 MW | 520 | 520 | 520 | 520 | 510 | 470 | 450 | 450 | 440 | 280 |  |  |  | 90 | 200 | 260 | 350 | 340 |  | 463 | 500 | 500 | 535 | 530 | 530 | 530 | 9768100
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 151 | 150 | 150 | 150 |  | 150 | 151 | 150 | 150 | 150 | 150 | 150 | 3682200
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP | [25 empty] | 60 | 19000
| Baghabari 50 MW Peaking PP | 50 | 50 | [17 empty] | 25 | 50 | 50 | 50 | 50 | 50 | 50 | 384944
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 184 | 185 | 185 | 190 | 189 | 186 | 177 | 153 | 154 | 187 | 196 | 171 | 159 | 154 | 171 | 161 | 161 | 140 |  | 165 | 171 | 164 | 153 | 157 | 163 | 163 | 4297355
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 216 | 216 | 217 | 216 | 217 | 220 | 170 | 170 | 170 | 170 | 170 | 150 | 150 | 150 | 150 | 150 | 150 | 130 |  | 170 | 210 | 210 | 210 | 210 | 212 | 213 | 4866582
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 382 | 409 | 413 | 409 | 412 | 377 | 374 | 321 | 374 | 405 | 401 | 356 | 396 | 403 | 401 | 367 | 404 | 240 |  | 396 | 372 | 378 | 348 | 371 | 371 | 341 | 9191636
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 5 |  | 34 | 34 | 34 | 34 |  |  |  | 124787
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 20 |  | 21 | 21 | 21 | 21 | 22 | 22 | 22 | 491040
163 | Bogura 20 MW PP (Energyprima) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 251352
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 |  |  | 11 | 11 | 11 | 11 | 209844
165 | Amnura 50 MW PP(Sinha) | [20 empty] | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | 42 | 42 | 42 | 42 | [13 empty] | 10 |  | 43 | 43 | 47 | 43 | 43 | 43 | 43 | 410400
168 | Santahar 50 MW Peaking PP | 31 | 31 | 31 | [14 empty] | 3 |  | 25 | 32 | 31 | 30 | 30 | 30 | 30 | 265065
169 | Natore 52 MW PP (Rajlanka) | 43 | 43 | 43 | [8 empty] | 35 | 35 | 8 | 8 |  |  |  |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 457920
170 | Chapainawabganj 100 MW Peaking PP | 96 | 96 | 96 | 88 | 88 | 48 | 24 | 24 | [9 empty] | 15 |  | 90 | 96 | 98 | 96 | 96 | 96 | 96 | 1739064
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 50 | [6 empty] | 32 | 54 | 55 | 55 | 35 |  | 4 |  | 57 | 102 | 107 | 113 | 113 | 113 | 113 | 1451424
172 | Confidence Power Bogura Unit-1 113 MW | 90 | 90 | 90 | 90 | 90 | 90 | 50 | 50 | 35 | 35 | 50 | 50 | 50 |  |  | 50 | 65 | 70 |  | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 1657728
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 106 | 107 | 80 | 72 | 70 | 65 | 41 | 34 | 35 | 35 | 35 | 52 | 71 | 83 | 79 | 76 | 81 | 85 |  | 84 | 84 | 84 | 95 | 105 | 107 | 106 | 1805760
177 | Sympa Solar Power 8MW | [5 empty] | 0.1 | 0.6 | 1.8 | 3.1 | 4.6 | 5.6 | 7.2 | 7.6 | 6.2 | 3.6 | 3 | 1.4 | 0.2 | [8 empty] | 45636
178
178