## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-09-09 | Wednesday
|  |  | Date (day): | 2020-09-09 |  | Wednesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14442.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15249 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-09-08 | 2020-09-09 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 140 | 140 | 100 | 140 | 40 |  | Gas shortage
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 110 | 110 | 110 | 110 | 80 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 81 | 82 | 82 | 82 | 26 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 342 | 340 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 300 | 300 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 390 | 320 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 7 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 130 | 120 | 150 | 150 | 155 |  | GT-1 S/D for gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 80 | 80 | 96 | 96
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 11 | 100 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 35 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 278 | 265 | 335 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 93 | 93 | 93 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 70 | 150 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 55 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 36 | 52 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 268 | 284 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 58 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 50 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 103 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 131 | 139 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 105 | 105 | 100 | 100
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 90 | 18 | 104 | 104
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 3135 | 3378 | 3954 | 4244 | 853 | 789
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 12 | 25 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19.4 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 34 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 79 | 75 | 75 | 75 | 155 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 205 | 203 | 225 | 225
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 147 | 100 | 140 | 150
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 100 | 100 | 100
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 100 | 30 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 20 | 20 | 20
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 30 | 10 | 30
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 11 | 11 | 12 | 12 |  | 96 | Engine problem
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 6 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 179 | 214 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 17 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 1134.4 | 1195 | 1666 | 1671 | 395 | 194
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 100 | 80 | 80 | 80 | 54 |  | Gas shortage
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 213 | 215 | 225 | 225
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 265 | 295 | 360 | 360
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 265 | 265 | 360 | 360
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 35 | 35 | 36 |  | 9 | Engine problem
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 10 | 10 | 45 |  | Gas shortage
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 4 | 8 | 8 | 187 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 43 | 43 |  | 8 | Engine problem
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 42 | 0 | 42
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 85 | 85 | 100 | 100 |  | 63 | ST under shut down
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 50 | 90 | 200 | 200
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 18 | 21 | 21
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 150 | 182 | 150 | 180
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 24 | 43 | 43 | 43 |  | 9 | Engine problem
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 16 | 14 | 20 | 20 |  | 5 | Engine problem
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 114 | 114 | 114 | 114
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 76 | 113 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1425 | 1644 | 2076 | 2349 | 550 | 94
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 159 | 159 | 160 | 160 | 42 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 20 | 22 | 22
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 40 | 64 | 72 | 72 |  | 23 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 195 | 100 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 7 | 45 | 115 | 115
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 420 | 388 | 570.6 | 569 | 42 | 23
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 91 | 91 | 90 | 90
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 28 | 28 | 30 | 30 |  | 60 | Unit-4 under shut down
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 110 | 163 | 163
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 297 | 295 | 300 | 300
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 52 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 49 | 49 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 20 | 52 | 64 | 64 |  | 35 | GT-8 under maint.
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 85 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 177 | 190 | 190 | 190 |  | 41 | Machine problem
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 23 | 25 | 25
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 270 | 341 | 341
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 10 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1238 | 1284 | 1423 | 1423 | 0 | 536
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 931 | 930 | 942 | 942
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 66 | 115 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 155 | 225 | 225
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 345 | 410 | 410 | 410
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 32 | 40 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 80 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 35 | 70 | 105 | 105
| 108 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1529 | 1820 | 2017 | 2143 | 0 | 0
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 96 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 27 | 40 | 33 | 33
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 65 | 65 | 65 | 65 |  | 129 | GT-2 & ST Under maint.
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 78 | 77 | 80 | 80 |  | 15 | Engine problem
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 340 | 510 | 620 | 620
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 510 | 788 | 908 | 908 | 0 | 144
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 65 | 70 | 70 | 70 | 30 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 35 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 43 | 43 | 43
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 220 | 220
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 154 | 145 | 0 | 0 | 220 |  | Gas shortage
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 140 | 135 | 220 | 220 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 355 | 370 | 414 | 414 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 32
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 21 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 8 | 8 | 11 | 11
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 8 | 43 | 43 | 43 |  | 9 | Engine problem
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 98 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 14 | 113 | 113 | 113
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 70 | 90 | 90 | 90 |  | 23 | Engine problem
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 846 | 1264 | 1557 | 1679 | 421 | 32
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 10 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 105 | 113 | 113
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 153 | 255 | 271 | 263 | 294 | 30
|  | Total |  |  |  |  | 20383 | 19892 | 10390.4 | 12016 | 14442.6 | 15249 | 2555 | 1842
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10086.0208 | 11664 | 14019.5145 | 14802.2916
| A. |  | 2020-09-08 | (Yesterday) |  |  |  |  | Tuesday
| 1 | Highest Generation : |  |  | 12016 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
| 2 | Minimum Generation : |  |  | 8985 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12016 | MW
| 3 | Day peak Generation : |  |  | 10390.4 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11664 | MW
| 4 | Evening peak Generation : |  |  | 12016 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 250.1472 | MKWHr | By Solar | 0.18618 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 144.7103 | MKWHr |  | By Oil: | 61.7446 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 15.436 | MKWHr |  | By Hydro: | 1.888 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2555 | MW | Dhaka | 4125 | 4125 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 1842 | MW | Chittagong | 1170 | 1170 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4397 | MW | Khulna | 1507 | 1507 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1207.42 | MMCFD |  |  | Rajshahi | 1227 | 1227 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 168842036.228 | ii) Oil : | Taka | 496448790.07 | Comilla | 1213 | 1213 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 71562989 | Total | Taka | 736853815.298 | Mymensingh | 766 | 766 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.057 | MKWHr. | Sylhet | 500 | 500 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -14 | MW (E to W) at | 19:30 | hrs | Barisal | 354 | 354 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -75 | MW at | 15:00 | hrs | Rangpur | 802 | 802 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.5° C |  |  | Total | 11664 | 11664 |  | 0
| B. |  | 2020-09-09 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 32.4° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15249 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10800 | MW
| 4 | Reserve(Generation end) |  |  |  | 2249 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 270.632 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9122 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.3527 | MKWHr. | ii) HVDC Flow at Peak Time |  | 930 | MW at | 19:30 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.8294 | MKWHr. | iii) Maximum HVDC Flow : |  | 935 | MW at | 3:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 93.2 |  | (b) Today: | 93.11 |  | (c) Rule Curve: |  | 100.84
.

## YesterdayGen
2020-09-08
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 140 | 110 | 0 | 82 | 0 | 341 | 354 |  | 0 | 400 | 140 | 100 | 64 | 45 | 303 | 0 | 0 | 0 | 100 | 93 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 22 | 25 | 30 | 28 | 33 | 0 | 0 | 45 | 35 | 120 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 84 | 0 | 12 | 18 | 11 | 32 | 0 | 0 | 80 | 265 | 250 | 186 | 8 | 93 | 35 | 5 | 0 | 43 | 0 | 0 | 43 | 15 | 10 | 33 | 21 | 164 | 160 | 71 | 22 | 0 | 90 | 28 | 53 | 49 | 163 | 284 | 32 | 85 | 0 | 163 | 18 | 0 | 10 | 295 | 24 | 11 | 0 | 238 | 0 | 0 | 200 | 0 | 132 | 0 | 100 | 0 | 40 | 0 | 8 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 113 | 100 | 0 | 104 |  | 934 | 0 | 345 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 33 | 65 | 38 | 64 | 0 | 70 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 182 | 0 | 76 | 0 | 200 | 0 | 410 | 53 | 0 | 0 | 0 | 106 | 0 | 0 | 90 | 560 |  | 7204 | 3681 | 10885 | 4196 | 934 | 2133 | 2432 | 710 | 80 | 236 | 164 | 0 | 0 | 93.21
2:00 | 0 | 0 | 140 | 110 | 0 | 82 | 0 | 341 | 353 |  | 0 | 400 | 135 | 100 | 64 | 55 | 298 | 0 | 0 | 0 | 100 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 30 | 28 | 33 | 0 | 0 | 45 | 35 | 120 | 0 | 0 | 204 | 0 | 140 | 0 |  | 0 | 0 | 50 | 0 | 0 | 0 | 18 | 41 | 0 | 0 | 80 | 265 | 250 | 186 | 8 | 88 | 32 | 5 | 0 | 43 | 0 | 0 | 0 | 15 | 10 | 33 | 21 | 162 | 161 | 32 | 22 | 0 | 90 | 28 | 53 | 49 | 163 | 284 | 32 | 85 | 0 | 163 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 218 | 0 | 0 | 200 | 0 | 122 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 113 | 100 | 0 | 104 |  | 934 | 0 | 345 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 38 | 64 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 181 | 0 | 77 | 0 | 200 | 0 | 411 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 90 | 560 |  | 6935 | 3547 | 10482 | 4188 | 934 | 2128 | 2110 | 710 | 80 | 170 | 162 | 0 | 0 | 93.21
3:00 | 0 | 0 | 140 | 110 | 0 | 82 | 0 | 339 | 354 |  | 0 | 400 | 135 | 100 | 48 | 55 | 287 | 0 | 0 | 0 | 100 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 30 | 24 | 33 | 0 | 0 | 44 | 35 | 120 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 23 | 0 | 0 | 0 | 18 | 41 | 0 | 0 | 80 | 265 | 250 | 193 | 8 | 96 | 32 | 5 | 0 | 43 | 0 | 0 | 0 | 15 | 10 | 33 | 21 | 158 | 161 | 8 | 22 | 0 | 90 | 28 | 53 | 49 | 163 | 282 | 32 | 85 | 0 | 163 | 18 | 0 | 10 | 285 | 24 | 8 | 0 | 218 | 0 | 0 | 200 | 0 | 100 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 113 | 100 | 0 | 104 |  | 935 | 0 | 340 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 38 | 48 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 178 | 0 | 76 | 0 | 200 | 0 | 401 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 90 | 560 |  | 6785 | 3475 | 10260 | 4175 | 935 | 2123 | 1937 | 710 | 79 | 143 | 158 | 0 | 0 | 93.21
4:00 | 0 | 0 | 142 | 110 | 0 | 82 | 0 | 340 | 355 |  | 0 | 400 | 140 | 100 | 48 | 15 | 300 | 0 | 0 | 0 | 100 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 30 | 24 | 33 | 0 | 0 | 43 | 35 | 120 | 0 | 0 | 203 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 41 | 0 | 0 | 80 | 265 | 250 | 198 | 8 | 91 | 29 | 5 | 0 | 43 | 0 | 0 | 0 | 15 | 10 | 33 | 21 | 160 | 161 | 0 | 22 | 0 | 90 | 28 | 53 | 49 | 163 | 286 | 31 | 85 | 0 | 163 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 170 | 0 | 0 | 200 | 0 | 100 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 113 | 100 | 0 | 104 |  | 935 | 0 | 345 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 39 | 32 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 181 | 0 | 77 | 0 | 200 | 0 | 413 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 50 | 560 |  | 6660 | 3363 | 10023 | 4196 | 935 | 2143 | 1681 | 710 | 78 | 120 | 160 | 0 | 0 | 93.2
5:00 | 0 | 0 | 140 | 110 | 0 | 82 | 0 | 344 | 352 |  | 0 | 400 | 145 | 60 | 48 | 15 | 307 | 0 | 0 | 0 | 50 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 30 | 24 | 33 | 0 | 0 | 42 | 35 | 120 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 41 | 0 | 0 | 80 | 265 | 250 | 195 | 8 | 96 | 29 | 5 | 0 | 43 | 0 | 0 | 0 | 15 | 10 | 33 | 21 | 152 | 159 | 0 | 22 | 0 | 90 | 28 | 53 | 49 | 163 | 284 | 32 | 85 | 0 | 164 | 18 | 0 | 10 | 305 | 24 | 8 | 0 | 65 | 0 | 0 | 200 | 0 | 100 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 113 | 100 | 0 | 70 |  | 934 | 0 | 340 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 38 | 32 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 187 | 0 | 76 | 0 | 200 | 0 | 419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 560 |  | 6448 | 3342 | 9790 | 4206 | 934 | 2159 | 1432 | 710 | 77 | 120 | 152 | 0 | 0 | 93.2
6:00 | 0 | 0 | 140 | 110 | 0 | 82 | 0 | 345 | 309 |  | 0 | 360 | 130 | 50 | 48 | 15 | 281 | 0 | 0 | 0 | 18 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 30 | 24 | 33 | 0 | 0 | 40 | 35 | 120 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 41 | 0 | 0 | 80 | 265 | 250 | 201 | 0 | 85 | 29 | 5 | 0 | 40 | 0 | 0 | 0 | 15 | 10 | 33 | 18 | 146 | 160 | 0 | 22 | 0 | 90 | 28 | 53 | 49 | 130 | 286 | 32 | 85 | 0 | 164 | 18 | 0 | 10 | 285 | 24 | 8 | 0 | 25 | 0 | 0 | 200 | 0 | 100 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 109 | 100 | 0 | 54 |  | 934 | 0 | 340 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 32 | 16 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 184 | 0 | 77 | 0 | 190 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 550 |  | 6103 | 3227 | 9330 | 4163 | 934 | 1951 | 1241 | 700 | 75 | 120 | 146 | 0 | 0 | 93.2
7:00 | 0 | 0 | 140 | 110 | 0 | 81 | 0 | 340 | 279 |  | 0 | 360 | 135 | 50 | 48 | 15 | 300 | 0 | 0 | 0 | 7 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 30 | 24 | 33 | 0 | 0 | 41 | 35 | 120 | 0 | 0 | 204 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 38 | 0 | 0 | 80 | 265 | 250 | 181 | 0 | 96 | 29 | 5 | 0 | 0 | 0 | 0 | 0 | 15 | 10 | 33 | 14 | 136 | 159 | 0 | 22 | 0 | 90 | 28 | 53 | 49 | 100 | 285 | 32 | 85 | 0 | 164 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 15 | 0 | 0 | 200 | 0 | 102 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 125 | 0 | 0 | 0 | 55 | 100 | 0 | 54 |  | 934 | 0 | 345 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 32 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 168 | 0 | 72 | 0 | 170 | 0 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 530 |  | 5885 | 3100 | 8985 | 4129 | 934 | 1842 | 1067 | 680 | 76 | 120 | 136 | 1 | 0 | 93.19
8:00 | 0 | 0 | 140 | 110 | 0 | 81 | 0 | 350 | 279 |  | 0 | 360 | 145 | 50 | 48 | 15 | 309 | 0 | 0 | 0 | 7 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 30 | 28 | 33 | 0 | 0 | 41 | 35 | 120 | 0 | 0 | 205 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 6 | 0 | 0 | 80 | 285 | 270 | 193 | 0 | 96 | 29 | 5 | 0 | 0 | 0 | 0 | 0 | 15 | 10 | 33 | 16 | 130 | 159 | 0 | 20 | 0 | 90 | 28 | 53 | 49 | 100 | 298 | 32 | 85 | 0 | 164 | 18 | 0 | 10 | 305 | 16 | 8 | 0 | 15 | 0 | 0 | 200 | 0 | 108 | 10.3 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 125 | 0 | 0 | 0 | 55 | 100 | 0 | 54 |  | 934 | 0 | 360 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 26 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 161 | 0 | 75 | 0 | 170 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 35 | 480 |  | 5973.3 | 3053 | 9026.3 | 4221 | 934 | 1819 | 1083 | 630 | 76 | 120 | 130 | 13.3 | 0 | 93.19
9:00 | 0 | 0 | 130 | 110 | 0 | 81 | 0 | 356 | 351 |  | 0 | 420 | 130 | 56 | 48 | 15 | 251 | 0 | 0 | 0 | 8 | 64 | 0 | 3 | 0 | 0 | 0 | 54 | 35 | 45 | 22 | 25 | 30 | 33 | 33 | 5 | 0 | 42 | 35 | 120 | 0 | 0 | 203 | 0 | 150 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 18 | 4 | 0 | 0 | 80 | 265 | 265 | 201 | 0 | 85 | 35 | 5 | 0 | 0 | 0 | 0 | 0 | 15 | 10 | 33 | 16 | 136 | 161 | 7 | 20 | 1 | 91 | 30 | 53 | 49 | 163 | 295 | 32 | 83 | 0 | 164 | 18 | 0 | 0 | 300 | 0 | 8 | 0 | 86 | 0 | 0 | 200 | 0 | 128 | 16.6 | 100 | 0 | 0 | 0 | 4 | 40 | 0 | 4 | 175 | 0 | 0 | 0 | 57 | 100 | 0 | 72 |  | 930 | 0 | 345 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 62 | 25 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 77 | 0 | 140 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 35 | 430 |  | 6486.6 | 2893 | 9379.6 | 4079 | 930 | 1946 | 1489 | 580 | 77 | 120 | 136 | 22.6 | 0 | 93.19
10:00 | 0 | 0 | 140 | 110 | 0 | 81 | 0 | 342 | 347 |  | 0 | 420 | 150 | 94 | 48 | 40 | 308 | 0 | 0 | 0 | 40 | 93 | 0 | 11 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 33 | 33 | 8 | 0 | 42 | 35 | 120 | 0 | 0 | 204 | 0 | 148 | 0 |  | 0 | 0 | 0 | 0 | 3 | 24 | 18 | 6 | 0 | 0 | 120 | 270 | 270 | 212 | 0 | 96 | 5 | 5 | 0 | 0 | 0 | 0 | 5 | 15 | 8 | 33 | 16 | 134 | 158 | 8 | 20 | 1 | 91 | 28 | 50 | 49 | 130 | 299 | 31 | 83 | 0 | 170 | 18 | 0 | 10 | 280 | 8 | 8 | 0 | 244 | 0 | 0 | 195 | 0 | 128 | 13.2 | 100 | 0 | 0 | 0 | 7 | 87 | 0 | 2 | 179 | 0 | 0 | 0 | 101 | 100 | 0 | 104 |  | 930 | 0 | 360 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 26 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 161 | 0 | 77 | 0 | 140 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 35 | 310 |  | 7029.2 | 2855 | 9884.2 | 4212 | 930 | 1949 | 1984 | 460 | 77 | 120 | 134 | 18.2 | 0 | 93.18
11:00 | 0 | 0 | 142 | 110 | 0 | 81 | 0 | 345 | 347 |  | 0 | 420 | 140 | 100 | 76 | 40 | 305 | 0 | 0 | 0 | 35 | 93 | 0 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 8 | 0 | 44 | 35 | 120 | 0 | 0 | 230 | 0 | 147 | 0 |  | 0 | 0 | 0 | 10 | 10 | 24 | 18 | 4 | 0 | 0 | 135 | 265 | 265 | 211 | 0 | 96 | 5 | 5 | 0 | 0 | 0 | 0 | 8 | 15 | 8 | 33 | 16 | 146 | 158 | 8 | 17 | 1 | 91 | 28 | 50 | 49 | 130 | 297 | 31 | 83 | 0 | 177 | 18 | 0 | 10 | 295 | 8 | 8 | 0 | 255 | 0 | 0 | 195 | 0 | 132 | 20.1 | 100 | 0 | 0 | 0 | 7 | 87 | 0 | 3 | 179 | 0 | 0 | 0 | 100 | 90 | 0 | 104 |  | 931 | 0 | 355 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 26 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 77 | 0 | 140 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 35 | 420 |  | 7138.1 | 2954 | 10092.1 | 4234 | 931 | 1961 | 2026 | 570 | 79 | 120 | 146 | 25.1 | 0 | 93.18
12:00 | 0 | 0 | 140 | 110 | 0 | 81 | 0 | 342 | 300 |  | 0 | 390 | 130 | 100 | 80 | 40 | 278 | 0 | 0 | 0 | 35 | 93 | 70 | 11 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 36 | 0 | 44 | 35 | 120 | 0 | 12 | 205 | 0 | 147 | 0 |  | 0 | 0 | 0 | 100 | 11 | 34 | 18 | 4 | 0 | 0 | 100 | 265 | 265 | 213 | 0 | 85 | 29 | 5 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 33 | 16 | 150 | 159 | 40 | 17 | 2 | 91 | 28 | 47 | 49 | 130 | 297 | 20 | 83 | 0 | 177 | 18 | 0 | 0 | 290 | 0 | 8 | 0 | 268 | 0 | 0 | 195 | 0 | 131 | 19.4 | 100 | 50 | 0 | 0 | 7 | 105 | 0 | 6 | 179 | 0 | 0 | 114 | 76 | 100 | 0 | 90 |  | 931 | 0 | 345 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 32 | 65 | 27 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 154 | 0 | 78 | 0 | 140 | 0 | 355 | 35 | 0 | 14 | 0 | 0 | 0 | 3 | 70 | 340 |  | 7352.4 | 3038 | 10390.4 | 4102 | 931 | 1868 | 2550 | 490 | 79 | 190 | 150 | 30.4 | 0 | 93.18
13:00 | 0 | 0 | 134 | 110 | 0 | 82 | 0 | 340 | 270 |  | 0 | 360 | 130 | 100 | 80 | 43 | 263 | 0 | 0 | 0 | 55 | 93 | 133 | 11 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 25 | 51 | 0 | 44 | 35 | 120 | 0 | 25 | 204 | 0 | 151 | 0 |  | 0 | 0 | 67 | 40 | 11 | 50 | 18 | 4 | 0 | 0 | 100 | 265 | 265 | 213 | 0 | 85 | 33 | 5 | 0 | 0 | 0 | 0 | 43 | 0 | 8 | 33 | 17 | 154 | 124 | 48 | 20 | 2 | 91 | 28 | 49 | 50 | 130 | 297 | 20 | 82 | 0 | 177 | 18 | 0 | 10 | 270 | 8 | 8 | 0 | 268 | 0 | 0 | 195 | 0 | 129 | 20 | 100 | 100 | 0 | 0 | 7 | 105 | 0 | 3 | 179 | 0 | 0 | 114 | 35 | 100 | 0 | 90 |  | 930 | 0 | 345 | 0 | 83 | 120 | 0 | 0 | 0 | 0 | 32 | 65 | 27 | 16 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 151 | 0 | 79 | 0 | 140 | 0 | 345 | 35 | 0 | 35 | 0 | 32 | 0 | 4 | 90 | 310 |  | 7419 | 3102 | 10521 | 4060 | 930 | 1792 | 2697 | 460 | 79 | 320 | 154 | 29 | 0 | 93.17
14:00 | 0 | 0 | 140 | 110 | 0 | 82 | 0 | 343 | 270 |  | 0 | 330 | 125 | 100 | 80 | 54 | 260 | 0 | 0 | 0 | 80 | 93 | 149 | 11 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 25 | 8 | 0 | 44 | 35 | 120 | 0 | 25 | 204 | 0 | 151 | 0 |  | 0 | 0 | 65 | 30 | 11 | 50 | 18 | 5 | 0 | 0 | 80 | 265 | 265 | 213 | 0 | 86 | 35 | 5 | 0 | 0 | 0 | 0 | 43 | 0 | 8 | 33 | 17 | 158 | 108 | 0 | 17 | 2 | 91 | 28 | 47 | 50 | 110 | 297 | 31 | 83 | 0 | 177 | 18 | 0 | 10 | 275 | 16 | 8 | 0 | 282 | 0 | 0 | 0 | 0 | 131 | 19 | 100 | 17 | 0 | 0 | 0 | 105 | 0 | 5 | 179 | 0 | 0 | 34 | 52 | 100 | 0 | 36 |  | 930 | 0 | 290 | 0 | 83 | 120 | 0 | 0 | 0 | 0 | 32 | 65 | 27 | 16 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 79 | 0 | 140 | 0 | 280 | 35 | 0 | 35 | 0 | 75 | 0 | 2 | 90 | 310 |  | 6926 | 3009 | 9935 | 3983 | 930 | 1679 | 2284 | 460 | 79 | 334 | 158 | 28 | 0 | 93.17
15:00 | 0 | 0 | 140 | 110 | 0 | 82 | 0 | 340 | 250 |  | 0 | 300 | 140 | 96 | 80 | 55 | 287 | 0 | 0 | 0 | 91 | 93 | 150 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 24 | 33 | 33 | 8 | 0 | 45 | 35 | 120 | 0 | 25 | 204 | 0 | 147 | 0 |  | 0 | 0 | 65 | 36 | 11 | 50 | 18 | 5 | 0 | 0 | 80 | 265 | 265 | 213 | 0 | 86 | 35 | 5 | 0 | 0 | 0 | 0 | 43 | 0 | 8 | 33 | 17 | 162 | 83 | 0 | 20 | 0 | 89 | 28 | 44 | 50 | 110 | 296 | 31 | 83 | 0 | 178 | 18 | 0 | 10 | 275 | 24 | 8 | 0 | 285 | 0 | 0 | 0 | 0 | 125 | 9 | 100 | 0 | 0 | 0 | 0 | 105 | 0 | 3 | 179 | 0 | 0 | 23 | 82 | 100 | 0 | 35 |  | 929 | 0 | 270 | 0 | 83 | 120 | 0 | 0 | 0 | 0 | 32 | 65 | 27 | 16 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 5 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 78 | 0 | 140 | 0 | 305 | 17 | 0 | 35 | 0 | 80 | 0 | 3 | 90 | 310 |  | 6879 | 2992 | 9871 | 3941 | 929 | 1650 | 2299 | 460 | 80 | 335 | 162 | 15 | 0 | 93.17
16:00 | 0 | 0 | 140 | 110 | 0 | 82 | 0 | 339 | 250 |  | 0 | 300 | 140 | 38 | 80 | 55 | 300 | 0 | 0 | 0 | 91 | 93 | 98 | 22 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 29 | 33 | 33 | 0 | 0 | 43 | 35 | 120 | 0 | 0 | 204 | 0 | 147 | 0 |  | 0 | 0 | 65 | 0 | 8 | 50 | 20 | 5 | 0 | 0 | 80 | 265 | 265 | 213 | 0 | 95 | 35 | 5 | 0 | 0 | 0 | 0 | 43 | 17 | 8 | 33 | 17 | 166 | 85 | 0 | 20 | 0 | 89 | 28 | 52 | 49 | 110 | 296 | 31 | 83 | 0 | 204 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 285 | 0 | 0 | 0 | 0 | 120 | 9 | 100 | 0 | 0 | 0 | 0 | 105 | 0 | 1 | 160 | 0 | 0 | 0 | 99 | 100 | 0 | 35 |  | 931 | 0 | 275 | 0 | 94 | 120 | 0 | 0 | 0 | 0 | 40 | 65 | 25 | 16 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 5 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 78 | 0 | 140 | 0 | 335 | 0 | 0 | 35 | 0 | 84 | 0 | 1 | 90 | 310 |  | 6772 | 3023 | 9795 | 4019 | 931 | 1700 | 2147 | 460 | 78 | 283 | 166 | 11 | 0 | 93.16
17:00 | 0 | 0 | 140 | 110 | 0 | 82 | 0 | 339 | 250 |  | 0 | 300 | 130 | 7 | 80 | 55 | 270 | 0 | 0 | 0 | 91 | 93 | 98 | 28 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 42 | 35 | 120 | 0 | 0 | 204 | 0 | 100 | 0 |  | 0 | 0 | 65 | 0 | 11 | 50 | 20 | 9 | 0 | 0 | 80 | 265 | 265 | 213 | 0 | 86 | 35 | 5 | 0 | 0 | 0 | 0 | 43 | 17 | 8 | 33 | 17 | 152 | 104 | 0 | 20 | 0 | 89 | 28 | 14 | 10 | 110 | 294 | 31 | 40 | 0 | 225 | 18 | 0 | 10 | 280 | 16 | 8 | 0 | 285 | 0 | 0 | 0 | 0 | 125 | 2 | 100 | 0 | 0 | 0 | 4 | 105 | 0 | 0 | 160 | 0 | 0 | 0 | 102 | 100 | 0 | 18 |  | 930 | 0 | 270 | 0 | 90 | 120 | 0 | 0 | 0 | 0 | 40 | 65 | 25 | 16 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 6 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 78 | 0 | 140 | 0 | 257 | 0 | 0 | 35 | 0 | 92 | 0 | 1 | 90 | 310 |  | 6552 | 2944 | 9496 | 3980 | 930 | 1497 | 2114 | 460 | 77 | 283 | 152 | 3 | 0 | 93.16
18:00 | 0 | 0 | 100 | 110 | 0 | 43 | 0 | 300 | 250 |  | 0 | 290 | 150 | 7 | 80 | 55 | 309 | 0 | 0 | 0 | 95 | 93 | 105 | 22 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 41 | 35 | 120 | 0 | 0 | 215 | 0 | 80 | 0 |  | 0 | 0 | 87 | 0 | 11 | 50 | 20 | 10 | 0 | 0 | 80 | 280 | 290 | 210 | 0 | 96 | 35 | 5 | 0 | 0 | 0 | 5 | 24 | 18 | 8 | 33 | 14 | 156 | 104 | 19 | 22 | 0 | 91 | 30 | 14 | 10 | 110 | 297 | 31 | 10 | 0 | 225 | 18 | 0 | 10 | 240 | 23 | 8 | 0 | 284 | 0 | 0 | 35 | 0 | 136 | 0 | 100 | 0 | 0 | 0 | 34 | 105 | 0 | 0 | 124 | 0 | 0 | 0 | 102 | 100 | 0 | 18 |  | 931 | 0 | 275 | 0 | 115 | 120 | 0 | 0 | 0 | 4 | 16 | 65 | 25 | 16 | 0 | 70 | 0 | 0 | 5 | 17 | 0 | 0 | 10 | 0 | 5 | 21 | 8 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 130 | 0 | 78 | 0 | 140 | 0 | 258 | 0 | 0 | 35 | 0 | 95 | 0 | 0 | 90 | 310 |  | 6538 | 2996 | 9534 | 3997 | 931 | 1382 | 2175 | 459 | 76 | 358 | 156 | 0 | 0 | 93.16
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 140 | 110 | 0 | 82 | 0 | 344 | 330 |  | 0 | 390 | 120 | 7 | 80 | 55 | 258 | 0 | 0 | 0 | 100 | 93 | 150 | 33 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 47 | 0 | 40 | 35 | 120 | 0 | 22 | 204 | 0 | 148 | 0 |  | 0 | 0 | 100 | 30 | 11 | 50 | 20 | 27 | 0 | 0 | 80 | 280 | 265 | 215 | 0 | 85 | 35 | 5 | 0 | 0 | 0 | 42 | 38 | 18 | 11 | 33 | 14 | 176 | 124 | 64 | 22 | 0 | 91 | 30 | 52 | 39 | 130 | 296 | 52 | 85 | 0 | 190 | 18 | 0 | 10 | 280 | 23 | 8 | 50 | 284 | 58 | 50 | 100 | 95 | 139 | 0 | 100 | 25 | 0 | 0 | 45 | 105 | 0 | 0 | 214 | 0 | 12 | 114 | 104 | 100 | 0 | 18 |  | 930 | 0 | 410 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 65 | 39 | 96 | 0 | 70 | 0 | 50 | 35 | 98 | 0 | 0 | 43 | 43 | 30 | 21 | 8 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 135 | 0 | 79 | 58 | 159 | 0 | 358 | 70 | 50 | 88 | 0 | 105 | 0 | 0 | 90 | 450 |  | 7869 | 4015 | 11884 | 4219 | 930 | 1935 | 3282 | 599 | 75 | 668 | 176 | 0 | 0 | 93.15
19:30 | 0 | 0 | 140 | 110 | 0 | 82 | 0 | 340 | 300 |  | 0 | 320 | 120 | 7 | 80 | 55 | 265 | 0 | 0 | 0 | 100 | 93 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 40 | 35 | 120 | 0 | 25 | 203 | 0 | 100 | 0 |  | 0 | 0 | 100 | 30 | 11 | 50 | 20 | 30 | 0 | 0 | 80 | 295 | 265 | 215 | 4 | 85 | 35 | 5 | 0 | 0 | 0 | 42 | 43 | 18 | 11 | 33 | 14 | 182 | 159 | 64 | 20 | 0 | 91 | 28 | 52 | 49 | 110 | 295 | 52 | 85 | 0 | 190 | 18 | 0 | 10 | 270 | 23 | 11 | 0 | 284 | 58 | 50 | 100 | 103 | 139 | 0 | 100 | 90 | 0 | 0 | 45 | 105 | 0 | 0 | 214 | 0 | 17 | 114 | 113 | 100 | 0 | 18 |  | 930 | 0 | 410 | 0 | 115 | 155 | 0 | 0 | 0 | 0 | 40 | 65 | 40 | 96 | 0 | 70 | 0 | 50 | 35 | 98 | 0 | 0 | 43 | 43 | 32 | 21 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 145 | 0 | 77 | 100 | 135 | 0 | 370 | 70 | 0 | 113 | 0 | 105 | 0 | 0 | 90 | 510 |  | 7889 | 4127 | 12016 | 4215 | 930 | 1833 | 3416 | 660 | 75 | 705 | 182 | 0 | 0 | 0
20:00 | 5 | 0 | 140 | 110 | 0 | 82 | 0 | 338 | 250 |  | 0 | 300 | 146 | 7 | 96 | 55 | 288 | 0 | 0 | 0 | 100 | 93 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 41 | 35 | 120 | 0 | 25 | 203 | 0 | 100 | 0 |  | 0 | 0 | 98 | 30 | 11 | 50 | 20 | 34 | 0 | 0 | 80 | 310 | 265 | 214 | 8 | 90 | 35 | 5 | 0 | 0 | 0 | 42 | 43 | 18 | 11 | 33 | 20 | 180 | 143 | 64 | 20 | 0 | 91 | 28 | 51 | 49 | 110 | 298 | 52 | 85 | 0 | 185 | 18 | 0 | 10 | 270 | 16 | 11 | 0 | 282 | 0 | 0 | 108 | 0 | 145 | 0 | 100 | 150 | 0 | 0 | 47 | 105 | 0 | 0 | 215 | 0 | 17 | 114 | 106 | 100 | 0 | 17 |  | 930 | 0 | 370 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 65 | 41 | 96 | 0 | 70 | 0 | 50 | 35 | 96 | 0 | 0 | 47 | 43 | 33 | 21 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 145 | 0 | 77 | 100 | 130 | 0 | 399 | 70 | 0 | 113 | 0 | 107 | 0 | 0 | 90 | 540 |  | 7747 | 4192 | 11939 | 4196 | 930 | 1800 | 3316 | 690 | 76 | 751 | 180 | 0 | 0 | 93.15
21:00 | 20 | 0 | 140 | 110 | 0 | 82 | 0 | 341 | 273 |  | 0 | 300 | 140 | 7 | 96 | 55 | 308 | 0 | 0 | 0 | 100 | 93 | 150 | 32 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 41 | 35 | 120 | 0 | 25 | 213 | 0 | 100 | 0 |  | 0 | 0 | 101 | 30 | 12 | 50 | 20 | 36 | 0 | 0 | 80 | 360 | 285 | 212 | 8 | 96 | 35 | 5 | 0 | 16 | 0 | 8 | 43 | 18 | 11 | 33 | 21 | 180 | 144 | 64 | 20 | 0 | 89 | 30 | 52 | 49 | 110 | 298 | 63 | 85 | 0 | 185 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 285 | 0 | 0 | 150 | 0 | 149 | 0 | 100 | 0 | 0 | 0 | 65 | 103 | 0 | 0 | 215 | 0 | 17 | 88 | 113 | 100 | 0 | 17 |  | 931 | 0 | 370 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 65 | 40 | 96 | 0 | 70 | 0 | 50 | 25 | 96 | 0 | 0 | 43 | 43 | 32 | 21 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 148 | 0 | 77 | 100 | 130 | 0 | 408 | 70 | 0 | 113 | 0 | 106 | 0 | 0 | 90 | 570 |  | 7736 | 4218 | 11954 | 4334 | 931 | 1870 | 3138 | 720 | 76 | 705 | 180 | 0 | 0 | 93.14
22:00 | 35 | 0 | 141 | 110 | 0 | 82 | 0 | 347 | 335 |  | 0 | 340 | 132 | 7 | 96 | 55 | 300 | 0 | 0 | 0 | 100 | 93 | 150 | 24 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 23 | 33 | 33 | 16 | 0 | 42 | 35 | 120 | 0 | 0 | 204 | 0 | 100 | 0 |  | 0 | 0 | 100 | 30 | 12 | 50 | 20 | 39 | 0 | 0 | 80 | 360 | 355 | 214 | 8 | 91 | 35 | 5 | 0 | 34 | 0 | 0 | 43 | 18 | 11 | 33 | 21 | 180 | 144 | 64 | 20 | 0 | 90 | 30 | 53 | 49 | 110 | 297 | 62 | 85 | 0 | 184 | 18 | 0 | 10 | 290 | 23 | 11 | 0 | 283 | 0 | 0 | 155 | 0 | 149 | 0 | 100 | 0 | 6 | 0 | 35 | 103 | 0 | 0 | 215 | 0 | 17 | 34 | 113 | 100 | 0 | 17 |  | 930 | 0 | 370 | 0 | 115 | 155 | 0 | 0 | 0 | 0 | 40 | 65 | 41 | 110 | 0 | 70 | 0 | 0 | 0 | 99 | 0 | 0 | 43 | 25 | 32 | 21 | 7 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 151 | 0 | 77 | 100 | 130 | 0 | 410 | 70 | 0 | 113 | 0 | 106 | 0 | 0 | 90 | 570 |  | 7770 | 4101 | 11871 | 4407 | 930 | 1996 | 2982 | 720 | 77 | 579 | 180 | 0 | 0 | 93.14
23:00 | 35 | 0 | 140 | 110 | 0 | 82 | 0 | 339 | 333 |  | 0 | 340 | 130 | 7 | 96 | 55 | 281 | 0 | 0 | 0 | 100 | 93 | 82 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 42 | 35 | 120 | 0 | 0 | 205 | 0 | 100 | 0 |  | 0 | 0 | 99 | 0 | 12 | 50 | 20 | 35 | 0 | 0 | 80 | 360 | 285 | 215 | 8 | 93 | 35 | 5 | 0 | 43 | 0 | 0 | 43 | 18 | 11 | 33 | 21 | 182 | 144 | 64 | 22 | 0 | 90 | 28 | 53 | 49 | 110 | 297 | 64 | 85 | 0 | 184 | 18 | 0 | 10 | 290 | 23 | 11 | 0 | 283 | 0 | 0 | 155 | 0 | 149 | 0 | 100 | 0 | 65 | 0 | 35 | 103 | 0 | 0 | 215 | 0 | 17 | 44 | 112 | 100 | 0 | 17 |  | 931 | 0 | 370 | 0 | 115 | 140 | 0 | 0 | 0 | 0 | 33 | 65 | 39 | 110 | 0 | 70 | 0 | 0 | 0 | 99 | 0 | 0 | 43 | 25 | 32 | 17 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 40 | 0 | 139 | 0 | 78 | 60 | 130 | 0 | 406 | 70 | 0 | 113 | 0 | 106 | 0 | 0 | 90 | 570 |  | 7642 | 4057 | 11699 | 4350 | 931 | 1988 | 2956 | 720 | 77 | 495 | 182 | 0 | 0 | 93.13
24:00 | 35 | 0 | 140 | 110 | 0 | 82 | 0 | 340 | 328 |  | 0 | 340 | 130 | 7 | 96 | 55 | 288 | 0 | 0 | 0 | 100 | 93 | 82 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 43 | 35 | 120 | 0 | 0 | 204 | 0 | 100 | 0 |  | 0 | 0 | 99 | 0 | 12 | 50 | 20 | 39 | 0 | 0 | 80 | 360 | 285 | 187 | 8 | 86 | 35 | 5 | 0 | 43 | 0 | 0 | 43 | 18 | 11 | 33 | 21 | 176 | 145 | 72 | 22 | 0 | 90 | 28 | 53 | 49 | 110 | 296 | 64 | 85 | 0 | 184 | 18 | 0 | 10 | 290 | 23 | 11 | 0 | 286 | 0 | 0 | 155 | 0 | 149 | 0 | 100 | 0 | 115 | 0 | 35 | 103 | 0 | 0 | 215 | 0 | 17 | 52 | 113 | 100 | 0 | 17 |  | 930 | 0 | 370 | 0 | 115 | 140 | 0 | 0 | 0 | 0 | 33 | 65 | 39 | 110 | 0 | 70 | 0 | 0 | 0 | 99 | 0 | 0 | 43 | 25 | 31 | 21 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 0 | 0 | 78 | 60 | 130 | 0 | 400 | 70 | 0 | 113 | 0 | 106 | 0 | 0 | 90 | 570 |  | 7678 | 4004 | 11682 | 4273 | 930 | 1985 | 3026 | 720 | 78 | 494 | 176 | 0 | 0 | 93.13
KWH | 90000 | 0 | 3310000 | 2772000 | 0 | 1897500 | 0 | 8315910 | 7398000 |  | 0 | 8738000 | 3309324 | 1391040 | 1731480 | 1072980 | 7044485 | 0 | 0 | 0 | 1752000 | 2084832 | 1603200 | 402374 | 0 | 0 | 0 | 864360 | 869735 | 865396 | 442692 | 600000 | 662040 | 779100 | 795400 | 328128 | 0 | 1036015 | 852000 | 2900000 | 0 | 189412 | 4871931 | 0 | 3110089 | 0 |  | 0 | 0 | 1182438 | 358080 | 194880 | 718560 | 428112 | 545280 | 0 | 0 | 2053690 | 7147400 | 6590000 | 4950000 | 100363 | 2149490 | 696744 | 137280 | 0 | 404936 | 0 | 122048 | 594989 | 326916 | 224100 | 817600 | 459940 | 3829440 | 3241640 | 632640 | 452808 | 4750 | 2136000 | 672360 | 1171800 | 1144656 | 3185918 | 6654000 | 513024 | 1929600 | 0 | 4301850 | 429000 | 0 | 227520 | 7077700 | 415320 | 210000 | 29376 | 5233962 | 72453 | 48677 | 3480000 | 111481 | 3051360 | 132165 | 2358720 | 507360 | 247563 | 0 | 380400 | 1538028 | 0 | 29160 | 4212764 | 0 | 103708 | 744420 | 2276400 | 2425920 | 0 | 1416000 |  | 22352727 | 0 | 8223840 | 0 | 1822080 | 3167040 | 0 | 0 | 0 | 2480 | 481875 | 1549000 | 767900 | 968832 | 0 | 1666000 | 0 | 183180 | 93027 | 601544 | 0 | 0 | 242344 | 240000 | 174349 | 494400 | 163656 | 205074 | 0 | 0 | 3688300 | 0 | 0 | 182600 | 0 | 3861136 | 0 | 1855 | 528000 | 4230182 | 0 | 8842455 | 571680 | 38368 | 901056 | 0 | 1441920 | 0 | 20102 | 1780320 | 11747700 |  | 168912212 | 81235022 | 250147234 | 100481473 | 22352727 | 44228819 | 54372933 | 15436000 | 1888015 | 7371650 | 3829440 | 186177 | 0
Fuel Cost | 147600 | 0 | 4832600 | 4074840 | 0 | 2504700 | 0 | 8399069.1 | 7619940 |  | 0 | 9524420 | 3673349.64 | 10557993.6 | 11929897.2 | 9077410.8 | 7326264.4 | 0 | 0 | 0 | 13192560 | 19013667.84 | 15775488 | 3709888.28 | 0 | 0 | 0 | 6309828 | 6723051.55 | 8532804.56 | 332019 | 450000 | 0 | 0 | 0 | 3172997.76 | 0 | 279724.05 | 230040 | 5249000 | 0 | 1759637.48 | 5310404.79 | 0 | 5287151.3 | 0 |  | 0 | 0 | 11469648.6 | 3419664 | 1695456 | 5690995.2 | 539421.12 | 1619481.6 | 0 | 0 | 3018924.3 | 5289076 | 6590000 | 4554000 | 129468.27 | 2471913.5 | 787320.72 | 192192 | 0 | 692440.56 | 0 | 1232684.8 | 5682144.95 | 415183.32 | 168075 | 1430800 | 344955 | 28720800 | 3436138.4 | 5744371.2 | 575066.16 | 75715 | 3503040 | 1075776 | 2085804 | 1785663.36 | 3631946.52 | 6920160 | 1010657.28 | 3685536 | 0 | 7442200.5 | 939510 | 0 | 464140.8 | 7148477 | 311490 | 159600 | 499685.76 | 39568752.72 | 1230251.94 | 813879.44 | 18096000 | 1863962.32 | 30025382.4 | 1545008.85 | 19223568 | 5504856 | 1745319.15 | 0 | 3469248 | 14534364.6 | 0 | 0 | 31848495.84 | 0 | 911593.32 | 7429311.6 | 19508748 | 16156627.2 | 0 | 0 |  | 128751707.52 | 0 | 8635032 | 0 | 14321548.8 | 43895174.4 | 0 | 0 | 0 | 25990.4 | 5021137.5 | 1750370 | 1190245 | 9455800.32 | 0 | 3415300 | 0 | 1802491.2 | 945154.32 | 5323664.4 | 0 | 0 | 2348313.36 | 2325600 | 1691185.3 | 949248 | 253666.8 | 155241.018 | 0 | 0 | 19990586 | 0 | 0 | 213642 | 0 | 5096699.52 | 0 | 2782.5 | 8981280 | 4949312.94 | 0 | 8754030.45 | 5968339.2 | 652639.68 | 8551021.44 | 0 | 11189299.2 | 0 | 222127.1 | 13156564.8 | 51572403 |  | 525121339.65 | 371557598.168 | 896678937.818 | 116607853.368 | 128751707.52 | 52234182.86 | 411938995.29 | 71562989 | 509764.05 | 84509794.78 | 28720800 | 1842850.95 | 0
Yesterday Day Peak | 0 | 0 | 140 | 110 | 0 | 81 | 0 | 342 | 300 |  | 0 | 390 | 130 | 100 | 80 | 40 | 278 | 0 | 0 | 0 | 35 | 93 | 70 | 11 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 36 | 0 | 44 | 35 | 120 | 0 | 12 | 205 | 0 | 147 | 0 |  | 0 | 0 | 0 | 100 | 11 | 34 | 18 | 4 | 0 | 0 | 100 | 265 | 265 | 213 | 0 | 85 | 29 | 5 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 33 | 16 | 150 | 159 | 40 | 17 | 2 | 91 | 28 | 47 | 49 | 130 | 297 | 20 | 83 | 0 | 177 | 18 | 0 | 0 | 290 | 0 | 8 | 0 | 268 | 0 | 0 | 195 | 0 | 131 | 19.4 | 100 | 50 | 0 | 0 | 7 | 105 | 0 | 6 | 179 | 0 | 0 | 114 | 76 | 100 | 0 | 90 |  | 931 | 0 | 345 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 32 | 65 | 27 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 154 | 0 | 78 | 0 | 140 | 0 | 355 | 35 | 0 | 14 | 0 | 0 | 0 | 3 | 70 | 340 |  | 10390.4 | DayPeak
Yesterday Evening Peak | 0 | 0 | 140 | 110 | 0 | 82 | 0 | 340 | 300 | 0 | 0 | 320 | 120 | 7 | 80 | 55 | 265 | 0 | 0 | 0 | 100 | 93 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 40 | 35 | 120 | 0 | 25 | 203 | 0 | 100 | 0 | 0 | 0 | 0 | 100 | 30 | 11 | 50 | 20 | 30 | 0 | 0 | 80 | 295 | 265 | 215 | 4 | 85 | 35 | 5 | 0 | 0 | 0 | 42 | 43 | 18 | 11 | 33 | 14 | 182 | 159 | 64 | 20 | 0 | 91 | 28 | 52 | 49 | 110 | 295 | 52 | 85 | 0 | 190 | 18 | 0 | 10 | 270 | 23 | 11 | 0 | 284 | 58 | 50 | 100 | 103 | 139 | 0 | 100 | 90 | 0 | 0 | 45 | 105 | 0 | 0 | 214 | 0 | 17 | 114 | 113 | 100 | 0 | 18 |  | 930 | 0 | 410 | 0 | 115 | 155 | 0 | 0 | 0 | 0 | 40 | 65 | 40 | 96 | 0 | 70 | 0 | 50 | 35 | 98 | 0 | 0 | 43 | 43 | 32 | 21 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 145 | 0 | 77 | 100 | 135 | 0 | 370 | 70 | 0 | 113 | 0 | 105 | 0 | 0 | 90 | 510 |  | 12016 | EvPeak
Forecast for Evening | 0 | 0 | 140 | 110 | 0 | 82 | 0 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 96 | 55 | 335 | 0 | 0 | 0 | 100 | 93 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 40 | 35 | 120 | 0 | 25 | 225 | 0 | 150 | 0 | 0 | 0 |  | 100 | 100 | 12 | 50 | 20 | 30 | 0 | 0 | 80 | 360 | 360 | 225 | 8 | 100 | 36 | 10 | 0 | 43 | 0 | 42 | 43 | 21 | 11 | 33 | 20 | 180 | 160 | 72 | 22 | 0 | 90 | 30 | 51 | 44 | 163 | 300 | 64 | 86 | 0 | 190 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 104 |  | 942 | 16 | 410 | 0 | 115 | 225 | 0 | 0 | 30 | 60 | 40 | 65 | 33 | 110 | 0 | 70 | 0 | 50 | 40 | 100 | 0 | 0 | 43 | 43 | 32 | 22 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 220 | 0 | 0 | 0 | 80 | 100 | 220 | 0 | 414 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 90 | 620
Forecast for Day | 0 | 0 | 100 | 110 | 0 | 82 | 0 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 96 | 55 | 335 | 0 | 0 | 0 | 100 | 93 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 40 | 35 | 120 | 0 | 25 | 225 | 0 | 140 | 0 | 0 | 0 |  | 100 | 100 | 12 | 50 | 20 | 10 | 0 | 0 | 80 | 360 | 360 | 225 | 8 | 100 | 35 | 10 | 0 | 43 | 0 | 0 | 43 | 21 | 11 | 33 | 20 | 150 | 160 | 72 | 22 | 1.6 | 90 | 30 | 51 | 44 | 163 | 300 | 64 | 86 | 0 | 190 | 18 | 0 | 10 | 341 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 104 |  | 942 | 0 | 410 | 0 | 115 | 225 | 0 | 0 | 0 | 0 | 40 | 65 | 33 | 110 | 0 | 70 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 43 | 0 | 22 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 220 | 0 | 0 |  | 80 | 80 | 220 | 0 | 414 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 90 | 620
Generation at 08:00(Today) | 0 | 0 | 140 | 110 | 0 | 82 | 0 | 353 | 304 | 0 | 0 | 350 | 142 |  | 48 | 25 | 306 | 0 | 0 | 0 | 50 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 23 | 33 | 25 | 0 | 0 | 42 | 35 | 120 | 0 | 0 | 210 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 0 | 0 | 80 | 275 | 270 | 213 | 8 | 96 | 31 | 5 | 0 | 40 | 0 | 0 | 0 | 18 | 11 | 25 | 9 | 138 | 156 | 48 | 22 | 1 | 90 | 30 | 53 | 49 | 130 | 296 | 63 | 83 | 0 | 185 | 18 | 0 | 10 | 300 | 23 | 8 | 0 | 45 | 0 | 0 | 120 | 0 | 100 | 11 | 50 | 0 | 0 | 0 | 8 | 0 | 0 | 2 | 106 | 0 | 0 | 0 | 75 | 100 | 0 | 17 | 0 | 934 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 16 | 65 | 26 | 16 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 5 | 8 | 0 | 0 | 150 | 0 | 0 | 145 | 0 | 0 | 0 | 78 | 0 | 150 | 0 | 365 | 35 | 0 | 0 | 0 | 35 | 0 | 1 | 50 | 520 | 0
199
| Minimum Generation |  | 8985 | 7:00
| Highest Generation |  | 12016 | 19:30
| Day Peak Generation |  | 10390.4 | 12:00
| Evening Peak Generation |  | 12016 | 19:30
| HVDC Max Flow |  | 935 | 3:00
| HVDC EvPeak Flow |  | 930 | 19:30
| Load factor L.F |  | 86.74%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-09-09
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-09-08 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10390.4 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 9122 | MW
Evening Peak Generation : |  | 12016 | MW Hour : | 19:30 | Available Max Generation : |  | 15249 | MW
E.P. Demand (at gen end) : |  | 12016 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 13000 | MW
Maximum Generation : |  | 12016 | MW Hour : | 19:30 | Reserve(Generation end) |  | 2249 | MW
Total Gen. (MKWH) : |  | 250.1472 | System Load Factor : | 86.74% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -75 | MW at | 15:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-09-09
Actual : | 93.11 | Ft.(MSL) , | Rule curve : | 100.84 | Ft.( MSL )
Gas Consumed : | Total = | 1207.42 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 168842036.228
: |  | Coal : | 71562989 | Oil : | 496448790.07 | Total : | 736853815.298
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4687.1254 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1599.2411 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1433.822 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1295.9181 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1170.9155 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 944.9009 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 521.4458 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 243.1041 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 728.7875 |  |  | 0 | 0%
Total | 0 |  | 12625.2604 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 9) Bhola 225 MW GT-2 & ST
|  |  |  | 2) Bibiyana #3 | 10) Payra Unit-1
3) Ghorasal Unit-1,2,3,7
4) Ashuganj unit-3,4
5) Kaptai-1,2,5
6) Raozan #1,2
7) Sirajganj #2
8) Baghabari-71 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Cumilla(N) 132/33 kV T-3 transformer was under shut down from 10:08 to 10:33 for C/M.
b) Cumilla(N) 132/33 kV T-4 transformer was under shut down from 10:37 to 11:23 for C/M.
c) Ashuganj 230 kV Bus-1 was under shut down from 09:50 to 18:32 for C/M.
d) Ashuganj-Ashuganj(S) 230 kV Ckt-2 was under shut down from 09:28 to 18:39 for Bus-1 isolator problem.
e) Ashuganj-Sirajganj 230 kV Ckt-2 was under shut down from 08:08 to 18:32 for Bus-1 isolator problem.
f) Aminbazar-Bosila-108 MW 132 kV Ckt was under shut down from 09:25 to 21:15 for D/W.
g) Mymensing 132/33 kV T-2 transformer on fire & T-1, T-3 also tripped at 13:15. |  |  |  |  | About 420 MW power interruption occurred under Mymensing zone area
At the same time Mymensing RPCL, Mymensing-200 MW, Jamalpur-115 MW & Jamalpur-95 MW |  |  |  |  | from 13:15 to 16:34.
also tripped and were synchronized at 13:38,17:07, 16:45 & 17:13 respectively. T-3 transformer
was switched on at 16:34.
h) Mymensing 132 kV Bus-1 & 2 were switched on at 15:58.
i) Mymensing-Kishorganj 132 kV Ckt-1 & 2 were switched on at 15:58 & 17:45 respectively.
j) Mymensing-Netrokona 132 kV Ckt-1 & 2 were switched on at 16:03 & 17:47 respectively.
k) Mymensing-RPCL 132 kV Ckt-1 & 2 were switched on at 16:04 & 17:47 respectively.
l) Mymensing-Jamalpur 132 kV Ckt-1 & 2 were switched on at 22:33 & 15:59 respectively.
m) Feni-Choddagram 132 kV Ckt-1 tripped at 11:43 showing O/C & E/F relays and was switched on at 14:36.
n) Sirajganj #1 was synchronized at 22:33.
o) Sirajganj #2 was shut down at 23:56 for MI.
p) Khulna©-KPCL-2 132 kV Ckt is under shut down since 07:25(9/9/20) for C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-09-08 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 90000 | Unit-1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 140 | 3310000 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 110 | 2772000 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 82 | 1897500 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 340 | 8315910 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 300 | 7398000 | frequency control.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 320 | 8738000 | frequency control.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 7 | 1391040 | Fuel Shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 120 | 3309324 | GT-1 Under S/D due to gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 80 | 1731480 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1072980
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 100 | 402374
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 442692
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 1752000
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 265 | 7044485 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 2084832 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel Shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 864360
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1603200
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 869735
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 865396
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1262040 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 779100
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 795400
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 52 | 328128
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 284 | 5233962 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 58 | 72453 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 50 | 48677 | Low demand
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 103 | 111481
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 139 | 3051360 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 1538028
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 18 | 1416000 | Engine problem
| Dhaka area Total |  |  |  | 5895 | 3378 | 70591937
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2900000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 189412
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 132165
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 718560
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 75 | 1888015 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4871931
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 100 | 3110089 | Gas shortage.
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 100 | 1182438
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 30 | 358080 | Low demand
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2358720
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 428112
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 30 | 545280
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 11 | 194880 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 29160
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 214 | 4212764 | Low demand
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 17 | 103708 | Low demand
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2425920
| Chattogram area Total |  |  |  | 2266 | 1195 | 25649234
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 2053690 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 215 | 4950000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 295 | 7147400 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 265 | 6590000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 35 | 696744 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 137280 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 4 | 100363 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 404936 | 230 kV bus S/D.
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 247563 | 230 kV bus S/D.
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 42 | 122048
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 85 | 2149490
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 90 | 507360 | Low demand
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 326916
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 224100
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 182 | 3829440
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 817600
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 594989 | Engine problem
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 14 | 459940
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 29376 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 744420
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 2276400
| Cumilla Area Total |  |  |  | 2980 | 1644 | 34410055
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 159 | 3241640 | Machine problem
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 452808
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 64 | 632640 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 4750
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 100 | 3480000 | Grid fault
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 45 | 380400 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 388 | 8192238
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 91 | 2136000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 28 | 672360 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 3185918 | Frequency control.
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 295 | 6654000
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 52 | 1171800
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 49 | 1144656
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 210000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 52 | 513024 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1929600
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 190 | 4301850
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 429000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 23 | 415320
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 270 | 7077700 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 227520
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1284 | 30068748
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 930 | 22352727
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 1822080
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 155 | 3167040 | Low demand
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 2480 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 410 | 8223840 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 481875
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 528000
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 70 | 571680 | Low demand
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Reserve
| Khulna Area Total |  |  |  | 2284 | 1820 | 37149722
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 96 | 968832 | L/O
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 40 | 767900
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 65 | 1549000 | GT-2 Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 77 | 1855 | Engine problem
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 510 | 11747700
| Barisal Area Total |  |  |  | 1054 | 788 | 15035287
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 70 | 1666000
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 183180
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 35 | 93027 | Engine problem
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 43 | 242344 | Engine problem
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 182600 | Gas shortage.
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 145 | 3861136 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 135 | 4230182 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 370 | 8842455 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 174349
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 494400
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 8 | 163656
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 205074
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 240000 | Engine problem
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 98 | 601544
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 38368 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 901056
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 90 | 1780320 | Engine problem
| Rajshahi Area Total |  |  |  | 2183 | 1264 | 23899691
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3688300 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Machine problem
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 105 | 1441920 | Engine problem
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 20102
| Rangpur Area Total |  |  |  | 605 | 255 | 5150322
| Total |  |  |  | 19892 | 12016 | 250147234
| Eastern Grid Total |  |  |  | 13766 | 7889 | 168912212
| Western Grid Total |  |  |  | 6126 | 4127 | 81235022
| National Grid Total |  |  |  | 19892 | 12016 | 250147234
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-09-08
| (a) ENTIRE EASTERN GRID : |  | 7774 | MW | (b) ENTIRE WESTERN GRID : |  | 3890 | MW
| i) Dhaka area |  | 4125 | MW | i) Khulna area |  | 1507 | MW
| ii) Chittagong area |  | 1170 | MW | ii) Rajshahi area |  | 1227 | MW
| iii) Comilla area |  | 1213 | MW | iii) Barisal area |  | 354 | MW
| iv) Mymensingh area |  | 766 | MW | iv) Rangpur area |  | 802 | MW
| v) Sylhet area |  | 500 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11664 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 126 | 9:00 | Sherpur | 106 | 19:30 | Jhenida | 114 | 19:00
| Munsiganj | 128 | 21:00 | Srimongal | 51 | 21:00 | Bottail | 130 | 21:00
| Sonargaon | 78 | 12:00 | Shahjibazar | 126 | 21:00 | G.K Project | 56 | 20:00
| Shyampur | 204 | 24:00 | Fenchuganj | 48 | 19:00 | Faridpur | 188 | 0.8125
| Bhulta | 195 | 22:00 | Kulawara | 41 | 23:00 | Madaripur | 106 | 0.91667
| Madanganj | 56 | 16:00 | Sylhet | 123 | 19:30 | Sariatpur | 66 | 22:00
| Shitalakhya | 113 | 13:00 | Chatak | 28 | 21:00 | Gopalganj | 101 | 19:00
| Rahim steel | 22 | 17:00 | Sunamganj | 44 | 19:30 | Bagerhat | 98 | 20:00
| Matuail | 84 | 12:00 | Biani Bazar | 56 | 18:30 | Mongla | 36 | 8:00
| Ghorasal | 73 | 22:00 | Comilla (S) | 182 | 19:30 | Satkhira | 113 | 0.91667
| Narsingdi | 161 | 22:00 | Comilla(N) | 111 | 19:00 | Gallamari | 51 | 13:00
| Haripur (SBU) | 116 | 13:00 | Chandpur | 112 | 19:30 | Magura | 56 | 0.79167
| Ullon | 54 | 18:30 | Feni | 127 | 18:30 | Norail | 42 | 18:30
| Hasnabad | 202 | 21:00 | Chowmuhani | 184 | 20:00 | Chuadanga | 93 | 20:00
| Magbazar | 106 | 13:00 | Ashuganj | 60 | 20:00 | Barisal(N) | 47 | 0.91667
| Maniknagar | 102 | 13:00 | Daudkandi | 145 | 20:00 | Barisal (S) | 110 | 0.91667
| Bangabhaban | 40 | 11:00 | B.Baria | 161 | 21:00 | Patuakhali | 132 | 0.91667
| Narinda | 92 | 11:00 | Ramganj | 120 | 22:00 | Bhandaria | 58 | 0.91667
| Dhanmondi | 178 | 13:00 | Chaddagram | 39 | 19:00 | Borhan Uddin | 44 | 19:30
| Lalbag | 88 | 12:00 | PHP | 7 | 17:00 | Ishurdi | 59 | 19:00
| Madartek | 74 | 24:00 | Madunaghat | 55 | 18:30 | Ruppur Paromanobik | 2 | 21:00
| Dhaka University | 0 | #NUM! | Hathazari | 106 | 0.8125 | Natore | 122 | 21:00
| Fatullah | 39 | 0.41667 | Khulshi | 194 | 0 | Bogra | 170 | 20:00
| Mirpur | 108 | 18:30 | Halishahar | 144 | 0.625 | Noagaon | 125 | 21:00
| Kalyanpur | 111 | 19:00 | Baraulia | 152 | 0 | Rajshahi | 145 | 20:00
| Gulshan | 130 | 13:00 | Sikalbaha | 27 | 0.77083 | Rajshahi New | 12 | 20:00
| Uttara | 87 | 13:00 | Dohazari | 86 | 0.79167 | C.Nawabganj | 76 | 21:00
| Uttara New | 32 | 13:00 | Cox'sbazar | 106 | 0.83333 | Amnura | 44 | 21:00
| Kamrangirchar | 96 | 19:00 | Chandraghona | 32 | 0.77083 | Pabna | 124 | 20:00
| Savar | 131 | 15:00 | Kaptai | 4.9 | 0.79167 | Shahjadpur | 97 | 21:00
| Bhasantec | 154 | 14:00 | A. Khaer Stl. | 0 | 0.041667 | Serajganj | 100 | 20:00
| Agargaon | 77 | 13:00 | Bakulia | 104 | 0.79167 | Niyamatpur | 56 | 19:00
| Satmosjid | 88 | 13:00 | Julda | 21 | 0.16667 | Joypurhat | 54 | 21:00
| Tongi | 100 | 0.375 | TK chemical | 28.5 | 0.8125 | Sherpur(Bogura) | 46 | 21:00
| Kabirpur | 223 | 18:30 | Modern Steel | 12 | 0.041667 | Mohastangor | 47 | 21:00
| Basundhara | 160 | 13:00 | Shahmirpur | 24.6 | 0.625 | Rangpur | 155 | 19:30
| Manikganj | 72 | 0.875 | Khagrachhari | 26 | 0.8125 | Lalmonirhat | 60 | 20:00
| Joydevpur | 132 | 12:00 | Matarbari | 34.5 | 0.79167 | Saidpur | 110 | 20:00
| New Tongi | 121 | 12:00 | Baroiar Hat | 44 | 0.58333 | Purbasadipur | 106 | 21:00
| Korda | 280 | 19:30 | Rangamati | 13 | 0.79167 | Thakurgaon | 82 | 20:00
| Dhamrai | 90 | 21:00 | Abul Khair 230 | 159 | 0.16667 | Palashbari | 129 | 20:00
| Rajendrapur | 100 | 9:00 | BSRM | 102 | 0.66667 | Barapukuria | 50 | 20:00
| Valuka | 130 | 20:00 | GPH Ispat | 77 | 0.75 | Panchagar | 47 | 20:00
| Tangail | 90 | 20:00 | Goalpara | 24 | 0.79167 | Joldhaka | 28 | 20:00
| Mymensing | 156 | 2:00 | Central s/s | 93 | 19:30 | Kurigram | 56 | 20:00
| Kishorganj | 136 | 21:00 | Noapara | 52 | 22:00
| Netrokona | 107 | 24:00 | Jessore | 116 | 19:30
| Jamalpur | 133 | 20:00 | Benapol | 52 | 19:00
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-09-08 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 394 | 3:00 | 388 | 7:00 | Kaliakoir | 374 | 0.041667 | 365 | 0.33333
| Bheramara | 392 | 7:00 | 387 | 1:00 | Bhulta | 387 | 24:00 | 378 | 0.33333
| Ashuganj(N) | 393 | 24:00 | 383 | 11:00 | Gopalganj | 420 | 0.375 | 401 | 0.041667
| Payra | 423 | 13:00 | 407 | 21:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 232 | 1:00 | 232 | 1:00 | Comilla (N) | 234 | 19:00 | 228 | 8:00
| Ishurdi | 236 | 13:00 | 226 | 2:00 | Hathazari | 225 | 13:00 | 219 | 5:00
| Ashuganj | 235 | 1:00 | 226 | 13:00 | Megnaghat | 232 | 1:00 | 224 | 12:00
| Serajganj | 233 | 18:00 | 226 | 20:00 | Fenchuganj | 240 | 13:00 | 235 | 8:00
| Baghabari | 242 | 18:00 | 237 | 11:00 | Siddhirganj | 229 | 1:00 | 224 | 11:00
| Barapukuria | 237 | 17:00 | 227 | 19:30 | Maniknagar | 227 | 19:30 | 222 | 11:00
| Bogra | 227 | 17:00 | 215 | 19:30 | Agargaon | 224 | 3:00 | 218 | 11:00
| Rajshahi | 226 | 18:00 | 218 | 1:00 | Barisal | 243 | 8:00 | 231 | 18:30
| Khulna South | 286 | 18:30 | 205 | 20:00 | AKSML | 223 | 14:00 | 216 | 1:00
| Rampura | 226 | 1:00 | 222 | 10:00 | BSRM | 224 | 13:00 | 218 | 1:00
| Haripur | 226 | 1:00 | 223 | 10:00 | Bibiyana | 235 | 2:00 | 231 | 22:00
| Hasnabad | 227 | 18:30 | 220 | 10:00 | Bhulta | 229 | 19:00 | 223 | 17:00
| Shyampur | 224 | 19:00 | 219 | 11:00 | Ashuganj (S) | 234 | 23:00 | 230 | 11:00
| Aminbazar | 225 | 19:00 | 221 | 4:00 | Kaliakoir | 229 | 22:00 | 221 | 11:00
| Tongi | 225 | 1:00 | 220 | 15:00 | GPH | 221 | 22:00 | 218 | 1:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 131 | 15:00 | 127 | 7:00 | Hathazari | 134 | 0.54167 | 131 | 0.041667
| Munsiganj | 132 | 1:00 | 127 | 8:00 | Khulshi | 134 | 0.83333 | 129 | 0.20833
| Sonargaon | 131 | 13:00 | 128 | 21:00 | Halishahar | 137 | 0.8125 | 130 | 0.16667
| Shyampur | 133 | 19:00 | 128 | 11:00 | Baraulia | 133 | 0.8125 | 129 | 0.041667
| Bhulta | 124 | 18:00 | 120 | 11:00 | Sikalbaha | 136 | 20:00 | 130 | 0.33333
| Madanganj | 133 | 1:00 | 128 | 12:00 | Dohazari | 132 | 13:00 | 127 | 0.083333
| Shitalakhya | 142 | 19:00 | 133 | 7:00 | Cox'sbazar | 124 | 0.70833 | 116 | 0.041667
| Rahim steal | 131 | 1:00 | 128 | 12:00 | Chandraghona | 134 | 0.54167 | 131 | 0.125
| Matuail | 131 | 15:00 | 127 | 7:00 | Kaptai | 134 | 5:00 | 131 | 0.41667
| Ghorasal | 138 | 1:00 | 136 | 7:00 | A. Khaer Stl. | 132 | 0.8125 | 128 | 7:00
| Narsinghdi | 127 | 18:00 | 122 | 9:00 | Bakulia | 134 | 0.79167 | 130 | 0.16667
| Haripur (SBU) | 131 | 5:00 | 129 | 11:00 | Julda | 135 | 0.77083 | 131 | 0.041667
| Ullon | 132 | 2:00 | 126 | 11:00 | TK Chemical | 135 | 0.83333 | 130 | 4:00
| Hasnabad | 138 | 19:30 | 130 | 9:00 | Modern Steel | 134 | 0.8125 | 130 | 0.041667
| Magbazar | 132 | 3:00 | 126 | 10:00 | Shahmirpur | 135 | 0.8125 | 131 | 0.041667
| Maniknagar | 132 | 1:00 | 127 | 11:00 | Khagrachhari | 133 | 0.8125 | 129 | 0.125
| Bangabhaban | 132 | 1:00 | 127 | 11:00 | Matarbari | 130 | 0.58333 | 120 | 0.91667
| Narinda | 132 | 1:00 | 127 | 11:00 | Baroiar Hat | 133 | 0.83333 | 125 | 0.91667
| Dhanmondi | 132 | 2:00 | 126 | 11:00 | Rangamati | 133 | 0.54167 | 130 | 1:00
| Lalbag | 137 | 19:00 | 127 | 11:00 | Goalpara S/S | 136 | 17:00 | 127 | 2:00
| Madartek | 132 | 1:00 | 125 | 11:00 | Khulna Central S/S | 135 | 0.75 | 129 | 3:00
| Dhaka University | 0 | #NUM! | 0 | #NUM! | Noapara | 134 | 18:00 | 122 | 2:00
| Fatuiiah | 133 | 0.77083 | 129 | 8:00 | Jessore | 130 | 17:00 | 122 | 1:00
| Mirpur | 130 | 4:00 | 124 | 11:00 | Benapol | 129 | 18:00 | 119 | 2:00
| Kalyanpur | 130 | 4:00 | 126 | 11:00 | Jhenida | 127 | 0.70833 | 115 | 19:00
| Gulshan | 130 | 4:00 | 125 | 11:00 | Bottail | 134 | 18:00 | 126 | 19:00
| Uttara | 129 | 4:00 | 125 | 11:00 | G.K Project | 140 | 0.58333 | 135 | 1:00
| Uttara New | 136 | 19:00 | 128 | 7:00 | Faridpur | 135 | 13:00 | 126 | 1:00
| Kamrangirchar | 131 | 2:00 | 126 | 11:00 | Madaripur | 138 | 0.20833 | 130 | 18:30
| Savar | 127 | 3:00 | 124 | 11:00 | Shariyatpur S/S | 137 | 0.375 | 127 | 18:30
| Bhasantec | 130 | 4:00 | 125 | 11:00 | Gopalganj | 140 | 13:00 | 126 | 21:00
| Agargaon | 132 | 3:00 | 127 | 11:00 | Bagerhat | 130 | 17:00 | 120 | 2:00
| Satmosjid | 131 | 4:00 | 126 | 11:00 | Mongla | 127 | 0.75 | 117 | 11:00
| Tongi | 136 | 0.91667 | 132 | 8:00 | Satkhira | 133 | 0.70833 | 126 | 1:00
| Kabirpur | 134 | 13:00 | 129 | 8:00 | Gallamari | 136 | 18:00 | 127 | 2:00
| Basundhara | 131 | 2:00 | 125 | 11:00 | Magura | 125 | 14:00 | 113 | 19:00
| Manikganj | 139 | 21:00 | 129 | 8:00 | Norail | 124 | 0.75 | 109 | 19:30
| Joydevpur | 142 | 13:00 | 135 | 9:00 | Chuadanga | 122 | 17:00 | 105 | 19:00
| New Tongi | 135 | 0.95833 | 127 | 8:00 | Barisal(N) | 138 | 8:00 | 131 | 3:00
| Kodda | 136 | 12:00 | 123 | 0.33333 | Barisal (S) | 136 | 0.54167 | 127 | 15:00
| Dhamrai | 133 | 18:00 | 129 | 22:00 | Patuakhali(S) | 132 | 0.33333 | 122 | 18:30
| Rajendrapur | 134 | 19:00 | 122 | 8:00 | Bhandaria | 128 | 17:00 | 113 | 2:00
| Valuka | 134 | 17:00 | 116 | 22:00 | Ishurdi | 138 | 18:00 | 133 | 3:00
| Tangail | 134 | 5:00 | 128 | 20:00 | Ruppur Paromanobik | 138 | 17:00 | 134 | 21:00
| Mymensing | 132 | 9:00 | 121 | 22:00 | Natore | 137 | 17:00 | 131 | 21:00
| Kishorganj | 132 | 9:00 | 122 | 22:00 | Bogra | 137 | 17:00 | 129 | 21:00
| Netrokona | 133 | 17:00 | 117 | 22:00 | Noagaon | 133 | 17:00 | 123 | 21:00
| Jamalpur | 138 | 1:00 | 131 | 19:30 | Rajshahi | 136 | 17:00 | 130 | 5:00
| Sherpur | 138 | 12:00 | 128 | 19:30 | Rajshahi New | 137 | 18:00 | 130 | 11:00
| Srimongal | 137 | 7:00 | 133 | 0.75 | C.Nawabganj | 136 | 17:00 | 129 | 1:00
| Shahjibazar | 136 | 7:00 | 130 | 0.875 | Amnura | 135 | 17:00 | 129 | 11:00
| Fenchuganj | 136 | 6:00 | 133 | 0.77083 | Pabna | 135 | 17:00 | 129 | 12:00
| Khulawara | 135 | 8:00 | 132 | 0.95833 | Shahjadpur | 137 | 1:00 | 135 | 21:00
| Sylhet | 135 | 8:00 | 130 | 0.91667 | Serajganj | 134 | 14:00 | 129 | 21:00
| Chatak | 136 | 14:00 | 129 | 21:00 | Niyamatpur | 131 | 18:00 | 121 | 21:00
| Sunamganj | 134 | 8:00 | 127 | 0.875 | Joypurhat | 134 | 18:00 | 122 | 21:00
| Biani Bazar | 134 | 9:00 | 127 | 0.91667 | Sherpur(Bogura) | 137 | 18:00 | 129 | 19:30
| Comilla(s) | 126 | 8:00 | 120 | 18:30 | Mohastangor | 136 | 17:00 | 127 | 21:00
| Comilla(n) | 137 | 13:00 | 132 | 8:00 | Rangpur | 132 | 17:00 | 115 | 19:30
| Chandpur | 138 | 19:30 | 125 | 21:00 | Lalmonirhat | 131 | 17:00 | 114 | 19:00
| Feni | 135 | 20:00 | 125 | 23:00 | Saidpur | 131 | 18:00 | 118 | 19:30
| Chowmuhani | 130 | 12:00 | 122 | 19:00 | Purbasadipur | 128 | 17:00 | 112 | 19:00
| Ashuganj | 137 | 17:00 | 132 | 22:00 | Thakurgaon | 126 | 17:00 | 112 | 19:30
| Daudkandi | 132 | 19:00 | 127 | 7:00 | Palashbari | 130 | 18:00 | 118 | 20:00
| B.Baria | 133 | 7:00 | 127 | 21:00 | Barapukuria | 137 | 17:00 | 127 | 21:00
| Ramganj | 126 | 18:30 | 116 | 23:00 | Panchagar | 127 | 17:00 | 109 | 19:30
| Chaddagram | 135 | 12:00 | 128 | 7:00 | Joldhaka | 131 | 6:00 | 114 | 20:00
| PHP | 132 | 12:00 | 125 | 23:00 | Kurigram | 129 | 17:00 | 110 | 19:30
| Madanhat | 137 | 19:30 | 131 | 4:00

## L-Curve
Date | 2020-09-08
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 187 | 7678 | 4004 | 11682 |  |  |  | QF-LDC-11
0:30 | 209 | 7441 | 3842.5 | 11283.5 | Date: | 2020-09-08
1:00 | 231 | 7204 | 3681 | 10885
1:30 | 229.5 | 7069.5 | 3614 | 10683.5
2:00 | 228 | 6935 | 3547 | 10482
2:30 | 214.5 | 6860 | 3511 | 10371 | [5 empty] | Gen. at Eve. Peak | 12016 | 12016 MW (19:30 )
3:00 | 201 | 6785 | 3475 | 10260 | [6 empty] | 19:30
3:30 | 240.5 | 6722.5 | 3419 | 10141.5 | [5 empty] | Gen. at Day Peak | 10390.4 | 10390.4 MW (12:00 )
4:00 | 280 | 6660 | 3363 | 10023 | [6 empty] | 12:00
4:30 | 295 | 6554 | 3352.5 | 9906.5 | [5 empty] | Highest Generation | 12016
5:00 | 310 | 6448 | 3342 | 9790 | [6 empty] | 19:30
5:30 | 342 | 6275.5 | 3284.5 | 9560
6:00 | 374 | 6103 | 3227 | 9330
6:30 | 372 | 5994 | 3163.5 | 9157.5
7:00 | 370 | 5885 | 3100 | 8985
7:30 | 370.5 | 5929.15 | 3076.5 | 9005.65
8:00 | 371 | 5973.3 | 3053 | 9026.3
8:30 | 265.5 | 6229.95 | 2973 | 9202.95
9:00 | 160 | 6486.6 | 2893 | 9379.6
9:30 | 118 | 6757.9 | 2874 | 9631.9
10:00 | 76 | 7029.2 | 2855 | 9884.2
10:30 | 109 | 7083.65 | 2904.5 | 9988.15
11:00 | 142 | 7138.1 | 2954 | 10092.1
11:30 | 131 | 7245.25 | 2996 | 10241.25
12:00 | 120 | 7352.4 | 3038 | 10390.4
12:30 | 97 | 7385.7 | 3070 | 10455.7
13:00 | 74 | 7419 | 3102 | 10521
13:30 | 38 | 7172.5 | 3055.5 | 10228
14:00 | 2 | 6926 | 3009 | 9935
14:30 | 38.5 | 6902.5 | 3000.5 | 9903
15:00 | 75 | 6879 | 2992 | 9871
15:30 | 49 | 6825.5 | 3007.5 | 9833
16:00 | 23 | 6772 | 3023 | 9795
16:30 | 66.5 | 6662 | 2983.5 | 9645.5
17:00 | 110 | 6552 | 2944 | 9496
17:30 | 131 | 6545 | 2970 | 9515
18:00 | 152 | 6538 | 2996 | 9534
18:30 | 77 | 7203.5 | 3505.5 | 10709
19:00 | 2 | 7869 | 4015 | 11884
19:30 | 14 | 7889 | 4127 | 12016
20:00 | 96 | 7747 | 4192 | 11939 |  |  |  | Executive Engineer
20:30 | 124.5 | 7741.5 | 4205 | 11946.5 |  |  |  | Network Operation Division
21:00 | 153 | 7736 | 4218 | 11954
21:30 | 144 | 7753 | 4159.5 | 11912.5
22:00 | 135 | 7770 | 4101 | 11871 |  |  |  |  | Page 6 of 7
22:30 | 213 | 7706 | 4079 | 11785
23:00 | 291 | 7642 | 4057 | 11699
23:30 | 239 | 7660 | 4030.5 | 11690.5
24:00 | 187 | 7678 | 4004 | 11682
12016 MW (19:30 )
10390.4 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-09-08 |  | Energy | 250147234
[10 empty] | 2020-09-08 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4273 | 930 | 1985 | 2956 | 720 | 78 | 494 | 0 | 176
0:30 | 4234.5 | 932 | 2059 | 2694 | 715 | 79 | 365 | 0 | 170 | Date: | 2020-09-08
1:00 | 4196 | 934 | 2133 | 2432 | 710 | 80 | 236 | 0 | 164
1:30 | 4192 | 934 | 2130.5 | 2271 | 710 | 80 | 203 | 0 | 163 | [7 empty] | Total Energy | 250.1472 | Total Energy Gen 250.147 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 250.147 MKWHr
2:00 | 4188 | 934 | 2128 | 2110 | 710 | 80 | 170 | 0 | 162 | [7 empty] | Energy not Served | 0
2:30 | 4181.5 | 934.5 | 2125.5 | 2023.5 | 710 | 79.5 | 156.5 | 0 | 160 | [7 empty] | Energy Requirement | 250.1472
3:00 | 4175 | 935 | 2123 | 1937 | 710 | 79 | 143 | 0 | 158
3:30 | 4185.5 | 935 | 2133 | 1809 | 710 | 78.5 | 131.5 | 0 | 159 | [6 empty] | Shortage
4:00 | 4196 | 935 | 2143 | 1681 | 710 | 78 | 120 | 0 | 160
4:30 | 4201 | 934.5 | 2151 | 1556.5 | 710 | 77.5 | 120 | 0 | 156
5:00 | 4206 | 934 | 2159 | 1432 | 710 | 77 | 120 | 0 | 152
5:30 | 4184.5 | 934 | 2055 | 1336.5 | 705 | 76 | 120 | 0 | 149
6:00 | 4163 | 934 | 1951 | 1241 | 700 | 75 | 120 | 0 | 146
6:30 | 4146 | 934 | 1896.5 | 1154 | 690 | 75.5 | 120 | 0 | 141 |  |  |  |  | Coal
7:00 | 4129 | 934 | 1842 | 1067 | 680 | 76 | 120 | 0 | 136
7:30 | 4175 | 934 | 1830.5 | 1075 | 655 | 76 | 120 | 0 | 133 |  |  |  | Oil |  |  |  | ,
8:00 | 4221 | 934 | 1819 | 1083 | 630 | 76 | 120 | 0 | 130
8:30 | 4150 | 932 | 1882.5 | 1286 | 605 | 76.5 | 120 | 0 | 133
9:00 | 4079 | 930 | 1946 | 1489 | 580 | 77 | 120 | 0 | 136
9:30 | 4145.5 | 930 | 1947.5 | 1736.5 | 520 | 77 | 120 | 0 | 135
10:00 | 4212 | 930 | 1949 | 1984 | 460 | 77 | 120 | 0 | 134
10:30 | 4223 | 930.5 | 1955 | 2005 | 515 | 78 | 120 | 0 | 140
11:00 | 4234 | 931 | 1961 | 2026 | 570 | 79 | 120 | 0 | 146
11:30 | 4168 | 931 | 1914.5 | 2288 | 530 | 79 | 155 | 0 | 148
12:00 | 4102 | 931 | 1868 | 2550 | 490 | 79 | 190 | 0 | 150
12:30 | 4081 | 930.5 | 1830 | 2623.5 | 475 | 79 | 255 | 0 | 152
13:00 | 4060 | 930 | 1792 | 2697 | 460 | 79 | 320 | 0 | 154
13:30 | 4060 | 930 | 1792 | 2697 | 460 | 79 | 320 | 0 | 154
14:00 | 4060 | 930 | 1792 | 2697 | 460 | 79 | 320 | 0 | 154
14:30 | 4000.5 | 929.5 | 1721 | 2498 | 460 | 79.5 | 327.5 | 0 | 158
15:00 | 3941 | 929 | 1650 | 2299 | 460 | 80 | 335 | 0 | 162
15:30 | 3980 | 930 | 1675 | 2223 | 460 | 79 | 309 | 0 | 164
16:00 | 4019 | 931 | 1700 | 2147 | 460 | 78 | 283 | 0 | 166
16:30 | 3999.5 | 930.5 | 1598.5 | 2130.5 | 460 | 77.5 | 283 | 0 | 159
17:00 | 3980 | 930 | 1497 | 2114 | 460 | 77 | 283 | 0 | 152
17:30 | 3988.5 | 930.5 | 1439.5 | 2144.5 | 459.5 | 76.5 | 320.5 | 0 | 154
18:00 | 3997 | 931 | 1382 | 2175 | 459 | 76 | 358 | 0 | 156
18:30 | 4108 | 930.5 | 1658.5 | 2728.5 | 529 | 75.5 | 513 | 0 | 166
19:00 | 4219 | 930 | 1935 | 3282 | 599 | 75 | 668 | 0 | 176
19:30 | 4215 | 930 | 1833 | 3416 | 660 | 75 | 705 | 0 | 182
20:00 | 4196 | 930 | 1800 | 3316 | 690 | 76 | 751 | 0 | 180
20:30 | 4265 | 930.5 | 1835 | 3227 | 705 | 76 | 728 | 0 | 180
21:00 | 4334 | 931 | 1870 | 3138 | 720 | 76 | 705 | 0 | 180
21:30 | 4370.5 | 930.5 | 1933 | 3060 | 720 | 76.5 | 642 | 0 | 180
22:00 | 4407 | 930 | 1996 | 2982 | 720 | 77 | 579 | 0 | 180
22:30 | 4378.5 | 930.5 | 1992 | 2969 | 720 | 77 | 537 | 0 | 181
23:00 | 4350 | 931 | 1988 | 2956 | 720 | 77 | 495 | 0 | 182
23:30 | 4311.5 | 930.5 | 1986.5 | 2956 | 720 | 77.5 | 494.5 | 0 | 179 | Max Temp. in Dhaka |  | 34.5° C
24:00 | 4273 | 930 | 1985 | 2956 | 720 | 78 | 494 | 0 | 176
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 250.147 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 250.147 MKWHr
Note on W13: Author:

## Generation
g | 2020-09-08
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 45 | 45 | 44 | 43 | 42 | 40 | 41 | 41 | 42 | 42 | 44 | 44 | 44 | 44 | 45 | 43 | 42 | 41 |  | 40 | 40 | 41 | 41 | 42 | 42 | 43 | 1036015
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 852000
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2900000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [11 empty] | 12 | 25 | 25 | 25 |  |  |  |  | 22 | 25 | 25 | 25 |  |  | 0 | 189412
| Teknaf 20MW PP (Solartech) | [7 empty] | 10.3 | 16.6 | 13.2 | 20.1 | 19.4 | 20 | 19 | 9 | 9 | 2 | [9 empty] | 132165
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 204 | 204 | 203 | 204 | 204 | 204 | 205 | 203 | 204 | 230 | 205 | 204 | 204 | 204 | 204 | 204 | 215 |  | 204 | 203 | 203 | 213 | 204 | 205 | 204 | 4871931
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 139 | 140 | 139 | 140 | 139 | 139 | 140 | 140 | 150 | 148 | 147 | 147 | 151 | 151 | 147 | 147 | 100 | 80 |  | 148 | 100 | 100 | 100 | 100 | 100 | 100 | 3110089
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 84 | 50 | 23 | 0 | [8 empty] | 67 | 65 | 65 | 65 | 65 | 87 |  | 100 | 100 | 98 | 101 | 100 | 99 | 99 | 1182438
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [19 empty] | 50 | [6 empty] | 29376
14 | Titas 50 MW Peaking PP | [17 empty] | 5 |  | 42 | 42 | 42 | 8 |  |  | 0 | 122048
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 303 | 298 | 287 | 300 | 307 | 281 | 300 | 309 | 251 | 308 | 305 | 278 | 263 | 260 | 287 | 300 | 270 | 309 |  | 258 | 265 | 288 | 308 | 300 | 281 | 288 | 7044485
18 | Kodda 300 MW PP Unit-2 (Summit) | 238 | 218 | 218 | 170 | 65 | 25 | 15 | 15 | 86 | 244 | 255 | 268 | 268 | 282 | 285 | 285 | 285 | 284 |  | 284 | 284 | 282 | 285 | 283 | 283 | 286 | 5233962
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 0 | [14 empty] | 4 | 8 | 8 | 8 | 8 | 8 | 100363
20 | Ghorasal TPP (Unit-1&2) | [21 empty] | 5 | 20 | 35 | 35 | 35 | 90000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 140 | 140 | 140 | 142 | 140 | 140 | 140 | 140 | 130 | 140 | 142 | 140 | 134 | 140 | 140 | 140 | 140 | 100 |  | 140 | 140 | 140 | 140 | 141 | 140 | 140 | 3310000
23 | Ghorasal TPP Unit-5 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2772000
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 120 | 135 | 100 | 100 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2053690
32 | Ashuganj 50 MW PP | 35 | 32 | 32 | 29 | 29 | 29 | 29 | 29 | 35 | 5 | 5 | 29 | 33 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 696744
33 | Ashuganj 225 MW CCPP | 186 | 186 | 193 | 198 | 195 | 201 | 181 | 193 | 201 | 212 | 211 | 213 | 213 | 213 | 213 | 213 | 213 | 210 |  | 215 | 215 | 214 | 212 | 214 | 215 | 187 | 4950000
34 | Ashuganj 450 MW CCPP(South) | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 270 | 265 | 270 | 265 | 265 | 265 | 265 | 265 | 265 | 265 | 290 |  | 265 | 265 | 265 | 285 | 355 | 285 | 285 | 6590000
| Ashuganj 450 MW CCPP(North) | 265 | 265 | 265 | 265 | 265 | 265 | 265 | 285 | 265 | 270 | 265 | 265 | 265 | 265 | 265 | 265 | 265 | 280 |  | 280 | 295 | 310 | 360 | 360 | 360 | 360 | 7147400
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 137280
36 | Chandpur 150 MW CCPP | 93 | 88 | 96 | 91 | 96 | 85 | 96 | 96 | 85 | 96 | 96 | 85 | 85 | 86 | 86 | 95 | 86 | 96 |  | 85 | 85 | 90 | 96 | 91 | 93 | 86 | 2149490
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 341 | 341 | 339 | 340 | 344 | 345 | 340 | 350 | 356 | 342 | 345 | 342 | 340 | 343 | 340 | 339 | 339 | 300 |  | 344 | 340 | 338 | 341 | 347 | 339 | 340 | 8315910
40 | Meghnaghat 450 MW CCPP(MPL) | 400 | 400 | 400 | 400 | 400 | 360 | 360 | 360 | 420 | 420 | 420 | 390 | 360 | 330 | 300 | 300 | 300 | 290 |  | 390 | 320 | 300 | 300 | 340 | 340 | 340 | 8738000
41 | Haripur 360MW CCPP(HPL) | 354 | 353 | 354 | 355 | 352 | 309 | 279 | 279 | 351 | 347 | 347 | 300 | 270 | 270 | 250 | 250 | 250 | 250 |  | 330 | 300 | 250 | 273 | 335 | 333 | 328 | 7398000
42 | RPCL 210MW CCPP | 160 | 161 | 161 | 161 | 159 | 160 | 159 | 159 | 161 | 158 | 158 | 159 | 124 | 108 | 83 | 85 | 104 | 104 |  | 124 | 159 | 143 | 144 | 144 | 144 | 145 | 3241640
43
44 | Fenchugonj CCPP Phase-1 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 91 | 91 | 91 | 91 | 91 | 91 | 89 | 89 | 89 | 91 |  | 91 | 91 | 91 | 89 | 90 | 90 | 90 | 2136000
45 | Fenchugonj CCPP Phase-2 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 30 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 30 |  | 30 | 28 | 28 | 30 | 30 | 28 | 28 | 672360
46 | Shajibazar 330 MW CCPP | 284 | 284 | 282 | 286 | 284 | 286 | 285 | 298 | 295 | 299 | 297 | 297 | 297 | 297 | 296 | 296 | 294 | 297 |  | 296 | 295 | 298 | 298 | 297 | 297 | 296 | 6654000
47 | Shahjibazar GTPP Unit- 8 & 9 | 32 | 32 | 32 | 31 | 32 | 32 | 32 | 32 | 32 | 31 | 31 | 20 | 20 | 31 | 31 | 31 | 31 | 31 |  | 52 | 52 | 52 | 63 | 62 | 64 | 64 | 513024
48 | Shahjibazar 86MW PP (Shahjibazar) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 83 | 83 | 83 | 83 | 82 | 83 | 83 | 83 | 40 | 10 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1929600
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 163 | 163 | 163 | 163 | 164 | 164 | 164 | 164 | 164 | 170 | 177 | 177 | 177 | 177 | 178 | 204 | 225 | 225 |  | 190 | 190 | 185 | 185 | 184 | 184 | 184 | 4301850
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 429000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 227520
54 | Hobiganj 11MW PP Cofidence-E | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 210000
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 50 | 47 | 49 | 47 | 44 | 52 | 14 | 14 |  | 52 | 52 | 51 | 52 | 53 | 53 | 53 | 1171800
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 |  | 8 | 8 |  | 8 | 16 | 24 | 24 | 16 | 23 |  | 23 | 23 | 16 | 16 | 23 | 23 | 23 | 415320
57 | Bibiana-II 341 MW CCPP (Summit) | 295 | 280 | 285 | 290 | 305 | 285 | 290 | 305 | 300 | 280 | 295 | 290 | 270 | 275 | 275 | 290 | 280 | 240 |  | 280 | 270 | 270 | 290 | 290 | 290 | 290 | 7077700
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | [8 empty] | 45 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 865396
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 11 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 428112
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  |  | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 442692
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 17 | 17 | 20 | 17 | 20 | 20 | 20 | 22 |  | 22 | 20 | 20 | 20 | 20 | 22 | 22 | 452808
63 | Impoprt (Tripura) | 164 | 162 | 158 | 160 | 152 | 146 | 136 | 130 | 136 | 134 | 146 | 150 | 154 | 158 | 162 | 166 | 152 | 156 |  | 176 | 182 | 180 | 180 | 180 | 182 | 176 | 3829440
64 | Malancha, Ctg. EPZ (United) | 32 | 41 | 41 | 41 | 41 | 41 | 38 | 6 | 4 | 6 | 4 | 4 | 4 | 5 | 5 | 5 | 9 | 10 |  | 27 | 30 | 34 | 36 | 39 | 35 | 39 | 545280
65 | Feni 22MW PP (Doreen) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  |  |  |  | 17 | 17 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 326916
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 224100
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 817600
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 18 | 14 | 16 | 16 | 16 | 16 | 16 | 17 | 17 | 17 | 17 | 17 | 14 |  | 14 | 14 | 20 | 21 | 21 | 21 | 21 | 459940
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 28 | 28 | 28 | 28 | 24 | 29 | 29 | 29 |  | 22 | 30 | 30 | 30 | 23 | 30 | 30 | 662040
71 | Maona 33 MW PP(Summit) | 28 | 28 | 24 | 24 | 24 | 24 | 24 | 28 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 779100
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 795400
73 | Ghorashal 108MW PP (Regent) | 82 | 82 | 82 | 82 | 82 | 82 | 81 | 81 | 81 | 81 | 81 | 81 | 82 | 82 | 82 | 82 | 82 | 43 |  | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 1897500
| Feni Lanka Power | [11 empty] | 114 | 114 | 34 | 23 |  |  |  |  | 114 | 114 | 114 | 88 | 34 | 44 | 52 | 744420
| Chowmuhani 113 MW | 113 | 113 | 113 | 113 | 113 | 109 | 55 | 55 | 57 | 101 | 100 | 76 | 35 | 52 | 82 | 99 | 102 | 102 |  | 104 | 113 | 106 | 113 | 113 | 112 | 113 | 2276400
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 100 | 100 | 100 | 50 | 18 | 7 | 7 | 8 | 40 | 35 | 35 | 55 | 80 | 91 | 91 | 91 | 95 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1752000
78 | Gazipur 52 MW PP | [8 empty] | 5 | 8 | 8 | 36 | 51 | 8 | 8 |  |  |  |  | 47 | 52 | 52 | 52 | 16 |  | 0 | 328128
79 | Kodda 150MW PP | [11 empty] | 70 | 133 | 149 | 150 | 98 | 98 | 105 |  | 150 | 150 | 150 | 150 | 150 | 82 | 82 | 1603200
80 | Jamalpur 95 MW PP(Powerpac) | 71 | 32 | 8 | 0 |  |  |  |  | 7 | 8 | 8 | 40 | 48 |  |  |  |  | 19 |  | 64 | 64 | 64 | 64 | 64 | 64 | 72 | 632640
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 0 | [7 empty] | 5 | 8 | 24 | 43 | 43 | 43 | 43 | 43 | 24 |  | 38 | 43 | 43 | 43 | 43 | 43 | 43 | 594989
| Gazipur 100 MW PP | [8 empty] | 40 | 87 | 87 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 103 | 103 | 103 | 103 | 1538028
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 4 | 2 | 3 | 6 | 3 | 5 | 3 | 1 | 0 | [9 empty] | 29160
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | [19 empty] | 12 | 17 | 17 | 17 | 17 | 17 | 17 | 103708
82 | Madanganj 102 PP(Summit) | 64 | 64 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 76 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 96 | 96 | 96 | 96 | 96 | 1731480
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [8 empty] | 3 | 11 | 10 | 11 | 11 | 11 | 12 | 22 | 28 | 22 |  | 33 | 100 | 100 | 32 | 24 | 25 | 25 | 402374
86 | Meghnaghat CCPP(Summit) | 140 | 135 | 135 | 140 | 145 | 130 | 135 | 145 | 130 | 150 | 140 | 130 | 130 | 125 | 140 | 140 | 130 | 150 |  | 120 | 120 | 146 | 140 | 132 | 130 | 130 | 3309324
87 | Meghnaghat 100 MW(IEL) | 100 | 100 | 100 | 100 | 60 | 50 | 50 | 50 | 56 | 94 | 100 | 100 | 100 | 100 | 96 | 38 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 1391040
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 104 | 70 | 54 | 54 | 54 | 72 | 104 | 104 | 90 | 90 | 36 | 35 | 35 | 18 | 18 |  | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 1416000
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [9 empty] | 0 | 10 | 100 | 40 | 30 | 36 |  |  |  |  | 30 | 30 | 30 | 30 | 30 |  | 0 | 358080
92 | Fenchuganj 44MW (Energyprima) | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 50 | 50 | 50 | 49 | 10 | 10 |  | 39 | 49 | 49 | 49 | 49 | 49 | 49 | 1144656
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 40 | [15 empty] | 0 | 16 | 34 | 43 | 43 | 404936
94 | Gagnagar 102 MW PP (Digital Power) | 93 | 93 | 93 | 93 | 93 | 50 | 50 | 50 | 64 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 |  | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 2084832
95 | Patenga 50MW PP (Baraka) | 18 | [7 empty] | 6 | 24 | 24 | 34 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 718560
96 | Chattogram 108 MW PP (ECPV) | 12 | [8 empty] | 3 | 10 | 11 | 11 | 11 | 11 | 8 | 11 | 11 |  | 11 | 11 | 11 | 12 | 12 | 12 | 12 | 194880
97 | Katpotti 52 MW PP (Sinha) | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | 45 | 55 | 55 | 15 | 15 | 15 | 15 | 15 | 15 | 40 | 40 | 40 | 43 | 54 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1072980
100 | Manikganj 55 MW PP (Northern) | 17 | [7 empty] | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 869735
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 130 | 100 | 100 | 163 | 130 | 130 | 130 | 130 | 110 | 110 | 110 | 110 | 110 |  | 130 | 110 | 110 | 110 | 110 | 110 | 110 | 3185918
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 1 | 1 | 2 | 2 | 2 |  |  | 0 | [9 empty] | 4750
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | [7 empty] | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 864360
104 | Keranigonj 300 MW PP (APR) | [19 empty] | 58 | 58 |  |  |  |  | 0 | 72453
105 | Bramhangoan 100 MW PP (Aggreko) | [19 empty] | 50 | 50 |  |  |  |  | 0 | 48677
106 | Mymensingh 200 MW PP (United) | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 195 | 195 | 195 | 195 |  |  |  |  | 35 |  | 100 | 100 | 108 | 150 | 155 | 155 | 155 | 3480000
112 | Aurahati 100MW PP (Aggreko) | [19 empty] | 95 | 103 |  |  |  |  | 0 | 111481
114 | Kodda 149 MW PP Unit-1 (Summit) | 132 | 122 | 100 | 100 | 100 | 100 | 102 | 108 | 128 | 128 | 132 | 131 | 129 | 131 | 125 | 120 | 125 | 136 |  | 139 | 139 | 145 | 149 | 149 | 149 | 149 | 3051360
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 60 | 60 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2358720
116 | Chandpur 200MW (Desh energy) | [11 empty] | 50 | 100 | 17 | [5 empty] | 25 | 90 | 150 |  |  |  | 0 | 507360
117 | Ashuganj 150MW PP (Midland) | 40 | [22 empty] | 6 | 65 | 115 | 247563
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 8 | [7 empty] | 4 | 7 | 7 | 7 | 7 |  |  |  | 4 | 34 |  | 45 | 45 | 47 | 65 | 35 | 35 | 35 | 380400
| Anwara 300 MW PP (United) | 216 | 216 | 159 | 125 | 125 | 125 | 125 | 125 | 175 | 179 | 179 | 179 | 179 | 179 | 179 | 160 | 160 | 124 |  | 214 | 214 | 215 | 215 | 215 | 215 | 215 | 4212764
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2425920
120 | Eastern Zone Total | 7204 | 6935 | 6785 | 6660 | 6448 | 6103 | 5885 | 5973.3 | 6486.6 | 7029.2 | 7138.1 | 7352.4 | 7419 | 6926 | 6879 | 6772 | 6552 | 6538 |  | 7869 | 7889 | 7747 | 7736 | 7770 | 7642 | 7678 | 168912212
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 115 | 99 | 66 | 66 | 66 | 66 | 16 | 16 | 16 | 16 | 16 | 66 | 83 | 83 | 83 | 94 | 90 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 1822080
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
| Khulna 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 155 | 200 | 200 | 155 | 140 | 140 | 3167040
129 | Rupsha 105 MW PP (Orion rupsha) | 53 | [10 empty] | 35 | 35 | 35 | 17 |  |  |  |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 571680
130
131
132
133
| Barisal 110 MW PP (Summit ) | 64 | 64 | 48 | 32 | 32 | 16 | [6 empty] | 16 | 16 | 16 | 16 | 16 | 16 |  | 96 | 96 | 96 | 96 | 110 | 110 | 110 | 968832
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 76 | 77 | 76 | 77 | 76 | 77 | 72 | 75 | 77 | 77 | 77 | 78 | 79 | 79 | 78 | 78 | 78 | 78 |  | 79 | 77 | 77 | 77 | 77 | 78 | 78 | 1855
| Bhola 225 MW CCPP | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 62 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1549000
140 | Bhola 33 MW PP (Venture) | 38 | 38 | 38 | 39 | 38 | 32 | 32 | 26 | 25 | 26 | 26 | 27 | 27 | 27 | 27 | 25 | 25 | 25 |  | 39 | 40 | 41 | 40 | 41 | 39 | 39 | 767900
141 | Noapara 100 MW PP (Bangla Trac) | [19 empty] | 58 | 100 | 100 | 100 | 100 | 60 | 60 | 528000
142 | Noapara 40 MW PP (Khanjahan Ali) | 33 | [10 empty] | 32 | 32 | 32 | 32 | 40 | 40 | 16 |  | 40 | 40 | 40 | 40 | 40 | 33 | 33 | 481875
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 4 | [8 empty] | 2480
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 934 | 934 | 935 | 935 | 934 | 934 | 934 | 934 | 930 | 930 | 931 | 931 | 930 | 930 | 929 | 931 | 930 | 931 |  | 930 | 930 | 930 | 931 | 930 | 931 | 930 | 22352727
147 | Bheramara 410 MW CCPP | 345 | 345 | 340 | 345 | 340 | 340 | 345 | 360 | 345 | 360 | 355 | 345 | 345 | 290 | 270 | 275 | 270 | 275 |  | 410 | 410 | 370 | 370 | 370 | 370 | 370 | 8223840
148 | Payra 1320 MW | 560 | 560 | 560 | 560 | 560 | 550 | 530 | 480 | 430 | 310 | 420 | 340 | 310 | 310 | 310 | 310 | 310 | 310 |  | 450 | 510 | 540 | 570 | 570 | 570 | 570 | 11747700
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 |  | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 3688300
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 65 | 65 | 65 | 65 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1666000
| Baghabari 50 MW Peaking PP | [19 empty] | 50 | 50 | 50 | 50 |  |  | 0 | 183180
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | [24 empty] | 40 | 130 | 182600
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 182 | 181 | 178 | 181 | 187 | 184 | 168 | 161 | 152 | 161 | 158 | 154 | 151 | 140 | 130 | 130 | 130 | 130 |  | 135 | 145 | 145 | 148 | 151 | 139 |  | 3861136
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 200 | 200 | 200 | 200 | 200 | 190 | 170 | 170 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 |  | 159 | 135 | 130 | 130 | 130 | 130 | 130 | 4230182
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 410 | 411 | 401 | 413 | 419 | 363 | 358 | 355 | 305 | 355 | 355 | 355 | 345 | 280 | 305 | 335 | 257 | 258 |  | 358 | 370 | 399 | 408 | 410 | 406 | 400 | 8842455
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 5 |  | 35 | 35 | 35 | 25 |  |  |  | 93027
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 17 | 21 | 494400
163 | Bogura 20 MW PP (Energyprima) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 6 | 8 |  | 8 | 8 | 8 | 8 | 7 | 5 | 5 | 163656
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 205074
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [17 empty] | 10 |  | 43 | 43 | 47 | 43 | 43 | 43 | 43 | 242344
168 | Santahar 50 MW Peaking PP | [17 empty] | 5 |  | 30 | 32 | 33 | 32 | 32 | 32 | 31 | 174349
169 | Natore 52 MW PP (Rajlanka) | [11 empty] | 8 | 8 | 8 | 8 |  |  |  |  | 43 | 43 | 43 | 43 | 25 | 25 | 25 | 240000
170 | Chapainawabganj 100 MW Peaking PP | 32 | 0 | [15 empty] | 17 |  | 98 | 98 | 96 | 96 | 99 | 99 | 99 | 601544
171 | Baghabari 200 MW PP (Paramount) | [19 empty] | 50 | [5 empty] | 0 | 38368
| Bagura 113 MW PP (Confidence)-2 | [11 empty] | 14 | 35 | 35 | 35 | 35 | 35 | 35 |  | 88 | 113 | 113 | 113 | 113 | 113 | 113 | 901056
172 | Confidence Power Bogura Unit-1 113 MW | 90 | 90 | 90 | 50 | 50 | 35 | 35 | 35 | 35 | 35 | 35 | 70 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1780320
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 106 | 105 | 100 | 25 | 0 | [7 empty] | 32 | 75 | 80 | 84 | 92 | 95 |  | 105 | 105 | 107 | 106 | 106 | 106 | 106 | 1441920
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 1 | 2 | 1 | 3 | 4 | 2 | 3 | 1 | 1 | 0 | [8 empty] | 20102
178
178