## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-09-10 | Thursday
|  |  | Date (day): | 2020-09-10 |  | Thursday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13498.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14870 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-09-09 | 2020-09-10 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 157 | 0 | 0 | 0 |  | 180 | Under maint
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 110 | 0 | 0 | 0 |  | 190 | Under maint
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 40 | 120 | 300
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 72 | 72 | 72
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 82 | 91 | 94 | 94
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 347 | 340 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 277 | 267 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 420 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 7 | 7 | 7 | 93 |  | Fuel shortage
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 125 | 125 | 150 | 150 | 155 |  | GT-1 S/D for gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 96 | 96 | 96 | 96
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 46 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 91 | 100 | 7 | 7 | 93 |  | Fuel shortage
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 305 | 293 | 50 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 93 | 93 | 50 | 50 | 52 |  | Fuel shortage
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 150 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 49 | 55 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 51 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 222 | 286 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 53 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 25 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 42 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 127 | 131 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 50 | 103 | 100 | 100
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 17 | 17 | 17 | 97 |  | Fuel shortage
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 2856 | 3210 | 3347 | 4062 | 964 | 785
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 13 | 25 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 8 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 12 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 77 | 80 | 44 | 44 | 186 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 209 | 204 | 180 | 180 |  |  | Gas Shortage
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 140 | 140 | 10 | 10 |  |  | Engine problem
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 100 | 100
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 30 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 100 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 21 | 20 | 20
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 36 | 10 | 30
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 10 | 84 | 97 | 97 |  | 11 | Engine problem
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 197 | 198 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 17 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 1004 | 1307 | 1545 | 1540 | 426 | 109
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 80 | 80 | 80 | 54 |  | Gas shortage
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 211 | 190 | 50 | 214
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 265 | 270 | 360 | 360
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 250 | 360 | 360
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 35 | 35 | 35 | 36 |  | 9 | Engine problem
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 42 | 20 | 20 | 35 |  | Gas shortage
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 28 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 78 | 133 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 50 | 0 | 42
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 86 | 100 | 100 |  | 63 | ST under shut down
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 200 | 200 | 200
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 21 | 21
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 146 | 148 | 157 | 173
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 25 | 43 | 43 | 43 |  | 9 | Engine problem
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 9 | 21 | 20 | 20 |  | 5 | Engine problem
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 114 | 114 | 114
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 110 | 113 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1434 | 1873 | 1926 | 2349 | 540 | 86
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 154 | 159 | 160 | 160 | 42 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 22 | 22 | 22
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 56 | 63 | 72 | 72 |  | 23 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 165 | 200 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 53 | 115 | 115 | 115
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 450 | 559 | 570.6 | 569 | 42 | 23
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 91 | 91 | 90 | 90
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 28 | 28 | 30 | 30 |  | 60 | Unit-4 under shut down
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 300 | 308 | 300 | 300
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 49 | 49 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 63 | 64 | 64 | 64 |  | 35 | GT-8 under maint.
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 85 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 186 | 184 | 190 | 190 |  | 41 | Machine problem
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 25 | 25
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 290 | 341 | 341
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1375 | 1378 | 1423 | 1423 | 0 | 536
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 931 | 931 | 946 | 946
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 99 | 99 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 12 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 200 | 225 | 225
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 355 | 345 | 410 | 410
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 16 | 40 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 80 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 70 | 105 | 105
| 108 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1521 | 1797 | 2021 | 2147 | 0 | 0
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 64 | 80 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 23 | 41 | 33 | 33
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 15 | 87 | 65 | 65 |  | 129 | GT-2 & ST Under maint.
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 77 | 78 | 80 | 80 |  | 15 | Engine problem
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 430 | 580 | 620 | 620
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 609 | 866 | 908 | 908 | 0 | 144
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 35 | 0 | 0 | 0 | 100 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 34 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 43 | 43 | 43
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 141 | 145 | 220 | 220 |  |  | FGMO
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 170 | 180 | 220 | 220 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 398 | 414 | 414 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 32
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 21 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 5 | 8 | 11 | 11
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 34 | 43 | 43 |  | 9 | Engine problem
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 96 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 90 | 90 | 90 | 90 |  | 23 | Engine problem
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 887 | 1255 | 1487 | 1609 | 491 | 32
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 151 | 150 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 10 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 79 | 98 | 113 | 113
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 234 | 248 | 271 | 263 | 294 | 30
|  | Total |  |  |  |  | 20383 | 19892 | 10370 | 12493 | 13498.6 | 14870 | 2757 | 1745
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10003.9414 | 12052 | 13022.1026 | 14345.0925
| A. |  | 2020-09-09 | (Yesterday) |  |  |  |  | Wednesday
| 1 | Highest Generation : |  |  | 12493 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 9122 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12493 | MW
| 3 | Day peak Generation : |  |  | 10370 | MW at | 11:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12052 | MW
| 4 | Evening peak Generation : |  |  | 12493 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 258.0441 | MKWHr | By Solar | 0.1797 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 141.0559 | MKWHr |  | By Oil: | 72.1332 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 16.6904 | MKWHr |  | By Hydro: | 1.8814 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2757 | MW | Dhaka | 4074 | 4074 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 1745 | MW | Chittagong | 1257 | 1257 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4502 | MW | Khulna | 1557 | 1557 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1134.43 | MMCFD |  |  | Rajshahi | 1329 | 1329 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 163674225.234 | ii) Oil : | Taka | 608438399.76 | Comilla | 1179 | 1179 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 77073101 | Total | Taka | 849185725.994 | Mymensingh | 992 | 992 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.117 | MKWHr. | Sylhet | 549 | 549 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -42 | MW (E to W) at | 21:00 | hrs | Barisal | 372 | 372 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -60 | MW at | 20:00 | hrs | Rangpur | 743 | 743 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.1° C |  |  | Total | 12052 | 12052 |  | 0
| B. |  | 2020-09-10 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 33.0° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12700 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14870 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10600 | MW
| 4 | Reserve(Generation end) |  |  |  | 2170 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 262.3197 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9121 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.3615 | MKWHr. | ii) HVDC Flow at Peak Time |  | 931 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.7421 | MKWHr. | iii) Maximum HVDC Flow : |  | 935 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 93.11 |  | (b) Today: | 93.06 |  | (c) Rule Curve: |  | 101.07
.

## YesterdayGen
2020-09-09
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 141 | 110 | 0 | 82 | 0 | 339 | 333 |  | 0 | 340 | 123 | 7 | 96 | 55 | 300 | 0 | 0 | 0 | 91 | 93 | 16 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 44 | 35 | 120 | 0 | 0 | 204 | 0 | 100 | 0 |  | 0 | 0 | 66 | 0 | 12 | 19 | 20 | 36 | 0 | 0 | 80 | 360 | 280 | 173 | 8 | 86 | 35 | 5 | 0 | 43 | 0 | 0 | 43 | 18 | 11 | 33 | 21 | 172 | 158 | 72 | 22 | 0 | 90 | 28 | 53 | 49 | 110 | 300 | 64 | 85 | 0 | 185 | 18 | 0 | 10 | 265 | 23 | 8 | 0 | 283 | 0 | 0 | 155 | 0 | 149 | 0 | 100 | 0 | 125 | 0 | 35 | 34 | 0 | 0 | 215 | 0 | 0 | 17 | 113 | 100 | 0 | 17 |  | 934 | 0 | 370 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 33 | 65 | 37 | 64 | 0 | 70 | 0 | 0 | 0 | 96 | 0 | 0 | 36 | 0 | 31 | 21 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 77 | 20 | 130 | 0 | 412 | 35 | 0 | 113 | 0 | 106 | 0 | 0 | 90 | 560 |  | 7400 | 3841 | 11241 | 4291 | 934 | 1971 | 2719 | 710 | 79 | 365 | 172 | 0 | 0 | 93.12
2:00 | 35 | 0 | 140 | 110 | 0 | 82 | 0 | 348 | 333 |  | 0 | 380 | 142 | 7 | 96 | 55 | 310 | 0 | 0 | 0 | 91 | 93 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 44 | 35 | 120 | 0 | 0 | 204 | 0 | 106 | 0 |  | 0 | 0 | 33 | 0 | 0 | 0 | 20 | 41 | 0 | 0 | 80 | 360 | 300 | 161 | 8 | 87 | 35 | 5 | 0 | 43 | 0 | 0 | 43 | 18 | 11 | 33 | 21 | 170 | 159 | 72 | 22 | 0 | 90 | 28 | 53 | 49 | 130 | 294 | 63 | 85 | 0 | 184 | 18 | 0 | 10 | 275 | 23 | 8 | 0 | 286 | 0 | 0 | 155 | 0 | 117 | 0 | 100 | 0 | 10 | 0 | 35 | 0 | 0 | 0 | 215 | 0 | 0 | 17 | 113 | 100 | 0 | 17 |  | 935 | 0 | 370 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 33 | 65 | 38 | 64 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 145 | 0 | 0 | 0 | 76 | 0 | 130 | 0 | 416 | 35 | 0 | 113 | 0 | 106 | 0 | 0 | 90 | 560 |  | 7197 | 3663 | 10860 | 4317 | 935 | 2050 | 2446 | 710 | 79 | 153 | 170 | 0 | 0 | 93.12
3:00 | 35 | 0 | 140 | 110 | 0 | 82 | 0 | 345 | 334 |  | 0 | 380 | 128 | 7 | 96 | 40 | 296 | 0 | 0 | 0 | 95 | 93 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 44 | 35 | 120 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 33 | 0 | 0 | 0 | 20 | 42 | 0 | 0 | 80 | 360 | 275 | 158 | 8 | 98 | 35 | 5 | 0 | 43 | 0 | 0 | 43 | 18 | 11 | 33 | 21 | 166 | 159 | 72 | 22 | 0 | 90 | 28 | 53 | 49 | 130 | 298 | 64 | 85 | 0 | 184 | 18 | 0 | 10 | 300 | 23 | 8 | 0 | 275 | 0 | 0 | 155 | 0 | 115 | 0 | 100 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 108 | 100 | 0 | 17 |  | 934 | 0 | 370 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 16 | 65 | 38 | 64 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 145 | 0 | 0 | 0 | 79 | 0 | 130 | 0 | 418 | 35 | 0 | 113 | 0 | 106 | 0 | 0 | 90 | 560 |  | 7017 | 3645 | 10662 | 4281 | 934 | 2082 | 2257 | 710 | 79 | 153 | 166 | 0 | 0 | 93.12
4:00 | 35 | 0 | 140 | 110 | 0 | 82 | 0 | 341 | 334 |  | 0 | 380 | 130 | 7 | 64 | 40 | 288 | 0 | 0 | 0 | 100 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 43 | 35 | 120 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 33 | 0 | 0 | 0 | 20 | 38 | 0 | 0 | 80 | 360 | 275 | 162 | 8 | 97 | 35 | 5 | 0 | 43 | 0 | 0 | 43 | 18 | 11 | 33 | 21 | 164 | 159 | 72 | 22 | 0 | 90 | 28 | 53 | 49 | 130 | 298 | 64 | 85 | 0 | 184 | 18 | 0 | 10 | 285 | 23 | 8 | 0 | 215 | 0 | 0 | 155 | 0 | 115 | 0 | 100 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 113 | 100 | 0 | 17 |  | 934 | 0 | 370 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 16 | 65 | 39 | 64 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 145 | 0 | 0 | 0 | 78 | 0 | 150 | 0 | 404 | 35 | 0 | 113 | 0 | 106 | 0 | 0 | 90 | 560 |  | 6872 | 3651 | 10523 | 4292 | 934 | 2049 | 2143 | 710 | 78 | 153 | 164 | 0 | 0 | 93.11
5:00 | 35 | 0 | 140 | 110 | 0 | 82 | 0 | 341 | 332 |  | 0 | 380 | 138 | 7 | 64 | 40 | 296 | 0 | 0 | 0 | 100 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 43 | 35 | 120 | 0 | 0 | 204 | 0 | 103 | 0 |  | 0 | 0 | 33 | 0 | 0 | 0 | 20 | 40 | 0 | 0 | 80 | 360 | 275 | 164 | 8 | 97 | 35 | 5 | 0 | 43 | 0 | 0 | 25 | 18 | 11 | 25 | 21 | 158 | 159 | 72 | 22 | 0 | 90 | 28 | 53 | 49 | 130 | 296 | 64 | 85 | 0 | 184 | 18 | 0 | 10 | 290 | 23 | 8 | 0 | 143 | 0 | 0 | 155 | 0 | 115 | 0 | 100 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 113 | 100 | 0 | 17 |  | 934 | 0 | 370 | 0 | 104 | 120 | 0 | 0 | 0 | 0 | 16 | 65 | 40 | 64 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 145 | 0 | 0 | 0 | 78 | 0 | 150 | 0 | 412 | 17 | 0 | 35 | 0 | 106 | 0 | 0 | 90 | 540 |  | 6771 | 3533 | 10304 | 4291 | 934 | 2063 | 1937 | 690 | 78 | 153 | 158 | 0 | 0 | 93.11
6:00 | 0 | 0 | 140 | 110 | 0 | 82 | 0 | 339 | 304 |  | 0 | 380 | 138 | 7 | 48 | 25 | 276 | 0 | 0 | 0 | 90 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 30 | 33 | 25 | 0 | 0 | 42 | 35 | 120 | 0 | 0 | 203 | 0 | 103 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 41 | 0 | 0 | 80 | 360 | 250 | 175 | 8 | 86 | 35 | 5 | 0 | 40 | 0 | 0 | 0 | 18 | 11 | 25 | 21 | 148 | 161 | 48 | 22 | 0 | 90 | 28 | 53 | 49 | 130 | 296 | 64 | 85 | 0 | 184 | 18 | 0 | 10 | 270 | 23 | 8 | 0 | 95 | 0 | 0 | 155 | 0 | 113 | 1 | 50 | 0 | 0 | 0 | 8 | 0 | 0 | 1 | 161 | 0 | 0 | 0 | 113 | 100 | 0 | 17 |  | 934 | 0 | 370 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 35 | 32 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 5 | 8 | 0 | 0 | 150 | 0 | 0 | 145 | 0 | 0 | 0 | 78 | 0 | 150 | 0 | 389 | 0 | 0 | 0 | 0 | 89 | 0 | 0 | 50 | 520 |  | 6318 | 3331 | 9649 | 4194 | 934 | 1985 | 1502 | 670 | 77 | 137 | 148 | 2 | 0 | 93.11
7:00 | 0 | 0 | 140 | 110 | 0 | 82 | 0 | 341 | 304 |  | 0 | 350 | 140 | 7 | 48 | 25 | 292 | 0 | 0 | 0 | 50 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 30 | 33 | 25 | 0 | 0 | 42 | 35 | 120 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 35 | 0 | 0 | 80 | 260 | 250 | 215 | 8 | 88 | 31 | 5 | 0 | 40 | 0 | 0 | 0 | 18 | 11 | 25 | 10 | 138 | 160 | 48 | 22 | 0 | 91 | 28 | 53 | 49 | 130 | 298 | 64 | 83 | 0 | 183 | 18 | 0 | 10 | 290 | 23 | 8 | 0 | 45 | 0 | 0 | 120 | 0 | 102 | 4 | 50 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 106 | 0 | 0 | 0 | 75 | 100 | 0 | 17 |  | 935 | 0 | 320 | 0 | 69 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 28 | 32 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 5 | 8 | 0 | 0 | 150 | 0 | 0 | 145 | 0 | 0 | 0 | 79 | 0 | 150 | 0 | 341 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 50 | 520 |  | 5993 | 3129 | 9122 | 4089 | 935 | 1913 | 1176 | 670 | 77 | 120 | 138 | 4 | 0 | 93.1
8:00 | 0 | 0 | 140 | 110 | 0 | 82 | 0 | 353 | 304 |  | 0 | 350 | 142 | 7 | 48 | 25 | 306 | 0 | 0 | 0 | 50 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 23 | 33 | 25 | 0 | 0 | 42 | 35 | 120 | 0 | 0 | 210 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 0 | 0 | 80 | 275 | 270 | 213 | 8 | 96 | 31 | 5 | 0 | 40 | 0 | 0 | 0 | 18 | 11 | 25 | 9 | 138 | 156 | 48 | 22 | 1 | 90 | 30 | 53 | 49 | 130 | 296 | 63 | 83 | 0 | 185 | 18 | 0 | 10 | 300 | 23 | 8 | 0 | 45 | 0 | 0 | 120 | 0 | 100 | 11 | 50 | 0 | 0 | 0 | 8 | 0 | 0 | 2 | 106 | 0 | 0 | 0 | 75 | 100 | 0 | 17 |  | 934 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 16 | 65 | 26 | 16 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 5 | 8 | 0 | 0 | 150 | 0 | 0 | 145 | 0 | 0 | 0 | 78 | 0 | 150 | 0 | 365 | 35 | 0 | 0 | 0 | 35 | 0 | 1 | 50 | 520 |  | 6047 | 3115 | 9162 | 4150 | 934 | 1917 | 1141 | 670 | 77 | 120 | 138 | 15 | 0 | 93.1
9:00 | 0 | 0 | 160 | 110 | 0 | 82 | 0 | 368 | 303 |  | 0 | 420 | 140 | 7 | 48 | 35 | 307 | 0 | 0 | 0 | 55 | 64 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 19 | 25 | 29 | 33 | 25 | 0 | 0 | 42 | 35 | 120 | 0 | 0 | 206 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 2 | 7 | 20 | 5 | 0 | 0 | 80 | 280 | 325 | 213 | 8 | 90 | 35 | 5 | 0 | 35 | 0 | 0 | 1 | 18 | 8 | 25 | 9 | 134 | 156 | 48 | 22 | 1 | 91 | 28 | 53 | 49 | 163 | 295 | 63 | 83 | 0 | 185 | 18 | 0 | 10 | 305 | 23 | 8 | 0 | 58 | 0 | 0 | 120 | 0 | 103 | 16 | 100 | 0 | 3 | 0 | 8 | 4 | 0 | 4 | 170 | 0 | 0 | 0 | 86 | 100 | 0 | 17 |  | 932 | 0 | 360 | 0 | 23 | 120 | 0 | 0 | 0 | 0 | 16 | 15 | 27 | 64 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 5 | 8 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 0 | 0 | 77 | 0 | 150 | 0 | 410 | 35 | 0 | 0 | 0 | 35 | 0 | 1 | 70 | 430 |  | 6499 | 3148 | 9647 | 4231 | 932 | 2061 | 1490 | 580 | 77 | 120 | 134 | 22 | 0 | 93.1
10:00 | 0 | 0 | 160 | 110 | 0 | 82 | 0 | 359 | 282 |  | 0 | 420 | 140 | 7 | 78 | 40 | 306 | 0 | 0 | 0 | 80 | 93 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 29 | 33 | 25 | 0 | 0 | 42 | 35 | 120 | 0 | 0 | 215 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 10 | 12 | 18 | 6 | 0 | 0 | 80 | 285 | 290 | 212 | 8 | 97 | 35 | 5 | 0 | 35 | 0 | 0 | 16 | 18 | 8 | 25 | 9 | 142 | 154 | 48 | 20 | 1 | 91 | 30 | 50 | 49 | 163 | 296 | 63 | 83 | 0 | 186 | 18 | 0 | 10 | 300 | 23 | 8 | 0 | 175 | 0 | 0 | 144 | 0 | 127 | 0 | 90 | 0 | 33 | 0 | 21 | 50 | 0 | 5 | 197 | 0 | 0 | 0 | 113 | 100 | 0 | 17 |  | 931 | 0 | 370 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 16 | 15 | 27 | 64 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 0 | 0 | 76 | 0 | 150 | 0 | 410 | 0 | 0 | 0 | 0 | 41 | 0 | 2 | 90 | 310 |  | 6941 | 3092 | 10033 | 4236 | 931 | 2032 | 2027 | 460 | 77 | 120 | 142 | 8 | 0 | 93.09
11:00 | 0 | 0 | 157 | 110 | 0 | 82 | 0 | 347 | 277 |  | 0 | 420 | 125 | 7 | 96 | 40 | 305 | 0 | 0 | 0 | 91 | 93 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 24 | 33 | 25 | 0 | 0 | 42 | 35 | 120 | 0 | 13 | 209 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 10 | 12 | 18 | 5 | 0 | 0 | 80 | 265 | 270 | 211 | 8 | 90 | 35 | 5 | 0 | 43 | 0 | 0 | 25 | 18 | 8 | 33 | 9 | 146 | 154 | 56 | 20 | 2 | 91 | 28 | 50 | 49 | 163 | 300 | 63 | 83 | 0 | 186 | 18 | 0 | 10 | 310 | 16 | 8 | 0 | 222 | 0 | 0 | 165 | 0 | 127 | 8 | 90 | 0 | 78 | 0 | 53 | 50 | 0 | 5 | 197 | 0 | 0 | 0 | 110 | 100 | 0 | 17 |  | 931 | 0 | 355 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 16 | 15 | 23 | 64 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 5 | 11 | 0 | 0 | 151 | 0 | 0 | 141 | 0 | 0 | 0 | 77 | 0 | 170 | 0 | 414 | 0 | 0 | 0 | 0 | 79 | 0 | 4 | 90 | 430 |  | 7119 | 3251 | 10370 | 4162 | 931 | 2045 | 2289 | 581 | 77 | 120 | 146 | 19 | 0 | 93.09
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 312 |  | 0 | 420 | 140 | 7 | 96 | 40 | 0 | 0 | 0 | 0 | 14 | 93 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 24 | 0 | 25 | 0 | 0 | 44 | 35 | 120 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 46 | 14 | 26 | 18 | 5 | 0 | 0 | 80 | 260 | 340 | 0 | 8 | 87 | 0 | 0 | 0 | 3 | 0 | 0 | 25 | 18 | 0 | 33 | 9 | 156 | 76 | 8 | 22 | 3 | 91 | 30 | 50 | 47 | 163 | 160 | 66 | 30 | 0 | 186 | 18 | 0 | 10 | 300 | 16 | 0 | 0 | 248 | 0 | 0 | 45 | 0 | 122 | 19 | 90 | 1 | 0 | 0 | 28 | 53 | 0 | 5 | 198 | 0 | 0 | 114 | 105 | 100 | 0 | 17 |  | 929 | 0 | 330 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 16 | 15 | 26 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 21 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 138 | 0 | 0 | 0 | 77 | 0 | 170 | 0 | 380 | 0 | 0 | 0 | 0 | 84 | 0 | 5 | 90 | 440 |  | 5832 | 3171 | 9003 | 3067 | 929 | 1857 | 2173 | 590 | 79 | 120 | 156 | 32 | 0 | 93.09
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 314 |  | 0 | 420 | 120 | 7 | 96 | 40 | 26 | 0 | 0 | 0 | 45 | 93 | 55 | 7 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 24 | 0 | 25 | 42 | 0 | 44 | 35 | 120 | 0 | 25 | 205 | 0 | 139 | 0 |  | 0 | 0 | 3 | 100 | 11 | 50 | 20 | 8 | 0 | 0 | 80 | 260 | 340 | 0 | 8 | 87 | 0 | 0 | 0 | 25 | 0 | 0 | 34 | 18 | 8 | 33 | 9 | 152 | 54 | 64 | 22 | 1 | 91 | 28 | 50 | 47 | 163 | 232 | 66 | 83 | 0 | 185 | 18 | 0 | 10 | 290 | 16 | 5 | 0 | 262 | 168 | 95 | 180 | 100 | 149 | 20 | 100 | 80 | 15 | 0 | 107 | 88 | 0 | 4 | 197 | 0 | 0 | 114 | 111 | 90 | 0 | 17 |  | 929 | 0 | 330 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 16 | 15 | 27 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 21 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 141 | 0 | 0 | 0 | 77 | 0 | 180 | 0 | 370 | 0 | 0 | 10 | 0 | 89 | 0 | 6 | 90 | 480 |  | 7005 | 3264 | 10269 | 3179 | 929 | 1918 | 3173 | 630 | 79 | 178 | 152 | 31 | 0 | 93.09
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 300 |  | 0 | 380 | 135 | 7 | 96 | 40 | 26 | 0 | 0 | 0 | 70 | 93 | 100 | 26 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 10 | 0 | 33 | 51 | 0 | 44 | 35 | 120 | 0 | 25 | 164 | 0 | 145 | 0 |  | 0 | 0 | 64 | 100 | 11 | 50 | 18 | 2 | 0 | 0 | 80 | 320 | 340 | 0 | 8 | 88 | 10 | 30 | 0 | 25 | 0 | 0 | 43 | 18 | 8 | 33 | 9 | 164 | 71 | 64 | 22 | 3 | 90 | 29 | 50 | 47 | 163 | 235 | 65 | 83 | 0 | 185 | 18 | 0 | 10 | 290 | 24 | 5 | 0 | 286 | 155 | 95 | 183 | 102 | 149 | 18 | 100 | 191 | 86 | 0 | 115 | 93 | 0 | 4 | 197 | 0 | 0 | 114 | 111 | 100 | 0 | 17 |  | 930 | 0 | 320 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 16 | 85 | 28 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 21 | 5 | 11 | 0 | 0 | 149 | 0 | 0 | 143 | 0 | 0 | 0 | 43 | 0 | 180 | 0 | 343 | 0 | 0 | 35 | 0 | 94 | 0 | 6 | 90 | 450 |  | 7425 | 3259 | 10684 | 3275 | 930 | 1828 | 3494 | 599 | 79 | 284 | 164 | 31 | 0 | 93.08
15:00 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 340 | 303 |  | 0 | 380 | 140 | 7 | 96 | 30 | 165 | 0 | 0 | 0 | 80 | 93 | 150 | 24 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 26 | 0 | 25 | 51 | 0 | 45 | 35 | 120 | 0 | 25 | 204 | 0 | 145 | 0 |  | 0 | 0 | 65 | 100 | 12 | 50 | 18 | 10 | 0 | 0 | 80 | 320 | 340 | 0 | 8 | 82 | 23 | 47 | 0 | 25 | 0 | 50 | 43 | 16 | 8 | 33 | 9 | 158 | 54 | 64 | 22 | 1 | 89 | 29 | 50 | 47 | 163 | 237 | 62 | 80 | 0 | 185 | 18 | 0 | 10 | 270 | 24 | 5 | 0 | 283 | 0 | 40 | 183 | 42 | 148 | 10 | 100 | 199 | 112 | 0 | 115 | 104 | 0 | 1 | 197 | 0 | 0 | 114 | 113 | 100 | 0 | 17 |  | 930 | 0 | 320 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 16 | 87 | 29 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 21 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 143 | 0 | 0 | 0 | 43 | 0 | 180 | 0 | 364 | 0 | 0 | 35 | 0 | 98 | 0 | 3 | 90 | 450 |  | 7488 | 3285 | 10773 | 3464 | 930 | 1866 | 3275 | 600 | 80 | 385 | 158 | 15 | 0 | 93.08
16:00 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 339 | 283 |  | 0 | 380 | 130 | 7 | 96 | 25 | 294 | 0 | 0 | 0 | 91 | 93 | 150 | 24 | 0 | 0 | 0 | 17 | 55 | 55 | 19 | 25 | 28 | 0 | 25 | 51 | 0 | 45 | 35 | 120 | 0 | 25 | 203 | 0 | 147 | 0 |  | 0 | 0 | 68 | 0 | 33 | 50 | 18 | 8 | 0 | 0 | 80 | 320 | 340 | 26 | 8 | 86 | 35 | 46 | 0 | 25 | 0 | 50 | 43 | 16 | 8 | 0 | 15 | 154 | 105 | 64 | 22 | 1 | 89 | 29 | 47 | 47 | 163 | 239 | 61 | 85 | 0 | 185 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 286 | 0 | 0 | 192 | 0 | 131 | 6 | 100 | 16 | 113 | 0 | 115 | 88 | 0 | 0 | 197 | 0 | 0 | 17 | 113 | 100 | 0 | 17 |  | 930 | 0 | 320 | 0 | 61 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 0 | 0 | 44 | 0 | 180 | 0 | 334 | 0 | 0 | 35 | 0 | 84 | 0 | 2 | 50 | 450 |  | 7212 | 3067 | 10279 | 3666 | 930 | 1862 | 2590 | 600 | 80 | 388 | 154 | 9 | 0 | 93.08
17:00 | 0 | 0 | 0 | 0 | 0 | 82 | 60 | 340 | 283 |  | 0 | 380 | 130 | 7 | 96 | 25 | 280 | 0 | 0 | 0 | 50 | 93 | 150 | 26 | 0 | 0 | 0 | 17 | 55 | 55 | 19 | 25 | 28 | 33 | 25 | 25 | 0 | 45 | 35 | 120 | 0 | 25 | 204 | 0 | 147 | 0 |  | 0 | 0 | 68 | 0 | 50 | 18 | 18 | 17 | 0 | 0 | 80 | 270 | 265 | 42 | 8 | 82 | 35 | 42 | 0 | 34 | 0 | 50 | 24 | 18 | 5 | 33 | 15 | 142 | 116 | 63 | 22 | 0 | 88 | 29 | 52 | 47 | 130 | 245 | 61 | 85 | 0 | 185 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 281 | 0 | 0 | 191 | 0 | 129 | 1 | 100 | 0 | 118 | 0 | 115 | 95 | 0 | 0 | 197 | 0 | 0 | 17 | 113 | 100 | 0 | 17 |  | 930 | 0 | 290 | 0 | 32 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 0 | 0 | 43 | 0 | 180 | 0 | 334 | 0 | 0 | 35 | 0 | 39 | 0 | 1 | 50 | 450 |  | 7123 | 2959 | 10082 | 3592 | 930 | 1944 | 2404 | 600 | 80 | 388 | 142 | 2 | 0 | 93.08
18:00 | 0 | 0 | 0 | 0 | 0 | 86 | 40 | 323 | 283 |  | 0 | 300 | 140 | 7 | 96 | 25 | 300 | 0 | 0 | 0 | 50 | 93 | 150 | 24 | 0 | 0 | 0 | 17 | 55 | 55 | 19 | 25 | 24 | 33 | 33 | 25 | 0 | 45 | 35 | 120 | 0 | 25 | 204 | 0 | 79 | 0 |  | 0 | 0 | 71 | 10 | 50 | 18 | 20 | 13 | 0 | 0 | 80 | 270 | 265 | 48 | 8 | 90 | 35 | 42 | 0 | 28 | 0 | 50 | 24 | 18 | 11 | 33 | 15 | 142 | 156 | 63 | 22 | 0 | 91 | 30 | 53 | 48 | 110 | 276 | 40 | 30 | 0 | 151 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 286 | 0 | 0 | 192 | 0 | 127 | 0 | 100 | 0 | 123 | 0 | 115 | 105 | 0 | 0 | 143 | 0 | 0 | 17 | 113 | 100 | 0 | 17 |  | 930 | 0 | 260 | 0 | 32 | 135 | 0 | 0 | 4 | 0 | 8 | 88 | 25 | 16 | 0 | 0 | 0 | 0 | 23 | 12 | 0 | 0 | 16 | 8 | 4 | 21 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 120 | 0 | 0 | 0 | 43 | 0 | 130 | 0 | 334 | 0 | 0 | 35 | 0 | 42 | 0 | 0 | 50 | 410 |  | 6900 | 2915 | 9815 | 3470 | 930 | 1762 | 2406 | 560 | 80 | 465 | 142 | 0 | 0 | 93.07
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 89 | 60 | 336 | 277 |  | 0 | 420 | 120 | 7 | 96 | 55 | 278 | 0 | 0 | 0 | 80 | 93 | 150 | 26 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 47 | 0 | 45 | 35 | 120 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 102 | 30 | 74 | 47 | 20 | 24 | 0 | 0 | 80 | 290 | 280 | 73 | 8 | 80 | 35 | 42 | 0 | 29 | 0 | 50 | 40 | 18 | 11 | 33 | 21 | 162 | 157 | 63 | 22 | 0 | 91 | 28 | 53 | 48 | 163 | 271 | 65 | 85 | 0 | 185 | 18 | 0 | 10 | 300 | 24 | 11 | 50 | 283 | 107 | 25 | 193 | 42 | 122 | 0 | 100 | 61 | 130 | 0 | 115 | 103 | 0 | 0 | 195 | 0 | 8 | 114 | 70 | 100 | 0 | 17 |  | 930 | 0 | 410 | 0 | 115 | 195 | 0 | 0 | 19 | 0 | 40 | 88 | 38 | 80 | 0 | 0 | 0 | 50 | 34 | 98 | 0 | 0 | 43 | 43 | 32 | 21 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 78 | 64 | 186 | 0 | 388 | 70 | 100 | 86 | 0 | 80 | 0 | 0 | 90 | 530 |  | 7984 | 4217 | 12201 | 3865 | 930 | 2141 | 3570 | 680 | 80 | 773 | 162 | 0 | 0 | 93.07
19:30 | 0 | 0 | 0 | 0 | 0 | 92 | 72 | 340 | 278 |  | 0 | 420 | 130 | 7 | 96 | 55 | 280 | 0 | 0 | 0 | 100 | 93 | 150 | 24 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 45 | 35 | 120 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 101 | 30 | 84 | 50 | 20 | 26 | 0 | 0 | 80 | 290 | 280 | 116 | 8 | 80 | 35 | 42 | 0 | 29 | 0 | 50 | 43 | 18 | 11 | 33 | 21 | 164 | 157 | 63 | 22 | 0 | 91 | 28 | 53 | 48 | 163 | 295 | 63 | 85 | 0 | 185 | 18 | 0 | 9 | 290 | 24 | 11 | 50 | 283 | 107 | 25 | 193 | 42 | 122 | 0 | 100 | 113 | 130 | 0 | 115 | 103 | 0 | 0 | 198 | 0 | 17 | 114 | 113 | 100 | 0 | 17 |  | 932 | 0 | 345 | 0 | 115 | 200 | 0 | 0 | 18 | 0 | 40 | 88 | 39 | 80 | 0 | 0 | 0 | 50 | 34 | 98 | 0 | 0 | 43 | 43 | 32 | 21 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 146 | 0 | 0 | 0 | 78 | 100 | 180 | 0 | 394 | 70 | 50 | 113 | 0 | 98 | 0 | 0 | 90 | 560 |  | 8221 | 4226 | 12447 | 3874 | 932 | 2155 | 3756 | 710 | 80 | 776 | 164 | 0 | 0 | 93.07
20:00 | 0 | 0 | 0 | 0 | 0 | 92 | 72 | 339 | 267 |  | 0 | 420 | 138 | 7 | 96 | 55 | 301 | 0 | 0 | 0 | 100 | 93 | 150 | 24 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 45 | 35 | 120 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 88 | 30 | 84 | 50 | 21 | 30 | 0 | 0 | 80 | 290 | 280 | 204 | 8 | 84 | 35 | 42 | 0 | 27 | 0 | 50 | 43 | 18 | 11 | 33 | 21 | 152 | 156 | 63 | 22 | 0 | 88 | 28 | 53 | 48 | 163 | 295 | 63 | 85 | 0 | 185 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 283 | 56 | 25 | 193 | 43 | 131 | 0 | 100 | 166 | 128 | 0 | 115 | 103 | 0 | 0 | 198 | 0 | 17 | 114 | 99 | 100 | 0 | 17 |  | 932 | 0 | 345 | 0 | 115 | 200 | 0 | 0 | 12 | 0 | 40 | 88 | 39 | 80 | 0 | 0 | 0 | 50 | 34 | 98 | 0 | 0 | 47 | 43 | 32 | 21 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 146 | 0 | 0 | 0 | 78 | 100 | 180 | 0 | 407 | 70 | 0 | 113 | 0 | 98 | 0 | 0 | 90 | 570 |  | 8241 | 4197 | 12438 | 3983 | 932 | 2150 | 3660 | 720 | 80 | 761 | 152 | 0 | 0 | 93.07
21:00 | 0 | 0 | 0 | 0 | 40 | 91 | 72 | 340 | 267 |  | 0 | 420 | 125 | 7 | 96 | 55 | 293 | 0 | 0 | 0 | 100 | 93 | 150 | 46 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 45 | 35 | 120 | 0 | 25 | 204 | 0 | 140 | 0 |  | 0 | 0 | 102 | 30 | 84 | 50 | 21 | 36 | 0 | 0 | 80 | 270 | 250 | 190 | 8 | 86 | 35 | 42 | 0 | 28 | 0 | 50 | 43 | 18 | 11 | 33 | 21 | 148 | 159 | 63 | 22 | 0 | 91 | 28 | 53 | 49 | 163 | 308 | 64 | 85 | 0 | 184 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 286 | 53 | 25 | 200 | 42 | 131 | 0 | 100 | 200 | 133 | 0 | 115 | 103 | 0 | 0 | 198 | 0 | 17 | 114 | 113 | 100 | 0 | 17 |  | 931 | 0 | 345 | 0 | 99 | 200 | 0 | 0 | 12 | 0 | 40 | 87 | 41 | 80 | 0 | 0 | 0 | 50 | 34 | 96 | 0 | 0 | 43 | 34 | 32 | 21 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 145 | 0 | 0 | 0 | 78 | 100 | 180 | 0 | 398 | 70 | 0 | 113 | 0 | 98 | 0 | 0 | 90 | 580 |  | 8327 | 4166 | 12493 | 3972 | 931 | 2160 | 3703 | 730 | 80 | 769 | 148 | 0 | 0 | 93.07
22:00 | 0 | 0 | 0 | 0 | 120 | 91 | 72 | 347 | 257 |  | 0 | 420 | 138 | 7 | 96 | 55 | 297 | 0 | 0 | 0 | 100 | 93 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 43 | 35 | 120 | 0 | 25 | 205 | 0 | 139 | 0 |  | 0 | 0 | 101 | 30 | 84 | 50 | 21 | 39 | 0 | 0 | 80 | 270 | 250 | 158 | 8 | 80 | 35 | 25 | 0 | 38 | 0 | 50 | 43 | 18 | 11 | 33 | 21 | 156 | 156 | 63 | 22 | 0 | 89 | 30 | 53 | 49 | 163 | 260 | 63 | 85 | 0 | 185 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 283 | 0 | 0 | 200 | 0 | 148 | 0 | 100 | 102 | 130 | 0 | 115 | 103 | 0 | 0 | 198 | 0 | 17 | 101 | 113 | 100 | 0 | 17 |  | 932 | 0 | 350 | 0 | 115 | 225 | 0 | 0 | 12 | 0 | 40 | 87 | 41 | 80 | 0 | 0 | 0 | 50 | 34 | 96 | 0 | 0 | 43 | 43 | 32 | 21 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 145 | 0 | 0 | 0 | 77 | 100 | 180 | 0 | 411 | 70 | 0 | 113 | 0 | 98 | 0 | 0 | 90 | 590 |  | 8177 | 4244 | 12421 | 3979 | 932 | 2168 | 3575 | 740 | 78 | 793 | 156 | 0 | 0 | 93.06
23:00 | 0 | 0 | 0 | 0 | 120 | 92 | 71 | 369 | 257 |  | 0 | 420 | 130 | 7 | 96 | 55 | 296 | 0 | 0 | 0 | 100 | 93 | 150 | 33 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 43 | 35 | 120 | 0 | 25 | 193 | 0 | 110 | 0 |  | 0 | 0 | 102 | 30 | 84 | 50 | 21 | 42 | 0 | 0 | 80 | 280 | 270 | 144 | 8 | 75 | 25 | 5 | 0 | 43 | 0 | 50 | 43 | 18 | 11 | 33 | 21 | 160 | 154 | 71 | 22 | 0 | 90 | 28 | 53 | 49 | 163 | 259 | 63 | 85 | 0 | 184 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 283 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 140 | 123 | 0 | 115 | 103 | 0 | 0 | 215 | 0 | 0 | 101 | 113 | 100 | 0 | 17 |  | 931 | 0 | 340 | 0 | 115 | 225 | 0 | 0 | 11 | 0 | 40 | 87 | 40 | 80 | 0 | 0 | 0 | 50 | 34 | 96 | 0 | 0 | 43 | 43 | 32 | 21 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 145 | 0 | 0 | 0 | 77 | 100 | 180 | 0 | 416 | 70 | 0 | 113 | 0 | 98 | 0 | 0 | 90 | 530 |  | 8111 | 4176 | 12287 | 3945 | 931 | 2160 | 3540 | 680 | 78 | 793 | 160 | 0 | 0 | 93.06
24:00 | 0 | 0 | 0 | 0 | 120 | 92 | 72 | 343 | 303 |  | 0 | 340 | 120 | 7 | 96 | 55 | 270 | 0 | 0 | 0 | 100 | 93 | 150 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 43 | 35 | 120 | 0 | 25 | 177 | 0 | 103 | 0 |  | 0 | 0 | 102 | 30 | 84 | 50 | 21 | 42 | 0 | 0 | 80 | 260 | 255 | 170 | 8 | 75 | 25 | 5 | 0 | 51 | 0 | 50 | 43 | 18 | 11 | 33 | 21 | 164 | 159 | 71 | 22 | 0 | 91 | 30 | 53 | 49 | 130 | 260 | 63 | 85 | 0 | 185 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 286 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 101 | 125 | 0 | 115 | 103 | 0 | 0 | 233 | 0 | 0 | 101 | 109 | 100 | 0 | 17 |  | 931 | 0 | 340 | 0 | 115 | 215 | 0 | 0 | 12 | 0 | 40 | 87 | 39 | 110 | 0 | 0 | 0 | 50 | 21 | 96 | 0 | 0 | 43 | 43 | 0 | 21 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 146 | 0 | 0 | 0 | 77 | 100 | 160 | 0 | 383 | 90 | 0 | 113 | 0 | 99 | 0 | 0 | 90 | 530 |  | 7925 | 4117 | 12042 | 3849 | 931 | 2048 | 3553 | 680 | 78 | 739 | 164 | 0 | 0 | 93.06
KWH | 0 | 0 | 1614000 | 1323000 | 361000 | 1654954 | 551936 | 8411130 | 7148000 |  | 0 | 8817250 | 3247098 | 197760 | 2083344 | 1032935 | 6091866 | 0 | 0 | 0 | 1924800 | 2120832 | 1613760 | 434046 | 0 | 0 | 0 | 916560 | 947108 | 913759 | 401760 | 600000 | 629100 | 771100 | 734400 | 552084 | 0 | 1033396 | 848000 | 2900000 | 0 | 346545 | 4826656 | 0 | 2942487 | 0 |  | 0 | 0 | 1142476 | 510360 | 722880 | 642720 | 471552 | 577920 | 0 | 0 | 1923456 | 7629200 | 7053000 | 3058000 | 200727 | 2042400 | 660168 | 455040 | 0 | 862276 | 0 | 467464 | 780984 | 408000 | 219240 | 732600 | 412870 | 3742080 | 3191720 | 1448640 | 459477 | 10400 | 2120000 | 683640 | 1245000 | 1162368 | 3517118 | 6243000 | 1374240 | 1871040 | 0 | 4422980 | 416000 | 0 | 244620 | 7185500 | 523512 | 174960 | 55872 | 5512471 | 587885 | 297620 | 3916800 | 374391 | 3093120 | 107055 | 2263680 | 1525440 | 1689454 | 0 | 1657200 | 1427940 | 0 | 31920 | 4586618 | 0 | 81963 | 1216380 | 2536800 | 2425920 | 0 | 432000 |  | 22361454 | 0 | 8525952 | 0 | 2154240 | 3472320 | 0 | 0 | 72000 | 0 | 510375 | 1787674 | 767552 | 1429440 | 0 | 624000 | 0 | 285316 | 195864 | 678104 | 0 | 0 | 283300 | 382080 | 196030 | 494160 | 131544 | 250182 | 0 | 0 | 3691500 | 0 | 0 | 3553200 | 0 | 0 | 0 | 1707 | 608640 | 4393345 | 0 | 9206273 | 688320 | 100802 | 1400640 | 0 | 1960320 | 0 | 30329 | 1987680 | 12998900 |  | 172820823 | 85223243 | 258044066 | 94960867 | 22361454 | 46094985 | 63726546 | 16690400 | 1881396 | 8406634 | 3742080 | 179704 | 0
Fuel Cost | 0 | 0 | 2356440 | 1944810 | 400710 | 2184539.28 | 938291.2 | 8495241.3 | 7362440 |  | 0 | 9610802.5 | 3604278.78 | 1500998.4 | 14354240.16 | 8738630.1 | 6335540.64 | 0 | 0 | 0 | 14493744 | 19341987.84 | 15879398.4 | 4001904.12 | 0 | 0 | 0 | 6690888 | 7321144.84 | 9009663.74 | 301320 | 450000 | 0 | 0 | 0 | 5338652.28 | 0 | 279016.92 | 228960 | 5249000 | 0 | 3219403.05 | 5261055.04 | 0 | 5002227.9 | 0 |  | 0 | 0 | 11082017.2 | 4873938 | 6289056 | 5090342.4 | 594155.52 | 1716422.4 | 0 | 0 | 2827480.32 | 5645608 | 7053000 | 2813360 | 258937.83 | 2348760 | 745989.84 | 637056 | 0 | 1474491.96 | 0 | 4721386.4 | 7458397.2 | 518160 | 164430 | 1282050 | 309652.5 | 28065600 | 3383223.2 | 13153651.2 | 583535.79 | 165776 | 3476800 | 1093824 | 2216100 | 1813294.08 | 4009514.52 | 6492720 | 2707252.8 | 3573686.4 | 0 | 7651755.4 | 911040 | 0 | 499024.8 | 7257355 | 392634 | 132969.6 | 950382.72 | 41674280.76 | 9982287.3 | 4976206.4 | 20367360 | 6259817.52 | 30436300.8 | 1251472.95 | 18448992 | 16551024 | 11910650.7 | 0 | 15113664 | 13494033 | 0 | 0 | 34674832.08 | 0 | 720454.77 | 12139472.4 | 21740376 | 16156627.2 | 0 | 0 |  | 128801975.04 | 0 | 8952249.6 | 0 | 16932326.4 | 48126355.2 | 0 | 0 | 755280 | 0 | 5318107.5 | 2020071.62 | 1189705.6 | 13951334.4 | 0 | 1279200 | 0 | 2807509.44 | 1989978.24 | 6001220.4 | 0 | 0 | 2745177 | 3702355.2 | 1901491 | 948787.2 | 203893.2 | 189387.774 | 0 | 0 | 20007930 | 0 | 0 | 4157244 | 0 | 0 | 0 | 2560.5 | 10352966.4 | 5140213.65 | 0 | 9114210.27 | 7186060.8 | 1714642.02 | 13292073.6 | 0 | 15212083.2 | 0 | 335135.45 | 14688955.2 | 57065171 |  | 602228011.45 | 406085650.904 | 1008313662.354 | 108663112.494 | 128801975.04 | 55011112.74 | 512428586.48 | 77073101 | 507976.92 | 96009813.28 | 28065600 | 1752384.4 | 0
Yesterday Day Peak | 0 | 0 | 157 | 110 | 0 | 82 | 0 | 347 | 277 |  | 0 | 420 | 125 | 7 | 96 | 40 | 305 | 0 | 0 | 0 | 91 | 93 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 24 | 33 | 25 | 0 | 0 | 42 | 35 | 120 | 0 | 13 | 209 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 10 | 12 | 18 | 5 | 0 | 0 | 80 | 265 | 270 | 211 | 8 | 90 | 35 | 5 | 0 | 43 | 0 | 0 | 25 | 18 | 8 | 33 | 9 | 146 | 154 | 56 | 20 | 2 | 91 | 28 | 50 | 49 | 163 | 300 | 63 | 83 | 0 | 186 | 18 | 0 | 10 | 310 | 16 | 8 | 0 | 222 | 0 | 0 | 165 | 0 | 127 | 8 | 90 | 0 | 78 | 0 | 53 | 50 | 0 | 5 | 197 | 0 | 0 | 0 | 110 | 100 | 0 | 17 |  | 931 | 0 | 355 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 16 | 15 | 23 | 64 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 5 | 11 | 0 | 0 | 151 | 0 | 0 | 141 | 0 | 0 | 0 | 77 | 0 | 170 | 0 | 414 | 0 | 0 | 0 | 0 | 79 | 0 | 4 | 90 | 430 |  | 10370 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 40 | 91 | 72 | 340 | 267 | 0 | 0 | 420 | 125 | 7 | 96 | 55 | 293 | 0 | 0 | 0 | 100 | 93 | 150 | 46 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 45 | 35 | 120 | 0 | 25 | 204 | 0 | 140 | 0 | 0 | 0 | 0 | 102 | 30 | 84 | 50 | 21 | 36 | 0 | 0 | 80 | 270 | 250 | 190 | 8 | 86 | 35 | 42 | 0 | 28 | 0 | 50 | 43 | 18 | 11 | 33 | 21 | 148 | 159 | 63 | 22 | 0 | 91 | 28 | 53 | 49 | 163 | 308 | 64 | 85 | 0 | 184 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 286 | 53 | 25 | 200 | 42 | 131 | 0 | 100 | 200 | 133 | 0 | 115 | 103 | 0 | 0 | 198 | 0 | 17 | 114 | 113 | 100 | 0 | 17 |  | 931 | 0 | 345 | 0 | 99 | 200 | 0 | 0 | 12 | 0 | 40 | 87 | 41 | 80 | 0 | 0 | 0 | 50 | 34 | 96 | 0 | 0 | 43 | 34 | 32 | 21 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 145 | 0 | 0 | 0 | 78 | 100 | 180 | 0 | 398 | 70 | 0 | 113 | 0 | 98 | 0 | 0 | 90 | 580 |  | 12493 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 300 | 94 | 72 | 412 | 360 | 0 | 0 | 450 | 150 | 7 | 96 | 55 | 335 | 0 | 0 | 0 | 7 | 50 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 44 | 0 | 120 | 0 | 25 | 180 | 0 | 10 | 0 | 0 | 0 |  | 100 | 100 | 97 | 50 | 20 | 30 | 0 | 0 | 80 | 360 | 360 | 214 | 8 | 100 | 36 | 20 | 0 | 51 | 0 | 42 | 43 | 21 | 11 | 33 | 20 | 173 | 160 | 72 | 22 | 0 | 90 | 30 | 51 | 44 | 163 | 300 | 64 | 86 | 0 | 190 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 17 |  | 946 | 16 | 410 | 0 | 115 | 225 | 0 | 0 | 30 | 60 | 40 | 65 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 0 | 0 | 43 | 43 | 32 | 22 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 220 | 0 | 0 | 0 | 80 | 100 | 220 | 0 | 414 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 90 | 620
Forecast for Day | 0 | 0 | 0 | 0 | 120 | 94 | 72 | 412 | 360 | 0 | 0 | 450 | 150 | 7 | 96 | 55 | 50 | 0 | 0 | 0 | 7 | 50 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 44 | 0 | 120 | 0 | 25 | 180 | 0 | 10 | 0 | 0 | 0 |  | 100 | 100 | 97 | 50 | 20 | 10 | 0 | 0 | 80 | 360 | 360 | 50 | 8 | 100 | 35 | 20 | 0 | 51 | 0 | 0 | 43 | 21 | 11 | 33 | 20 | 157 | 160 | 72 | 22 | 1.6 | 90 | 30 | 51 | 44 | 163 | 300 | 64 | 86 | 0 | 190 | 18 | 0 | 10 | 341 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 17 |  | 946 | 0 | 410 | 0 | 115 | 225 | 0 | 0 | 0 | 0 | 40 | 65 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 43 | 0 | 22 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 220 | 0 | 0 |  | 80 | 80 | 220 | 0 | 414 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 90 | 620
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 120 | 94 | 70 | 340 | 251 | 0 | 0 | 320 | 138 |  | 97 | 55 | 0 | 0 | 0 | 0 | 98 | 83 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 44 | 0 | 120 | 0 | 0 | 177 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 21 | 12 | 0 | 0 | 80 | 260 | 255 | 25 | 8 | 94 | 35 | 20 | 0 | 51 | 0 | 0 | 16 | 18 | 8 | 33 | 21 | 124 | 160 | 32 | 22 | 0 | 90 | 30 | 53 | 49 | 163 | 260 | 64 | 85 | 0 | 185 | 18 | 0 | 9 | 280 | 24 | 5 | 0 | 250 | 0 | 0 | 200 | 0 | 149 | 2 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 236 | 0 | 0 | 0 | 96 | 100 | 0 | 17 | 0 | 936 | 0 | 345 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 147 | 0 | 0 | 0 | 77 | 0 | 148 | 0 | 330 | 0 | 0 | 0 | 0 | 71 | 0 | 1 | 90 | 450 | 0
199
| Minimum Generation |  | 9122 | 7:00
| Highest Generation |  | 12493 | 21:00
| Day Peak Generation |  | 10370 | 11:00
| Evening Peak Generation |  | 12493 | 21:00
| HVDC Max Flow |  | 935 | 2:00
| HVDC EvPeak Flow |  | 931 | 21:00
| Load factor L.F |  | 86.06%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-09-10
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-09-09 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10370 | MW Hour : | 11:00 | Min. Gen. at | 7:00 | 9121 | MW
Evening Peak Generation : |  | 12493 | MW Hour : | 21:00 | Available Max Generation : |  | 14870 | MW
E.P. Demand (at gen end) : |  | 12493 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12700 | MW
Maximum Generation : |  | 12493 | MW Hour : | 21:00 | Reserve(Generation end) |  | 2170 | MW
Total Gen. (MKWH) : |  | 258.0441 | System Load Factor : | 86.06% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -60 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-09-10
Actual : | 93.06 | Ft.(MSL) , | Rule curve : | 101.07 | Ft.( MSL )
Gas Consumed : | Total = | 1134.43 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 163674225.234
: |  | Coal : | 77073101 | Oil : | 608438399.76 | Total : | 849185725.994
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4552.6643 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1552.5421 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1391.8075 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1257.8928 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1136.5866 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 917.1962 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 507.2091 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 236.004 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 707.4142 |  |  | 0 | 0%
Total | 0 |  | 12259.3168 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 9) Bhola 225 MW GT-2 & ST
2) Bibiyana #3
3) Ghorasal Unit-1,2,3,7
4) Ashuganj unit-3,4
5) Kaptai-1,2,5
6) Raozan #1,2
7) Sirajganj #2
8) Baghabari-71 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Mymensingh 132/33 kV T-1 transformer was switched on at 08:05.
b) Ghorashal 230 kV Bus section 3 & 4 tripped at 11:08 and Ghorashal-Ashuganj(S) 230 kV both Ckts |  |  |  |  | About 919 MW power interruption occurred under Mymensing zone,
tripped at 11:08 showing Dist. Z2 Ashuganj end and Ckt-2 was switched on at 14:59. |  |  |  |  | Ghorashal, Ashuganj, Shahjibazar, B.Baria, Srimongal & Joydevpur
c) Ghorashal-Bhulta 230 kV Ckts tripped at 11:08 from Bhulta end and was switched on at 13:19. |  |  |  |  | S/S areas from 11:08 to 13:37.
d) Ghorashal-Ishurdi 230 kV Ckt-1 tripped at 11:08 from both ends and was switched on at 13:37.
e) Ghorashal 230/132 kV OAT-12 transformer tripped at 11:08 and was switched on at 12:35.
f) Sreemangal-Fenchuganj 132 kV both Ckts tripped at 11:08 and was switched on at 11:51.
g) Mymensingh RPCL-Mymensingh S/S 132 kV both Ckts tripped at 11:08 and was switched on at 11:14.
h) Shahjibazar-Ashuganj 132 kV Ckt-3 tripped at 11:08 and was switched on at 11:32.
i)Ghorashal-Tongi 230 kV Ckts 1 & 2 tripped at 11:12 and were switched on at 16:21 & 21:10 respectively.
j) Ishurdi-Baghabari 230 kV both Ckts tripped at 11:37 and was switched on at 12:15.
At the same time Ashuganj 225 MW CCPP, EGCB 335, Jamalpur 200 MW,115 MW, 95 MW,Ashuganj Midland 51
150, TSK, Ghorashal unit-4,5, Regent, Dutch Bangla also tripped. Siddhirganj EGCB 335 MW GT & ST were
synchronized at 12:29 & 14:02 respectively.About 1564 MW generation shortfall occurred.
k) Madunaghat 132/33 kV T-2 transformer was under shut down from 10:45 to 12:20 for C/M.
l) Feni-Chowddagram 132 kV Ckt-1 was under shut down from 09:26 to 14:49.
m) Bhola 225 MW CCPP ST was synchronized at 13:26.
n) Haripur-Norsingdi 132 kV Ckt tripped at 15:55 from Haripur end showing Dist. C,Z1 at Haripur end and was
switched on at 16:31.
o) Ashuganj-Kishorganj 132 kV Ckt-2 was under shut down from 09:58 to 13:30 for C/M.
p) Ashuganj 225 MW CCPP GT and STG were synchronized at 15:17 and 18:52 respectively.
q) Ghorashal unit-7 CCPP GT was synchronized at 20:33.
r) Chandraghona-Madunaghat 132 kV Ckt-1 was under shut down from 20:24 to 08:26(10/9/2020) for R/H
maintenance work at Chandraghona end.
s) Payra unit-1 was synchronized at 22:21 and unit-2 was shut down at 05:17(10/9/2020).
t) Ashuganj-Ghorashal 132 kV Ckts 1 & 2 tripped at 05:23(10/9/2020) showing power swing at Ashuganj
end and AZ2 at Ghorashal end and Ckt-1 was switched on at 07:50.
u) Tongi 132/33 kV T-1 transformer was under shut down from 06:25(10/9/2020) to 07:50 for C/M.
v) Siddhirganj 335 MW ST and GT were shut down at 06:20(10/9/2020) and 06:31 respectively for R/H
maint. at Siddhirganj 230 kV S/S and GT was synchronized at
w) Kallyanpur 132/33 kV GT-1 transformer was under shut down from 06:30(10/9/2020) to 11:05 for C/M.
x) Siddhirganj 230 kV S/S-Siddhirganj 335 MW Ckt-1 was under shut down from 06:49(10/9/2020) to 09:46
for R/H maintenance work.
y) Khulna(C)-NWPGCL 132 kV Ckt-1 was under shut down from 07:11(10/9/2020) to 10:14 for C/M.
z) Ashuganj 225 MW CCPP GT was shut down at 07:23(10/9/2020) for Ashuganj 132 kV Bus-1 maint. work.
and was synchronized at 07:36.
aa) Naogaon-Niamatpur 132 kV Ckt tripped at 23:45 showing Dist. Z1 at Naogaon end and was switched |  |  |  |  | About 60 MW power interruption occurred under Niamatpur S/S area
on at 23:52. |  |  |  |  | from 23:45 to 23:52.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-09-09 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 1614000 | Grid fault
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 1323000 | Grid fault
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 40 | 361000 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 72 | 551936 | Engine problem
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 91 | 1654954 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 340 | 8411130 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 267 | 7148000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 8817250 | frequency control.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 7 | 197760 | Fuel Shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 125 | 3247098 | GT-1 Under S/D due to gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 96 | 2083344 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1032935
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 46 | 434046 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 401760
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 1924800
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 293 | 6091866 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 2120832 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel Shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 916560
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1613760
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 947108
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 913759
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1229100 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 771100
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 734400
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 552084
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 286 | 5512471 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 53 | 587885 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 25 | 297620 | Low demand
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 42 | 374391 | Low demand
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 131 | 3093120 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 103 | 1427940
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 432000 | Fuel Shortage
| Dhaka area Total |  |  |  | 5895 | 3210 | 66819009
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2900000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 346545
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 107055
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 642720
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 80 | 1881396 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4826656
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 140 | 2942487 | Gas shortage.
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 1142476
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 30 | 510360 | Low demand
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2263680
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 471552
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 36 | 577920
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 84 | 722880 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 31920
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 198 | 4586618 | Low demand
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 17 | 81963 | Low demand
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2425920
| Chattogram area Total |  |  |  | 2266 | 1307 | 26462148
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 1923456 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 190 | 3058000 | Gas shortage
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 270 | 7629200 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 250 | 7053000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 35 | 660168 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 42 | 455040 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 28 | 862276
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 133 | 1689454
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 467464
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 86 | 2042400
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 1525440
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 408000
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 219240
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 148 | 3742080
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 732600
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 780984 | Engine problem
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 412870
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 55872 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1216380
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 2536800
| Cumilla Area Total |  |  |  | 2980 | 1873 | 37671451
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 159 | 3191720 | Machine problem
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 459477
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 63 | 1448640 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10400
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 3916800
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1657200 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 559 | 10684237
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 91 | 2120000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 28 | 683640 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3517118
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 308 | 6243000
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1245000
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 49 | 1162368
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 174960
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 64 | 1374240 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1871040
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 184 | 4422980
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 416000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 523512
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7185500 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 244620
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1378 | 31183978
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 931 | 22361454
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 2154240
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 12 | 72000
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 200 | 3472320 | Low demand
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 345 | 8525952 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 510375
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 608640
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 70 | 688320 | Low demand
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Reserve
| Khulna Area Total |  |  |  | 2284 | 1797 | 38393301
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 80 | 1429440 | L/O
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 41 | 767552
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 87 | 1787674 | GT-2 Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 78 | 1707 | Engine problem
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 580 | 12998900
| Barisal Area Total |  |  |  | 1054 | 866 | 16985273
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 624000 | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 285316
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 34 | 195864 | Engine problem
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 43 | 283300 | Engine problem
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 145 | 3553200 | Gas shortage.
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 180 | 4393345 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 398 | 9206273 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 196030
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 494160
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 8 | 131544 | Engine problem
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 250182
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 34 | 382080 | Engine problem
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 96 | 678104 | Engine problem
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 100802 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 1400640
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 90 | 1987680 | Engine problem
| Rajshahi Area Total |  |  |  | 2183 | 1255 | 24162520
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3691500 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Machine problem
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 98 | 1960320 | Engine problem
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 30329
| Rangpur Area Total |  |  |  | 605 | 248 | 5682149
| Total |  |  |  | 19892 | 12493 | 258044066
| Eastern Grid Total |  |  |  | 13766 | 8327 | 172820823
| Western Grid Total |  |  |  | 6126 | 4166 | 85223243
| National Grid Total |  |  |  | 19892 | 12493 | 258044066
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-09-09
| (a) ENTIRE EASTERN GRID : |  | 8051 | MW | (b) ENTIRE WESTERN GRID : |  | 4001 | MW
| i) Dhaka area |  | 4074 | MW | i) Khulna area |  | 1557 | MW
| ii) Chittagong area |  | 1257 | MW | ii) Rajshahi area |  | 1329 | MW
| iii) Comilla area |  | 1179 | MW | iii) Barisal area |  | 372 | MW
| iv) Mymensingh area |  | 992 | MW | iv) Rangpur area |  | 743 | MW
| v) Sylhet area |  | 549 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 12052 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 124 | 12:00 | Sherpur | 112 | 23:00 | Jhenida | 116 | 19:00
| Munsiganj | 128 | 0:00 | Srimongal | 49 | 18:30 | Bottail | 140 | 19:00
| Sonargaon | 82 | 1:00 | Shahjibazar | 128 | 21:00 | G.K Project | 61 | 19:00
| Shyampur | 196 | 1:00 | Fenchuganj | 54 | 19:00 | Faridpur | 197 | 0.8125
| Bhulta | 197 | 22:00 | Kulawara | 49 | 19:00 | Madaripur | 104 | 0.91667
| Madanganj | 60 | 0:00 | Sylhet | 138 | 19:30 | Sariatpur | 66 | 21:00
| Shitalakhya | 115 | 16:00 | Chatak | 32 | 21:00 | Gopalganj | 97 | 20:00
| Rahim steel | 14 | 13:00 | Sunamganj | 51 | 20:00 | Bagerhat | 96 | 21:00
| Matuail | 80 | 10:00 | Biani Bazar | 65 | 21:00 | Mongla | 44 | 9:00
| Ghorasal | 81 | 20:00 | Comilla (S) | 180 | 18:30 | Satkhira | 114 | 0.91667
| Narsingdi | 168 | 20:00 | Comilla(N) | 113 | 22:00 | Gallamari | 50 | 13:00
| Haripur (SBU) | 107 | 17:00 | Chandpur | 110 | 22:00 | Magura | 56 | 0.83333
| Ullon | 60 | 18:30 | Feni | 127 | 19:30 | Norail | 41 | 20:00
| Hasnabad | 211 | 21:00 | Chowmuhani | 196 | 23:00 | Chuadanga | 91 | 19:30
| Magbazar | 109 | 13:00 | Ashuganj | 64 | 23:00 | Barisal(N) | 46 | 0.91667
| Maniknagar | 100 | 12:00 | Daudkandi | 145 | 21:00 | Barisal (S) | 104 | 0.91667
| Bangabhaban | 39 | 11:00 | B.Baria | 161 | 21:00 | Patuakhali | 132 | 0.875
| Narinda | 96 | 14:00 | Ramganj | 120 | 23:00 | Bhandaria | 56 | 0.91667
| Dhanmondi | 199 | 13:00 | Chaddagram | 38 | 19:00 | Borhan Uddin | 44 | 19:30
| Lalbag | 94 | 13:00 | PHP | 9 | 9:00 | Ishurdi | 62 | 20:00
| Madartek | 71 | 22:00 | Madunaghat | 68 | 15:00 | Ruppur Paromanobik | 2 | 21:00
| Dhaka University |  |  | Hathazari | 101 | 0.91667 | Natore | 129 | 21:00
| Fatullah | 40 | 0.41667 | Khulshi | 213 | 0.66667 | Bogra | 177 | 19:00
| Mirpur | 106 | 15:00 | Halishahar | 141 | 0.41667 | Noagaon | 131 | 21:00
| Kalyanpur | 114 | 19:30 | Baraulia | 150 | 0.041667 | Rajshahi | 154 | 22:00
| Gulshan | 140 | 13:00 | Sikalbaha | 28 | 0.77083 | Rajshahi New | 11 | 21:00
| Uttara | 84 | 13:00 | Dohazari | 84 | 0.83333 | C.Nawabganj | 75 | 21:00
| Uttara New | 32 | 14:00 | Cox'sbazar | 100 | 0.77083 | Amnura | 46 | 21:00
| Kamrangirchar | 97 | 13:00 | Chandraghona | 30 | 0.77083 | Pabna | 130 | 19:00
| Savar | 146 | 13:00 | Kaptai | 4.8 | 0.77083 | Shahjadpur | 111 | 19:30
| Bhasantec | 150 | 14:00 | A. Khaer Stl. | 0 | 0.041667 | Serajganj | 105 | 21:00
| Agargaon | 77 | 13:00 | Bakulia | 103 | 0.54167 | Niyamatpur | 60 | 21:00
| Satmosjid | 89 | 13:00 | Julda | 25 | 0.625 | Joypurhat | 56 | 21:00
| Tongi | 103 | 14:0 | TK chemical | 29 | 0.8125 | Sherpur(Bogura) | 48 | 19:00
| Kabirpur | 220 | 10:00 | Modern Steel | 12 | 0.125 | Mohastangor | 52 | 22:00
| Basundhara | 142 | 14:00 | Shahmirpur | 24 | 0 | Rangpur | 140 | 18:30
| Manikganj | 70 | 0.91667 | Khagrachhari | 26 | 0.625 | Lalmonirhat | 57 | 20:00
| Joydevpur | 145 | 15:00 | Matarbari | 33 | 0.041667 | Saidpur | 104 | 21:00
| New Tongi | 123 | 12:00 | Baroiar Hat | 52 | 0.625 | Purbasadipur | 100 | 21:00
| Korda | 251 | 21:00 | Rangamati | 12 | 0.77083 | Thakurgaon | 79 | 20:00
| Dhamrai | 88 | 22:00 | Abul Khair 230 | 146 | 0.45833 | Palashbari | 125 | 21:00
| Rajendrapur | 96 | 21:00 | BSRM | 106 | 0.29167 | Barapukuria | 49 | 21:00
| Valuka | 128 | 20:00 | GPH Ispat | 77 | 0.375 | Panchagar | 50 | 19:00
| Tangail | 208 | 20:00 | Goalpara | 24 | 0.79167 | Joldhaka | 28 | 19:30
| Mymensing | 165 | 21:00 | Central s/s | 93 | 19:00 | Kurigram | 60 | 19:00
| Kishorganj | 148 | 23:00 | Noapara | 58 | 19:00
| Netrokona | 113 | 22:00 | Jessore | 122 | 19:00
| Jamalpur | 143 | 21:00 | Benapol | 50 | 20:00
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-09-09 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 394 | 24:00 | 385 | 15:00 | Kaliakoir | 373 | 0.041667 | 362 | 0.45833
| Bheramara | 393 | 7:00 | 386 | 18:30 | Bhulta | 388 | 0.25 | 362 | 0.45833
| Ashuganj(N) | 393 | 1:00 | 373 | 12:00 | Gopalganj | 418 | 0.45833 | 396 | 0.79167
| Payra | 419 | 10:00 | 405 | 19:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 14:00 | 230 | 12:00 | Comilla (N) | 232 | 18:00 | 225 | 12:00
| Ishurdi | 234 | 22:00 | 223 | 12:00 | Hathazari | 226 | 19:00 | 218 | 10:00
| Ashuganj | 236 | 1:00 | 230 | 11:00 | Megnaghat | 230 | 1:00 | 222 | 12:00
| Serajganj | 230 | 3:00 | 225 | 20:00 | Fenchuganj | 238 | 6:00 | 233 | 11:00
| Baghabari | 241 | 6:00 | 235 | 19:30 | Siddhirganj | 228 | 1:00 | 214 | 12:00
| Barapukuria | 235 | 5:00 | 227 | 20:00 | Maniknagar | 227 | 1:00 | 213 | 12:00
| Bogra | 224 | 18:00 | 215 | 20:00 | Agargaon | 224 | 1:00 | 213 | 12:00
| Rajshahi | 224 | 6:00 | 214 | 21:00 | Barisal | 247 | 7:00 | 236 | 1:00
| Khulna South | 234 | 6:00 | 225 | 16:00 | AKSML | 224 | 19:00 | 214 | 11:00
| Rampura | 227 | 3:00 | 212 | 12:00 | BSRM | 224 | 18:00 | 216 | 9:00
| Haripur | 225 | 1:00 | 213 | 12:00 | Bibiyana | 235 | 1:00 | 229 | 10:00
| Hasnabad | 225 | 1:00 | 213 | 12:00 | Bhulta | 229 | 19:00 | 213 | 17:00
| Shyampur | 223 | 1:00 | 212 | 12:00 | Ashuganj (S) | 234 | 6:00 | 228 | 12:00
| Aminbazar | 225 | 1:00 | 215 | 12:00 | Kaliakoir | 228 | 1:00 | 219 | 12:00
| Tongi | 230 | 12:00 | 214 | 9:00 | GPH | 222 | 1:00 | 217 | 1:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 130 | 1:00 | 122 | 12:00 | Hathazari | 135 | 0.79167 | 130 | 0.29167
| Munsiganj | 130 | 1:00 | 124 | 12:00 | Khulshi | 134 | 0.79167 | 127 | 0.45833
| Sonargaon | 129 | 1:00 | 122 | 12:00 | Halishahar | 138 | 0.8125 | 128 | 0.45833
| Shyampur | 131 | 1:00 | 124 | 12:00 | Baraulia | 134 | 0.79167 | 128 | 0.375
| Bhulta | 123 | 18:00 | 117 | 12:00 | Sikalbaha | 137 | 19:00 | 131 | 0.29167
| Madanganj | 134 | 1:00 | 127 | 8:00 | Dohazari | 135 | 19:00 | 127 | 0.375
| Shitalakhya | 139 | 1:00 | 130 | 12:00 | Cox'sbazar | 130 | 0.5 | 116 | 0.041667
| Rahim steal | 130 | 1:00 | 122 | 12:00 | Chandraghona | 135 | 0.79167 | 130 | 0.125
| Matuail | 130 | 1:00 | 122 | 12:00 | Kaptai | 135 | 19:00 | 130 | 0.375
| Ghorasal | 136 | 1:00 | 132 | 13:00 | A. Khaer Stl. | 133 | 0.83333 | 128 | 9:00
| Narsinghdi | 126 | 16:00 | 116 | 12:00 | Bakulia | 136 | 0.79167 | 129 | 0.29167
| Haripur (SBU) | 131 | 6:00 | 123 | 12:00 | Julda | 137 | 0.79167 | 130 | 0.45833
| Ullon | 132 | 3:00 | 121 | 12:00 | TK Chemical | 136 | 0.79167 | 132 | 1:00
| Hasnabad | 135 | 1:00 | 127 | 12:00 | Modern Steel | 135 | 0.77083 | 130 | 0.125
| Magbazar | 132 | 4:00 | 120 | 12:00 | Shahmirpur | 136 | 0.8125 | 130 | 0.41667
| Maniknagar | 132 | 1:00 | 123 | 12:00 | Khagrachhari | 133 | 0.625 | 129 | 0.375
| Bangabhaban | 132 | 1:00 | 123 | 12:00 | Matarbari | 130 | 0.5 | 120 | 0.041667
| Narinda | 132 | 1:00 | 123 | 12:00 | Baroiar Hat | 134 | 0.5 | 126 | 0.041667
| Dhanmondi | 132 | 3:00 | 121 | 12:00 | Rangamati | 134 | 0.79167 | 129 | 10:00
| Lalbag | 135 | 21:00 | 122 | 12:00 | Goalpara S/S | 135 | 6:00 | 130 | 16:00
| Madartek | 131 | 1:00 | 120 | 12:00 | Khulna Central S/S | 135 | 0.25 | 130 | 21:00
| Dhaka University |  |  |  |  | Noapara | 133 | 6:00 | 127 | 16:00
| Fatuiiah | 133 | 0.16667 | 124 | 12:00 | Jessore | 128 | 6:00 | 120 | 19:30
| Mirpur | 129 | 3:00 | 122 | 12:00 | Benapol | 129 | 10:00 | 120 | 20:00
| Kalyanpur | 130 | 1:00 | 125 | 9:00 | Jhenida | 126 | 0.375 | 111 | 21:00
| Gulshan | 131 | 6:00 | 120 | 12:00 | Bottail | 132 | 9:00 | 124 | 19:30
| Uttara | 129 | 1:00 | 122 | 12:00 | G.K Project | 138 | 0.20833 | 134 | 20:00
| Uttara New | 135 | 13:00 | 127 | 8:00 | Faridpur | 133 | 6:00 | 125 | 21:00
| Kamrangirchar | 133 | 21:00 | 121 | 12:00 | Madaripur | 140 | 0.29167 | 130 | 18:30
| Savar | 130 | 5:00 | 122 | 12:00 | Shariyatpur S/S | 139 | 0.29167 | 128 | 19:00
| Bhasantec | 130 | 1:00 | 122 | 12:00 | Gopalganj | 137 | 6:00 | 124 | 19:00
| Agargaon | 131 | 1:00 | 124 | 12:00 | Bagerhat | 129 | 9:00 | 121 | 19:30
| Satmosjid | 131 | 1:00 | 123 | 12:00 | Mongla | 125 | 0.16667 | 119 | 12:00
| Tongi | 137 | 0.5 | 132 | 18:00 | Satkhira | 133 | 0.25 | 125 | 21:00
| Kabirpur | 133 | 2:00 | 128 | 21:00 | Gallamari | 135 | 6:00 | 130 | 16:00
| Basundhara | 131 | 3:00 | 120 | 12:00 | Magura | 126 | 9:00 | 110 | 19:00
| Manikganj | 142 | 13:00 | 133 | 6:00 | Norail | 125 | 0.29167 | 107 | 22:00
| Joydevpur | 140 | 24:00 | 124 | 12:00 | Chuadanga | 121 | 6:00 | 101 | 20:00
| New Tongi | 136 | 1904-01-02 | 127 | 8:00 | Barisal(N) | 141 | 7:00 | 133 | 1:00
| Kodda | 141 | 13:00 | 121 | 0.33333 | Barisal (S) | 138 | 0.25 | 132 | 19:00
| Dhamrai | 132 | 1800 | 127 | 21:00 | Patuakhali(S) | 134 | 0.29167 | 125 | 1:00
| Rajendrapur | 136 | 12:00 | 122 | 8:00 | Bhandaria | 127 | 6:00 | 116 | 20:00
| Valuka | 127 | 7:00 | 111 | 21:00 | Ishurdi | 137 | 18:00 | 132 | 21:00
| Tangail | 133 | 6:00 | 125 | 19:30 | Ruppur Paromanobik | 136 | 6:00 | 130 | 21:00
| Mymensing | 131 | 7:00 | 116 | 21:00 | Natore | 135 | 18:00 | 128 | 21:00
| Kishorganj | 131 | 7:00 | 116 | 13:00 | Bogra | 136 | 18:00 | 128 | 21:00
| Netrokona | 128 | 7:00 | 112 | 21:00 | Noagaon | 131 | 18:00 | 120 | 21:0
| Jamalpur | 138 | 15:00 | 123 | 12:00 | Rajshahi | 135 | 18:00 | 129 | 21:00
| Sherpur | 138 | 17:00 | 122 | 12:00 | Rajshahi New | 136 | 18:00 | 130 | 21:00
| Srimongal | 136 | 6:00 | 131 | 0.875 | C.Nawabganj | 134 | 18:00 | 127 | 21:00
| Shahjibazar | 135 | 6:00 | 125 | 0.5 | Amnura | 134 | 18:00 | 126 | 3:00
| Fenchuganj | 136 | 6:00 | 132 | 0.8125 | Pabna | 134 | 6:00 | 127 | 21:00
| Khulawara | 134 | 6:00 | 131 | 0.5 | Shahjadpur | 137 | 18:00 | 131 | 21:00
| Sylhet | 133 | 9:00 | 130 | 0.77083 | Serajganj | 133 | 7:00 | 126 | 21:00
| Chatak | 131 | 6:00 | 128 | 19:00 | Niyamatpur | 130 | 7:00 | 117 | 21:00
| Sunamganj | 130 | 5:00 | 125 | 0.83333 | Joypurhat | 131 | 18:00 | 117 | 21:00
| Biani Bazar | 131 | 6:00 | 126 | 0.75 | Sherpur(Bogura) | 134 | 18:00 | 127 | 21:00
| Comilla(s) | 125 | 6:00 | 119 | 18:30 | Mohastangor | 133 | 18:00 | 125 | 21:00
| Comilla(n) | 136 | 18:30 | 131 | 12:00 | Rangpur | 129 | 15:00 | 117 | 19:00
| Chandpur | 137 | 15:00 | 126 | 10:00 | Lalmonirhat | 128 | 15:00 | 115 | 20:00
| Feni | 137 | 14:00 | 127 | 11:00 | Saidpur | 130 | 7:00 | 120 | 20:00
| Chowmuhani | 130 | 12:00 | 123 | 9:00 | Purbasadipur | 127 | 17:00 | 114 | 20:00
| Ashuganj | 135 | 7:00 | 125 | 13:00 | Thakurgaon | 127 | 6:00 | 112 | 20:00
| Daudkandi | 129 | 18:00 | 123 | 12:00 | Palashbari | 129 | 15:00 | 120 | 20:00
| B.Baria | 132 | 10:00 | 125 | 19:00 | Barapukuria | 135 | 6:00 | 127 | 20:00
| Ramganj | 130 | 19:30 | 122 | 18:00 | Panchagar | 128 | 6:00 | 111 | 20:00
| Chaddagram | 135 | 19:30 | 127 | 10:00 | Joldhaka | 130 | 6:00 | 115 | 20:00
| PHP | 133 | 20:00 | 125 | 10:00 | Kurigram | 126 | 15:00 | 112 | 19:00
| Madanhat | 137 | 19:00 | 132 | 6:00

## L-Curve
Date | 2020-09-09
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 189 | 7925 | 4117 | 12042 |  |  |  | QF-LDC-11
0:30 | 169.5 | 7662.5 | 3979 | 11641.5 | Date: | 2020-09-09
1:00 | 150 | 7400 | 3841 | 11241
1:30 | 131.5 | 7298.5 | 3752 | 11050.5
2:00 | 113 | 7197 | 3663 | 10860
2:30 | 156.5 | 7107 | 3654 | 10761 | [5 empty] | Gen. at Eve. Peak | 12493 | 12493 MW (21:00 )
3:00 | 200 | 7017 | 3645 | 10662 | [6 empty] | 21:00
3:30 | 202.5 | 6944.5 | 3648 | 10592.5 | [5 empty] | Gen. at Day Peak | 10370 | 10370 MW (11:00 )
4:00 | 205 | 6872 | 3651 | 10523 | [6 empty] | 11:00
4:30 | 248.5 | 6821.5 | 3592 | 10413.5 | [5 empty] | Highest Generation | 12493
5:00 | 292 | 6771 | 3533 | 10304 | [6 empty] | 21:00
5:30 | 311 | 6544.5 | 3432 | 9976.5
6:00 | 330 | 6318 | 3331 | 9649
6:30 | 335 | 6155.5 | 3230 | 9385.5
7:00 | 340 | 5993 | 3129 | 9122
7:30 | 331.5 | 6020 | 3122 | 9142
8:00 | 323 | 6047 | 3115 | 9162
8:30 | 305.5 | 6273 | 3131.5 | 9404.5
9:00 | 288 | 6499 | 3148 | 9647
9:30 | 284.5 | 6720 | 3120 | 9840
10:00 | 281 | 6941 | 3092 | 10033
10:30 | 330.5 | 7030 | 3171.5 | 10201.5
11:00 | 380 | 7119 | 3251 | 10370
11:30 | 310 | 6475.5 | 3211 | 9686.5
12:00 | 240 | 5832 | 3171 | 9003
12:30 | 160 | 6418.5 | 3217.5 | 9636
13:00 | 80 | 7005 | 3264 | 10269
13:30 | 62.5 | 7215 | 3261.5 | 10476.5
14:00 | 45 | 7425 | 3259 | 10684
14:30 | 71 | 7456.5 | 3272 | 10728.5
15:00 | 97 | 7488 | 3285 | 10773
15:30 | 53.5 | 7350 | 3176 | 10526
16:00 | 10 | 7212 | 3067 | 10279
16:30 | 72.5 | 7167.5 | 3013 | 10180.5
17:00 | 135 | 7123 | 2959 | 10082
17:30 | 109 | 7011.5 | 2937 | 9948.5
18:00 | 83 | 6900 | 2915 | 9815
18:30 | 91.5 | 7442 | 3566 | 11008
19:00 | 100 | 7984 | 4217 | 12201
19:30 | 1 | 8221 | 4226 | 12447
20:00 | 60 | 8241 | 4197 | 12438 |  |  |  | Executive Engineer
20:30 | 51 | 8284 | 4181.5 | 12465.5 |  |  |  | Network Operation Division
21:00 | 42 | 8327 | 4166 | 12493
21:30 | 56 | 8252 | 4205 | 12457
22:00 | 70 | 8177 | 4244 | 12421 |  |  |  |  | Page 6 of 7
22:30 | 98 | 8144 | 4210 | 12354
23:00 | 126 | 8111 | 4176 | 12287
23:30 | 157.5 | 8018 | 4146.5 | 12164.5
24:00 | 189 | 7925 | 4117 | 12042
12493 MW (21:00 )
10370 MW (11:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-09-09 |  | Energy | 258044066
[10 empty] | 2020-09-09 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3849 | 931 | 2048 | 3540 | 680 | 78 | 739 | 0 | 164
0:30 | 4070 | 932.5 | 2009.5 | 3129.5 | 695 | 78.5 | 552 | 0 | 168 | Date: | 2020-09-09
1:00 | 4291 | 934 | 1971 | 2719 | 710 | 79 | 365 | 0 | 172
1:30 | 4304 | 934.5 | 2010.5 | 2582.5 | 710 | 79 | 259 | 0 | 171 | [7 empty] | Total Energy | 258.0441 | Total Energy Gen 258.044 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 258.044 MKWHr
2:00 | 4317 | 935 | 2050 | 2446 | 710 | 79 | 153 | 0 | 170 | [7 empty] | Energy not Served | 0
2:30 | 4299 | 934.5 | 2066 | 2351.5 | 710 | 79 | 153 | 0 | 168 | [7 empty] | Energy Requirement | 258.0441
3:00 | 4281 | 934 | 2082 | 2257 | 710 | 79 | 153 | 0 | 166
3:30 | 4286.5 | 934 | 2065.5 | 2200 | 710 | 78.5 | 153 | 0 | 165 | [6 empty] | Shortage
4:00 | 4292 | 934 | 2049 | 2143 | 710 | 78 | 153 | 0 | 164
4:30 | 4291.5 | 934 | 2056 | 2040 | 700 | 78 | 153 | 0 | 161
5:00 | 4291 | 934 | 2063 | 1937 | 690 | 78 | 153 | 0 | 158
5:30 | 4242.5 | 934 | 2024 | 1719.5 | 680 | 77.5 | 145 | 0 | 153
6:00 | 4194 | 934 | 1985 | 1502 | 670 | 77 | 137 | 0 | 148
6:30 | 4141.5 | 934.5 | 1949 | 1339 | 670 | 77 | 128.5 | 0 | 143 |  |  |  |  | Coal
7:00 | 4089 | 935 | 1913 | 1176 | 670 | 77 | 120 | 0 | 138
7:30 | 4119.5 | 934.5 | 1915 | 1158.5 | 670 | 77 | 120 | 0 | 138 |  |  |  | Oil |  |  |  | ,
8:00 | 4150 | 934 | 1917 | 1141 | 670 | 77 | 120 | 0 | 138
8:30 | 4190.5 | 933 | 1989 | 1315.5 | 625 | 77 | 120 | 0 | 136
9:00 | 4231 | 932 | 2061 | 1490 | 580 | 77 | 120 | 0 | 134
9:30 | 4233.5 | 931.5 | 2046.5 | 1758.5 | 520 | 77 | 120 | 0 | 138
10:00 | 4236 | 931 | 2032 | 2027 | 460 | 77 | 120 | 0 | 142
10:30 | 4199 | 931 | 2038.5 | 2158 | 520.5 | 77 | 120 | 0 | 144
11:00 | 4162 | 931 | 2045 | 2289 | 581 | 77 | 120 | 0 | 146
11:30 | 3614.5 | 930 | 1951 | 2231 | 585.5 | 78 | 120 | 0 | 151
12:00 | 3067 | 929 | 1857 | 2173 | 590 | 79 | 120 | 0 | 156
12:30 | 3123 | 929 | 1887.5 | 2673 | 610 | 79 | 149 | 0 | 154
13:00 | 3179 | 929 | 1918 | 3173 | 630 | 79 | 178 | 0 | 152
13:30 | 3179 | 929 | 1918 | 3173 | 630 | 79 | 178 | 0 | 152
14:00 | 3179 | 929 | 1918 | 3173 | 630 | 79 | 178 | 0 | 152
14:30 | 3321.5 | 929.5 | 1892 | 3224 | 615 | 79.5 | 281.5 | 0 | 155
15:00 | 3464 | 930 | 1866 | 3275 | 600 | 80 | 385 | 0 | 158
15:30 | 3565 | 930 | 1864 | 2932.5 | 600 | 80 | 386.5 | 0 | 156
16:00 | 3666 | 930 | 1862 | 2590 | 600 | 80 | 388 | 0 | 154
16:30 | 3629 | 930 | 1903 | 2497 | 600 | 80 | 388 | 0 | 148
17:00 | 3592 | 930 | 1944 | 2404 | 600 | 80 | 388 | 0 | 142
17:30 | 3531 | 930 | 1853 | 2405 | 580 | 80 | 426.5 | 0 | 142
18:00 | 3470 | 930 | 1762 | 2406 | 560 | 80 | 465 | 0 | 142
18:30 | 3667.5 | 930 | 1951.5 | 2988 | 620 | 80 | 619 | 0 | 152
19:00 | 3865 | 930 | 2141 | 3570 | 680 | 80 | 773 | 0 | 162
19:30 | 3874 | 932 | 2155 | 3756 | 710 | 80 | 776 | 0 | 164
20:00 | 3983 | 932 | 2150 | 3660 | 720 | 80 | 761 | 0 | 152
20:30 | 3977.5 | 931.5 | 2155 | 3681.5 | 725 | 80 | 765 | 0 | 150
21:00 | 3972 | 931 | 2160 | 3703 | 730 | 80 | 769 | 0 | 148
21:30 | 3975.5 | 931.5 | 2164 | 3639 | 735 | 79 | 781 | 0 | 152
22:00 | 3979 | 932 | 2168 | 3575 | 740 | 78 | 793 | 0 | 156
22:30 | 3962 | 931.5 | 2164 | 3557.5 | 710 | 78 | 793 | 0 | 158
23:00 | 3945 | 931 | 2160 | 3540 | 680 | 78 | 793 | 0 | 160
23:30 | 3897 | 931 | 2104 | 3540 | 680 | 78 | 766 | 0 | 162 | Max Temp. in Dhaka |  | 34.1° C
24:00 | 3849 | 931 | 2048 | 3540 | 680 | 78 | 739 | 0 | 164
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 258.044 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 258.044 MKWHr
Note on W13: Author:

## Generation
g | 2020-09-09
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 44 | 44 | 44 | 43 | 43 | 42 | 42 | 42 | 42 | 42 | 42 | 44 | 44 | 44 | 45 | 45 | 45 | 45 |  | 45 | 45 | 45 | 45 | 43 | 43 | 43 | 1033396
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 848000
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2900000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [10 empty] | 13 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 346545
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 4 | 11 | 16 |  | 8 | 19 | 20 | 18 | 10 | 6 | 1 | 0 | [8 empty] | 107055
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 204 | 204 | 204 | 204 | 203 | 204 | 210 | 206 | 215 | 209 | 204 | 205 | 164 | 204 | 203 | 204 | 204 |  | 204 | 204 | 204 | 204 | 205 | 193 | 177 | 4826656
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 100 | 106 | 104 | 104 | 103 | 103 | 104 | 104 | 105 | 139 | 140 | 139 | 139 | 145 | 145 | 147 | 147 | 79 |  | 139 | 139 | 139 | 140 | 139 | 110 | 103 | 2942487
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 66 | 33 | 33 | 33 | 33 | 17 | [6 empty] | 3 | 64 | 65 | 68 | 68 | 71 |  | 102 | 101 | 88 | 102 | 101 | 102 | 102 | 1142476
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
| Daudkandi 200 MW PP (B.Trac) | [19 empty] | 50 | 50 | [5 empty] | 55872
14 | Titas 50 MW Peaking PP | [14 empty] | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 467464
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 300 | 310 | 296 | 288 | 296 | 276 | 292 | 306 | 307 | 306 | 305 |  | 26 | 26 | 165 | 294 | 280 | 300 |  | 278 | 280 | 301 | 293 | 297 | 296 | 270 | 6091866
18 | Kodda 300 MW PP Unit-2 (Summit) | 283 | 286 | 275 | 215 | 143 | 95 | 45 | 45 | 58 | 175 | 222 | 248 | 262 | 286 | 283 | 286 | 281 | 286 |  | 283 | 283 | 283 | 286 | 283 | 283 | 286 | 5512471
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 141 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 160 | 160 | 157 | [15 empty] | 1614000
23 | Ghorasal TPP Unit-5 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | [15 empty] | 1323000
24
25 | Ghorasal 365 MW CCPP Unit-7 | [22 empty] | 40 | 120 | 120 | 120 | 361000
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1923456
32 | Ashuganj 50 MW PP | 35 | 35 | 35 | 35 | 35 | 35 | 31 | 31 | 35 | 35 | 35 |  |  | 10 | 23 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 25 | 25 | 660168
33 | Ashuganj 225 MW CCPP | 173 | 161 | 158 | 162 | 164 | 175 | 215 | 213 | 213 | 212 | 211 |  |  |  |  | 26 | 42 | 48 |  | 73 | 116 | 204 | 190 | 158 | 144 | 170 | 3058000
34 | Ashuganj 450 MW CCPP(South) | 280 | 300 | 275 | 275 | 275 | 250 | 250 | 270 | 325 | 290 | 270 | 340 | 340 | 340 | 340 | 340 | 265 | 265 |  | 280 | 280 | 280 | 250 | 250 | 270 | 255 | 7053000
| Ashuganj 450 MW CCPP(North) | 360 | 360 | 360 | 360 | 360 | 360 | 260 | 275 | 280 | 285 | 265 | 260 | 260 | 320 | 320 | 320 | 270 | 270 |  | 290 | 290 | 290 | 270 | 270 | 280 | 260 | 7629200
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 0 | 30 | 47 | 46 | 42 | 42 |  | 42 | 42 | 42 | 42 | 25 | 5 | 5 | 455040
36 | Chandpur 150 MW CCPP | 86 | 87 | 98 | 97 | 97 | 86 | 88 | 96 | 90 | 97 | 90 | 87 | 87 | 88 | 82 | 86 | 82 | 90 |  | 80 | 80 | 84 | 86 | 80 | 75 | 75 | 2042400
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 339 | 348 | 345 | 341 | 341 | 339 | 341 | 353 | 368 | 359 | 347 | 356 | 347 | 345 | 340 | 339 | 340 | 323 |  | 336 | 340 | 339 | 340 | 347 | 369 | 343 | 8411130
40 | Meghnaghat 450 MW CCPP(MPL) | 340 | 380 | 380 | 380 | 380 | 380 | 350 | 350 | 420 | 420 | 420 | 420 | 420 | 380 | 380 | 380 | 380 | 300 |  | 420 | 420 | 420 | 420 | 420 | 420 | 340 | 8817250
41 | Haripur 360MW CCPP(HPL) | 333 | 333 | 334 | 334 | 332 | 304 | 304 | 304 | 303 | 282 | 277 | 312 | 314 | 300 | 303 | 283 | 283 | 283 |  | 277 | 278 | 267 | 267 | 257 | 257 | 303 | 7148000
42 | RPCL 210MW CCPP | 158 | 159 | 159 | 159 | 159 | 161 | 160 | 156 | 156 | 154 | 154 | 76 | 54 | 71 | 54 | 105 | 116 | 156 |  | 157 | 157 | 156 | 159 | 156 | 154 | 159 | 3191720
43
44 | Fenchugonj CCPP Phase-1 | 90 | 90 | 90 | 90 | 90 | 90 | 91 | 90 | 91 | 91 | 91 | 91 | 91 | 90 | 89 | 89 | 88 | 91 |  | 91 | 91 | 88 | 91 | 89 | 90 | 91 | 2120000
45 | Fenchugonj CCPP Phase-2 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 30 | 28 | 30 | 28 | 30 | 28 | 29 | 29 | 29 | 29 | 30 |  | 28 | 28 | 28 | 28 | 30 | 28 | 30 | 683640
46 | Shajibazar 330 MW CCPP | 300 | 294 | 298 | 298 | 296 | 296 | 298 | 296 | 295 | 296 | 300 | 160 | 232 | 235 | 237 | 239 | 245 | 276 |  | 271 | 295 | 295 | 308 | 260 | 259 | 260 | 6243000
47 | Shahjibazar GTPP Unit- 8 & 9 | 64 | 63 | 64 | 64 | 64 | 64 | 64 | 63 | 63 | 63 | 63 | 66 | 66 | 65 | 62 | 61 | 61 | 40 |  | 65 | 63 | 63 | 64 | 63 | 63 | 63 | 1374240
48 | Shahjibazar 86MW PP (Shahjibazar) | 85 | 85 | 85 | 85 | 85 | 85 | 83 | 83 | 83 | 83 | 83 | 30 | 83 | 83 | 80 | 85 | 85 | 30 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1871040
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 185 | 184 | 184 | 184 | 184 | 184 | 183 | 185 | 185 | 186 | 186 | 186 | 185 | 185 | 185 | 185 | 185 | 151 |  | 185 | 185 | 185 | 184 | 185 | 184 | 185 | 4422980
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 416000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 9 | 10 | 10 | 10 | 10 | 10 | 244620
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 5 | 5 | 5 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 174960
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 52 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1245000
56 | Shahjahanulla 25 MW PP | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 16 | 16 | 16 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 523512
57 | Bibiana-II 341 MW CCPP (Summit) | 265 | 275 | 300 | 285 | 290 | 270 | 290 | 300 | 305 | 300 | 310 | 300 | 290 | 290 | 270 | 280 | 290 | 280 |  | 300 | 290 | 280 | 290 | 300 | 300 | 280 | 7185500
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 55 | 17 | 17 | 17 |  |  |  |  | 17 | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 913759
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 20 | 18 | 18 | 18 | 18 | 20 |  | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 471552
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 |  | 19 |  | 19 | 19 | 19 | 19 |  | 19 | 22 | 22 | 22 | 22 | 22 | 22 | 401760
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 459477
63 | Impoprt (Tripura) | 172 | 170 | 166 | 164 | 158 | 148 | 138 | 138 | 134 | 142 | 146 | 156 | 152 | 164 | 158 | 154 | 142 | 142 |  | 162 | 164 | 152 | 148 | 156 | 160 | 164 | 3742080
64 | Malancha, Ctg. EPZ (United) | 36 | 41 | 42 | 38 | 40 | 41 | 35 | 8 | 5 | 6 | 5 | 5 | 8 | 2 | 10 | 8 | 17 | 13 |  | 24 | 26 | 30 | 36 | 39 | 42 | 42 | 577920
65 | Feni 22MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 16 | 16 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 408000
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 5 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 219240
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 732600
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 10 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 15 | 15 | 15 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 412870
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 23 | 29 | 29 | 24 | 24 | 24 | 10 | 26 | 28 | 28 | 24 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 629100
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 |  |  | 0 |  | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 771100
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 25 | 25 | 25 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 734400
73 | Ghorashal 108MW PP (Regent) | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 |  |  |  | 11 | 53 | 82 | 86 |  | 89 | 92 | 92 | 91 | 91 | 92 | 92 | 1654954
| Feni Lanka Power | 17 | 17 | [9 empty] | 114 | 114 | 114 | 114 | 17 | 17 | 17 |  | 114 | 114 | 114 | 114 | 101 | 101 | 101 | 1216380
| Chowmuhani 113 MW | 113 | 113 | 108 | 113 | 113 | 113 | 75 | 75 | 86 | 113 | 110 | 105 | 111 | 111 | 113 | 113 | 113 | 113 |  | 70 | 113 | 99 | 113 | 113 | 113 | 109 | 2536800
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 91 | 91 | 95 | 100 | 100 | 90 | 50 | 50 | 55 | 80 | 91 | 14 | 45 | 70 | 80 | 91 | 50 | 50 |  | 80 | 100 | 100 | 100 | 100 | 100 | 100 | 1924800
78 | Gazipur 52 MW PP | [12 empty] | 42 | 51 | 51 | 51 | 25 | 25 |  | 47 | 51 | 51 | 51 | 51 | 51 | 51 | 552084
79 | Kodda 150MW PP | 16 | [11 empty] | 55 | 100 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 1613760
80 | Jamalpur 95 MW PP(Powerpac) | 72 | 72 | 72 | 72 | 72 | 48 | 48 | 48 | 48 | 48 | 56 | 8 | 64 | 64 | 64 | 64 | 63 | 63 |  | 63 | 63 | 63 | 63 | 63 | 71 | 71 | 1448640
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 43 | 25 |  |  |  | 1 | 16 | 25 | 25 | 34 | 43 | 43 | 43 | 24 | 24 |  | 40 | 43 | 43 | 43 | 43 | 43 | 43 | 780984
| Gazipur 100 MW PP | 34 | [7 empty] | 4 | 50 | 50 | 53 | 88 | 93 | 104 | 88 | 95 | 105 |  | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 1427940
| Kaptai 7 MW Solar PP | [5 empty] | 1 | 0 | 2 | 4 | 5 | 5 | 5 | 4 | 4 | 1 | 0 | 0 | [9 empty] | 31920
| Jodiac Power | [26 empty] | 0
| Karnaphuli Power Ltd. | [19 empty] | 8 | 17 | 17 | 17 | 17 |  |  | 81963
82 | Madanganj 102 PP(Summit) | 96 | 96 | 96 | 64 | 64 | 48 | 48 | 48 | 48 | 78 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 |  | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 2083344
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 25 | [11 empty] | 7 | 26 | 24 | 24 | 26 | 24 |  | 26 | 24 | 24 | 46 | 100 | 33 | 25 | 434046
86 | Meghnaghat CCPP(Summit) | 123 | 142 | 128 | 130 | 138 | 138 | 140 | 142 | 140 | 140 | 125 | 140 | 120 | 135 | 140 | 130 | 130 | 140 |  | 120 | 130 | 138 | 125 | 138 | 130 | 120 | 3247098
87 | Meghnaghat 100 MW(IEL) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 197760
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 432000
88 | Ghorashal 78.5 MW PP(MAX) | [16 empty] | 60 | 40 |  | 60 | 72 | 72 | 72 | 72 | 71 | 72 | 551936
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [11 empty] | 46 | 100 | 100 | 100 |  |  | 10 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 510360
92 | Fenchuganj 44MW (Energyprima) | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 47 | 47 | 47 | 47 | 47 | 47 | 48 |  | 48 | 48 | 48 | 49 | 49 | 49 | 49 | 1162368
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 40 | 40 | 40 | 35 | 35 | 43 | 3 | 25 | 25 | 25 | 25 | 34 | 28 |  | 29 | 29 | 27 | 28 | 38 | 43 | 51 | 862276
94 | Gagnagar 102 MW PP (Digital Power) | 93 | 93 | 93 | 93 | 93 | 48 | 48 | 48 | 64 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 |  | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 2120832
95 | Patenga 50MW PP (Baraka) | 19 | [7 empty] | 7 | 12 | 12 | 26 | 50 | 50 | 50 | 50 | 18 | 18 |  | 47 | 50 | 50 | 50 | 50 | 50 | 50 | 642720
96 | Chattogram 108 MW PP (ECPV) | 12 | [7 empty] | 2 | 10 | 10 | 14 | 11 | 11 | 12 | 33 | 50 | 50 |  | 74 | 84 | 84 | 84 | 84 | 84 | 84 | 722880
97 | Katpotti 52 MW PP (Sinha)
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 40 | 40 | 40 | 25 | 25 | 25 | 35 | 40 | 40 | 40 | 40 | 40 | 30 | 25 | 25 | 25 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1032935
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 17 | [6 empty] | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 947108
101 | Kushiara 163 MW CCPP (KP) | 110 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 130 | 110 |  | 163 | 163 | 163 | 163 | 163 | 163 | 130 | 3517118
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 1 | 2 | 3 | 1 | 3 | 1 | 1 | 0 | [9 empty] | 10400
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 17 | [5 empty] | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 17 | 17 | 17 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 916560
104 | Keranigonj 300 MW PP (APR) | [12 empty] | 168 | 155 | [5 empty] | 107 | 107 | 56 | 53 |  |  |  | 587885
105 | Bramhangoan 100 MW PP (Aggreko) | [12 empty] | 95 | 95 | 40 |  |  |  |  | 25 | 25 | 25 | 25 |  |  |  | 297620
106 | Mymensingh 200 MW PP (United) | 155 | 155 | 155 | 155 | 155 | 155 | 120 | 120 | 120 | 144 | 165 | 45 | 180 | 183 | 183 | 192 | 191 | 192 |  | 193 | 193 | 193 | 200 | 200 | 200 | 200 | 3916800
112 | Aurahati 100MW PP (Aggreko) | [12 empty] | 100 | 102 | 42 |  |  |  |  | 42 | 42 | 43 | 42 |  |  |  | 374391
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 117 | 115 | 115 | 115 | 113 | 102 | 100 | 103 | 127 | 127 | 122 | 149 | 149 | 148 | 131 | 129 | 127 |  | 122 | 122 | 131 | 131 | 148 | 149 | 149 | 3093120
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 50 | 100 | 90 | 90 | 90 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2263680
116 | Chandpur 200MW (Desh energy) | [11 empty] | 1 | 80 | 191 | 199 | 16 |  |  |  | 61 | 113 | 166 | 200 | 102 | 140 | 101 | 1525440
117 | Ashuganj 150MW PP (Midland) | 125 | 10 | [6 empty] | 3 | 33 | 78 |  | 15 | 86 | 112 | 113 | 118 | 123 |  | 130 | 130 | 128 | 133 | 130 | 123 | 125 | 1689454
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 35 | 35 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 21 | 53 | 28 | 107 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 1657200
| Anwara 300 MW PP (United) | 215 | 215 | 215 | 215 | 215 | 161 | 106 | 106 | 170 | 197 | 197 | 198 | 197 | 197 | 197 | 197 | 197 | 143 |  | 195 | 198 | 198 | 198 | 198 | 215 | 233 | 4586618
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2425920
120 | Eastern Zone Total | 7400 | 7197 | 7017 | 6872 | 6771 | 6318 | 5993 | 6047 | 6499 | 6941 | 7119 | 5832 | 7005 | 7425 | 7488 | 7212 | 7123 | 6900 |  | 7984 | 8221 | 8241 | 8327 | 8177 | 8111 | 7925 | 172820823
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 115 | 115 | 115 | 115 | 104 | 115 | 69 |  | 23 | 99 | 99 | 99 | 99 | 99 | 99 | 61 | 32 | 32 |  | 115 | 115 | 115 | 99 | 115 | 115 | 115 | 2154240
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [17 empty] | 4 |  | 19 | 18 | 12 | 12 | 12 | 11 | 12 | 72000
| Khulna 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 135 |  | 195 | 200 | 200 | 200 | 225 | 225 | 215 | 3472320
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | 35 | 35 | 35 | 17 |  |  | 35 | 35 | [10 empty] | 70 | 70 | 70 | 70 | 70 | 70 | 90 | 688320
130
131
132
133
| Barisal 110 MW PP (Summit ) | 64 | 64 | 64 | 64 | 64 | 32 | 32 | 16 | 64 | 64 | 64 | 64 | 64 | 48 | 48 | 16 | 16 | 16 |  | 80 | 80 | 80 | 80 | 80 | 80 | 110 | 1429440
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 77 | 76 | 79 | 78 | 78 | 78 | 79 | 78 | 77 | 76 | 77 | 77 | 77 | 43 | 43 | 44 | 43 | 43 |  | 78 | 78 | 78 | 78 | 77 | 77 | 77 | 1707
| Bhola 225 MW CCPP | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 15 | 15 | 15 | 15 | 15 | 85 | 87 | 87 | 87 | 88 |  | 88 | 88 | 88 | 87 | 87 | 87 | 87 | 1787674
140 | Bhola 33 MW PP (Venture) | 37 | 38 | 38 | 39 | 40 | 35 | 28 | 26 | 27 | 27 | 23 | 26 | 27 | 28 | 29 | 23 | 21 | 25 |  | 38 | 39 | 39 | 41 | 41 | 40 | 39 | 767552
141 | Noapara 100 MW PP (Bangla Trac) | 20 | [18 empty] | 64 | 100 | 100 | 100 | 100 | 100 | 100 | 608640
142 | Noapara 40 MW PP (Khanjahan Ali) | 33 | 33 | 16 | 16 | 16 |  |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  |  | 8 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 510375
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 934 | 935 | 934 | 934 | 934 | 934 | 935 | 934 | 932 | 931 | 931 | 929 | 929 | 930 | 930 | 930 | 930 | 930 |  | 930 | 932 | 932 | 931 | 932 | 931 | 931 | 22361454
147 | Bheramara 410 MW CCPP | 370 | 370 | 370 | 370 | 370 | 370 | 320 | 320 | 360 | 370 | 355 | 330 | 330 | 320 | 320 | 320 | 290 | 260 |  | 410 | 345 | 345 | 345 | 350 | 340 | 340 | 8525952
148 | Payra 1320 MW | 560 | 560 | 560 | 560 | 540 | 520 | 520 | 520 | 430 | 310 | 430 | 440 | 480 | 450 | 450 | 450 | 450 | 410 |  | 530 | 560 | 570 | 580 | 590 | 530 | 530 | 12998900
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 151 | 150 | 150 | 149 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3691500
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP | 70 | 65 | 60 | 60 | 60 | 55 | 55 | 55 | 55 | 40 | 35 | [15 empty] | 624000
| Baghabari 50 MW Peaking PP | [19 empty] | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 285316
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 140 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 144 | 144 | 141 | 138 | 141 | 143 | 143 | 144 | 144 | 120 |  | 140 | 146 | 146 | 145 | 145 | 145 | 146 | 3553200
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 130 | 130 | 130 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 170 | 170 | 180 | 180 | 180 | 180 | 180 | 130 |  | 186 | 180 | 180 | 180 | 180 | 180 | 160 | 4393345
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 412 | 416 | 418 | 404 | 412 | 389 | 341 | 365 | 410 | 410 | 414 | 380 | 370 | 343 | 364 | 334 | 334 | 334 |  | 388 | 394 | 407 | 398 | 411 | 416 | 383 | 9206273
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 23 |  | 34 | 34 | 34 | 34 | 34 | 34 | 21 | 195864
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 494160
163 | Bogura 20 MW PP (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 131544
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 250182
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | 36 | [16 empty] | 16 |  | 43 | 43 | 47 | 43 | 43 | 43 | 43 | 283300
168 | Santahar 50 MW Peaking PP | 31 | [16 empty] | 4 |  | 32 | 32 | 32 | 32 | 32 | 32 | 0 | 196030
169 | Natore 52 MW PP (Rajlanka) | [11 empty] | 1 | 34 | 43 | 43 |  |  | 8 |  | 43 | 43 | 43 | 34 | 43 | 43 | 43 | 382080
170 | Chapainawabganj 100 MW Peaking PP | 96 | [16 empty] | 12 |  | 98 | 98 | 98 | 96 | 96 | 96 | 96 | 678104
171 | Baghabari 200 MW PP (Paramount) | [19 empty] | 100 | 50 | [5 empty] | 100802
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 35 | [7 empty] | 10 | 35 | 35 | 35 | 35 | 35 |  | 86 | 113 | 113 | 113 | 113 | 113 | 113 | 1400640
172 | Confidence Power Bogura Unit-1 113 MW | 90 | 90 | 90 | 90 | 90 | 50 | 50 | 50 | 70 | 90 | 90 | 90 | 90 | 90 | 90 | 50 | 50 | 50 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1987680
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 106 | 106 | 106 | 106 | 106 | 89 | 36 | 35 | 35 | 41 | 79 | 84 | 89 | 94 | 98 | 84 | 39 | 42 |  | 80 | 98 | 98 | 98 | 98 | 98 | 99 | 1960320
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 1 | 2 | 4 | 5 | 6 | 6 | 3 | 2 | 1 | 0 | [8 empty] | 30329
178
178