## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-09-11 | Friday
|  |  | Date (day): | 2020-09-11 |  | Friday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13846.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14997 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-09-10 | 2020-09-11 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 120 | 120 | 120 | 300
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 69 | 70 | 72 | 72
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 88 | 94 | 95 | 95
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 369 | 340 | 412 | 412 |  |  | FGMO
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 348 | 282 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 420 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 7 | 7 | 7 | 93 |  | Fuel shortage
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 134 | 135 | 150 | 150 | 155 |  | GT-1 S/D for gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 97 | 97 | 96 | 96
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 1 | 100 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 7 | 7 | 7 | 93 |  | Fuel shortage
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 277 | 335 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 84 | 50 | 40 | 40 | 62 |  | Fuel shortage
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 32 | 150 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 55 | 45 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 10 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 258 | 286 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 19 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 145 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 50 | 103 | 100 | 100
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 17 | 17 | 17 | 87 |  | Fuel shortage
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 2626 | 3085 | 3623 | 4053 | 964 | 785
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 13 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 44 | 46 | 44 | 44 | 186 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 178 | 177 | 180 | 180 | 45 |  | Gas Shortage
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 140 | 147 | 150 | 150
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 100 | 100
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 70 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 21 | 20 | 20
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 6 | 35 | 25 | 40
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 30 | 84 | 85 | 85 |  | 23 | Engine problem
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 236 | 213 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 17 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 990 | 1290 | 1688 | 1678 | 471 | 121
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 80 | 80 | 80 | 54 |  | Gas shortage
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 43 | 189 | 214 | 214 |  |  | FGMO
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 260 | 360 | 360 |  |  | FGMO
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 280 | 360 | 360 |  |  | FGMO
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 33 | 19 | 35 | 36 |  | 9 | Engine problem
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 42 | 20 | 20 | 20 | 35 |  | Gas shortage
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 36 | 8 | 8 | 8 | 187 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 1 | 50 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 50 | 0 | 50
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 80 | 100 | 100 |  | 63 | ST under shut down
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 55 | 200 | 200
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 21 | 21
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 128 | 156 | 157 | 173
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 43 | 43 | 43 |  | 9 | Engine problem
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 21 | 21 | 20 | 20 |  | 5 | Engine problem
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 70 | 114 | 114
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 105 | 113 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1249 | 1607 | 2090 | 2357 | 540 | 86
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 158 | 126 | 160 | 160 | 42 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 48 | 52 | 72 | 72 |  | 23 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 200 | 200 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 110 | 115 | 115
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 429 | 510 | 570.6 | 569 | 42 | 23
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 88 | 91 | 90 | 90
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 28 | 28 | 30 | 30 |  | 60 | Unit-4 under shut down
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 262 | 308 | 300 | 300
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 50 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 49 | 49 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 65 | 35 | 64 | 64 |  |  | FGMO
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 88 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 185 | 184 | 225 | 225
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 285 | 341 | 341
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1339 | 1340 | 1458 | 1458 | 0 | 460
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 931 | 930 | 750 | 945
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 115 | 115 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 215 | 225 | 225
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 350 | 340 | 410 | 410
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 35 | 105 | 105
| 108 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1516 | 1775 | 1795 | 2146 | 0 | 0
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 64 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 24 | 40 | 33 | 33
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 87 | 88 | 90 | 90 |  | 104 | GT-2 & ST Under maint.
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 77 | 79 | 80 | 80 |  | 15 | Engine problem
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 440 | 560 | 620 | 620
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 628 | 831 | 933 | 933 | 0 | 119
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 34 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 43 | 43 | 43
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 144 | 145 | 144 | 144 |  |  | ST Under maint.
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 165 | 216 | 220 | 220 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 370 | 359 | 414 | 414 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 0 | 32
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 8 | 8 | 8 | 8
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 43 | 43 | 43 |  | 9 | Engine problem
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 97 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 108 | 113 | 113
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 90 | 109 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 806 | 1270 | 1431 | 1553 | 491 | 9
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 149 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 10 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 70 | 84 | 100 | 100
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 223 | 233 | 258 | 250 | 294 | 30
|  | Total |  |  |  |  | 20383 | 19892 | 9806 | 11941 | 13846.6 | 14997 | 2802 | 1633
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9406.0735 | 11454 | 13281.8823 | 14385.3645
| A. |  | 2020-09-10 | (Yesterday) |  |  |  |  | Thursday
| 1 | Highest Generation : |  |  | 11941 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
| 2 | Minimum Generation : |  |  | 9121 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11941 | MW
| 3 | Day peak Generation : |  |  | 9806 | MW at | 10:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11454 | MW
| 4 | Evening peak Generation : |  |  | 11941 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 249.7728 | MKWHr | By Solar | 0.16896 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 138.2242 | MKWHr |  | By Oil: | 69.9065 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 14.5711 | MKWHr |  | By Hydro: | 1.0577 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2802 | MW | Dhaka | 3979 | 3979 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 1633 | MW | Chittagong | 1192 | 1192 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4435 | MW | Khulna | 1512 | 1512 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1159.72 | MMCFD |  |  | Rajshahi | 1225 | 1225 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 160686569.868 | ii) Oil : | Taka | 573532985.63 | Comilla | 1153 | 1153 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 67643920 | Total | Taka | 801863475.498 | Mymensingh | 803 | 803 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.129 | MKWHr. | Sylhet | 508 | 508 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -23 | MW (E to W) at | 19:30 | hrs | Barisal | 343 | 343 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -68 | MW at | 19:00 | hrs | Rangpur | 739 | 739 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 31.5° C |  |  | Total | 11454 | 11454 |  | 0
| B. |  | 2020-09-11 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 32.7° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 11500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14997 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 9000 | MW
| 4 | Reserve(Generation end) |  |  |  | 3497 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 240.5483 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8190 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.3673 | MKWHr. | ii) HVDC Flow at Peak Time |  | 930 | MW at | 19:30 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.4771 | MKWHr. | iii) Maximum HVDC Flow : |  | 936 | MW at | 3:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 93.06 |  | (b) Today: | 93.2 |  | (c) Rule Curve: |  | 100.3
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-09-10
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 120 | 92 | 71 | 341 | 322 |  | 0 | 340 | 130 | 11 | 96 | 55 | 307 | 0 | 0 | 0 | 100 | 93 | 150 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 45 | 0 | 120 | 0 | 0 | 176 | 0 | 106 | 0 |  | 0 | 0 | 30 | 30 | 84 | 50 | 21 | 42 | 0 | 0 | 80 | 260 | 255 | 174 | 8 | 80 | 25 | 5 | 0 | 51 | 0 | 0 | 43 | 18 | 11 | 33 | 21 | 158 | 159 | 71 | 22 | 0 | 90 | 28 | 53 | 49 | 130 | 260 | 63 | 85 | 0 | 184 | 18 | 0 | 9 | 280 | 24 | 8 | 0 | 283 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 125 | 0 | 115 | 103 | 0 | 0 | 234 | 0 | 0 | 50 | 107 | 100 | 0 | 17 |  | 935 | 0 | 340 | 0 | 115 | 160 | 0 | 0 | 0 | 0 | 40 | 87 | 39 | 80 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 36 | 43 | 5 | 21 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 146 | 0 | 0 | 0 | 78 | 40 | 160 | 0 | 406 | 53 | 0 | 113 | 0 | 98 | 0 | 0 | 90 | 530 |  | 7602 | 3877 | 11479 | 3888 | 935 | 2089 | 3207 | 680 | 45 | 477 | 158 | 0 | 0 | 93.06
2:00 | 0 | 0 | 0 | 0 | 120 | 91 | 71 | 355 | 321 |  | 0 | 340 | 132 | 7 | 96 | 47 | 301 | 0 | 0 | 0 | 100 | 93 | 150 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 45 | 0 | 120 | 0 | 0 | 176 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 84 | 50 | 21 | 42 | 0 | 0 | 80 | 260 | 255 | 169 | 8 | 84 | 25 | 5 | 0 | 51 | 0 | 0 | 43 | 18 | 11 | 33 | 21 | 156 | 161 | 72 | 22 | 0 | 90 | 30 | 53 | 49 | 130 | 263 | 64 | 85 | 0 | 185 | 18 | 0 | 9 | 300 | 24 | 8 | 0 | 283 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 127 | 0 | 95 | 103 | 0 | 0 | 234 | 0 | 0 | 0 | 107 | 100 | 0 | 17 |  | 935 | 0 | 365 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 87 | 39 | 48 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 24 | 21 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 146 | 0 | 0 | 0 | 77 | 20 | 160 | 0 | 414 | 35 | 0 | 113 | 0 | 99 | 0 | 0 | 90 | 530 |  | 7495 | 3740 | 11235 | 3927 | 935 | 2114 | 2988 | 680 | 45 | 390 | 156 | 0 | 0 | 93.06
3:00 | 0 | 0 | 0 | 0 | 120 | 91 | 71 | 349 | 338 |  | 0 | 340 | 127 | 7 | 96 | 55 | 300 | 0 | 0 | 0 | 100 | 93 | 150 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 45 | 0 | 120 | 0 | 0 | 177 | 0 | 106 | 0 |  | 0 | 0 | 0 | 0 | 84 | 43 | 21 | 42 | 0 | 0 | 80 | 260 | 255 | 166 | 8 | 84 | 25 | 5 | 0 | 51 | 0 | 0 | 16 | 18 | 11 | 33 | 21 | 152 | 160 | 72 | 22 | 0 | 90 | 28 | 53 | 49 | 130 | 260 | 64 | 85 | 0 | 185 | 18 | 0 | 9 | 295 | 24 | 8 | 0 | 283 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 128 | 0 | 95 | 67 | 0 | 0 | 234 | 0 | 0 | 0 | 113 | 100 | 0 | 17 |  | 936 | 0 | 340 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 87 | 39 | 16 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 146 | 0 | 0 | 0 | 76 | 20 | 160 | 0 | 411 | 35 | 0 | 0 | 0 | 99 | 0 | 0 | 90 | 530 |  | 7430 | 3543 | 10973 | 3889 | 936 | 2122 | 2783 | 680 | 45 | 366 | 152 | 0 | 0 | 93.06
4:00 | 0 | 0 | 0 | 0 | 120 | 92 | 71 | 342 | 349 |  | 0 | 340 | 130 | 7 | 96 | 55 | 307 | 0 | 0 | 0 | 100 | 85 | 150 | 25 | 0 | 0 | 0 | 17 | 17 | 17 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 45 | 0 | 120 | 0 | 0 | 176 | 0 | 108 | 0 |  | 0 | 0 | 0 | 0 | 79 | 25 | 21 | 42 | 0 | 0 | 80 | 260 | 255 | 166 | 8 | 88 | 25 | 5 | 0 | 51 | 0 | 0 | 16 | 18 | 11 | 33 | 21 | 144 | 161 | 72 | 22 | 0 | 90 | 28 | 53 | 49 | 130 | 261 | 64 | 85 | 0 | 185 | 18 | 0 | 9 | 300 | 16 | 8 | 0 | 286 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 98 | 0 | 75 | 50 | 0 | 0 | 234 | 0 | 0 | 0 | 113 | 100 | 0 | 17 |  | 935 | 0 | 340 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 87 | 39 | 16 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 147 | 0 | 0 | 0 | 75 | 10 | 160 | 0 | 351 | 35 | 0 | 0 | 0 | 98 | 0 | 0 | 90 | 550 |  | 7233 | 3468 | 10701 | 3889 | 935 | 2078 | 2567 | 700 | 45 | 343 | 144 | 0 | 0 | 93.06
5:00 | 0 | 0 | 0 | 0 | 120 | 93 | 70 | 349 | 349 |  | 0 | 340 | 135 | 7 | 96 | 55 | 298 | 0 | 0 | 0 | 100 | 85 | 150 | 25 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 25 | 30 | 33 | 33 | 0 | 0 | 46 | 0 | 120 | 0 | 0 | 176 | 0 | 109 | 0 |  | 0 | 0 | 0 | 0 | 84 | 25 | 21 | 42 | 0 | 0 | 80 | 260 | 255 | 166 | 8 | 93 | 25 | 5 | 0 | 51 | 0 | 0 | 16 | 18 | 11 | 33 | 21 | 142 | 159 | 72 | 22 | 0 | 90 | 28 | 53 | 49 | 130 | 258 | 64 | 85 | 0 | 185 | 18 | 0 | 9 | 300 | 16 | 8 | 0 | 283 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 26 | 0 | 55 | 50 | 0 | 0 | 234 | 0 | 0 | 0 | 113 | 100 | 0 | 17 |  | 935 | 0 | 365 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 87 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 146 | 0 | 0 | 0 | 76 | 0 | 160 | 0 | 340 | 35 | 0 | 0 | 0 | 99 | 0 | 0 | 90 | 550 |  | 7124 | 3452 | 10576 | 3890 | 935 | 2063 | 2457 | 700 | 46 | 343 | 142 | 0 | 0 | 93.06
6:00 | 0 | 0 | 0 | 0 | 120 | 93 | 70 | 342 | 303 |  | 0 | 380 | 110 | 7 | 93 | 55 | 249 | 0 | 0 | 0 | 100 | 85 | 82 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 43 | 0 | 120 | 0 | 0 | 177 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 72 | 25 | 21 | 42 | 0 | 0 | 80 | 260 | 255 | 125 | 8 | 86 | 0 | 5 | 0 | 51 | 0 | 0 | 16 | 18 | 11 | 33 | 21 | 122 | 164 | 71 | 22 | 0 | 90 | 28 | 53 | 49 | 130 | 260 | 64 | 85 | 0 | 172 | 18 | 0 | 9 | 265 | 16 | 5 | 0 | 283 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 10 | 0 | 8 | 6 | 0 | 0 | 249 | 0 | 0 | 0 | 109 | 100 | 0 | 17 |  | 935 | 0 | 345 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 147 | 0 | 0 | 0 | 79 | 0 | 130 | 0 | 284 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 90 | 470 |  | 6659 | 3145 | 9804 | 3687 | 935 | 1962 | 2203 | 620 | 43 | 232 | 122 | 0 | 0 | 93.06
7:00 | 0 | 0 | 0 | 0 | 120 | 94 | 70 | 344 | 272 |  | 0 | 340 | 125 | 7 | 80 | 55 | 0 | 0 | 0 | 0 | 92 | 83 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 44 | 0 | 120 | 0 | 0 | 177 | 0 | 60 | 0 |  | 0 | 0 | 0 | 0 | 25 | 0 | 21 | 35 | 0 | 0 | 80 | 260 | 255 | 62 | 8 | 85 | 0 | 5 | 0 | 51 | 0 | 0 | 16 | 18 | 8 | 33 | 21 | 114 | 160 | 32 | 22 | 0 | 91 | 28 | 53 | 49 | 130 | 260 | 64 | 85 | 0 | 183 | 18 | 0 | 9 | 265 | 24 | 5 | 0 | 250 | 0 | 0 | 200 | 0 | 149 | 2 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 236 | 0 | 0 | 0 | 99 | 100 | 0 | 17 |  | 935 | 0 | 350 | 0 | 102 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 147 | 0 | 0 | 0 | 79 | 0 | 130 | 0 | 327 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 90 | 480 |  | 5988 | 3133 | 9121 | 3384 | 935 | 1925 | 1950 | 630 | 44 | 136 | 114 | 3 | 0 | 93.06
8:00 | 0 | 0 | 0 | 0 | 120 | 94 | 70 | 340 | 251 |  | 0 | 320 | 138 | 7 | 97 | 55 | 0 | 0 | 0 | 0 | 98 | 83 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 44 | 0 | 120 | 0 | 0 | 177 | 0 | 47 | 0 |  | 0 | 0 | 0 | 0 | 25 | 0 | 21 | 12 | 0 | 0 | 80 | 260 | 255 | 25 | 8 | 94 | 35 | 20 | 0 | 51 | 0 | 0 | 16 | 18 | 8 | 33 | 21 | 124 | 160 | 32 | 22 | 0 | 90 | 30 | 53 | 49 | 163 | 260 | 64 | 85 | 0 | 185 | 18 | 0 | 9 | 280 | 24 | 5 | 0 | 250 | 0 | 0 | 200 | 0 | 149 | 2 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 236 | 0 | 0 | 0 | 96 | 100 | 0 | 17 |  | 936 | 0 | 345 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 147 | 0 | 0 | 0 | 77 | 0 | 148 | 0 | 330 | 0 | 0 | 0 | 0 | 71 | 0 | 1 | 90 | 450 |  | 6024 | 3127 | 9151 | 3390 | 936 | 1924 | 1992 | 600 | 44 | 136 | 124 | 5 | 0 | 93.06
9:00 | 0 | 0 | 0 | 0 | 120 | 91 | 69 | 370 | 346 |  | 0 | 400 | 138 | 7 | 97 | 55 | 0 | 0 | 0 | 0 | 100 | 75 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 15 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 44 | 0 | 120 | 0 | 0 | 178 | 0 | 25 | 0 |  | 0 | 0 | 0 | 0 | 25 | 6 | 21 | 4 | 0 | 0 | 80 | 330 | 285 | 25 | 36 | 95 | 35 | 20 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 21 | 124 | 159 | 32 | 22 | 1 | 91 | 30 | 50 | 49 | 163 | 260 | 65 | 83 | 0 | 185 | 18 | 0 | 9 | 310 | 24 | 5 | 0 | 250 | 0 | 0 | 200 | 0 | 149 | 19 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 236 | 0 | 0 | 0 | 103 | 100 | 0 | 17 |  | 935 | 0 | 370 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 0 | 0 | 77 | 0 | 140 | 0 | 365 | 0 | 0 | 0 | 0 | 71 | 0 | 2 | 90 | 450 |  | 6378 | 3176 | 9554 | 3515 | 935 | 2175 | 2015 | 600 | 44 | 120 | 124 | 26 | 0 | 93.06
10:00 | 0 | 0 | 0 | 0 | 120 | 88 | 69 | 369 | 348 |  | 0 | 400 | 134 | 7 | 97 | 55 | 0 | 0 | 0 | 0 | 100 | 84 | 32 | 1 | 0 | 0 | 0 | 54 | 55 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 44 | 0 | 120 | 0 | 0 | 178 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 30 | 19 | 0 | 6 | 0 | 0 | 80 | 300 | 260 | 43 | 36 | 90 | 33 | 42 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 21 | 128 | 158 | 48 | 22 | 1 | 88 | 28 | 50 | 49 | 163 | 262 | 65 | 83 | 0 | 185 | 18 | 0 | 9 | 310 | 24 | 5 | 0 | 258 | 0 | 0 | 200 | 0 | 145 | 13 | 100 | 0 | 1 | 0 | 0 | 50 | 0 | 4 | 236 | 0 | 0 | 0 | 105 | 100 | 0 | 17 |  | 931 | 0 | 350 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 0 | 0 | 77 | 0 | 165 | 0 | 370 | 0 | 0 | 0 | 0 | 70 | 0 | 3 | 90 | 440 |  | 6633 | 3173 | 9806 | 3565 | 931 | 2204 | 2171 | 590 | 44 | 152 | 128 | 21 | 0 | 93.06
11:00 | 0 | 0 | 0 | 0 | 120 | 86 | 70 | 342 | 349 |  | 0 | 370 | 124 | 7 | 97 | 55 | 0 | 0 | 0 | 0 | 100 | 50 | 32 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 24 | 33 | 33 | 0 | 0 | 0 | 0 | 120 | 0 | 2 | 177 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 60 | 41 | 18 | 6 | 0 | 0 | 80 | 290 | 250 | 47 | 36 | 90 | 33 | 42 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 15 | 136 | 0 | 0 | 0 | 0 | 91 | 28 | 50 | 49 | 130 | 260 | 32 | 85 | 0 | 226 | 18 | 0 | 9 | 290 | 24 | 8 | 0 | 268 | 0 | 0 | 0 | 0 | 126 | 20 | 100 | 0 | 10 | 0 | 0 | 102 | 0 | 6 | 236 | 0 | 0 | 0 | 103 | 100 | 0 | 17 |  | 930 | 0 | 345 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 145 | 0 | 0 | 0 | 76 | 0 | 150 | 0 | 340 | 0 | 0 | 0 | 0 | 70 | 0 | 5 | 90 | 440 |  | 6174 | 3109 | 9283 | 3318 | 930 | 2093 | 2033 | 590 | 0 | 152 | 136 | 31 | 0 | 93.06
12:00 | 0 | 0 | 0 | 0 | 120 | 90 | 71 | 349 | 349 |  | 0 | 400 | 140 | 7 | 97 | 55 | 7 | 0 | 0 | 0 | 100 | 50 | 32 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 24 | 33 | 33 | 0 | 0 | 46 | 0 | 120 | 0 | 16 | 177 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 66 | 50 | 18 | 6 | 0 | 0 | 80 | 300 | 255 | 57 | 36 | 90 | 33 | 42 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 15 | 132 | 76 | 0 | 22 | 2 | 88 | 28 | 50 | 49 | 163 | 284 | 32 | 85 | 0 | 224 | 18 | 0 | 9 | 290 | 24 | 8 | 0 | 268 | 0 | 0 | 38 | 0 | 0 | 11 | 100 | 0 | 10 | 0 | 2 | 0 | 0 | 3 | 235 | 0 | 0 | 0 | 107 | 100 | 0 | 17 |  | 930 | 0 | 355 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 0 | 0 | 77 | 0 | 150 | 0 | 340 | 0 | 0 | 0 | 0 | 70 | 0 | 2 | 90 | 440 |  | 6290 | 3116 | 9406 | 3483 | 930 | 2162 | 1893 | 590 | 46 | 152 | 132 | 18 | 0 | 93.06
13:00 | 0 | 0 | 0 | 0 | 120 | 91 | 71 | 366 | 328 |  | 0 | 420 | 134 | 7 | 97 | 55 | 27 | 0 | 0 | 0 | 100 | 40 | 32 | 13 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 24 | 33 | 33 | 0 | 0 | 46 | 0 | 120 | 0 | 16 | 178 | 0 | 148 | 0 |  | 0 | 0 | 0 | 0 | 75 | 50 | 18 | 9 | 0 | 0 | 80 | 260 | 280 | 121 | 8 | 80 | 19 | 20 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 21 | 136 | 84 | 32 | 20 | 1 | 88 | 28 | 50 | 47 | 163 | 283 | 30 | 85 | 0 | 225 | 18 | 0 | 9 | 310 | 24 | 8 | 0 | 268 | 0 | 0 | 200 | 0 | 6 | 18 | 100 | 0 | 21 | 0 | 8 | 50 | 0 | 2 | 234 | 0 | 0 | 0 | 113 | 100 | 0 | 17 |  | 930 | 0 | 345 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 0 | 0 | 77 | 0 | 191 | 0 | 402 | 0 | 0 | 6 | 0 | 70 | 0 | 6 | 90 | 440 |  | 6617 | 3224 | 9841 | 3598 | 930 | 2197 | 2165 | 590 | 46 | 152 | 136 | 27 | 0 | 93.06
14:00 | 0 | 0 | 0 | 0 | 120 | 92 | 71 | 329 | 254 |  | 0 | 300 | 140 | 7 | 97 | 55 | 176 | 0 | 0 | 0 | 100 | 50 | 16 | 12 | 0 | 0 | 0 | 54 | 0 | 55 | 0 | 25 | 30 | 25 | 33 | 0 | 0 | 46 | 0 | 120 | 0 | 16 | 177 | 0 | 147 | 0 |  | 0 | 0 | 0 | 0 | 65 | 18 | 18 | 9 | 0 | 0 | 80 | 260 | 280 | 178 | 8 | 80 | 19 | 20 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 21 | 136 | 104 | 24 | 20 | 0 | 89 | 28 | 50 | 49 | 110 | 284 | 30 | 85 | 0 | 191 | 18 | 0 | 9 | 265 | 24 | 8 | 0 | 282 | 0 | 0 | 200 | 0 | 72 | 15 | 100 | 0 | 45 | 0 | 8 | 50 | 0 | 1 | 234 | 0 | 0 | 0 | 104 | 100 | 0 | 17 |  | 930 | 0 | 290 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 21 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 0 | 77 | 0 | 140 | 0 | 326 | 0 | 0 | 33 | 0 | 63 | 0 | 3 | 90 | 440 |  | 6465 | 3072 | 9537 | 3616 | 930 | 1833 | 2231 | 590 | 46 | 136 | 136 | 19 | 0 | 93.06
15:00 | 0 | 0 | 0 | 0 | 120 | 89 | 71 | 281 | 305 |  | 0 | 360 | 140 | 7 | 96 | 55 | 307 | 0 | 0 | 0 | 50 | 50 | 16 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 25 | 0 | 0 | 46 | 0 | 120 | 0 | 16 | 179 | 0 | 146 | 0 |  | 0 | 0 | 0 | 0 | 50 | 19 | 21 | 6 | 0 | 0 | 80 | 280 | 280 | 173 | 8 | 80 | 19 | 20 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 21 | 132 | 103 | 24 | 20 | 0 | 88 | 28 | 50 | 46 | 163 | 282 | 30 | 85 | 0 | 223 | 18 | 0 | 9 | 300 | 24 | 5 | 0 | 286 | 0 | 0 | 200 | 0 | 128 | 11 | 100 | 0 | 50 | 0 | 8 | 50 | 0 | 1 | 234 | 0 | 0 | 0 | 111 | 100 | 0 | 17 |  | 930 | 0 | 294 | 0 | 99 | 120 | 0 | 0 | 0 | 2 | 0 | 87 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 0 | 77 | 0 | 130 | 0 | 333 | 0 | 0 | 35 | 0 | 63 | 0 | 1 | 90 | 440 |  | 6858 | 3078 | 9936 | 3759 | 930 | 2031 | 2297 | 590 | 46 | 138 | 132 | 13 | 0 | 93.06
16:00 | 0 | 0 | 0 | 0 | 120 | 91 | 69 | 280 | 293 |  | 0 | 360 | 130 | 7 | 97 | 55 | 282 | 0 | 0 | 0 | 40 | 50 | 16 | 12 | 0 | 0 | 0 | 17 | 35 | 17 | 22 | 25 | 20 | 33 | 33 | 0 | 0 | 46 | 0 | 120 | 0 | 16 | 178 | 0 | 146 | 0 |  | 0 | 0 | 0 | 0 | 50 | 19 | 21 | 8 | 0 | 0 | 80 | 260 | 280 | 182 | 8 | 82 | 19 | 20 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 21 | 136 | 92 | 24 | 20 | 0 | 89 | 28 | 52 | 49 | 163 | 285 | 30 | 85 | 0 | 232 | 18 | 0 | 9 | 290 | 24 | 8 | 0 | 283 | 0 | 0 | 200 | 0 | 130 | 6 | 90 | 0 | 50 | 0 | 8 | 34 | 0 | 1 | 234 | 0 | 0 | 0 | 110 | 100 | 0 | 17 |  | 930 | 0 | 295 | 0 | 103 | 120 | 0 | 0 | 0 | 6 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 135 | 0 | 0 | 0 | 77 | 0 | 130 | 0 | 299 | 0 | 0 | 0 | 0 | 84 | 0 | 3 | 90 | 440 |  | 6667 | 3008 | 9675 | 3744 | 930 | 1975 | 2102 | 590 | 46 | 142 | 136 | 10 | 0 | 93.07
17:00 | 0 | 0 | 0 | 0 | 120 | 92 | 69 | 280 | 293 |  | 0 | 360 | 125 | 7 | 97 | 40 | 270 | 0 | 0 | 0 | 7 | 50 | 16 | 12 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 25 | 12 | 33 | 25 | 0 | 0 | 46 | 0 | 120 | 0 | 16 | 177 | 0 | 147 | 0 |  | 0 | 0 | 0 | 0 | 50 | 19 | 21 | 15 | 0 | 0 | 80 | 260 | 280 | 182 | 8 | 82 | 19 | 20 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 21 | 128 | 126 | 24 | 22 | 0 | 91 | 28 | 50 | 49 | 163 | 284 | 30 | 85 | 0 | 184 | 18 | 0 | 9 | 280 | 24 | 8 | 0 | 286 | 0 | 0 | 200 | 0 | 129 | 2 | 70 | 0 | 50 | 0 | 8 | 34 | 0 | 1 | 160 | 0 | 0 | 0 | 75 | 70 | 0 | 17 |  | 930 | 0 | 295 | 0 | 86 | 120 | 0 | 0 | 0 | 2 | 0 | 88 | 27 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 8 | 0 | 0 | 148 | 0 | 0 | 145 | 0 | 0 | 0 | 77 | 0 | 130 | 0 | 291 | 0 | 0 | 0 | 0 | 82 | 0 | 1 | 70 | 440 |  | 6399 | 2982 | 9381 | 3713 | 930 | 1969 | 1853 | 588 | 46 | 150 | 128 | 4 | 0 | 93.07
18:00 | 0 | 0 | 0 | 0 | 120 | 52 | 40 | 280 | 273 |  | 0 | 360 | 140 | 7 | 97 | 40 | 307 | 0 | 0 | 0 | 7 | 50 | 16 | 15 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 25 | 12 | 33 | 33 | 0 | 0 | 46 | 0 | 120 | 0 | 16 | 177 | 0 | 100 | 0 |  | 0 | 0 | 85 | 0 | 50 | 19 | 21 | 22 | 0 | 0 | 80 | 280 | 280 | 184 | 8 | 91 | 19 | 20 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 21 | 130 | 126 | 24 | 22 | 0 | 88 | 30 | 50 | 49 | 130 | 285 | 20 | 50 | 0 | 184 | 18 | 0 | 9 | 280 | 24 | 8 | 0 | 283 | 0 | 0 | 200 | 0 | 131 | 0 | 70 | 0 | 50 | 0 | 8 | 34 | 0 | 0 | 160 | 0 | 0 | 0 | 75 | 70 | 0 | 17 |  | 930 | 0 | 295 | 0 | 83 | 120 | 0 | 0 | 0 | 8 | 0 | 88 | 28 | 16 | 0 | 0 | 0 | 0 | 17 | 60 | 0 | 0 | 10 | 0 | 5 | 22 | 8 | 8 | 0 | 0 | 108 | 0 | 0 | 145 | 0 | 0 | 0 | 42 | 0 | 130 | 0 | 334 | 0 | 0 | 0 | 0 | 74 | 0 | 0 | 70 | 400 |  | 6369 | 3001 | 9370 | 3732 | 930 | 1828 | 1875 | 508 | 46 | 321 | 130 | 0 | 0 | 93.08
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 120 | 93 | 60 | 326 | 282 |  | 0 | 420 | 130 | 7 | 97 | 50 | 266 | 0 | 0 | 0 | 7 | 50 | 150 | 49 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 12 | 33 | 33 | 0 | 0 | 46 | 0 | 120 | 0 | 20 | 177 | 0 | 148 | 0 |  | 0 | 0 | 85 | 70 | 64 | 26 | 21 | 33 | 0 | 0 | 80 | 260 | 280 | 187 | 8 | 76 | 19 | 20 | 0 | 51 | 0 | 50 | 16 | 18 | 8 | 33 | 21 | 162 | 136 | 35 | 22 | 0 | 91 | 28 | 52 | 49 | 163 | 310 | 35 | 88 | 0 | 184 | 18 | 0 | 9 | 290 | 24 | 8 | 0 | 286 | 104 | 50 | 200 | 101 | 148 | 0 | 100 | 33 | 50 | 0 | 40 | 103 | 0 | 0 | 213 | 0 | 13 | 70 | 105 | 100 | 0 | 17 |  | 930 | 0 | 345 | 0 | 115 | 180 | 0 | 0 | 0 | 0 | 40 | 88 | 39 | 64 | 0 | 0 | 0 | 43 | 34 | 97 | 0 | 0 | 42 | 26 | 25 | 22 | 8 | 8 | 0 | 0 | 130 | 0 | 0 | 145 | 0 | 0 | 0 | 78 | 60 | 194 | 0 | 353 | 35 | 0 | 50 | 0 | 78 | 0 | 0 | 90 | 480 |  | 7770 | 3799 | 11569 | 3921 | 930 | 2118 | 3076 | 610 | 46 | 706 | 162 | 0 | 0 | 93.09
19:30 | 0 | 0 | 0 | 0 | 120 | 94 | 70 | 340 | 282 |  | 0 | 420 | 135 | 7 | 97 | 55 | 277 | 0 | 0 | 0 | 7 | 50 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 33 | 10 | 0 | 46 | 0 | 120 | 0 | 25 | 177 | 0 | 147 | 0 |  | 0 | 0 | 85 | 70 | 84 | 50 | 21 | 35 | 0 | 0 | 80 | 260 | 280 | 189 | 8 | 80 | 19 | 20 | 0 | 51 | 0 | 50 | 43 | 18 | 11 | 33 | 21 | 156 | 126 | 52 | 22 | 0 | 91 | 28 | 50 | 49 | 163 | 308 | 35 | 88 | 0 | 184 | 18 | 0 | 9 | 285 | 24 | 8 | 0 | 286 | 19 | 0 | 200 | 0 | 149 | 0 | 100 | 55 | 50 | 0 | 110 | 103 | 0 | 0 | 213 | 0 | 17 | 70 | 113 | 100 | 0 | 17 |  | 930 | 0 | 340 | 0 | 115 | 215 | 0 | 0 | 0 | 0 | 40 | 88 | 40 | 64 | 0 | 0 | 0 | 50 | 34 | 97 | 0 | 0 | 43 | 43 | 25 | 22 | 8 | 11 | 0 | 0 | 149 | 0 | 0 | 145 | 0 | 0 | 0 | 79 | 100 | 216 | 0 | 359 | 35 | 0 | 108 | 0 | 84 | 0 | 0 | 109 | 560 |  | 7832 | 4109 | 11941 | 3970 | 930 | 2132 | 3249 | 709 | 46 | 749 | 156 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 120 | 95 | 70 | 339 | 282 |  | 0 | 420 | 135 | 7 | 96 | 55 | 271 | 0 | 0 | 0 | 7 | 50 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 33 | 0 | 45 | 0 | 120 | 0 | 25 | 177 | 0 | 148 | 0 |  | 0 | 0 | 85 | 40 | 82 | 50 | 21 | 37 | 0 | 0 | 80 | 260 | 280 | 194 | 8 | 86 | 19 | 20 | 0 | 51 | 0 | 50 | 42 | 18 | 11 | 33 | 21 | 170 | 125 | 55 | 22 | 0 | 91 | 28 | 53 | 49 | 163 | 308 | 20 | 88 | 0 | 184 | 18 | 0 | 9 | 270 | 24 | 8 | 0 | 286 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 69 | 50 | 0 | 109 | 103 | 0 | 0 | 214 | 0 | 17 | 70 | 113 | 100 | 0 | 17 |  | 930 | 0 | 345 | 0 | 115 | 220 | 0 | 0 | 0 | 0 | 40 | 87 | 38 | 64 | 0 | 0 | 0 | 50 | 34 | 97 | 0 | 0 | 47 | 43 | 26 | 22 | 8 | 11 | 0 | 0 | 149 | 0 | 0 | 145 | 0 | 0 | 0 | 79 | 100 | 213 | 0 | 357 | 35 | 0 | 110 | 0 | 87 | 0 | 0 | 109 | 560 |  | 7814 | 4121 | 11935 | 3962 | 930 | 2119 | 3241 | 709 | 45 | 759 | 170 | 0 | 0 | 93.1
21:00 | 0 | 0 | 0 | 0 | 120 | 95 | 70 | 340 | 282 |  | 0 | 420 | 135 | 5 | 97 | 55 | 277 | 0 | 0 | 0 | 7 | 50 | 150 | 33 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 42 | 0 | 45 | 0 | 120 | 0 | 25 | 177 | 0 | 147 | 0 |  | 0 | 0 | 85 | 20 | 82 | 50 | 21 | 42 | 0 | 0 | 80 | 260 | 280 | 196 | 8 | 85 | 19 | 20 | 0 | 51 | 0 | 50 | 43 | 18 | 11 | 33 | 21 | 166 | 126 | 54 | 22 | 0 | 91 | 28 | 53 | 49 | 163 | 312 | 35 | 88 | 0 | 184 | 18 | 0 | 10 | 270 | 24 | 8 | 0 | 286 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 34 | 50 | 0 | 115 | 103 | 0 | 0 | 216 | 0 | 17 | 70 | 113 | 100 | 0 | 17 |  | 930 | 0 | 340 | 0 | 115 | 225 | 0 | 0 | 0 | 0 | 40 | 87 | 38 | 64 | 0 | 0 | 0 | 50 | 34 | 97 | 0 | 0 | 43 | 43 | 33 | 22 | 8 | 11 | 0 | 0 | 149 | 0 | 0 | 145 | 0 | 0 | 0 | 78 | 100 | 214 | 0 | 361 | 35 | 0 | 113 | 0 | 98 | 0 | 0 | 109 | 560 |  | 7745 | 4142 | 11887 | 3993 | 930 | 2128 | 3149 | 709 | 45 | 767 | 166 | 0 | 0 | 93.11
22:00 | 0 | 0 | 0 | 0 | 120 | 95 | 70 | 340 | 272 |  | 0 | 420 | 135 | 7 | 97 | 55 | 288 | 0 | 0 | 0 | 7 | 50 | 150 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 42 | 0 | 45 | 0 | 120 | 0 | 25 | 178 | 0 | 149 | 0 |  | 0 | 0 | 85 | 20 | 78 | 50 | 21 | 42 | 0 | 0 | 80 | 260 | 280 | 195 | 8 | 85 | 19 | 20 | 0 | 51 | 0 | 50 | 43 | 18 | 11 | 33 | 21 | 168 | 124 | 55 | 22 | 0 | 91 | 28 | 53 | 50 | 163 | 287 | 35 | 88 | 0 | 184 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 298 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 34 | 50 | 0 | 115 | 103 | 0 | 0 | 216 | 0 | 0 | 70 | 113 | 100 | 0 | 17 |  | 931 | 0 | 345 | 0 | 115 | 225 | 0 | 0 | 0 | 0 | 40 | 87 | 38 | 64 | 0 | 0 | 0 | 50 | 34 | 97 | 0 | 0 | 43 | 43 | 32 | 22 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 145 | 0 | 0 | 0 | 79 | 100 | 214 | 0 | 362 | 35 | 0 | 113 | 0 | 98 | 0 | 0 | 109 | 560 |  | 7730 | 4150 | 11880 | 3984 | 931 | 2141 | 3135 | 710 | 45 | 766 | 168 | 0 | 0 | 93.12
23:00 | 0 | 0 | 0 | 0 | 120 | 95 | 70 | 340 | 272 |  | 0 | 400 | 140 | 7 | 97 | 55 | 296 | 0 | 0 | 0 | 7 | 50 | 150 | 23 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 42 | 0 | 45 | 0 | 120 | 0 | 25 | 176 | 0 | 148 | 0 |  | 0 | 0 | 68 | 10 | 78 | 50 | 18 | 42 | 0 | 0 | 80 | 260 | 280 | 196 | 8 | 89 | 19 | 20 | 0 | 51 | 0 | 0 | 43 | 18 | 11 | 33 | 21 | 168 | 126 | 64 | 22 | 0 | 91 | 28 | 53 | 50 | 130 | 286 | 35 | 88 | 0 | 185 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 16 | 50 | 0 | 115 | 103 | 0 | 0 | 216 | 0 | 0 | 70 | 113 | 100 | 0 | 17 |  | 930 | 0 | 340 | 0 | 115 | 225 | 0 | 0 | 0 | 0 | 40 | 87 | 38 | 64 | 0 | 0 | 0 | 50 | 0 | 97 | 0 | 0 | 43 | 43 | 32 | 22 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 145 | 0 | 0 | 0 | 78 | 100 | 190 | 0 | 400 | 35 | 0 | 113 | 0 | 99 | 0 | 0 | 109 | 560 |  | 7595 | 4124 | 11719 | 3964 | 930 | 2115 | 3122 | 710 | 45 | 665 | 168 | 0 | 0 | 93.13
24:00 | 0 | 0 | 0 | 0 | 120 | 95 | 70 | 340 | 323 |  | 0 | 400 | 130 | 7 | 96 | 55 | 262 | 0 | 0 | 0 | 7 | 50 | 133 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 25 | 0 | 45 | 0 | 120 | 0 | 25 | 177 | 0 | 149 | 0 |  | 0 | 0 | 42 | 10 | 80 | 50 | 21 | 42 | 0 | 0 | 80 | 260 | 289 | 216 | 8 | 82 | 19 | 20 | 0 | 51 | 0 | 0 | 43 | 18 | 11 | 33 | 21 | 164 | 145 | 64 | 22 | 0 | 91 | 28 | 53 | 50 | 130 | 285 | 35 | 88 | 0 | 184 | 18 | 0 | 10 | 285 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 50 | 0 | 115 | 103 | 0 | 0 | 216 | 0 | 0 | 50 | 105 | 100 | 0 | 17 |  | 930 | 0 | 340 | 0 | 115 | 225 | 0 | 0 | 0 | 0 | 40 | 87 | 39 | 64 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 43 | 43 | 32 | 22 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 145 | 0 | 0 | 0 | 75 | 100 | 190 | 0 | 350 | 35 | 0 | 113 | 0 | 99 | 0 | 0 | 109 | 560 |  | 7533 | 4022 | 11555 | 3974 | 930 | 2119 | 3041 | 710 | 45 | 572 | 164 | 0 | 0 | 93.14
KWH | 0 | 0 | 0 | 0 | 2855100 | 211391 | 1611904 | 8181760 | 7307000 |  | 0 | 8683750 | 3193571 | 199680 | 2306184 | 1307452 | 4869729 | 0 | 0 | 0 | 1570560 | 1581264 | 1993920 | 507240 | 0 | 0 | 0 | 977760 | 1008542 | 918330 | 361440 | 600000 | 616320 | 753700 | 804900 | 236976 | 0 | 1057724 | 0 | 2800000 | 0 | 297345 | 4169024 | 0 | 2813611 | 0 |  | 0 | 0 | 605944 | 221760 | 1551360 | 799680 | 466848 | 653280 | 0 | 0 | 1913438 | 6823900 | 6522000 | 3429000 | 301090 | 2048490 | 484200 | 478560 | 0 | 1243730 | 0 | 200016 | 452242 | 426132 | 219960 | 818900 | 503970 | 3477120 | 3000430 | 1100160 | 467892 | 5500 | 2128000 | 657360 | 1243200 | 1170288 | 3522763 | 6193000 | 1096896 | 2038080 | 0 | 4635450 | 420000 | 0 | 212220 | 7183300 | 552024 | 159120 | 0 | 6716834 | 121109 | 494520 | 4495200 | 93765 | 3149280 | 110295 | 2369280 | 227520 | 1154181 | 0 | 1184400 | 1360692 | 0 | 23641 | 5402073 | 0 | 57708 | 505020 | 2555280 | 2369280 | 0 | 431040 |  | 22367273 | 0 | 8373600 | 0 | 2591040 | 3607680 | 0 | 0 | 0 | 15184 | 466125 | 2105998 | 753361 | 597120 | 0 | 0 | 0 | 295248 | 174930 | 1097472 | 0 | 0 | 306800 | 375840 | 187900 | 488160 | 186372 | 228204 | 0 | 0 | 3569700 | 0 | 0 | 3561900 | 0 | 0 | 0 | 1821667 | 722880 | 4455636 | 0 | 8596145 | 471360 | 0 | 986784 | 0 | 2036160 | 0 | 29527 | 2256768 | 11001400 |  | 166044598 | 83728234 | 249772832 | 90517932 | 22367273 | 47706261 | 61421365 | 14571100 | 1057724 | 8485094 | 3477120 | 168963 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 3169161 | 279036.12 | 2740236.8 | 8263577.6 | 7526210 |  | 0 | 9465287.5 | 3544863.81 | 1515571.2 | 15889607.76 | 11061043.92 | 5064518.16 | 0 | 0 | 0 | 11826316.8 | 14421127.68 | 19620172.8 | 4676752.8 | 0 | 0 | 0 | 7137648 | 7796029.66 | 9054733.8 | 271080 | 450000 | 0 | 0 | 0 | 2291557.92 | 0 | 285585.48 | 0 | 5068000 | 0 | 2762335.05 | 4544236.16 | 0 | 4783138.7 | 0 |  | 0 | 0 | 5877656.8 | 2117808 | 13496832 | 6333465.6 | 588228.48 | 1940241.6 | 0 | 0 | 2812753.86 | 5049686 | 6522000 | 3154680 | 388406.1 | 2355763.5 | 547146 | 669984 | 0 | 2126778.3 | 0 | 2020161.6 | 4318911.1 | 541187.64 | 164970 | 1433075 | 377977.5 | 26078400 | 3180455.8 | 9989452.8 | 594222.84 | 87670 | 3489920 | 1051776 | 2212896 | 1825649.28 | 4015949.82 | 6440720 | 2160885.12 | 3892732.8 | 0 | 8019328.5 | 919800 | 0 | 432928.8 | 7255133 | 414018 | 120931.2 | 0 | 50779265.04 | 2056430.82 | 8268374.4 | 23375040 | 1567750.8 | 30988915.2 | 1289348.55 | 19309632 | 2468592 | 8136976.05 | 0 | 10801728 | 12858539.4 | 0 | 0 | 40839671.88 | 0 | 507253.32 | 5040099.6 | 21898749.6 | 15779404.8 | 0 | 0 |  | 128835492.48 | 0 | 8792280 | 0 | 20365574.4 | 50002444.8 | 0 | 0 | 0 | 159128.32 | 4857022.5 | 2379777.74 | 1167709.55 | 5827891.2 | 0 | 0 | 0 | 2905240.32 | 1777288.8 | 9712627.2 | 0 | 0 | 2972892 | 3641889.6 | 1822630 | 937267.2 | 288876.6 | 172750.428 | 0 | 0 | 19347774 | 0 | 0 | 4167423 | 0 | 0 | 0 | 2732500.5 | 12296188.8 | 5213094.12 | 0 | 8510183.55 | 4920998.4 | 0 | 9364580.16 | 0 | 15800601.6 | 0 | 326273.35 | 16677515.52 | 48296146 |  | 564494183.22 | 394272062.138 | 958766245.358 | 102278562.348 | 128835492.48 | 58408007.52 | 476662742.99 | 67643920 | 285585.48 | 96870242.64 | 26078400 | 1703291.9 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 120 | 88 | 69 | 369 | 348 |  | 0 | 400 | 134 | 7 | 97 | 55 | 0 | 0 | 0 | 0 | 100 | 84 | 32 | 1 | 0 | 0 | 0 | 54 | 55 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 44 | 0 | 120 | 0 | 0 | 178 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 30 | 19 | 0 | 6 | 0 | 0 | 80 | 300 | 260 | 43 | 36 | 90 | 33 | 42 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 21 | 128 | 158 | 48 | 22 | 1 | 88 | 28 | 50 | 49 | 163 | 262 | 65 | 83 | 0 | 185 | 18 | 0 | 9 | 310 | 24 | 5 | 0 | 258 | 0 | 0 | 200 | 0 | 145 | 13 | 100 | 0 | 1 | 0 | 0 | 50 | 0 | 4 | 236 | 0 | 0 | 0 | 105 | 100 | 0 | 17 |  | 931 | 0 | 350 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 0 | 0 | 77 | 0 | 165 | 0 | 370 | 0 | 0 | 0 | 0 | 70 | 0 | 3 | 90 | 440 |  | 9806 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 120 | 94 | 70 | 340 | 282 | 0 | 0 | 420 | 135 | 7 | 97 | 55 | 277 | 0 | 0 | 0 | 7 | 50 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 33 | 10 | 0 | 46 | 0 | 120 | 0 | 25 | 177 | 0 | 147 | 0 | 0 | 0 | 0 | 85 | 70 | 84 | 50 | 21 | 35 | 0 | 0 | 80 | 260 | 280 | 189 | 8 | 80 | 19 | 20 | 0 | 51 | 0 | 50 | 43 | 18 | 11 | 33 | 21 | 156 | 126 | 52 | 22 | 0 | 91 | 28 | 50 | 49 | 163 | 308 | 35 | 88 | 0 | 184 | 18 | 0 | 9 | 285 | 24 | 8 | 0 | 286 | 19 | 0 | 200 | 0 | 149 | 0 | 100 | 55 | 50 | 0 | 110 | 103 | 0 | 0 | 213 | 0 | 17 | 70 | 113 | 100 | 0 | 17 |  | 930 | 0 | 340 | 0 | 115 | 215 | 0 | 0 | 0 | 0 | 40 | 88 | 40 | 64 | 0 | 0 | 0 | 50 | 34 | 97 | 0 | 0 | 43 | 43 | 25 | 22 | 8 | 11 | 0 | 0 | 149 | 0 | 0 | 145 | 0 | 0 | 0 | 79 | 100 | 216 | 0 | 359 | 35 | 0 | 108 | 0 | 84 | 0 | 0 | 109 | 560 |  | 11941 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 300 | 95 | 72 | 412 | 360 | 0 | 0 | 450 | 150 | 7 | 96 | 55 | 335 | 0 | 0 | 0 | 7 | 40 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 44 | 0 | 120 | 0 | 25 | 180 | 0 | 150 | 0 | 0 | 0 |  | 100 | 100 | 85 | 50 | 20 | 40 | 0 | 0 | 80 | 360 | 360 | 214 | 8 | 100 | 36 | 20 | 0 | 51 | 0 | 50 | 43 | 21 | 11 | 33 | 20 | 173 | 160 | 72 | 22 | 0 | 90 | 30 | 51 | 44 | 163 | 300 | 64 | 86 | 0 | 225 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 17 |  | 945 | 16 | 410 | 0 | 115 | 225 | 0 | 0 | 30 | 60 | 40 | 90 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 0 | 0 | 43 | 43 | 32 | 22 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 0 | 0 | 80 | 100 | 220 | 0 | 414 | 105 | 200 | 113 | 100 | 100 | 0 | 0 | 113 | 620
Forecast for Day | 0 | 0 | 0 | 0 | 120 | 95 | 72 | 412 | 360 | 0 | 0 | 450 | 150 | 7 | 96 | 55 | 335 | 0 | 0 | 0 | 7 | 40 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 44 | 0 | 120 | 0 | 25 | 180 | 0 | 150 | 0 | 0 | 0 |  | 100 | 100 | 85 | 50 | 20 | 25 | 0 | 0 | 80 | 360 | 360 | 214 | 8 | 100 | 35 | 20 | 0 | 51 | 0 | 0 | 43 | 21 | 11 | 33 | 20 | 157 | 160 | 72 | 22 | 1.6 | 90 | 30 | 51 | 44 | 163 | 300 | 64 | 86 | 0 | 225 | 18 | 0 | 10 | 341 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 17 |  | 750 | 0 | 410 | 0 | 115 | 225 | 0 | 0 | 0 | 0 | 40 | 90 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 43 | 0 | 22 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 0 |  | 80 | 50 | 220 | 0 | 414 | 105 | 100 | 113 | 100 | 100 | 0 | 8 | 113 | 620
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 120 | 95 | 68 | 339 | 303 | 0 | 0 | 360 | 130 |  | 48 | 0 | 263 | 0 | 0 | 0 | 7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 44 | 0 | 120 | 0 | 6 | 178 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 35 | 0 | 0 | 80 | 260 | 265 | 177 | 8 | 82 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 15 | 96 | 161 | 0 | 22 | 0 | 91 | 28 | 50 | 50 | 110 | 285 | 20 | 88 | 0 | 185 | 18 | 0 | 10 | 285 | 24 | 8 | 0 | 0 | 0 | 0 | 80 | 0 | 80 | 11 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 124 | 0 | 0 | 0 | 9 | 100 | 0 | 17 | 0 | 935 | 0 | 340 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 110 | 0 | 0 | 0 | 53 | 0 | 130 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 400 | 0
199
| Minimum Generation |  | 9121 | 7:00
| Highest Generation |  | 11941 | 19:30
| Day Peak Generation |  | 9806 | 10:00
| Evening Peak Generation |  | 11941 | 19:30
| HVDC Max Flow |  | 936 | 3:00
| HVDC EvPeak Flow |  | 930 | 19:30
| Load factor L.F |  | 87.16%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-09-11
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-09-10 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9806 | MW Hour : | 10:00 | Min. Gen. at | 8:00 | 8190 | MW
Evening Peak Generation : |  | 11941 | MW Hour : | 19:30 | Available Max Generation : |  | 14997 | MW
E.P. Demand (at gen end) : |  | 11941 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 11500 | MW
Maximum Generation : |  | 11941 | MW Hour : | 19:30 | Reserve(Generation end) |  | 3497 | MW
Total Gen. (MKWH) : |  | 249.7728 | System Load Factor : | 87.16% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -68 | MW at | 19:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-09-11
Actual : | 93.2 | Ft.(MSL) , | Rule curve : | 100.3 | Ft.( MSL )
Gas Consumed : | Total = | 1159.72 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 160686569.868
: |  | Coal : | 67643920 | Oil : | 573532985.63 | Total : | 801863475.498
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4104.6801 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1396.9548 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1251.8277 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1131.2038 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1022.2128 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 824.8925 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 459.777 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 212.3489 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 636.205 |  |  | 0 | 0%
Total | 0 |  | 11040.1025 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 9) Bhola 225 MW GT-2 & ST
|  |  |  | 2) Bibiyana #3 | 10) Sirajganj unit-1 ST
3) Ghorasal Unit-1,2,3,4,7
4) Ashuganj unit-3,4
5) Kaptai-1,2,5
6) Raozan #1,2
7) Sirajganj #2
8) Baghabari-71 MW & 100 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Kodda-Rajendrapur 132 kV Ckt-1 tripped at 11:11 from both ends showing Z1, main protection relay at
Kodda end & Dist. R-phase, Z1 at Rajendrapur end and was switched on at 11:29.
b) ACE Kodda Summit 149 MW tripped at 11:12 due to low voltage and was synchronized at 12:39.
c) Siddirganj 335 MW GT & STG were synchronized at 11:41 and 13:11 respectively.
d) Ashuganj 225 MW STG was synchronized at 11:58.
e) Mymensingh 132/33 kV T1 transformer tripped at 10:24 due to fire at 33 kV incoming breaker & |  |  |  |  | Mymensing zone (Except Tangail-Kishoreganj) isolated due to above trouble
associated CT3 while charging 33 kV Muktagacha Feeder. |  |  |  |  | at Mymensingh grid. All running P/P at Mymensingh zone tripped.
About 480 MW power interruption occurred under Mymensing zone
from 10:24 to 11:08.
f) Mymensingh-Kishoreganj 132 kV Ckt-1 was switched on at 11:08 and Restored power to Mymensingh Zone.
g) Aminbazar-Manikganj 132 kV Ckt-1 tripped at 13:25 from Manikganj end showing Dist. Relay and was
switched on at 13:37.
h) Mymensingh 132/33 kV T3 Transformer 132 kV side was charged at 12:37.
i) Ashuganj 132 kV Bus-1 was switch on at 17:00.
j) Ghorashal 132 kV Bus-1, Joydebpur 132 kV Ckt-1 & Narshingdi 132 kV Ckt were under shut down from
15:49 to 21:05 due to flashing at Ghorashal 132 kV Bus-1.
k) Kabirpur 132/33 kV T1 transformer was shut down at 6:30(11/09/2020) for C/M.
l) Siddirganj 132/33 kV T1 transformer was shut down at 6:20(11/09/2020) for C/M. |  |  |  |  | About 15 MW power interruption has been occurring under Siddirganj S/S
area since 6:20(11/09/2020).
m) Mymensingh 132/33 kV T1 transformer 33 kV Bus was shut down at 06:20(11/09/2020) for Bus DS
replacement work by Energypack.
n) Madunaghat-Chandraghona 132 kV Ckt-2 was shut down at 23:53 due to 902 CB trip.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-09-10 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 120 | 2855100
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 70 | 1611904 | Engine problem
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 94 | 211391 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 340 | 8181760 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 282 | 7307000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 8683750 | Frequency control.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 7 | 199680 | Fuel Shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 135 | 3193571 | GT-1 Under S/D due to gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 97 | 2306184
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1307452
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 100 | 507240
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 361440
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 7 | 1570560 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 277 | 4869729 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 50 | 1581264 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel Shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 977760
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1993920
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1008542
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 918330
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 45 | 1216320 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 753700
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 804900
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 10 | 236976 | Low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 286 | 6716834 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 19 | 121109 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 494520 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 93765 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3149280
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 103 | 1360692
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 431040 | Fuel Shortage
| Dhaka area Total |  |  |  | 5895 | 3085 | 65025713
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2800000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 297345
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 110295
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 799680
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1057724 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 177 | 4169024
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 147 | 2813611
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 605944
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 70 | 221760 | High voltage
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2369280
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 466848
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 35 | 653280
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 84 | 1551360 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 23641
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 213 | 5402073 | Low demand
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 17 | 57708 | Low demand
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2369280
| Chattogram area Total |  |  |  | 2266 | 1290 | 25768853
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 1913438 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 189 | 3429000 | Gas shortage
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 260 | 6823900 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 280 | 6522000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 19 | 484200 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 20 | 478560 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 301090 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1243730
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 50 | 1154181 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 200016
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 2048490
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 55 | 227520
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 426132 | Engine problem
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 219960
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 156 | 3477120
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 818900
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 452242 | Engine problem
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 503970
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 70 | 505020 | Low demand
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 2555280
| Cumilla Area Total |  |  |  | 2980 | 1607 | 33784749
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 126 | 3000430 | Machine problem
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 467892
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 52 | 1100160 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 5500
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 4495200
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 110 | 1184400 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 510 | 10253582
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 91 | 2128000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 28 | 657360 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3522763
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 308 | 6193000
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1243200
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 49 | 1170288
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 159120 | Engine problem
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 35 | 1096896 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 88 | 2038080
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 184 | 4635450
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 420000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 552024
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 7183300 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 212220
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1340 | 31211701
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 930 | 22367273
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 2591040
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 215 | 3607680
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 15184 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 340 | 8373600 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 466125
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 722880
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 35 | 471360 | Engine problem
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Reserve
| Khulna Area Total |  |  |  | 2284 | 1775 | 38615142
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 64 | 597120 | Line over load
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 40 | 753361
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 88 | 2105998 | GT-2 Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 79 | 1821667 | Engine problem
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 560 | 11001400
| Barisal Area Total |  |  |  | 1054 | 831 | 16279546
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 295248
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 34 | 174930 | Engine problem
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 43 | 306800 | Engine problem
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 145 | 3561900 | ST Under maint.
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 216 | 4455636 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 359 | 8596145 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 187900
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 488160
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 8 | 186372 | Engine problem
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 228204
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 375840 | Engine problem
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 97 | 1097472
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 108 | 986784
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 2256768
| Rajshahi Area Total |  |  |  | 2183 | 1270 | 23198159
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 149 | 3569700 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Machine problem
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 84 | 2036160 | Engine problem
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 29527
| Rangpur Area Total |  |  |  | 605 | 233 | 5635387
| Total |  |  |  | 19892 | 11941 | 249772832
| Eastern Grid Total |  |  |  | 13766 | 7832 | 166044598
| Western Grid Total |  |  |  | 6126 | 4109 | 83728234
| National Grid Total |  |  |  | 19892 | 11941 | 249772832
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-09-10
| (a) ENTIRE EASTERN GRID : |  | 7635 | MW | (b) ENTIRE WESTERN GRID : |  | 3819 | MW
| i) Dhaka area |  | 3979 | MW | i) Khulna area |  | 1512 | MW
| ii) Chittagong area |  | 1192 | MW | ii) Rajshahi area |  | 1225 | MW
| iii) Comilla area |  | 1153 | MW | iii) Barisal area |  | 343 | MW
| iv) Mymensingh area |  | 803 | MW | iv) Rangpur area |  | 739 | MW
| v) Sylhet area |  | 508 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11454 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 124 | 12:00 | Sherpur | 112 | 24:00 | Jhenida | 116 | 19:00
| Munsiganj | 130 | 3:00 | Srimongal | 48 | 19:00 | Bottail | 128 | 19:00
| Sonargaon | 74 | 1:00 | Shahjibazar | 123 | 20:00 | G.K Project | 56 | 20:00
| Shyampur | 188 | 0:00 | Fenchuganj | 43 | 19:30 | Faridpur | 187 | 0.83333
| Bhulta | 195 | 1:00 | Kulawara | 43 | 20:00 | Madaripur | 100 | 0.91667
| Madanganj | 60 | 10:00 | Sylhet | 130 | 19:00 | Sariatpur | 62 | 20:00
| Shitalakhya | 121 | 12:00 | Chatak | 29 | 1:00 | Gopalganj | 96 | 19:00
| Rahim steel | 15 | 10:00 | Sunamganj | 47 | 22:00 | Bagerhat | 95 | 19:30
| Matuail | 78 | 10:00 | Biani Bazar | 57 | 19:30 | Mongla | 44 | 24:00
| Ghorasal | 75 | 23:00 | Comilla (S) | 170 | 20:00 | Satkhira | 110 | 0.875
| Narsingdi | 160 | 21:00 | Comilla(N) | 107 | 19:30 | Gallamari | 47 | 13:00
| Haripur (SBU) | 94 | 20:00 | Chandpur | 107 | 22:00 | Magura | 55 | 0.8125
| Ullon | 56 | 14:00 | Feni | 117 | 21:00 | Norail | 41 | 21:00
| Hasnabad | 211 | 21:00 | Chowmuhani | 180 | 19:00 | Chuadanga | 90 | 21:00
| Magbazar | 102 | 10:00 | Ashuganj | 63 | 23:00 | Barisal(N) | 44 | 0.79167
| Maniknagar | 94 | 10:00 | Daudkandi | 140 | 20:00 | Barisal (S) | 100 | 0.77083
| Bangabhaban | 36 | 10:00 | B.Baria | 157 | 20:00 | Patuakhali | 122 | 1904-01-02
| Narinda | 92 | 13:00 | Ramganj | 118 | 21:00 | Bhandaria | 55 | 0.875
| Dhanmondi | 185 | 13:00 | Chaddagram | 35 | 18:30 | Borhan Uddin | 45 | 22:00
| Lalbag | 90 | 13:00 | PHP | 10 | 19:30 | Ishurdi | 62 | 19:30
| Madartek | 73 | 22:00 | Madunaghat | 63 | 15:00 | Ruppur Paromanobik | 2 | 1:00
| Dhaka University |  |  | Hathazari | 100 | 0.8125 | Natore | 120 | 1:00
| Fatullah | 38 | 0.41667 | Khulshi | 199 | 0.5 | Bogra | 167 | 20:00
| Mirpur | 102 | 18:00 | Halishahar | 139 | 0.79167 | Noagaon | 131 | 21:00
| Kalyanpur | 93 | 18:30 | Baraulia | 155 | 0.95833 | Rajshahi | 145 | 1:00
| Gulshan | 120 | 16:00 | Sikalbaha | 27 | 0.77083 | Rajshahi New | 10 | 1:00
| Uttara | 82 | 11:00 | Dohazari | 84 | 0.77083 | C.Nawabganj | 75 | 21:00
| Uttara New | 30 | 18:30 | Cox'sbazar | 99 | 0.875 | Amnura | 46 | 21:00
| Kamrangirchar | 95 | 19:00 | Chandraghona | 30 | 0.77083 | Pabna | 119 | 20:00
| Savar | 129 | 19:00 | Kaptai | 4.5 | 0.77083 | Shahjadpur | 95 | 19:30
| Bhasantec | 146 | 12:00 | A. Khaer Stl. | 0 | 0.041667 | Serajganj | 90 | 20:00
| Agargaon | 74 | 11:00 | Bakulia | 100 | 0.5 | Niyamatpur | 60 | 21:00
| Satmosjid | 98 | 19:00 | Julda | 22 | 0.041667 | Joypurhat | 56 | 20:00
| Tongi | 91 | 0.375 | TK chemical | 29 | 0.79167 | Sherpur(Bogura) | 47 | 20:00
| Kabirpur | 223 | 15:00 | Modern Steel | 15 | 0.16667 | Mohastangor | 50 | 20:00
| Basundhara | 140 | 12:00 | Shahmirpur | 29 | 0.58333 | Rangpur | 152 | 21:00
| Manikganj | 76 | 0.91667 | Khagrachhari | 26 | 0.25 | Lalmonirhat | 49 | 1:00
| Joydevpur | 133 | 9:00 | Matarbari | 31.5 | 0.91667 | Saidpur | 91 | 19:00
| New Tongi | 117 | 9:00 | Baroiar Hat | 38 | 0.79167 | Purbasadipur | 102 | 19:00
| Korda | 232 | 18:30 | Rangamati | 12 | 0.77083 | Thakurgaon | 86 | 19:00
| Dhamrai | 82 | 19:30 | Abul Khair 230 | 139 | 0.16667 | Palashbari | 129 | 20:00
| Rajendrapur | 94 | 19:00 | BSRM | 100 | 0.083333 | Barapukuria | 55 | 21:00
| Valuka | 132 | 18:00 | GPH Ispat | 76 | 0.29167 | Panchagar | 57 | 21:00
| Tangail | 199 | 20:00 | Goalpara | 29 | 1 | Joldhaka | 27 | 20:00
| Mymensing | 150 | 1:00 | Central s/s | 90 | 20:00 | Kurigram | 59 | 21:00
| Kishorganj | 140 | 23:00 | Noapara | 59 | 19:00
| Netrokona | 112 | 1:00 | Jessore | 122 | 20:00
| Jamalpur | 137 | 22:00 | Benapol | 50 | 19:30
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-09-10 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 396 | 7:00 | 386 | 9:00 | Kaliakoir | 377 | 0.25 | 364 | 0.375
| Bheramara | 393 | 7:00 | 386 | 20:00 | Bhulta | 387 | 0.25 | 370 | 0.41667
| Ashuganj(N) | 394 | 6:00 | 379 | 10:00 | Gopalganj | 418 | 0.25 | 399 | 0.77083
| Payra | 417 | 2:00 | 410 | 18:30
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 232 | 4:00 | 230 | 1:00 | Comilla (N) | 232 | 19:00 | 227 | 10:00
| Ishurdi | 236 | 18:00 | 228 | 2:00 | Hathazari | 226 | 2:00 | 220 | 7:00
| Ashuganj | 236 | 1:00 | 230 | 9:00 | Megnaghat | 230 | 4:00 | 224 | 11:00
| Serajganj | 232 | 8:00 | 227 | 4:00 | Fenchuganj | 239 | 7:00 | 233 | 11:00
| Baghabari | 243 | 6:00 | 237 | 19:00 | Siddhirganj | 229 | 4:00 | 219 | 10:00
| Barapukuria | 237 | 6:00 | 228 | 18:30 | Maniknagar | 228 | 6:00 | 217 | 10:00
| Bogra | 227 | 18:00 | 216 | 19:00 | Agargaon | 226 | 6:00 | 214 | 10:00
| Rajshahi | 227 | 18:00 | 218 | 13:00 | Barisal | 245 | 6:00 | 240 | 15:00
| Khulna South | 236 | 8:00 | 224 | 18:00 | AKSML | 225 | 6:00 | 218 | 2:00
| Rampura | 228 | 5:00 | 218 | 10:00 | BSRM | 225 | 19:00 | 219 | 2:00
| Haripur | 227 | 4:00 | 216 | 10:00 | Bibiyana | 236 | 2:00 | 229 | 10:00
| Hasnabad | 226 | 5:00 | 215 | 10:00 | Bhulta | 230 | 19:00 | 218 | 17:00
| Shyampur | 224 | 3:00 | 214 | 10:00 | Ashuganj (S) | 235 | 6:00 | 229 | 10:00
| Aminbazar | 226 | 3:00 | 216 | 9:00 | Kaliakoir | 230 | 3:00 | 221 | 9:00
| Tongi | 227 | 4:00 | 217 | 9:00 | GPH | 222 | 3:00 | 217 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 129 | 1:00 | 125 | 9:00 | Hathazari | 135 | 0.77083 | 131 | 0.625
| Munsiganj | 130 | 3:00 | 126 | 16:00 | Khulshi | 134 | 0.25 | 130 | 0.375
| Sonargaon | 129 | 6:00 | 124 | 10:00 | Halishahar | 137 | 0.25 | 131 | 0.625
| Shyampur | 132 | 3:00 | 125 | 10:00 | Baraulia | 135 | 0.79167 | 131 | 0.083333
| Bhulta | 122 | 3:00 | 119 | 12:00 | Sikalbaha | 137 | 19:00 | 133 | 0.083333
| Madanganj | 132 | 17:00 | 129 | 4:00 | Dohazari | 133 | 19:00 | 128 | 0.625
| Shitalakhya | 140 | 3:00 | 128 | 12:00 | Cox'sbazar | 125 | 0.375 | 120 | 0.77083
| Rahim steal | 130 | 2:00 | 125 | 10:00 | Chandraghona | 134 | 0.041667 | 131 | 0.41667
| Matuail | 129 | 1:00 | 125 | 9:00 | Kaptai | 135 | 1:00 | 130 | 0.41667
| Ghorasal | 138 | 7:00 | 132 | 17:00 | A. Khaer Stl. | 133 | 0.25 | 130 | 8:00
| Narsinghdi | 126 | 6:00 | 120 | 1:00 | Bakulia | 135 | 0.20833 | 131 | 0.41667
| Haripur (SBU) | 130 | 5:00 | 125 | 9:00 | Julda | 137 | 0.77083 | 132 | 0.58333
| Ullon | 132 | 4:00 | 124 | 10:00 | TK Chemical | 136 | 0.79167 | 131 | 17:00
| Hasnabad | 137 | 19:00 | 126 | 12:00 | Modern Steel | 135 | 0.79167 | 130 | 0.66667
| Magbazar | 132 | 5:00 | 123 | 10:00 | Shahmirpur | 136 | 0.79167 | 132 | 0.20833
| Maniknagar | 132 | 4:00 | 123 | 11:00 | Khagrachhari | 133 | 0.25 | 130 | 0.083333
| Bangabhaban | 132 | 4:00 | 123 | 11:00 | Matarbari | 129 | 0.25 | 121 | 0.083333
| Narinda | 132 | 4:00 | 123 | 11:00 | Baroiar Hat | 131 | 0.041667 | 128 | 0.54167
| Dhanmondi | 132 | 4:00 | 124 | 10:00 | Rangamati | 134 | 0.875 | 130 | 11:00
| Lalbag | 136 | 19:00 | 124 | 10:00 | Goalpara S/S | 136 | 10:00 | 132 | 15:00
| Madartek | 133 | 6:00 | 123 | 10:00 | Khulna Central S/S | 136 | 0.25 | 132 | 19:00
| Dhaka University |  |  |  |  | Noapara | 132 | 5:00 | 128 | 1:00
| Fatuiiah | 133 | 0.16667 | 125 | 10:00 | Jessore | 130 | 11:00 | 121 | 19:00
| Mirpur | 130 | 20:00 | 124 | 9:00 | Benapol | 130 | 10:00 | 120 | 19:00
| Kalyanpur | 132 | 19:00 | 124 | 10:00 | Jhenida | 128 | 0.45833 | 114 | 19:00
| Gulshan | 131 | 3:00 | 123 | 10:00 | Bottail | 136 | 15:00 | 126 | 19:00
| Uttara | 131 | 21:00 | 124 | 9:00 | G.K Project | 140 | 0.75 | 136 | 19:00
| Uttara New | 134 | 20:00 | 126 | 9:00 | Faridpur | 132 | 7:00 | 126 | 22:00
| Kamrangirchar | 136 | 19:00 | 122 | 11:00 | Madaripur | 140 | 0.25 | 130 | 18:30
| Savar | 130 | 6:00 | 123 | 10:00 | Shariyatpur S/S | 137 | 0.25 | 129 | 22:00
| Bhasantec | 133 | 19:00 | 123 | 10:00 | Gopalganj | 137 | 6:00 | 129 | 21:00
| Agargaon | 134 | 19:00 | 124 | 10:00 | Bagerhat | 131 | 8:00 | 122 | 3:00
| Satmosjid | 133 | 6:00 | 124 | 10:00 | Mongla | 129 | 0.33333 | 120 | 1:00
| Tongi | 137 | 0.16667 | 127 | 9:00 | Satkhira | 135 | 0.33333 | 127 | 21:00
| Kabirpur | 134 | 8:00 | 128 | 16:00 | Gallamari | 136 | 8:00 | 132 | 2:00
| Basundhara | 131 | 4:00 | 123 | 10:00 | Magura | 127 | 11:00 | 113 | 19:00
| Manikganj | 139 | 1:00 | 132 | 19:00 | Norail | 126 | 0.45833 | 109 | 19:00
| Joydevpur | 140 | 24:00 | 130 | 17:00 | Chuadanga | 122 | 18:00 | 104 | 21:00
| New Tongi | 136 | 1904-01-02 | 127 | 9:00 | Barisal(N) | 139 | 6:00 | 134 | 15:00
| Kodda | 137 | 24:00 | 121 | 0.375 | Barisal (S) | 138 | 0.083333 | 132 | 15:00
| Dhamrai | 135 | 6:00 | 128 | 10:00 | Patuakhali(S) | 132 | 0.20833 | 126 | 1:00
| Rajendrapur | 134 | 23:00 | 120 | 12:00 | Bhandaria | 127 | 7:00 | 116 | 21:00
| Valuka | 132 | 12:00 | 115 | 1:00 | Ishurdi | 138 | 6:00 | 133 | 20:00
| Tangail | 135 | 5:00 | 128 | 18:00 | Ruppur Paromanobik | 137 | 6:00 | 133 | 21:00
| Mymensing | 135 | 12:00 | 121 | 1:00 | Natore | 138 | 18:00 | 130 | 3:00
| Kishorganj | 130 | 17:00 | 121 | 1:00 | Bogra | 137 | 6:00 | 130 | 20:00
| Netrokona | 130 | 12:00 | 106 | 19:00 | Noagaon | 133 | 6:00 | 123 | 20:00
| Jamalpur | 139 | 4:00 | 132 | 18:30 | Rajshahi | 136 | 6:00 | 130 | 2:00
| Sherpur | 138 | 4:00 | 130 | 18:30 | Rajshahi New | 138 | 18:00 | 130 | 13:00
| Srimongal | 136 | 7:00 | 131 | 0.875 | C.Nawabganj | 137 | 18:00 | 129 | 13:00
| Shahjibazar | 134 | 6:00 | 130 | 0.041667 | Amnura | 135 | 5:00 | 128 | 13:00
| Fenchuganj | 135 | 6:00 | 132 | 0.041667 | Pabna | 135 | 8:00 | 130 | 18:30
| Khulawara | 135 | 8:00 | 132 | 0.041667 | Shahjadpur | 139 | 6:00 | 135 | 1:00
| Sylhet | 134 | 9:00 | 130 | 0.041667 | Serajganj | 133 | 18:00 | 129 | 20:00
| Chatak | 133 | 7:00 | 128 | 1:00 | Niyamatpur | 131 | 6:00 | 120 | 1:00
| Sunamganj | 132 | 9:00 | 126 | 0.041667 | Joypurhat | 133 | 6:00 | 122 | 19:30
| Biani Bazar | 133 | 9:00 | 127 | 0.041667 | Sherpur(Bogura) | 136 | 6:00 | 130 | 3:00
| Comilla(s) | 126 | 7:00 | 120 | 13:00 | Mohastangor | 135 | 6:00 | 126 | 19:00
| Comilla(n) | 134 | 19:30 | 131 | 12:00 | Rangpur | 131 | 6:00 | 117 | 19:00
| Chandpur | 132 | 1:00 | 125 | 24:00 | Lalmonirhat | 130 | 6:00 | 118 | 18:30
| Feni | 131 | 18:30 | 127 | 11:00 | Saidpur | 131 | 17:00 | 120 | 19:00
| Chowmuhani | 127 | 7:00 | 124 | 18:00 | Purbasadipur | 129 | 6:00 | 112 | 19:00
| Ashuganj | 135 | 12:00 | 130 | 1:00 | Thakurgaon | 127 | 21:00 | 114 | 19:00
| Daudkandi | 129 | 19:00 | 125 | 10:00 | Palashbari | 130 | 6:00 | 121 | 19:00
| B.Baria | 130 | 8:00 | 126 | 21:00 | Barapukuria | 137 | 6:00 | 128 | 18:30
| Ramganj | 126 | 9:00 | 118 | 24:00 | Panchagar | 127 | 6:00 | 108 | 19:00
| Chaddagram | 133 | 19:00 | 128 | 11:00 | Joldhaka | 132 | 6:00 | 119 | 18:30
| PHP | 131 | 19:00 | 126 | 16:00 | Kurigram | 129 | 6:00 | 113 | 19:00
| Madanhat | 137 | 5:00 | 132 | 11:00

## L-Curve
Date | 2020-09-10
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 132 | 7533 | 4022 | 11555 |  |  |  | QF-LDC-11
0:30 | 88 | 7567.5 | 3949.5 | 11517 | Date: | 2020-09-10
1:00 | 44 | 7602 | 3877 | 11479
1:30 | 23 | 7548.5 | 3808.5 | 11357
2:00 | 2 | 7495 | 3740 | 11235
2:30 | 12 | 7462.5 | 3641.5 | 11104 | [5 empty] | Gen. at Eve. Peak | 11941 | 11941 MW (19:30 )
3:00 | 22 | 7430 | 3543 | 10973 | [6 empty] | 19:30
3:30 | 27.5 | 7331.5 | 3505.5 | 10837 | [5 empty] | Gen. at Day Peak | 9806 | 9806 MW (10:00 )
4:00 | 33 | 7233 | 3468 | 10701 | [6 empty] | 10:00
4:30 | 27.5 | 7178.5 | 3460 | 10638.5 | [5 empty] | Highest Generation | 11941
5:00 | 22 | 7124 | 3452 | 10576 | [6 empty] | 19:30
5:30 | 61 | 6891.5 | 3298.5 | 10190
6:00 | 100 | 6659 | 3145 | 9804
6:30 | 232 | 6323.5 | 3139 | 9462.5
7:00 | 364 | 5988 | 3133 | 9121
7:30 | 370.5 | 6006 | 3130 | 9136
8:00 | 377 | 6024 | 3127 | 9151
8:30 | 431 | 6201 | 3151.5 | 9352.5
9:00 | 485 | 6378 | 3176 | 9554
9:30 | 500 | 6505.5 | 3174.5 | 9680
10:00 | 515 | 6633 | 3173 | 9806
10:30 | 441 | 6403.5 | 3141 | 9544.5
11:00 | 367 | 6174 | 3109 | 9283
11:30 | 292 | 6232 | 3112.5 | 9344.5
12:00 | 217 | 6290 | 3116 | 9406
12:30 | 233.5 | 6453.5 | 3170 | 9623.5
13:00 | 250 | 6617 | 3224 | 9841
13:30 | 217.5 | 6541 | 3148 | 9689
14:00 | 185 | 6465 | 3072 | 9537
14:30 | 182.5 | 6661.5 | 3075 | 9736.5
15:00 | 180 | 6858 | 3078 | 9936
15:30 | 210 | 6762.5 | 3043 | 9805.5
16:00 | 240 | 6667 | 3008 | 9675
16:30 | 248.5 | 6533 | 2995 | 9528
17:00 | 257 | 6399 | 2982 | 9381
17:30 | 253 | 6384 | 2991.5 | 9375.5
18:00 | 249 | 6369 | 3001 | 9370
18:30 | 158.5 | 7069.5 | 3400 | 10469.5
19:00 | 68 | 7770 | 3799 | 11569
19:30 | 23 | 7832 | 4109 | 11941
20:00 | 8 | 7814 | 4121 | 11935 |  |  |  | Executive Engineer
20:30 | 65.5 | 7779.5 | 4131.5 | 11911 |  |  |  | Network Operation Division
21:00 | 123 | 7745 | 4142 | 11887
21:30 | 139 | 7737.5 | 4146 | 11883.5
22:00 | 155 | 7730 | 4150 | 11880 |  |  |  |  | Page 6 of 7
22:30 | 170 | 7662.5 | 4137 | 11799.5
23:00 | 185 | 7595 | 4124 | 11719
23:30 | 158.5 | 7564 | 4073 | 11637
24:00 | 132 | 7533 | 4022 | 11555
11941 MW (19:30 )
9806 MW (10:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-09-10 |  | Energy | 249772832
[10 empty] | 2020-09-10 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3974 | 930 | 2119 | 3122 | 710 | 45 | 572 | 0 | 164
0:30 | 3931 | 932.5 | 2104 | 3164.5 | 695 | 45 | 524.5 | 0 | 161 | Date: | 2020-09-10
1:00 | 3888 | 935 | 2089 | 3207 | 680 | 45 | 477 | 0 | 158
1:30 | 3907.5 | 935 | 2101.5 | 3097.5 | 680 | 45 | 433.5 | 0 | 157 | [7 empty] | Total Energy | 249.7728 | Total Energy Gen 249.773 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 249.773 MKWHr
2:00 | 3927 | 935 | 2114 | 2988 | 680 | 45 | 390 | 0 | 156 | [7 empty] | Energy not Served | 0
2:30 | 3908 | 935.5 | 2118 | 2885.5 | 680 | 45 | 378 | 0 | 154 | [7 empty] | Energy Requirement | 249.7728
3:00 | 3889 | 936 | 2122 | 2783 | 680 | 45 | 366 | 0 | 152
3:30 | 3889 | 935.5 | 2100 | 2675 | 690 | 45 | 354.5 | 0 | 148 | [6 empty] | Shortage
4:00 | 3889 | 935 | 2078 | 2567 | 700 | 45 | 343 | 0 | 144
4:30 | 3889.5 | 935 | 2070.5 | 2512 | 700 | 45.5 | 343 | 0 | 143
5:00 | 3890 | 935 | 2063 | 2457 | 700 | 46 | 343 | 0 | 142
5:30 | 3788.5 | 935 | 2012.5 | 2330 | 660 | 44.5 | 287.5 | 0 | 132
6:00 | 3687 | 935 | 1962 | 2203 | 620 | 43 | 232 | 0 | 122
6:30 | 3535.5 | 935 | 1943.5 | 2076.5 | 625 | 43.5 | 184 | 0 | 118 |  |  |  |  | Coal
7:00 | 3384 | 935 | 1925 | 1950 | 630 | 44 | 136 | 0 | 114
7:30 | 3387 | 935.5 | 1924.5 | 1971 | 615 | 44 | 136 | 0 | 119 |  |  |  | Oil |  |  |  | ,
8:00 | 3390 | 936 | 1924 | 1992 | 600 | 44 | 136 | 0 | 124
8:30 | 3452.5 | 935.5 | 2049.5 | 2003.5 | 600 | 44 | 128 | 0 | 124
9:00 | 3515 | 935 | 2175 | 2015 | 600 | 44 | 120 | 0 | 124
9:30 | 3540 | 933 | 2189.5 | 2093 | 595 | 44 | 136 | 0 | 126
10:00 | 3565 | 931 | 2204 | 2171 | 590 | 44 | 152 | 0 | 128
10:30 | 3441.5 | 930.5 | 2148.5 | 2102 | 590 | 22 | 152 | 0 | 132
11:00 | 3318 | 930 | 2093 | 2033 | 590 | 0 | 152 | 0 | 136
11:30 | 3400.5 | 930 | 2127.5 | 1963 | 590 | 23 | 152 | 0 | 134
12:00 | 3483 | 930 | 2162 | 1893 | 590 | 46 | 152 | 0 | 132
12:30 | 3540.5 | 930 | 2179.5 | 2029 | 590 | 46 | 152 | 0 | 134
13:00 | 3598 | 930 | 2197 | 2165 | 590 | 46 | 152 | 0 | 136
13:30 | 3598 | 930 | 2197 | 2165 | 590 | 46 | 152 | 0 | 136
14:00 | 3598 | 930 | 2197 | 2165 | 590 | 46 | 152 | 0 | 136
14:30 | 3678.5 | 930 | 2114 | 2231 | 590 | 46 | 145 | 0 | 134
15:00 | 3759 | 930 | 2031 | 2297 | 590 | 46 | 138 | 0 | 132
15:30 | 3751.5 | 930 | 2003 | 2199.5 | 590 | 46 | 140 | 0 | 134
16:00 | 3744 | 930 | 1975 | 2102 | 590 | 46 | 142 | 0 | 136
16:30 | 3728.5 | 930 | 1972 | 1977.5 | 589 | 46 | 146 | 0 | 132
17:00 | 3713 | 930 | 1969 | 1853 | 588 | 46 | 150 | 0 | 128
17:30 | 3722.5 | 930 | 1898.5 | 1864 | 548 | 46 | 235.5 | 0 | 129
18:00 | 3732 | 930 | 1828 | 1875 | 508 | 46 | 321 | 0 | 130
18:30 | 3826.5 | 930 | 1973 | 2475.5 | 559 | 46 | 513.5 | 0 | 146
19:00 | 3921 | 930 | 2118 | 3076 | 610 | 46 | 706 | 0 | 162
19:30 | 3970 | 930 | 2132 | 3249 | 709 | 46 | 749 | 0 | 156
20:00 | 3962 | 930 | 2119 | 3241 | 709 | 45 | 759 | 0 | 170
20:30 | 3977.5 | 930 | 2123.5 | 3195 | 709 | 45 | 763 | 0 | 168
21:00 | 3993 | 930 | 2128 | 3149 | 709 | 45 | 767 | 0 | 166
21:30 | 3988.5 | 930.5 | 2134.5 | 3142 | 709.5 | 45 | 766.5 | 0 | 167
22:00 | 3984 | 931 | 2141 | 3135 | 710 | 45 | 766 | 0 | 168
22:30 | 3974 | 930.5 | 2128 | 3128.5 | 710 | 45 | 715.5 | 0 | 168
23:00 | 3964 | 930 | 2115 | 3122 | 710 | 45 | 665 | 0 | 168
23:30 | 3969 | 930 | 2117 | 3122 | 710 | 45 | 618.5 | 0 | 166 | Max Temp. in Dhaka |  | 31.5° C
24:00 | 3974 | 930 | 2119 | 3122 | 710 | 45 | 572 | 0 | 164
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 249.773 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 249.773 MKWHr
Note on W13: Author:

## Generation
g | 2020-09-10
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 45 | 45 | 45 | 45 | 46 | 43 | 44 | 44 | 44 | 44 | 0 | 46 | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 45 | 45 | 45 | 45 | 45 | 1057724
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [10 empty] | 2 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 20 | 25 | 25 | 25 | 25 | 25 | 25 | 297345
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 2 | 2 | 19 | 13 | 20 | 11 | 18 | 15 | 11 | 6 | 2 | [9 empty] | 110295
6 | Sikalbaha 225MW CCPP (Gas) | 176 | 176 | 177 | 176 | 176 | 177 | 177 | 177 | 178 | 178 | 177 | 177 | 178 | 177 | 179 | 178 | 177 | 177 |  | 177 | 177 | 177 | 177 | 178 | 176 | 177 | 4169024
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 106 | 104 | 106 | 108 | 109 | 70 | 60 | 47 | 25 | 140 | 140 | 140 | 148 | 147 | 146 | 146 | 147 | 100 |  | 148 | 147 | 148 | 147 | 149 | 148 | 149 | 2813611
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 30 | [16 empty] | 85 |  | 85 | 85 | 85 | 85 | 85 | 68 | 42 | 605944
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [19 empty] | 50 | 50 | 50 | 50 | 50 |  | 0 | 200016
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 307 | 301 | 300 | 307 | 298 | 249 | [5 empty] | 7 | 27 | 176 | 307 | 282 | 270 | 307 |  | 266 | 277 | 271 | 277 | 288 | 296 | 262 | 4869729
18 | Kodda 300 MW PP Unit-2 (Summit) | 283 | 283 | 283 | 286 | 283 | 283 | 250 | 250 | 250 | 258 | 268 | 268 | 268 | 282 | 286 | 283 | 286 | 283 |  | 286 | 286 | 286 | 286 | 298 | 300 | 300 | 6716834
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 36 | 36 | 36 | 36 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 301090
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2855100
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1913438
32 | Ashuganj 50 MW PP | 25 | 25 | 25 | 25 | 25 | 0 |  | 35 | 35 | 33 | 33 | 33 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 484200
33 | Ashuganj 225 MW CCPP | 174 | 169 | 166 | 166 | 166 | 125 | 62 | 25 | 25 | 43 | 47 | 57 | 121 | 178 | 173 | 182 | 182 | 184 |  | 187 | 189 | 194 | 196 | 195 | 196 | 216 | 3429000
34 | Ashuganj 450 MW CCPP(South) | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 285 | 260 | 250 | 255 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 289 | 6522000
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 330 | 300 | 290 | 300 | 260 | 260 | 280 | 260 | 260 | 280 |  | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 6823900
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 20 | 20 | 42 | 42 | 42 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 478560
36 | Chandpur 150 MW CCPP | 80 | 84 | 84 | 88 | 93 | 86 | 85 | 94 | 95 | 90 | 90 | 90 | 80 | 80 | 80 | 82 | 82 | 91 |  | 76 | 80 | 86 | 85 | 85 | 89 | 82 | 2048490
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 341 | 355 | 349 | 342 | 349 | 342 | 344 | 340 | 370 | 369 | 342 | 349 | 366 | 329 | 281 | 280 | 280 | 280 |  | 326 | 340 | 339 | 340 | 340 | 340 | 340 | 8181760
40 | Meghnaghat 450 MW CCPP(MPL) | 340 | 340 | 340 | 340 | 340 | 380 | 340 | 320 | 400 | 400 | 370 | 400 | 420 | 300 | 360 | 360 | 360 | 360 |  | 420 | 420 | 420 | 420 | 420 | 400 | 400 | 8683750
41 | Haripur 360MW CCPP(HPL) | 322 | 321 | 338 | 349 | 349 | 303 | 272 | 251 | 346 | 348 | 349 | 349 | 328 | 254 | 305 | 293 | 293 | 273 |  | 282 | 282 | 282 | 282 | 272 | 272 | 323 | 7307000
42 | RPCL 210MW CCPP | 159 | 161 | 160 | 161 | 159 | 164 | 160 | 160 | 159 | 158 |  | 76 | 84 | 104 | 103 | 92 | 126 | 126 |  | 136 | 126 | 125 | 126 | 124 | 126 | 145 | 3000430
43
44 | Fenchugonj CCPP Phase-1 | 90 | 90 | 90 | 90 | 90 | 90 | 91 | 90 | 91 | 88 | 91 | 88 | 88 | 89 | 88 | 89 | 91 | 88 |  | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 2128000
45 | Fenchugonj CCPP Phase-2 | 28 | 30 | 28 | 28 | 28 | 28 | 28 | 30 | 30 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 30 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 657360
46 | Shajibazar 330 MW CCPP | 260 | 263 | 260 | 261 | 258 | 260 | 260 | 260 | 260 | 262 | 260 | 284 | 283 | 284 | 282 | 285 | 284 | 285 |  | 310 | 308 | 308 | 312 | 287 | 286 | 285 | 6193000
47 | Shahjibazar GTPP Unit- 8 & 9 | 63 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 65 | 65 | 32 | 32 | 30 | 30 | 30 | 30 | 30 | 20 |  | 35 | 35 | 20 | 35 | 35 | 35 | 35 | 1096896
48 | Shahjibazar 86MW PP (Shahjibazar) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 83 | 83 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 50 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 2038080
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 184 | 185 | 185 | 185 | 185 | 172 | 183 | 185 | 185 | 185 | 226 | 224 | 225 | 191 | 223 | 232 | 184 | 184 |  | 184 | 184 | 184 | 184 | 184 | 185 | 184 | 4635450
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 420000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 212220
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 5 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 159120
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 52 | 50 | 50 |  | 52 | 50 | 53 | 53 | 53 | 53 | 53 | 1243200
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 16 | 16 | 16 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 552024
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 300 | 295 | 300 | 300 | 265 | 265 | 280 | 310 | 310 | 290 | 290 | 310 | 265 | 300 | 290 | 280 | 280 |  | 290 | 285 | 270 | 270 | 290 | 280 | 285 | 7183300
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 17 | 17 |  |  |  | 15 |  | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 17 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 918330
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 18 | 18 | 18 | 18 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 18 | 21 | 466848
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 |  |  |  |  | 22 | 22 | 19 | 19 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 361440
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 20 | 20 | 20 | 20 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 467892
63 | Impoprt (Tripura) | 158 | 156 | 152 | 144 | 142 | 122 | 114 | 124 | 124 | 128 | 136 | 132 | 136 | 136 | 132 | 136 | 128 | 130 |  | 162 | 156 | 170 | 166 | 168 | 168 | 164 | 3477120
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 35 | 12 | 4 | 6 | 6 | 6 | 9 | 9 | 6 | 8 | 15 | 22 |  | 33 | 35 | 37 | 42 | 42 | 42 | 42 | 653280
65 | Feni 22MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 426132
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 219960
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 818900
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15 | 15 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 503970
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 30 | 30 | 20 | 12 | 12 |  | 12 | 20 | 22 | 30 | 30 | 30 | 30 | 616320
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 753700
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 33 | 25 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 804900
73 | Ghorashal 108MW PP (Regent) | 92 | 91 | 91 | 92 | 93 | 93 | 94 | 94 | 91 | 88 | 86 | 90 | 91 | 92 | 89 | 91 | 92 | 52 |  | 93 | 94 | 95 | 95 | 95 | 95 | 95 | 211391
| Feni Lanka Power | 50 | [18 empty] | 70 | 70 | 70 | 70 | 70 | 70 | 50 | 505020
| Chowmuhani 113 MW | 107 | 107 | 113 | 113 | 113 | 109 | 99 | 96 | 103 | 105 | 103 | 107 | 113 | 104 | 111 | 110 | 75 | 75 |  | 105 | 113 | 113 | 113 | 113 | 113 | 105 | 2555280
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 100 | 100 | 100 | 100 | 100 | 92 | 98 | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 40 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 1570560
78 | Gazipur 52 MW PP | [20 empty] | 10 | 33 | 42 | 42 | 42 | 25 | 236976
79 | Kodda 150MW PP | 150 | 150 | 150 | 150 | 150 | 82 | 16 | 16 |  | 32 | 32 | 32 | 32 | 16 | 16 | 16 | 16 | 16 |  | 150 | 150 | 150 | 150 | 150 | 150 | 133 | 1993920
80 | Jamalpur 95 MW PP(Powerpac) | 71 | 72 | 72 | 72 | 72 | 71 | 32 | 32 | 32 | 48 |  |  | 32 | 24 | 24 | 24 | 24 | 24 |  | 35 | 52 | 55 | 54 | 55 | 64 | 64 | 1100160
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 16 | 16 | 16 | 16 | 16 | 16 | [11 empty] | 16 | 43 | 42 | 43 | 43 | 43 | 43 | 452242
| Gazipur 100 MW PP | 103 | 103 | 67 | 50 | 50 | 6 |  |  |  | 50 | 102 |  | 50 | 50 | 50 | 34 | 34 | 34 |  | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 1360692
| Kaptai 7 MW Solar PP | [6 empty] | 1 | 2 | 4 | 4 | 6 | 3 | 2 | 1 | 1 | 1 | 1 | [9 empty] | 23641
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | [19 empty] | 13 | 17 | 17 | 17 |  |  | 0 | 57708
82 | Madanganj 102 PP(Summit) | 96 | 96 | 96 | 96 | 96 | 93 | 80 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 96 | 97 | 97 | 97 |  | 97 | 97 | 96 | 97 | 97 | 97 | 96 | 2306184
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 25 | 25 | 25 | 25 | 25 |  |  |  |  | 1 | 12 | 12 | 13 | 12 | 12 | 12 | 12 | 15 |  | 49 | 100 | 100 | 33 | 25 | 23 | 12 | 507240
86 | Meghnaghat CCPP(Summit) | 130 | 132 | 127 | 130 | 135 | 110 | 125 | 138 | 138 | 134 | 124 | 140 | 134 | 140 | 140 | 130 | 125 | 140 |  | 130 | 135 | 135 | 135 | 135 | 140 | 130 | 3193571
87 | Meghnaghat 100 MW(IEL) | 11 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 5 | 7 | 7 | 7 | 199680
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 431040
88 | Ghorashal 78.5 MW PP(MAX) | 71 | 71 | 71 | 71 | 70 | 70 | 70 | 70 | 69 | 69 | 70 | 71 | 71 | 71 | 71 | 69 | 69 | 40 |  | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 1611904
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 30 | [18 empty] | 70 | 70 | 40 | 20 | 20 | 10 | 10 | 221760
92 | Fenchuganj 44MW (Energyprima) | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 47 | 49 | 46 | 49 | 49 | 49 |  | 49 | 49 | 49 | 49 | 50 | 50 | 50 | 1170288
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1243730
94 | Gagnagar 102 MW PP (Digital Power) | 93 | 93 | 93 | 85 | 85 | 85 | 83 | 83 | 75 | 84 | 50 | 50 | 40 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1581264
95 | Patenga 50MW PP (Baraka) | 50 | 50 | 43 | 25 | 25 | 25 |  |  | 6 | 19 | 41 | 50 | 50 | 18 | 19 | 19 | 19 | 19 |  | 26 | 50 | 50 | 50 | 50 | 50 | 50 | 799680
96 | Chattogram 108 MW PP (ECPV) | 84 | 84 | 84 | 79 | 84 | 72 | 25 | 25 | 25 | 30 | 60 | 66 | 75 | 65 | 50 | 50 | 50 | 50 |  | 64 | 84 | 82 | 82 | 78 | 78 | 80 | 1551360
97 | Katpotti 52 MW PP (Sinha) | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | 55 | 47 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 40 | 40 |  | 50 | 55 | 55 | 55 | 55 | 55 | 55 | 1307452
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 17 | 17 | 17 | 17 | 17 | 17 | 55 | 55 | 55 | 55 |  | 55 | 35 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1008542
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 163 | 163 | 163 | 130 | 163 | 163 | 110 | 163 | 163 | 163 | 130 |  | 163 | 163 | 163 | 163 | 163 | 130 | 130 | 3522763
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 1 |  | 2 | 1 | 0 | 0 | 0 | 0 | [9 empty] | 5500
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 17 | 17 | 17 |  |  | 17 | 54 | 54 | 54 | 54 | 54 | 54 | 17 | 17 | 17 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 977760
104 | Keranigonj 300 MW PP (APR) | [19 empty] | 104 | 19 |  |  |  |  | 0 | 121109
105 | Bramhangoan 100 MW PP (Aggreko) | [19 empty] | 50 | [5 empty] | 0 | 494520
106 | Mymensingh 200 MW PP (United) | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 38 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4495200
112 | Aurahati 100MW PP (Aggreko) | [19 empty] | 101 | [5 empty] | 0 | 93765
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 145 | 126 |  | 6 | 72 | 128 | 130 | 129 | 131 |  | 148 | 149 | 149 | 149 | 149 | 149 | 149 | 3149280
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 70 | 70 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2369280
116 | Chandpur 200MW (Desh energy) | [19 empty] | 33 | 55 | 69 | 34 | 34 | 16 | 0 | 227520
117 | Ashuganj 150MW PP (Midland) | 125 | 127 | 128 | 98 | 26 | 10 |  |  |  | 1 | 10 | 10 | 21 | 45 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1154181
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 115 | 95 | 95 | 75 | 55 | 8 | [5 empty] | 2 | 8 | 8 | 8 | 8 | 8 | 8 |  | 40 | 110 | 109 | 115 | 115 | 115 | 115 | 1184400
| Anwara 300 MW PP (United) | 234 | 234 | 234 | 234 | 234 | 249 | 236 | 236 | 236 | 236 | 236 | 235 | 234 | 234 | 234 | 234 | 160 | 160 |  | 213 | 213 | 214 | 216 | 216 | 216 | 216 | 5402073
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 70 | 70 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2369280
120 | Eastern Zone Total | 7602 | 7495 | 7430 | 7233 | 7124 | 6659 | 5988 | 6024 | 6378 | 6633 | 6174 | 6290 | 6617 | 6465 | 6858 | 6667 | 6399 | 6369 |  | 7770 | 7832 | 7814 | 7745 | 7730 | 7595 | 7533 | 166044598
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 115 | 115 | 115 | 115 | 115 | 115 | 102 | 115 | 115 | 115 | 99 | 99 | 99 | 99 | 99 | 103 | 86 | 83 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2591040
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
| Khulna 225 MW CCPP | 160 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 180 | 215 | 220 | 225 | 225 | 225 | 225 | 3607680
129 | Rupsha 105 MW PP (Orion rupsha) | 53 | 35 | 35 | 35 | 35 | [14 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 471360
130
131
132
133
| Barisal 110 MW PP (Summit ) | 80 | 48 | 16 | 16 | [13 empty] | 16 |  | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 597120
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 78 | 77 | 76 | 75 | 76 | 79 | 79 | 77 | 77 | 77 | 76 | 77 | 77 | 77 | 77 | 77 | 77 | 42 |  | 78 | 79 | 79 | 78 | 79 | 78 | 75 | 1821667
| Bhola 225 MW CCPP | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 88 | 88 |  | 88 | 88 | 87 | 87 | 87 | 87 | 87 | 2105998
140 | Bhola 33 MW PP (Venture) | 39 | 39 | 39 | 39 | 34 | 27 | 24 | 23 | 23 | 24 | 25 | 28 | 27 | 28 | 28 | 25 | 27 | 28 |  | 39 | 40 | 38 | 38 | 38 | 38 | 39 | 753361
141 | Noapara 100 MW PP (Bangla Trac) | 40 | 20 | 20 | 10 | [15 empty] | 60 | 100 | 100 | 100 | 100 | 100 | 100 | 722880
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 40 | 40 | 40 | [14 empty] | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 466125
143 | Gopalganj 100 MW Peaking PP | [14 empty] | 2 | 6 | 2 | 8 | [8 empty] | 15184
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 935 | 935 | 936 | 935 | 935 | 935 | 935 | 936 | 935 | 931 | 930 | 930 | 930 | 930 | 930 | 930 | 930 | 930 |  | 930 | 930 | 930 | 930 | 931 | 930 | 930 | 22367273
147 | Bheramara 410 MW CCPP | 340 | 365 | 340 | 340 | 365 | 345 | 350 | 345 | 370 | 350 | 345 | 355 | 345 | 290 | 294 | 295 | 295 | 295 |  | 345 | 340 | 345 | 340 | 345 | 340 | 340 | 8373600
148 | Payra 1320 MW | 530 | 530 | 530 | 550 | 550 | 470 | 480 | 450 | 450 | 440 | 440 | 440 | 440 | 440 | 440 | 440 | 440 | 400 |  | 480 | 560 | 560 | 560 | 560 | 560 | 560 | 11001400
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 148 | 108 |  | 130 | 149 | 149 | 149 | 150 | 150 | 150 | 3569700
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 43 | 50 | 50 | 50 | 50 | 50 | 0 | 295248
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 146 | 146 | 146 | 147 | 146 | 147 | 147 | 147 | 144 | 144 | 145 | 144 | 144 | 115 | 115 | 135 | 145 | 145 |  | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 3561900
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 160 | 160 | 160 | 160 | 160 | 130 | 130 | 148 | 140 | 165 | 150 | 150 | 191 | 140 | 130 | 130 | 130 | 130 |  | 194 | 216 | 213 | 214 | 214 | 190 | 190 | 4455636
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 406 | 414 | 411 | 351 | 340 | 284 | 327 | 330 | 365 | 370 | 340 | 340 | 402 | 326 | 333 | 299 | 291 | 334 |  | 353 | 359 | 357 | 361 | 362 | 400 | 350 | 8596145
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 4 | 17 |  | 34 | 34 | 34 | 34 | 34 |  |  | 174930
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 21 | 21 | 22 | 18 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 488160
163 | Bogura 20 MW PP (Energyprima) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 186372
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 8 | 8 | 8 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 228204
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern) | [25 empty] | 0
167 | Katakhali 50 MW Peaking PP | 36 | [16 empty] | 10 |  | 42 | 43 | 47 | 43 | 43 | 43 | 43 | 306800
168 | Santahar 50 MW Peaking PP | 5 | 24 | [15 empty] | 5 |  | 25 | 25 | 26 | 33 | 32 | 32 | 32 | 187900
169 | Natore 52 MW PP (Rajlanka) | 43 | [12 empty] | 41 | 43 |  |  |  |  | 26 | 43 | 43 | 43 | 43 | 43 | 43 | 375840
170 | Chapainawabganj 100 MW Peaking PP | 96 | 96 | 96 | 73 | 73 | 30 | [10 empty] | 8 | 60 |  | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 1097472
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | [10 empty] | 6 | 33 | 35 |  |  |  |  | 50 | 108 | 110 | 113 | 113 | 113 | 113 | 986784
172 | Confidence Power Bogura Unit-1 113 MW | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 70 | 70 |  | 90 | 109 | 109 | 109 | 109 | 109 | 109 | 2256768
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 98 | 99 | 99 | 98 | 99 | 99 | 75 | 71 | 71 | 70 | 70 | 70 | 70 | 63 | 63 | 84 | 82 | 74 |  | 78 | 84 | 87 | 98 | 98 | 99 | 99 | 2036160
177 | Sympa Solar Power 8MW | [7 empty] | 1 | 2 | 3 | 5 | 2 | 6 | 3 | 1 | 3 | 1 | 0 | [8 empty] | 29527
178
178