## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-09-14 | Monday
|  |  | Date (day): | 2020-09-14 |  | Monday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14382.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15189 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-09-13 | 2020-09-14 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 150 | 150 | 150 | 150
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 200 | 200
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 66 | 67 | 67 | 67 |  | 11 | Engine problem
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 83 | 83 | 83 | 83 | 25 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 3 | 336 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 344 | 334 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 320 | 380 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 93 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 135 | 135 | 150 | 150 | 155 |  | GT-1 S/D for gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 64 | 96 | 96 | 96
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 100 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 35 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 288 | 282 | 335 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 93 | 93 | 93 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 150 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 47 | 47 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 28 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 51 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 300 | 300 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 146 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 88 | 87 | 100 | 100
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 17 | 70 | 80 | 24 |  | Fuel shortage
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 2891 | 3552 | 4128 | 4388 | 678 | 625
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 130 | 130 | 130 | 130 | 50 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 10 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 42 | 85 | 84 | 85 | 145 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 205 | 203 | 203 | 204
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 139 | 139 | 0 | 0 |  | 150 | Under maint.
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 100 | 100
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 20 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 95 | 90 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 21 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 24 | 5 | 25
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 77 | 85 | 85 | 85 |  | 23 | Engine problem
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 6 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 197 | 199 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 1046 | 1273 | 1592 | 1589 | 375 | 271
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 80 | 80 | 80 | 54 |  | Gas shortage
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 171 | 177 | 214 | 214 |  |  | FGMO
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 275 | 360 | 360 |  |  | FGMO
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 270 | 360 | 360 |  |  | FGMO
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 22 | 20 | 20 | 20 |  | 25 | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 97 | 130 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 50 | 0 | 50
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 82 | 80 | 100 | 100 |  | 63 | ST under shut down
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 200 | 200 | 200
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 21 | 21
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 140 | 164 | 157 | 173
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 0 | 33 | 33
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 25 | 43 | 43 | 43 |  | 9 | Engine problem
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 21 | 21 | 21
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 26 | 114 | 114
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 113 | 113 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1436 | 1742 | 2061 | 2327 | 555 | 97
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 138 | 123 | 160 | 160 | 42 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 22 | 22 | 22
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 56 | 56 | 55 | 56 |  | 39 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 3 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 200 | 200 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 48 | 113 | 115 | 115
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 465 | 514 | 553.6 | 553 | 42 | 39
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 90 | 91 | 90 | 90
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 28 | 30 | 30 |  | 60 | Unit-4 under shut down
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 110 | 163 | 163
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 284 | 287 | 300 | 300
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 50 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 47 | 50 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 52 | 64 | 64 |  |  | FGMO
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 88 | 88 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 233 | 184 | 225 | 225
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 25 | 25
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 280 | 341 | 341
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1395 | 1283 | 1458 | 1458 | 0 | 460
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 927 | 927 | 945 | 945
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 115 | 115 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 26 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 45 | 170 | 225 | 225
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 395 | 310 | 410 | 410
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 8 | 40 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 35 | 105 | 105
| 108 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1490 | 1723 | 1990 | 2146 | 0 | 0
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 96 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 28 | 38 | 33 | 33
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 65 | 65 | 65 | 65 |  | 129 | GT-2 & ST Under maint.
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 79 | 77 | 80 | 80 |  | 15 | Engine problem
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 460 | 500 | 620 | 620
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 648 | 776 | 908 | 908 | 0 | 144
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 22 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 43 | 43 | 43
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 144 | 147 | 147 | 147 |  | 75 | ST Under maint.
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 193 | 150 | 0 | 0 | 220 |  | Gas shortage
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 402 | 390 | 414 | 414 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 32
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 21 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 8 | 8 | 8 | 8
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 44 | 43 | 44 |  | 8 | Engine problem
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 97 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 109 | 109 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 885 | 1234 | 1434 | 1557 | 491 | 83
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 160 | 150 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 10 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 87 | 98 | 100 | 113
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 250 | 248 | 258 | 263 | 294 | 30
|  | Total |  |  |  |  | 20383 | 19892 | 10506 | 12345 | 14382.6 | 15189 | 2435 | 1749
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10036.2299 | 11793 | 13739.4898 | 14509.8321
| A. |  | 2020-09-13 | (Yesterday) |  |  |  |  | Sunday
| 1 | Highest Generation : |  |  | 12345 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
| 2 | Minimum Generation : |  |  | 9316 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12345 | MW
| 3 | Day peak Generation : |  |  | 10506 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11793 | MW
| 4 | Evening peak Generation : |  |  | 12345 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 260.9851 | MKWHr | By Solar | 0.16975 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 147.0494 | MKWHr |  | By Oil: | 69.8862 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 16.5582 | MKWHr |  | By Hydro: | 1.408 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2435 | MW | Dhaka | 4139 | 4139 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 1749 | MW | Chittagong | 1153 | 1153 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4184 | MW | Khulna | 1527 | 1527 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1188.94 | MMCFD |  |  | Rajshahi | 1277 | 1277 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 172523091.4 | ii) Oil : | Taka | 559286023.76 | Comilla | 1143 | 1143 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 76409004 | Total | Taka | 808218119.16 | Mymensingh | 907 | 907 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.205 | MKWHr. | Sylhet | 508 | 508 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -180 | MW (E to W) at | 19:30 | hrs | Barisal | 351 | 351 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -180 | MW at | 19:30 | hrs | Rangpur | 788 | 788 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 33.9° C |  |  | Total | 11793 | 11793 |  | 0
| B. |  | 2020-09-14 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 33.7° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12700 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15189 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10600 | MW
| 4 | Reserve(Generation end) |  |  |  | 2489 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 268.4901 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9206 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.2415 | MKWHr. | ii) HVDC Flow at Peak Time |  | 927 | MW at | 19:30 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.672 | MKWHr. | iii) Maximum HVDC Flow : |  | 930 | MW at | 17:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 93.91 |  | (b) Today: | 94.01 |  | (c) Rule Curve: |  | 100.99
.

## YesterdayGen
2020-09-13
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 100 | 0 | 200 | 62 | 40 | 351 | 351 |  | 0 | 420 | 140 | 100 | 80 | 55 | 292 | 0 | 0 | 0 | 7 | 85 | 32 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 0 | 0 | 45 | 0 | 130 | 0 | 0 | 203 | 0 | 140 | 0 |  | 0 | 0 | 17 | 0 | 84 | 39 | 21 | 42 | 0 | 0 | 80 | 275 | 270 | 180 | 8 | 85 | 35 | 5 | 0 | 51 | 0 | 0 | 43 | 18 | 11 | 33 | 21 | 162 | 143 | 55 | 22 | 0 | 91 | 28 | 50 | 47 | 163 | 285 | 66 | 88 | 0 | 185 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 300 | 0 | 0 | 180 | 0 | 137 | 0 | 100 | 0 | 100 | 0 | 110 | 52 | 0 | 0 | 216 | 0 | 0 | 70 | 113 | 100 | 0 | 17 |  | 927 | 0 | 345 | 0 | 115 | 110 | 0 | 0 | 0 | 0 | 40 | 65 | 39 | 64 | 0 | 60 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 146 | 0 | 0 | 0 | 77 | 100 | 200 | 0 | 398 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 109 | 550 |  | 7740 | 3719 | 11459 | 4277 | 927 | 2180 | 2912 | 700 | 45 | 256 | 162 | 0 | 0 | 93.86
2:00 | 0 | 0 | 100 | 0 | 200 | 62 | 40 | 351 | 353 |  | 0 | 420 | 140 | 100 | 80 | 55 | 290 | 0 | 0 | 0 | 10 | 85 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 0 | 0 | 45 | 0 | 130 | 0 | 0 | 203 | 0 | 140 | 0 |  | 0 | 0 | 17 | 0 | 70 | 0 | 21 | 40 | 0 | 0 | 80 | 275 | 270 | 192 | 8 | 86 | 35 | 5 | 0 | 51 | 0 | 0 | 43 | 18 | 11 | 33 | 21 | 158 | 143 | 55 | 22 | 0 | 91 | 28 | 50 | 47 | 163 | 287 | 66 | 88 | 0 | 184 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 300 | 0 | 0 | 180 | 0 | 144 | 0 | 100 | 0 | 100 | 0 | 75 | 3 | 0 | 0 | 216 | 0 | 0 | 17 | 113 | 100 | 0 | 17 |  | 927 | 0 | 345 | 0 | 115 | 25 | 0 | 0 | 0 | 0 | 40 | 65 | 38 | 64 | 0 | 60 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 146 | 0 | 0 | 0 | 78 | 50 | 200 | 0 | 370 | 17 | 0 | 0 | 0 | 38 | 0 | 0 | 109 | 550 |  | 7482 | 3475 | 10957 | 4289 | 927 | 2132 | 2600 | 700 | 45 | 106 | 158 | 0 | 0 | 93.87
3:00 | 0 | 0 | 100 | 0 | 200 | 62 | 40 | 351 | 355 |  | 0 | 420 | 140 | 100 | 80 | 55 | 293 | 0 | 0 | 0 | 28 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 22 | 25 | 22 | 33 | 33 | 0 | 0 | 46 | 0 | 130 | 0 | 0 | 213 | 0 | 140 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 21 | 42 | 0 | 0 | 80 | 275 | 270 | 195 | 8 | 85 | 35 | 5 | 0 | 51 | 0 | 0 | 34 | 18 | 11 | 33 | 21 | 154 | 156 | 55 | 22 | 0 | 91 | 28 | 50 | 47 | 163 | 285 | 66 | 88 | 0 | 184 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 300 | 0 | 0 | 180 | 0 | 134 | 0 | 100 | 0 | 50 | 0 | 24 | 0 | 0 | 0 | 198 | 0 | 0 | 0 | 108 | 100 | 0 | 17 |  | 927 | 0 | 345 | 0 | 115 | 15 | 0 | 0 | 0 | 0 | 40 | 65 | 38 | 32 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 145 | 0 | 0 | 0 | 78 | 64 | 200 | 0 | 382 | 17 | 0 | 0 | 0 | 55 | 0 | 0 | 109 | 550 |  | 7141 | 3427 | 10568 | 4314 | 927 | 2158 | 2237 | 700 | 46 | 32 | 154 | 0 | 0 | 93.88
4:00 | 0 | 0 | 100 | 0 | 200 | 62 | 40 | 351 | 354 |  | 0 | 420 | 140 | 100 | 60 | 55 | 300 | 0 | 0 | 0 | 90 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 22 | 33 | 33 | 0 | 0 | 46 | 0 | 130 | 0 | 0 | 203 | 0 | 141 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 21 | 42 | 0 | 0 | 80 | 275 | 270 | 196 | 8 | 86 | 35 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 21 | 152 | 158 | 55 | 22 | 0 | 91 | 28 | 50 | 47 | 163 | 284 | 66 | 88 | 0 | 184 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 300 | 0 | 0 | 180 | 0 | 110 | 0 | 100 | 0 | 5 | 0 | 24 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 108 | 100 | 0 | 17 |  | 927 | 0 | 345 | 0 | 115 | 35 | 0 | 0 | 0 | 0 | 40 | 65 | 35 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 145 | 0 | 0 | 0 | 78 | 70 | 200 | 0 | 400 | 17 | 0 | 0 | 0 | 55 | 0 | 0 | 109 | 550 |  | 7055 | 3431 | 10486 | 4310 | 927 | 2182 | 2117 | 700 | 46 | 52 | 152 | 0 | 0 | 93.89
5:00 | 0 | 0 | 100 | 0 | 200 | 62 | 40 | 351 | 354 |  | 0 | 420 | 140 | 100 | 48 | 55 | 300 | 0 | 0 | 0 | 90 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 22 | 33 | 33 | 0 | 0 | 46 | 0 | 130 | 0 | 0 | 209 | 0 | 138 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 21 | 42 | 0 | 0 | 80 | 275 | 270 | 201 | 8 | 91 | 35 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 21 | 146 | 158 | 55 | 22 | 0 | 91 | 28 | 50 | 47 | 163 | 287 | 65 | 88 | 0 | 185 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 200 | 0 | 0 | 180 | 0 | 110 | 0 | 100 | 0 | 5 | 0 | 24 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 108 | 100 | 0 | 17 |  | 927 | 0 | 370 | 0 | 115 | 35 | 0 | 0 | 0 | 0 | 0 | 65 | 33 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 145 | 0 | 0 | 0 | 78 | 0 | 200 | 0 | 400 | 17 | 0 | 0 | 0 | 50 | 0 | 0 | 109 | 550 |  | 6941 | 3339 | 10280 | 4351 | 927 | 2180 | 1878 | 700 | 46 | 52 | 146 | 0 | 0 | 93.9
6:00 | 0 | 0 | 100 | 0 | 200 | 62 | 40 | 314 | 354 |  | 0 | 420 | 140 | 100 | 48 | 15 | 287 | 0 | 0 | 0 | 70 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 22 | 33 | 33 | 0 | 0 | 47 | 0 | 130 | 0 | 0 | 203 | 0 | 137 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 0 | 0 | 80 | 275 | 270 | 175 | 8 | 86 | 35 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 21 | 138 | 160 | 55 | 22 | 0 | 91 | 28 | 50 | 47 | 130 | 284 | 65 | 88 | 0 | 185 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 145 | 0 | 0 | 180 | 0 | 110 | 0 | 100 | 0 | 5 | 0 | 24 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 108 | 100 | 0 | 17 |  | 928 | 0 | 340 | 0 | 115 | 35 | 0 | 0 | 0 | 0 | 0 | 65 | 32 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 146 | 0 | 0 | 0 | 78 | 0 | 170 | 0 | 340 | 17 | 0 | 0 | 0 | 40 | 0 | 0 | 109 | 550 |  | 6668 | 3207 | 9875 | 4200 | 928 | 2076 | 1751 | 700 | 47 | 35 | 138 | 0 | 0 | 93.91
7:00 | 0 | 0 | 100 | 0 | 200 | 62 | 40 | 0 | 303 |  | 0 | 360 | 135 | 100 | 48 | 15 | 275 | 0 | 0 | 0 | 50 | 90 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 22 | 33 | 33 | 0 | 0 | 47 | 0 | 130 | 0 | 0 | 202 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 34 | 0 | 0 | 80 | 275 | 270 | 175 | 8 | 82 | 32 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 21 | 128 | 160 | 48 | 22 | 0 | 91 | 28 | 50 | 47 | 130 | 286 | 65 | 88 | 0 | 185 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 145 | 0 | 0 | 180 | 0 | 110 | 7 | 100 | 0 | 5 | 0 | 8 | 0 | 0 | 1 | 160 | 0 | 0 | 0 | 113 | 100 | 0 | 17 |  | 927 | 0 | 340 | 0 | 99 | 40 | 0 | 0 | 0 | 0 | 0 | 65 | 27 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 147 | 0 | 0 | 0 | 79 | 0 | 170 | 0 | 340 | 0 | 0 | 0 | 0 | 34 | 0 | 1 | 109 | 520 |  | 6182 | 3140 | 9322 | 3872 | 927 | 1943 | 1666 | 670 | 47 | 60 | 128 | 9 | 0 | 93.92
8:00 | 0 | 0 | 100 | 0 | 200 | 62 | 40 | 0 | 302 |  | 0 | 360 | 135 | 100 | 48 | 15 | 277 | 0 | 0 | 0 | 50 | 93 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 22 | 33 | 33 | 0 | 0 | 46 | 0 | 130 | 0 | 0 | 204 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 0 | 0 | 80 | 275 | 270 | 175 | 8 | 81 | 35 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 21 | 128 | 160 | 8 | 22 | 0 | 91 | 28 | 50 | 47 | 130 | 284 | 65 | 88 | 0 | 185 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 145 | 0 | 0 | 185 | 0 | 110 | 12 | 100 | 0 | 5 | 0 | 8 | 0 | 0 | 2 | 159 | 0 | 0 | 0 | 113 | 100 | 0 | 17 |  | 927 | 0 | 345 | 0 | 115 | 40 | 0 | 0 | 0 | 0 | 0 | 65 | 27 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 147 | 0 | 0 | 0 | 78 | 0 | 170 | 0 | 340 | 0 | 0 | 0 | 0 | 35 | 0 | 1 | 109 | 500 |  | 6175 | 3141 | 9316 | 3881 | 927 | 1915 | 1650 | 650 | 46 | 104 | 128 | 15 | 0 | 93.93
9:00 | 0 | 0 | 100 | 0 | 200 | 62 | 40 | 0 | 333 |  | 0 | 360 | 135 | 100 | 48 | 21 | 268 | 0 | 0 | 0 | 65 | 93 | 64 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 25 | 22 | 33 | 33 | 5 | 0 | 45 | 0 | 130 | 0 | 0 | 204 | 0 | 141 | 0 |  | 0 | 0 | 0 | 0 | 0 | 4 | 21 | 4 | 0 | 0 | 80 | 345 | 270 | 175 | 8 | 81 | 35 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 21 | 130 | 161 | 20 | 20 | 0 | 91 | 28 | 50 | 47 | 130 | 286 | 64 | 88 | 0 | 185 | 18 | 0 | 10 | 260 | 24 | 8 | 0 | 174 | 0 | 0 | 200 | 0 | 131 | 18 | 90 | 0 | 10 | 0 | 8 | 50 | 0 | 5 | 195 | 0 | 0 | 0 | 113 | 100 | 0 | 17 |  | 927 | 0 | 345 | 0 | 115 | 20 | 0 | 0 | 0 | 0 | 8 | 65 | 25 | 16 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 146 | 0 | 0 | 0 | 78 | 0 | 170 | 0 | 332 | 0 | 0 | 0 | 0 | 37 | 0 | 1 | 109 | 480 |  | 6508 | 3116 | 9624 | 3939 | 927 | 1912 | 1933 | 630 | 45 | 84 | 130 | 24 | 0 | 93.94
10:00 | 0 | 0 | 100 | 0 | 200 | 65 | 40 | 0 | 304 |  | 0 | 320 | 140 | 100 | 60 | 55 | 290 | 0 | 33 | 0 | 100 | 93 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 16 | 0 | 44 | 0 | 130 | 0 | 0 | 203 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 33 | 18 | 21 | 4 | 0 | 0 | 80 | 260 | 270 | 193 | 8 | 90 | 35 | 5 | 0 | 51 | 0 | 0 | 20 | 18 | 11 | 33 | 21 | 138 | 156 | 47 | 20 | 1 | 91 | 28 | 47 | 47 | 130 | 287 | 63 | 88 | 0 | 196 | 18 | 0 | 10 | 280 | 16 | 8 | 0 | 293 | 0 | 0 | 200 | 0 | 149 | 16 | 90 | 0 | 40 | 0 | 8 | 50 | 0 | 4.1 | 197 | 0 | 0 | 0 | 113 | 100 | 0 | 17 |  | 928 | 0 | 345 | 0 | 115 | 30 | 0 | 0 | 0 | 0 | 8 | 65 | 27 | 16 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 146 | 0 | 0 | 0 | 78 | 0 | 170 | 0 | 357 | 0 | 0 | 0 | 0 | 69 | 0 | 2 | 109 | 430 |  | 6915.1 | 3130 | 10045.1 | 3928 | 928 | 1890 | 2420 | 580 | 44 | 94 | 138 | 23.1 | 0 | 93.95
11:00 | 0 | 0 | 150 | 0 | 200 | 82 | 50 | 0 | 305 |  | 0 | 320 | 140 | 100 | 64 | 55 | 292 | 0 | 97 | 0 | 100 | 93 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 25 | 0 | 0 | 43 | 0 | 130 | 0 | 0 | 203 | 0 | 141 | 0 |  | 0 | 0 | 0 | 0 | 72 | 19 | 21 | 3 | 0 | 0 | 80 | 270 | 280 | 183 | 8 | 81 | 35 | 5 | 0 | 51 | 0 | 0 | 25 | 18 | 11 | 33 | 21 | 140 | 142 | 56 | 20 | 1 | 90 | 28 | 47 | 46 | 163 | 285 | 61 | 88 | 0 | 233 | 18 | 0 | 10 | 300 | 16 | 2 | 0 | 300 | 0 | 0 | 200 | 0 | 144 | 4 | 90 | 0 | 41 | 0 | 18 | 50 | 0 | 4 | 197 | 0 | 0 | 0 | 113 | 100 | 0 | 17 |  | 928 | 0 | 400 | 0 | 115 | 30 | 0 | 0 | 0 | 0 | 8 | 65 | 25 | 16 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 142 | 0 | 0 | 0 | 77 | 0 | 178 | 0 | 369 | 0 | 0 | 0 | 0 | 70 | 0 | 2 | 109 | 450 |  | 7128 | 3211 | 10339 | 4101 | 928 | 1978 | 2476 | 600 | 43 | 62 | 140 | 11 | 0 | 93.95
12:00 | 0 | 0 | 150 | 0 | 200 | 83 | 66 | 3 | 344 |  | 0 | 320 | 135 | 100 | 64 | 55 | 288 | 0 | 35 | 0 | 100 | 93 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 22 | 33 | 25 | 0 | 0 | 42 | 0 | 130 | 0 | 0 | 205 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 77 | 19 | 21 | 5 | 0 | 0 | 80 | 280 | 280 | 171 | 8 | 82 | 22 | 5 | 0 | 51 | 0 | 0 | 25 | 18 | 11 | 33 | 20 | 140 | 138 | 56 | 20 | 3 | 90 | 30 | 47 | 47 | 163 | 284 | 61 | 88 | 0 | 233 | 18 | 0 | 10 | 300 | 16 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 146 | 10 | 95 | 0 | 97 | 0 | 48 | 88 | 0 | 6 | 197 | 0 | 0 | 0 | 113 | 100 | 0 | 17 |  | 927 | 0 | 395 | 0 | 115 | 45 | 0 | 0 | 0 | 0 | 8 | 65 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 8 | 0 | 0 | 160 | 0 | 0 | 144 | 0 | 0 | 0 | 79 | 0 | 193 | 0 | 402 | 0 | 0 | 0 | 0 | 87 | 0 | 3 | 109 | 460 |  | 7233 | 3273 | 10506 | 3995 | 927 | 2075 | 2624 | 620 | 42 | 61 | 140 | 22 | 0 | 93.95
13:00 | 0 | 0 | 148 | 0 | 200 | 83 | 67 | 81 | 348 |  | 0 | 320 | 125 | 100 | 64 | 55 | 265 | 0 | 32 | 0 | 100 | 93 | 16 | 66 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 22 | 33 | 25 | 0 | 0 | 68 | 0 | 130 | 0 | 0 | 203 | 0 | 141 | 0 |  | 0 | 0 | 0 | 0 | 77 | 37 | 21 | 9 | 0 | 0 | 80 | 270 | 280 | 175 | 8 | 81 | 22 | 5 | 0 | 51 | 0 | 0 | 40 | 18 | 11 | 33 | 15 | 142 | 124 | 50 | 20 | 2 | 91 | 28 | 50 | 47 | 163 | 284 | 61 | 88 | 0 | 184 | 18 | 0 | 10 | 285 | 24 | 0 | 0 | 300 | 0 | 0 | 182 | 0 | 136 | 20 | 90 | 0 | 130 | 0 | 65 | 88 | 0 | 0.8 | 197 | 0 | 0 | 0 | 106 | 100 | 0 | 20 |  | 928 | 0 | 405 | 0 | 115 | 100 | 0 | 0 | 0 | 0 | 8 | 65 | 29 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 8 | 0 | 0 | 145 | 0 | 0 | 145 | 0 | 0 | 0 | 77 | 0 | 206 | 0 | 379 | 0 | 0 | 40 | 0 | 104 | 0 | 5 | 109 | 470 |  | 7312.8 | 3383 | 10695.8 | 3974 | 928 | 2048 | 2777 | 615 | 68 | 116 | 142 | 27.8 | 0 | 93.96
14:00 | 0 | 0 | 150 | 0 | 200 | 83 | 67 | 21 | 304 |  | 0 | 320 | 140 | 100 | 64 | 55 | 294 | 0 | 35 | 0 | 100 | 93 | 16 | 81 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 22 | 33 | 33 | 0 | 0 | 68 | 0 | 130 | 0 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 77 | 50 | 21 | 7 | 0 | 0 | 80 | 270 | 280 | 169 | 8 | 89 | 22 | 5 | 0 | 51 | 0 | 0 | 43 | 18 | 11 | 33 | 21 | 152 | 120 | 56 | 20 | 2 | 91 | 28 | 50 | 47 | 110 | 285 | 61 | 88 | 0 | 184 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 300 | 0 | 0 | 170 | 0 | 149 | 6 | 90 | 0 | 125 | 0 | 45 | 70 | 0 | 0 | 197 | 0 | 0 | 0 | 110 | 100 | 0 | 29 |  | 927 | 0 | 400 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 8 | 65 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 8 | 0 | 0 | 141 | 0 | 0 | 145 | 0 | 0 | 0 | 78 | 0 | 170 | 0 | 367 | 0 | 0 | 50 | 0 | 102 | 0 | 3 | 109 | 470 |  | 7185 | 3335 | 10520 | 3891 | 927 | 1932 | 2792 | 611 | 68 | 136 | 152 | 11 | 0 | 93.96
15:00 | 0 | 0 | 150 | 0 | 200 | 83 | 67 | 54 | 350 |  | 0 | 320 | 135 | 96 | 64 | 55 | 287 | 0 | 34 | 0 | 100 | 93 | 16 | 84 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 22 | 33 | 33 | 0 | 0 | 69 | 0 | 130 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 77 | 50 | 21 | 4 | 0 | 0 | 80 | 270 | 280 | 163 | 8 | 80 | 20 | 5 | 0 | 51 | 0 | 0 | 43 | 18 | 11 | 33 | 21 | 156 | 122 | 56 | 22 | 1 | 91 | 28 | 50 | 47 | 163 | 282 | 61 | 88 | 0 | 185 | 18 | 0 | 10 | 295 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 11 | 90 | 0 | 132 | 0 | 35 | 88 | 0 | 0 | 198 | 0 | 0 | 0 | 113 | 100 | 0 | 20 |  | 927 | 0 | 385 | 0 | 102 | 120 | 0 | 0 | 0 | 0 | 8 | 65 | 29 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 8 | 0 | 0 | 139 | 0 | 0 | 144 | 0 | 0 | 0 | 77 | 0 | 200 | 0 | 348 | 0 | 0 | 72 | 0 | 98 | 0 | 2 | 109 | 480 |  | 7369 | 3355 | 10724 | 3935 | 927 | 2021 | 2847 | 619 | 69 | 136 | 156 | 14 | 0 | 93.96
16:00 | 0 | 0 | 150 | 0 | 200 | 83 | 67 | 101 | 349 |  | 0 | 320 | 150 | 93 | 64 | 55 | 306 | 0 | 60 | 0 | 93 | 93 | 16 | 50 | 0 | 0 | 0 | 17 | 17 | 17 | 22 | 25 | 22 | 28 | 33 | 0 | 0 | 70 | 0 | 130 | 0 | 0 | 218 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 57 | 30 | 21 | 6 | 0 | 0 | 80 | 280 | 270 | 138 | 8 | 91 | 20 | 5 | 0 | 51 | 0 | 0 | 25 | 18 | 11 | 33 | 21 | 156 | 122 | 56 | 22 | 0 | 91 | 28 | 50 | 48 | 163 | 283 | 60 | 88 | 0 | 185 | 18 | 0 | 10 | 295 | 24 | 8 | 0 | 200 | 0 | 0 | 200 | 0 | 149 | 5 | 90 | 0 | 80 | 0 | 35 | 88 | 0 | 1 | 163 | 0 | 0 | 0 | 106 | 100 | 0 | 17 |  | 927 | 0 | 375 | 0 | 69 | 120 | 0 | 0 | 0 | 0 | 8 | 65 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 8 | 0 | 0 | 139 | 0 | 0 | 144 | 0 | 0 | 0 | 77 | 0 | 180 | 0 | 376 | 0 | 0 | 35 | 0 | 85 | 0 | 2 | 109 | 490 |  | 7059 | 3282 | 10341 | 3995 | 927 | 2053 | 2367 | 629 | 70 | 136 | 156 | 8 | 0 | 93.97
17:00 | 0 | 0 | 150 | 0 | 200 | 83 | 40 | 206 | 309 |  | 0 | 320 | 125 | 93 | 65 | 55 | 260 | 0 | 0 | 0 | 93 | 93 | 16 | 40 | 0 | 0 | 0 | 17 | 17 | 17 | 22 | 25 | 22 | 28 | 33 | 0 | 0 | 70 | 0 | 130 | 0 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 30 | 19 | 21 | 11 | 0 | 0 | 80 | 270 | 270 | 159 | 8 | 82 | 20 | 5 | 0 | 51 | 0 | 0 | 8 | 18 | 11 | 33 | 21 | 138 | 123 | 56 | 22 | 0 | 91 | 28 | 50 | 49 | 110 | 284 | 62 | 88 | 0 | 184 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 200 | 0 | 0 | 200 | 0 | 149 | 1 | 90 | 0 | 80 | 0 | 35 | 88 | 0 | 0 | 163 | 0 | 0 | 0 | 110 | 100 | 0 | 17 |  | 930 | 0 | 290 | 0 | 66 | 120 | 0 | 0 | 0 | 5 | 8 | 65 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 8 | 0 | 0 | 141 | 0 | 0 | 145 | 0 | 0 | 0 | 78 | 0 | 130 | 0 | 323 | 0 | 0 | 35 | 0 | 70 | 0 | 1 | 109 | 450 |  | 6831 | 3045 | 9876 | 3850 | 930 | 1890 | 2264 | 591 | 70 | 141 | 138 | 2 | 0 | 93.97
18:00 | 0 | 0 | 100 | 0 | 200 | 83 | 40 | 276 | 275 |  | 0 | 350 | 135 | 93 | 80 | 55 | 278 | 0 | 0 | 0 | 100 | 93 | 133 | 40 | 0 | 0 | 0 | 17 | 17 | 28 | 22 | 25 | 22 | 28 | 33 | 16 | 0 | 80 | 0 | 130 | 0 | 4 | 204 | 0 | 104 | 0 |  | 0 | 0 | 26 | 20 | 31 | 19 | 21 | 13 | 0 | 0 | 80 | 275 | 270 | 165 | 8 | 80 | 22 | 5 | 0 | 51 | 0 | 9 | 8 | 18 | 11 | 0 | 0 | 144 | 122 | 56 | 22 | 0 | 91 | 28 | 25 | 20 | 110 | 287 | 67 | 20 | 0 | 184 | 18 | 0 | 10 | 280 | 24 | 0 | 0 | 200 | 0 | 0 | 170 | 0 | 149 | 0 | 90 | 6 | 80 | 0 | 35 | 88 | 0 | 0 | 180 | 0 | 0 | 17 | 113 | 100 | 0 | 15 |  | 926 | 0 | 260 | 0 | 66 | 120 | 0 | 0 | 4 | 10 | 24 | 65 | 31 | 53 | 0 | 0 | 0 | 4 | 0 | 75 | 0 | 0 | 12 | 8 | 7 | 21 | 8 | 0 | 0 | 0 | 140 | 0 | 0 | 145 | 0 | 0 | 0 | 78 | 0 | 130 | 0 | 280 | 0 | 0 | 35 | 0 | 71 | 0 | 0 | 109 | 450 |  | 6944 | 3132 | 10076 | 3807 | 926 | 1708 | 2421 | 590 | 80 | 400 | 144 | 0 | 0 | 93.97
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 150 | 0 | 200 | 83 | 60 | 337 | 334 |  | 0 | 370 | 130 | 100 | 95 | 55 | 304 | 0 | 0 | 0 | 100 | 93 | 150 | 98 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 28 | 33 | 51 | 0 | 85 | 0 | 130 | 0 | 25 | 203 | 0 | 139 | 0 |  | 0 | 0 | 102 | 20 | 78 | 44 | 21 | 21 | 0 | 0 | 80 | 270 | 270 | 172 | 8 | 80 | 22 | 5 | 0 | 51 | 0 | 50 | 35 | 18 | 11 | 0 | 21 | 172 | 122 | 56 | 22 | 0 | 91 | 28 | 50 | 42 | 110 | 285 | 52 | 88 | 0 | 185 | 18 | 0 | 10 | 270 | 24 | 11 | 0 | 265 | 0 | 0 | 200 | 0 | 149 | 0 | 90 | 104 | 112 | 0 | 84 | 88 | 0 | 0 | 199 | 0 | 0 | 101 | 113 | 100 | 0 | 2 |  | 926 | 0 | 310 | 0 | 115 | 160 | 0 | 0 | 21 | 0 | 40 | 65 | 38 | 96 | 0 | 0 | 0 | 50 | 0 | 98 | 0 | 0 | 43 | 35 | 32 | 21 | 8 | 0 | 0 | 0 | 150 | 0 | 0 | 145 | 0 | 0 | 0 | 77 | 92 | 150 | 0 | 380 | 35 | 0 | 92 | 0 | 94 | 0 | 0 | 109 | 470 |  | 8208 | 3852 | 12060 | 4066 | 926 | 2026 | 3459 | 620 | 85 | 706 | 172 | 0 | 0 | 93.98
19:30 | 0 | 0 | 150 | 0 | 200 | 83 | 67 | 336 | 334 |  | 0 | 380 | 135 | 93 | 96 | 55 | 282 | 0 | 0 | 0 | 100 | 93 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 28 | 33 | 51 | 0 | 85 | 0 | 130 | 0 | 25 | 203 | 0 | 139 | 0 |  | 0 | 0 | 102 | 20 | 85 | 50 | 21 | 24 | 0 | 0 | 80 | 275 | 270 | 177 | 8 | 80 | 20 | 5 | 0 | 51 | 0 | 50 | 43 | 18 | 11 | 0 | 21 | 164 | 123 | 56 | 22 | 0 | 91 | 28 | 50 | 50 | 110 | 287 | 52 | 88 | 0 | 184 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 90 | 200 | 130 | 0 | 113 | 87 | 0 | 0 | 199 | 0 | 0 | 26 | 113 | 100 | 0 | 17 |  | 927 | 0 | 310 | 0 | 115 | 170 | 0 | 0 | 26 | 0 | 40 | 65 | 38 | 96 | 0 | 0 | 0 | 50 | 22 | 97 | 0 | 0 | 43 | 44 | 32 | 21 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 147 | 0 | 0 | 0 | 77 | 100 | 150 | 0 | 390 | 35 | 0 | 113 | 0 | 98 | 0 | 0 | 109 | 500 |  | 8364 | 3981 | 12345 | 4063 | 927 | 2074 | 3640 | 650 | 85 | 742 | 164 | 0 | 0 | 0
20:00 | 0 | 0 | 150 | 0 | 200 | 83 | 67 | 336 | 335 |  | 0 | 380 | 140 | 92 | 96 | 55 | 280 | 0 | 0 | 0 | 100 | 93 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 28 | 33 | 51 | 0 | 85 | 0 | 130 | 0 | 25 | 203 | 0 | 139 | 0 |  | 0 | 0 | 102 | 20 | 85 | 50 | 21 | 28 | 0 | 0 | 80 | 275 | 270 | 184 | 8 | 87 | 22 | 5 | 0 | 51 | 0 | 50 | 43 | 18 | 11 | 0 | 21 | 174 | 122 | 56 | 22 | 0 | 91 | 28 | 50 | 50 | 110 | 286 | 52 | 88 | 0 | 185 | 18 | 0 | 10 | 270 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 90 | 100 | 132 | 0 | 115 | 87 | 0 | 0 | 199 | 0 | 0 | 17 | 113 | 100 | 0 | 17 |  | 926 | 0 | 310 | 0 | 115 | 170 | 0 | 0 | 18 | 0 | 40 | 67 | 39 | 96 | 0 | 0 | 0 | 50 | 35 | 97 | 0 | 0 | 47 | 47 | 32 | 21 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 147 | 0 | 0 | 0 | 77 | 100 | 150 | 0 | 400 | 35 | 0 | 113 | 0 | 99 | 0 | 0 | 109 | 500 |  | 8281 | 4009 | 12290 | 4081 | 926 | 2080 | 3543 | 650 | 85 | 751 | 174 | 0 | 0 | 93.98
21:00 | 0 | 0 | 150 | 0 | 200 | 83 | 67 | 336 | 335 |  | 0 | 380 | 140 | 92 | 96 | 55 | 301 | 0 | 0 | 0 | 100 | 93 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 28 | 33 | 51 | 0 | 85 | 0 | 130 | 0 | 25 | 165 | 0 | 100 | 0 |  | 0 | 0 | 102 | 20 | 85 | 50 | 21 | 35 | 0 | 0 | 80 | 275 | 270 | 197 | 8 | 92 | 22 | 5 | 0 | 51 | 0 | 0 | 43 | 18 | 11 | 0 | 21 | 174 | 123 | 56 | 22 | 0 | 91 | 30 | 50 | 50 | 110 | 285 | 52 | 85 | 0 | 185 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 137 | 0 | 115 | 104 | 0 | 0 | 199 | 0 | 0 | 17 | 113 | 100 | 0 | 17 |  | 926 | 0 | 310 | 0 | 115 | 170 | 0 | 0 | 18 | 0 | 40 | 67 | 39 | 96 | 0 | 0 | 0 | 50 | 34 | 97 | 0 | 0 | 43 | 47 | 32 | 21 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 146 | 0 | 0 | 0 | 78 | 100 | 150 | 0 | 405 | 35 | 0 | 113 | 0 | 112 | 0 | 0 | 109 | 560 |  | 8151 | 4082 | 12233 | 4044 | 926 | 2110 | 3488 | 710 | 85 | 696 | 174 | 0 | 0 | 93.98
22:00 | 0 | 0 | 150 | 0 | 200 | 83 | 67 | 348 | 330 |  | 0 | 380 | 150 | 100 | 97 | 55 | 240 | 0 | 0 | 0 | 100 | 93 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 22 | 28 | 33 | 25 | 0 | 85 | 0 | 130 | 0 | 25 | 164 | 0 | 100 | 0 |  | 0 | 0 | 102 | 20 | 85 | 50 | 21 | 39 | 0 | 0 | 80 | 280 | 270 | 180 | 8 | 90 | 22 | 5 | 0 | 51 | 0 | 0 | 43 | 18 | 11 | 0 | 21 | 174 | 126 | 56 | 22 | 0 | 91 | 30 | 50 | 50 | 130 | 277 | 62 | 88 | 0 | 185 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 138 | 0 | 115 | 104 | 0 | 0 | 199 | 0 | 0 | 17 | 113 | 100 | 0 | 17 |  | 926 | 0 | 380 | 0 | 115 | 170 | 0 | 0 | 18 | 0 | 40 | 68 | 39 | 96 | 0 | 0 | 0 | 50 | 34 | 97 | 0 | 0 | 43 | 32 | 32 | 21 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 0 | 0 | 79 | 100 | 137 | 0 | 405 | 35 | 0 | 113 | 0 | 111 | 0 | 0 | 109 | 570 |  | 8086 | 4119 | 12205 | 4005 | 926 | 2133 | 3466 | 720 | 85 | 696 | 174 | 0 | 0 | 93.99
23:00 | 0 | 0 | 154 | 0 | 200 | 83 | 67 | 338 | 324 |  | 0 | 380 | 140 | 100 | 97 | 55 | 287 | 0 | 0 | 0 | 100 | 93 | 150 | 80 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 28 | 33 | 0 | 0 | 85 | 0 | 130 | 0 | 25 | 168 | 0 | 104 | 0 |  | 0 | 0 | 102 | 20 | 85 | 50 | 21 | 40 | 0 | 0 | 80 | 275 | 270 | 175 | 8 | 87 | 22 | 5 | 0 | 51 | 0 | 0 | 43 | 18 | 11 | 33 | 21 | 174 | 127 | 55 | 22 | 0 | 91 | 28 | 50 | 50 | 130 | 260 | 64 | 88 | 0 | 185 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 137 | 0 | 115 | 104 | 0 | 0 | 199 | 0 | 0 | 17 | 113 | 100 | 0 | 17 |  | 926 | 0 | 370 | 0 | 99 | 170 | 0 | 0 | 18 | 0 | 40 | 68 | 40 | 96 | 0 | 0 | 0 | 0 | 6 | 97 | 0 | 0 | 43 | 25 | 32 | 21 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 5 | 0 | 79 | 100 | 208 | 0 | 405 | 35 | 0 | 113 | 0 | 113 | 0 | 0 | 109 | 570 |  | 8089 | 4087 | 12176 | 4146 | 926 | 2119 | 3388 | 720 | 85 | 618 | 174 | 0 | 0 | 93.99
24:00 | 0 | 0 | 150 | 0 | 200 | 83 | 67 | 355 | 310 |  | 0 | 380 | 140 | 100 | 97 | 55 | 300 | 0 | 0 | 0 | 100 | 92 | 114 | 81 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 28 | 33 | 0 | 0 | 85 | 0 | 130 | 0 | 0 | 164 | 0 | 17 | 0 |  | 0 | 0 | 102 | 0 | 85 | 50 | 21 | 41 | 0 | 0 | 80 | 275 | 270 | 175 | 8 | 84 | 22 | 5 | 0 | 51 | 0 | 0 | 43 | 18 | 11 | 33 | 21 | 168 | 144 | 55 | 22 | 0 | 91 | 28 | 50 | 50 | 163 | 263 | 64 | 88 | 0 | 185 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 290 | 0 | 0 | 192 | 0 | 149 | 0 | 100 | 0 | 132 | 0 | 115 | 104 | 0 | 0 | 199 | 0 | 0 | 17 | 113 | 100 | 0 | 17 |  | 926 | 0 | 365 | 0 | 99 | 170 | 0 | 0 | 18 | 0 | 40 | 65 | 39 | 96 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 43 | 25 | 32 | 21 | 8 | 11 | 0 | 0 | 151 | 0 | 0 | 130 | 0 | 9 | 0 | 78 | 100 | 216 | 0 | 365 | 35 | 0 | 113 | 0 | 107 | 0 | 0 | 109 | 570 |  | 7971 | 4039 | 12010 | 4102 | 926 | 2117 | 3314 | 721 | 85 | 577 | 168 | 0 | 0 | 93.99
KWH | 0 | 0 | 2998000 | 0 | 4808236 | 1752181 | 1304576 | 4997980 | 7857000 |  | 0 | 7910250 | 3362182 | 2395200 | 1744632 | 1201794 | 6952903 | 0 | 367000 | 0 | 2010240 | 2208096 | 1347360 | 1019635 | 0 | 0 | 0 | 874800 | 843205 | 859129 | 398880 | 600000 | 521100 | 786600 | 786400 | 243060 | 0 | 1408015 | 0 | 3100000 | 0 | 143906 | 4667898 | 0 | 2997402 | 0 |  | 0 | 0 | 693921 | 139200 | 1202880 | 618240 | 487824 | 565440 | 0 | 0 | 1923456 | 6998000 | 6687000 | 4334000 | 217454 | 2027090 | 661608 | 137280 | 0 | 1247501 | 0 | 117112 | 643584 | 416088 | 239580 | 633200 | 500380 | 3672000 | 3267600 | 1220160 | 453132 | 9250 | 2151000 | 677160 | 1161000 | 1110528 | 3485127 | 6438000 | 1474464 | 2028480 | 0 | 4532720 | 423000 | 0 | 245700 | 7156000 | 540288 | 174000 | 0 | 6327924 | 0 | 23940 | 4627200 | 26968 | 3345120 | 124335 | 2323200 | 294240 | 1985527 | 0 | 1414800 | 1360176 | 0 | 19439 | 4548982 | 0 | 0 | 323760 | 2687160 | 2433600 | 0 | 430080 |  | 22241455 | 0 | 8717184 | 0 | 2551680 | 2207040 | 0 | 0 | 117550 | 11904 | 489750 | 1555000 | 770711 | 967872 | 0 | 627000 | 0 | 219216 | 124381 | 761840 | 0 | 0 | 243600 | 230400 | 185692 | 487200 | 186552 | 218340 | 0 | 0 | 3610200 | 0 | 0 | 3568000 | 0 | 15200 | 0 | 1879243 | 969600 | 4802218 | 0 | 9022272 | 298560 | 0 | 1028064 | 0 | 1835520 | 0 | 16727 | 2602560 | 12948000 |  | 175474558 | 85510531 | 260985089 | 98524931 | 22241455 | 48524495 | 63856626 | 16558200 | 1408015 | 6029616 | 3672000 | 169751 | 0
Fuel Cost | 0 | 0 | 4377080 | 0 | 5337141.96 | 2312878.92 | 2217779.2 | 5047959.8 | 8092710 |  | 0 | 8622172.5 | 3732022.02 | 18179568 | 12020514.48 | 10167177.24 | 7231019.12 | 0 | 634910 | 0 | 15137107.2 | 20137835.52 | 13258022.4 | 9401034.7 | 0 | 0 | 0 | 6386040 | 6517974.65 | 8471011.94 | 299160 | 450000 | 0 | 0 | 0 | 2350390.2 | 0 | 380164.05 | 0 | 5611000 | 0 | 1336886.74 | 5088008.82 | 0 | 5095583.4 | 0 |  | 0 | 0 | 6731033.7 | 1329360 | 10465056 | 4896460.8 | 614658.24 | 1679356.8 | 0 | 0 | 2827480.32 | 5178520 | 6687000 | 3987280 | 280515.66 | 2331153.5 | 747617.04 | 192192 | 0 | 2133226.71 | 0 | 1182831.2 | 6146227.2 | 528431.76 | 179685 | 1108100 | 375285 | 27540000 | 3463656 | 11079052.8 | 575477.64 | 147445 | 3527640 | 1083456 | 2066580 | 1732423.68 | 3973044.78 | 6695520 | 2904694.08 | 3874396.8 | 0 | 7841605.6 | 926370 | 0 | 501228 | 7227560 | 405216 | 132240 | 0 | 47839105.44 | 0 | 400276.8 | 24061440 | 450904.96 | 32915980.8 | 1453476.15 | 18934080 | 3192504 | 13997965.35 | 0 | 12902976 | 12853663.2 | 0 | 0 | 34390303.92 | 0 | 0 | 3231124.8 | 23028961.2 | 16207776 | 0 | 0 |  | 128110780.8 | 0 | 9153043.2 | 0 | 20056204.8 | 30589574.4 | 0 | 0 | 1233099.5 | 124753.92 | 5103195 | 1757150 | 1194602.05 | 9446430.72 | 0 | 1285350 | 0 | 2157085.44 | 1263710.96 | 6742284 | 0 | 0 | 2360484 | 2232576 | 1801212.4 | 935424 | 289155.6 | 165283.38 | 0 | 0 | 19567284 | 0 | 0 | 4174560 | 0 | 0 | 0 | 2818864.5 | 16492896 | 5618595.06 | 0 | 8932049.28 | 3116966.4 | 0 | 9756327.36 | 0 | 14243635.2 | 0 | 184833.35 | 19232918.4 | 56841720 |  | 579052768.79 | 386982049.72 | 966034818.51 | 113446930.92 | 128110780.8 | 59076160.48 | 491841931.84 | 76409004 | 380164.05 | 67444091.92 | 27540000 | 1785754.5 | 0
Yesterday Day Peak | 0 | 0 | 150 | 0 | 200 | 83 | 66 | 3 | 344 |  | 0 | 320 | 135 | 100 | 64 | 55 | 288 | 0 | 35 | 0 | 100 | 93 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 22 | 33 | 25 | 0 | 0 | 42 | 0 | 130 | 0 | 0 | 205 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 77 | 19 | 21 | 5 | 0 | 0 | 80 | 280 | 280 | 171 | 8 | 82 | 22 | 5 | 0 | 51 | 0 | 0 | 25 | 18 | 11 | 33 | 20 | 140 | 138 | 56 | 20 | 3 | 90 | 30 | 47 | 47 | 163 | 284 | 61 | 88 | 0 | 233 | 18 | 0 | 10 | 300 | 16 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 146 | 10 | 95 | 0 | 97 | 0 | 48 | 88 | 0 | 6 | 197 | 0 | 0 | 0 | 113 | 100 | 0 | 17 |  | 927 | 0 | 395 | 0 | 115 | 45 | 0 | 0 | 0 | 0 | 8 | 65 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 8 | 0 | 0 | 160 | 0 | 0 | 144 | 0 | 0 | 0 | 79 | 0 | 193 | 0 | 402 | 0 | 0 | 0 | 0 | 87 | 0 | 3 | 109 | 460 |  | 10506 | DayPeak
Yesterday Evening Peak | 0 | 0 | 150 | 0 | 200 | 83 | 67 | 336 | 334 | 0 | 0 | 380 | 135 | 93 | 96 | 55 | 282 | 0 | 0 | 0 | 100 | 93 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 28 | 33 | 51 | 0 | 85 | 0 | 130 | 0 | 25 | 203 | 0 | 139 | 0 | 0 | 0 | 0 | 102 | 20 | 85 | 50 | 21 | 24 | 0 | 0 | 80 | 275 | 270 | 177 | 8 | 80 | 20 | 5 | 0 | 51 | 0 | 50 | 43 | 18 | 11 | 0 | 21 | 164 | 123 | 56 | 22 | 0 | 91 | 28 | 50 | 50 | 110 | 287 | 52 | 88 | 0 | 184 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 90 | 200 | 130 | 0 | 113 | 87 | 0 | 0 | 199 | 0 | 0 | 26 | 113 | 100 | 0 | 17 |  | 927 | 0 | 310 | 0 | 115 | 170 | 0 | 0 | 26 | 0 | 40 | 65 | 38 | 96 | 0 | 0 | 0 | 50 | 22 | 97 | 0 | 0 | 43 | 44 | 32 | 21 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 147 | 0 | 0 | 0 | 77 | 100 | 150 | 0 | 390 | 35 | 0 | 113 | 0 | 98 | 0 | 0 | 109 | 500 |  | 12345 | EvPeak
Forecast for Evening | 0 | 0 | 150 | 0 | 200 | 83 | 67 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 96 | 55 | 335 | 0 | 0 | 0 | 100 | 93 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 85 | 0 | 130 | 0 | 25 | 204 | 0 | 0 | 0 | 0 | 0 |  | 100 | 100 | 85 | 50 | 21 | 25 | 0 | 0 | 80 | 360 | 360 | 214 | 8 | 100 | 20 | 5 | 0 | 51 | 0 | 50 | 43 | 21 | 11 | 33 | 21 | 173 | 160 | 56 | 22 | 0 | 90 | 30 | 51 | 44 | 163 | 300 | 64 | 86 | 0 | 225 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 80 |  | 945 | 16 | 410 | 0 | 115 | 225 | 0 | 0 | 30 | 60 | 40 | 65 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 0 | 0 | 43 | 44 | 32 | 22 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 147 | 0 | 220 | 0 | 80 | 100 | 0 | 0 | 414 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620
Forecast for Day | 0 | 0 | 150 | 0 | 200 | 83 | 67 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 96 | 55 | 335 | 0 | 0 | 0 | 100 | 93 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 84 | 0 | 130 | 0 | 25 | 203 | 0 | 0 | 0 | 0 | 0 |  | 100 | 100 | 85 | 50 | 21 | 5 | 0 | 0 | 80 | 360 | 360 | 214 | 8 | 100 | 20 | 5 | 0 | 51 | 0 | 0 | 43 | 21 | 11 | 33 | 21 | 157 | 160 | 55 | 22 | 1.6 | 90 | 30 | 51 | 44 | 163 | 300 | 64 | 86 | 0 | 225 | 18 | 0 | 10 | 341 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 70 |  | 945 | 0 | 410 | 0 | 115 | 225 | 0 | 0 | 0 | 0 | 40 | 65 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 43 | 0 | 22 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 147 | 0 | 220 |  | 80 | 50 | 0 | 0 | 414 | 105 | 100 | 113 | 100 | 100 | 0 | 8 | 113 | 620
Generation at 08:00(Today) | 0 | 0 | 150 | 0 | 200 | 83 | 67 | 361 | 300 | 0 | 0 | 320 | 150 |  | 30 | 15 | 309 | 0 | 0 | 0 | 55 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 22 | 28 | 33 | 0 | 0 | 84 | 0 | 130 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 0 | 0 | 80 | 280 | 270 | 173 | 8 | 90 | 22 | 5 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 33 | 21 | 128 | 158 | 54 | 22 | 0 | 91 | 28 | 50 | 50 | 110 | 261 | 63 | 85 | 0 | 185 | 18 | 0 | 10 | 305 | 24 | 0 | 0 | 45 | 0 | 0 | 140 | 0 | 113 | 11 | 76 | 0 | 6 | 0 | 8 | 1 | 0 | 3 | 160 | 0 | 0 | 0 | 104 | 100 | 0 | 17 | 0 | 927 | 0 | 295 | 0 | 83 | 120 | 0 | 0 | 0 | 0 | 8 | 68 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 108 | 0 | 0 | 142 | 0 | 145 | 0 | 77 | 0 | 0 | 0 | 415 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 70 | 500 | 0
199
| Minimum Generation |  | 9316 | 8:00
| Highest Generation |  | 12345 | 19:30
| Day Peak Generation |  | 10506 | 12:00
| Evening Peak Generation |  | 12345 | 19:30
| HVDC Max Flow |  | 930 | 17:00
| HVDC EvPeak Flow |  | 927 | 19:30
| Load factor L.F |  | 88.09%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-09-14
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-09-13 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10506 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 9206 | MW
Evening Peak Generation : |  | 12345 | MW Hour : | 19:30 | Available Max Generation : |  | 15189 | MW
E.P. Demand (at gen end) : |  | 12345 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 12700 | MW
Maximum Generation : |  | 12345 | MW Hour : | 19:30 | Reserve(Generation end) |  | 2489 | MW
Total Gen. (MKWH) : |  | 260.9851 | System Load Factor : | 88.09% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -180 | MW at | 19:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-09-14
Actual : | 94.01 | Ft.(MSL) , | Rule curve : | 100.99 | Ft.( MSL )
Gas Consumed : | Total = | 1188.94 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 172523091.4
: |  | Coal : | 76409004 | Oil : | 559286023.76 | Total : | 808218119.16
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4509.6003 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1537.5857 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1378.3514 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1245.7144 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1125.592 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 908.3232 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 502.6496 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 233.7301 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 700.569 |  |  | 0 | 0%
Total | 0 |  | 12142.1157 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 9) Bhola 225 MW GT-2 & ST
|  |  |  | 2) Bibiyana #3 | 10) Sirajganj unit-1 ST
|  |  |  | 3) Ghorasal Unit-1,2,3,4,7 | 11) Sikalbaha-150 MW.
4) Ashuganj unit-3,4
5) Kaptai-1,2,5
6) Raozan #1,2
7) Sirajganj #3
8) Baghabari-71 MW & 100 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Faridpur-Gopalganj(N) 132 kV Ckt-2 tripped at 09:11 showing E/F & O/C relay and was switched on at 09:22.
b) Halishahar-Kulshi 132 kV Ckt1 tripped at 09:45 showing SOTF.
c) Bheramara 230/132 kV T-1 transformer tripped at 10:35 showing buchholz relay and was switched
on at 14:29.
d) After maintenance Haripur-412 MW CCPP GT & ST were synchronized at 11:53 & 15:26 respectively
e) Baghabari-100 MW was shut down at 11:45 due to gas shortage.
f) Sirajganj 230-Sirajganj #2 230 kV Ckt was under shut down from 08:29 to 14:55 for maintenance.
g) Naogaon 132/33 kV T-1 & T-2 transformers were shut down at 08:45 due to red hot maintenance and |  |  |  |  | About 35 MW power interruption occurring under Naogaon S/S area
were switched on at 09:55 &10:35 respectively. |  |  |  |  | from 08:45 to 09:35.
h) Mohastanghor 132/33 kV T-2 transformer was under shut down at 10:31 due to red hot maintenance
at 33 kV CT and was switched on at 11:57.
i) Mohastanghor 132/33 kV T-1 transformer was under shut down at 11:45 due to red hot maintenance
at 33 kV CT and was switched on at 13:37.
j) Mymensing-Jamalpur 132 kV Ckt-1 tripped at 13:52 showing E/F relay at Jamalpur end & dist.Z1,
C-phase at Mymensing end and was switched on at 14:03.
k) Siddirganj GT-2 was shut down at 16:31 due to gas shortage.
l) Cumilla(N) 132/33 kV T-3 transformer tripped at 17:15 showing O/C relay and was switched on at 17:22.
m) Naogaon 132/33 kV T-2 transformer tripped at 17:59 showing O/C relay due to 33 kV Baludanga |  |  |  |  | About 25 MW power interruption occurring under Naogaon S/S area
feeder fault and was switched on at 18:09. |  |  |  |  | from 17:59 to 18:09.
n) Sirajganj 132/33 kV T-1 transformer was under shut down from 21:11 to 21:47 for C/M.
o) Bakulia 132/33 kV T-2 transformer was under shut down from 06:06 to 06:54(14/9/20) for C/M.
p) Feni 132/33 kV T-1 transformer is under shut down since 06:45(14/9/20) for DC Ckt unhethy.
q) Daudkandi 132/33 kV T-3 transformer is under shut down since 07:01(14/9/20) for C/M.
r) Chandraghona 132/33 kV T-1 transformer was under shut down from 07:11 to 08:55(14/9/20) for C/M.
s) Siddirganj 230/132 kV MTR-01 transformer is under shut down from 07:13 to 09:32(14/9/20) for C/M.
t) Sirajganj #2 GT & ST were synchronized at 22:52 & 01:31(14/9/20)respectively.
u) Sirajganj #3 GT & ST were shut down at 07:16 & 07:09(14/9/20)respectively.
r) Sikalbaha-150 MW was forced shut down at 00:50(14/9/20).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-09-13 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 150 | 2998000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 4808236 | Machine problem
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 67 | 1304576 | Machine problem
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 83 | 1752181 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 336 | 4997980 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 334 | 7857000 | Dirty fuel
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 380 | 7910250 | Frequency control
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 93 | 2395200 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 135 | 3362182 | GT-1 Under S/D due to gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 96 | 1744632
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1201794
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 100 | 1019635
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 398880
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 367000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 2010240
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 282 | 6952903
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 2208096
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel Shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 874800
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1347360
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 843205
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 859129
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 47 | 1121100 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 28 | 786600 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 786400
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 243060
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 6327924
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 23940 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 26968 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3345120
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 87 | 1360176 | Engine problem
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 430080 | Fuel Shortage
| Dhaka area Total |  |  |  | 5895 | 3552 | 71664647
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 130 | 3100000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 143906
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 124335
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 618240
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 85 | 1408015 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4667898
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 139 | 2997402
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 693921
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 20 | 139200 | Line over load
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 2323200 | Engine problem
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 487824
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 24 | 565440
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 85 | 1202880 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 19439
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 199 | 4548982 | Transformer O/L
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2433600
| Chattogram area Total |  |  |  | 2266 | 1273 | 25474282
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 1923456 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 177 | 4334000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 275 | 6998000 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 6687000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 20 | 661608 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 137280 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1247501
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 130 | 1985527 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 117112
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 2027090
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 294240
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 416088 | Engine problem
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 239580
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 164 | 3672000
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 0 | 633200
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 643584 | Engine problem
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 500380
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 26 | 323760 | Low demand
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 2687160
| Cumilla Area Total |  |  |  | 2980 | 1742 | 35746020
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 123 | 3267600 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 453132
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 56 | 1220160 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9250
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 4627200
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 113 | 1414800 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 514 | 10992142
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 91 | 2151000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 28 | 677160 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 3485127 | Frequency control
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 287 | 6438000
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1161000
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 1110528
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 174000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 52 | 1474464 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 88 | 2028480
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 184 | 4532720
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 423000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 540288
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7156000 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 245700
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1283 | 31597467
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 927 | 22241455
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 2551680
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 26 | 117550 | Low demand
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 170 | 2207040 | Low demand
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 11904 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 310 | 8717184 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 489750
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 969600
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 35 | 298560 | Engine problem
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Reserve
| Khulna Area Total |  |  |  | 2284 | 1723 | 37604723
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 96 | 967872
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 38 | 770711
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 65 | 1555000 | GT-2 Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 77 | 1879243 | Engine problem
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 500 | 12948000
| Barisal Area Total |  |  |  | 1054 | 776 | 18120826
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 627000 | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 219216
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 22 | 124381 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 43 | 243600
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 147 | 3568000 | ST Under maint.
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 15200 | Gas shortage
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 150 | 4802218 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 390 | 9022272 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 185692
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 487200
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 8 | 186552 | Engine problem
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 218340 | Engine problem
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 44 | 230400 | Engine problem
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 97 | 761840
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 1028064
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 2602560
| Rajshahi Area Total |  |  |  | 2183 | 1234 | 24322535
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3610200 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Condenser
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 98 | 1835520 | Engine problem
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 16727
| Rangpur Area Total |  |  |  | 605 | 248 | 5462447
| Total |  |  |  | 19892 | 12345 | 260985089
| Eastern Grid Total |  |  |  | 13766 | 8364 | 175474558
| Western Grid Total |  |  |  | 6126 | 3981 | 85510531
| National Grid Total |  |  |  | 19892 | 12345 | 260985089
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-09-13
| (a) ENTIRE EASTERN GRID : |  | 7850 | MW | (b) ENTIRE WESTERN GRID : |  | 3943 | MW
| i) Dhaka area |  | 4139 | MW | i) Khulna area |  | 1527 | MW
| ii) Chittagong area |  | 1153 | MW | ii) Rajshahi area |  | 1277 | MW
| iii) Comilla area |  | 1143 | MW | iii) Barisal area |  | 351 | MW
| iv) Mymensingh area |  | 907 | MW | iv) Rangpur area |  | 788 | MW
| v) Sylhet area |  | 508 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11793 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 132 | 18:30 | Sherpur | 110 | 22:00 | Jhenida | 116 | 19:30
| Munsiganj | 124 | 21:00 | Srimongal | 48 | 19:00 | Bottail | 136 | 19:00
| Sonargaon | 86 | 19:00 | Shahjibazar | 122 | 20:00 | G.K Project | 58 | 20:00
| Shyampur | 192 | 10:00 | Fenchuganj | 44 | 18:30 | Faridpur | 193 | 0.83333
| Bhulta | 199 | 12:00 | Kulawara | 40 | 19:00 | Madaripur | 106 | 0.91667
| Madanganj | 43 | 1:00 | Sylhet | 128 | 19:00 | Sariatpur | 66 | 21:00
| Shitalakhya | 116 | 10:00 | Chatak | 30 | 21:00 | Gopalganj | 100 | 21:00
| Rahim steel | 19 | 12:00 | Sunamganj | 47 | 20:00 | Bagerhat | 95 | 19:00
| Matuail | 85 | 12:00 | Biani Bazar | 59 | 19:00 | Mongla | 42 | 1:00
| Ghorasal | 84 | 21:00 | Comilla (S) | 174 | 20:00 | Satkhira | 110 | 0.91667
| Narsingdi | 167 | 20:00 | Comilla(N) | 90 | 21:00 | Gallamari | 44 | 13:00
| Haripur (SBU) | 103 | 10:00 | Chandpur | 102 | 20:00 | Magura | 54 | 0.79167
| Ullon | 60 | 18:00 | Feni | 125 | 18:30 | Norail | 41 | 19:00
| Hasnabad | 205 | 19:00 | Chowmuhani | 184 | 18:30 | Chuadanga | 92 | 22:00
| Magbazar | 103 | 13:00 | Ashuganj | 56 | 23:00 | Barisal(N) | 48 | 0.875
| Maniknagar | 100 | 11:00 | Daudkandi | 142 | 20:00 | Barisal (S) | 98 | 0.83333
| Bangabhaban | 40 | 10:00 | B.Baria | 162 | 21:00 | Patuakhali | 126 | 0.95833
| Narinda | 90 | 12:00 | Ramganj | 116 | 19:30 | Bhandaria | 54 | 0.79167
| Dhanmondi | 192 | 13:00 | Chaddagram | 38 | 19:00 | Borhan Uddin | 44 | 22:00
| Lalbag | 92 | 13:00 | PHP | 8 | 18:00 | Ishurdi | 67 | 18:30
| Madartek | 70 | 21:00 | Madunaghat | 55 | 18:30 | Ruppur Paromanobik | 2 | 21:00
| Dhaka University |  |  | Hathazari | 98 | 0.8125 | Natore | 126 | 21:00
| Fatullah | 38 | 0.5 | Khulshi | 205 | 0.45833 | Bogra | 171 | 21:00
| Mirpur | 105 | 18:30 | Halishahar | 140 | 0.625 | Noagaon | 126 | 20:00
| Kalyanpur | 99 | 18:30 | Baraulia | 138 | 0.41667 | Rajshahi | 150 | 21:00
| Gulshan | 136 | 12:00 | Sikalbaha | 28 | 0.77083 | Rajshahi New | 13 | 21:00
| Uttara | 83 | 19:00 | Dohazari | 82 | 0.79167 | C.Nawabganj | 73 | 21:00
| Uttara New | 31 | 19:00 | Cox'sbazar | 102 | 0.8125 | Amnura | 46 | 21:00
| Kamrangirchar | 94 | 18:30 | Chandraghona | 28 | 0.77083 | Pabna | 128 | 20:00
| Savar | 143 | 15:00 | Kaptai | 4.2 | 0.77083 | Shahjadpur | 105 | 19:00
| Bhasantec | 153 | 12:00 | A. Khaer Stl. | 0 | 0.041667 | Serajganj | 109 | 19:30
| Agargaon | 73 | 12:00 | Bakulia | 100 | 0.66667 | Niyamatpur | 58 | 21:00
| Satmosjid | 101 | 13:00 | Julda | 24 | 0.45833 | Joypurhat | 54 | 21:00
| Tongi | 95 | 0.45833 | TK chemical | 27.8 | 0.77083 | Sherpur(Bogura) | 49 | 18:30
| Kabirpur | 240 | 14:00 | Modern Steel | 10 | 0.95833 | Mohastangor | 50 | 21:00
| Basundhara | 138 | 12:00 | Shahmirpur | 24 | 0.041667 | Rangpur | 149 | 19:00
| Manikganj | 68 | 0.875 | Khagrachhari | 24 | 0.79167 | Lalmonirhat | 54 | 20:00
| Joydevpur | 136 | 18:30 | Matarbari | 34 | 0.83333 | Saidpur | 108 | 19:00
| New Tongi | 121 | 15:00 | Baroiar Hat | 38 | 0.77083 | Purbasadipur | 102 | 21:00
| Korda | 261 | 18:30 | Rangamati | 12 | 0.77083 | Thakurgaon | 86 | 21:00
| Dhamrai | 100 | 19:00 | Abul Khair 230 | 140 | 0.45833 | Palashbari | 129 | 20:00
| Rajendrapur | 96 | 21:00 | BSRM | 154 | 0.375 | Barapukuria | 50 | 21:00
| Valuka | 126 | 19:00 | GPH Ispat | 72 | 0.41667 | Panchagar | 49 | 21:00
| Tangail | 207 | 21:00 | Goalpara | 29 | 0.54167 | Joldhaka | 26 | 19:00
| Mymensing | 150 | 20:00 | Central s/s | 93 | 20:00 | Kurigram | 58 | 19:00
| Kishorganj | 140 | 21:00 | Noapara | 58 | 20:00
| Netrokona | 107 | 20:00 | Jessore | 120 | 19:00
| Jamalpur | 148 | 21:00 | Benapol | 50 | 20:00
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-09-13 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 393 | 19:00 | 386 | 12:00 | Kaliakoir | 374 | 24:00 | 364 | 0.33333
| Bheramara | 393 | 9:00 | 386 | 19:30 | Bhulta | 386 | 0.75 | 375 | 0.45833
| Ashuganj(N) | 391 | 22:00 | 382 | 11:00 | Gopalganj | 411 | 0.41667 | 387 | 0.875
| Payra | 414 | 10:00 | 401 | 21:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 230 | 1:00 | Comilla (N) | 233 | 19:00 | 226 | 11:00
| Ishurdi | 235 | 10:00 | 225 | 21:00 | Hathazari | 226 | 19:00 | 218 | 11:00
| Ashuganj | 236 | 18:30 | 232 | 8:00 | Megnaghat | 230 | 1:00 | 223 | 11:00
| Serajganj | 239 | 17:00 | 225 | 21:00 | Fenchuganj | 238 | 3:00 | 235 | 9:00
| Baghabari | 240 | 4:00 | 235 | 21:00 | Siddhirganj | 228 | 22:00 | 221 | 10:00
| Barapukuria | 238 | 7:00 | 226 | 19:00 | Maniknagar | 225 | 6:00 | 219 | 11:00
| Bogra | 228 | 7:00 | 214 | 19:00 | Agargaon | 223 | 22:00 | 215 | 11:00
| Rajshahi | 229 | 18:00 | 215 | 3:00 | Barisal | 246 | 14:00 | 232 | 4:00
| Khulna South | 232 | 18:00 | 221 | 5:00 | AKSML | 222 | 18:30 | 213 | 2:00
| Rampura | 224 | 1:00 | 220 | 10:00 | BSRM | 224 | 18:30 | 216 | 9:00
| Haripur | 224 | 19:00 | 218 | 11:00 | Bibiyana | 236 | 17:00 | 229 | 10:00
| Hasnabad | 225 | 18:30 | 219 | 11:00 | Bhulta | 228 | 19:00 | 220 | 17:00
| Shyampur | 223 | 22:00 | 214 | 12:00 | Ashuganj (S) | 234 | 17:00 | 229 | 11:00
| Aminbazar | 225 | 24:00 | 217 | 12:00 | Kaliakoir | 228 | 18:00 | 222 | 10:00
| Tongi | 226 | 23:00 | 217 | 11:00 | GPH | 223 | 18:00 | 213 | 11:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 129 | 5:00 | 124 | 11:00 | Hathazari | 135 | 0.75 | 130 | 0.041667
| Munsiganj | 131 | 18:30 | 125 | 9:00 | Khulshi | 132 | 0.75 | 128 | 0.25
| Sonargaon | 128 | 1:00 | 125 | 10:00 | Halishahar | 135 | 0.77083 | 130 | 0.20833
| Shyampur | 138 | 6:00 | 126 | 12:00 | Baraulia | 133 | 0.875 | 128 | 0.375
| Bhulta | 123 | 18:30 | 116 | 10:00 | Sikalbaha | 135 | 18:00 | 130 | 0.083333
| Madanganj | 134 | 1:00 | 124 | 11:00 | Dohazari | 131 | 19:00 | 125 | 0.20833
| Shitalakhya | 139 | 18:30 | 131 | 12:00 | Cox'sbazar | 123 | 0.375 | 115 | 0.083333
| Rahim steal | 129 | 1:00 | 124 | 9:00 | Chandraghona | 134 | 0.77083 | 129 | 0.125
| Matuail | 129 | 5:00 | 124 | 11:00 | Kaptai | 133 | 18:00 | 131 | 0.041667
| Ghorasal | 138 | 18:00 | 136 | 1:00 | A. Khaer Stl. | 131 | 0.75 | 127 | 10:00
| Narsinghdi | 123 | 6:00 | 118 | 10:00 | Bakulia | 134 | 0.79167 | 129 | 0.45833
| Haripur (SBU) | 131 | 5:00 | 125 | 10:00 | Julda | 135 | 0.79167 | 130 | 0.041667
| Ullon | 132 | 6:00 | 125 | 11:00 | TK Chemical | 135 | 0.77083 | 130 | 7:00
| Hasnabad | 135 | 19:00 | 127 | 11:00 | Modern Steel | 134 | 0.79167 | 129 | 0.5
| Magbazar | 132 | 6:00 | 125 | 10:00 | Shahmirpur | 135 | 0.8125 | 129 | 0.375
| Maniknagar | 132 | 24:00 | 125 | 12:00 | Khagrachhari | 133 | 0.79167 | 128 | 0.125
| Bangabhaban | 132 | 24:00 | 125 | 12:00 | Matarbari | 124 | 0.375 | 121 | 0.041667
| Narinda | 132 | 24:00 | 125 | 12:00 | Baroiar Hat | 132 | 0.77083 | 126 | 0.875
| Dhanmondi | 132 | 6:00 | 125 | 11:00 | Rangamati | 133 | 0.77083 | 129 | 3:00
| Lalbag | 136 | 24:00 | 124 | 12:00 | Goalpara S/S | 134 | 17:00 | 128 | 5:00
| Madartek | 130 | 1:00 | 125 | 10:00 | Khulna Central S/S | 137 | 0.75 | 126 | 4:00
| Dhaka University |  |  |  |  | Noapara | 134 | 18:00 | 126 | 5:00
| Fatuiiah | 131 | 0.125 | 126 | 8:00 | Jessore | 130 | 18:00 | 119 | 21:00
| Mirpur | 135 | 7:00 | 127 | 12:00 | Benapol | 130 | 18:00 | 118 | 21:00
| Kalyanpur | 132 | 6:00 | 126 | 12:00 | Jhenida | 127 | 0.75 | 112 | 20:00
| Gulshan | 130 | 6:00 | 124 | 12:00 | Bottail | 132 | 18:00 | 123 | 21:00
| Uttara | 131 | 6:00 | 127 | 12:00 | G.K Project | 141 | 0.75 | 134 | 20:00
| Uttara New | 131 | 6:00 | 128 | 12:00 | Faridpur | 132 | 8:00 | 123 | 21:00
| Kamrangirchar | 132 | 3:00 | 123 | 12:00 | Madaripur | 137 | 0.33333 | 126 | 21:00
| Savar | 131 | 5:00 | 126 | 12:00 | Shariyatpur S/S | 137 | 0.33333 | 124 | 20:00
| Bhasantec | 134 | 6:00 | 127 | 12:00 | Gopalganj | 135 | 9:00 | 123 | 20:00
| Agargaon | 135 | 5:00 | 129 | 12:00 | Bagerhat | 132 | 18:00 | 120 | 4:00
| Satmosjid | 135 | 6:00 | 129 | 11:00 | Mongla | 129 | 0.75 | 118 | 1:00
| Tongi | 136 | 0.875 | 130 | 11:00 | Satkhira | 135 | 0.75 | 124 | 5:00
| Kabirpur | 133 | 24:00 | 128 | 11:00 | Gallamari | 136 | 18:00 | 127 | 5:00
| Basundhara | 134 | 22:00 | 123 | 12:00 | Magura | 126 | 18:00 | 110 | 21:00
| Manikganj | 139 | 18:00 | 131 | 1:00 | Norail | 125 | 0.33333 | 106 | 21:00
| Joydevpur | 142 | 18:00 | 134 | 14:00 | Chuadanga | 120 | 18:00 | 100 | 21:00
| New Tongi | 135 | 0.875 | 129 | 12:00 | Barisal(N) | 138 | 7:00 | 129 | 4:00
| Kodda | 135 | 21:00 | 120 | 0.33333 | Barisal (S) | 138 | 0.75 | 129 | 4:00
| Dhamrai | 132 | 18:00 | 127 | 11:00 | Patuakhali(S) | 135 | 0.75 | 122 | 21:00
| Rajendrapur | 132 | 21:00 | 122 | 8:00 | Bhandaria | 126 | 18:00 | 115 | 1:00
| Valuka | 126 | 6:00 | 117 | 18:30 | Ishurdi | 138 | 18:00 | 132 | 21:00
| Tangail | 135 | 17:00 | 129 | 22:00 | Ruppur Paromanobik | 137 | 17:00 | 132 | 21:00
| Mymensing | 131 | 17:00 | 123 | 20:00 | Natore | 137 | 18:00 | 130 | 21:00
| Kishorganj | 131 | 17:00 | 122 | 19:00 | Bogra | 137 | 8:00 | 128 | 21:00
| Netrokona | 128 | 17:00 | 119 | 18:30 | Noagaon | 134 | 6:00 | 122 | 21:00
| Jamalpur | 138 | 19:00 | 132 | 18:30 | Rajshahi | 138 | 18:00 | 129 | 21:00
| Sherpur | 139 | 17:00 | 131 | 3:00 | Rajshahi New | 138 | 18:00 | 130 | 21:00
| Srimongal | 137 | 17:00 | 132 | 0.29167 | C.Nawabganj | 138 | 18:00 | 128 | 21:00
| Shahjibazar | 136 | 17:00 | 131 | 0.041667 | Amnura | 138 | 18:00 | 128 | 1:00
| Fenchuganj | 136 | 7:00 | 133 | 0.8125 | Pabna | 135 | 7:00 | 128 | 21:00
| Khulawara | 134 | 3:00 | 132 | 0.75 | Shahjadpur | 140 | 18:00 | 135 | 21:00
| Sylhet | 133 | 4:00 | 131 | 0.91667 | Serajganj | 133 | 18:00 | 128 | 21:00
| Chatak | 132 | 7:00 | 129 | 1:00 | Niyamatpur | 134 | 9:00 | 120 | 21:00
| Sunamganj | 132 | 7:00 | 126 | 0.79167 | Joypurhat | 135 | 6:00 | 120 | 21:00
| Biani Bazar | 132 | 8:00 | 128 | 0.041667 | Sherpur(Bogura) | 136 | 6:00 | 128 | 21:00
| Comilla(s) | 126 | 5:00 | 120 | 18:30 | Mohastangor | 136 | 9:00 | 126 | 21:00
| Comilla(n) | 135 | 13:00 | 132 | 15:00 | Rangpur | 133 | 6:00 | 115 | 19:00
| Chandpur | 134 | 19:30 | 126 | 22:00 | Lalmonirhat | 133 | 7:00 | 115 | 19:00
| Feni | 132 | 19:00 | 126 | 21:00 | Saidpur | 136 | 6:00 | 117 | 19:30
| Chowmuhani | 130 | 7:00 | 125 | 16:00 | Purbasadipur | 132 | 7:00 | 112 | 21:00
| Ashuganj | 135 | 14:00 | 132 | 2:00 | Thakurgaon | 131 | 7:00 | 110 | 19:00
| Daudkandi | 129 | 18:30 | 125 | 11:00 | Palashbari | 133 | 7:00 | 119 | 19:00
| B.Baria | 132 | 14:00 | 127 | 21:00 | Barapukuria | 138 | 7:00 | 126 | 19:00
| Ramganj | 128 | 19:00 | 118 | 23:00 | Panchagar | 129 | 7:00 | 107 | 19:00
| Chaddagram | 134 | 19:00 | 127 | 2:00 | Joldhaka | 133 | 7:00 | 113 | 19:00
| PHP | 133 | 19:00 | 127 | 15:00 | Kurigram | 131 | 6:00 | 111 | 19:30
| Madanhat | 137 | 19:00 | 131 | 12:00

## L-Curve
Date | 2020-09-13
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 40 | 7971 | 4039 | 12010 |  |  |  | QF-LDC-11
0:30 | 26 | 7855.5 | 3879 | 11734.5 | Date: | 2020-09-13
1:00 | 12 | 7740 | 3719 | 11459
1:30 | 15 | 7611 | 3597 | 11208
2:00 | 18 | 7482 | 3475 | 10957
2:30 | 26.5 | 7311.5 | 3451 | 10762.5 | [5 empty] | Gen. at Eve. Peak | 12345 | 12345 MW (19:30 )
3:00 | 35 | 7141 | 3427 | 10568 | [6 empty] | 19:30
3:30 | 42.5 | 7098 | 3429 | 10527 | [5 empty] | Gen. at Day Peak | 10506 | 10506 MW (12:00 )
4:00 | 50 | 7055 | 3431 | 10486 | [6 empty] | 12:00
4:30 | 69.5 | 6998 | 3385 | 10383 | [5 empty] | Highest Generation | 12345
5:00 | 89 | 6941 | 3339 | 10280 | [6 empty] | 19:30
5:30 | 213.5 | 6804.5 | 3273 | 10077.5
6:00 | 338 | 6668 | 3207 | 9875
6:30 | 355.5 | 6425 | 3173.5 | 9598.5
7:00 | 373 | 6182 | 3140 | 9322
7:30 | 370.5 | 6178.5 | 3140.5 | 9319
8:00 | 368 | 6175 | 3141 | 9316
8:30 | 376 | 6341.5 | 3128.5 | 9470
9:00 | 384 | 6508 | 3116 | 9624
9:30 | 382.5 | 6711.55 | 3123 | 9834.55
10:00 | 381 | 6915.1 | 3130 | 10045.1
10:30 | 402.5 | 7021.55 | 3170.5 | 10192.05
11:00 | 424 | 7128 | 3211 | 10339
11:30 | 396 | 7180.5 | 3242 | 10422.5
12:00 | 368 | 7233 | 3273 | 10506
12:30 | 340 | 7272.9 | 3328 | 10600.9
13:00 | 312 | 7312.8 | 3383 | 10695.8
13:30 | 291.5 | 7248.9 | 3359 | 10607.9
14:00 | 271 | 7185 | 3335 | 10520
14:30 | 265.5 | 7277 | 3345 | 10622
15:00 | 260 | 7369 | 3355 | 10724
15:30 | 270 | 7214 | 3318.5 | 10532.5
16:00 | 280 | 7059 | 3282 | 10341
16:30 | 267 | 6945 | 3163.5 | 10108.5
17:00 | 254 | 6831 | 3045 | 9876
17:30 | 213 | 6887.5 | 3088.5 | 9976
18:00 | 172 | 6944 | 3132 | 10076
18:30 | 164.5 | 7576 | 3492 | 11068
19:00 | 157 | 8208 | 3852 | 12060
19:30 | 180 | 8364 | 3981 | 12345
20:00 | 138 | 8281 | 4009 | 12290 |  |  |  | Executive Engineer
20:30 | 108 | 8216 | 4045.5 | 12261.5 |  |  |  | Network Operation Division
21:00 | 78 | 8151 | 4082 | 12233
21:30 | 47 | 8118.5 | 4100.5 | 12219
22:00 | 16 | 8086 | 4119 | 12205 |  |  |  |  | Page 6 of 7
22:30 | 22 | 8087.5 | 4103 | 12190.5
23:00 | 28 | 8089 | 4087 | 12176
23:30 | 34 | 8030 | 4063 | 12093
24:00 | 40 | 7971 | 4039 | 12010
12345 MW (19:30 )
10506 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-09-13 |  | Energy | 260985089
[10 empty] | 2020-09-13 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4102 | 926 | 2117 | 3388 | 721 | 85 | 577 | 0 | 168
0:30 | 4189.5 | 926.5 | 2148.5 | 3150 | 710.5 | 65 | 416.5 | 0 | 165 | Date: | 2020-09-13
1:00 | 4277 | 927 | 2180 | 2912 | 700 | 45 | 256 | 0 | 162
1:30 | 4283 | 927 | 2156 | 2756 | 700 | 45 | 181 | 0 | 160 | [7 empty] | Total Energy | 260.9851 | Total Energy Gen 260.985 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 260.985 MKWHr
2:00 | 4289 | 927 | 2132 | 2600 | 700 | 45 | 106 | 0 | 158 | [7 empty] | Energy not Served | 0
2:30 | 4301.5 | 927 | 2145 | 2418.5 | 700 | 45.5 | 69 | 0 | 156 | [7 empty] | Energy Requirement | 260.9851
3:00 | 4314 | 927 | 2158 | 2237 | 700 | 46 | 32 | 0 | 154
3:30 | 4312 | 927 | 2170 | 2177 | 700 | 46 | 42 | 0 | 153 | [6 empty] | Shortage
4:00 | 4310 | 927 | 2182 | 2117 | 700 | 46 | 52 | 0 | 152
4:30 | 4330.5 | 927 | 2181 | 1997.5 | 700 | 46 | 52 | 0 | 149
5:00 | 4351 | 927 | 2180 | 1878 | 700 | 46 | 52 | 0 | 146
5:30 | 4275.5 | 927.5 | 2128 | 1814.5 | 700 | 46.5 | 43.5 | 0 | 142
6:00 | 4200 | 928 | 2076 | 1751 | 700 | 47 | 35 | 0 | 138
6:30 | 4036 | 927.5 | 2009.5 | 1708.5 | 685 | 47 | 47.5 | 0 | 133 |  |  |  |  | Coal
7:00 | 3872 | 927 | 1943 | 1666 | 670 | 47 | 60 | 0 | 128
7:30 | 3876.5 | 927 | 1929 | 1658 | 660 | 46.5 | 82 | 0 | 128 |  |  |  | Oil |  |  |  | ,
8:00 | 3881 | 927 | 1915 | 1650 | 650 | 46 | 104 | 0 | 128
8:30 | 3910 | 927 | 1913.5 | 1791.5 | 640 | 45.5 | 94 | 0 | 129
9:00 | 3939 | 927 | 1912 | 1933 | 630 | 45 | 84 | 0 | 130
9:30 | 3933.5 | 927.5 | 1901 | 2176.5 | 605 | 44.5 | 89 | 0 | 134
10:00 | 3928 | 928 | 1890 | 2420 | 580 | 44 | 94 | 0 | 138
10:30 | 4014.5 | 928 | 1934 | 2448 | 590 | 43.5 | 78 | 0 | 139
11:00 | 4101 | 928 | 1978 | 2476 | 600 | 43 | 62 | 0 | 140
11:30 | 4048 | 927.5 | 2026.5 | 2550 | 610 | 42.5 | 61.5 | 0 | 140
12:00 | 3995 | 927 | 2075 | 2624 | 620 | 42 | 61 | 0 | 140
12:30 | 3984.5 | 927.5 | 2061.5 | 2700.5 | 617.5 | 55 | 88.5 | 0 | 141
13:00 | 3974 | 928 | 2048 | 2777 | 615 | 68 | 116 | 0 | 142
13:30 | 3974 | 928 | 2048 | 2777 | 615 | 68 | 116 | 0 | 142
14:00 | 3974 | 928 | 2048 | 2777 | 615 | 68 | 116 | 0 | 142
14:30 | 3954.5 | 927.5 | 2034.5 | 2812 | 617 | 68.5 | 126 | 0 | 149
15:00 | 3935 | 927 | 2021 | 2847 | 619 | 69 | 136 | 0 | 156
15:30 | 3965 | 927 | 2037 | 2607 | 624 | 69.5 | 136 | 0 | 156
16:00 | 3995 | 927 | 2053 | 2367 | 629 | 70 | 136 | 0 | 156
16:30 | 3922.5 | 928.5 | 1971.5 | 2315.5 | 610 | 70 | 138.5 | 0 | 147
17:00 | 3850 | 930 | 1890 | 2264 | 591 | 70 | 141 | 0 | 138
17:30 | 3828.5 | 928 | 1799 | 2342.5 | 590.5 | 75 | 270.5 | 0 | 141
18:00 | 3807 | 926 | 1708 | 2421 | 590 | 80 | 400 | 0 | 144
18:30 | 3936.5 | 926 | 1867 | 2940 | 605 | 82.5 | 553 | 0 | 158
19:00 | 4066 | 926 | 2026 | 3459 | 620 | 85 | 706 | 0 | 172
19:30 | 4063 | 927 | 2074 | 3640 | 650 | 85 | 742 | 0 | 164
20:00 | 4081 | 926 | 2080 | 3543 | 650 | 85 | 751 | 0 | 174
20:30 | 4062.5 | 926 | 2095 | 3515.5 | 680 | 85 | 723.5 | 0 | 174
21:00 | 4044 | 926 | 2110 | 3488 | 710 | 85 | 696 | 0 | 174
21:30 | 4024.5 | 926 | 2121.5 | 3477 | 715 | 85 | 696 | 0 | 174
22:00 | 4005 | 926 | 2133 | 3466 | 720 | 85 | 696 | 0 | 174
22:30 | 4075.5 | 926 | 2126 | 3427 | 720 | 85 | 657 | 0 | 174
23:00 | 4146 | 926 | 2119 | 3388 | 720 | 85 | 618 | 0 | 174
23:30 | 4124 | 926 | 2118 | 3388 | 720.5 | 85 | 597.5 | 0 | 171 | Max Temp. in Dhaka |  | 33.9° C
24:00 | 4102 | 926 | 2117 | 3388 | 721 | 85 | 577 | 0 | 168
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 260.985 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 260.985 MKWHr
Note on W13: Author:

## Generation
g | 2020-09-13
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 45 | 45 | 46 | 46 | 46 | 47 | 47 | 46 | 45 | 44 | 43 | 42 | 68 | 68 | 69 | 70 | 70 | 80 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1408015
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3100000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 4 |  | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 143906
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 7 | 12 | 18 | 16 | 4 | 10 | 20 | 6 | 11 | 5 | 1 | [9 empty] | 124335
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 203 | 213 | 203 | 209 | 203 | 202 | 204 | 204 | 203 | 203 | 205 | 203 | 203 | 204 | 218 | 203 | 204 |  | 203 | 203 | 203 | 165 | 164 | 168 | 164 | 4667898
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 140 | 140 | 140 | 141 | 138 | 137 | 140 | 140 | 141 | 140 | 141 | 139 | 141 | 104 | 104 | 104 | 104 | 104 |  | 139 | 139 | 139 | 100 | 100 | 104 | 17 | 2997402
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 17 | 17 | 17 | 17 | 17 | 0 | [11 empty] | 26 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 693921
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [17 empty] | 9 |  | 50 | 50 | 50 |  |  |  | 0 | 117112
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | [9 empty] | 33 | 97 | 35 | 32 | 35 | 34 | 60 | [10 empty] | 367000
17 | Siddhirganj 335 MW CCPP | 292 | 290 | 293 | 300 | 300 | 287 | 275 | 277 | 268 | 290 | 292 | 288 | 265 | 294 | 287 | 306 | 260 | 278 |  | 304 | 282 | 280 | 301 | 240 | 287 | 300 | 6952903
18 | Kodda 300 MW PP Unit-2 (Summit) | 300 | 300 | 300 | 300 | 200 | 145 | 145 | 145 | 174 | 293 | 300 | 300 | 300 | 300 | 300 | 200 | 200 | 200 |  | 265 | 300 | 300 | 300 | 300 | 300 | 290 | 6327924
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 150 | 150 | 148 | 150 | 150 | 150 | 150 | 100 |  | 150 | 150 | 150 | 150 | 150 | 154 | 150 | 2998000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4808236
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1923456
32 | Ashuganj 50 MW PP | 35 | 35 | 35 | 35 | 35 | 35 | 32 | 35 | 35 | 35 | 35 | 22 | 22 | 22 | 20 | 20 | 20 | 22 |  | 22 | 20 | 22 | 22 | 22 | 22 | 22 | 661608
33 | Ashuganj 225 MW CCPP | 180 | 192 | 195 | 196 | 201 | 175 | 175 | 175 | 175 | 193 | 183 | 171 | 175 | 169 | 163 | 138 | 159 | 165 |  | 172 | 177 | 184 | 197 | 180 | 175 | 175 | 4334000
34 | Ashuganj 450 MW CCPP(South) | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 280 | 280 | 280 | 280 | 280 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 6687000
| Ashuganj 450 MW CCPP(North) | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 345 | 260 | 270 | 280 | 270 | 270 | 270 | 280 | 270 | 275 |  | 270 | 275 | 275 | 275 | 280 | 275 | 275 | 6998000
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 137280
36 | Chandpur 150 MW CCPP | 85 | 86 | 85 | 86 | 91 | 86 | 82 | 81 | 81 | 90 | 81 | 82 | 81 | 89 | 80 | 91 | 82 | 80 |  | 80 | 80 | 87 | 92 | 90 | 87 | 84 | 2027090
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 351 | 351 | 351 | 351 | 351 | 314 | [5 empty] | 3 | 81 | 21 | 54 | 101 | 206 | 276 |  | 337 | 336 | 336 | 336 | 348 | 338 | 355 | 4997980
40 | Meghnaghat 450 MW CCPP(MPL) | 420 | 420 | 420 | 420 | 420 | 420 | 360 | 360 | 360 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 350 |  | 370 | 380 | 380 | 380 | 380 | 380 | 380 | 7910250
41 | Haripur 360MW CCPP(HPL) | 351 | 353 | 355 | 354 | 354 | 354 | 303 | 302 | 333 | 304 | 305 | 344 | 348 | 304 | 350 | 349 | 309 | 275 |  | 334 | 334 | 335 | 335 | 330 | 324 | 310 | 7857000
42 | RPCL 210MW CCPP | 143 | 143 | 156 | 158 | 158 | 160 | 160 | 160 | 161 | 156 | 142 | 138 | 124 | 120 | 122 | 122 | 123 | 122 |  | 122 | 123 | 122 | 123 | 126 | 127 | 144 | 3267600
43
44 | Fenchugonj CCPP Phase-1 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 90 | 90 | 91 | 91 | 91 | 91 | 91 | 91 |  | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 2151000
45 | Fenchugonj CCPP Phase-2 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 30 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 30 | 30 | 28 | 28 | 677160
46 | Shajibazar 330 MW CCPP | 285 | 287 | 285 | 284 | 287 | 284 | 286 | 284 | 286 | 287 | 285 | 284 | 284 | 285 | 282 | 283 | 284 | 287 |  | 285 | 287 | 286 | 285 | 277 | 260 | 263 | 6438000
47 | Shahjibazar GTPP Unit- 8 & 9 | 66 | 66 | 66 | 66 | 65 | 65 | 65 | 65 | 64 | 63 | 61 | 61 | 61 | 61 | 61 | 60 | 62 | 67 |  | 52 | 52 | 52 | 52 | 62 | 64 | 64 | 1474464
48 | Shahjibazar 86MW PP (Shahjibazar) | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 20 |  | 88 | 88 | 88 | 85 | 88 | 88 | 88 | 2028480
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 185 | 184 | 184 | 184 | 185 | 185 | 185 | 185 | 185 | 196 | 233 | 233 | 184 | 184 | 185 | 185 | 184 | 184 |  | 185 | 184 | 185 | 185 | 185 | 185 | 185 | 4532720
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 423000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 245700
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 2 | 8 |  | 8 | 8 | 8 | 8 |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 174000
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 47 | 47 | 50 | 50 | 50 | 50 | 50 | 25 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1161000
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 540288
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 280 | 290 | 300 | 300 | 290 | 280 | 280 | 260 | 280 | 300 | 300 | 285 | 280 | 295 | 295 | 300 | 280 |  | 270 | 280 | 270 | 290 | 290 | 280 | 300 | 7156000
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | [6 empty] | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 28 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 859129
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 487824
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 |  |  | 19 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 |  | 22 | 22 | 398880
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 20 | 20 | 20 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 453132
63 | Impoprt (Tripura) | 162 | 158 | 154 | 152 | 146 | 138 | 128 | 128 | 130 | 138 | 140 | 140 | 142 | 152 | 156 | 156 | 138 | 144 |  | 172 | 164 | 174 | 174 | 174 | 174 | 168 | 3672000
64 | Malancha, Ctg. EPZ (United) | 42 | 40 | 42 | 42 | 42 | 42 | 34 | 8 | 4 | 4 | 3 | 5 | 9 | 7 | 4 | 6 | 11 | 13 |  | 21 | 24 | 28 | 35 | 39 | 40 | 41 | 565440
65 | Feni 22MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 416088
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 239580
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | [7 empty] | 33 | 33 | 633200
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 15 | 21 | 21 | 21 | 21 |  |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 500380
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 521100
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 786600
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 786400
73 | Ghorashal 108MW PP (Regent) | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 65 | 82 | 83 | 83 | 83 | 83 | 83 | 83 | 83 |  | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 1752181
| Feni Lanka Power | 70 | 17 | [15 empty] | 17 |  | 101 | 26 | 17 | 17 | 17 | 17 | 17 | 323760
| Chowmuhani 113 MW | 113 | 113 | 108 | 108 | 108 | 108 | 113 | 113 | 113 | 113 | 113 | 113 | 106 | 110 | 113 | 106 | 110 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2687160
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 7 | 10 | 28 | 90 | 90 | 70 | 50 | 50 | 65 | 100 | 100 | 100 | 100 | 100 | 100 | 93 | 93 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2010240
78 | Gazipur 52 MW PP | [8 empty] | 5 | 16 | [7 empty] | 16 |  | 51 | 51 | 51 | 51 | 25 |  | 0 | 243060
79 | Kodda 150MW PP | 32 | 16 |  |  |  |  | 20 | 64 | 64 | 64 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 133 |  | 150 | 150 | 150 | 150 | 150 | 150 | 114 | 1347360
80 | Jamalpur 95 MW PP(Powerpac) | 55 | 55 | 55 | 55 | 55 | 55 | 48 | 8 | 20 | 47 | 56 | 56 | 50 | 56 | 56 | 56 | 56 | 56 |  | 56 | 56 | 56 | 56 | 56 | 55 | 55 | 1220160
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 34 | [6 empty] | 20 | 25 | 25 | 40 | 43 | 43 | 25 | 8 | 8 |  | 35 | 43 | 43 | 43 | 43 | 43 | 43 | 643584
| Gazipur 100 MW PP | 52 | 3 | [6 empty] | 50 | 50 | 50 | 88 | 88 | 70 | 88 | 88 | 88 | 88 |  | 88 | 87 | 87 | 104 | 104 | 104 | 104 | 1360176
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 5 | 4.1 | 4 | 6 | 0.8 | 0 | 0 | 1 | 0 | [9 empty] | 19439
| Jodiac Power | [25 empty] | 0 | 0
Karnaphuli Power Ltd.
82 | Madanganj 102 PP(Summit) | 80 | 80 | 80 | 60 | 48 | 48 | 48 | 48 | 48 | 60 | 64 | 64 | 64 | 64 | 64 | 64 | 65 | 80 |  | 95 | 96 | 96 | 96 | 97 | 97 | 97 | 1744632
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 50 | [11 empty] | 66 | 81 | 84 | 50 | 40 | 40 |  | 98 | 100 | 100 | 100 | 100 | 80 | 81 | 1019635
86 | Meghnaghat CCPP(Summit) | 140 | 140 | 140 | 140 | 140 | 140 | 135 | 135 | 135 | 140 | 140 | 135 | 125 | 140 | 135 | 150 | 125 | 135 |  | 130 | 135 | 140 | 140 | 150 | 140 | 140 | 3362182
87 | Meghnaghat 100 MW(IEL) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 96 | 93 | 93 | 93 |  | 100 | 93 | 92 | 92 | 100 | 100 | 100 | 2395200
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 29 | 20 | 17 | 17 | 15 |  | 2 | 17 | 17 | 17 | 17 | 17 | 17 | 430080
88 | Ghorashal 78.5 MW PP(MAX) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 50 | 66 | 67 | 67 | 67 | 67 | 40 | 40 |  | 60 | 67 | 67 | 67 | 67 | 67 | 67 | 1304576
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [17 empty] | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 0 | 139200
92 | Fenchuganj 44MW (Energyprima) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 46 | 47 | 47 | 47 | 47 | 48 | 49 | 20 |  | 42 | 50 | 50 | 50 | 50 | 50 | 50 | 1110528
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1247501
94 | Gagnagar 102 MW PP (Digital Power) | 85 | 85 | 85 | 87 | 93 | 93 | 90 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 |  | 93 | 93 | 93 | 93 | 93 | 93 | 92 | 2208096
95 | Patenga 50MW PP (Baraka) | 39 | [7 empty] | 4 | 18 | 19 | 19 | 37 | 50 | 50 | 30 | 19 | 19 |  | 44 | 50 | 50 | 50 | 50 | 50 | 50 | 618240
96 | Chattogram 108 MW PP (ECPV) | 84 | 70 | [6 empty] | 0 | 33 | 72 | 77 | 77 | 77 | 77 | 57 | 30 | 31 |  | 78 | 85 | 85 | 85 | 85 | 85 | 85 | 1202880
97 | Katpotti 52 MW PP (Sinha) | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 15 | 15 | 15 | 21 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1201794
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 17 | [5 empty] | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 17 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 843205
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 130 | 130 | 130 | 130 | 130 | 163 | 163 | 163 | 110 | 163 | 163 | 110 | 110 |  | 110 | 110 | 110 | 110 | 130 | 130 | 163 | 3485127
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 1 | 1 | 3 | 2 | 2 | 1 | 0 | 0 | [9 empty] | 9250
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | [6 empty] | 17 | 54 | 54 | 54 | 54 | 54 | 54 | 17 | 17 | 17 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 874800
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko) | [25 empty] | 0 | 23940
106 | Mymensingh 200 MW PP (United) | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 185 | 200 | 200 | 200 | 200 | 182 | 170 | 200 | 200 | 200 | 170 |  | 200 | 200 | 200 | 200 | 200 | 200 | 192 | 4627200
112 | Aurahati 100MW PP (Aggreko) | [25 empty] | 0 | 26968
114 | Kodda 149 MW PP Unit-1 (Summit) | 137 | 144 | 134 | 110 | 110 | 110 | 110 | 110 | 131 | 149 | 144 | 146 | 136 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3345120
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 90 | 95 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 100 | 100 | 100 | 100 | 2323200
116 | Chandpur 200MW (Desh energy) | [17 empty] | 6 |  | 104 | 200 | 100 |  |  |  | 0 | 294240
117 | Ashuganj 150MW PP (Midland) | 100 | 100 | 50 | 5 | 5 | 5 | 5 | 5 | 10 | 40 | 41 | 97 | 130 | 125 | 132 | 80 | 80 | 80 |  | 112 | 130 | 132 | 137 | 138 | 137 | 132 | 1985527
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 110 | 75 | 24 | 24 | 24 | 24 | 8 | 8 | 8 | 8 | 18 | 48 | 65 | 45 | 35 | 35 | 35 | 35 |  | 84 | 113 | 115 | 115 | 115 | 115 | 115 | 1414800
| Anwara 300 MW PP (United) | 216 | 216 | 198 | 180 | 162 | 160 | 160 | 159 | 195 | 197 | 197 | 197 | 197 | 197 | 198 | 163 | 163 | 180 |  | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 4548982
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2433600
120 | Eastern Zone Total | 7740 | 7482 | 7141 | 7055 | 6941 | 6668 | 6182 | 6175 | 6508 | 6915.1 | 7128 | 7233 | 7312.8 | 7185 | 7369 | 7059 | 6831 | 6944 |  | 8208 | 8364 | 8281 | 8151 | 8086 | 8089 | 7971 | 175474558
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 115 | 115 | 115 | 115 | 115 | 115 | 99 | 115 | 115 | 115 | 115 | 115 | 115 | 99 | 102 | 69 | 66 | 66 |  | 115 | 115 | 115 | 115 | 115 | 99 | 99 | 2551680
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [17 empty] | 4 |  | 21 | 26 | 18 | 18 | 18 | 18 | 18 | 117550
| Khulna 225 MW CCPP | 110 | 25 | 15 | 35 | 35 | 35 | 40 | 40 | 20 | 30 | 30 | 45 | 100 | 120 | 120 | 120 | 120 | 120 |  | 160 | 170 | 170 | 170 | 170 | 170 | 170 | 2207040
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | 17 | 17 | 17 | 17 | 17 | [13 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 298560
130
131
132
133
| Barisal 110 MW PP (Summit ) | 64 | 64 | 32 | 0 |  |  |  |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 53 |  | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 967872
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 77 | 78 | 78 | 78 | 78 | 78 | 79 | 78 | 78 | 78 | 77 | 79 | 77 | 78 | 77 | 77 | 78 | 78 |  | 77 | 77 | 77 | 78 | 79 | 79 | 78 | 1879243
| Bhola 225 MW CCPP | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 |  | 65 | 65 | 67 | 67 | 68 | 68 | 65 | 1555000
140 | Bhola 33 MW PP (Venture) | 39 | 38 | 38 | 35 | 33 | 32 | 27 | 27 | 25 | 27 | 25 | 28 | 29 | 28 | 29 | 28 | 26 | 31 |  | 38 | 38 | 39 | 39 | 39 | 40 | 39 | 770711
141 | Noapara 100 MW PP (Bangla Trac) | 100 | 50 | 64 | 70 | 0 | [14 empty] | 92 | 100 | 100 | 100 | 100 | 100 | 100 | 969600
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 40 | 40 | 0 |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 24 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 489750
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 5 | 10 | [8 empty] | 11904
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 927 | 927 | 927 | 927 | 927 | 928 | 927 | 927 | 927 | 928 | 928 | 927 | 928 | 927 | 927 | 927 | 930 | 926 |  | 926 | 927 | 926 | 926 | 926 | 926 | 926 | 22241455
147 | Bheramara 410 MW CCPP | 345 | 345 | 345 | 345 | 370 | 340 | 340 | 345 | 345 | 345 | 400 | 395 | 405 | 400 | 385 | 375 | 290 | 260 |  | 310 | 310 | 310 | 310 | 380 | 370 | 365 | 8717184
148 | Payra 1320 MW | 550 | 550 | 550 | 550 | 550 | 550 | 520 | 500 | 480 | 430 | 450 | 460 | 470 | 470 | 480 | 490 | 450 | 450 |  | 470 | 500 | 500 | 560 | 570 | 570 | 570 | 12948000
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 160 | 145 | 141 | 139 | 139 | 141 | 140 |  | 150 | 150 | 150 | 150 | 150 | 150 | 151 | 3610200
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP | 60 | 60 | 60 | 55 | 55 | 55 | 55 | 55 | 55 | 45 | 40 | [14 empty] | 0 | 627000
| Baghabari 50 MW Peaking PP | [17 empty] | 4 |  | 50 | 50 | 50 | 50 | 50 |  | 0 | 219216
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 146 | 146 | 145 | 145 | 145 | 146 | 147 | 147 | 146 | 146 | 142 | 144 | 145 | 145 | 144 | 144 | 145 | 145 |  | 145 | 147 | 147 | 146 | 130 | 130 | 130 | 3568000
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | [24 empty] | 5 | 9 | 15200
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 200 | 200 | 200 | 200 | 200 | 170 | 170 | 170 | 170 | 170 | 178 | 193 | 206 | 170 | 200 | 180 | 130 | 130 |  | 150 | 150 | 150 | 150 | 137 | 208 | 216 | 4802218
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 398 | 370 | 382 | 400 | 400 | 340 | 340 | 340 | 332 | 357 | 369 | 402 | 379 | 367 | 348 | 376 | 323 | 280 |  | 380 | 390 | 400 | 405 | 405 | 405 | 365 | 9022272
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [20 empty] | 22 | 35 | 34 | 34 | 6 |  | 124381
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 487200
163 | Bogura 20 MW PP (Energyprima) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 186552
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  |  |  | 8 | 11 | 11 | 11 | 11 | 11 | 218340
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [25 empty] | 0
167 | Katakhali 50 MW Peaking PP | [17 empty] | 12 |  | 43 | 43 | 47 | 43 | 43 | 43 | 43 | 243600
168 | Santahar 50 MW Peaking PP | [17 empty] | 7 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 185692
169 | Natore 52 MW PP (Rajlanka) | [17 empty] | 8 |  | 35 | 44 | 47 | 47 | 32 | 25 | 25 | 230400
170 | Chapainawabganj 100 MW Peaking PP | 97 | 48 | 0 | [14 empty] | 75 |  | 98 | 97 | 97 | 97 | 97 | 97 | 98 | 761840
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [12 empty] | 40 | 50 | 72 | 35 | 35 | 35 |  | 92 | 113 | 113 | 113 | 113 | 113 | 113 | 1028064
172 | Confidence Power Bogura Unit-1 113 MW | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 |  | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 2602560
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 70 | 38 | 55 | 55 | 50 | 40 | 34 | 35 | 37 | 69 | 70 | 87 | 104 | 102 | 98 | 85 | 70 | 71 |  | 94 | 98 | 99 | 112 | 111 | 113 | 107 | 1835520
177 | Sympa Solar Power 8MW | [6 empty] | 1 | 1 | 1 | 2 | 2 | 3 | 5 | 3 | 2 | 2 | 1 | 0 | [8 empty] | 16727
178
178