## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-09-15 | Tuesday
|  |  | Date (day): | 2020-09-15 |  | Tuesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14229.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15045 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-09-14 | 2020-09-15 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 150 | 100 | 0 | 0 |  | 180 | Under maint
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 115 | 115 | 115
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 200 | 200
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 40 | 40 | 67 | 68 |  | 10 | Engine problem
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 62 | 12 | 100 | 100
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 359 | 339 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 304 | 305 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 320 | 380 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 100 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 138 | 125 | 150 | 150 | 155 |  | GT-1 S/D for gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 80 | 97 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 55 | 100 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 303 | 278 | 335 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 93 | 102 | 100 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 150 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 46 | 48 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 16 | 8 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 292 | 300 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 133 | 131 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 105 | 104 | 100 | 100
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 17 | 70 | 80 | 24 |  | Fuel shortage
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 3143 | 3458 | 4121 | 4384 | 653 | 605
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 130 | 130 | 130 | 130 | 50 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 8 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 10 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 37 | 40 | 40 | 40 | 190 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 206 | 189 | 0 | 0 |  | 225 | Under maint
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 120 | 120 | 120
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 100 | 100
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 50 | 30 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 100 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 21 | 21 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 33 | 5 | 30
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 75 | 85 | 85 | 85 |  | 23 | Engine problem
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 179 | 197 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 52 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 952 | 1257 | 1465 | 1465 | 420 | 346
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 80 | 80 | 80 | 54 |  | Gas shortage
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 186 | 162 | 214 | 214 |  |  | FGMO
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 290 | 290 | 360 | 360 |  |  | FGMO
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 270 | 360 | 360 |  |  | FGMO
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 10 | 10 | 10 |  | 35 | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 35 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 132 | 138 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 85 | 100 | 100 |  | 63 | ST under shut down
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 51 | 200 | 200
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 21 | 21
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 148 | 176 | 157 | 173
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 20 | 43 | 43 | 43 |  | 9 | Engine problem
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 21 | 21 | 21
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 68 | 114 | 114
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 104 | 113 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1468 | 1617 | 2051 | 2317 | 555 | 107
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 123 | 109 | 140 | 140 | 62 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 20 | 20 | 22
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 54 | 55 | 55 | 55 |  | 40 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 170 | 184 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 24 | 65 | 115 | 115
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 394 | 433 | 531.6 | 532 | 62 | 40
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 91 | 88 | 90 | 90
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 28 | 22 | 30 | 30 |  | 60 | Unit-4 under shut down
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 130 | 163 | 163
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 263 | 310 | 300 | 300
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 52 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 46 | 50 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 0 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 59 | 62 | 64 | 64 |  |  | FGMO
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 88 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 200 | 185 | 225 | 225
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 280 | 341 | 341
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1350 | 1319 | 1458 | 1458 | 0 | 460
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 932 | 927 | 945 | 945
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 99 | 115 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 27 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 170 | 225 | 225
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 310 | 320 | 410 | 410
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 8 | 40 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 92 | 50 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 53 | 105 | 105
| 108 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1469 | 1744 | 1990 | 2146 | 0 | 0
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 96 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 27 | 39 | 33 | 33
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 67 | 68 | 65 | 68 |  | 126 | GT-2 & ST Under maint.
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 76 | 77 | 77 | 77 |  | 18 | Engine problem
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 360 | 520 | 620 | 620
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 546 | 800 | 905 | 908 | 0 | 144
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 47 | 50 | 50
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 135 | 105 | 147 | 147 |  | 75 | ST Under maint.
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 190 | 158 | 220 | 220 |  |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 405 | 365 | 414 | 414 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 32
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 8 | 8
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 52 | 52 | 52
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 15 | 88 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 48 | 111 | 113 | 113
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 70 | 109 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 895 | 1150 | 1450 | 1572 | 491 | 75
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 149 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 10 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 99 | 113 | 100 | 113
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 1 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 250 | 262 | 258 | 263 | 294 | 30
|  | Total |  |  |  |  | 20383 | 19892 | 10467 | 12040 | 14229.6 | 15045 | 2475 | 1807
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10014.0675 | 11519 | 13613.8507 | 14393.9664
| A. |  | 2020-09-14 | (Yesterday) |  |  |  |  | Monday
| 1 | Highest Generation : |  |  | 12040 | MW at | 20:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
| 2 | Minimum Generation : |  |  | 9206 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12040 | MW
| 3 | Day peak Generation : |  |  | 10467 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11519 | MW
| 4 | Evening peak Generation : |  |  | 12040 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 258.0371 | MKWHr | By Solar | 0.15285 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 144.3859 | MKWHr |  | By Oil: | 70.1885 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 16.097 | MKWHr |  | By Hydro: | 1.3302 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2475 | MW | Dhaka | 4034 | 4034 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 1807 | MW | Chittagong | 1120 | 1120 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4282 | MW | Khulna | 1528 | 1528 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1173.53 | MMCFD |  |  | Rajshahi | 1275 | 1275 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 168144344.636 | ii) Oil : | Taka | 571310154.65 | Comilla | 1176 | 1176 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 74215519 | Total | Taka | 813670018.286 | Mymensingh | 876 | 876 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.3245 | MKWHr. | Sylhet | 467 | 467 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -135 | MW (E to W) at | 20:00 | hrs | Barisal | 273 | 273 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -170 | MW at | 19:00 | hrs | Rangpur | 770 | 770 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 33.6° C |  |  | Total | 11519 | 11519 |  | 0
| B. |  | 2020-09-15 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 33.2° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15045 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10600 | MW
| 4 | Reserve(Generation end) |  |  |  | 2545 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 267.8956 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9158 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.248 | MKWHr. | ii) HVDC Flow at Peak Time |  | 927 | MW at | 20:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.6346 | MKWHr. | iii) Maximum HVDC Flow : |  | 932 | MW at | 12:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 94.01 |  | (b) Today: | 94.19 |  | (c) Rule Curve: |  | 100.99
.

## YesterdayGen
2020-09-14
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 150 | 0 | 200 | 83 | 68 | 337 | 316 |  | 0 | 380 | 130 | 100 | 81 | 55 | 279 | 0 | 0 | 0 | 100 | 93 | 64 | 20 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 28 | 33 | 0 | 0 | 83 | 0 | 130 | 0 | 0 | 164 | 0 | 0 | 0 |  | 0 | 0 | 102 | 0 | 85 | 34 | 21 | 37 | 0 | 0 | 80 | 275 | 270 | 175 | 8 | 80 | 22 | 5 | 0 | 51 | 0 | 0 | 43 | 18 | 11 | 33 | 21 | 166 | 147 | 55 | 20 | 0 | 91 | 28 | 50 | 50 | 163 | 263 | 66 | 88 | 0 | 185 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 296 | 0 | 0 | 185 | 0 | 144 | 0 | 100 | 0 | 133 | 0 | 115 | 104 | 0 | 0 | 198 | 0 | 0 | 0 | 113 | 100 | 0 | 17 |  | 927 | 0 | 345 | 0 | 99 | 145 | 0 | 0 | 18 | 0 | 40 | 66 | 39 | 96 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 36 | 24 | 31 | 21 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 16 | 0 | 77 | 100 | 217 | 0 | 330 | 17 | 0 | 113 | 0 | 105 | 0 | 0 | 109 | 570 |  | 7715 | 3938 | 11653 | 4031 | 927 | 2064 | 3168 | 720 | 83 | 494 | 166 | 0 | 0 | 94
2:00 | 0 | 0 | 151 | 0 | 200 | 84 | 68 | 336 | 340 |  | 0 | 380 | 130 | 100 | 81 | 55 | 279 | 0 | 0 | 0 | 100 | 93 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 28 | 33 | 0 | 0 | 83 | 0 | 130 | 0 | 0 | 165 | 0 | 0 | 0 |  | 0 | 0 | 68 | 0 | 32 | 0 | 21 | 40 | 0 | 0 | 80 | 275 | 270 | 175 | 8 | 88 | 22 | 5 | 0 | 51 | 0 | 0 | 43 | 0 | 0 | 33 | 21 | 162 | 160 | 55 | 20 | 0 | 91 | 28 | 50 | 50 | 163 | 260 | 66 | 88 | 0 | 185 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 300 | 0 | 0 | 185 | 0 | 141 | 0 | 100 | 0 | 133 | 0 | 115 | 0 | 0 | 0 | 198 | 0 | 0 | 0 | 113 | 100 | 0 | 17 |  | 927 | 0 | 335 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 40 | 67 | 39 | 80 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 20 | 0 | 77 | 100 | 218 | 0 | 330 | 17 | 0 | 113 | 0 | 105 | 0 | 0 | 109 | 570 |  | 7453 | 3731 | 11184 | 4017 | 927 | 2092 | 2918 | 720 | 83 | 265 | 162 | 0 | 0 | 94
3:00 | 0 | 0 | 147 | 0 | 200 | 84 | 68 | 336 | 340 |  | 0 | 380 | 125 | 100 | 81 | 55 | 273 | 0 | 0 | 0 | 100 | 93 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 22 | 25 | 22 | 28 | 33 | 0 | 0 | 83 | 0 | 130 | 0 | 0 | 164 | 0 | 0 | 0 |  | 0 | 0 | 68 | 0 | 30 | 0 | 21 | 40 | 0 | 0 | 80 | 275 | 270 | 180 | 8 | 81 | 22 | 5 | 0 | 51 | 0 | 0 | 43 | 18 | 11 | 33 | 21 | 154 | 161 | 54 | 22 | 0 | 91 | 28 | 50 | 50 | 163 | 262 | 65 | 88 | 0 | 185 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 300 | 0 | 0 | 184 | 0 | 141 | 0 | 100 | 0 | 50 | 0 | 75 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 108 | 100 | 0 | 17 |  | 927 | 0 | 335 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 65 | 36 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 37 | 0 | 75 | 100 | 217 | 0 | 325 | 17 | 0 | 113 | 0 | 99 | 0 | 0 | 109 | 570 |  | 7308 | 3684 | 10992 | 4051 | 927 | 2082 | 2755 | 720 | 83 | 220 | 154 | 0 | 0 | 94
4:00 | 0 | 0 | 150 | 0 | 200 | 84 | 68 | 336 | 346 |  | 0 | 380 | 145 | 100 | 48 | 55 | 277 | 0 | 0 | 0 | 100 | 93 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 22 | 25 | 22 | 28 | 33 | 0 | 0 | 84 | 0 | 130 | 0 | 0 | 164 | 0 | 0 | 0 |  | 0 | 0 | 68 | 0 | 0 | 0 | 21 | 42 | 0 | 0 | 80 | 275 | 270 | 183 | 8 | 80 | 22 | 5 | 0 | 51 | 0 | 0 | 43 | 18 | 11 | 33 | 21 | 152 | 160 | 54 | 22 | 0 | 90 | 28 | 50 | 50 | 163 | 262 | 64 | 88 | 0 | 185 | 18 | 0 | 10 | 275 | 24 | 8 | 0 | 195 | 0 | 0 | 182 | 0 | 148 | 0 | 100 | 0 | 5 | 0 | 55 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 113 | 100 | 0 | 17 |  | 927 | 0 | 335 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 68 | 37 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 11 | 0 | 0 | 151 | 0 | 0 | 130 | 0 | 88 | 0 | 76 | 40 | 217 | 0 | 330 | 17 | 0 | 113 | 0 | 105 | 0 | 0 | 109 | 570 |  | 7023 | 3692 | 10715 | 4111 | 927 | 2092 | 2424 | 721 | 84 | 204 | 152 | 0 | 0 | 94.01
5:00 | 0 | 0 | 150 | 0 | 200 | 83 | 68 | 339 | 348 |  | 0 | 380 | 145 | 100 | 48 | 20 | 295 | 0 | 0 | 0 | 100 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 22 | 28 | 33 | 0 | 0 | 84 | 0 | 130 | 0 | 0 | 164 | 0 | 0 | 0 |  | 0 | 0 | 68 | 0 | 0 | 0 | 21 | 42 | 0 | 0 | 80 | 275 | 270 | 186 | 8 | 88 | 22 | 5 | 0 | 51 | 0 | 0 | 25 | 18 | 11 | 33 | 21 | 144 | 160 | 55 | 22 | 0 | 91 | 28 | 50 | 50 | 163 | 262 | 64 | 88 | 0 | 185 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 130 | 0 | 0 | 185 | 0 | 138 | 0 | 100 | 0 | 5 | 0 | 35 | 0 | 0 | 0 | 198 | 0 | 0 | 0 | 113 | 100 | 0 | 17 |  | 926 | 0 | 320 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 68 | 34 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 8 | 0 | 0 | 143 | 0 | 0 | 130 | 0 | 120 | 0 | 76 | 40 | 217 | 0 | 360 | 17 | 0 | 35 | 0 | 85 | 0 | 0 | 109 | 550 |  | 6824 | 3606 | 10430 | 4158 | 926 | 2125 | 2112 | 693 | 84 | 188 | 144 | 0 | 0 | 94.01
6:00 | 0 | 0 | 150 | 0 | 200 | 83 | 67 | 337 | 351 |  | 0 | 340 | 130 | 75 | 47 | 15 | 251 | 0 | 0 | 0 | 80 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 22 | 28 | 33 | 0 | 0 | 84 | 0 | 130 | 0 | 0 | 164 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 0 | 0 | 21 | 25 | 0 | 0 | 80 | 275 | 270 | 187 | 8 | 82 | 22 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 15 | 132 | 160 | 54 | 22 | 0 | 91 | 28 | 50 | 50 | 163 | 263 | 64 | 88 | 0 | 185 | 18 | 0 | 10 | 275 | 24 | 8 | 0 | 95 | 0 | 0 | 160 | 0 | 124 | 0 | 50 | 0 | 5 | 0 | 8 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 104 | 100 | 0 | 17 |  | 927 | 0 | 310 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 68 | 29 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 8 | 0 | 0 | 108 | 0 | 0 | 130 | 0 | 120 | 0 | 77 | 0 | 217 | 0 | 320 | 17 | 0 | 0 | 0 | 63 | 0 | 0 | 70 | 500 |  | 6409 | 3300 | 9709 | 4092 | 927 | 2021 | 1674 | 608 | 84 | 171 | 132 | 0 | 0 | 94.01
7:00 | 0 | 0 | 150 | 0 | 200 | 83 | 67 | 337 | 351 |  | 0 | 320 | 150 | 55 | 30 | 15 | 296 | 0 | 0 | 0 | 50 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 22 | 28 | 33 | 0 | 0 | 84 | 0 | 130 | 0 | 0 | 164 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 21 | 35 | 0 | 0 | 80 | 275 | 270 | 187 | 8 | 86 | 22 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 21 | 126 | 160 | 54 | 22 | 0 | 91 | 28 | 50 | 50 | 110 | 260 | 63 | 85 | 0 | 185 | 18 | 0 | 10 | 280 | 16 | 8 | 0 | 45 | 0 | 0 | 130 | 0 | 113 | 2 | 50 | 0 | 6 | 0 | 8 | 0 | 0 | 1 | 161 | 0 | 0 | 0 | 104 | 100 | 0 | 17 |  | 927 | 0 | 305 | 0 | 83 | 120 | 0 | 0 | 0 | 0 | 8 | 69 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 8 | 0 | 0 | 107 | 0 | 0 | 130 | 0 | 120 | 0 | 77 | 0 | 150 | 0 | 360 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 70 | 500 |  | 6187 | 3125 | 9312 | 4053 | 927 | 1999 | 1376 | 607 | 84 | 137 | 126 | 3 | 0 | 94.02
8:00 | 0 | 0 | 150 | 0 | 200 | 83 | 67 | 361 | 300 |  | 0 | 320 | 150 | 55 | 30 | 15 | 309 | 0 | 0 | 0 | 55 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 22 | 28 | 33 | 0 | 0 | 84 | 0 | 130 | 0 | 0 | 164 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 0 | 0 | 80 | 280 | 270 | 173 | 8 | 90 | 22 | 5 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 33 | 21 | 128 | 158 | 54 | 22 | 0 | 91 | 28 | 50 | 50 | 110 | 261 | 63 | 85 | 0 | 185 | 18 | 0 | 10 | 305 | 24 | 0 | 0 | 45 | 0 | 0 | 140 | 0 | 113 | 11 | 76 | 0 | 6 | 0 | 8 | 1 | 0 | 3 | 160 | 0 | 0 | 0 | 104 | 100 | 0 | 17 |  | 927 | 0 | 295 | 0 | 83 | 120 | 0 | 0 | 0 | 0 | 8 | 68 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 108 | 0 | 0 | 142 | 0 | 145 | 0 | 77 | 0 | 0 | 0 | 415 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 70 | 500 |  | 6162 | 3044 | 9206 | 3923 | 927 | 1985 | 1417 | 608 | 84 | 120 | 128 | 14 | 0 | 94.02
9:00 | 0 | 0 | 150 | 0 | 200 | 83 | 66 | 355 | 304 |  | 0 | 320 | 130 | 63 | 30 | 50 | 283 | 0 | 0 | 0 | 90 | 93 | 0 | 10 | 0 | 0 | 0 | 54 | 17 | 35 | 22 | 25 | 22 | 33 | 33 | 0 | 0 | 40 | 0 | 130 | 0 | 0 | 164 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 1 | 2 | 21 | 4 | 0 | 0 | 80 | 275 | 270 | 157 | 8 | 87 | 10 | 5 | 0 | 51 | 0 | 0 | 1 | 0 | 0 | 33 | 20 | 132 | 158 | 54 | 22 | 1 | 91 | 28 | 50 | 50 | 163 | 260 | 61 | 85 | 0 | 185 | 18 | 0 | 9 | 300 | 24 | 0 | 0 | 86 | 0 | 0 | 150 | 0 | 146 | 18 | 76 | 0 | 18 | 0 | 17 | 33 | 0 | 4 | 197 | 0 | 0 | 0 | 104 | 100 | 0 | 17 |  | 927 | 0 | 310 | 0 | 88 | 120 | 0 | 0 | 0 | 0 | 8 | 67 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 123 | 0 | 0 | 144 | 0 | 163 | 0 | 76 | 0 | 0 | 0 | 398 | 0 | 0 | 0 | 0 | 35 | 0 | 1 | 70 | 480 |  | 6484 | 3077 | 9561 | 3912 | 927 | 2012 | 1791 | 603 | 40 | 120 | 132 | 24 | 0 | 94.02
10:00 | 0 | 0 | 147 | 0 | 200 | 62 | 40 | 338 | 303 |  | 0 | 320 | 125 | 97 | 45 | 39 | 279 | 0 | 0 | 0 | 90 | 93 | 8 | 41 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 0 | 0 | 40 | 0 | 130 | 0 | 0 | 216 | 0 | 0 | 0 |  | 0 | 0 | 0 | 20 | 53 | 20 | 18 | 3 | 0 | 0 | 80 | 275 | 270 | 174 | 8 | 81 | 10 | 5 | 0 | 43 | 0 | 0 | 8 | 16 | 0 | 33 | 20 | 136 | 123 | 54 | 22 | 1 | 91 | 28 | 47 | 46 | 163 | 260 | 40 | 85 | 0 | 185 | 18 | 0 | 9 | 280 | 24 | 0 | 0 | 270 | 0 | 0 | 170 | 0 | 149 | 16 | 76 | 0 | 108 | 0 | 24 | 70 | 0 | 5 | 197 | 0 | 0 | 0 | 103 | 100 | 0 | 17 |  | 927 | 0 | 305 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 8 | 67 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 147 | 0 | 0 | 145 | 0 | 152 | 0 | 77 | 0 | 0 | 0 | 359 | 0 | 0 | 5 | 0 | 74 | 0 | 0 | 70 | 410 |  | 6966 | 3034 | 10000 | 3893 | 927 | 1892 | 2405 | 557 | 40 | 128 | 136 | 22 | 0 | 94.03
11:00 | 0 | 0 | 150 | 0 | 200 | 62 | 40 | 340 | 304 |  | 0 | 320 | 130 | 100 | 70 | 40 | 300 | 0 | 0 | 0 | 100 | 93 | 16 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 21 | 33 | 33 | 13 | 0 | 39 | 0 | 130 | 0 | 0 | 206 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 75 | 49 | 18 | 3 | 0 | 0 | 80 | 275 | 270 | 192 | 8 | 86 | 10 | 5 | 0 | 43 | 0 | 0 | 8 | 16 | 11 | 33 | 20 | 146 | 123 | 54 | 22 | 1 | 91 | 28 | 50 | 46 | 130 | 261 | 40 | 85 | 0 | 185 | 18 | 0 | 9 | 280 | 24 | 8 | 0 | 290 | 0 | 0 | 170 | 0 | 133 | 20 | 90 | 0 | 133 | 0 | 24 | 92 | 0 | 5 | 179 | 0 | 0 | 0 | 103 | 100 | 0 | 17 |  | 927 | 0 | 305 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 8 | 67 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 120 | 0 | 151 | 0 | 77 | 0 | 0 | 0 | 375 | 0 | 0 | 35 | 0 | 97 | 0 | 1 | 70 | 400 |  | 7170 | 3071 | 10241 | 3925 | 927 | 1879 | 2612 | 550 | 39 | 136 | 146 | 27 | 0 | 94.03
12:00 | 0 | 0 | 150 | 0 | 200 | 62 | 40 | 359 | 304 |  | 0 | 320 | 138 | 100 | 80 | 40 | 303 | 0 | 0 | 0 | 100 | 93 | 16 | 55 | 0 | 0 | 0 | 54 | 0 | 35 | 19 | 25 | 21 | 33 | 33 | 16 | 0 | 37 | 0 | 130 | 0 | 0 | 206 | 0 | 0 | 0 |  | 0 | 0 | 0 | 50 | 75 | 50 | 18 | 3 | 0 | 0 | 80 | 290 | 270 | 186 | 8 | 90 | 10 | 5 | 0 | 43 | 0 | 0 | 20 | 18 | 11 | 33 | 20 | 148 | 123 | 54 | 22 | 1 | 91 | 28 | 50 | 46 | 163 | 263 | 59 | 85 | 0 | 200 | 18 | 0 | 10 | 305 | 24 | 8 | 0 | 292 | 0 | 0 | 170 | 0 | 133 | 10 | 90 | 0 | 132 | 0 | 24 | 105 | 0 | 4 | 179 | 0 | 0 | 0 | 104 | 100 | 0 | 17 |  | 932 | 0 | 310 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 8 | 67 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 135 | 0 | 190 | 0 | 76 | 0 | 0 | 0 | 405 | 0 | 0 | 48 | 0 | 99 | 0 | 1 | 70 | 360 |  | 7307 | 3160 | 10467 | 4054 | 932 | 1973 | 2646 | 510 | 37 | 151 | 148 | 16 | 0 | 94.03
13:00 | 0 | 0 | 150 | 0 | 200 | 62 | 40 | 345 | 305 |  | 0 | 320 | 125 | 100 | 80 | 40 | 251 | 0 | 0 | 0 | 82 | 93 | 16 | 70 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 25 | 0 | 33 | 33 | 8 | 0 | 37 | 0 | 130 | 0 | 15 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 100 | 72 | 50 | 18 | 8 | 0 | 0 | 80 | 290 | 270 | 178 | 8 | 81 | 10 | 5 | 0 | 43 | 0 | 0 | 40 | 18 | 11 | 33 | 15 | 142 | 116 | 54 | 22 | 1 | 91 | 28 | 50 | 48 | 110 | 262 | 60 | 85 | 0 | 231 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 285 | 0 | 0 | 183 | 0 | 133 | 5 | 100 | 0 | 128 | 0 | 8 | 70 | 0 | 4 | 179 | 0 | 0 | 52 | 105 | 100 | 0 | 17 |  | 927 | 0 | 300 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 8 | 67 | 29 | 16 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 142 | 0 | 180 | 0 | 75 | 0 | 0 | 0 | 310 | 0 | 0 | 70 | 0 | 109 | 0 | 3 | 70 | 440 |  | 7227 | 3168 | 10395 | 3935 | 927 | 1809 | 2785 | 589 | 37 | 158 | 142 | 13 | 0 | 94.04
14:00 | 0 | 0 | 157 | 0 | 200 | 63 | 40 | 339 | 304 |  | 0 | 320 | 122 | 100 | 80 | 40 | 273 | 0 | 0 | 0 | 98 | 93 | 0 | 40 | 0 | 0 | 0 | 35 | 35 | 30 | 0 | 25 | 0 | 33 | 33 | 0 | 0 | 37 | 0 | 130 | 0 | 8 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 100 | 71 | 50 | 18 | 4 | 0 | 0 | 80 | 290 | 270 | 167 | 8 | 84 | 10 | 5 | 0 | 43 | 0 | 0 | 43 | 18 | 11 | 33 | 20 | 148 | 103 | 40 | 22 | 2 | 91 | 28 | 50 | 48 | 110 | 261 | 60 | 50 | 0 | 232 | 18 | 0 | 10 | 270 | 24 | 8 | 0 | 283 | 0 | 0 | 140 | 0 | 133 | 3 | 100 | 0 | 128 | 0 | 8 | 17 | 0 | 2 | 179 | 0 | 0 | 0 | 75 | 100 | 0 | 17 |  | 927 | 0 | 300 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 0 | 67 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 145 | 0 | 158 | 0 | 78 | 0 | 0 | 0 | 316 | 0 | 0 | 35 | 0 | 80 | 0 | 4 | 70 | 400 |  | 6924 | 3048 | 9972 | 3923 | 927 | 1768 | 2465 | 549 | 37 | 144 | 148 | 11 | 0 | 94.04
15:00 | 0 | 0 | 150 | 0 | 200 | 63 | 40 | 358 | 304 |  | 0 | 400 | 132 | 100 | 80 | 43 | 303 | 0 | 0 | 0 | 100 | 93 | 0 | 20 | 0 | 0 | 0 | 17 | 35 | 17 | 0 | 25 | 17 | 25 | 33 | 0 | 0 | 37 | 0 | 130 | 0 | 8 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 80 | 72 | 50 | 18 | 4 | 0 | 0 | 80 | 290 | 270 | 167 | 8 | 96 | 10 | 5 | 0 | 43 | 0 | 0 | 43 | 18 | 11 | 33 | 0 | 152 | 103 | 40 | 22 | 0 | 89 | 20 | 47 | 48 | 110 | 261 | 55 | 84 | 0 | 232 | 18 | 0 | 10 | 300 | 16 | 0 | 0 | 295 | 0 | 0 | 140 | 0 | 129 | 11 | 100 | 0 | 130 | 0 | 8 | 17 | 0 | 0 | 179 | 0 | 0 | 0 | 75 | 100 | 0 | 17 |  | 927 | 0 | 300 | 0 | 83 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 29 | 16 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 135 | 0 | 0 | 144 | 0 | 171 | 0 | 77 | 0 | 0 | 0 | 402 | 0 | 0 | 35 | 0 | 75 | 0 | 4 | 70 | 400 |  | 7040 | 3109 | 10149 | 3945 | 927 | 1995 | 2399 | 535 | 37 | 144 | 152 | 15 | 0 | 94.05
16:00 | 0 | 0 | 100 | 22 | 200 | 63 | 40 | 339 | 305 |  | 0 | 400 | 123 | 100 | 80 | 55 | 276 | 0 | 0 | 0 | 100 | 95 | 0 | 10 | 0 | 0 | 0 | 17 | 35 | 17 | 0 | 25 | 27 | 25 | 17 | 0 | 0 | 38 | 0 | 130 | 0 | 8 | 203 | 0 | 50 | 0 |  | 0 | 0 | 0 | 80 | 72 | 50 | 21 | 4 | 0 | 0 | 80 | 290 | 270 | 173 | 8 | 86 | 10 | 5 | 0 | 43 | 0 | 0 | 43 | 18 | 11 | 33 | 21 | 132 | 108 | 8 | 22 | 0 | 90 | 20 | 47 | 48 | 130 | 262 | 61 | 84 | 0 | 232 | 18 | 0 | 10 | 290 | 16 | 0 | 0 | 200 | 0 | 0 | 140 | 0 | 114 | 5 | 100 | 0 | 70 | 0 | 8 | 16 | 0 | 0 | 179 | 0 | 0 | 0 | 75 | 100 | 0 | 17 |  | 928 | 0 | 300 | 0 | 84 | 120 | 0 | 0 | 0 | 0 | 0 | 67 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 120 | 0 | 0 | 147 | 0 | 159 | 0 | 77 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 75 | 0 | 2 | 90 | 400 |  | 6820 | 3026 | 9846 | 3937 | 928 | 1963 | 2177 | 520 | 38 | 144 | 132 | 7 | 0 | 94.05
17:00 | 0 | 0 | 100 | 60 | 200 | 63 | 40 | 339 | 304 |  | 0 | 400 | 123 | 75 | 80 | 30 | 263 | 0 | 0 | 0 | 65 | 98 | 0 | 10 | 0 | 0 | 0 | 17 | 35 | 17 | 0 | 25 | 23 | 33 | 17 | 0 | 0 | 39 | 0 | 130 | 0 | 8 | 203 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 81 | 28 | 21 | 10 | 0 | 0 | 80 | 290 | 270 | 184 | 8 | 86 | 10 | 5 | 0 | 43 | 0 | 0 | 16 | 18 | 11 | 33 | 21 | 140 | 108 | 8 | 20 | 0 | 91 | 20 | 47 | 49 | 130 | 284 | 62 | 87 | 0 | 185 | 18 | 0 | 10 | 280 | 16 | 0 | 0 | 200 | 0 | 0 | 100 | 0 | 122 | 1 | 100 | 0 | 70 | 0 | 8 | 16 | 0 | 0 | 179 | 0 | 0 | 0 | 75 | 100 | 0 | 24 |  | 927 | 0 | 300 | 0 | 49 | 120 | 0 | 0 | 0 | 5 | 0 | 67 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 127 | 0 | 0 | 148 | 0 | 157 | 0 | 78 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 0 | 65 | 0 | 1 | 50 | 400 |  | 6672 | 2956 | 9628 | 4001 | 927 | 1960 | 1875 | 527 | 39 | 157 | 140 | 2 | 0 | 94.06
18:00 | 0 | 0 | 100 | 70 | 200 | 63 | 40 | 342 | 305 |  | 0 | 340 | 143 | 52 | 80 | 30 | 303 | 0 | 0 | 0 | 50 | 100 | 20 | 10 | 0 | 0 | 0 | 17 | 35 | 30 | 0 | 25 | 23 | 33 | 33 | 2 | 0 | 40 | 0 | 130 | 0 | 8 | 216 | 0 | 100 | 0 |  | 0 | 0 | 25 | 10 | 85 | 18 | 21 | 13 | 0 | 0 | 80 | 290 | 270 | 166 | 8 | 96 | 10 | 5 | 0 | 43 | 0 | 12 | 16 | 18 | 11 | 33 | 21 | 148 | 108 | 24 | 20 | 0 | 91 | 22 | 25 | 49 | 110 | 308 | 51 | 30 | 0 | 185 | 18 | 0 | 10 | 280 | 16 | 0 | 0 | 200 | 0 | 0 | 108 | 0 | 131 | 0 | 100 | 2 | 75 | 0 | 8 | 16 | 0 | 0 | 179 | 0 | 0 | 17 | 75 | 100 | 0 | 31 |  | 927 | 0 | 310 | 0 | 49 | 120 | 0 | 0 | 7 | 10 | 8 | 67 | 30 | 25 | 0 | 0 | 0 | 0 | 5 | 75 | 0 | 0 | 22 | 2 | 5 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 160 | 0 | 76 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 50 | 400 |  | 6728 | 3064 | 9792 | 4085 | 927 | 1799 | 1942 | 550 | 40 | 301 | 148 | 0 | 0 | 94.07
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 100 | 100 | 200 | 63 | 40 | 352 | 304 |  | 0 | 380 | 120 | 78 | 85 | 50 | 267 | 0 | 0 | 0 | 90 | 100 | 150 | 83 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 23 | 33 | 33 | 25 | 0 | 40 | 0 | 130 | 0 | 8 | 189 | 0 | 120 | 0 |  | 0 | 0 | 102 | 60 | 85 | 43 | 21 | 24 | 0 | 0 | 80 | 290 | 270 | 165 | 8 | 85 | 10 | 5 | 0 | 35 | 0 | 50 | 32 | 18 | 11 | 33 | 21 | 166 | 108 | 55 | 20 | 0 | 91 | 22 | 51 | 50 | 130 | 305 | 62 | 88 | 0 | 185 | 18 | 0 | 10 | 290 | 24 | 0 | 0 | 268 | 0 | 0 | 194 | 0 | 135 | 0 | 100 | 35 | 135 | 0 | 54 | 68 | 0 | 0 | 196 | 0 | 16 | 68 | 111 | 100 | 0 | 17 |  | 926 | 0 | 310 | 0 | 115 | 170 | 0 | 0 | 28 | 0 | 40 | 63 | 38 | 96 | 0 | 0 | 0 | 50 | 34 | 97 | 0 | 0 | 43 | 26 | 32 | 22 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 104 | 0 | 167 | 0 | 77 | 55 | 0 | 0 | 352 | 35 | 0 | 70 | 0 | 102 | 0 | 0 | 109 | 470 |  | 7972 | 3791 | 11763 | 4066 | 926 | 1967 | 3223 | 619 | 40 | 756 | 166 | 0 | 0 | 94.08
19:30 | 0 | 0 | 100 | 115 | 200 | 12 | 40 | 339 | 304 |  | 0 | 380 | 125 | 100 | 97 | 55 | 282 | 0 | 0 | 0 | 100 | 102 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 23 | 33 | 33 | 8 | 0 | 40 | 0 | 130 | 0 | 8 | 190 | 0 | 120 | 0 |  | 0 | 0 | 102 | 30 | 85 | 50 | 21 | 28 | 0 | 0 | 80 | 290 | 270 | 165 | 8 | 85 | 10 | 5 | 0 | 35 | 0 | 0 | 43 | 18 | 11 | 33 | 21 | 172 | 108 | 55 | 20 | 0 | 91 | 22 | 51 | 50 | 130 | 306 | 62 | 88 | 0 | 185 | 18 | 0 | 10 | 290 | 24 | 0 | 0 | 300 | 0 | 0 | 184 | 0 | 131 | 0 | 100 | 50 | 139 | 0 | 65 | 70 | 0 | 0 | 197 | 0 | 52 | 68 | 113 | 100 | 0 | 17 |  | 928 | 0 | 310 | 0 | 115 | 170 | 0 | 0 | 27 | 0 | 40 | 63 | 38 | 96 | 0 | 0 | 0 | 50 | 12 | 97 | 0 | 0 | 43 | 52 | 32 | 22 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 106 | 0 | 157 | 0 | 77 | 100 | 0 | 0 | 371 | 53 | 0 | 110 | 0 | 112 | 0 | 0 | 109 | 520 |  | 8055 | 3970 | 12025 | 4099 | 928 | 1939 | 3495 | 669 | 40 | 683 | 172 | 0 | 0 | 0
20:00 | 0 | 0 | 100 | 115 | 200 | 12 | 40 | 339 | 305 |  | 0 | 380 | 125 | 100 | 97 | 55 | 278 | 0 | 0 | 0 | 100 | 102 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 23 | 33 | 33 | 8 | 0 | 40 | 0 | 130 | 0 | 8 | 189 | 0 | 120 | 0 |  | 0 | 0 | 102 | 30 | 85 | 50 | 21 | 33 | 0 | 0 | 80 | 290 | 270 | 162 | 8 | 85 | 10 | 5 | 0 | 35 | 0 | 0 | 43 | 18 | 11 | 33 | 21 | 176 | 109 | 55 | 20 | 0 | 88 | 22 | 52 | 50 | 130 | 310 | 62 | 88 | 0 | 185 | 18 | 0 | 10 | 280 | 24 | 0 | 0 | 300 | 0 | 0 | 184 | 0 | 131 | 0 | 100 | 51 | 138 | 0 | 65 | 104 | 0 | 0 | 197 | 0 | 52 | 68 | 113 | 100 | 0 | 17 |  | 927 | 0 | 320 | 0 | 115 | 170 | 0 | 0 | 27 | 0 | 40 | 68 | 39 | 96 | 0 | 0 | 0 | 50 | 0 | 88 | 0 | 0 | 47 | 52 | 32 | 22 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 105 | 0 | 158 | 0 | 77 | 92 | 0 | 0 | 365 | 53 | 0 | 111 | 0 | 113 | 0 | 0 | 109 | 520 |  | 8084 | 3956 | 12040 | 4108 | 927 | 1931 | 3523 | 669 | 40 | 666 | 176 | 0 | 0 | 94.09
21:00 | 0 | 0 | 100 | 115 | 200 | 12 | 40 | 339 | 300 |  | 0 | 400 | 144 | 100 | 97 | 55 | 287 | 0 | 0 | 0 | 100 | 102 | 150 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 23 | 33 | 33 | 0 | 0 | 40 | 0 | 130 | 0 | 8 | 191 | 0 | 120 | 0 |  | 0 | 0 | 102 | 30 | 85 | 50 | 21 | 35 | 0 | 0 | 80 | 290 | 270 | 149 | 8 | 96 | 10 | 5 | 0 | 35 | 0 | 0 | 43 | 18 | 11 | 33 | 21 | 172 | 109 | 55 | 20 | 0 | 91 | 30 | 52 | 50 | 130 | 257 | 64 | 88 | 0 | 185 | 18 | 0 | 10 | 290 | 24 | 0 | 0 | 300 | 0 | 0 | 184 | 0 | 134 | 0 | 100 | 17 | 138 | 0 | 65 | 50 | 0 | 0 | 197 | 0 | 52 | 68 | 113 | 100 | 0 | 17 |  | 927 | 0 | 320 | 0 | 115 | 170 | 0 | 0 | 27 | 0 | 40 | 68 | 39 | 64 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 43 | 52 | 32 | 22 | 8 | 11 | 0 | 0 | 149 | 0 | 0 | 132 | 0 | 177 | 0 | 78 | 100 | 0 | 0 | 395 | 53 | 0 | 113 | 0 | 113 | 0 | 0 | 109 | 520 |  | 7952 | 3974 | 11926 | 4123 | 927 | 1997 | 3377 | 669 | 40 | 621 | 172 | 0 | 0 | 94.1
22:00 | 0 | 0 | 0 | 115 | 200 | 41 | 40 | 350 | 293 |  | 0 | 400 | 130 | 97 | 97 | 55 | 270 | 0 | 0 | 0 | 100 | 102 | 150 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 23 | 28 | 33 | 0 | 0 | 40 | 0 | 130 | 0 | 8 | 191 | 0 | 120 | 0 |  | 0 | 0 | 102 | 30 | 85 | 50 | 21 | 35 | 0 | 0 | 80 | 290 | 270 | 159 | 8 | 82 | 10 | 5 | 0 | 35 | 0 | 0 | 43 | 18 | 11 | 33 | 21 | 174 | 108 | 55 | 20 | 0 | 91 | 30 | 52 | 50 | 163 | 258 | 64 | 88 | 0 | 185 | 18 | 0 | 10 | 290 | 24 | 2 | 0 | 300 | 0 | 0 | 184 | 0 | 136 | 0 | 100 | 17 | 138 | 0 | 97 | 50 | 0 | 0 | 197 | 0 | 52 | 68 | 113 | 100 | 0 | 17 |  | 927 | 0 | 325 | 0 | 115 | 170 | 0 | 0 | 27 | 0 | 40 | 68 | 40 | 64 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 43 | 52 | 32 | 22 | 8 | 11 | 0 | 0 | 149 | 0 | 0 | 147 | 0 | 192 | 0 | 78 | 100 | 0 | 0 | 385 | 53 | 0 | 113 | 0 | 112 | 0 | 0 | 109 | 530 |  | 7913 | 4009 | 11922 | 4045 | 927 | 2043 | 3393 | 679 | 40 | 621 | 174 | 0 | 0 | 94.11
23:00 | 0 | 0 | 0 | 115 | 200 | 78 | 40 | 354 | 293 |  | 0 | 420 | 150 | 100 | 97 | 55 | 304 | 0 | 0 | 0 | 100 | 102 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 28 | 33 | 0 | 0 | 40 | 0 | 130 | 0 | 0 | 190 | 0 | 120 | 0 |  | 0 | 0 | 102 | 0 | 85 | 50 | 21 | 41 | 0 | 0 | 80 | 290 | 270 | 169 | 8 | 96 | 10 | 5 | 0 | 35 | 0 | 0 | 43 | 18 | 11 | 33 | 21 | 170 | 107 | 55 | 20 | 0 | 90 | 30 | 52 | 50 | 130 | 263 | 64 | 88 | 0 | 185 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 300 | 0 | 0 | 185 | 0 | 149 | 0 | 100 | 0 | 135 | 0 | 115 | 50 | 0 | 0 | 197 | 0 | 52 | 34 | 113 | 100 | 0 | 17 |  | 927 | 0 | 310 | 0 | 115 | 170 | 0 | 0 | 27 | 0 | 32 | 67 | 39 | 64 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 43 | 0 | 32 | 22 | 8 | 11 | 0 | 0 | 149 | 0 | 0 | 147 | 0 | 177 | 0 | 77 | 100 | 0 | 0 | 405 | 35 | 0 | 113 | 0 | 113 | 0 | 0 | 109 | 550 |  | 7912 | 3939 | 11851 | 4084 | 927 | 2081 | 3229 | 699 | 40 | 621 | 170 | 0 | 0 | 94.13
24:00 | 0 | 0 | 0 | 115 | 200 | 95 | 40 | 346 | 300 |  | 0 | 420 | 135 | 100 | 97 | 55 | 277 | 0 | 0 | 0 | 100 | 102 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 23 | 28 | 33 | 0 | 0 | 40 | 0 | 130 | 0 | 0 | 190 | 0 | 121 | 0 |  | 0 | 0 | 56 | 0 | 85 | 50 | 21 | 41 | 0 | 0 | 80 | 290 | 270 | 172 | 8 | 81 | 10 | 5 | 0 | 51 | 0 | 0 | 43 | 18 | 11 | 33 | 21 | 164 | 146 | 55 | 20 | 0 | 91 | 30 | 52 | 50 | 130 | 261 | 64 | 88 | 0 | 185 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 300 | 0 | 0 | 185 | 0 | 149 | 0 | 100 | 0 | 133 | 0 | 115 | 50 | 0 | 0 | 198 | 0 | 52 | 0 | 113 | 100 | 0 | 17 |  | 927 | 0 | 300 | 0 | 115 | 170 | 0 | 0 | 27 | 0 | 32 | 68 | 39 | 64 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 11 | 0 | 0 | 149 | 0 | 0 | 147 | 0 | 181 | 0 | 78 | 100 | 0 | 0 | 395 | 13 | 0 | 113 | 0 | 112 | 0 | 0 | 109 | 570 |  | 7855 | 3847 | 11702 | 4074 | 927 | 2122 | 3156 | 719 | 40 | 500 | 164 | 0 | 0 | 94.13
KWH | 0 | 0 | 2913000 | 740250 | 4730227 | 1556681 | 1238720 | 8357256 | 7417000 |  | 0 | 7952800 | 3205615 | 2221440 | 1794168 | 1052187 | 6928021 | 0 | 0 | 0 | 2208000 | 2296800 | 1135680 | 711871 | 0 | 0 | 0 | 932400 | 878985 | 826639 | 301320 | 600000 | 475560 | 761200 | 784600 | 86748 | 0 | 1330211 | 0 | 3100000 | 0 | 105960 | 4377444 | 0 | 857376 | 0 |  | 0 | 0 | 1084747 | 600960 | 1355520 | 714720 | 476016 | 575040 | 0 | 0 | 1923456 | 7132000 | 6574000 | 4215000 | 200727 | 2055110 | 380644 | 138240 | 0 | 1032504 | 0 | 66672 | 728376 | 360360 | 210060 | 819300 | 489890 | 3634560 | 3028200 | 1144320 | 439884 | 8100 | 2147000 | 645480 | 1171200 | 1174392 | 3471954 | 5990000 | 1436640 | 1992000 | 0 | 4661260 | 423000 | 0 | 242460 | 7117000 | 527784 | 109000 | 0 | 5798506 | 0 | 0 | 4027200 | 0 | 3251520 | 99495 | 2243520 | 203040 | 2271563 | 0 | 1203600 | 1088616 | 0 | 28920 | 4611709 | 0 | 289380 | 428640 | 2468760 | 2401920 | 0 | 452160 |  | 22248000 | 0 | 7777728 | 0 | 2344320 | 3312960 | 0 | 0 | 171360 | 14336 | 522750 | 1596000 | 736617 | 1075584 | 0 | 0 | 0 | 93184 | 41832 | 922904 | 0 | 0 | 295910 | 223680 | 213491 | 494880 | 83124 | 241308 | 0 | 0 | 3446300 | 0 | 0 | 3366000 | 0 | 3627491 | 0 | 1855456 | 1000320 | 1555627 | 0 | 8800636 | 355200 | 0 | 1470048 | 0 | 2099520 | 0 | 16340 | 2139168 | 12650700 |  | 173244284 | 84792774 | 258037058 | 97134492 | 22248000 | 47251431 | 62835433 | 16097000 | 1330211 | 7353076 | 3634560 | 152855 | 0
Fuel Cost | 0 | 0 | 4252980 | 1088167.5 | 5250551.97 | 2054818.92 | 2105824 | 8440828.56 | 7639510 |  | 0 | 8668552 | 3558232.65 | 16860729.6 | 12361817.52 | 8901502.02 | 7205141.84 | 0 | 0 | 0 | 16626240 | 20946816 | 11175091.2 | 6563450.62 | 0 | 0 | 0 | 6806520 | 6794554.05 | 8150660.54 | 225990 | 450000 | 0 | 0 | 0 | 838853.16 | 0 | 359156.97 | 0 | 5611000 | 0 | 984368.4 | 4771413.96 | 0 | 1457539.2 | 0 |  | 0 | 0 | 10522045.9 | 5739168 | 11793024 | 5660582.4 | 599780.16 | 1707868.8 | 0 | 0 | 2827480.32 | 5277680 | 6574000 | 3877800 | 258937.83 | 2363376.5 | 430127.72 | 193536 | 0 | 1765581.84 | 0 | 673387.2 | 6955990.8 | 457657.2 | 157545 | 1433775 | 367417.5 | 27259200 | 3209892 | 10390425.6 | 558652.68 | 129114 | 3521080 | 1032768 | 2084736 | 1832051.52 | 3958027.56 | 6229600 | 2830180.8 | 3804720 | 0 | 8063979.8 | 926370 | 0 | 494618.4 | 7188170 | 395838 | 82840 | 0 | 43836705.36 | 0 | 0 | 20941440 | 0 | 31994956.8 | 1163096.55 | 18284688 | 2202984 | 16014519.15 | 0 | 10976832 | 10287421.2 | 0 | 0 | 34864520.04 | 0 | 2543650.2 | 4277827.2 | 21157273.2 | 15996787.2 | 0 | 0 |  | 128148480 | 0 | 8166614.4 | 0 | 18426355.2 | 45917625.6 | 0 | 0 | 1797566.4 | 150241.28 | 5447055 | 1803480 | 1141756.35 | 10497699.84 | 0 | 0 | 0 | 916930.56 | 425013.12 | 8167700.4 | 0 | 0 | 2867367.9 | 2167459.2 | 2070862.7 | 950169.6 | 128842.2 | 182670.156 | 0 | 0 | 18678946 | 0 | 0 | 3938220 | 0 | 4788288.12 | 0 | 2783184 | 17015443.2 | 1820083.59 | 0 | 8712629.64 | 3708288 | 0 | 13950755.52 | 0 | 16292275.2 | 0 | 180557 | 15808451.52 | 55536573 |  | 568322038.11 | 402587584.696 | 970909622.806 | 110670809.976 | 128148480 | 57473534.66 | 486626322.39 | 74215519 | 359156.97 | 84683832.26 | 27259200 | 1472767.55 | 0
Yesterday Day Peak | 0 | 0 | 150 | 0 | 200 | 62 | 40 | 359 | 304 |  | 0 | 320 | 138 | 100 | 80 | 40 | 303 | 0 | 0 | 0 | 100 | 93 | 16 | 55 | 0 | 0 | 0 | 54 | 0 | 35 | 19 | 25 | 21 | 33 | 33 | 16 | 0 | 37 | 0 | 130 | 0 | 0 | 206 | 0 | 0 | 0 |  | 0 | 0 | 0 | 50 | 75 | 50 | 18 | 3 | 0 | 0 | 80 | 290 | 270 | 186 | 8 | 90 | 10 | 5 | 0 | 43 | 0 | 0 | 20 | 18 | 11 | 33 | 20 | 148 | 123 | 54 | 22 | 1 | 91 | 28 | 50 | 46 | 163 | 263 | 59 | 85 | 0 | 200 | 18 | 0 | 10 | 305 | 24 | 8 | 0 | 292 | 0 | 0 | 170 | 0 | 133 | 10 | 90 | 0 | 132 | 0 | 24 | 105 | 0 | 4 | 179 | 0 | 0 | 0 | 104 | 100 | 0 | 17 |  | 932 | 0 | 310 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 8 | 67 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 135 | 0 | 190 | 0 | 76 | 0 | 0 | 0 | 405 | 0 | 0 | 48 | 0 | 99 | 0 | 1 | 70 | 360 |  | 10467 | DayPeak
Yesterday Evening Peak | 0 | 0 | 100 | 115 | 200 | 12 | 40 | 339 | 305 | 0 | 0 | 380 | 125 | 100 | 97 | 55 | 278 | 0 | 0 | 0 | 100 | 102 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 23 | 33 | 33 | 8 | 0 | 40 | 0 | 130 | 0 | 8 | 189 | 0 | 120 | 0 | 0 | 0 | 0 | 102 | 30 | 85 | 50 | 21 | 33 | 0 | 0 | 80 | 290 | 270 | 162 | 8 | 85 | 10 | 5 | 0 | 35 | 0 | 0 | 43 | 18 | 11 | 33 | 21 | 176 | 109 | 55 | 20 | 0 | 88 | 22 | 52 | 50 | 130 | 310 | 62 | 88 | 0 | 185 | 18 | 0 | 10 | 280 | 24 | 0 | 0 | 300 | 0 | 0 | 184 | 0 | 131 | 0 | 100 | 51 | 138 | 0 | 65 | 104 | 0 | 0 | 197 | 0 | 52 | 68 | 113 | 100 | 0 | 17 |  | 927 | 0 | 320 | 0 | 115 | 170 | 0 | 0 | 27 | 0 | 40 | 68 | 39 | 96 | 0 | 0 | 0 | 50 | 0 | 88 | 0 | 0 | 47 | 52 | 32 | 22 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 105 | 0 | 158 | 0 | 77 | 92 | 0 | 0 | 365 | 53 | 0 | 111 | 0 | 113 | 0 | 0 | 109 | 520 |  | 12040 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 115 | 200 | 100 | 68 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 335 | 0 | 0 | 0 | 100 | 102 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 40 | 0 | 130 | 0 | 25 | 0 | 0 | 120 | 0 | 0 | 0 |  | 100 | 100 | 85 | 50 | 21 | 30 | 0 | 0 | 80 | 360 | 360 | 214 | 8 | 100 | 10 | 5 | 0 | 51 | 0 | 50 | 43 | 21 | 11 | 33 | 21 | 173 | 140 | 55 | 22 | 0 | 90 | 30 | 51 | 44 | 163 | 300 | 64 | 86 | 0 | 225 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 80 |  | 945 | 16 | 410 | 0 | 115 | 225 | 0 | 0 | 30 | 60 | 40 | 68 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 0 | 0 | 50 | 52 | 32 | 22 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 147 | 0 | 220 | 0 | 77 | 100 | 0 | 0 | 414 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620
Forecast for Day | 0 | 0 | 0 | 115 | 200 | 100 | 67 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 335 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 40 | 0 | 130 | 0 | 25 | 0 | 0 | 120 | 0 | 0 | 0 |  | 100 | 100 | 85 | 50 | 21 | 5 | 0 | 0 | 80 | 360 | 360 | 214 | 8 | 100 | 10 | 5 | 0 | 51 | 0 | 0 | 43 | 21 | 11 | 33 | 21 | 157 | 140 | 55 | 20 | 1.6 | 90 | 30 | 51 | 44 | 163 | 300 | 64 | 86 | 0 | 225 | 18 | 0 | 10 | 341 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 70 |  | 945 | 0 | 410 | 0 | 115 | 225 | 0 | 0 | 0 | 0 | 40 | 65 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 50 | 52 | 0 | 22 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 147 | 0 | 220 |  | 77 | 50 | 0 | 0 | 414 | 105 | 100 | 113 | 100 | 100 | 0 | 8 | 113 | 620
Generation at 08:00(Today) | 0 | 0 | 0 | 115 | 200 | 42 | 40 | 339 | 270 | 0 | 0 | 320 | 136 |  | 97 | 15 | 277 | 0 | 0 | 0 | 100 | 59 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 22 | 25 | 23 | 28 | 33 | 0 | 0 | 40 | 0 | 130 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 6 | 0 | 0 | 80 | 275 | 270 | 143 | 8 | 88 | 32 | 0 | 0 | 15 | 0 | 0 | 0 | 17 | 11 | 33 | 21 | 120 | 145 | 2 | 17 | 0 | 91 | 30 | 50 | 47 | 110 | 262 | 32 | 88 | 0 | 185 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 250 | 0 | 0 | 183 | 0 | 134 | 11 | 100 | 0 | 10 | 0 | 0 | 16 | 0 | 3 | 270 | 0 | 0 | 0 | 113 | 100 | 0 | 17 | 0 | 932 | 0 | 260 | 0 | 83 | 120 | 0 | 0 | 0 | 0 | 0 | 66 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 8 | 0 | 0 | 149 | 0 | 0 | 100 | 0 | 145 | 0 | 77 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 109 | 400 | 0
199
| Minimum Generation |  | 9206 | 8:00
| Highest Generation |  | 12040 | 20:00
| Day Peak Generation |  | 10467 | 12:00
| Evening Peak Generation |  | 12040 | 20:00
| HVDC Max Flow |  | 932 | 12:00
| HVDC EvPeak Flow |  | 927 | 20:00
| Load factor L.F |  | 89.3%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-09-15
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-09-14 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10467 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 9158 | MW
Evening Peak Generation : |  | 12040 | MW Hour : | 20:00 | Available Max Generation : |  | 15045 | MW
E.P. Demand (at gen end) : |  | 12040 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 12500 | MW
Maximum Generation : |  | 12040 | MW Hour : | 20:00 | Reserve(Generation end) |  | 2545 | MW
Total Gen. (MKWH) : |  | 258.0371 | System Load Factor : | 89.3% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -170 | MW at | 19:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-09-15
Actual : | 94.19 | Ft.(MSL) , | Rule curve : | 100.99 | Ft.( MSL )
Gas Consumed : | Total = | 1173.53 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 168144344.636
: |  | Coal : | 74215519 | Oil : | 571310154.65 | Total : | 813670018.286
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4445.896 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1515.4609 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1358.446 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1227.6989 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1109.3278 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 895.1974 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 495.9046 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 230.3663 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 690.4429 |  |  | 0 | 0%
Total | 0 |  | 11968.7408 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 9) Bhola 225 MW GT-2 & ST
|  |  |  | 2) Bibiyana #3 | 10) Sirajganj unit-1 ST
|  |  |  | 3) Ghorasal Unit-1,2,3,4 | 11) Sikalbaha-225 MW.
4) Ashuganj unit-3,4
5) Kaptai-1,2,5
6) Raozan #1,2
7) Sirajganj #3
8) Baghabari-71 MW & 100 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Mymensing 132/33 kV T-3 transformer with 33 kV Bus section-2 were shut down from 08:20 to 09:53 |  |  |  |  | About 10 MW power interruption occurring under Mymensing S/S area
for red hot maintenance. |  |  |  |  | from 08:20 to 09:53.
b) Rangpur 132/33 kV T-3 transformer along with 33 kV Bus section-2,3 were shut down from 09:50 to |  |  |  |  | About 60 MW power interruption occurring under Rangpur S/S area
11:02 for red hot maintenance at 33 kV incoming DS. |  |  |  |  | from 09:50 to 11:02.
c) Bibiyana S/S- Bibiyana #3 400 kV STG line was shut down due to P/S work.
d) Rampura 132 kV capacitor bank-1 was switched on at 12:26 and shut down at 19:40 due to high temperature.
e) Julda 132/33 kV T-2 transformer was shut down at 12:27 due to oil leakage in valve and was switched
on at 13:36.
f) Feni 132/33 kV T-2 transformer was under shut down from 10:51 to 14:26 due to tap changer problem.
g) Mymensing-Netrokona 132 kV Ckt-1 & 2 tripped at 13:28 showing dist.Z2,3-phase at Mymensing end |  |  |  |  | About 72 MW power interruption occurring under Netrokona S/S area
& dist.Z1,A-phase at Netrokona end and were switched on at 13:45 & 15:08 respectively. |  |  |  |  | from 13:28 to 13:45.
h) Ghorasal #5 was synchronized at 15:06.
i) After maintenance Sikalbaha-150 MW GT was synchronized at 15:54.
j) Ghorasal #4 was shut down at 21:20 for conducting performance test.
k) Sikalbaha-225 MW tripped at 05:47(15/9/20) due to cooling water pump trip.
l) After maintenance Ashuganj-225 MW CCPP ST was shut down at 06:27(15/9/20) due to Ashuganj
132 kV Bus-2 shut down.
m) Mymemsing 132/33 kV T-3 transformer with 33 kV Bus were under shut down from 06:15 to 09:32 |  |  |  |  | About 27 MW power interruption occurring under Mymensing S/S area
(15/9/20) due to maintenance work. |  |  |  |  | from 06:15 to 09:32(15/9/20).
n) Sonargaon 132/33 kV T-1 transformer along with 33 kV Bus were under shut down from 07:05 to 09:20 |  |  |  |  | About 20 MW power interruption occurring under Sonargaon S/S area
(15/9/20) due to maintenance work. |  |  |  |  | from 07:05 to 09:20(15/9/20).
o) Ashuganj 132 kV Bus-2 is under shut down since 06:14(15/9/20) for C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-09-14 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 100 | 2913000 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 115 | 740250 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 4730227 | Machine problem
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 40 | 1238720 | Machine problem
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 12 | 1556681 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 339 | 8357256 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 305 | 7417000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 380 | 7952800 | Frequency control
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 2221440
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 125 | 3205615 | GT-1 Under S/D due to gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 97 | 1794168
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1052187
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 100 | 711871
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 301320
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 2208000
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 278 | 6928021 | Machine problem
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 2296800
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel Shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 932400
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1135680
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 878985
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 826639
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 48 | 1075560 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 761200
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 784600
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 8 | 86748 | Low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 5798506
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 131 | 3251520 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 104 | 1088616 | Engine problem
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 452160 | Fuel Shortage
| Dhaka area Total |  |  |  | 5895 | 3458 | 72697970
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 130 | 3100000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 8 | 105960
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 99495
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 714720
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 1330211 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 189 | 4377444
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 120 | 857376
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 1084747
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 30 | 600960 | Low demand
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2243520
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 476016
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 33 | 575040
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 85 | 1355520 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 28920
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 197 | 4611709 | Transformer O/L
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | DCT preparation
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 52 | 289380 | Low demand
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2401920
| Chattogram area Total |  |  |  | 2266 | 1257 | 24252938
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 1923456 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 162 | 4215000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 290 | 7132000 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 6574000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 10 | 380644 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 138240 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 35 | 1032504 | Gas shortage
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 138 | 2271563 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 66672 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 85 | 2055110
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 51 | 203040 | Low demand
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 360360 | Engine problem
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 210060
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 176 | 3634560
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 819300
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 728376 | Engine problem
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 489890
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 68 | 428640 | Low demand
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 2468760
| Cumilla Area Total |  |  |  | 2980 | 1617 | 35332902
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 109 | 3028200 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 439884
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 55 | 1144320 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 8100
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 184 | 4027200 | Engine problem
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 65 | 1203600 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 433 | 9851304
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 88 | 2147000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 22 | 645480 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3471954 | Frequency control
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 310 | 5990000
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 52 | 1171200
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 1174392
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 109000 | PBS Line problem
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 1436640 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 88 | 1992000
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 185 | 4661260
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 423000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 527784
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7117000 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 242460
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1319 | 31109170
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 927 | 22248000
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 2344320
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 27 | 171360 | Low demand
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 170 | 3312960 | Low demand
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 14336 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 320 | 7777728 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 522750
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 92 | 1000320 | Engine problem
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 355200 | Engine problem
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Reserve
| Khulna Area Total |  |  |  | 2284 | 1744 | 37746974
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 96 | 1075584
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 39 | 736617
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 68 | 1596000 | GT-2 Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 77 | 1855456 | Engine problem
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 520 | 12650700
| Barisal Area Total |  |  |  | 1054 | 800 | 17914357
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 93184
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 41832 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 47 | 295910
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 105 | 3366000 | ST Under maint.
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 158 | 3627491 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 1555627 | Gas shortage
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 365 | 8800636 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 213491
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 494880
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 83124 | Engine problem
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 241308
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 223680
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 88 | 922904 | Engine problem
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 111 | 1470048
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 2139168
| Rajshahi Area Total |  |  |  | 2183 | 1150 | 23569283
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 149 | 3446300 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Condenser
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 2099520
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 16340
| Rangpur Area Total |  |  |  | 605 | 262 | 5562160
| Total |  |  |  | 19892 | 12040 | 258037058
| Eastern Grid Total |  |  |  | 13766 | 8084 | 173244284
| Western Grid Total |  |  |  | 6126 | 3956 | 84792774
| National Grid Total |  |  |  | 19892 | 12040 | 258037058
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-09-14
| (a) ENTIRE EASTERN GRID : |  | 7673 | MW | (b) ENTIRE WESTERN GRID : |  | 3846 | MW
| i) Dhaka area |  | 4034 | MW | i) Khulna area |  | 1528 | MW
| ii) Chittagong area |  | 1120 | MW | ii) Rajshahi area |  | 1275 | MW
| iii) Comilla area |  | 1176 | MW | iii) Barisal area |  | 273 | MW
| iv) Mymensingh area |  | 876 | MW | iv) Rangpur area |  | 770 | MW
| v) Sylhet area |  | 467 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11519 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 130 | 11:00 | Sherpur | 106 | 22:00 | Jhenida | 112 | 20:00
| Munsiganj | 122 | 21:00 | Srimongal | 47 | 21:00 | Bottail | 126 | 19:30
| Sonargaon | 90 | 19:30 | Shahjibazar | 113 | 1:00 | G.K Project | 56 | 19:30
| Shyampur | 196 | 11:00 | Fenchuganj | 41 | 19:30 | Faridpur | 188 | 0.83333
| Bhulta | 196 | 24:00 | Kulawara | 40 | 19:00 | Madaripur | 102 | 0.91667
| Madanganj | 45 | 24:00 | Sylhet | 128 | 19:30 | Sariatpur | 64 | 20:00
| Shitalakhya | 128 | 13:00 | Chatak | 29 | 19:30 | Gopalganj | 97 | 19:00
| Rahim steel | 14 | 13:00 | Sunamganj | 45 | 20:00 | Bagerhat | 95 | 19:30
| Matuail | 74 | 1:00 | Biani Bazar | 51 | 19:30 | Mongla | 40 | 2:00
| Ghorasal | 80 | 24:00 | Comilla (S) | 176 | 20:00 | Satkhira | 114 | 0.875
| Narsingdi | 161 | 19:30 | Comilla(N) | 109 | 20:00 | Gallamari | 47 | 12:00
| Haripur (SBU) | 101 | 10:00 | Chandpur | 102 | 20:00 | Magura | 54 | 0.77083
| Ullon | 58 | 19:00 | Feni | 125 | 18:30 | Norail | 40 | 21:00
| Hasnabad | 205 | 21:00 | Chowmuhani | 180 | 20:00 | Chuadanga | 88 | 19:00
| Magbazar | 112 | 12:00 | Ashuganj | 56 | 23:00 | Barisal(N) | 46 | 0.91667
| Maniknagar | 98 | 12:00 | Daudkandi | 134 | 20:00 | Barisal (S) | 102 | 0.79167
| Bangabhaban | 40 | 10:00 | B.Baria | 162 | 21:00 | Patuakhali | 118 | 0.91667
| Narinda | 90 | 16:00 | Ramganj | 112 | 19:00 | Bhandaria | 52 | 0.79167
| Dhanmondi | 177 | 12:00 | Chaddagram | 38 | 20:00 | Borhan Uddin | 43 | 1:00
| Lalbag | 89 | 13:00 | PHP | 9 | 17:00 | Ishurdi | 63 | 20:00
| Madartek | 70 | 22:00 | Madunaghat | 51 | 12:00 | Ruppur Paromanobik | 2 | 20:00
| Dhaka University | 0 | 0 | Hathazari | 98 | 0.79167 | Natore | 122 | 19:30
| Fatullah | 37 | 0.375 | Khulshi | 211 | 0.58333 | Bogra | 170 | 19:30
| Mirpur | 105 | 18:30 | Halishahar | 138 | 0.58333 | Noagaon | 130 | 21:00
| Kalyanpur | 96 | 18:30 | Baraulia | 135 | 0.5 | Rajshahi | 149 | 21:00
| Gulshan | 136 | 12:00 | Sikalbaha | 27 | 0.8125 | Rajshahi New | 12 | 21:00
| Uttara | 88 | 13:00 | Dohazari | 82 | 0.79167 | C.Nawabganj | 74 | 21:00
| Uttara New | 32 | 12:00 | Cox'sbazar | 102 | 0.91667 | Amnura | 46 | 21:00
| Kamrangirchar | 90 | 12:00 | Chandraghona | 28 | 0.77083 | Pabna | 117 | 20:00
| Savar | 137 | 15:00 | Kaptai | 4.3 | 0.77083 | Shahjadpur | 93 | 21:00
| Bhasantec | 157 | 13:00 | A. Khaer Stl. | 0 | 0.041667 | Serajganj | 104 | 20:00
| Agargaon | 75 | 13:00 | Bakulia | 109 | 0.75 | Niyamatpur | 60 | 21:00
| Satmosjid | 100 | 13:00 | Julda | 24 | 0.41667 | Joypurhat | 57 | 21:00
| Tongi | 95 | 0.45833 | TK chemical | 26.9 | 0.77083 | Sherpur(Bogura) | 47 | 21:00
| Kabirpur | 234 | 12:00 | Modern Steel | 12 | 0.041667 | Mohastangor | 49 | 20:00
| Basundhara | 138 | 13:00 | Shahmirpur | 23 | 0.58333 | Rangpur | 142 | 18:30
| Manikganj | 66 | 0.875 | Khagrachhari | 22 | 0.8125 | Lalmonirhat | 59 | 19:00
| Joydevpur | 153 | 19:00 | Matarbari | 33 | 0.95833 | Saidpur | 108 | 19:00
| New Tongi | 122 | 10:00 | Baroiar Hat | 36 | 0.75 | Purbasadipur | 104 | 18:30
| Korda | 235 | 18:30 | Rangamati | 12 | 0.77083 | Thakurgaon | 82 | 21:00
| Dhamrai | 98 | 19:00 | Abul Khair 230 | 133 | 0.125 | Palashbari | 129 | 19:00
| Rajendrapur | 92 | 22:00 | BSRM | 154 | 0.54167 | Barapukuria | 53 | 21:00
| Valuka | 120 | 9:00 | GPH Ispat | 70 | 0.083333 | Panchagar | 49 | 18:30
| Tangail | 180 | 1:00 | Goalpara | 24 | 0.91667 | Joldhaka | 24 | 21:00
| Mymensing | 144 | 22:00 | Central s/s | 93 | 20:00 | Kurigram | 53 | 19:00
| Kishorganj | 136 | 22:00 | Noapara | 57 | 20:00
| Netrokona | 108 | 1:00 | Jessore | 122 | 19:00
| Jamalpur | 148 | 22:00 | Benapol | 50 | 19:30
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-09-14 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 395 | 3:00 | 387 | 14:00 | Kaliakoir | 375 | 0.083333 | 365 | 0.5
| Bheramara | 392 | 7:00 | 383 | 22:00 | Bhulta | 388 | 0.54167 | 378 | 0.5
| Ashuganj(N) | 392 | 1:00 | 385 | 12:00 | Gopalganj | 415 | 0.375 | 398 | 0.875
| Payra | 415 | 9:00 | 406 | 22:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 232 | 19:00 | 230 | 1:00 | Comilla (N) | 232 | 19:30 | 228 | 9:00
| Ishurdi | 235 | 6:00 | 227 | 20:00 | Hathazari | 225 | 19:00 | 217 | 9:00
| Ashuganj | 237 | 14:00 | 232 | 8:00 | Megnaghat | 230 | 1:00 | 224 | 12:00
| Serajganj | 230 | 4:00 | 226 | 19:00 | Fenchuganj | 237 | 2:00 | 234 | 14:00
| Baghabari | 240 | 10:00 | 235 | 22:00 | Siddhirganj | 228 | 1:00 | 223 | 12:00
| Barapukuria | 238 | 10:00 | 228 | 19:00 | Maniknagar | 226 | 1:00 | 220 | 12:00
| Bogra | 226 | 10:00 | 216 | 19:30 | Agargaon | 225 | 3:00 | 216 | 12:00
| Rajshahi | 227 | 18:00 | 218 | 21:00 | Barisal | 248 | 9:00 | 235 | 23:00
| Khulna South | 235 | 6:00 | 227 | 19:00 | AKSML | 223 | 22:00 | 214 | 12:00
| Rampura | 226 | 16:00 | 220 | 12:00 | BSRM | 223 | 3:00 | 216 | 12:00
| Haripur | 225 | 18:30 | 220 | 12:00 | Bibiyana | 236 | 19:00 | 230 | 9:00
| Hasnabad | 225 | 1:00 | 218 | 12:00 | Bhulta | 230 | 19:00 | 222 | 17:00
| Shyampur | 222 | 1:00 | 217 | 12:00 | Ashuganj (S) | 235 | 2:00 | 231 | 12:00
| Aminbazar | 225 | 1:00 | 219 | 10:00 | Kaliakoir | 230 | 13:00 | 223 | 2:00
| Tongi | 226 | 1:00 | 217 | 8:00 | GPH | 221 | 13:00 | 213 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 130 | 1:00 | 127 | 9:00 | Hathazari | 134 | 0.83333 | 130 | 0.33333
| Munsiganj | 132 | 19:00 | 128 | 12:00 | Khulshi | 133 | 0.77083 | 126 | 0.375
| Sonargaon | 129 | 21:00 | 126 | 7:00 | Halishahar | 135 | 0.79167 | 127 | 0.375
| Shyampur | 131 | 1:00 | 127 | 12:00 | Baraulia | 132 | 0.77083 | 126 | 0.375
| Bhulta | 124 | 13:00 | 120 | 7:00 | Sikalbaha | 136 | 19:00 | 127 | 0.375
| Madanganj | 129 | 13:00 | 124 | 6:00 | Dohazari | 131 | 19:00 | 125 | 0.375
| Shitalakhya | 139 | 1:00 | 132 | 12:00 | Cox'sbazar | 123 | 0.41667 | 118 | 0.083333
| Rahim steal | 129 | 1:00 | 126 | 12:00 | Chandraghona | 134 | 0.77083 | 127 | 0.375
| Matuail | 130 | 1:00 | 127 | 9:00 | Kaptai | 133 | 18:00 | 130 | 0.33333
| Ghorasal | 137 | 22:00 | 136 | 1:00 | A. Khaer Stl. | 132 | 0.77083 | 125 | 9:00
| Narsinghdi | 126 | 13:00 | 121 | 1:00 | Bakulia | 134 | 0.79167 | 127 | 0.375
| Haripur (SBU) | 130 | 2:00 | 126 | 11:00 | Julda | 135 | 0.79167 | 128 | 0.375
| Ullon | 132 | 3:00 | 125 | 12:00 | TK Chemical | 135 | 0.77083 | 129 | 7:00
| Hasnabad | 135 | 1:00 | 130 | 10:00 | Modern Steel | 134 | 0.79167 | 126 | 0.375
| Magbazar | 132 | 4:00 | 125 | 12:00 | Shahmirpur | 135 | 0.79167 | 128 | 0.375
| Maniknagar | 132 | 1:00 | 126 | 12:00 | Khagrachhari | 133 | 0.8125 | 127 | 0.375
| Bangabhaban | 132 | 1:00 | 126 | 12:00 | Matarbari | 127 | 0.66667 | 121 | 0.083333
| Narinda | 132 | 1:00 | 126 | 12:00 | Baroiar Hat | 129 | 0.83333 | 125 | 0.375
| Dhanmondi | 132 | 3:00 | 125 | 12:00 | Rangamati | 133 | 0.79167 | 128 | 10:00
| Lalbag | 135 | 1:00 | 127 | 17:00 | Goalpara S/S | 136 | 6:00 | 131 | 15:00
| Madartek | 132 | 1:00 | 125 | 12:00 | Khulna Central S/S | 135 | 0.41667 | 131 | 14:00
| Dhaka University |  |  |  |  | Noapara | 132 | 10:00 | 128 | 13:00
| Fatuiiah | 132 | 0.79167 | 128 | 12:00 | Jessore | 128 | 10:00 | 120 | 19:00
| Mirpur | 135 | 3:00 | 126 | 12:00 | Benapol | 130 | 6:00 | 119 | 18:30
| Kalyanpur | 134 | 3:00 | 127 | 12:00 | Jhenida | 126 | 0.75 | 114 | 19:00
| Gulshan | 131 | 3:00 | 125 | 12:00 | Bottail | 133 | 16:00 | 125 | 20:00
| Uttara | 132 | 3:00 | 126 | 12:00 | G.K Project | 140 | 0.375 | 135 | 19:00
| Uttara New | 135 | 2:00 | 128 | 8:00 | Faridpur | 134 | 10:00 | 126 | 1:00
| Kamrangirchar | 133 | 1:00 | 126 | 12:00 | Madaripur | 138 | 0.375 | 130 | 21:00
| Savar | 133 | 1:00 | 125 | 12:00 | Shariyatpur S/S | 136 | 0.29167 | 127 | 22:00
| Bhasantec | 136 | 3:00 | 128 | 12:00 | Gopalganj | 137 | 18:30 | 125 | 22:00
| Agargaon | 137 | 2:00 | 130 | 12:00 | Bagerhat | 130 | 6:00 | 121 | 19:00
| Satmosjid | 137 | 3:00 | 129 | 12:00 | Mongla | 127 | 0.75 | 122 | 1:00
| Tongi | 137 | 0.54167 | 131 | 8:00 | Satkhira | 135 | 0.25 | 127 | 19:00
| Kabirpur | 134 | 3:00 | 128 | 12:00 | Gallamari | 137 | 6:00 | 131 | 15:00
| Basundhara | 131 | 19:00 | 124 | 12:00 | Magura | 125 | 17:00 | 114 | 19:00
| Manikganj | 139 | 2:00 | 131 | 15:00 | Norail | 124 | 0.70833 | 109 | 19:00
| Joydevpur | 140 | 23:00 | 134 | 21:00 | Chuadanga | 123 | 17:00 | 104 | 21:00
| New Tongi | 135 | 0.54167 | 129 | 8:00 | Barisal(N) | 141 | 9:00 | 132 | 23:00
| Kodda | 135 | 13:00 | 124 | 0.33333 | Barisal (S) | 138 | 0.29167 | 118 | 23:00
| Dhamrai | 133 | 5:00 | 128 | 21:00 | Patuakhali(S) | 136 | 0.83333 | 125 | 23:00
| Rajendrapur | 134 | 13:00 | 123 | 16:00 | Bhandaria | 126 | 9:00 | 119 | 19:00
| Valuka | 132 | 15:00 | 118 | 21:00 | Ishurdi | 138 | 10:00 | 134 | 21:00
| Tangail | 135 | 6:00 | 128 | 21:00 | Ruppur Paromanobik | 136 | 10:00 | 133 | 20:00
| Mymensing | 134 | 15:00 | 121 | 21:00 | Natore | 136 | 10:00 | 131 | 20:00
| Kishorganj | 133 | 15:00 | 121 | 21:00 | Bogra | 137 | 10:00 | 130 | 20:00
| Netrokona | 130 | 15:00 | 117 | 21:00 | Noagaon | 133 | 10:00 | 123 | 20:00
| Jamalpur | 138 | 6:00 | 130 | 18:00 | Rajshahi | 136 | 18:00 | 130 | 1:00
| Sherpur | 138 | 6:00 | 129 | 18:00 | Rajshahi New | 138 | 18:00 | 131 | 3:00
| Srimongal | 136 | 4:00 | 133 | 0.8125 | C.Nawabganj | 136 | 18:00 | 129 | 20:00
| Shahjibazar | 136 | 15:00 | 131 | 0.75 | Amnura | 136 | 18:00 | 126 | 5:00
| Fenchuganj | 135 | 1:00 | 134 | 0.125 | Pabna | 134 | 18:00 | 129 | 21:00
| Khulawara | 134 | 1:00 | 132 | 0.75 | Shahjadpur | 138 | 18:00 | 133 | 21:00
| Sylhet | 134 | 8:00 | 131 | 0.8125 | Serajganj | 132 | 18:00 | 128 | 21:00
| Chatak | 132 | 6:00 | 128 | 21:00 | Niyamatpur | 132 | 10:00 | 120 | 21:00
| Sunamganj | 131 | 8:00 | 126 | 0.8125 | Joypurhat | 134 | 11:00 | 121 | 21:00
| Biani Bazar | 133 | 9:00 | 128 | 0.041667 | Sherpur(Bogura) | 136 | 10:00 | 129 | 21:00
| Comilla(s) | 128 | 7:00 | 120 | 18:30 | Mohastangor | 136 | 10:00 | 127 | 20:00
| Comilla(n) | 136 | 19:30 | 131 | 9:00 | Rangpur | 135 | 10:00 | 117 | 19:00
| Chandpur | 131 | 18:00 | 125 | 24:00 | Lalmonirhat | 135 | 10:00 | 115 | 19:00
| Feni | 131 | 19:00 | 125 | 15:00 | Saidpur | 132 | 10:00 | 117 | 19:00
| Chowmuhani | 130 | 7:00 | 123 | 23:00 | Purbasadipur | 128 | 10:00 | 115 | 19:00
| Ashuganj | 136 | 7:00 | 133 | 20:00 | Thakurgaon | 128 | 10:00 | 114 | 20:00
| Daudkandi | 130 | 13:00 | 125 | 23:00 | Palashbari | 133 | 11:00 | 120 | 19:30
| B.Baria | 132 | 18:00 | 127 | 21:00 | Barapukuria | 137 | 11:00 | 128 | 20:00
| Ramganj | 122 | 18:30 | 120 | 19:30 | Panchagar | 128 | 6:00 | 112 | 19:00
| Chaddagram | 131 | 20:00 | 129 | 7:00 | Joldhaka | 132 | 6:00 | 116 | 20:00
| PHP | 130 | 13:00 | 125 | 15:00 | Kurigram | 132 | 10:00 | 114 | 19:00
| Madanhat | 136 | 18:30 | 128 | 9:00

## L-Curve
Date | 2020-09-14
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 18 | 7855 | 3847 | 11702 |  |  |  | QF-LDC-11
0:30 | 28 | 7785 | 3892.5 | 11677.5 | Date: | 2020-09-14
1:00 | 38 | 7715 | 3938 | 11653
1:30 | 24 | 7584 | 3834.5 | 11418.5
2:00 | 10 | 7453 | 3731 | 11184
2:30 | 30.5 | 7380.5 | 3707.5 | 11088 | [5 empty] | Gen. at Eve. Peak | 12040 | 12040 MW (20:00 )
3:00 | 51 | 7308 | 3684 | 10992 | [6 empty] | 20:00
3:30 | 111 | 7165.5 | 3688 | 10853.5 | [5 empty] | Gen. at Day Peak | 10467 | 10467 MW (12:00 )
4:00 | 171 | 7023 | 3692 | 10715 | [6 empty] | 12:00
4:30 | 164.5 | 6923.5 | 3649 | 10572.5 | [5 empty] | Highest Generation | 12040
5:00 | 158 | 6824 | 3606 | 10430 | [6 empty] | 20:00
5:30 | 186.5 | 6616.5 | 3453 | 10069.5
6:00 | 215 | 6409 | 3300 | 9709
6:30 | 198 | 6298 | 3212.5 | 9510.5
7:00 | 181 | 6187 | 3125 | 9312
7:30 | 223 | 6174.5 | 3084.5 | 9259
8:00 | 265 | 6162 | 3044 | 9206
8:30 | 340 | 6323 | 3060.5 | 9383.5
9:00 | 415 | 6484 | 3077 | 9561
9:30 | 418.5 | 6725 | 3055.5 | 9780.5
10:00 | 422 | 6966 | 3034 | 10000
10:30 | 338.5 | 7068 | 3052.5 | 10120.5
11:00 | 255 | 7170 | 3071 | 10241
11:30 | 267 | 7238.5 | 3115.5 | 10354
12:00 | 279 | 7307 | 3160 | 10467
12:30 | 182 | 7267 | 3164 | 10431
13:00 | 85 | 7227 | 3168 | 10395
13:30 | 87.5 | 7075.5 | 3108 | 10183.5
14:00 | 90 | 6924 | 3048 | 9972
14:30 | 86 | 6982 | 3078.5 | 10060.5
15:00 | 82 | 7040 | 3109 | 10149
15:30 | 114 | 6930 | 3067.5 | 9997.5
16:00 | 146 | 6820 | 3026 | 9846
16:30 | 205.5 | 6746 | 2991 | 9737
17:00 | 265 | 6672 | 2956 | 9628
17:30 | 237.5 | 6700 | 3010 | 9710
18:00 | 210 | 6728 | 3064 | 9792
18:30 | 190 | 7350 | 3427.5 | 10777.5
19:00 | 170 | 7972 | 3791 | 11763
19:30 | 128 | 8055 | 3970 | 12025
20:00 | 135 | 8084 | 3956 | 12040 |  |  |  | Executive Engineer
20:30 | 101.5 | 8018 | 3965 | 11983 |  |  |  | Network Operation Division
21:00 | 68 | 7952 | 3974 | 11926
21:30 | 44 | 7932.5 | 3991.5 | 11924
22:00 | 20 | 7913 | 4009 | 11922 |  |  |  |  | Page 6 of 7
22:30 | 26.5 | 7912.5 | 3974 | 11886.5
23:00 | 33 | 7912 | 3939 | 11851
23:30 | 25.5 | 7883.5 | 3893 | 11776.5
24:00 | 18 | 7855 | 3847 | 11702
12040 MW (20:00 )
10467 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-09-14 |  | Energy | 258037058
[10 empty] | 2020-09-14 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4074 | 927 | 2122 | 3229 | 719 | 40 | 500 | 0 | 164
0:30 | 4052.5 | 927 | 2093 | 3198.5 | 719.5 | 61.5 | 497 | 0 | 165 | Date: | 2020-09-14
1:00 | 4031 | 927 | 2064 | 3168 | 720 | 83 | 494 | 0 | 166
1:30 | 4024 | 927 | 2078 | 3043 | 720 | 83 | 379.5 | 0 | 164 | [7 empty] | Total Energy | 258.0371 | Total Energy Gen 258.037 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 258.037 MKWHr
2:00 | 4017 | 927 | 2092 | 2918 | 720 | 83 | 265 | 0 | 162 | [7 empty] | Energy not Served | 0
2:30 | 4034 | 927 | 2087 | 2836.5 | 720 | 83 | 242.5 | 0 | 158 | [7 empty] | Energy Requirement | 258.0371
3:00 | 4051 | 927 | 2082 | 2755 | 720 | 83 | 220 | 0 | 154
3:30 | 4081 | 927 | 2087 | 2589.5 | 720.5 | 83.5 | 212 | 0 | 153 | [6 empty] | Shortage
4:00 | 4111 | 927 | 2092 | 2424 | 721 | 84 | 204 | 0 | 152
4:30 | 4134.5 | 926.5 | 2108.5 | 2268 | 707 | 84 | 196 | 0 | 148
5:00 | 4158 | 926 | 2125 | 2112 | 693 | 84 | 188 | 0 | 144
5:30 | 4125 | 926.5 | 2073 | 1893 | 650.5 | 84 | 179.5 | 0 | 138
6:00 | 4092 | 927 | 2021 | 1674 | 608 | 84 | 171 | 0 | 132
6:30 | 4072.5 | 927 | 2010 | 1525 | 607.5 | 84 | 154 | 0 | 129 |  |  |  |  | Coal
7:00 | 4053 | 927 | 1999 | 1376 | 607 | 84 | 137 | 0 | 126
7:30 | 3988 | 927 | 1992 | 1396.5 | 607.5 | 84 | 128.5 | 0 | 127 |  |  |  | Oil |  |  |  | ,
8:00 | 3923 | 927 | 1985 | 1417 | 608 | 84 | 120 | 0 | 128
8:30 | 3917.5 | 927 | 1998.5 | 1604 | 605.5 | 62 | 120 | 0 | 130
9:00 | 3912 | 927 | 2012 | 1791 | 603 | 40 | 120 | 0 | 132
9:30 | 3902.5 | 927 | 1952 | 2098 | 580 | 40 | 124 | 0 | 134
10:00 | 3893 | 927 | 1892 | 2405 | 557 | 40 | 128 | 0 | 136
10:30 | 3909 | 927 | 1885.5 | 2508.5 | 553.5 | 39.5 | 132 | 0 | 141
11:00 | 3925 | 927 | 1879 | 2612 | 550 | 39 | 136 | 0 | 146
11:30 | 3989.5 | 929.5 | 1926 | 2629 | 530 | 38 | 143.5 | 0 | 147
12:00 | 4054 | 932 | 1973 | 2646 | 510 | 37 | 151 | 0 | 148
12:30 | 3994.5 | 929.5 | 1891 | 2715.5 | 549.5 | 37 | 154.5 | 0 | 145
13:00 | 3935 | 927 | 1809 | 2785 | 589 | 37 | 158 | 0 | 142
13:30 | 3935 | 927 | 1809 | 2785 | 589 | 37 | 158 | 0 | 142
14:00 | 3935 | 927 | 1809 | 2785 | 589 | 37 | 158 | 0 | 142
14:30 | 3940 | 927 | 1902 | 2592 | 562 | 37 | 151 | 0 | 147
15:00 | 3945 | 927 | 1995 | 2399 | 535 | 37 | 144 | 0 | 152
15:30 | 3941 | 927.5 | 1979 | 2288 | 527.5 | 37.5 | 144 | 0 | 142
16:00 | 3937 | 928 | 1963 | 2177 | 520 | 38 | 144 | 0 | 132
16:30 | 3969 | 927.5 | 1961.5 | 2026 | 523.5 | 38.5 | 150.5 | 0 | 136
17:00 | 4001 | 927 | 1960 | 1875 | 527 | 39 | 157 | 0 | 140
17:30 | 4043 | 927 | 1879.5 | 1908.5 | 538.5 | 39.5 | 229 | 0 | 144
18:00 | 4085 | 927 | 1799 | 1942 | 550 | 40 | 301 | 0 | 148
18:30 | 4075.5 | 926.5 | 1883 | 2582.5 | 584.5 | 40 | 528.5 | 0 | 157
19:00 | 4066 | 926 | 1967 | 3223 | 619 | 40 | 756 | 0 | 166
19:30 | 4099 | 928 | 1939 | 3495 | 669 | 40 | 683 | 0 | 172
20:00 | 4108 | 927 | 1931 | 3523 | 669 | 40 | 666 | 0 | 176
20:30 | 4115.5 | 927 | 1964 | 3450 | 669 | 40 | 643.5 | 0 | 174
21:00 | 4123 | 927 | 1997 | 3377 | 669 | 40 | 621 | 0 | 172
21:30 | 4084 | 927 | 2020 | 3385 | 674 | 40 | 621 | 0 | 173
22:00 | 4045 | 927 | 2043 | 3393 | 679 | 40 | 621 | 0 | 174
22:30 | 4064.5 | 927 | 2062 | 3311 | 689 | 40 | 621 | 0 | 172
23:00 | 4084 | 927 | 2081 | 3229 | 699 | 40 | 621 | 0 | 170
23:30 | 4079 | 927 | 2101.5 | 3229 | 709 | 40 | 560.5 | 0 | 167 | Max Temp. in Dhaka |  | 33.6° C
24:00 | 4074 | 927 | 2122 | 3229 | 719 | 40 | 500 | 0 | 164
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 258.037 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 258.037 MKWHr
Note on W13: Author:

## Generation
g | 2020-09-14
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 83 | 83 | 83 | 84 | 84 | 84 | 84 | 84 | 40 | 40 | 39 | 37 | 37 | 37 | 37 | 38 | 39 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 1330211
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3100000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [12 empty] | 15 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 |  | 0 | 105960
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 2 | 11 | 18 | 16 | 20 | 10 | 5 | 3 | 11 | 5 | 1 | [9 empty] | 99495
6 | Sikalbaha 225MW CCPP (Gas) | 164 | 165 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 216 | 206 | 206 | 204 | 204 | 204 | 203 | 203 | 216 |  | 189 | 190 | 189 | 191 | 191 | 190 | 190 | 4377444
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | [15 empty] | 50 | 100 | 100 |  | 120 | 120 | 120 | 120 | 120 | 120 | 121 | 857376
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 102 | 68 | 68 | 68 | 68 | 51 | 17 | [10 empty] | 25 |  | 102 | 102 | 102 | 102 | 102 | 102 | 56 | 1084747
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [17 empty] | 12 |  | 50 | [6 empty] | 66672
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 279 | 279 | 273 | 277 | 295 | 251 | 296 | 309 | 283 | 279 | 300 | 303 | 251 | 273 | 303 | 276 | 263 | 303 |  | 267 | 282 | 278 | 287 | 270 | 304 | 277 | 6928021
18 | Kodda 300 MW PP Unit-2 (Summit) | 296 | 300 | 300 | 195 | 130 | 95 | 45 | 45 | 86 | 270 | 290 | 292 | 285 | 283 | 295 | 200 | 200 | 200 |  | 268 | 300 | 300 | 300 | 300 | 300 | 300 | 5798506
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 150 | 151 | 147 | 150 | 150 | 150 | 150 | 150 | 150 | 147 | 150 | 150 | 150 | 157 | 150 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 |  |  | 0 | 2913000
23 | Ghorasal TPP Unit-5 | [15 empty] | 22 | 60 | 70 |  | 100 | 115 | 115 | 115 | 115 | 115 | 115 | 740250
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4730227
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1923456
32 | Ashuganj 50 MW PP | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 380644
33 | Ashuganj 225 MW CCPP | 175 | 175 | 180 | 183 | 186 | 187 | 187 | 173 | 157 | 174 | 192 | 186 | 178 | 167 | 167 | 173 | 184 | 166 |  | 165 | 165 | 162 | 149 | 159 | 169 | 172 | 4215000
34 | Ashuganj 450 MW CCPP(South) | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 6574000
| Ashuganj 450 MW CCPP(North) | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 280 | 275 | 275 | 275 | 290 | 290 | 290 | 290 | 290 | 290 | 290 |  | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 7132000
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 138240
36 | Chandpur 150 MW CCPP | 80 | 88 | 81 | 80 | 88 | 82 | 86 | 90 | 87 | 81 | 86 | 90 | 81 | 84 | 96 | 86 | 86 | 96 |  | 85 | 85 | 85 | 96 | 82 | 96 | 81 | 2055110
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 337 | 336 | 336 | 336 | 339 | 337 | 337 | 361 | 355 | 338 | 340 | 359 | 345 | 339 | 358 | 339 | 339 | 342 |  | 352 | 339 | 339 | 339 | 350 | 354 | 346 | 8357256
40 | Meghnaghat 450 MW CCPP(MPL) | 380 | 380 | 380 | 380 | 380 | 340 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 400 | 400 | 400 | 340 |  | 380 | 380 | 380 | 400 | 400 | 420 | 420 | 7952800
41 | Haripur 360MW CCPP(HPL) | 316 | 340 | 340 | 346 | 348 | 351 | 351 | 300 | 304 | 303 | 304 | 304 | 305 | 304 | 304 | 305 | 304 | 305 |  | 304 | 304 | 305 | 300 | 293 | 293 | 300 | 7417000
42 | RPCL 210MW CCPP | 147 | 160 | 161 | 160 | 160 | 160 | 160 | 158 | 158 | 123 | 123 | 123 | 116 | 103 | 103 | 108 | 108 | 108 |  | 108 | 108 | 109 | 109 | 108 | 107 | 146 | 3028200
43
44 | Fenchugonj CCPP Phase-1 | 91 | 91 | 91 | 90 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 89 | 90 | 91 | 91 |  | 91 | 91 | 88 | 91 | 91 | 90 | 91 | 2147000
45 | Fenchugonj CCPP Phase-2 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 20 | 20 | 20 | 22 |  | 22 | 22 | 22 | 30 | 30 | 30 | 30 | 645480
46 | Shajibazar 330 MW CCPP | 263 | 260 | 262 | 262 | 262 | 263 | 260 | 261 | 260 | 260 | 261 | 263 | 262 | 261 | 261 | 262 | 284 | 308 |  | 305 | 306 | 310 | 257 | 258 | 263 | 261 | 5990000
47 | Shahjibazar GTPP Unit- 8 & 9 | 66 | 66 | 65 | 64 | 64 | 64 | 63 | 63 | 61 | 40 | 40 | 59 | 60 | 60 | 55 | 61 | 62 | 51 |  | 62 | 62 | 62 | 64 | 64 | 64 | 64 | 1436640
48 | Shahjibazar 86MW PP (Shahjibazar) | 88 | 88 | 88 | 88 | 88 | 88 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 50 | 84 | 84 | 87 | 30 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 1992000
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 200 | 231 | 232 | 232 | 232 | 185 | 185 |  | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 4661260
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 423000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 242460
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  |  |  | 8 | 8 | 8 | 8 | [9 empty] | 2 | 11 | 11 | 109000
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 50 | 50 | 50 | 50 | 47 | 47 | 47 | 25 |  | 51 | 51 | 52 | 52 | 52 | 52 | 52 | 1171200
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 16 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 527784
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 280 | 280 | 275 | 280 | 275 | 280 | 305 | 300 | 280 | 280 | 305 | 280 | 270 | 300 | 290 | 280 | 280 |  | 290 | 290 | 280 | 290 | 290 | 280 | 290 | 7117000
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 17 | [5 empty] | 35 | 55 | 55 | 35 | 35 | 30 | 17 | 17 | 17 | 30 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 826639
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 18 | 18 | 18 | 18 | 18 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 476016
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 19 | [8 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 301320
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 439884
63 | Impoprt (Tripura) | 166 | 162 | 154 | 152 | 144 | 132 | 126 | 128 | 132 | 136 | 146 | 148 | 142 | 148 | 152 | 132 | 140 | 148 |  | 166 | 172 | 176 | 172 | 174 | 170 | 164 | 3634560
64 | Malancha, Ctg. EPZ (United) | 37 | 40 | 40 | 42 | 42 | 25 | 35 | 8 | 4 | 3 | 3 | 3 | 8 | 4 | 4 | 4 | 10 | 13 |  | 24 | 28 | 33 | 35 | 35 | 41 | 41 | 575040
65 | Feni 22MW PP (Doreen) | 18 |  | 18 | 18 | 18 | 18 | 18 |  |  | 16 | 16 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 360360
66 | Feni 11 MW PP (Doreen) | 11 |  | 11 | 11 | 11 | 11 |  |  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 210060
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 819300
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 15 | 21 | 21 | 20 | 20 | 20 | 20 | 15 | 20 |  | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 489890
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 0 |  | 17 | 27 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 20 | 23 | 475560
71 | Maona 33 MW PP(Summit) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 33 | 33 |  | 33 | 33 | 33 | 33 | 28 | 28 | 28 | 761200
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 17 | 17 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 784600
73 | Ghorashal 108MW PP (Regent) | 83 | 84 | 84 | 84 | 83 | 83 | 83 | 83 | 83 | 62 | 62 | 62 | 62 | 63 | 63 | 63 | 63 | 63 |  | 63 | 12 | 12 | 12 | 41 | 78 | 95 | 1556681
| Feni Lanka Power | [12 empty] | 52 |  |  |  |  | 17 |  | 68 | 68 | 68 | 68 | 68 | 34 | 0 | 428640
| Chowmuhani 113 MW | 113 | 113 | 108 | 113 | 113 | 104 | 104 | 104 | 104 | 103 | 103 | 104 | 105 | 75 | 75 | 75 | 75 | 75 |  | 111 | 113 | 113 | 113 | 113 | 113 | 113 | 2468760
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 100 | 100 | 100 | 100 | 80 | 50 | 55 | 90 | 90 | 100 | 100 | 82 | 98 | 100 | 100 | 65 | 50 |  | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 2208000
78 | Gazipur 52 MW PP | [10 empty] | 13 | 16 | 8 |  |  |  |  | 2 |  | 25 | 8 | 8 |  |  |  | 0 | 86748
79 | Kodda 150MW PP | 64 | 32 | 32 | 16 | [5 empty] | 8 | 16 | 16 | 16 |  |  |  |  | 20 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 1135680
80 | Jamalpur 95 MW PP(Powerpac) | 55 | 55 | 54 | 54 | 55 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 40 | 40 | 8 | 8 | 24 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1144320
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 43 | 25 |  |  |  | 1 | 8 | 8 | 20 | 40 | 43 | 43 | 43 | 16 | 16 |  | 32 | 43 | 43 | 43 | 43 | 43 | 43 | 728376
| Gazipur 100 MW PP | 104 | [6 empty] | 1 | 33 | 70 | 92 | 105 | 70 | 17 | 17 | 16 | 16 | 16 |  | 68 | 70 | 104 | 50 | 50 | 50 | 50 | 1088616
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 3 | 4 | 5 | 5 | 4 | 4 | 2 | 0 | 0 | 0 | [9 empty] | 28920
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | [19 empty] | 16 | 52 | 52 | 52 | 52 | 52 | 52 | 289380
82 | Madanganj 102 PP(Summit) | 81 | 81 | 81 | 48 | 48 | 47 | 30 | 30 | 30 | 45 | 70 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 85 | 97 | 97 | 97 | 97 | 97 | 97 | 1794168
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 20 | [7 empty] | 10 | 41 | 50 | 55 | 70 | 40 | 20 | 10 | 10 | 10 |  | 83 | 100 | 100 | 50 | 50 |  | 0 | 711871
86 | Meghnaghat CCPP(Summit) | 130 | 130 | 125 | 145 | 145 | 130 | 150 | 150 | 130 | 125 | 130 | 138 | 125 | 122 | 132 | 123 | 123 | 143 |  | 120 | 125 | 125 | 144 | 130 | 150 | 135 | 3205615
87 | Meghnaghat 100 MW(IEL) | 100 | 100 | 100 | 100 | 100 | 75 | 55 | 55 | 63 | 97 | 100 | 100 | 100 | 100 | 100 | 100 | 75 | 52 |  | 78 | 100 | 100 | 100 | 97 | 100 | 100 | 2221440
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 24 | 31 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 452160
88 | Ghorashal 78.5 MW PP(MAX) | 68 | 68 | 68 | 68 | 68 | 67 | 67 | 67 | 66 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 1238720
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [9 empty] | 20 | 10 | 50 | 100 | 100 | 80 | 80 | 10 | 10 |  | 60 | 30 | 30 | 30 | 30 |  | 0 | 600960
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 46 | 46 | 46 | 48 | 48 | 48 | 48 | 49 | 49 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1174392
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 35 | 35 | 35 | 35 | 35 | 35 | 51 | 1032504
94 | Gagnagar 102 MW PP (Digital Power) | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 95 | 98 | 100 |  | 100 | 102 | 102 | 102 | 102 | 102 | 102 | 2296800
95 | Patenga 50MW PP (Baraka) | 34 | [7 empty] | 2 | 20 | 49 | 50 | 50 | 50 | 50 | 50 | 28 | 18 |  | 43 | 50 | 50 | 50 | 50 | 50 | 50 | 714720
96 | Chattogram 108 MW PP (ECPV) | 85 | 32 | 30 | [5 empty] | 1 | 53 | 75 | 75 | 72 | 71 | 72 | 72 | 81 | 85 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1355520
97 | Katpotti 52 MW PP (Sinha) | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 20 | 15 | 15 | 15 | 50 | 39 | 40 | 40 | 40 | 40 | 43 | 55 | 30 | 30 |  | 50 | 55 | 55 | 55 | 55 | 55 | 55 | 1052187
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 17 |  |  |  |  | 17 | 55 | 55 |  | 35 | 35 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 878985
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 163 | 110 | 110 | 163 | 163 | 130 | 163 | 110 | 110 | 110 | 130 | 130 | 110 |  | 130 | 130 | 130 | 130 | 163 | 130 | 130 | 3471954
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 0 | 0 | [10 empty] | 8100
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 17 |  |  |  |  | 54 | 54 | 54 | 54 | 54 | 35 | 17 | 17 | 17 | 17 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 932400
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 185 | 185 | 184 | 182 | 185 | 160 | 130 | 140 | 150 | 170 | 170 | 170 | 183 | 140 | 140 | 140 | 100 | 108 |  | 194 | 184 | 184 | 184 | 184 | 185 | 185 | 4027200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 144 | 141 | 141 | 148 | 138 | 124 | 113 | 113 | 146 | 149 | 133 | 133 | 133 | 133 | 129 | 114 | 122 | 131 |  | 135 | 131 | 131 | 134 | 136 | 149 | 149 | 3251520
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 76 | 76 | 76 | 90 | 90 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2243520
116 | Chandpur 200MW (Desh energy) | [17 empty] | 2 |  | 35 | 50 | 51 | 17 | 17 |  | 0 | 203040
117 | Ashuganj 150MW PP (Midland) | 133 | 133 | 50 | 5 | 5 | 5 | 6 | 6 | 18 | 108 | 133 | 132 | 128 | 128 | 130 | 70 | 70 | 75 |  | 135 | 139 | 138 | 138 | 138 | 135 | 133 | 2271563
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 115 | 115 | 75 | 55 | 35 | 8 | 8 | 8 | 17 | 24 | 24 | 24 | 8 | 8 | 8 | 8 | 8 | 8 |  | 54 | 65 | 65 | 65 | 97 | 115 | 115 | 1203600
| Anwara 300 MW PP (United) | 198 | 198 | 216 | 234 | 198 | 180 | 161 | 160 | 197 | 197 | 179 | 179 | 179 | 179 | 179 | 179 | 179 | 179 |  | 196 | 197 | 197 | 197 | 197 | 197 | 198 | 4611709
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2401920
120 | Eastern Zone Total | 7715 | 7453 | 7308 | 7023 | 6824 | 6409 | 6187 | 6162 | 6484 | 6966 | 7170 | 7307 | 7227 | 6924 | 7040 | 6820 | 6672 | 6728 |  | 7972 | 8055 | 8084 | 7952 | 7913 | 7912 | 7855 | 173244284
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 99 | 99 | 115 | 115 | 115 | 115 | 83 | 83 | 88 | 99 | 99 | 99 | 99 | 99 | 83 | 84 | 49 | 49 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2344320
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 18 | [16 empty] | 7 |  | 28 | 27 | 27 | 27 | 27 | 27 | 27 | 171360
| Khulna 225 MW CCPP | 145 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 3312960
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | 17 | 17 | 17 | 17 | 17 | [13 empty] | 35 | 53 | 53 | 53 | 53 | 35 | 13 | 355200
130
131
132
133
| Barisal 110 MW PP (Summit ) | 96 | 80 | 64 | 64 | 64 | 32 |  |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 25 |  | 96 | 96 | 96 | 64 | 64 | 64 | 64 | 1075584
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 77 | 77 | 75 | 76 | 76 | 77 | 77 | 77 | 76 | 77 | 77 | 76 | 75 | 78 | 77 | 77 | 78 | 76 |  | 77 | 77 | 77 | 78 | 78 | 77 | 78 | 1855456
| Bhola 225 MW CCPP | 66 | 67 | 65 | 68 | 68 | 68 | 69 | 68 | 67 | 67 | 67 | 67 | 67 | 67 | 65 | 67 | 67 | 67 |  | 63 | 63 | 68 | 68 | 68 | 67 | 68 | 1596000
140 | Bhola 33 MW PP (Venture) | 39 | 39 | 36 | 37 | 34 | 29 | 28 | 20 | 19 | 21 | 21 | 27 | 29 | 28 | 29 | 25 | 24 | 30 |  | 38 | 38 | 39 | 39 | 40 | 39 | 39 | 736617
141 | Noapara 100 MW PP (Bangla Trac) | 100 | 100 | 100 | 40 | 40 | [14 empty] | 55 | 100 | 92 | 100 | 100 | 100 | 100 | 1000320
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 40 | 40 | 40 | 40 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  |  |  |  | 8 |  | 40 | 40 | 40 | 40 | 40 | 32 | 32 | 522750
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 5 | 10 | [8 empty] | 14336
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 927 | 927 | 927 | 927 | 926 | 927 | 927 | 927 | 927 | 927 | 927 | 932 | 927 | 927 | 927 | 928 | 927 | 927 |  | 926 | 928 | 927 | 927 | 927 | 927 | 927 | 22248000
147 | Bheramara 410 MW CCPP | 345 | 335 | 335 | 335 | 320 | 310 | 305 | 295 | 310 | 305 | 305 | 310 | 300 | 300 | 300 | 300 | 300 | 310 |  | 310 | 310 | 320 | 320 | 325 | 310 | 300 | 7777728
148 | Payra 1320 MW | 570 | 570 | 570 | 570 | 550 | 500 | 500 | 500 | 480 | 410 | 400 | 360 | 440 | 400 | 400 | 400 | 400 | 400 |  | 470 | 520 | 520 | 520 | 530 | 550 | 570 | 12650700
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 151 | 143 | 108 | 107 | 108 | 123 | 147 | 150 | 150 | 149 | 149 | 135 | 120 | 127 | 150 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3446300
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 50 | 50 | 50 |  |  |  | 0 | 93184
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 142 | 144 | 145 | 120 | 135 | 142 | 145 | 144 | 147 | 148 | 130 |  | 104 | 106 | 105 | 132 | 147 | 147 | 147 | 3366000
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 16 | 20 | 37 | 88 | 120 | 120 | 120 | 145 | 163 | 152 | 151 | 190 | 180 | 158 | 171 | 159 | 157 | 160 |  | 167 | 157 | 158 | 177 | 192 | 177 | 181 | 3627491
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 217 | 218 | 217 | 217 | 217 | 217 | 150 | [18 empty] | 0 | 1555627
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 330 | 330 | 325 | 330 | 360 | 320 | 360 | 415 | 398 | 359 | 375 | 405 | 310 | 316 | 402 | 363 | 361 | 350 |  | 352 | 371 | 365 | 395 | 385 | 405 | 395 | 8800636
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 5 |  | 34 | 12 | [5 empty] | 41832
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 494880
163 | Bogura 20 MW PP (Energyprima) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [15 empty] | 8 | 8 | 8 | 8 | 83124
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 241308
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | 36 | [16 empty] | 22 |  | 43 | 43 | 47 | 43 | 43 | 43 | 0 | 295910
168 | Santahar 50 MW Peaking PP | 31 | [16 empty] | 5 |  | 32 | 32 | 32 | 32 | 32 | 32 | 0 | 213491
169 | Natore 52 MW PP (Rajlanka) | 24 | [16 empty] | 2 |  | 26 | 52 | 52 | 52 | 52 |  | 0 | 223680
170 | Chapainawabganj 100 MW Peaking PP | 98 | 45 | [9 empty] | 15 | 22 | 24 | 24 | 24 | 32 | 75 |  | 97 | 97 | 88 | 97 | 97 | 97 | 97 | 922904
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 35 |  |  |  |  | 5 | 35 | 48 | 70 | 35 | 35 |  |  |  |  | 70 | 110 | 111 | 113 | 113 | 113 | 113 | 1470048
172 | Confidence Power Bogura Unit-1 113 MW | 109 | 109 | 109 | 109 | 109 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 90 | 50 | 50 |  | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 2139168
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 105 | 105 | 99 | 105 | 85 | 63 | 34 | 34 | 35 | 74 | 97 | 99 | 109 | 80 | 75 | 75 | 65 | 56 |  | 102 | 112 | 113 | 113 | 112 | 113 | 112 | 2099520
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 0 | 1 | 0 | 1 | 1 | 3 | 4 | 4 | 2 | 1 | 0 | [8 empty] | 16340
178
178