## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-08-20 | Tuesday
|  | Date (day): | 2019-08-20 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13082 | MW |  |  | (b) At Evening Peak Hour : |  | 15025 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-08-19 | 2019-08-20 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 70 | 70 | 70 | 70 |  | 15
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 190 | 189 | 190 | 190
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 350 | 380 | 350 | 350
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 25 | 73 | 50 | 75
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 70 | 83 | 90 | 90
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 20 | 20 | 20 | 20 | 20 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 361 | 349 | 350 | 350 |  |  | FGMO
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 346 | 354 | 300 | 300
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 360 | 360 | 350 | 350 |  |  | Machine problem
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 7 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 290 | 272 | 280 | 280 |  |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 125 | 190 | 100 | 150 | 60 |  | Gas shortage
| Siddhirganj Desh |  | HSD | QRPP | 96*1.2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217 | 217 | 217 | 0 | 0 | 0 | 0 |  | 217 | Under maint.
| Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 7 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 6 | 34 | 46 | 46 |  | 5 | Engine problem
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 149 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 55 | 72 | 72 | 72 |  | 36 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 41 | 43 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 25 | 34 | 51 | 51 |  | 10 | Engine problem
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 15 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 100 | 81 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 105 | 105 | 100 | 100
| Dhaka area Total |  |  |  |  | 5929 | 5693 | 2654 | 3118 | 3781 | 4456 | 185 | 791
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Under maint.
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 8 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 24 | 50 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 211 | 214 | 215 | 215
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 205 | 204 | 215 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 140 | 130 | 130 | 150
44 | Sikalbaha 51 MW PP(Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | Contract expired
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 50 | 100
46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D
47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 50 | 80
48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 10 | 100 | 100
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 22 | 100 | 100 | 100
50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 0 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 38 | 5 | 25
51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 51 | 95 | 97 |  | 11 | Engine problem
52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 6.8 | 0 | 4.4 | 0
53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 16 | 87 | 230 | 260
| Jodiac Power |  | HFO | IPP | 54.36 | 0 | 0 | 18 | 0 | 0 | 0
| Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 0 | 0 | 99 | 114 | 113 | 113 |  |  | RRT
| Chattogram area Total |  |  |  |  | 2113 | 2053 | 883.8 | 1174 | 1524.4 | 1652 | 260 | 109
54 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 |  |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 100 | 100 | 100 |  |  | Gas shortage
55 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 183 | 215 | 0 | 220
56 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 345 | 340 | 250 | 360 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 265 | 360 | 360 |  |  | FGMO
58 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 33 | 33 | 33 | 33 |  | 12 | Engine problem
59 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 50 | 53 | 52 | 52
60 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract expired
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 25 | 26 | 68 | 68 | 127 |  | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 100 | 150 | 150
64 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract expired
65 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
66 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 140 | 140 | 140 | 140
67 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 17 | 198 | 200 | 200
68 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 21 | 22 | 22
69 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 5 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 142 | 180 | 131 | 185
70 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 52 | 52 | 52
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 17 | 21 | 20 | 20 |  | 5 | Engine problem
73 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1444 | 1825 | 1665 | 2299 | 256 | 25
74 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 153 | 175 | 204 | 204
75 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
76 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 95 | 95 | 95
77 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.6 | 0 | 1.6 | 0
78 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 7 | 187 | 200 | 200
79 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 109 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 305.6 | 586 | 635.6 | 634 | 0 | 0
80 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 60 | 60 | 60
81 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 58 | 58 | 58 | 58
82 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
83 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 153 | 151 | 160 | 160 |  |  | FGMO
84 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 50 | 51 | 51
85 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 50 | 44 | 44
86 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
87 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 63 | 63 | 63 |  |  | FGMO
88 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 75 | 75 | 73 | 75
89 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 40 | 44 | 44 | 44 |  | 6 | Engine problem
90 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0 |  |  | under maint.
91 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 18 | 17 | 17 |  | 3 | Engine problem
92 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 39 | 45 | 42 | 43 |  | 7 | Engine problem
93 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
94 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 300 | 300 | 320 |  |  | FGMO
95 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285 MW | 285 | 285 | 0 | 15 | 80 | 80
96 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1879 | 1834 | 1087 | 1134 | 1200 | 1223 | 0 | 16
97 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 32
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 931 | 926 | 943 | 943
| Khulna 115 MW PP (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
98 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 99 | 115 | 115
99 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 31 | 0 | 42
100 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 200 | 200
101 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 65 | 0 | 75
102 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 350 | 300 | 320 | 410
103 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 8 | 40 | 40 | 40
| Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
104 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 80 | 100
105 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 105 | 105 | 105
106 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 88 | 87 | 50 | 100 |  | 5 | Engine problem
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 1394 | 1753 | 1853 | 2162 | 0 | 5
107 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 70 | 110
108 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
109 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 10 | 13 | 25 | 35
110 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 125 | 180 | 180 | 180
111 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 97 | 97 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 232 | 400 | 370 | 450 | 0 | 0
112 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 55 | 55 | 60 | 60
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
113 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 25 | 50 | 50
114 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 30
115 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 12 | 50 | 40 | 50
116 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 24 | 50 | 50 | 50
117 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 47 | 47
118 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 197 | 202 | 215 | 215 |  |  | FGMO
119 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas Shortage
120 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 200 | 193 | 205 | 215 |  |  | FGMO
121 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 370 | 392 | 400 | 400
122 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 0 | 35
123 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
124 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 16 | 16 | 16 | 15
125 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
126 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 52 | 52 | 52
127 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 95 | 80 | 100
128 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
129 | Bagura 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 101 | 96 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 1002 | 1289 | 1561 | 1665 | 220 | 100
130 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 92 | 90 | 90 | 90
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
131 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 280 | 275 | 280 | 280
132 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
133 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  |  | Under maint.
| Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 0 | 0 | 40 | 113 | 114 | 114
| Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 572 | 492 | 418 | 478 | 492 | 484 | 0 | 105
| Total |  |  |  |  | 18969 | 18446 | 9420.4 | 11757 | 13082 | 15025 | 921 | 1151
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8991.7265 | 11222 | 12486.7061 | 14341.2903
A. |  | 2019-08-19 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 11757 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 8108.7 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11757 | MW
3 | Day peak Generation : |  |  | 9420.4 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11222 | MW
4 | Evening peak Generation : |  |  | 11757 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 244.8763 | MKWHr | By Solar | 0.21762 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 159.7873 | MKWHr |  | By Oil: | 44.3289 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 9.6598 | MKWHr |  | By Hydro: | 4.9248 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 921 | MW | Dhaka | 3671 | 3671 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1151 | MW | Chittagong | 1209 | 1209 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2072 | MW | Khulna | 1440 | 1440 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1349.01 | MMCFD |  |  | Rajshahi | 1252 | 1252 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 155166545.452 | ii) Oil : | Taka | 352684450.66 | Comilla | 1072 | 1072 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 44519786.31 | Total | Taka | 552370782.422 | Mymensingh | 991 | 991 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.209 | MKWHr. | Sylhet | 496 | 496 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -100 | MW (E to W) at | 21:00 | hrs | Barisal | 338 | 338 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -100 | MW at | 21:00 | hrs | Rangpur | 753 | 753 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 34.6° C |  |  | Total | 11222 | 11222 |  | 0
B. |  | 2019-08-20 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 32.9° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12300 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15025 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10000 | MW
4 | Reserve(Generation end) |  |  |  | 2725 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 256.186 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8713.2 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.3004 | MKWHr. | ii) HVDC Flow at Peak Time |  | 926 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.6576 | MKWHr. | iii) Maximum HVDC Flow : |  | 932 | MW at | 9:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 105.76 |  | (b) Today: | 105.75 |  | (c) Rule Curve: |  | 95.08
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-08-19
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence) | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 70 | 190 | 0 | 0 | 320 | 84 | 75 | 344 | 300 |  | 20 | 360 | 265 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 20 | 0 | 40 | 0 | 47 | 0 | 0 | 0 | 22 | 25 | 18 | 33 | 33 | 8 | 0 | 121 | 90 | 100 | 0 | 8 | 204 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 10 | 50 | 22 | 38 | 80 | 0 | 100 | 18 | 305 | 181 | 8 | 138 | 33 | 54 | 0 | 43 | 0 | 0 | 43 | 21 | 11 | 29 | 20 | 156 | 185 | 90 | 20 | 0 | 58 | 58 | 50 | 50 | 130 | 152 | 54 | 76 | 44 | 109 | 17 | 45 | 10 | 270 | 24 | 8 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 100 | 200 | 0 | 0 | 115 | 105 | 0 | 0 | 105 | 0 | 50 |  | 929 | 0 | 330 | 0 | 59 | 0 | 0 | 0 | 40 | 20 | 40 | 154 | 33 | 80 | 0 | 0 | 55 | 0 | 0 | 94 | 12 | 50 | 0 | 8 | 22 | 22 | 16 | 11 | 93 | 0 | 270 | 0 | 0 | 180 | 0 | 0 | 0 | 95 | 40 | 188 | 0 | 340 | 105 | 0 | 113 | 88 | 107 | 0 | 0 |  | 6712 | 3594 | 10306 | 4190 | 929 | 2143 | 2118 | 363 | 211 | 196 | 156 | 0 | 0 | 105.76
2:00 | 70 | 104 | 0 | 0 | 320 | 84 | 75 | 353 | 300 |  | 20 | 360 | 270 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 22 | 25 | 13 | 33 | 33 | 0 | 0 | 121 | 90 | 100 | 0 | 0 | 204 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 38 | 80 | 0 | 100 | 15 | 305 | 181 | 8 | 138 | 33 | 55 | 0 | 43 | 0 | 0 | 24 | 21 | 11 | 29 | 20 | 154 | 187 | 90 | 20 | 0 | 60 | 58 | 50 | 50 | 130 | 152 | 64 | 76 | 44 | 109 | 17 | 45 | 10 | 290 | 24 | 8 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 70 | 125 | 0 | 0 | 115 | 105 | 0 | 0 | 72 | 0 | 50 |  | 929 | 0 | 330 | 0 | 49 | 0 | 0 | 0 | 36 | 0 | 40 | 153 | 33 | 64 | 0 | 0 | 55 | 0 | 0 | 94 | 12 | 50 | 0 | 0 | 22 | 22 | 16 | 11 | 92 | 0 | 270 | 0 | 0 | 181 | 0 | 0 | 0 | 96 | 18 | 186 | 0 | 335 | 105 | 0 | 113 | 87 | 107 | 0 | 0 |  | 6387 | 3506 | 9893 | 4117 | 929 | 2160 | 1792 | 362 | 211 | 168 | 154 | 0 | 0 | 105.76
3:00 | 70 | 190 | 0 | 0 | 320 | 84 | 50 | 346 | 300 |  | 20 | 360 | 245 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 22 | 25 | 13 | 33 | 33 | 0 | 0 | 121 | 90 | 100 | 0 | 0 | 205 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 38 | 80 | 0 | 100 | 22 | 305 | 181 | 8 | 139 | 33 | 56 | 0 | 5 | 0 | 0 | 16 | 21 | 11 | 29 | 20 | 156 | 191 | 90 | 20 | 0 | 60 | 58 | 50 | 50 | 100 | 152 | 65 | 73 | 44 | 109 | 17 | 45 | 10 | 290 | 24 | 8 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 40 | 90 | 0 | 0 | 115 | 90 | 0 | 0 | 70 | 0 | 50 |  | 929 | 0 | 330 | 0 | 16 | 0 | 0 | 0 | 36 | 0 | 40 | 154 | 35 | 48 | 0 | 0 | 55 | 0 | 0 | 75 | 12 | 50 | 0 | 0 | 22 | 22 | 16 | 8 | 91 | 0 | 270 | 0 | 0 | 182 | 0 | 0 | 0 | 96 | 0 | 187 | 0 | 341 | 105 | 0 | 113 | 87 | 107 | 0 | 0 |  | 6186 | 3427 | 9613 | 4210 | 929 | 2073 | 1540 | 361 | 211 | 133 | 156 | 0 | 0 | 105.76
4:00 | 70 | 189 | 0 | 0 | 320 | 84 | 50 | 350 | 300 |  | 20 | 360 | 260 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 22 | 25 | 13 | 33 | 33 | 0 | 0 | 121 | 90 | 100 | 0 | 0 | 204 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 38 | 80 | 0 | 100 | 70 | 305 | 181 | 8 | 138 | 33 | 56 | 0 | 5 | 0 | 0 | 16 | 21 | 11 | 29 | 20 | 154 | 192 | 90 | 20 | 0 | 60 | 58 | 5 | 50 | 100 | 151 | 64 | 73 | 44 | 110 | 17 | 45 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 10 | 70 | 0 | 0 | 115 | 71 | 0 | 0 | 70 | 0 | 50 |  | 928 | 0 | 330 | 0 | 16 | 0 | 0 | 0 | 36 | 0 | 40 | 154 | 35 | 48 | 0 | 0 | 60 | 0 | 0 | 65 | 12 | 50 | 0 | 0 | 22 | 22 | 16 | 8 | 91 | 0 | 270 | 0 | 0 | 186 | 0 | 0 | 0 | 96 | 0 | 187 | 0 | 334 | 105 | 0 | 113 | 88 | 107 | 0 | 0 |  | 6149 | 3419 | 9568 | 4273 | 928 | 2031 | 1487 | 361 | 211 | 123 | 154 | 0 | 0 | 105.76
5:00 | 70 | 189 | 0 | 0 | 320 | 84 | 50 | 348 | 300 |  | 20 | 360 | 265 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 22 | 25 | 13 | 33 | 33 | 0 | 0 | 121 | 90 | 100 | 0 | 0 | 205 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 38 | 80 | 0 | 100 | 90 | 320 | 193 | 8 | 138 | 33 | 56 | 0 | 5 | 0 | 0 | 16 | 21 | 11 | 29 | 20 | 144 | 191 | 91 | 20 | 0 | 60 | 58 | 5 | 5 | 100 | 152 | 64 | 73 | 44 | 110 | 17 | 14 | 10 | 290 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 10 | 70 | 0 | 0 | 115 | 71 | 0 | 0 | 15 | 0 | 50 |  | 929 | 0 | 330 | 0 | 10 | 0 | 0 | 0 | 19 | 0 | 40 | 146 | 30 | 48 | 0 | 0 | 60 | 0 | 0 | 65 | 12 | 50 | 0 | 0 | 0 | 22 | 16 | 8 | 91 | 0 | 270 | 0 | 0 | 188 | 0 | 0 | 0 | 96 | 0 | 187 | 0 | 368 | 70 | 0 | 37 | 88 | 107 | 0 | 0 |  | 5952 | 3287 | 9239 | 4308 | 929 | 1974 | 1228 | 361 | 211 | 84 | 144 | 0 | 0 | 105.76
6:00 | 70 | 189 | 0 | 0 | 270 | 12 | 25 | 345 | 280 |  | 20 | 360 | 265 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 22 | 25 | 13 | 33 | 33 | 0 | 0 | 121 | 90 | 100 | 0 | 0 | 205 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 38 | 80 | 0 | 100 | 100 | 305 | 181 | 8 | 138 | 33 | 55 | 0 | 5 | 0 | 0 | 0 | 21 | 11 | 29 | 20 | 136 | 192 | 16 | 20 | 0.1 | 60 | 58 | 5 | 5 | 100 | 152 | 51 | 10 | 10 | 110 | 17 | 14 | 10 | 270 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 10 | 50 | 0 | 0 | 115 | 53 | 0 | 0 | 15 | 0 | 50 |  | 929 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 151 | 10 | 0 | 0 | 0 | 60 | 0 | 0 | 25 | 12 | 24 | 0 | 0 | 0 | 22 | 16 | 8 | 92 | 0 | 270 | 0 | 0 | 190 | 0 | 0 | 0 | 62 | 0 | 191 | 0 | 312 | 35 | 0 | 37 | 47 | 107 | 0 | 0 |  | 5458.1 | 2938 | 8396.1 | 4197 | 929 | 1629 | 907 | 362 | 211 | 25 | 136 | 0.1 | 0 | 105.76
7:00 | 70 | 189 | 0 | 0 | 270 | 13 | 25 | 345 | 240 |  | 20 | 300 | 260 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 25 | 13 | 33 | 33 | 0 | 0 | 123 | 90 | 100 | 0 | 0 | 206 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 27 | 80 | 0 | 100 | 125 | 305 | 181 | 8 | 138 | 33 | 55 | 0 | 5 | 0 | 0 | 0 | 21 | 11 | 29 | 20 | 122 | 191 | 8 | 20 | 0.7 | 60 | 58 | 5 | 5 | 100 | 153 | 63 | 10 | 10 | 123 | 17 | 12 | 10 | 275 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 3.7 | 10 | 17 | 0 | 0 | 80 | 53 | 0 | 1.2 | 15 | 0 | 50 |  | 928 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 152 | 11 | 0 | 0 | 0 | 60 | 0 | 0 | 25 | 12 | 24 | 0 | 0 | 0 | 22 | 16 | 8 | 92 | 0 | 270 | 0 | 0 | 174 | 0 | 0 | 0 | 62 | 0 | 174 | 0 | 370 | 17 | 0 | 37 | 35 | 35 | 0 | 0.1 |  | 5276.6 | 2832.1 | 8108.7 | 4164 | 928 | 1581 | 708 | 362 | 213 | 25 | 122 | 5.7 | 0 | 105.76
8:00 | 70 | 189 | 0 | 0 | 270 | 13 | 25 | 346 | 240 |  | 20 | 300 | 265 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 25 | 13 | 33 | 33 | 0 | 0 | 124 | 90 | 100 | 0 | 0 | 206 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 4 | 80 | 0 | 100 | 225 | 310 | 186 | 8 | 138 | 33 | 54 | 0 | 5 | 0 | 0 | 0 | 21 | 11 | 29 | 17 | 124 | 173 | 8 | 20 | 0.6 | 60 | 58 | 5 | 5 | 100 | 152 | 62 | 10 | 10 | 118 | 17 | 15 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 10 | 10 | 17 | 0 | 0 | 80 | 53 | 0 | 2.68 | 15 | 0 | 50 |  | 929 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 153 | 10 | 0 | 0 | 0 | 60 | 0 | 0 | 24 | 12 | 24 | 0 | 0 | 0 | 22 | 16 | 8 | 92 | 0 | 280 | 0 | 0 | 162 | 0 | 0 | 0 | 97 | 0 | 173 | 0 | 382 | 17 | 0 | 37 | 35 | 35 | 0 | 0 |  | 5375.28 | 2876 | 8251.28 | 4235 | 929 | 1631 | 709 | 372 | 214 | 24 | 124 | 13.28 | 0 | 0
9:00 | 70 | 189 | 0 | 0 | 270 | 13 | 25 | 355 | 274 |  | 20 | 300 | 268 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 26 | 0 | 0 | 0 | 22 | 25 | 13 | 33 | 33 | 17 | 0 | 124 | 90 | 100 | 0 | 0 | 207 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 7 | 22 | 2 | 80 | 0 | 100 | 368 | 320 | 196 | 8 | 140 | 33 | 54 | 0 | 5 | 0 | 0 | 0 | 21 | 11 | 33 | 17 | 130 | 170 | 8 | 20 | 0.6 | 60 | 58 | 5 | 5 | 100 | 153 | 61 | 10 | 10 | 123 | 17 | 12 | 10 | 315 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 9 | 15 | 10 | 17 | 0 | 0 | 80 | 105 | 0 | 4.14 | 15 | 0 | 50 |  | 932 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 153 | 10 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 12 | 8 | 0 | 0 | 0 | 22 | 16 | 8 | 92 | 0 | 280 | 0 | 0 | 171 | 0 | 0 | 0 | 97 | 0 | 172 | 0 | 385 | 17 | 0 | 37 | 36 | 35 | 0 | 2 |  | 5746.74 | 2853 | 8599.74 | 4446 | 932 | 1678 | 806 | 372 | 214 | 0 | 130 | 21.74 | 0 | 0
10:00 | 70 | 189 | 0 | 0 | 380 | 13 | 25 | 378 | 324 |  | 20 | 360 | 285 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 26 | 0 | 0 | 0 | 22 | 25 | 13 | 33 | 33 | 25 | 0 | 117 | 90 | 100 | 0 | 0 | 205 | 0 | 140 | 0 |  | 0 | 0 | 0 | 10 | 0 | 24 | 0 | 2 | 80 | 0 | 100 | 365 | 330 | 202 | 8 | 135 | 33 | 53 | 0 | 5 | 0 | 0 | 0 | 21 | 11 | 0 | 17 | 136 | 165 | 8 | 20 | 1.9 | 60 | 58 | 5 | 9 | 100 | 150 | 61 | 10 | 40 | 0 | 17 | 36 | 10 | 320 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 50 | 7 | 10 | 17 | 0 | 0 | 80 | 105 | 0 | 2.12 | 30 | 11 | 50 |  | 931 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 152 | 10 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 8 | 0 | 0 | 0 | 22 | 16 | 8 | 92 | 0 | 280 | 0 | 0 | 197 | 0 | 0 | 0 | 96 | 0 | 189 | 0 | 387 | 17 | 0 | 37 | 36 | 35 | 0 | 2.8 |  | 6001.02 | 2940.8 | 8941.82 | 4516 | 931 | 1851 | 915 | 372 | 207 | 0 | 136 | 13.82 | 0 | 0
11:00 | 70 | 189 | 0 | 0 | 350 | 13 | 25 | 348 | 340 |  | 20 | 360 | 300 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 9 | 5 | 0 | 0 | 22 | 25 | 13 | 33 | 33 | 25 | 0 | 118 | 90 | 100 | 0 | 0 | 206 | 0 | 140 | 0 |  | 0 | 0 | 0 | 10 | 0 | 24 | 22 | 2 | 30 | 0 | 80 | 345 | 320 | 174 | 25 | 140 | 33 | 50 | 0 | 15 | 0 | 0 | 0 | 21 | 11 | 0 | 17 | 140 | 150 | 8 | 20 | 2.5 | 60 | 58 | 50 | 47 | 130 | 151 | 61 | 75 | 40 | 0 | 17 | 39 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 100 | 20 | 10 | 17 | 0 | 0 | 115 | 105 | 0 | 3.52 | 15 | 18 | 92 |  | 931 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 152 | 10 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 8 | 0 | 0 | 0 | 22 | 16 | 5 | 92 | 0 | 280 | 0 | 0 | 188 | 0 | 0 | 0 | 96 | 0 | 200 | 0 | 370 | 17 | 0 | 37 | 58 | 38 | 0 | 2 |  | 6190.02 | 2947 | 9137.02 | 4361 | 931 | 2035 | 1062 | 372 | 208 | 0 | 140 | 28.02 | 0 | 0
12:00 | 70 | 190 | 0 | 0 | 350 | 70 | 25 | 361 | 346 |  | 20 | 360 | 290 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 6 | 35 | 0 | 0 | 22 | 25 | 16 | 25 | 33 | 25 | 0 | 121 | 90 | 100 | 0 | 0 | 205 | 0 | 140 | 0 |  | 0 | 0 | 0 | 10 | 0 | 24 | 22 | 2 | 0 | 0 | 80 | 345 | 305 | 183 | 25 | 140 | 33 | 50 | 0 | 43 | 0 | 0 | 0 | 20 | 11 | 33 | 17 | 142 | 153 | 8 | 20 | 2.6 | 60 | 58 | 47 | 50 | 130 | 153 | 61 | 75 | 40 | 0 | 17 | 39 | 10 | 315 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 100 | 8 | 22 | 17 | 0 | 0 | 115 | 105 | 0 | 6.8 | 16 | 18 | 99 |  | 931 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 125 | 10 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 24 | 0 | 0 | 0 | 22 | 16 | 5 | 92 | 0 | 280 | 0 | 0 | 197 | 0 | 0 | 0 | 97 | 0 | 200 | 0 | 370 | 17 | 0 | 101 | 88 | 40 | 0 | 6 |  | 6374.4 | 3046 | 9420.4 | 4357 | 931 | 2142 | 1242 | 372 | 211 | 0 | 142 | 23.4 | 0 | 0
13:00 | 70 | 189 | 0 | 0 | 350 | 78 | 60 | 365 | 342 |  | 20 | 360 | 301 | 0 | 0 | 0 | 0 | 0 | 127 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 6 | 35 | 0 | 0 | 22 | 25 | 7 | 25 | 33 | 30 | 0 | 122 | 90 | 100 | 0 | 0 | 205 | 0 | 140 | 0 |  | 0 | 0 | 0 | 10 | 0 | 24 | 22 | 10 | 0 | 0 | 90 | 363 | 320 | 187 | 25 | 139 | 33 | 52 | 0 | 43 | 0 | 0 | 0 | 20 | 11 | 33 | 17 | 142 | 156 | 8 | 20 | 1.1 | 60 | 58 | 50 | 47 | 130 | 152 | 60 | 75 | 42 | 0 | 17 | 42 | 10 | 315 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 100 | 14 | 50 | 17 | 0 | 0 | 115 | 105 | 0 | 5.42 | 16 | 17 | 111 |  | 931 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 100 | 10 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 24 | 0 | 0 | 0 | 22 | 16 | 8 | 92 | 0 | 280 | 0 | 0 | 196 | 0 | 0 | 0 | 93 | 0 | 203 | 0 | 385 | 78 | 0 | 111 | 87 | 42 | 0 | 2 |  | 6547.52 | 3005 | 9552.52 | 4280 | 931 | 2207 | 1386 | 372 | 212 | 0 | 142 | 22.52 | 0 | 0
14:00 | 70 | 188 | 0 | 0 | 350 | 84 | 71 | 366 | 340 |  | 20 | 360 | 280 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 6 | 35 | 17 | 0 | 22 | 25 | 12 | 25 | 33 | 51 | 0 | 117 | 90 | 100 | 0 | 0 | 205 | 0 | 140 | 0 |  | 0 | 0 | 0 | 10 | 0 | 25 | 22 | 5 | 0 | 0 | 100 | 347 | 310 | 190 | 26 | 139 | 33 | 52 | 0 | 43 | 0 | 0 | 0 | 20 | 8 | 33 | 17 | 154 | 156 | 12 | 20 | 2.1 | 60 | 58 | 50 | 47 | 163 | 153 | 59 | 75 | 42 | 0 | 17 | 42 | 10 | 310 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 100 | 17.6 | 85 | 18 | 0 | 0 | 115 | 105 | 0 | 4.7 | 16 | 0 | 114 |  | 931 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 100 | 10 | 48 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 24 | 0 | 0 | 0 | 22 | 16 | 8 | 92 | 0 | 280 | 0 | 0 | 195 | 0 | 0 | 0 | 94 | 0 | 208 | 0 | 383 | 89 | 0 | 112 | 87 | 76 | 0 | 7.1 |  | 6688.4 | 3107.1 | 9795.5 | 4331 | 931 | 2245 | 1524 | 372 | 207 | 0 | 154 | 31.5 | 0 | 0
15:00 | 70 | 189 | 0 | 0 | 370 | 84 | 70 | 373 | 340 |  | 20 | 360 | 270 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 6 | 35 | 17 | 0 | 22 | 25 | 13 | 33 | 33 | 50 | 0 | 113 | 90 | 100 | 0 | 0 | 203 | 0 | 140 | 0 |  | 0 | 0 | 0 | 10 | 0 | 38 | 22 | 3 | 0 | 0 | 100 | 360 | 335 | 203 | 26 | 140 | 33 | 51 | 0 | 43 | 0 | 0 | 8 | 20 | 8 | 33 | 17 | 156 | 156 | 18 | 20 | 1.4 | 60 | 58 | 50 | 45 | 163 | 152 | 59 | 74 | 42 | 0 | 17 | 41 | 10 | 325 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 105 | 15.2 | 80 | 68 | 25 | 14 | 115 | 105 | 0 | 3.9 | 16 | 0 | 114 |  | 931 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 180 | 12 | 48 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 24 | 0 | 0 | 0 | 22 | 15 | 8 | 91 | 0 | 280 | 0 | 0 | 202 | 0 | 0 | 0 | 95 | 0 | 209 | 0 | 399 | 90 | 0 | 113 | 88 | 107 | 0 | 2.9 |  | 6886.5 | 3249.9 | 10136.4 | 4525 | 931 | 2270 | 1657 | 371 | 203 | 0 | 156 | 23.4 | 0 | 0
16:00 | 70 | 189 | 0 | 0 | 370 | 80 | 71 | 354 | 340 |  | 20 | 360 | 280 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 6 | 53 | 35 | 0 | 22 | 25 | 13 | 33 | 33 | 50 | 0 | 106 | 90 | 100 | 0 | 0 | 203 | 0 | 140 | 0 |  | 0 | 0 | 0 | 10 | 0 | 50 | 22 | 5 | 0 | 0 | 100 | 345 | 305 | 181 | 26 | 132 | 33 | 51 | 0 | 43 | 0 | 0 | 25 | 0 | 11 | 33 | 17 | 148 | 157 | 50 | 20 | 1.6 | 60 | 58 | 50 | 46 | 163 | 152 | 61 | 74 | 42 | 0 | 17 | 41 | 10 | 290 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 127 | 10.5 | 78 | 105 | 50 | 15 | 115 | 105 | 0 | 0.9 | 16 | 0 | 114 |  | 931 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 179 | 11 | 48 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 24 | 0 | 0 | 0 | 22 | 15 | 8 | 91 | 0 | 280 | 0 | 0 | 201 | 0 | 0 | 0 | 93 | 0 | 208 | 0 | 346 | 90 | 0 | 113 | 87 | 109 | 0 | 4.4 |  | 6899 | 3220.4 | 10119.4 | 4403 | 931 | 2179 | 1871 | 371 | 196 | 3 | 148 | 17.4 | 0 | 0
17:00 | 70 | 189 | 0 | 0 | 300 | 80 | 50 | 353 | 304 |  | 20 | 360 | 282 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 6 | 53 | 17 | 0 | 22 | 25 | 13 | 33 | 33 | 50 | 0 | 106 | 90 | 100 | 0 | 0 | 204 | 0 | 140 | 0 |  | 0 | 0 | 0 | 10 | 0 | 50 | 22 | 14 | 0 | 0 | 100 | 345 | 305 | 182 | 26 | 130 | 33 | 50 | 0 | 43 | 0 | 0 | 25 | 15 | 11 | 33 | 18 | 144 | 160 | 17 | 20 | 0.4 | 60 | 58 | 50 | 46 | 100 | 152 | 62 | 74 | 42 | 0 | 18 | 43 | 10 | 280 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 134 | 3.4 | 40 | 105 | 10 | 15 | 108 | 105 | 0 | 1.2 | 16 | 0 | 114 |  | 931 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 179 | 11 | 16 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 24 | 0 | 0 | 0 | 22 | 15 | 8 | 91 | 0 | 280 | 0 | 0 | 184 | 0 | 0 | 0 | 95 | 0 | 180 | 0 | 286 | 35 | 0 | 56 | 87 | 65 | 0 | 2.3 |  | 6506 | 2912.3 | 9418.3 | 4224 | 931 | 2001 | 1524 | 371 | 196 | 20 | 144 | 7.3 | 0 | 0
18:00 | 70 | 189 | 0 | 0 | 300 | 52 | 50 | 346 | 274 |  | 20 | 360 | 256 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 6 | 53 | 17 | 0 | 22 | 25 | 13 | 33 | 33 | 50 | 0 | 107 | 90 | 100 | 0 | 1 | 204 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 0 | 50 | 22 | 16 | 0 | 0 | 100 | 260 | 260 | 181 | 26 | 140 | 27 | 15 | 0 | 43 | 0 | 0 | 25 | 19 | 11 | 10 | 18 | 142 | 163 | 16 | 20 | 0 | 60 | 58 | 11 | 10 | 100 | 151 | 59 | 10 | 10 | 0 | 18 | 10 | 10 | 280 | 24 | 8 | 0 | 0 | 0 | 0 | 14 | 0 | 149 | 0.5 | 40 | 105 | 10 | 80 | 115 | 105 | 0 | 0.2 | 16 | 0 | 114 |  | 932 | 0 | 250 | 0 | 3 | 0 | 0 | 0 | 0 | 41 | 8 | 180 | 11 | 16 | 0 | 0 | 55 | 0 | 10 | 0 | 12 | 24 | 0 | 0 | 0 | 22 | 15 | 8 | 93 | 0 | 280 | 0 | 0 | 170 | 0 | 0 | 0 | 24 | 0 | 169 | 0 | 288 | 35 | 0 | 56 | 53 | 55 | 0 | 0.7 |  | 6079.7 | 2810.7 | 8890.4 | 4071 | 932 | 1637 | 1486 | 373 | 197 | 51 | 142 | 1.4 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 70 | 189 | 0 | 0 | 380 | 84 | 50 | 350 | 304 |  | 20 | 360 | 270 | 1 | 0 | 0 | 0 | 0 | 90 | 0 | 5 | 24 | 80 | 3 | 72 | 0 | 6 | 53 | 55 | 35 | 22 | 25 | 13 | 33 | 33 | 50 | 0 | 124 | 90 | 100 | 0 | 14 | 203 | 0 | 130 | 0 |  | 0 | 0 | 51 | 40 | 50 | 50 | 22 | 30 | 0 | 20 | 100 | 320 | 265 | 214 | 26 | 130 | 33 | 15 | 0 | 43 | 0 | 42 | 25 | 19 | 11 | 33 | 18 | 176 | 163 | 56 | 20 | 0 | 60 | 58 | 41 | 19 | 130 | 151 | 63 | 75 | 43 | 0 | 18 | 43 | 5 | 290 | 24 | 8 | 0 | 11 | 0 | 0 | 81 | 0 | 149 | 0 | 100 | 137 | 50 | 80 | 109 | 105 | 0 | 0 | 55 | 0 | 114 |  | 931 | 0 | 250 | 0 | 109 | 0 | 0 | 0 | 0 | 80 | 40 | 180 | 35 | 110 | 23 | 0 | 55 | 50 | 15 | 95 | 50 | 50 | 29 | 52 | 26 | 22 | 16 | 8 | 93 | 0 | 280 | 0 | 0 | 171 | 0 | 0 | 0 | 92 | 3 | 167 | 0 | 356 | 90 | 0 | 90 | 88 | 113 | 0 | 0 |  | 7329 | 3769 | 11098 | 4319 | 931 | 2079 | 2515 | 373 | 214 | 491 | 176 | 0 | 0 | 0
19:30 | 70 | 189 | 0 | 0 | 380 | 84 | 73 | 345 | 304 |  | 20 | 360 | 246 | 7 | 0 | 15 | 0 | 0 | 90 | 0 | 0 | 50 | 149 | 0 | 72 | 0 | 25 | 53 | 55 | 35 | 22 | 25 | 13 | 33 | 33 | 50 | 0 | 124 | 90 | 100 | 0 | 25 | 202 | 0 | 130 | 0 |  | 0 | 0 | 51 | 10 | 55 | 50 | 22 | 37 | 0 | 0 | 100 | 340 | 265 | 215 | 26 | 131 | 33 | 52 | 0 | 43 | 0 | 0 | 52 | 0 | 0 | 33 | 20 | 178 | 163 | 95 | 20 | 0 | 60 | 58 | 50 | 46 | 163 | 151 | 58 | 75 | 43 | 0 | 18 | 42 | 10 | 270 | 24 | 8 | 0 | 64 | 0 | 0 | 185 | 0 | 149 | 0 | 100 | 200 | 100 | 15 | 109 | 105 | 0 | 0 | 82 | 0 | 114 |  | 932 | 0 | 250 | 0 | 115 | 0 | 0 | 0 | 0 | 75 | 40 | 180 | 35 | 110 | 23 | 0 | 55 | 25 | 0 | 95 | 50 | 50 | 36 | 52 | 30 | 22 | 16 | 11 | 92 | 0 | 280 | 0 | 0 | 189 | 0 | 0 | 0 | 95 | 100 | 185 | 0 | 341 | 90 | 0 | 95 | 87 | 113 | 0 | 0 |  | 7759 | 3869 | 11628 | 4256 | 932 | 2187 | 3005 | 372 | 214 | 484 | 178 | 0 | 0 | 0
20:00 | 70 | 189 | 0 | 0 | 380 | 84 | 74 | 345 | 305 |  | 20 | 360 | 276 | 30 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 24 | 149 | 0 | 72 | 0 | 15 | 53 | 55 | 35 | 22 | 25 | 13 | 33 | 33 | 43 | 0 | 124 | 90 | 100 | 0 | 25 | 204 | 0 | 130 | 0 |  | 0 | 0 | 51 | 10 | 55 | 50 | 22 | 38 | 0 | 0 | 100 | 340 | 265 | 214 | 26 | 140 | 33 | 52 | 0 | 43 | 0 | 0 | 52 | 13 | 0 | 33 | 21 | 180 | 163 | 95 | 20 | 0 | 60 | 58 | 50 | 50 | 100 | 151 | 63 | 75 | 44 | 0 | 18 | 45 | 10 | 270 | 24 | 8 | 0 | 15 | 0 | 0 | 185 | 0 | 149 | 0 | 100 | 199 | 100 | 15 | 109 | 105 | 0 | 0 | 83 | 0 | 114 |  | 926 | 0 | 250 | 0 | 115 | 0 | 0 | 0 | 2 | 75 | 40 | 180 | 14 | 110 | 23 | 0 | 55 | 25 | 0 | 95 | 50 | 50 | 0 | 52 | 30 | 22 | 16 | 11 | 91 | 0 | 280 | 0 | 0 | 193 | 0 | 0 | 0 | 96 | 97 | 183 | 0 | 379 | 90 | 0 | 95 | 87 | 113 | 0 | 0 |  | 7689 | 3845 | 11534 | 4292 | 926 | 2153 | 2948 | 371 | 214 | 450 | 180 | 0 | 0 | 0
21:00 | 70 | 189 | 0 | 0 | 380 | 83 | 73 | 349 | 354 |  | 20 | 360 | 272 | 7 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 7 | 149 | 0 | 72 | 0 | 34 | 53 | 55 | 35 | 22 | 25 | 18 | 33 | 33 | 34 | 0 | 124 | 90 | 100 | 0 | 25 | 204 | 0 | 130 | 0 |  | 0 | 0 | 51 | 10 | 51 | 50 | 0 | 38 | 0 | 0 | 100 | 340 | 265 | 215 | 26 | 140 | 33 | 53 | 0 | 43 | 0 | 0 | 52 | 21 | 5 | 33 | 21 | 180 | 175 | 95 | 20 | 0 | 60 | 58 | 50 | 50 | 163 | 151 | 63 | 75 | 44 | 0 | 18 | 45 | 10 | 300 | 24 | 8 | 0 | 15 | 0 | 0 | 187 | 0 | 81 | 0 | 100 | 198 | 100 | 15 | 109 | 105 | 0 | 0 | 87 | 0 | 114 |  | 926 | 0 | 300 | 0 | 99 | 0 | 0 | 0 | 31 | 65 | 40 | 180 | 13 | 110 | 0 | 0 | 55 | 25 | 0 | 95 | 50 | 50 | 0 | 52 | 30 | 22 | 16 | 11 | 90 | 0 | 275 | 0 | 0 | 202 | 0 | 0 | 0 | 97 | 100 | 193 | 0 | 392 | 105 | 0 | 96 | 87 | 113 | 0 | 0 |  | 7837 | 3920 | 11757 | 4469 | 926 | 2307 | 2850 | 365 | 214 | 446 | 180 | 0 | 0 | 0
22:00 | 70 | 189 | 0 | 0 | 380 | 84 | 74 | 345 | 355 |  | 20 | 360 | 260 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 7 | 136 | 0 | 72 | 0 | 39 | 53 | 55 | 35 | 22 | 25 | 22 | 33 | 33 | 43 | 0 | 124 | 90 | 100 | 0 | 25 | 203 | 0 | 130 | 0 |  | 0 | 0 | 51 | 10 | 51 | 50 | 21 | 39 | 0 | 0 | 100 | 340 | 265 | 215 | 26 | 130 | 33 | 55 | 0 | 43 | 0 | 0 | 52 | 21 | 5 | 33 | 20 | 180 | 174 | 95 | 20 | 0 | 60 | 58 | 50 | 50 | 163 | 150 | 63 | 75 | 44 | 0 | 18 | 45 | 10 | 290 | 8 | 8 | 0 | 2 | 0 | 0 | 194 | 0 | 81 | 0 | 100 | 198 | 0 | 80 | 109 | 107 | 0 | 0 | 88 | 0 | 114 |  | 926 | 0 | 300 | 0 | 68 | 0 | 0 | 0 | 34 | 65 | 40 | 180 | 33 | 110 | 0 | 0 | 60 | 25 | 0 | 95 | 50 | 50 | 0 | 52 | 22 | 22 | 16 | 11 | 91 | 0 | 270 | 0 | 0 | 200 | 0 | 0 | 0 | 97 | 100 | 195 | 0 | 378 | 105 | 0 | 95 | 87 | 112 | 0 | 0 |  | 7763 | 3889 | 11652 | 4525 | 926 | 2309 | 2709 | 361 | 214 | 428 | 180 | 0 | 0 | 0
23:00 | 70 | 189 | 0 | 0 | 340 | 84 | 74 | 345 | 320 |  | 20 | 360 | 285 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 100 | 0 | 72 | 0 | 39 | 53 | 18 | 17 | 22 | 25 | 22 | 33 | 33 | 43 | 0 | 124 | 90 | 100 | 0 | 25 | 205 | 0 | 130 | 0 |  | 0 | 0 | 51 | 10 | 51 | 50 | 22 | 40 | 0 | 0 | 100 | 345 | 275 | 214 | 26 | 137 | 33 | 55 | 0 | 43 | 0 | 0 | 52 | 21 | 5 | 33 | 21 | 176 | 174 | 95 | 20 | 0 | 60 | 58 | 50 | 50 | 163 | 151 | 63 | 75 | 44 | 0 | 18 | 45 | 10 | 290 | 16 | 8 | 0 | 0 | 0 | 0 | 194 | 0 | 60 | 0 | 100 | 200 | 0 | 80 | 109 | 107 | 0 | 0 | 88 | 0 | 112 |  | 927 | 0 | 300 | 0 | 66 | 0 | 0 | 0 | 31 | 64 | 33 | 180 | 39 | 110 | 0 | 0 | 60 | 25 | 0 | 93 | 50 | 24 | 0 | 52 | 22 | 22 | 16 | 11 | 90 | 0 | 270 | 0 | 0 | 190 | 0 | 0 | 0 | 98 | 100 | 196 | 0 | 410 | 105 | 0 | 102 | 87 | 108 | 0 | 0 |  | 7628 | 3881 | 11509 | 4515 | 927 | 2314 | 2617 | 360 | 214 | 386 | 176 | 0 | 0 | 0
24:00 | 70 | 189 | 0 | 0 | 340 | 84 | 74 | 345 | 320 |  | 20 | 360 | 285 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 149 | 0 | 72 | 0 | 11 | 53 | 18 | 17 | 22 | 25 | 20 | 33 | 33 | 43 | 0 | 124 | 90 | 100 | 0 | 25 | 204 | 0 | 130 | 0 |  | 0 | 0 | 51 | 10 | 51 | 50 | 22 | 40 | 0 | 0 | 100 | 340 | 265 | 215 | 26 | 131 | 33 | 55 | 0 | 43 | 0 | 0 | 52 | 21 | 5 | 33 | 20 | 174 | 188 | 95 | 20 | 0 | 60 | 58 | 50 | 50 | 163 | 149 | 63 | 75 | 44 | 0 | 18 | 45 | 10 | 315 | 24 | 8 | 0 | 0 | 0 | 0 | 185 | 0 | 20 | 0 | 100 | 200 | 0 | 79 | 109 | 107 | 0 | 0 | 88 | 0 | 115 |  | 926 | 0 | 300 | 0 | 66 | 0 | 0 | 0 | 31 | 64 | 33 | 180 | 38 | 96 | 0 | 0 | 60 | 25 | 0 | 93 | 12 | 24 | 0 | 52 | 22 | 22 | 16 | 11 | 88 | 0 | 270 | 0 | 0 | 180 | 0 | 0 | 0 | 97 | 100 | 192 | 0 | 400 | 105 | 0 | 113 | 87 | 113 | 0 | 0 |  | 7591 | 3816 | 11407 | 4466 | 926 | 2327 | 2507 | 358 | 214 | 435 | 174 | 0 | 0 | 0
KWH | 1528000 | 4819600 | 0 | 0 | 7866673 | 1521136 | 1345344 | 8589456 | 7389000 |  | 485500 | 8416750 | 6607273 | 47040 | 0 | 11571 | 0 | 0 | 3297000 | 0 | 8640 | 85680 | 700320 | 5583 | 992640 | 0 | 603408 | 632880 | 363973 | 184469 | 436608 | 600000 | 356760 | 790700 | 798100 | 670140 | 0 | 2772802 | 2152000 | 2300000 | 0 | 151938 | 4908684 | 0 | 3199156 | 0 |  | 0 | 0 | 282110 | 273000 | 354240 | 694560 | 486288 | 576480 | 879854 | 9895 | 2364248 | 6358000 | 7364000 | 4678000 | 468363 | 3255700 | 758448 | 1224000 | 0 | 756452 | 0 | 64067 | 518587 | 428796 | 220320 | 680900 | 445760 | 3657600 | 4040120 | 1248000 | 455580 | 14700 | 1422000 | 1365360 | 802800 | 875952 | 3257803 | 3352000 | 1453344 | 1416960 | 831240 | 5316631 | 432770 | 836400 | 246240 | 7397500 | 522408 | 190416 | 0 | 87818 | 0 | 0 | 1828800 | 0 | 1546560 | 134325 | 1291200 | 2343360 | 376363 | 356000 | 2564400 | 2299380 | 0 | 37080 | 1109018 | 74010 | 2062463 |  | 22300364 | 0 | 7687296 | 0 | 685440 | 0 | 0 | 0 | 292800 | 474368 | 579750 | 3806531 | 458228 | 1100160 | 56016 | 0 | 1370000 | 165304 | 19166 | 976072 | 492430 | 821324 | 40474 | 318240 | 228099 | 511440 | 372312 | 112526 | 2197963 | 0 | 7461800 | 0 | 0 | 4775345 | 0 | 0 | 0 | 2146194 | 591360 | 4778827 | 0 | 9593090 | 1610400 | 0 | 2025984 | 1794240 | 1973760 | 0 | 31514 |  | 163027493 | 81848817 | 244876310 | 109343600 | 22300364 | 50443684 | 41030082 | 9659763 | 4924802 | 3298796 | 3657600 | 217619 | 0
Fuel Cost | 1711360 | 5205168 | 0 | 0 | 5821338.02 | 1475501.92 | 1964202.24 | 6184408.32 | 5615640 |  | 859335 | 6733400 | 5946545.7 | 479808 | 0 | 118718.46 | 0 | 0 | 4121250 | 0 | 95904 | 870508.8 | 6940171.2 | 58509.84 | 9033024 | 0 | 5647898.88 | 6069319.2 | 3472302.42 | 1837311.24 | 327456 | 450000 | 0 | 0 | 0 | 6419941.2 | 0 | 720928.52 | 559520 | 3519000 | 0 | 1460124.18 | 5154118.2 | 0 | 4062928.12 | 0 |  | 0 | 0 | 2959333.9 | 2809170 | 3368822.4 | 6501081.6 | 447384.96 | 1602614.4 | 923846.7 | 10389.75 | 2482460.4 | 4704920 | 6185760 | 4303760 | 458995.74 | 4330081 | 621927.36 | 1260720 | 0 | 1081726.36 | 0 | 750865.24 | 4874717.8 | 437371.92 | 165240 | 1286901 | 334320 | 25237440 | 3312898.4 | 11868480 | 464691.6 | 241080 | 1933920 | 1856889.6 | 1091808 | 1094940 | 4039675.72 | 3083840 | 2165482.56 | 2493849.6 | 922676.4 | 8081279.12 | 688104.3 | 978588 | 578664 | 5252225 | 391806 | 144716.16 | 0 | 919454.46 | 0 | 0 | 17593056 | 0 | 15604790.4 | 1550110.5 | 12033984 | 21980716.8 | 3526521.31 | 334640 | 22489788 | 20487475.8 | 0 | 0 | 10225145.96 | 0 | 0 |  | 60210982.8 | 0 | 5996090.88 | 0 | 6607641.6 | 0 | 0 | 0 | 3396480 | 6214220.8 | 5733727.5 | 3045224.8 | 710253.4 | 11815718.4 | 1856930.4 | 0 | 2575600 | 1841486.56 | 234783.5 | 9663112.8 | 5106499.1 | 9617704.04 | 487711.7 | 3169670.4 | 2246775.15 | 562584 | 614314.8 | 85182.182 | 14001024.31 | 0 | 30518762 | 0 | 0 | 4202303.6 | 0 | 0 | 0 | 3412448.46 | 9993984 | 4205367.76 | 0 | 7002955.7 | 15234384 | 0 | 18598533.12 | 15986678.4 | 18434918.4 | 0 | 0 |  | 357506789.68 | 283384054.562 | 640890844.242 | 106218761.712 | 60210982.8 | 48947783.74 | 316092579.41 | 44519786.31 | 1280448.52 | 36591871.25 | 25237440 | 1791190.5 | 0
Yesterday Day Peak | 70 | 190 | 0 | 0 | 350 | 70 | 25 | 361 | 346 |  | 20 | 360 | 290 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 6 | 35 | 0 | 0 | 22 | 25 | 16 | 25 | 33 | 25 | 0 | 121 | 90 | 100 | 0 | 0 | 205 | 0 | 140 | 0 |  | 0 | 0 | 0 | 10 | 0 | 24 | 22 | 2 | 0 | 0 | 80 | 345 | 305 | 183 | 25 | 140 | 33 | 50 | 0 | 43 | 0 | 0 | 0 | 20 | 11 | 33 | 17 | 142 | 153 | 8 | 20 | 2.6 | 60 | 58 | 47 | 50 | 130 | 153 | 61 | 75 | 40 | 0 | 17 | 39 | 10 | 315 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 100 | 8 | 22 | 17 | 0 | 0 | 115 | 105 | 0 | 6.8 | 16 | 18 | 99 |  | 931 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 125 | 10 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 24 | 0 | 0 | 0 | 22 | 16 | 5 | 92 | 0 | 280 | 0 | 0 | 197 | 0 | 0 | 0 | 97 | 0 | 200 | 0 | 370 | 17 | 0 | 101 | 88 | 40 | 0 | 6 |  | 9420.4 | DayPeak
Yesterday Evening Peak | 70 | 189 | 0 | 0 | 380 | 83 | 73 | 349 | 354 | 0 | 20 | 360 | 272 | 7 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 7 | 149 | 0 | 72 | 0 | 34 | 53 | 55 | 35 | 22 | 25 | 18 | 33 | 33 | 34 | 0 | 124 | 90 | 100 | 0 | 25 | 204 | 0 | 130 | 0 | 0 | 0 | 0 | 51 | 10 | 51 | 50 | 0 | 38 | 0 | 0 | 100 | 340 | 265 | 215 | 26 | 140 | 33 | 53 | 0 | 43 | 0 | 0 | 52 | 21 | 5 | 33 | 21 | 180 | 175 | 95 | 20 | 0 | 60 | 58 | 50 | 50 | 163 | 151 | 63 | 75 | 44 | 0 | 18 | 45 | 10 | 300 | 24 | 8 | 0 | 15 | 0 | 0 | 187 | 0 | 81 | 0 | 100 | 198 | 100 | 15 | 109 | 105 | 0 | 0 | 87 | 0 | 114 |  | 926 | 0 | 300 | 0 | 99 | 0 | 0 | 0 | 31 | 65 | 40 | 180 | 13 | 110 | 0 | 0 | 55 | 25 | 0 | 95 | 50 | 50 | 0 | 52 | 30 | 22 | 16 | 11 | 90 | 0 | 275 | 0 | 0 | 202 | 0 | 0 | 0 | 97 | 100 | 193 | 0 | 392 | 105 | 0 | 96 | 87 | 113 | 0 | 0 |  | 11757 | EvPeak
Forecast for Evening | 70 | 190 | 0 | 0 | 350 | 90 | 75 | 350 | 300 | 0 | 20 | 350 | 280 | 100 | 100 | 55 | 0 | 0 | 150 | 0 | 100 | 100 | 149 | 100 | 72 | 0 | 46 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 125 | 90 | 100 | 0 | 25 | 215 | 0 | 150 | 0 | 0 | 0 | 0 | 80 | 100 | 97 | 50 | 22 | 25 | 0 | 0 | 100 | 360 | 360 | 220 | 68 | 140 | 33 | 52 | 0 | 43 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 185 | 204 | 95 | 20 | 0 | 60 | 58 | 51 | 44 | 163 | 160 | 63 | 75 | 44 | 0 | 17 | 43 | 10 | 320 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 80 | 115 | 100 | 100 | 0 | 260 |  | 113 |  | 943 | 32 | 410 | 0 | 115 | 200 | 0 | 0 | 42 | 75 | 40 | 180 | 35 | 110 | 30 | 0 | 60 | 50 | 30 | 100 | 50 | 50 | 47 | 52 | 35 | 22 | 15 | 11 | 90 | 0 | 280 | 0 | 0 | 215 | 0 | 0 | 0 | 95 | 100 | 215 | 0 | 400 | 105 | 200 | 113 | 100 | 114 | 0
Forecast for Day | 70 | 190 | 0 | 0 | 350 | 90 | 50 | 350 | 300 | 0 | 20 | 350 | 280 | 100 | 100 | 55 | 0 | 0 | 100 | 0 | 100 | 100 | 149 | 100 | 72 | 0 | 46 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 125 | 90 | 100 | 0 | 25 | 215 | 0 | 130 | 0 | 0 | 0 | 0 | 50 | 100 | 95 | 50 | 22 | 5 | 0 | 0 | 100 | 250 | 360 | 0 | 68 | 140 | 33 | 52 | 0 | 43 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 131 | 204 | 95 | 20 | 1.6 | 60 | 58 | 51 | 44 | 163 | 160 | 63 | 73 | 44 | 0 | 17 | 42 | 10 | 300 | 24 | 11 | 0 | 200 | 0 | 0 | 200 | 0 | 149 | 20 | 100 | 200 | 150 | 80 | 115 | 100 | 50 | 4.4 | 230 |  | 113 |  | 943 | 0 | 320 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 180 | 25 | 70 | 0 | 0 | 60 | 50 | 0 | 80 | 40 | 50 | 47 | 52 | 0 | 22 | 16 | 11 | 90 | 0 | 280 | 0 | 0 | 215 | 0 | 0 | 0 | 95 | 80 | 205 | 0 | 400 | 105 | 100 | 113 | 50 | 114 | 0 | 8
Generation at 08:00(Today) | 70 | 160 | 0 | 0 | 300 | 52 | 20 | 355 | 300 | 0 | 20 | 320 | 240 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 6 | 35 | 0 | 0 | 19 | 25 | 13 | 33 | 33 | 0 | 0 | 120 | 90 | 100 | 0 | 0 | 218 | 0 | 134 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 2 | 0 | 0 | 100 | 358 | 290 | 0 | 26 | 140 | 33 | 54 | 0 | 43 | 0 | 0 | 0 | 21 | 5 | 25 | 20 | 128 | 201 | 91 | 20 | 1.2 | 60 | 58 | 50 | 47 | 100 | 154 | 61 | 40 | 44 | 0 | 17 | 39 | 10 | 310 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 10 | 34 | 0 | 80 | 115 | 70 | 0 | 2.1 | 15 | 0 | 114 | 0 | 928 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 180 | 24 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 12 | 8 | 0 | 0 | 0 | 22 | 16 | 8 | 90 | 0 | 280 | 0 | 0 | 172 | 0 | 0 | 0 | 96 | 0 | 168 | 0 | 345 | 0 | 0 | 37 | 52 | 35 | 0 | 2.9 | 0
199
| Minimum Generation |  | 8108.7 | 7:00
| Highest Generation |  | 11757 | 21:00
| Day Peak Generation |  | 9420.4 | 12:00
| Evening Peak Generation |  | 11757 | 21:00
| HVDC Max Flow |  | 932 | 9:00
| HVDC EvPeak Flow |  | 926 | 21:00
| Load factor L.F |  | 86.78%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-08-20
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-08-19 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9420.4 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 8713.2 | MW
Evening Peak Generation : |  | 11757 | MW Hour : | 21:00 | Available Max Generation : |  | 15025 | MW
E.P. Demand (at gen end) : |  | 11757 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12300 | MW
Maximum Generation : |  | 11757 | MW Hour : | 21:00 | Reserve(Generation end) |  | 2725 | MW
Total Gen. (MKWH) : |  | 244.8763 | System Load Factor : | 86.78% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -100 | MW at | 21:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-08-20
Actual : | 105.75 | Ft.(MSL) , | Rule curve : | 95.08 | Ft.( MSL )
Gas Consumed : | Total = | 1349.01 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 155166545.452
|  | Coal : | 44519786.31 | Oil : | 352684450.66 | Total : | 552370782.422
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4365.7125 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1487.6127 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1333.3914 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1205.0232 |  |  | 0 | 0%
) | 0 | 0:00 | 1088.8564 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 878.6762 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 487.4148 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 226.1323 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 677.6974 |  |  | 0 | 0%
Total | 0 |  | 11750.5169 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit- 2. | 7) Ghorasal Unit-5
|  |  |  | 2) Khulna ST 110 MW | 8) Ghorashal Unit-4
|  |  |  | 3) Sikalbaha ST 60 MW | 9) Sirajganj Unit-2
|  |  |  | 4) Siddhirganj ST | 10) Siddhirganj 335 MW.
|  |  |  | 5) Ashuganj #4 | 11) Ashuganj #3
|  |  |  | 6) Baghabari 100 MW | 12) Sylhet 150 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Amnura 132/33 kV T1 transformer was under shut down from 08:21 to 10:30 due to changing 33 kv R-phase
bus incomer isolator.
b) Sylhet 150 MW GT tripped at 09:54 due to tripping of gas booster.
c) Barishal(N) 132/33 kV T5 transformer was under shut down from 11:37 to 13:01 for D/W.
d) Faridpur-Madaripur 132 kV Ckt-2 tripped at 12:19 from both end showing Dist. C-phase, Z1 at Faridpur end
& Dist. 3-phase Z1 at Madaripur end and was switched on at 12:33.
e) Barishal(N) 132/33 kV T4 transformer was under shut down from 13:10 to 13:57 due to 33 kV loop between
CT & breaker changing.
f) Ashuganj #3 was shut down at 11:05 due to gas shortage.
g) Rajshahi-Chapainawabganj 132 kV Ckt was under shut down from 10:15 to 17:09 for C/M.
feeder bus isolator.
h) Barapukuria 132/33 kV T3 transformer tripped at 16:17 due to LA burst at 33 kV end and was switched
on at 18:07.
i) Modunaghat 132/33 kV T1 & T2 transformers tripped at 15:58 due to 33 kV Noapara feeder fault and |  |  |  |  | About 40 MW power interruption occurred under Modunaghat S/S
was switched on at 16:03. |  |  |  |  | area from 15:58 to 16:03.
j) Ashuganj 225 MW GT was shut down at 04:11(20/08/2019) for maintenance work.
k) Chowmuhoni 132/33 kV T3 transformer was under shut down from 06:05(20/08/2019) to 07:10(20/08/2019) |  |  |  |  | About 35 MW power interruption occurred under Chowmuhoni S/S
due to red hot maintenance at 33 kV feeder. |  |  |  |  | area from 06:05 to 07:10(20/08/2019).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-08-19 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 70 | 1528000
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 189 | 4819600
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 380 | 7866673
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 73 | 1345344
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 83 | 1521136 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 20 | 485500 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 349 | 8589456 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 354 | 7389000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 360 | 8416750 | Machine problem
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 7 | 47040 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 272 | 6607273 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 0 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 11571 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 5583 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 436608
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 190 | 3297000 | FGMO
| Siddhirganj Desh |  | QRPP | 96*1.2 | 0 | 0 | 0 | Contract Expired
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 8640 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217 | 217 | 0 | 0 | ST Commissioning
| Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 7 | 85680 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 34 | 603408 | Low demand
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 632880
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 700320
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 363973
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 184469 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 72 | 992640 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 43 | 956760 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 790700
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 798100
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 34 | 670140 | Engine problem
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 15 | 87818 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 81 | 1546560 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 2299380
| Dhaka area Total |  |  |  | 5693 | 3118 | 63088002
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2300000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 151938
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 134325
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 694560
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 214 | 4924802
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4908684 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 130 | 3199156 | FGMO
44 | Sikalbaha 51 MW PP(Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 0 | 0 | Contract Expired
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
46 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
47 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 282110
48 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 273000 | Low demand
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1291200
50 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 486288 | Machine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 38 | 576480
51 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 51 | 354240 | Low demand
52 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 37080
53 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 87 | 1109018 | Transformer overload.
| Jodiac Power |  | IPP | 54.36 | 0 | 0 | 74010 | on test
| Karnaphuli Power Ltd. |  | IPP | 110 | 0 | 114 | 2062463 | RRT
| Chattogram area Total |  |  |  | 2053 | 1174 | 22859354
54 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 879854 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 9895 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 100 | 2364248 | Gas shortage
55 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 215 | 4678000 | FGMO
56 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 340 | 6358000 | FGMO
57 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 265 | 7364000 | FGMO
58 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 33 | 758448 | Engine problem
59 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 53 | 1224000
60 | Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
61 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 26 | 468363 | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 756452 | Engine problem
63 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 100 | 376363 | Transformer overload.
64 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
65 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 64067 | Reserve
66 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 140 | 3255700
67 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 198 | 2343360
68 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 428796
69 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 5 | 220320 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 180 | 3657600
70 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 680900
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 518587
72 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 445760 | Engine problem
73 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1825 | 36852713
74 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 175 | 4040120 | Gas shortage
75 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 455580
76 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 95 | 1248000
77 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14700
78 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 187 | 1828800 | Engine problem
79 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 109 | 2564400
| Mymensingh Area Total |  |  |  | 637 | 586 | 10151600
80 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1422000
81 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 58 | 1365360
82 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3257803
83 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 151 | 3352000 | GT-2 under maint.
84 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 802800
85 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 875952
86 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 190416 | Engine problem
87 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 63 | 1453344 | FGMO
88 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 75 | 1416960 | Engine problem
89 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 44 | 831240 | Engine problem
90 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 0 | 5316631 | Under S/D
91 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 432770
92 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 45 | 836400 | Machine problem
93 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 522408
94 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7397500 | FGMO
95 | Bibiyana-III 400 MW CCPP |  | PDB | 285 MW | 285 | 15 | 356000 | Test
96 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 246240
| Sylhet Area Total |  |  |  | 1834 | 1134 | 30075824
97 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 926 | 22300364
| Khulna 115 MW PP (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
98 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 685440
99 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 31 | 292800 | Engine problem
100 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
101 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 65 | 474368
102 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 300 | 7687296 | Line O/L
103 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 579750
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
104 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 591360
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1610400
106 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 87 | 1794240 | Engine problem
| Khulna Area Total |  |  |  | 2314 | 1753 | 36016018
107 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1100160
108 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 56016 | Reserve
109 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 13 | 458228 | Machine problem
110 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 180 | 3806531
111 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 97 | 2146194
| Barisal Area Total |  |  |  | 462 | 400 | 7567129
112 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 55 | 1370000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
113 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 25 | 165304 | Low demand
114 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 19166 | Reserve
115 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 492430
116 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 821324
117 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 40474 | Reserve
118 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 202 | 4775345 | FGMO
119 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
120 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 193 | 4778827 | FGMO
121 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 392 | 9593090 | FGMO
122 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 228099
123 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 511440
124 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 16 | 372312
125 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 112526
126 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 318240
127 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 95 | 976072
128 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
129 | Bagura 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 96 | 2025984 | Engine problem
| Rajshahi Area Total |  |  |  | 2070 | 1289 | 26600633
130 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 90 | 2197963
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
131 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 275 | 7461800
132 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
133 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
| Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 0 | 113 | 1973760 | On test
| Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 31514
| Rangpur Area Total |  |  |  | 492 | 478 | 11665037
| Total |  |  |  | 18446 | 11757 | 244876310
| Eastern Grid Total |  |  |  | 13108 | 7837 | 163027493
| Western Grid Total |  |  |  | 5338 | 3920 | 81848817
| National Grid Total |  |  |  | 18446 | 11757 | 244876310
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-08-19
(a) ENTIRE EASTERN GRID : |  | 7439 | MW | (b) ENTIRE WESTERN GRID : |  | 3783 | MW
i) Dhaka area |  | 3671 | MW | i) Khulna area |  | 1440 | MW
ii) Chittagong area |  | 1209 | MW | ii) Rajshahi area |  | 1252 | MW
iii) Comilla area |  | 1072 | MW | iii) Barisal area |  | 338 | MW
iv) Mymensingh area |  | 991 | MW | iv) Rangpur area |  | 753 | MW
v) Sylhet area |  | 496 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11222 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 100 | 1500 | Sherpur | 106 | 2200 | Jhenida | 110 | 1930
Munsiganj | 122 | 2300 | Srimongal | 41 | 2000 | Bottail | 120 | 2000
Sonargaon | 76 | 1930 | Shahjibazar | 123 | 2100 | G.K Project | 61 | 1900
Shyampur | 160 | 2400 | Fenchuganj | 46 | 2100 | Faridpur | 180 | 2100
Bhulta | 134 | 2200 | Kulawara | 47 | 2200 | Madaripur | 116 | 2200
Madanganj | 48 | 1300 | Sylhet | 146 | 1930 | Sariatpur | 42 | 100
Shitalakhya | 94 | 1600 | Chatak | 33 | 2100 | Gopalganj | 91 | 2200
Rahim steel | 6 | 1000 | Sunamganj | 40 | 2100 | Bagerhat | 86 | 2200
Matuail | 70 | 1600 | Biani Bazar | 56 | 2100 | Mongla | 32 | 1300
Ghorasal | 74 | 2200 | Comilla (S) | 180 | 2000 | Satkhira | 100 | 1930
Narsingdi | 126 | 2000 | Comilla(N) | 125 | 2100 | Gallamari | 47 | 1300
Haripur (SBU) | 74 | 1000 | Chandpur | 109 | 2200 | Magura | 54 | 1930
Ullon | 83 | 1900 | Feni | 111 | 2100 | Norail | 25 | 1930
Hasnabad | 190 | 2100 | Chowmuhani | 174 | 1930 | Chuadanga | 87 | 2000
Magbazar | 133 | 1900 | Ashuganj | 57 | 2200 | Barisal(N) | 46 | 2300
Maniknagar | 120 | 1300 | Daudkandi | 30 | 2000 | Barisal (S) | 108 | 2100
Bangabhaban | 36 | 1300 | B.Baria | 140 | 2200 | Patuakhali | 113 | 2300
Narinda | 84 | 1300 | Ramganj | 100 | 1900 | Bhandaria | 56 | 2100
Dhanmondi | 137 | 1300 | Madunaghat | 56 | 2100 | Borhan Uddin | 37 | 2200
Lalbag | 51 | 1300 | Hathazari | 96 | 1900 | Ishurdi | 66 | 2100
Madartek | 53 | 2100 | Khulshi | 190 | 1400 | Ruppur Paromanobik | 2 | 100
Mirpur | 102 | 1830 | Halishahar | 130 | 1500 | Natore | 123 | 2100
Kalyanpur | 108 | 1830 | Baraulia | 130 | 2000 | Bogra | 242 | 2000
Gulshan | 152 | 1400 | Sikalbaha | 24 | 1900 | Noagaon | 115 | 2000
Uttara | 80 | 1900 | Dohazari | 90 | 1900 | Rajshahi | 167 | 2100
Uttara New | 14 | 1900 | Cox'sbazar | 91 | 1930 | C.Nawabganj | 70 | 2100
Kamrangirchar | 56 | 1930 | Chandraghona | 28 | 1830 | Amnura | 37 | 2100
Savar | 121 | 1500 | Kaptai | 4.5 | 1900 | Pabna | 112 | 2000
Bhasantec | 161 | 1400 | A. Khaer Stl. | 0 | 0 | Shahjadpur | 96 | 1930
Agargaon | 61 | 1300 | Bakulia | 104 | 1700 | Serajganj | 97 | 2100
Satmosjid | 101 | 1900 | Julda | 18 | 2100 | Niyamatpur | 60 | 2000
Tongi | 135 | 1600 | TK chemical | 16.4 | 1900 | Joypurhat | 52 | 2100
Kabirpur | 204 | 1500 | Modern Steel | 10 | 200 | Mohastangor | 16 | 1930
Basundhara | 124 | 1300 | Shahmirpur | 27 | 1500 | Rangpur | 144 | 2000
Manikganj | 100 | 2000 | Khagrachhari | 20 | 1900 | Lalmonirhat | 69 | 2000
Joydevpur | 210 | 2100 | Matarbari | 29 | 2000 | Saidpur | 109 | 1930
New Tongi | 92 | 1100 | Baroiar Hat | 52 | 2100 | Purbasadipur | 98 | 2100
Korda | 234 | 1500 | Rangamati | 12 | 1900 | Thakurgaon | 72 | 1900
Dhamrai | 62 | 2100 | Abul Khair 230 | 32 | 1500 | Palashbari | 124 | 2000
Valuka | 86 | 2100 | BSRM | 145 | 2100 | Barapukuria | 52 | 2000
Tangail | 194 | 2000 | Goalpara | 27 | 1930 | Panchagar | 41 | 1900
Mymensing | 244 | 2200 | Central s/s | 96 | 1900 | Joldhaka | 28 | 1930
Kishorganj | 128 | 2100 | Noapara | 75 | 1930 | Kurigram | 37 | 2000
Netrokona | 107 | 1930 | Jessore | 116 | 1930
Jamalpur | 135 | 2100 | Benapol | 42 | 2100
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-08-19
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | 126
Bibiyana | 389 | 4:00 | 362 | 20:00 | Kaliakoir | 368 | 4:00 | 358
Bheramara | 393 | 7:00 | 384 | 19:30 | Bhulta | 383 | 20:00 | 372
Ashuganj(N) | 386 | 19:30 | 376 | 1:00
230 KV | KV |  | KV |  | 230 KV | KV |  | 15:00
Ghorasal | 230 | 18:30 | 222 | 15:00 | Hathazari | 219 | 2:00 | 214
Ishurdi | 233 | 18:30 | 226 | 13:00 | Megnaghat | 224 | 3:00 | 218
Ashuganj | 235 | 6:00 | 230 | 10:00 | Fenchuganj | 235 | 6:00 | 229
Serajganj | 231 | 18:30 | 225 | 20:00 | Siddhirganj | 223 | 3:00 | 216
Baghabari | 233 | 18:00 | 230 | 1:00 | Maniknagar | 222 | 6:00 | 214
Barapukuria | 233 | 6:00 | 222 | 21:00 | Old Airport | 222 | 6:00 | 212
Bogra | 226 | 18:30 | 212 | 20:00 | Barisal | 230 | 14:00 | 222
Khulna South | 223 | 2:00 | 210 | 12:00 | AKSML | 216 | 6:00 | 210
Rampura | 220 | 1:00 | 215 | 11:00 | BSRM | 220 | 6:00 | 210
Haripur | 220 | 1:00 | 216 | 11:00 | Bibiyana | 231 | 3:00 | 228
Hasnabad | 224 | 3:00 | 214 | 15:00 | Bhulta | 224 | 6:00 | 216
Aminbazar | 222 | 2:00 | 213 | 15:00 | Ashuganj (S) | 232 | 6:00 | 227
Tongi | 221 | 4:00 | 214 | 9:00 | Kaliakoir | 222 | 18:00 | 211
Comilla (N) | 228 | 5:00 | 223 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 133 | 300 | 128 | 1500 | Khulshi | 128 | 400 | 124
Munsiganj | 132 | 1930 | 126 | 1000 | Halishahar | 130 | 1200 | 128
Megnaghat | 131 | 100 | 126 | 1700 | Baraulia | 128 | 500 | 124
Shyampur | 132 | 100 | 125 | 1500 | Sikalbaha | 132 | 100 | 128
Bhulta | 128 | 500 | 125 | 1000 | Dohazari | 128 | 700 | 116
Madanganj | 131 | 300 | 124 | 1200 | Cox'sbazar | 121 | 1830 | 115
Shitalakhya | 133 | 600 | 124 | 1500 | Chandraghona | 131 | 100 | 128
Rahim steal | 134 | 300 | 129 | 1000 | Kaptai | 131 | 1100 | 130
Matuail | 132 | 500 | 128 | 1000 | A. Khaer Stl. | 128 | 400 | 126
Ghorasal | 135 | 100 | 132 | 1500 | Bakulia | 130 | 1900 | 126
Narsinghdi | 132 | 600 | 126 | 1000 | Julda | 130 | 1800 | 128
Haripur (SBU) | 134 | 600 | 130 | 1000 | TK Chemical | 134 | 100 | 130
Ullon | 133 | 600 | 126 | 1200 | Modern Steel | 130 | 2100 | 127
Hasnabad | 132 | 600 | 125 | 1700 | Shahmirpur | 131 | 100 | 127
Magbazar | 133 | 600 | 126 | 1400 | Khagrachhari | 130 | 700 | 127
Maniknagar | 137 | 600 | 131 | 1500 | Matarbari | 122 | 600 | 120
Bangabhaban | 137 | 600 | 131 | 1500 | Baroiar Hat | 126 | 1800 | 121
Narinda | 137 | 600 | 131 | 1500 | Rangamati | 133 | 1800 | 128
Dhanmondi | 133 | 600 | 126 | 1200 | Goalpara | 138 | 1830 | 126
Lalbag | 133 | 600 | 125 | 1200 | Central s/s | 137 | 1830 | 125
Madartek | 133 | 700 | 126 | 1500 | Noapara | 132 | 100 | 122
Mirpur | 135 | 600 | 127 | 1200 | Jessore | 128 | 1830 | 117
Kalyanpur | 136 | 300 | 129 | 1200 | Benapol | 131 | 1830 | 120
Gulshan | 132 | 300 | 126 | 1100 | Jhenida | 128 | 1900 | 114
Uttara | 133 | 600 | 125 | 1100 | Bottail | 134 | 1830 | 117
Uttara New | 134 | 1800 | 128 | 900 | G.K Project | 140 | 600 | 134
Kamrangirchar | 131 | 500 | 124 | 1100 | Faridpur | 130 | 600 | 120
Savar | 133 | 600 | 125 | 1100 | Madaripur | 134 | 1830 | 128
Bhasantec | 130 | 300 | 126 | 1500 | Sariatpur | 133 | 1830 | 125
Agargaon | 132 | 300 | 124 | 1100 | Gopalganj | 140 | 1700 | 131
Satmosjid | 131 | 600 | 124 | 1000 | Bagerhat | 135 | 1830 | 124
Tongi | 135 | 1900 | 130 | 800 | Mongla | 132 | 1830 | 122
Kabirpur | 133 | 500 | 127 | 1600 | Satkhira | 136 | 1830 | 125
Basundhara | 132 | 1800 | 126 | 1000 | Gallamari | 137 | 1830 | 127
Manikganj | 140 | 1800 | 131 | 800 | Magura | 127 | 1830 | 111
Joydevpur | 138 | 2100 | 130 | 1200 | Norail | 125 | 1830 | 110
New Tongi | 134 | 1800 | 128 | 800 | Chuadanga | 123 | 1830 | 104
Kodda | 136 | 1800 | 124 | 800 | Barisal(N) | 136 | 1400 | 131
Dhamrai | 132 | 400 | 127 | 1500 | Barisal (S) | 134 | 300 | 130
Valuka | 126 | 500 | 115 | 2200 | Patuakhali | 134 | 1830 | 126
Tangail | 131 | 600 | 122 | 2200 | Bhandaria | 134 | 1830 | 125
Mymensing | 126 | 400 | 118 | 2200 | Ishurdi | 137 | 700 | 132
Kishorganj | 126 | 500 | 120 | 2200 | Ruppur Paromanobik | 139 | 600 | 134
Netrokona | 126 | 1800 | 119 | 2100 | Natore | 137 | 1830 | 127
Jamalpur | 138 | 200 | 124 | 800 | Bogra | 134 | 1600 | 126
Sherpur | 135 | 1900 | 121 | 1000 | Noagaon | 132 | 1830 | 118
Srimongal | 135 | 200 | 131 | 1830 | Rajshahi | 131 | 600 | 122
Shahjibazar | 133 | 500 | 129 | 2200 | C.Nawabganj | 130 | 1830 | 114
Fenchuganj | 133 | 100 | 129 | 1930 | Amnura | 135 | 1830 | 115
Khulawara | 133 | 500 | 128 | 1900 | Pabna | 136 | 800 | 130
Sylhet | 133 | 700 | 124 | 2000 | Shahjadpur | 141 | 1830 | 133
Chatak | 133 | 600 | 121 | 1900 | Serajganj | 136 | 1830 | 128
Sunamganj | 132 | 700 | 119 | 2000 | Niyamatpur | 132 | 1800 | 114
Biani Bazar | 132 | 700 | 121 | 1930 | Joypurhat | 132 | 1830 | 116
Comilla(s) | 125 | 700 | 119 | 2200 | Mohastangor | 135 | 1830 | 123
Comilla(n) | 134 | 1000 | 129 | 1500 | Rangpur | 128 | 500 | 114
Chandpur | 130 | 200 | 125 | 1300 | Lalmonirhat | 125 | 600 | 110
Feni | 124 | 1800 | 120 | 1600 | Saidpur | 128 | 1800 | 113
Chowmuhani | 122 | 1900 | 119 | 2100 | Purbasadipur | 127 | 1800 | 110
Ashuganj | 134 | 2200 | 132 | 100 | Thakurgaon | 122 | 700 | 103
Daudkandi | 129 | 1830 | 124 | 1000 | Palashbari | 131 | 600 | 116
B.Baria | 130 | 700 | 126 | 2200 | Barapukuria | 133 | 600 | 122

## L-Curve
Date | 2019-08-19
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 16 | 7591 | 3816 | 11407 |  |  |  | QF-LDC-12
0:30 | 23 | 7151.5 | 3705 | 10856.5 | Date: | 2019-08-19
1:00 | 30 | 6712 | 3594 | 10306
1:30 | 34 | 6549.5 | 3550 | 10099.5
2:00 | 38 | 6387 | 3506 | 9893
2:30 | 50 | 6286.5 | 3466.5 | 9753 | [5 empty] | Gen. at Eve. Peak | 11757 | 11757 MW (21:00 )
3:00 | 62 | 6186 | 3427 | 9613 | [6 empty] | 21:00
3:30 | 73 | 6167.5 | 3423 | 9590.5 | [5 empty] | Gen. at Day Peak | 9420.4 | 9420.4 MW (12:00 )
4:00 | 84 | 6149 | 3419 | 9568 | [6 empty] | 12:00
4:30 | 92 | 6050.5 | 3353 | 9403.5 | [5 empty] | Highest Generation | 11757
5:00 | 100 | 5952 | 3287 | 9239 | [6 empty] | 21:00
5:30 | 120 | 5705.05 | 3112.5 | 8817.55
6:00 | 140 | 5458.1 | 2938 | 8396.1
6:30 | 180 | 5367.35 | 2885.05 | 8252.4
7:00 | 220 | 5276.6 | 2832.1 | 8108.7
7:30 | 285 | 5325.94 | 2854.05 | 8179.99
8:00 | 350 | 5375.28 | 2876 | 8251.28
8:30 | 390 | 5561.01 | 2864.5 | 8425.51
9:00 | 430 | 5746.74 | 2853 | 8599.74
9:30 | 450 | 5873.88 | 2896.9 | 8770.78
10:00 | 470 | 6001.02 | 2940.8 | 8941.82
10:30 | 415 | 6095.52 | 2943.9 | 9039.42
11:00 | 360 | 6190.02 | 2947 | 9137.02
11:30 | 330 | 6282.21 | 2996.5 | 9278.71
12:00 | 300 | 6374.4 | 3046 | 9420.4
12:30 | 238 | 6460.96 | 3025.5 | 9486.46
13:00 | 176 | 6547.52 | 3005 | 9552.52
13:30 | 223 | 6617.96 | 3056.05 | 9674.01
14:00 | 270 | 6688.4 | 3107.1 | 9795.5
14:30 | 292 | 6787.45 | 3178.5 | 9965.95
15:00 | 314 | 6886.5 | 3249.9 | 10136.4
15:30 | 322 | 6892.75 | 3235.15 | 10127.9
16:00 | 330 | 6899 | 3220.4 | 10119.4
16:30 | 300 | 6702.5 | 3066.35 | 9768.85
17:00 | 270 | 6506 | 2912.3 | 9418.3
17:30 | 275 | 6292.85 | 2861.5 | 9154.35
18:00 | 280 | 6079.7 | 2810.7 | 8890.4
18:30 | 142 | 6704.35 | 3289.85 | 9994.2
19:00 | 4 | 7329 | 3769 | 11098
19:30 | 76 | 7759 | 3869 | 11628
20:00 | 84 | 7689 | 3845 | 11534 |  |  |  | Executive Engineer
20:30 | 92 | 7763 | 3882.5 | 11645.5 |  |  |  | Network Operation Division
21:00 | 100 | 7837 | 3920 | 11757
21:30 | 90 | 7800 | 3904.5 | 11704.5
22:00 | 80 | 7763 | 3889 | 11652 |  |  |  |  | Page 6 of 7
22:30 | 40 | 7695.5 | 3885 | 11580.5
23:00 | 0 | 7628 | 3881 | 11509
23:30 | 8 | 7609.5 | 3848.5 | 11458
24:00 | 16 | 7591 | 3816 | 11407
11757 MW (21:00 )
9420.4 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-08-19 |  | Energy | 244876310
[10 empty] | 2019-08-19 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4466 | 926 | 2327 | 2507 | 358 | 214 | 435 | 0 | 174
0:30 | 4328 | 927.5 | 2235 | 2312.5 | 360.5 | 212.5 | 315.5 | 0 | 165 | Date: | 2019-08-19
1:00 | 4190 | 929 | 2143 | 2118 | 363 | 211 | 196 | 0 | 156
1:30 | 4153.5 | 929 | 2151.5 | 1955 | 362.5 | 211 | 182 | 0 | 155 | [7 empty] | Total Energy | 244.8763 | Total Energy Gen 187.552 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 187.552 MKWHr
2:00 | 4117 | 929 | 2160 | 1792 | 362 | 211 | 168 | 0 | 154 | [7 empty] | Energy not Served | 0
2:30 | 4163.5 | 929 | 2116.5 | 1666 | 361.5 | 211 | 150.5 | 0 | 155 | [7 empty] | Energy Requirement | 244.8763
3:00 | 4210 | 929 | 2073 | 1540 | 361 | 211 | 133 | 0 | 156
3:30 | 4241.5 | 928.5 | 2052 | 1513.5 | 361 | 211 | 128 | 0 | 155 | [6 empty] | Shortage
4:00 | 4273 | 928 | 2031 | 1487 | 361 | 211 | 123 | 0 | 154
4:30 | 4290.5 | 928.5 | 2002.5 | 1357.5 | 361 | 211 | 103.5 | 0 | 149
5:00 | 4308 | 929 | 1974 | 1228 | 361 | 211 | 84 | 0 | 144
5:30 | 4252.5 | 929 | 1801.5 | 1067.5 | 361.5 | 211 | 54.5 | 0 | 140
6:00 | 4197 | 929 | 1629 | 907 | 362 | 211 | 25 | 0 | 136
6:30 | 4180.5 | 928.5 | 1605 | 807.5 | 362 | 212 | 25 | 0 | 129 |  |  |  |  | Coal
7:00 | 4164 | 928 | 1581 | 708 | 362 | 213 | 25 | 0 | 122
7:30 | 4199.5 | 928.5 | 1606 | 708.5 | 367 | 213.5 | 24.5 | 0 | 123 |  |  |  | Oil |  |  |  | ,
8:00 | 4235 | 929 | 1631 | 709 | 372 | 214 | 24 | 0 | 124
8:30 | 4340.5 | 930.5 | 1654.5 | 757.5 | 372 | 214 | 12 | 0 | 127
9:00 | 4446 | 932 | 1678 | 806 | 372 | 214 | 0 | 0 | 130
9:30 | 4481 | 931.5 | 1764.5 | 860.5 | 372 | 210.5 | 0 | 0 | 133
10:00 | 4516 | 931 | 1851 | 915 | 372 | 207 | 0 | 0 | 136
10:30 | 4438.5 | 931 | 1943 | 988.5 | 372 | 207.5 | 0 | 0 | 138
11:00 | 4361 | 931 | 2035 | 1062 | 372 | 208 | 0 | 0 | 140
11:30 | 4359 | 931 | 2088.5 | 1152 | 372 | 209.5 | 0 | 0 | 141
12:00 | 4357 | 931 | 2142 | 1242 | 372 | 211 | 0 | 0 | 142
12:30 | 4318.5 | 931 | 2174.5 | 1314 | 372 | 211.5 | 0 | 0 | 142
13:00 | 4280 | 931 | 2207 | 1386 | 372 | 212 | 0 | 0 | 142
13:30 | 4280 | 931 | 2207 | 1386 | 372 | 212 | 0 | 0 | 142
14:00 | 4280 | 931 | 2207 | 1386 | 372 | 212 | 0 | 0 | 142
14:30 | 4402.5 | 931 | 2238.5 | 1521.5 | 371.5 | 207.5 | 0 | 0 | 149
15:00 | 4525 | 931 | 2270 | 1657 | 371 | 203 | 0 | 0 | 156
15:30 | 4464 | 931 | 2224.5 | 1764 | 371 | 199.5 | 1.5 | 0 | 152
16:00 | 4403 | 931 | 2179 | 1871 | 371 | 196 | 3 | 0 | 148
16:30 | 4313.5 | 931 | 2090 | 1697.5 | 371 | 196 | 11.5 | 0 | 146
17:00 | 4224 | 931 | 2001 | 1524 | 371 | 196 | 20 | 0 | 144
17:30 | 4147.5 | 931.5 | 1819 | 1505 | 372 | 196.5 | 35.5 | 0 | 143
18:00 | 4071 | 932 | 1637 | 1486 | 373 | 197 | 51 | 0 | 142
18:30 | 4195 | 931.5 | 1858 | 2000.5 | 373 | 205.5 | 271 | 0 | 159
19:00 | 4319 | 931 | 2079 | 2515 | 373 | 214 | 491 | 0 | 176
19:30 | 4256 | 932 | 2187 | 3005 | 372 | 214 | 484 | 0 | 178
20:00 | 4292 | 926 | 2153 | 2948 | 371 | 214 | 450 | 0 | 180
20:30 | 4380.5 | 926 | 2230 | 2899 | 368 | 214 | 448 | 0 | 180
21:00 | 4469 | 926 | 2307 | 2850 | 365 | 214 | 446 | 0 | 180
21:30 | 4497 | 926 | 2308 | 2779.5 | 363 | 214 | 437 | 0 | 180
22:00 | 4525 | 926 | 2309 | 2709 | 361 | 214 | 428 | 0 | 180
22:30 | 4520 | 926.5 | 2311.5 | 2663 | 360.5 | 214 | 407 | 0 | 178
23:00 | 4515 | 927 | 2314 | 2617 | 360 | 214 | 386 | 0 | 176
23:30 | 4490.5 | 926.5 | 2320.5 | 2562 | 359 | 214 | 410.5 | 0 | 175 | Max Temp. in Dhaka |  | 34.6° C
24:00 | 4466 | 926 | 2327 | 2507 | 358 | 214 | 435 | 0 | 174
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 187.552 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 187.552 MKWHr
Note on W13: Author:

## Generation
2019-08-19
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 121 | 121 | 121 | 121 | 121 | 121 | 123 | 124 | 124 | 117 | 118 | 121 | 122 | 117 | 113 | 106 | 106 | 107 |  | 124 | 124 | 124 | 124 | 124 | 124 | 124 | 2772802
2 | Karnaphuli Hydro PP Unit-4 & 5 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2152000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2300000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | [16 empty] | 1 |  | 14 | 25 | 25 | 25 | 25 | 25 | 25 | 151938
| Teknaf 20MW PP (Solartech) | [6 empty] | 3.7 | 10 | 15 | 7 | 20 | 8 | 14 | 17.6 | 15.2 | 10.5 | 3.4 | 0.5 | [8 empty] | 134325
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 204 | 205 | 204 | 205 | 205 | 206 | 206 | 207 | 205 | 206 | 205 | 205 | 205 | 203 | 203 | 204 | 204 |  | 203 | 202 | 204 | 204 | 203 | 205 | 204 | 4908684
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 100 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3199156
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 0 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 282110
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [17 empty] | 0 |  | 42 | 0 | 0 |  |  |  |  | 64067
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 120 | 120 | 120 | 125 | 120 | 80 | 80 | 80 | 80 | 100 | 120 | 125 | 127 | 185 | 191 | 179 | 95 | 95 |  | 90 | 90 | 95 | 190 | 185 | 190 | 160 | 3297000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [19 empty] | 11 | 64 | 15 | 15 | 2 | 0 | 0 | 87818
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 25 | 25 | 25 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 468363
20 | Ghorasal TPP (Unit-1&2) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1528000
21 | Ghorasal Repowered CCPP Unit-3 | 190 | 104 | 190 | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 190 | 189 | 188 | 189 | 189 | 189 | 189 |  | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 4819600
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 320 | 320 | 320 | 320 | 320 | 270 | 270 | 270 | 270 | 380 | 350 | 350 | 350 | 350 | 370 | 370 | 300 | 300 |  | 380 | 380 | 380 | 380 | 380 | 340 | 340 | 7866673
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 30 | 0 | [14 empty] | 879854
29 | Ashuganj TPP Unit- 4 | [19 empty] | 20 | 0 | 0 |  |  |  |  | 9895
30 | Ashuganj TPP Unit- 5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 80 | 80 | 90 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2364248
32 | Ashuganj 50 MW PP | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 27 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 758448
33 | Ashuganj 225 MW CCPP | 181 | 181 | 181 | 181 | 193 | 181 | 181 | 186 | 196 | 202 | 174 | 183 | 187 | 190 | 203 | 181 | 182 | 181 |  | 214 | 215 | 214 | 215 | 215 | 214 | 215 | 4678000
34 | Ashuganj 450 MW CCPP(South) | 305 | 305 | 305 | 305 | 320 | 305 | 305 | 310 | 320 | 330 | 320 | 305 | 320 | 310 | 335 | 305 | 305 | 260 |  | 265 | 265 | 265 | 265 | 265 | 275 | 265 | 7364000
| Ashuganj 450 MW CCPP(North) | 18 | 15 | 22 | 70 | 90 | 100 | 125 | 225 | 368 | 365 | 345 | 345 | 363 | 347 | 360 | 345 | 345 | 260 |  | 320 | 340 | 340 | 340 | 340 | 345 | 340 | 6358000
35 | Ashuganj 55 MW PP (Precision) | 54 | 55 | 56 | 56 | 56 | 55 | 55 | 54 | 54 | 53 | 50 | 50 | 52 | 52 | 51 | 51 | 50 | 15 |  | 15 | 52 | 52 | 53 | 55 | 55 | 55 | 1224000
36 | Chandpur 150 MW CCPP | 138 | 138 | 139 | 138 | 138 | 138 | 138 | 138 | 140 | 135 | 140 | 140 | 139 | 139 | 140 | 132 | 130 | 140 |  | 130 | 131 | 140 | 140 | 130 | 137 | 131 | 3255700
37 | Tongi 80 MW GTPP
38 | Haripur GTPP | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 485500
39 | Haripur 412 MW CCPP | 344 | 353 | 346 | 350 | 348 | 345 | 345 | 346 | 355 | 378 | 348 | 361 | 365 | 366 | 373 | 354 | 353 | 346 |  | 350 | 345 | 345 | 349 | 345 | 345 | 345 | 8589456
40 | Meghnaghat 450 MW CCPP(MPL) | 360 | 360 | 360 | 360 | 360 | 360 | 300 | 300 | 300 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 |  | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 8416750
41 | Haripur 360MW CCPP(HPL) | 300 | 300 | 300 | 300 | 300 | 280 | 240 | 240 | 274 | 324 | 340 | 346 | 342 | 340 | 340 | 340 | 304 | 274 |  | 304 | 304 | 305 | 354 | 355 | 320 | 320 | 7389000
42 | RPCL 210MW CCPP | 185 | 187 | 191 | 192 | 191 | 192 | 191 | 173 | 170 | 165 | 150 | 153 | 156 | 156 | 156 | 157 | 160 | 163 |  | 163 | 163 | 163 | 175 | 174 | 174 | 188 | 4040120
43
44 | Fenchugonj CCPP Phase-1 | 58 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1422000
45 | Fenchugonj CCPP Phase-2 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 |  | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 1365360
46 | Shajibazar 330 MW CCPP | 152 | 152 | 152 | 151 | 152 | 152 | 153 | 152 | 153 | 150 | 151 | 153 | 152 | 153 | 152 | 152 | 152 | 151 |  | 151 | 151 | 151 | 151 | 150 | 151 | 149 | 3352000
47 | Shahjibazar GTPP Unit- 8 & 9 | 54 | 64 | 65 | 64 | 64 | 51 | 63 | 62 | 61 | 61 | 61 | 61 | 60 | 59 | 59 | 61 | 62 | 59 |  | 63 | 58 | 63 | 63 | 63 | 63 | 63 | 1453344
48 | Shahjibazar 86MW PP (Shahjibazar) | 76 | 76 | 73 | 73 | 73 | 10 | 10 | 10 | 10 | 10 | 75 | 75 | 75 | 75 | 74 | 74 | 74 | 10 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1416960
49 | Shahjibazar 50MW PP (EPL) | 44 | 44 | 44 | 44 | 44 | 10 | 10 | 10 | 10 | 40 | 40 | 40 | 42 | 42 | 42 | 42 | 42 | 10 |  | 43 | 43 | 44 | 44 | 44 | 44 | 44 | 831240
50 | Sylhet 150 MW CCPP | 109 | 109 | 109 | 110 | 110 | 110 | 123 | 118 | 123 | 0 | 0 | [15 empty] | 5316631
51 | Sylhet 20 MW GTPP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 432770
52 | Sylhet 50MW PP (EPL) | 45 | 45 | 45 | 45 | 14 | 14 | 12 | 15 | 12 | 36 | 39 | 39 | 42 | 42 | 41 | 41 | 43 | 10 |  | 43 | 42 | 45 | 45 | 45 | 45 | 45 | 836400
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 5 | 10 | 10 | 10 | 10 | 10 | 10 | 246240
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 190416
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 50 | 47 | 50 | 50 | 50 | 50 | 50 | 11 |  | 41 | 50 | 50 | 50 | 50 | 50 | 50 | 802800
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 8 | 16 | 24 | 522408
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 290 | 290 | 300 | 290 | 270 | 275 | 300 | 315 | 320 | 300 | 315 | 315 | 310 | 325 | 290 | 280 | 280 |  | 290 | 270 | 270 | 300 | 290 | 290 | 315 | 7397500
58 | Nababganj 55 MW PP (Southern power ) | [19 empty] | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 184469
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 |  | 21 | 22 | 22 | 486288
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 |  | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 436608
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 455580
63 | Impoprt (Tripura) | 156 | 154 | 156 | 154 | 144 | 136 | 122 | 124 | 130 | 136 | 140 | 142 | 142 | 154 | 156 | 148 | 144 | 142 |  | 176 | 178 | 180 | 180 | 180 | 176 | 174 | 3657600
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 38 | 38 | 38 | 38 | 27 | 4 | 2 | 2 | 2 | 2 | 10 | 5 | 3 | 5 | 14 | 16 |  | 30 | 37 | 38 | 38 | 39 | 40 | 40 | 576480
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 20 |  | 15 | 19 |  | 19 |  | 13 | 21 | 21 | 21 | 21 | 428796
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 11 | 11 | 11 |  | 11 |  |  | 5 | 5 | 5 | 5 | 220320
67 | Jangalia 33MW PP (Summit) | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 33 | 0 | 0 | 33 | 33 | 33 | 33 | 33 | 33 | 10 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 680900
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 18 |  | 18 | 20 | 21 | 21 | 20 | 21 | 20 | 445760
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 18 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 16 | 7 | 12 | 13 | 13 | 13 | 13 |  | 13 | 13 | 13 | 18 | 22 | 22 | 20 | 356760
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 790700
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 798100
73 | Ghorashal 108MW PP (Regent) | 84 | 84 | 84 | 84 | 84 | 12 | 13 | 13 | 13 | 13 | 13 | 70 | 78 | 84 | 84 | 80 | 80 | 52 |  | 84 | 84 | 84 | 83 | 84 | 84 | 84 | 1521136
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [19 empty] | 5 | [5 empty] | 0 | 8640
78 | Gazipur 52 MW PP | 8 | [7 empty] | 17 | 25 | 25 | 25 | 30 | 51 | 50 | 50 | 50 | 50 |  | 50 | 50 | 43 | 34 | 43 | 43 | 43 | 670140
79 | Kodda 150MW PP | 20 | 16 | [17 empty] | 80 | 149 | 149 | 149 | 136 | 100 | 149 | 700320
80 | Jamalpur 95 MW PP(Powerpac) | 90 | 90 | 90 | 90 | 91 | 16 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 12 | 18 | 50 | 17 | 16 |  | 56 | 95 | 95 | 95 | 95 | 95 | 95 | 1248000
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 24 | 16 | 16 | 16 | [9 empty] | 8 | 25 | 25 | 25 |  | 25 | 52 | 52 | 52 | 52 | 52 | 52 | 518587
| Gazipur 100 MW PP | 105 | 105 | 90 | 71 | 71 | 53 | 53 | 53 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 107 | 107 | 107 | 2299380
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1.2 | 2.68 | 4.14 | 2.12 | 3.52 | 6.8 | 5.42 | 4.7 | 3.9 | 0.9 | 1.2 | 0.2 |  | 0 | [6 empty] | 37080
| Jodiac Power | [9 empty] | 11 | 18 | 18 | 17 |  | 0 | [10 empty] | 0 | 74010
| Karnaphuli Power Ltd. | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 92 | 99 | 111 | 114 | 114 | 114 | 114 | 114 |  | 114 | 114 | 114 | 114 | 114 | 112 | 115 | 2062463
82 | Madanganj 102 PP(Summit) | [25 empty] | 0
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [19 empty] | 3 | [5 empty] | 0 | 5583
86 | Meghnaghat CCPP(Summit) | 265 | 270 | 245 | 260 | 265 | 265 | 260 | 265 | 268 | 285 | 300 | 290 | 301 | 280 | 270 | 280 | 282 | 256 |  | 270 | 246 | 276 | 272 | 260 | 285 | 285 | 6607273
87 | Meghnaghat 100 MW(IEL) | [19 empty] | 1 | 7 | 30 | 7 |  |  | 0 | 47040
88 | Ghorashal 78.5 MW PP(MAX) | 75 | 75 | 50 | 50 | 50 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 60 | 71 | 70 | 71 | 50 | 50 |  | 50 | 73 | 74 | 73 | 74 | 74 | 74 | 1345344
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 40 | 10 | 10 | 10 | 10 | 10 | 10 | 273000
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 50 | 50 | 5 | 5 | 5 | 5 | 5 | 9 | 47 | 50 | 47 | 47 | 45 | 46 | 46 | 10 |  | 19 | 46 | 50 | 50 | 50 | 50 | 50 | 875952
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 15 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 756452
94 | Gagnagar 102 MW PP (Digital Power) | [19 empty] | 24 | 50 | 24 | 7 | 7 | 0 | 0 | 85680
95 | Patenga 50MW PP (Baraka) | 50 | [7 empty] | 7 | 24 | 24 | 24 | 24 | 25 | 38 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 694560
96 | Chattogram 108 MW PP (ECPV) | 10 | [18 empty] | 50 | 55 | 55 | 51 | 51 | 51 | 51 | 354240
97 | Katpotti 52 MW PP (Sinha) | 47 | 46 | 46 | 46 | 46 | 46 | 30 | 26 | 26 | 26 | 9 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 25 | 15 | 34 | 39 | 39 | 11 | 603408
98 | Bosila 108MW PP(CLC) | 40 | [7 empty] | 24 | 24 | 24 | 55 | 72 | 72 | 72 | 72 | 72 | 72 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 992640
99 | Madanganj-55 MW PP(Summit) | [19 empty] | 0 | 15 | 0 | 0 |  |  |  | 11571
100 | Manikganj 55 MW PP (Northern) | [13 empty] | 17 | 17 | 35 | 17 | 17 |  | 55 | 55 | 55 | 55 | 55 | 18 | 18 | 363973
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 130 | 130 | 163 | 163 | 163 | 100 | 100 |  | 130 | 163 | 100 | 163 | 163 | 163 | 163 | 3257803
102 | Sarishabari 3 MW Solar Plant |  |  |  |  | 0 | 0.1 | 0.7 | 0.6 | 0.6 | 1.9 | 2.5 | 2.6 | 1.1 | 2.1 | 1.4 | 1.6 | 0.4 | 0 |  | 0 | [6 empty] | 14700
103 | Kamalaghat 54 MW PP(Banco Energy) | [10 empty] | 5 | 35 | 35 | 35 | 35 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 632880
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 170 | 170 | 100 | 100 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 14 |  | 81 | 185 | 185 | 187 | 194 | 194 | 185 | 1828800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [8 empty] | 9 | 50 | 100 | 100 | 100 | 100 | 105 | 127 | 134 | 149 |  | 149 | 149 | 149 | 81 | 81 | 60 | 20 | 1546560
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 70 | 40 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 22 | 50 | 85 | 80 | 78 | 40 | 40 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1291200
116 | Chandpur 200MW (Desh energy) | 200 | 125 | 90 | 70 | 70 | 50 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 68 | 105 | 105 | 105 |  | 137 | 200 | 199 | 198 | 198 | 200 | 200 | 2343360
117 | Ashuganj 150MW PP (Midland) | [14 empty] | 25 | 50 | 10 | 10 |  | 50 | 100 | 100 | 100 |  |  | 0 | 376363
118 | Bibiyana-III 400 MW CCPP | [14 empty] | 14 | 15 | 15 | 80 |  | 80 | 15 | 15 | 15 | 80 | 80 | 79 | 356000
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 115 | 115 | 80 | 80 | 80 | 80 | 115 | 115 | 115 | 115 | 115 | 115 | 108 | 115 |  | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 2564400
| Anwara 300 MW PP (United) | 105 | 72 | 70 | 70 | 15 | 15 | 15 | 15 | 15 | 30 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 55 | 82 | 83 | 87 | 88 | 88 | 88 | 1109018
120 | Eastern Zone Total | 6712 | 6387 | 6186 | 6149 | 5952 | 5458.1 | 5276.6 | 5375.28 | 5746.74 | 6001.02 | 6190.02 | 6374.4 | 6547.52 | 6688.4 | 6886.5 | 6899 | 6506 | 6079.7 |  | 7329 | 7759 | 7689 | 7837 | 7763 | 7628 | 7591 | 163027493
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 59 | 49 | 16 | 16 | 10 | 0 | [11 empty] | 3 |  | 109 | 115 | 115 | 99 | 68 | 66 | 66 | 685440
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 40 | 36 | 36 | 36 | 19 | 0 | [15 empty] | 2 | 31 | 34 | 31 | 31 | 292800
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 105 | 105 | 70 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 78 | 89 | 90 | 90 | 35 | 35 |  | 90 | 90 | 90 | 105 | 105 | 105 | 105 | 1610400
130
131
132
133
| Barisal 110 MW PP (Summit ) | 80 | 64 | 48 | 48 | 48 | 0 | [7 empty] | 48 | 48 | 48 | 16 | 16 |  | 110 | 110 | 110 | 110 | 110 | 110 | 96 | 1100160
136 | Barisal GT PP Unit-1& 2 | [19 empty] | 23 | 23 | 23 | 0 |  |  |  | 56016
137 | Bhola 95 MW PP (Aggreko) | 95 | 96 | 96 | 96 | 96 | 62 | 62 | 97 | 97 | 96 | 96 | 97 | 93 | 94 | 95 | 93 | 95 | 24 |  | 92 | 95 | 96 | 97 | 97 | 98 | 97 | 2146194
| Bhola 225 MW CCPP | 154 | 153 | 154 | 154 | 146 | 151 | 152 | 153 | 153 | 152 | 152 | 125 | 100 | 100 | 180 | 179 | 179 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 3806531
140 | Bhola 33 MW PP (Venture) | 33 | 33 | 35 | 35 | 30 | 10 | 11 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 12 | 11 | 11 | 11 |  | 35 | 35 | 14 | 13 | 33 | 39 | 38 | 458228
141 | Noapara 100 MW PP (Bangla Trac) | 40 | 18 | 0 | [16 empty] | 3 | 100 | 97 | 100 | 100 | 100 | 100 | 591360
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 40 | 40 | 40 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 40 | 8 | 8 |  | 40 | 40 | 40 | 40 | 40 | 33 | 33 | 579750
143 | Gopalganj 100 MW Peaking PP | 20 | 0 | 0 | [12 empty] | 3 | 20 | 41 |  | 80 | 75 | 75 | 65 | 65 | 64 | 64 | 474368
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | 88 | 87 | 87 | 88 | 88 | 47 | 35 | 35 | 36 | 36 | 58 | 88 | 87 | 87 | 88 | 87 | 87 | 53 |  | 88 | 87 | 87 | 87 | 87 | 87 | 87 | 1794240
146 | Bheramara HVDC | 929 | 929 | 929 | 928 | 929 | 929 | 928 | 929 | 932 | 931 | 931 | 931 | 931 | 931 | 931 | 931 | 931 | 932 |  | 931 | 932 | 926 | 926 | 926 | 927 | 926 | 22300364
147 | Bheramara 360 MW CCPP | 330 | 330 | 330 | 330 | 330 | 330 | 300 | 300 | 300 | 350 | 350 | 350 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 300 | 300 | 300 | 300 | 7687296
148
149
150 | Barapukuria TPP Unit-1 | 93 | 92 | 91 | 91 | 91 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 91 | 91 | 91 | 93 |  | 93 | 92 | 91 | 90 | 91 | 90 | 88 | 2197963
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 275 | 270 | 270 | 270 | 7461800
153 | Baghabari 71 MW GTPP | 55 | 55 | 55 | 60 | 60 | 60 | 60 | 60 | 60 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 60 | 60 | 60 | 1370000
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 50 | 25 | 25 | 25 | 25 | 25 | 25 | 165304
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 180 | 181 | 182 | 186 | 188 | 190 | 174 | 162 | 171 | 197 | 188 | 197 | 196 | 195 | 202 | 201 | 184 | 170 |  | 171 | 189 | 193 | 202 | 200 | 190 | 180 | 4775345
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | [16 empty] | 0
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 188 | 186 | 187 | 187 | 187 | 191 | 174 | 173 | 172 | 189 | 200 | 200 | 203 | 208 | 209 | 208 | 180 | 169 |  | 167 | 185 | 183 | 193 | 195 | 196 | 192 | 4778827
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 340 | 335 | 341 | 334 | 368 | 312 | 370 | 382 | 385 | 387 | 370 | 370 | 385 | 383 | 399 | 346 | 286 | 288 |  | 356 | 341 | 379 | 392 | 378 | 410 | 400 | 9593090
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 10 |  | 15 | 0 | 0 | 0 |  |  |  | 19166
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 511440
163 | Bogura 20 MW PP (Energyprima) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 15 | 15 | 15 | 15 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 372312
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 112526
165 | Amnura 50 MW PP(Sinha) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 50 | 50 | 50 | 50 | 50 | 50 | 12 | 492430
166 | Katakhali 50 MW PP (Northern) | 50 | 50 | 50 | 50 | 50 | 24 | 24 | 24 | 8 | 8 | 8 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 50 | 50 | 50 | 50 | 50 | 24 | 24 | 821324
167 | Katakhali 50 MW Peaking PP | [19 empty] | 29 | 36 | 0 | 0 |  |  |  | 40474
168 | Santahar 50 MW Peaking PP | 22 | 22 | 22 | 22 | 0 | 0 | [13 empty] | 26 | 30 | 30 | 30 | 22 | 22 | 22 | 228099
169 | Natore 52 MW PP (Rajlanka) | 8 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 318240
170 | Chapainawabganj 100 MW Peaking PP | 94 | 94 | 75 | 65 | 65 | 25 | 25 | 24 | 0 | [10 empty] | 95 | 95 | 95 | 95 | 95 | 93 | 93 | 976072
171 | Baghabari 200 MW PP (Paramount) | [25 empty] | 0
172 | Bagura 113 MW PP (Confidence) | 113 | 113 | 113 | 113 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 101 | 111 | 112 | 113 | 113 | 56 | 56 |  | 90 | 95 | 95 | 96 | 95 | 102 | 113 | 2025984
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 107 | 107 | 107 | 107 | 107 | 107 | 35 | 35 | 35 | 35 | 38 | 40 | 42 | 76 | 107 | 109 | 65 | 55 |  | 113 | 113 | 113 | 113 | 112 | 108 | 113 | 1973760
177 | Sympa Solar Power 8MW | [6 empty] | 0.1 | 0 | 2 | 2.8 | 2 | 6 | 2 | 7.1 | 2.9 | 4.4 | 2.3 | 0.7 |  | 0 | [6 empty] | 31514
178
178