## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:August 2020
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | August 2020 |  | July 2020 |  | August 2019
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 12577 | 31/08/20 | 12552 | 26/07/20 | 12738 | 05/08/19 | 12893 | 29/05/19
|  |  | 19:30 |  | 22:00 |  | 19:30 |  | 21:00
2 | Minimum Generation (MW) | 6840.9 | 01/08/20 | 7092.1 | 31/07/20 | 6449 | 14/08/19 | - | -
|  |  | 9:00 |  | 8:00 |  | 8:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 12577 | 31/08/20 | 12536 | 26/07/20 | 12738 | 05/08/19 | 12893 | 29/05/19
|  |  | 19:30 |  | 21:00 |  | 19:30 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 10843.5 | 31/08/20 | 10525.4 | 26/07/20 | 10539.2 | 22/08/19 | 10843.5 | 31/08/20
|  |  | 12:00 |  | 12:00 |  | 21:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 12577 | 31/08/20 | 12536 | 26/07/20 | 12738 | 05/08/19 | 12893 | 29/05/19
|  |  | 19:30 |  | 21:00 |  | 19:30 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 11541.5161 |  | 11474.9032 |  | 11505.9032 |  | 11679.07 | 2019-09-19
7 | Average Generation (MW) at Day Peak | 9323.5619 |  | 9424.8087 |  | 8911.5948 |  | 9378.1933 | 2019-09-19
8 | Maximum Power Import from India, BIPTC (MW) | 945 | 04/08/2020 | 951 | 13/07/2020 | 934 | 18/08/19 | 956 | 27/3/2019
|  |  | 17:00 |  | 2:30 |  | 17:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 178 | 13/087/2020 | 174 | 27/07/2020 | 192 | 31/08/19 | 194 | 12/06/19
|  |  | 22:00 |  | 23:00 |  | 20:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 2010-05-04
20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 3707.5 | 05/04/10
20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 3338.6684 |  | 3547.5075 |  | 3752.2923 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 112.5022 |  | 100.2925 |  | 135.3315
22 | Net Generation of BPDB (MKWH) | 3226.1662 |  | 3447.2149 |  | 3616.9608
23 | Net Generation of IPP & RPCL (MKWH) | 2591.1866 |  | 2424.5663 |  | 2201.9123
24 | Net Generation of REB (MKWH) | 150.3385 |  | 150.4311 |  | 171.4948
24 | Net Generation of Rental Power Plant (MKWH) | 569.7029 |  | 531.8624 |  | 460.4374
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 6537.3941 |  | 6554.0747 |  | 6450.8053 |  | 6554.0747 | July-20
26 | Energy Generation by Gas (MKWH) | 4031.1453 |  | 4349.8373 |  | 4666.7708 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 434.2084 |  | 314.162 |  | 256.5472 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1616.2719 |  | 1406.9164 |  | 1284.2266 |  | 1616.2719 | August-20
29 | Energy Generation by Hydro (MKWH) | 89.1242 |  | 90.7677 |  | 151.3983 |  | 151.4 | August-19
30 | Energy Generation by Solar (MKWH) | 4.5842 |  | 4.1688 |  | 5.0388 |  | 22.56 | 2019-09-16
31 | Energy Generation by Coal (MKWH) | 474.5624 |  | 488.515 |  | 223.0374 |  | 488.515 | July-20
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 775.9511 |  | 769.1694 |  | 739.468 |  | 775.9511 | August-20
33 | Monthly Load Factor (%) | 79.359 |  | 79.4923 |  | 77.3075 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:August' 2020
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 12577 | 31/08/20 | 19:30
Generation Period
| Dhaka | MW | 4228
| Chattogram | MW | 1207
| Cumilla | MW | 1117
| Mymensingh | MW | 985
| Sylhet | MW | 494
a) | Total supply in East zone | MW | 8031
| Khulna | MW | 1490
| Barisal | MW | 383
| Rajshahi | MW | 1336
| Rangpur | MW | 781
b) | Total supply in West zone | MW | 3990
c) | Total supply in both zone ( a+b) | MW | 12021
Ref: | 27.21.0000.603.16.087.20.317 | Date: 17/09/2020
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:August' 2020
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 250 | 03/08/20 | 5:00
| b) Ishurdi end | MW | 272 | 22/08/20 | 9:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 675 | 22/08/20 | 9:00
| b) Ishurdi end | MW | 106 | 03/08/20 | 5:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | 1.4685 | 03/08/20
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | 1.1525 | 03/08/20
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 3.0875
| b) Ishurdi end | MKWH | 76.2279
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 73.941
| b) Ishurdi end | MKWH | 2.9975
23 | Transmission loss of EWI/ NO-1 | % | 2.91
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 400 | 03/08/20 | 5:00
| b)Serajganj end | MW | 480 | 27/08/20 | 10:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 480 | 27/08/20 | 10:00
| b)Sirajganj end | MW | 360 | 03/08/20 | 5:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 4.874 | 03/08/20
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 4.802 | 03/08/20
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 13.576
| b)Sirajganj end | MKWH | 106.83
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 105.12
| b)Sirajganj end | MKWH | 13.514
30 | Transmission loss of EWI /NO-2 | % | 1.472
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishwardi.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/3 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: August 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar | 230/132 kV Transformer-T01 | 2020-08-04 13:34 | 2020-08-04 17:31 | 3:57 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T-1 | 2020-08-06 08:30 | 2020-08-06 13:38 | 5:08 | E/O | Due to red-hot maintenance 33 kV side | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T-3 | 2020-08-13 20:23 | 2020-08-13 20:40 | 0:17 | E/O | Due to red-hot maintenance 33 kV side | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T2 | 2020-08-18 12:56 | 2020-08-18 13:22 | 0:26 | T | Tripped showing Diff. relay at 33 kV side | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T-1 | 2020-08-20 07:54 | 2020-08-20 09:27 | 1:33 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Dhamrai | 132/33 kV Transformer-T-2 | 2020-08-23 22:28 | 2020-08-23 22:47 | 0:19 | T | Tripped showing O/C. relay at 33 kV side | 38 | 12.0333 | Power interruption
Sherpur | 132/33 kV Transformer-T-1 | 2020-08-24 07:10 | 2020-08-24 08:06 | 0:56 | T | Tripped showing search trip oil TC/gas at 33 kV | 0 | 0 | No interruption
| 132/33 kV Transformers-T1 & T-2 | 2020-08-24 22:04 | 2020-08-24 22:28 | 0:24 | T | Tripped showing Bay -3 feeder fault | 0 | 0 | No interruption
Joydevpur | 132/33 kV Transformer-GT-3 | 2020-08-25 05:03 | 2020-08-25 10:30 | 5:27 | T | Tripped showing Overall bias diff. relay | 10 | 54.5 | Power interruption
| 132/33 kV Transformer-T-4 | 2020-08-28 23:46 | 2020-08-29 02:22 | 2:36 | T | Tripped showing Buchholz relay 33 kV | 0 | 0 | No interruption
| 132/33 kV Transformer-T-3 | 2020-08-29 09:32 | 2020-08-29 09:42 | 0:10 | T | Tripped showing O/C. relay | 74 | 57.9667 | Power interruption 09:32 to 10:19
| 132/33 kV Transformer-T-4 | 2020-08-29 09:39 | 2020-08-29 09:39 | 0:00 | T | Tripped showing PRD. relay | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T-3 | 2020-08-30 21:12 | 2020-08-30 23:16 | 2:04 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 23:17 |  | Unserved Energy: |  | 124.5
Dhaka (South) Grid Circle :
Rampura | 230/132 kV Transformer-Tx1 | 2020-08-02 14:27 | 2020-08-02 15:26 | 0:59 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| 132 kV bus-2 | 2020-08-02 14:27 | 2020-08-02 15:19 | 0:52 | E/O | Due to bursting of (R-phase) CT burst | 0 | 0 | No interruption
Ghorashal | 230/132 kV Transformer-T1 | 2020-08-13 09:05 | 2020-08-13 09:55 | 0:50 | T | Tripped showing KF2 & KH3 relay | 0 | 0 | No interruption
Fatulla | 132/33 kV Transformer-T2 | 2020-08-16 09:30 | 2020-08-16 10:38 | 1:08 | T | Tripped showing Lockout relay | 0 | 0 | No interruption
Shyampur(O) | 132/33 kV Transformer-T2 | 2020-08-22 21:55 | 2020-08-22 23:17 | 1:22 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Bhulta | 132/33 kV Transformer-T-1 | 2020-08-24 16:36 | 2020-08-24 17:58 | 1:22 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Maniknagar | 132/33 kV Transformers-T1 | 2020-08-25 09:20 | 2020-08-25 09:52 | 0:32 | E/O | Due to flashing of 33/11 kV Transformer
| 132/33 kV Transformers-T2 | 2020-08-25 09:20 | 2020-08-25 11:38 | 2:18 | E/O |  | 88 | 202.4 | Power interruption 09:20 to 11:38
Munshiganj | 132/33 kV Transformers-T1 | 2020-08-26 17:55 | 2020-08-26 18:26 | 0:31 | T | Due to 33 kV feeder fault | 82 | 42.3667 | Power interruption
| 132/33 kV Transformers-T2 | 2020-08-26 17:55 | 2020-08-26 20:30 | 2:35 | T |  | 0 | 0
Narsinghdi | 132/33 kV Transformer-T3 | 2020-08-30 19:51 | 2020-08-30 21:22 | 1:31 | E/O | Due to red-hot maintenance | 45 | 68.25 | Power interruption
|  |  | Total : | 14:00 |  | Unserved Energy: |  | 313.0167
Chattogram Grid Circle :
Hathazari | 230/132 kV Transformer-MT04 | 2020-08-07 07:23 | 2020-08-07 07:23 | 0:00 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Cox'sbazar | 132/33 kV Transformer-T3 | 2020-08-09 12:55 | 2020-08-09 13:13 | 0:18 | T | Tripped showing E/F relay at 33 kV feeder fault | 25 | 7.5 | Power interruption
Dohazari | 132/33 kV Transformer-T1 | 2020-08-14 05:56 | 2020-08-14 06:26 | 0:30 | T | Tripped showing differential relay | 14 | 7 | Power interruption
Halishahar | 132/33 kV Transformer-T2 | 2020-08-22 21:55 | 2020-08-22 22:53 | 0:58 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Dohazari | 132/33 kV Transformer-T1 | 2020-08-27 17:37 | 2020-08-27 18:04 | 0:27 | T | Tripped showing differential relay at 33 kV | 18 | 8.1 | Power interruption
Modern steel | 132/33 kV Transformer-T1 | 2020-08-28 04:17 | 2020-08-28 07:07 | 2:50 | T | Tripped showing differential relay at 33 kV | 0 | 0 | No interruption
Halishahar | 33 kV upper Bus | 2020-08-28 08:24 | 2020-08-28 10:23 | 1:59 | E/O | Due to red-hot maintenance | 50 | 99.1667 | Power interruption
| 33 kV Bus | 2020-08-31 08:25 | 2020-08-31 10:28 | 2:03 | E/O | Due to red-hot maintenance at 33 kV | 100 | 205 | Power interruption
|  |  | Total : | 9:05 |  | Unserved Energy: |  | 326.7667
Cumilla Grid Circle :
Ramganj | 132/33 kV Transformers-T1 & T2 | 2020-08-01 22:33 | 2020-08-01 22:38 | 0:05 | T | Tripped showing O/C relay | 120 | 10 | Power interruption
| 132/33 kV Transformers-T1 & T2 | 2020-08-02 05:19 | 2020-08-02 05:24 | 0:05 | T |  | 116 | 9.6667 | Power interruption
| 132/33 kV Transformer-T2 | 2020-08-04 21:40 | 2020-08-04 22:25 | 0:45 | E/O | Due to red-hot maintenance at 33 kV Bus | 0 | 0 | No interruption
Chowmuhani | 132/33 kV Transformers-T1 & T3 | 2020-08-06 02:55 | 2020-08-06 03:10 | 0:15 | T | Tripped showing O/C relay at 33 kV side | 136 | 34 | Power interruption
Ashuganj | 230 kV Bus-1 | 2020-08-09 17:38 | 2020-08-09 17:38 | 0:00 | E/O | Due to B-phase loop of 230 kV Midland Ckt snapped | 0 | 0 | No interruption
Comilla(N) | 132/33 kV Transformer-T3 | 2020-08-16 02:15 | 2020-08-16 02:29 | 0:14 | T | Tripped showing O/C & E/F relay | 15 | 3.5 | Power interruption
Kulaura | 132/33 kV Transformer-T1 | 2020-08-16 05:46 | 2020-08-16 13:00 | 7:14 | T | Tripped showing Buchholz & Diff. relay | 23 | 166.3667 | Power interruption
Sreemongal | 132/33 kV Transformer-T1 | 2020-08-16 08:42 | 2020-08-16 09:52 | 1:10 | E/O | Due to red-hot maintenance at 33 kV Bus | 52 | 60.6667 | Power interruption
Sylhet | 132/33 kV Transformers-T2 | 2020-08-17 13:05 | 2020-08-17 19:51 | 6:46 | T | Due to Baroikandi feeder fault
| 132/33 kV Transformers-T4 | 2020-08-17 13:05 | 2020-08-17 23:06 | 10:01 | T
Daudkandi | 132/33 kV Transformer-T3 | 2020-08-17 07:05 | 2020-08-17 09:04 | 1:59 | E/O | Due to red-hot maintenance at 33 kV side | 20 | 39.6667 | Power interruption
Chowmuhani | 132/33 kV Transformer-T3 | 2020-08-17 05:54 | 2020-08-17 05:54 | 0:00 | T | Tripped showing Buchholz & Diff.relay | 0 | 0 | No interruption
Kulaura | 132/33 kV Transformer-T-1 | 2020-08-17 11:31 | 2020-08-17 12:31 | 1:00 | E/O | Due to red-hot maintenance 33 kV side | 29 | 29 | Power interruption
Comilla(N) | 132/33 kV Transformer-T3 | 2020-08-18 05:02 | 2020-08-18 05:33 | 0:31 | T | Tripped showing 33 kV feeder fault | 20 | 10.3333 | Power interruption
Page: 2/3 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: August 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Kulaura | 132/33 kV Transformer-T1 | 2020-08-19 08:35 | 2020-08-19 12:10 | 3:35 | T | Tripped showing O/C relay | 22 | 78.8333 | Power interruption
Comilla(N) | 132/33 kV Transformer-T3 | 2020-08-19 23:19 | 2020-08-19 23:47 | 0:28 | T | Tripped showing O/C relay | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2020-08-20 14:50 | 2020-08-20 15:06 | 0:16 | T | Tripped showing O/C relay at 33 kV side | 0 | 0 | No interruption
Sreemongal | 132/33 kV Transformer-T3 | 2020-08-20 18:15 | 2020-08-21 11:55 | 17:40 | T | Tripped showing PRD relay | 12 | 7 | Power interruption 18:15 to 18:50
Ashuganj | 230 kV Bus-2 | 2020-08-22 00:20 | 2020-08-22 03:05 | 2:45 | T | Tripped showing general protection trip | 0 | 0 | No interruption
Comilla(N) | 132/33 kV Transformer-T3 & T4 | 2020-08-22 10:49 | 2020-08-22 11:09 | 0:20 | T | Tripped showing O/C relay at 33 kV side | 50 | 16.6667 | Power interruption
| 132/33 kV Transformer-T3 | 2020-08-22 22:04 | 2020-08-22 22:43 | 0:39 | T | Tripped showing E/F relay at 33 kV side | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2020-08-22 22:04 | 2020-08-22 23:33 | 1:29 | T |  | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2020-08-26 23:42 | 2020-08-27 00:14 | 0:32 | T | Tripped showing O/C relay at 33 kV side | 15 | 8 | Power interruption
| 132/33 kV Transformer-T3 | 2020-08-27 04:07 | 2020-08-27 04:57 | 0:50 | T | Tripped showing O/C relay at 33 kV side | 0 | 0 | No interruption
Kulaura | 132/33 kV Transformer-T1 | 2020-08-28 15:04 | 2020-08-28 22:12 | 7:08 | T | Tripped showing Buchholz & Diff.relay | 31 | 221.1333 | Power interruption
| 132/33 kV Transformer-T2 | 2020-08-28 15:04 | 2020-08-28 22:15 | 7:11
Chandpur | 132/33 kV Transformer-T5 | 2020-08-31 09:56 | 2020-08-31 11:10 | 1:14 | E/O | Due to red-hot maintenance at 33 kV Bus | 0 | 0 | No interruption
|  |  |  | 74:12 |  | Unserved Energy: |  | 694.8333
Khulna Grid Circle :
Patuakhali | 132/33 kV Transformers-T1 ,& T2 | 2020-08-03 10:58 | 2020-08-03 11:28 | 0:30 | E/O | Due to Y-phase PT burst at 33 kV side | 55 | 27.5 | Power interruption
Bagerhat | 132/33 kV Transformer-T1 | 2020-08-04 16:13 | 2020-08-04 17:55 | 1:42 | E/O | Due to red-hot maintenance | 22 | 37.4 | Power interruption
Faridpur | 132/33 kV Transformer-T2 | 2020-08-05 21:14 | 2020-08-05 23:57 | 2:43 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T1 | 2020-08-06 07:25 | 2020-08-06 07:30 | 0:05 | T | Tripped showing E/F relay at 33 kV side | 0 | 0 | No interruption
Satkhira | 132/33 kV Transformer-T1 | 2020-08-06 08:40 | 2020-08-06 10:09 | 1:29 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T2 | 2020-08-06 09:58 | 2020-08-06 11:15 | 1:17 | E/O | Due to red-hot maintenance at 33 kV side | 15 | 19.25 | Power interruption
Khulna(C) | 132/33 kV Transformer-T3 | 2020-08-06 12:25 | 2020-08-06 13:43 | 1:18 | E/O | Due to red-hot maintenance at 33 kV side | 5 | 6.5 | Power interruption
Satkhira | 132/33 kV Transformer-T2 | 2020-08-07 21:07 | 2020-08-08 12:12 | 15:05 | E/O | Due to red-hot maintenance at 33 kV side | 10 | 150.8333 | Power interruption
Faridpur | 132/33 kV Transformer-T2 | 2020-08-08 11:25 | 2020-08-08 12:26 | 1:01 | E/O | Due to Oil leakage | 35 | 35.5833 | Power interruption
Norail | 132/33 kV Transformer-T1 | 2020-08-09 08:53 | 2020-08-09 10:40 | 1:47 | E/O | Due to red-hot maintenance | 15 | 26.75 | Power interruption
| 132/33 kV Transformer-T2 | 2020-08-09 10:50 | 2020-08-09 11:16 | 0:26 | E/O | Due to red-hot maintenance | 6 | 2.6 | Power interruption
Gopalganj(O) | 132/33 kV Transformers-T1 ,& T2 | 2020-08-09 15:04 | 2020-08-09 15:18 | 0:14 | T | Tripped showing E/F relay at 33 kV side | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T1 | 2020-08-12 06:19 | 2020-08-12 09:23 | 3:04 | E/O | Due to red-hot maintenance | 18 | 55.2 | Power interruption
| 132/33 kV Transformer-T2 | 2020-08-13 17:02 | 2020-08-13 18:24 | 1:22 | E/O | Due to red-hot maintenance | 9 | 12.3 | Power interruption
Barishal(S) | 132/33 kV Transformers-T1 & T2 | 2020-08-15 08:48 | 2020-08-15 09:03 | 0:15 | E/O | Due to flashing at 33 kV Bus | 70 | 17.5 | Power interruption
Barishal(O) | 132/33 kV Transformer-T2 | 2020-08-19 15:50 | 2020-08-19 15:56 | 0:06 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
Goalpara | 132/33 kV Transformer-T6 | 2020-08-22 06:17 | 2020-08-22 08:45 | 2:28 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T1 & T3 | 2020-08-22 07:24 | 2020-08-22 08:58 | 1:34 | E/O | Due to red-hot maintenance | 40 | 62.6667 | Power interruption
Gopalganj(O) | 132/33 kV Transformer-T1 | 2020-08-25 07:42 | 2020-08-25 08:29 | 0:47 | E/O | Due to red-hot maintenance 33 kV side | 25 | 19.5833 | Power interruption
Mongla | 132/33 kV Transformer-T1 | 2020-08-25 09:03 | 2020-08-25 10:42 | 1:39 | E/O | Due to red-hot maintenance | 16 | 26.4 | Power interruption
Bagerhat | 132/33 kV Transformers-T1 & T2 | 2020-08-26 10:17 | 2020-08-26 10:23 | 0:06 | T | Due to 33 kV feeder fault | 26 | 2.6 | Power interruption
|  |  | Total : | 38:58 |  | Unserved Energy: |  | 502.6667
HVDC Grid Circle :
Jhenidah | 33 kV Bus | 2020-08-06 17:10 | 2020-08-06 17:56 | 0:46 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Bottail | 132/33 kV Transformer-T1 | 2020-08-07 11:02 | 2020-08-07 12:12 | 1:10 | E/O | Due to red-hot maintenance | 15 | 17.5 | Power interruption
Jhenidah | 132/33 kV Transformer-T1 | 2020-08-08 14:28 | 2020-08-08 17:04 | 2:36 | E/O | Due to red-hot maintenance 33 kV side | 36 | 93.6 | Power interruption
| 132/33 kV Transformer-T1 | 2020-08-09 08:11 | 2020-08-09 10:15 | 2:04 | E/O | Due to red-hot maintenance at Y-phase CB | 30 | 62 | Power interruption
Ishurdi | 230/132 kV Transformers-T3 | 2020-08-09 14:58 | 2020-08-09 17:53 | 2:55 | T | Tripped showing load tap changer trip signal | 0 | 0 | No interruption
Gallamari | 132/33 kV Transformers-T1 & T2 | 2020-08-11 16:33 | 2020-08-11 16:34 | 0:01 | T | Due to 33 kV kV feeder fault | 38 | 0.63333 | Power interruption
Ishurdi | 132/33 kV Transformer-T1 | 2020-08-26 11:55 | 2020-08-26 15:08 | 3:13 | E/O | Due to red-hot maintenance 33 kV side | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-08-27 21:25 | 2020-08-27 22:15 | 0:50 | E/O | Due to winding temperature high at 33 kV | 0 | 0 | No interruption
|  |  | Total : | 13:35 |  |  |  | 173.7333
Bogura Grid Circle:
Rajshahi | 132/33 kV Transformer-T2 | 2020-08-01 02:40 | 2020-08-01 03:46 | 1:06 | E/O | Due to red-hot maintenance | 35 | 38.5 | Power interruption
Juldhaka | 132/33 kV Transformer-T1 | 2020-08-02 00:55 | 2020-08-02 01:50 | 0:55 | E/O | Due to red-hot maintenance | 16 | 14.6667 | Power interruption
Amnura | 132/33 kV Transformer-T1 | 2020-08-02 21:10 | 2020-08-02 21:22 | 0:12 | T | Tripped showing O/C relay | 34 | 6.8 | Power interruption
Barapukuria | 132/33 kV Transformer-T4 | 2020-08-03 15:24 | 2020-08-17 20:35 | 341:11 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Purbasadipur | 132/33 kV Transformer-T1 | 2020-08-03 18:50 | 2020-08-03 19:40 | 0:50 | E/O | Due to red-hot maintenance 33 kV side | 20 | 16.6667 | Power interruption
Page: 3/3 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: August 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle:
Niyamatpur | 132/33 kV Transformer-T1 | 2020-08-04 10:10 | 2020-08-04 12:14 | 2:04 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Bogura | 230/132 kV Transformers-T3 & T4 & 33 kV Bus | 2020-08-04 21:57 | 2020-08-04 23:12 | 1:15 | E/O | Due to red-hot maintenance 33 kV side | 45 | 56.25 | Power interruption
Palashbari | 132/33 kV Transformer-T4 | 2020-08-04 22:40 | 2020-08-04 23:58 | 1:18 | E/O | Due to red-hot maintenance 33 kV side | 20 | 26 | Power interruption
Barapukuria | 132/33 kV Transformer-T3 | 2020-08-05 00:10 | 2020-08-05 01:45 | 1:35 | E/O | Due to red-hot maintenance 33 kV side | 37 | 58.5833 | Power interruption
Natore | 132/33 kV Transformer-T2 | 2020-08-09 07:13 | 2020-08-09 08:47 | 1:34 | E/O | Due to red-hot maintenance 33 kV side | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformer-T3 | 2020-08-10 06:18 | 2020-08-10 07:20 | 1:02 | E/O | Due to red-hot maintenance 33 kV side | 7 | 7.2333 | Power interruption
| 132/33 kV Transformer-T3 | 2020-08-10 10:02 | 2020-08-10 11:30 | 1:28 | E/O | Due to 33 kV kV CT Oil leakage | 5 | 7.3333 | Power interruption
Naogaon | 132/33 kV Transformer-T3 | 2020-08-10 13:02 | 2020-08-10 19:05 | 6:03 | E/O |  | 0 | 0 | No interruption
Niyamatpur | 132/33 kV Transformer-T3 | 2020-08-12 10:44 | 2020-08-12 18:30 | 7:46 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Natore | 132/33 kV Transformers-T1 & T2 | 2020-08-18 07:04 | 2020-08-18 08:31 | 1:27 | E/O | Due to red-hot maintenance 33 kV side | 58 | 84.1 | Power interruption
Palashbari | 132/33 kV Transformer-T3 | 2020-08-19 19:26 | 2020-08-19 20:31 | 1:05 | E/O | Due to red-hot maintenance 33 kV side | 20 | 21.6667 | Power interruption
Barapukuria | 132/33 kV Transformer-T4 | 2020-08-20 17:07 | 2020-08-20 21:19 | 4:12 | T | Tripped showing lockout relay | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2020-08-21 21:34 | 2020-08-22 09:15 | 11:41 | T |  | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2020-08-22 11:58 | 2020-08-22 17:55 | 5:57 | T | Tripped showing O/C relay | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2020-08-23 12:01 | 2020-08-23 13:04 | 1:03 | T | Tripped showing 33 kV feeder fault | 0 | 0 | No interruption
| 132/33 kV Transformer-T5 | 2020-08-25 08:40 | 2020-08-25 10:40 | 2:00 | E/O | Due to red-hot maintenance of 132 kV isolator | 0 | 0 | No interruption
| 132 kV Bus-2 | 2020-08-25 08:40 | 2020-08-25 10:50 | 2:10 |  |  | 0 | 0 | No interruption
C.nawabganj | 132/33 kV Transformer-T1 | 2020-08-26 23:40 | 2020-08-26 23:52 | 0:12 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T3 | 2020-08-28 15:04 | 2020-08-28 16:20 | 1:16 | T | Tripped showing E/F relay at 33 kV | 29 | 36.7333 | Power interruption
Barapukuria | 230/132 kV Transformer-T1 | 2020-08-31 20:33 | 2020-08-31 20:53 | 0:20 | T
|  |  | Total : | 399:42 |  |  |  | 374.5333
Others :
Ashuganj | 132/33 kV Transformer-OAT12 | 2020-08-22 00:20 | 2020-08-26 16:16 | 111:56 | T | Tripped showing master protection relay | 0 | 0 | No interruption
|  |  | Total : | 111:56 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 684:45 | Hours
T = Tripping
E/O = Emergency Outage
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/3 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: August 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tongi | Tongi-Kabirpur 132 kV line-2 | 2020-08-12 10:32 | 2020-08-12 10:40 | 0:08 | T | Tripped showing dist.relay | 0 | 0 | No interruption
| Tongi-Kabirpur 132 kV line-1 | 2020-08-23 09:43 | 2020-08-23 10:10 | 0:27 | T | Tripped showing dist.& E/F relay | 300 | 135 | Power interruption
| Tongi-Kabirpur 132 kV line-2 | 2020-08-23 09:43 | 2020-08-23 10:05 | 0:22 | T
Kabirpur | Kabirpur-Manikganj 132 kV line-1 | 2020-08-23 09:43 | 2020-08-23 10:10 | 0:27 | T
Kadda | Kadda-Gazipur 100 MW 132 kV line | 2020-08-23 09:43 | 2020-08-23 10:08 | 0:25 | T | Tripped showing O/C & dist. relay | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tangail 132 kV line-1 | 2020-08-23 10:06 | 2020-08-23 10:19 | 0:13 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Mymensingh | Mymensingh-Bhaluka 132 kV line-2 | 2020-08-23 13:31 | 2020-08-23 14:18 | 0:47 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Jamalpur | Jamalpur-United Mymensingh Power 132 kV line-1 & 2 | 2020-08-24 22:04 | 2020-08-24 22:28 | 0:24 | T | Tripped showing O/C . relay | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-1 | 2020-08-29 17:07 | 2020-08-29 17:16 | 0:09 | T | Tripped showing O/C . relay | 0 | 0 | No interruption
| Tongi-Kabirpur 132 kV line-2 | 2020-08-29 17:07 | 2020-08-29 17:28 | 0:21 | T | Tripped showing dist. relay | 325 | 113.75 | Power interruption
Mymensingh RPCL | Mymensingh RPCL-Mymensingh S/S 132 kV line-1 | 2020-08-30 03:12 | 2020-08-30 03:34 | 0:22 | T | Tripped showing O/C . relay | 0 | 0 | No interruption
| Mymensingh RPCL-Mymensingh S/S 132 kV line-2 | 2020-08-30 03:12 | 2020-08-30 03:35 | 0:23 | T
Tongi | Tongi-Kabirpur 132 kV line-1 & 2 | 2020-08-30 11:42 | 2020-08-30 11:55 | 0:13 | T | Tripped showing dist. relay | 350 | 75.8333 | Power interruption
| Tongi-Kabirpur 132 kV line-1 | 2020-08-30 12:20 | 2020-08-30 12:26 | 0:06 | T
| Tongi-Kabirpur 132 kV line-2 | 2020-08-30 12:20 | 2020-08-30 17:04 | 4:44 | T
Aminbazar | Aminbazar-Manikganj 160 MW P/S 132 kV line-1 | 2020-08-31 09:39 | 2020-08-31 09:39 | 0:00 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 9:31 |  | Unserved Energy: |  | 324.5833
Dhaka (South) Grid Circle :
Ghorashal | Ghorashal-Ashuganj(S) 230 kV-1 | 2020-08-07 12:19 | 2020-08-07 13:40 | 1:21 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ghorashal-Ashuganj(S) 230 kV-2 | 2020-08-07 12:19 | 2020-08-07 12:58 | 0:39 | T |  | 0 | 0 | No interruption
| Ghorashal-Ashuganj(S) 230 kV-2 | 2020-08-12 03:27 | 2020-08-12 05:04 | 1:37 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ghorashal-Ashuganj(S) 230 kV-1 | 2020-08-12 06:50 | 2020-08-12 07:44 | 0:54 | T | Tripped showing SOTF. relay | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV line-1 | 2020-08-12 16:35 | 2020-08-12 16:47 | 0:12 | T | Tripped showing lock out relay | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Matuail 132 kV line | 2020-08-16 09:59 | 2020-08-16 10:18 | 0:19 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Haripur | Haripur-Narsinghdi 132 kV line | 2020-08-16 12:57 | 2020-08-17 07:35 | 18:38 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Haripur-Bhulta 132 kV line | 2020-08-17 20:10 | 2020-08-17 20:37 | 0:27 | T | Tripped showing Backup protection . relay | 0 | 0 | No interruption
Shyampur(N) | Shyampur(N)-Shyampur (O) 132 kV line-1 | 2020-08-19 22:05 | 2020-08-19 22:38 | 0:33 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 132 kV line | 2020-08-21 12:06 | 2020-08-21 13:50 | 1:44 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj(S) 230 kV-2 | 2020-08-22 03:46 | 2020-08-22 05:04 | 1:18 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ghorashal-Ashuganj(S) 230 kV-2 | 2020-08-22 05:04 | 2020-08-22 15:56 | 10:52 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 132 kV line | 2020-08-22 06:30 | 2020-08-22 07:02 | 0:32 | T | Tripped showing dist. relay | 100 | 53.3333 | Power interruption
Madanganj S/S | Madanganj S/S-Madaganj P/S 132 kV line | 2020-08-24 18:08 | 2020-08-24 20:40 | 2:32 | T | Tripped showing O/C.& E/F relay | 0 | 0 | No interruption
Bhulta | Bhulta-Haripur 132 kV line | 2020-08-24 17:22 | 2020-08-24 18:08 | 0:46 | E/O | Due to red-hot maintenance | 50 | 38.3333 | Power interruption
Haripur | Haripur-Madanganj 132 kV line | 2020-08-26 17:55 | 2020-08-26 19:05 | 1:10 | T | Tripped showing auxiliary Transformer fault | 0 | 0 | No interruption
| Haripur-Haripur P/S 230 kV line-1 | 2020-08-30 11:27 | 2020-08-30 12:09 | 0:42 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
|  |  | Total : | 44:16 |  | Unserved Energy: |  | 91.6667
Chittagong Grid Circle :
Sikalbaha | Sikalbaha-Juldah 132 kV line | 2020-08-02 12:07 | 2020-08-02 12:24 | 0:17 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Dohazari | Dohazari-Sikalbaha 132 kV libne-1 | 2020-08-05 12:33 | 2020-08-05 19:44 | 7:11 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Dohazari-Sikalbaha 132 kV libne-2 | 2020-08-05 12:45 | 2020-08-05 12:48 | 0:03 | T | Tripped showing General trip . relay | 40 | 2 | Power interruption
Madunaghat | Madunaghat-Chandraghona 132 kV line-2 | 2020-08-08 12:05 | 2020-08-08 12:17 | 0:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Khulshi | Khulshi-Halishahar 132 kV line-2 | 2020-08-11 21:20 | 2020-08-11 23:23 | 2:03 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Dohazari 132 kV line-2 | 2020-08-15 13:14 | 2020-08-15 13:33 | 0:19 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Sikalbaha-Dohazari 132 kV line-1 | 2020-08-16 09:31 | 2020-08-16 15:48 | 6:17 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hathazari | Hathazari-Kaptai 132 kV line-1 & 2 | 2020-08-22 03:36 | 2020-08-22 04:30 | 0:54 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Hathazari-Baroierhat 132 kV line-1 & 2 | 2020-08-24 17:51 | 2020-08-24 17:58 | 0:07 | T | Tripped showing dist. E/F relay | 0 | 0 | No interruption
| Hathazari-Raozan P.P. 230 kV line-1 | 2020-08-26 10:39 | 2020-08-27 15:27 | 28:48 | E/O | Due to Oil leakage | 0 | 0 | No interruption
| Hathazari-Baroaulia 132 kV line-1 | 2020-08-26 16:11 | 2020-08-27 13:07 | 20:56 | T | Tripped showing dist. E/F relay | 0 | 0 | No interruption
Dohazari | Dohazari-Sikalbaha 132 kV line-2 | 2020-08-29 13:11 | 2020-08-29 14:23 | 1:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 68:19 |  | Unserved Energy: |  | 2
Page: 2/3 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: August 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Ramganj | Ramganj-Chandpur 132 kV line-1 | 2020-08-01 11:30 | 2020-08-01 12:50 | 1:20 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sreemongal 132 kV line-1 | 2020-08-05 17:13 | 2020-08-05 17:41 | 0:28 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Fenchuganj-Sreemongal 132 kV line-2 | 2020-08-05 17:13 | 2020-08-05 17:42 | 0:29 | T |  | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Shahjibazar 230 kV line-2 | 2020-08-07 08:20 | 2020-08-07 11:01 | 2:41 | T | Tripped showing dist. relay | 0 | 0 | No interruption
S.M. Nagar | S.M. Nagar-Cumilla(S) 132 kV line-1 & 2 | 2020-08-10 19:53 | 2020-08-10 20:39 | 0:46 | T | Tripped showing dist. relay | 146 | 111.9333 | Power interruption
Sylhet | Sylhet-Chatak 132 kV line-1 | 2020-08-11 01:40 | 2020-08-11 01:40 | 0:00 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Choddagram 132 kV line-2 | 2020-08-12 12:15 | 2020-08-12 12:38 | 0:23 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Cumilla(N)-Choddagram 132 kV line-2 | 2020-08-12 13:18 | 2020-08-12 15:51 | 2:33 | T | Tripped showing dist.(B-phase) relay | 0 | 0 | No interruption
| Cumilla(N)-Choddagram 132 kV line-2 | 2020-08-12 16:29 | 2020-08-12 18:34 | 2:05 | T | Tripped showing dist.(B-phase) relay | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Surjimoninagar 132 kV line | 2020-08-14 19:29 | 2020-08-14 20:12 | 0:43 | E/O | Due to deloaded black out at Surjamoninagar | 160 | 114.6667 | Power interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2020-08-14 20:30 | 2020-08-14 21:07 | 0:37 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV line-2 | 2020-08-15 21:09 | 2020-08-15 21:28 | 0:19 | T | Tripped showing OTT2.Gen.trip .relay | 0 | 0 | No interruption
| Ashuganj-Cumilla(N) 230 kV line-1 | 2020-08-18 08:27 | 2020-08-18 13:49 | 5:22 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
| Ashuganj-Midland P/S 230 kV line | 2020-08-18 10:20 | 2020-08-18 10:20 | 0:00 | T | Tripped showing Diff. relay | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV line-1 | 2020-08-21 22:56 | 2020-08-22 00:20 | 1:24 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj(S)-Ashuganj 230 kV line-1 | 2020-08-22 00:20 | 2020-08-22 00:20 | 0:00 | T | Tripped showing main protection. relay | 0 | 0 | No interruption
| Ashuganj-Cumilla(N) 230 kV line-1 | 2020-08-22 00:20 | 2020-08-22 00:20 | 0:00 | T |  | 0 | 0 | No interruption
Rangamati | Rangamati-Chandraghona 132 kV line-1 | 2020-08-22 03:38 | 2020-08-22 03:49 | 0:11 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2020-08-23 16:25 | 2020-08-24 10:58 | 18:33 | E/O | Due to flashing of Y-phase line DS | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Meghnaghat 230 kV line-2 | 2020-08-24 15:25 | 2020-08-24 16:16 | 0:51 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-2 | 2020-08-28 14:26 | 2020-08-28 14:53 | 0:27 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV line-1 | 2020-08-29 00:50 | 2020-08-29 01:32 | 0:42 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 kV line-2 | 2020-08-30 03:12 | 2020-08-30 03:46 | 0:34 | T | Tripped showing dist. relay
| Ashuganj-Kishoreganj 132 kV line-1 | 2020-08-30 03:12 | 2020-08-30 03:49 | 0:37 | T |  | 700 | 396.6667 | Power interruption
Fenchuganj | Fenchuganj-Kulaura 132 kV line-1 | 2020-08-30 04:21 | 2020-08-30 04:55 | 0:34 | T | Tripped showing dist. relay | 25 | 15.4167 | Power interruption
| Fenchuganj-Kulaura 132 kV line-2 | 2020-08-30 04:21 | 2020-08-30 04:50 | 0:29 | T
Cumilla(S) | Cumilla(S)-Tripura 132 kV line-1& 2 | 2020-08-31 07:56 | 2020-08-31 08:58 | 1:02 | E/O | Due to main power failure | 130 | 62.8333 | Power interruption
|  |  | Total : | 43:10 |  | Unserved Energy: |  | 701.5167
Khulna Grid Circle :
Bhola | Bhola-Barishal 230 kV line-2 | 2020-08-04 03:06 | 2020-08-04 04:06 | 1:00 | T | Tripped showing dist.carrier trip & bad weather | 0 | 0 | No interruption
Barishal | Barishal-Barishal GT 132 kV line | 2020-08-04 04:00 | 2020-08-04 04:52 | 0:52 | T | Tripped showing O/C relay | 0 | 0 | No interruption
| Barishal(N)-Madaripur 132 kV line-1 | 2020-08-04 09:29 | 2020-08-04 11:18 | 1:49 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Magura | Magura-Narail 132 kV line-2 | 2020-08-07 09:44 | 2020-08-07 11:20 | 1:36 | E/O | Due to red-hot maintenance | 28 | 44.8 | Power interruption
Bagerhat | Bagerhat-Mongla 132 kV line | 2020-08-10 18:25 | 2020-08-10 18:55 | 0:30 | T | Tripped showing dist. relay | 26 | 13 | Power interruption
Goalpara | Goalpara-Rupsha P/P -Bageraht 132 kV line | 2020-08-17 11:40 | 2020-08-17 12:14 | 0:34 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Barishal | Barishal-Patuakhali 132 kV line | 2020-08-21 21:47 | 2020-08-21 22:30 | 0:43 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Goalpara | Goalpara-Khulna© 132 kV line-2 | 2020-08-27 15:04 | 2020-08-27 17:18 | 2:14 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Khulna Zone | All 230 kV and 132 kV Ckts tripped | 2020-08-29 10:15 | 2020-08-29 15:20 | 5:05 | T | Kahulna and Barishal Zone outage | 965 | 4905.4167 | Power interruption
Barishal Zone | All 230 kV and 132 kV Ckts tripped | 2020-08-29 10:15 | 2020-08-29 13:40 | 3:25 | T |  | 216 | 738 | Power interruption
Jashore | Jashore-Noapara 132 kV line-1 | 2020-08-29 11:27 | 2020-08-29 15:17 | 3:50 | E/O | Due to bursting of L/A | 0 | 0 | No interruption
Barishal | Barishal-Goalpara 132 kV line | 2020-08-29 19:24 | 2020-08-29 19:33 | 0:09 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Bagerhat | Bagerhat-Goalpara 132 kV line | 2020-08-29 19:24 | 2020-08-29 19:33 | 0:09 | T | Tripped showing O/C relay | 185 | 27.75 | Power interruption
| Bagerhat-Oriaon P.S 132 kV line | 2020-08-29 19:24 | 2020-08-29 19:37 | 0:13 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Khulna© | Khulna©-Goalpara 132 k line-2 | 2020-08-30 08:16 | 2020-08-30 10:18 | 2:02 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Barishal(N) | Barishal(N)-Bhola 230 kV line-1 | 2020-08-31 21:24 | 2020-08-31 22:17 | 0:53 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 25:04 |  | Unserved Energy: |  | 5728.9667
Page: 3/3 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: August 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :
Bharamara | Bharamara-Ishurdi 132 kV line-1 | 2020-08-02 13:51 | 2020-08-02 14:14 | 0:23 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Jashore | Jashore-Jhenidah 132 kV line-2 | 2020-08-04 12:26 | 2020-08-04 13:08 | 0:42 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Ishurdi | Ishurdi-Natore 132 kV line-1 | 2020-08-02 13:51 | 2020-08-02 15:08 | 1:17 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ishurdi-Ghorashal 230 kV line-2 | 2020-08-26 07:55 | 2020-08-26 09:55 | 2:00 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ishurdi-Natore 132 kV line-1 | 2020-08-29 10:20 | 2020-08-30 16:09 | 29:49 | T |  | 0 | 0 | No interruption
| Ishurdi-Baghabari-132 kV line | 2020-08-29 10:15 | 2020-08-29 12:05 | 1:50 | T |  | 0 | 0 | No interruption
| Ishurdi-Bharamara-132 kV line-1 | 2020-08-29 10:15 | 2020-08-29 12:42 | 2:27 | T | Kahulna and Barishal Zone outage | 0 | 0 | No interruption
| Ishurdi-Bharamara-132 kV line-2 | 2020-08-29 10:21 | 2020-08-29 12:41 | 2:20 | T |  | 0 | 0 | No interruption
| Ishurdi- 230 Kv HVDC 3, | 2020-08-29 10:15 | 2020-08-29 11:13 | 0:58 | T |  | 0 | 0 | No interruption
| Ishurdi-HVDC 4 | 2020-08-29 10:15 | 2020-08-29 10:53 | 0:38 | T |  | 0 | 0 | No interruption
| Ishurdi-Ghorashal 230 kV line-1 | 2020-08-29 10:15 | 2020-08-29 11:50 | 1:35 | T |  | 0 | 0 | No interruption
| Ishurdi-Ghorashal 230 kV line-2 | 2020-08-29 10:15 | 2020-08-29 12:59 | 2:44 | T |  | 0 | 0 | No interruption
| Ishurdi-Bharamara-132 kV line-2 | 2020-08-29 10:21 | 2020-08-29 12:41 | 2:20 | T
|  |  | Total : | 49:03 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Natore | Natore-Bogura 132 kV line-2 | 2020-08-09 09:01 | 2020-08-09 09:36 | 0:35 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rajshahi(N) | Rajshahi(N)-C.nawabganj 132 kV line | 2020-08-16 07:12 | 2020-08-16 10:35 | 3:23 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Rangpur | Rangpur-Rangpur confidence 132 k line-2 | 2020-08-21 20:08 | 2020-08-21 23:29 | 3:21 | E/O | Due to Oil leakage | 5 | 16.75 | Power interruption
Natore | Natore-Bogura 132 kV line-1 | 2020-08-22 10:57 | 2020-08-23 17:39 | 30:42 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Palashbari | Palashbari-Mohasthangarth 132 kV line-1 | 2020-08-23 20:17 | 2020-08-23 20:20 | 0:03 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Palashbari-Mohasthangarth 132 kV line-2 | 2020-08-23 20:17 | 2020-08-23 20:55 | 0:38 | T |  | 0 | 0 | No interruption
Noapara S/S | Noapara S/S-Khanzahan Ali 33 kV line | 2020-08-28 09:13 | 2020-08-28 11:25 | 2:12 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Rangpur confidence | Rangpur confidence-Rangpur S/S 132 kV line-1 | 2020-08-28 14:20 | 2020-08-28 15:07 | 0:47 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
| Rangpur confidence-Palashbari 132 kV line-2 | 2020-08-28 15:16 | 2020-08-28 16:05 | 0:49 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Bogura (N) | Bogura (N)-Bogura (O) 132 kV line-1 | 2020-08-29 07:34 | 2020-08-29 09:36 | 2:02 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Rajshahi | Rajshahi-HVDC 230 kV line-2 | 2020-08-29 10:14 | 2020-08-29 12:08 | 1:54 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Rajshahi(O) | Rajshahi(O)-Rajshahi (n) 132 kV line-2 | 2020-08-29 16:44 | 2020-08-29 16:57 | 0:13 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Sirajganj | Sirajganj-Baghabari 230 kV line-2 | 2020-08-30 19:42 | 2020-08-30 21:03 | 1:21 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
| Sirajganj-Baghabari 230 kV line-2 | 2020-08-30 06:05 | 2020-08-30 09:03 | 2:58 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Rajshahi(O) | Rajshahi(O)-Rajshahi (n) 132 kV line-2 | 2020-08-31 11:28 | 2020-08-31 12:38 | 1:10 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Palashbari | Palashbari-Mohasthangarth 132 kV line-1 | 2020-08-31 20:33 | 2020-08-31 20:39 | 0:06 | T | Tripped showing dist. relay | 762 | 1930.4 | Power interruption 20:33 to 23:05
| Palashbari-Mohasthangarth 132 kV line-2 | 2020-08-31 20:33 | 2020-08-31 21:12 | 0:39 | T
Barapukuria | Barapukuria-Saidpur 132 kV line-1 | 2020-08-31 20:33 | 2020-08-31 20:44 | 0:11 | T | Tripped showing O/C relay | 0 | 0
|  |  | Total : | 53:04 |  | Unserved Energy: |  | 1947.15
Others :Nil
|  |  | Total : | 0:00 |  |  |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 341:30 | Hours
T = Tripping | [7 empty] | Executive Engineer
E/O = Emergency Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/3 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:August 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Netrakona | 132/33 kV Transformers-T1 | 2020-08-04 07:05 | 2020-08-04 07:28 | 0:23 | S/O | Due to C/M work | 20 | 7.6667 | Power interruption
| 132/33 kV Transformers-T2 | 2020-08-04 07:26 | 2020-08-04 07:40 | 0:14 | S/O
Kishoreganj | 132/33 kV Transformer-T1 | 2020-08-05 10:20 | 2020-08-05 12:06 | 1:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T2 | 2020-08-05 08:19 | 2020-08-05 12:03 | 3:44 | S/O | Due to C/M work | 20 | 74.6667 | Power interruption
Kabirpur | 132 kV Bus-1 | 2020-08-05 07:06 | 2020-08-05 09:26 | 2:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T2 | 2020-08-06 09:39 | 2020-08-06 11:12 | 1:33 | S/O | Due to C/M work | 10 | 15.5 | Power interruption
Netrakona | 132/33 kV Transformer-T2 | 2020-08-07 07:08 | 2020-08-07 17:55 | 10:47 | S/O | Due to C/M work | 30 | 323.5 | Power interruption
| 132/33 kV Transformer-T1 | 2020-08-08 07:03 | 2020-08-08 07:03 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T3 | 2020-08-08 07:12 | 2020-08-08 10:50 | 3:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T1 | 2020-08-09 07:02 | 2020-08-09 17:30 | 10:28 | S/O | Due to C/M work | 5 | 52.3333 | Power interruption
Uttara | 132/33 kV Transformer-T1 | 2020-08-10 09:21 | 2020-08-10 09:21 | 0:00 | S/O | Due to fire protection installation work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T2 | 2020-08-11 06:07 | 2020-08-11 07:18 | 1:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T2 | 2020-08-11 10:16 | 2020-08-11 14:56 | 4:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T3 | 2020-08-11 11:54 | 2020-08-11 12:44 | 0:50 | S/O | Due to spring change | 0 | 0 | No interruption
Uttara | 132/33 kV Transformer-T2 | 2020-08-11 13:38 | 2020-08-11 13:38 | 0:00 | S/O | Due to installation work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 |  | 2020-08-11 15:37 |  | S/O | After maintenance work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 |  | 2020-08-11 15:42 |  | S/O |  | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T2 | 2020-08-12 06:15 | 2020-08-12 08:52 | 2:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T1 | 2020-08-14 07:05 | 2020-08-14 08:10 | 1:05 | S/O | Due to C/M work | 35 | 37.9167 | Power interruption
Kabirpur | 132/33 kV Transformer-T2 | 2020-08-14 07:36 | 2020-08-14 11:42 | 4:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T2 | 2020-08-16 09:07 | 2020-08-16 21:25 | 12:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T1 |  | 2020-08-16 09:07 |  |  | After maintenance work | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T1 | 2020-08-17 09:25 | 2020-08-17 16:29 | 7:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T02 | 2020-08-17 15:48 | 2020-08-17 17:26 | 1:38 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-08-19 08:55 | 2020-08-19 11:09 | 2:14 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-08-19 11:20 | 2020-08-19 18:13 | 6:53 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T3 | 2020-08-20 06:16 | 2020-08-20 08:59 | 2:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T2 | 2020-08-20 09:41 | 2020-08-20 09:41 |  | S/O | Due to D/W work | 0 | 0 | No interruption
Sylhet | 132/33 kV Transformer-T1 & 33 kV Bus | 2020-08-21 07:58 | 2020-08-21 11:58 | 4:00 | S/O | Due to C/M work | 30 | 120 | Power interruption
Kishoreganj | 132/33 kV Transformer-T3 | 2020-08-22 17:35 | 2020-08-22 17:53 | 0:18 | S/O | Due to maintenance work | 8 | 2.4 | Power interruption
Aminbazar | 230/132 kV Transformer-T02 | 2020-08-23 11:37 | 2020-08-23 18:48 | 7:11 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | 132 kV Metro Rail Bay | 2020-08-23 13:22 | 2020-08-26 20:30 | 79:08 | S/O | Due to D/W work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T3 | 2020-08-23 11:30 | 2020-08-23 11:55 | 0:25 | S/O | Due to maintenance work | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T3 |  | 2020-08-25 23:30 |  | S/O | After replacement work | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T03 | 2020-08-25 08:54 | 2020-08-25 18:28 | 9:34 | S/O | Due to D/W work | 0 | 0 | No interruption
Joydevpur | 132/33 kV Transformer-T3 | 2020-08-25 14:20 | 2020-08-25 15:30 | 1:10 | S/O | Due to replacement work | 12 | 14 | Power interruption
| 132/33 kV Transformer-T2 | 2020-08-26 06:11 | 2020-08-26 07:11 | 1:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2020-08-26 06:40 | 2020-08-26 07:31 | 0:51 | S/O | Due to maintenance work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2020-08-27 06:10 | 2020-08-27 08:25 | 2:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T1 | 2020-08-28 07:21 | 2020-08-28 11:48 | 4:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi new | 132/33 kV Transformer-T1 | 2020-08-28 07:18 | 2020-08-28 08:10 | 0:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T1 | 2020-08-28 07:05 | 2020-08-28 22:20 | 15:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi(O) | 132/33 kV Transformer-T2 | 2020-08-28 09:37 | 2020-08-28 10:55 | 1:18 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-T02 | 2020-08-29 09:20 | 2020-08-29 09:58 | 0:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T2 | 2020-08-29 09:16 | 2020-08-29 11:05 | 1:49 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 212:23 |  | Unserved Energy: |  | 647.9833
Dhaka (South) Grid Circle :
Rampura | 132 kV bus-2 | 2020-08-02 21:44 | 2020-08-03 07:17 | 9:33 | S/O | Due to replacement work | 0 | 0 | No interruption
Hasnabad | 230/132 kV Transformer-T02 | 2020-08-04 07:39 | 2020-08-04 21:05 | 13:26 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-T03 | 2020-08-05 08:02 | 2020-08-05 16:15 | 8:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Munshiganj | 132/33 kV Transformer-T1 | 2020-08-06 09:15 | 2020-08-06 09:30 | 0:15 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-08-06 10:00 | 2020-08-06 10:15 | 0:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Page: 2/3 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:August 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (South) Grid Circle :
Bashundhara | 132/33 kV Transformer-T1 | 2020-08-10 10:07 | 2020-08-10 10:07 | 0:00 | S/O | Due to fire protection installation work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-08-11 12:49 | 2020-08-11 12:49 | 0:00 | S/O | Due to installation work | 0 | 0 | No interruption
Ghorashal | 230 kV Bus section-4 | 2020-08-13 16:25 | 2020-08-13 17:02 | 0:37 | S/O | Due to isolator line breaker of ghorashal-Ashuganj 230 kV line | 0 | 0 | No interruption
Munshiganj | 132/33 kV Transformer-T1 & 33 kV Bus | 2020-08-16 07:05 | 2020-08-16 09:05 | 2:00 | S/O | Due to isolator maintenance | 35 | 70 | Power interruption
Ghorashal | 230/132 kV Transformer-AT02 | 2020-08-16 09:01 | 2020-08-16 18:45 | 9:44 | S/O | Due to replacement work | 0 | 0 | No interruption
Bhulta | 132/33 kV Transformer-T1 | 2020-08-21 08:11 | 2020-08-21 17:12 | 9:01 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-08-28 10:45 | 2020-08-28 12:05 | 1:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Madanganj | 132 kV main Bus | 2020-08-29 08:36 | 2020-08-29 18:59 | 10:23 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 64:47 |  | Unserved Energy: |  | 70
Chattogram Grid Circle :
Dohazari | 132/33 kV Transformer-T2 | 2020-08-05 12:24 | 2020-08-05 14:23 | 1:59 | S/O | Due to relay change | 0 | 0 | No interruption
Hathazari | 230/132 kV Transformer-MT4 | 2020-08-06 09:24 | 2020-08-06 21:07 | 11:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Madunaghat | 132/33 kV Transformer-T1 | 2020-08-08 11:06 | 2020-08-08 12:58 | 1:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | 132 kV main Bus | 2020-08-16 06:16 | 2020-08-16 08:54 | 2:38 | S/O | Due to replacement work | 50 | 131.6667 | Power interruption
Hathazari | 132 kV Bus | 2020-08-21 04:30 | 2020-08-21 07:06 | 2:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulshi | 132 kV main Bus | 2020-08-22 03:56 | 2020-08-22 09:50 | 5:54 | S/O | Due to project work | 60 | 354 | Power interruption
Chandraghona | 132/33 kV Transformer-T2 | 2020-08-25 10:21 | 2020-08-25 11:00 | 0:39 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 27:21 |  | Unserved Energy : |  | 485.6667
Cumilla Grid Circle :
B.Baria | 132/33 kV Transformers-T1 & T2 | 2020-08-03 14:37 | 2020-08-03 14:58 | 0:21 | S/O | Due to fire at 11/33 distribution transformer | 120 | 42 | Power interruption
Cumilla (S) | 132/33 kV Transformer-T3 | 2020-08-07 10:04 | 2020-08-07 16:41 | 6:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Ramganj | 132/33 kV Transformer-T2 | 2020-08-08 09:16 | 2020-08-08 11:05 | 1:49 | S/O | Due to C/M work | 12 | 21.8 | Power interruption
Kulaura | 132/33 kV Transformers-T1 | 2020-08-11 10:38 | 2020-08-11 10:54 | 0:16 | S/O | Due to auxiliary transformer fuse | 18 | 4.8 | Power interruption
| 132/33 kV Transformers-T2 | 2020-08-11 10:38 | 2020-08-11 15:51 | 5:13 | S/O
Shahjibazar | 132/33 kV Transformers-T2 | 2020-08-12 07:08 | 2020-08-12 09:47 | 2:39 | S/O | Due to C/M work | 0 | 0 | No interruption
Chowmuhani | 132/33 kV Transformers-T2 | 2020-08-14 10:35 | 2020-08-14 12:52 | 2:17 | S/O | Due to protection test | 0 | 0 | No interruption
Cumilla (N) | 132/33 kV Transformer-T4 & 33 kV Bus | 2020-08-17 12:03 | 2020-08-17 14:07 | 2:04 | S/O | Due to maintenance work | 0 | 0 | No interruption
Sylhet | 132/33 kV Transformer-T1 & 33 kV Bus | 2020-08-21 07:57 | 2020-08-21 11:58 | 4:01 | S/O | Due to C/M work | 30 | 69.5 | Power interruption 07:57 to 10:16
Shahjibazar | 132/33 kV Transformer-T2 | 2020-08-22 07:27 | 2020-08-22 08:20 | 0:53 | S/O | Due to C/M work | 20 | 17.6667 | Power interruption
Cumilla (N) | 132/33 kV Transformer-T4,&T3 & 33 kV Bus | 2020-08-25 11:21 | 2020-08-25 12:57 | 1:36 | S/O | Due to C/M work | 10 | 16 | Power interruption
Kulaura | 132/33 kV Transformer-T2 | 2020-08-25 10:18 | 2020-08-25 11:36 | 1:18 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-08-25 10:20 | 2020-08-25 11:37 | 1:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | 230 kV Bus-1 | 2020-08-26 10:44 | 2020-08-26 18:22 | 7:38 | S/O | Due to maintenance work | 0 | 0 | No interruption
Sreemongal | 132/33 kV Transformer-T3 | 2020-08-31 16:20 | 2020-08-31 17:02 | 0:42 | S/O | Due to DT/CT test | 0 | 0 | No interruption
|  |  | Total : | 38:41 |  | Unserved Energy : |  | 171.7667
Khulna Grid Circle :
Faridpur | 132/33 kV Transformer-T2 | 2020-08-04 17:42 | 2020-08-04 18:44 | 1:02 | S/O | Due to high temperature at 33 kV CT | 0 | 0 | No interruption
Noapara | 132 kV breaker (no4352) | 2020-08-06 07:20 | 2020-08-06 07:20 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV CB 4152 | 2020-08-06 08:27 | 2020-08-06 08:57 | 0:30 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV CB 4152 | 2020-08-08 07:32 | 2020-08-08 07:32 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Gopalganj(O) | 132/33 kV Transformer-T1 | 2020-08-08 06:19 | 2020-08-08 09:17 | 2:58 | S/O | Due to C/M work | 20 | 59.3333 | Power interruption
Gopalganj(N) | 132 kV capacitor bank |  | 2020-08-11 14:26 |  | S/O | After maintenance work | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T1 | 2020-08-12 06:35 | 2020-08-12 08:05 | 1:30 | S/O | Due to C/M work | 20 | 30 | Power interruption
Narail | 132/33 kV Transformer-T1 | 2020-08-17 09:22 | 2020-08-17 12:35 | 3:13 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-08-17 12:38 | 2020-08-17 17:25 | 4:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Goalpara | 132/33 kV Transformers-T5 | 2020-08-21 07:02 | 2020-08-21 07:02 | 0:00 | S/O |  | 0 | 0 | No interruption
| 132/33 kV Transformers-T6 | 2020-08-21 07:02 | 2020-08-21 10:33 | 3:31 | S/O | Due to C/M work | 0.35 | 1.2308 | Power interruption
Patuakhali | 132/33 kV Transformer-T1 | 2020-08-25 12:05 | 2020-08-25 14:26 | 2:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T3 | 2020-08-28 07:21 | 2020-08-29 09:30 | 26:09 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 46:01 |  | Unserved Energy : |  | 90.5642
Page: 3/3 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:August 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :
Ishurdi | 132 kV Bus-1 | 2020-08-12 08:11 | 2020-08-12 11:25 | 3:14 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV Bus-1 | 2020-08-12 08:11 | 2020-08-12 11:25 | 3:14 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV Bus-2 | 2020-08-30 15:25 | 2020-08-30 16:02 | 0:37 | S/O | Due to maintenance work | 38 | 23.4333 | Power interruption
|  |  | Total : | 7:05 |  | Unserved Energy : |  | 23.4333
Bogura Grid Circle:
Bogura | 230/132 kV Transformer-T03 | 2020-08-06 03:47 | 2020-08-06 15:07 | 11:20 | S/O | Due to winding temperature high | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformer-T1 | 2020-08-07 06:51 | 2020-08-07 09:07 | 2:16 | S/O | Due to C/M work | 20 | 45.3333 | Power interruption
Ruppur | 132/33 kV Transformer-T1 | 2020-08-08 12:19 | 2020-08-08 14:50 | 2:31 | S/O | Due to measurment of earth resistance | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-08-08 14:56 | 2020-08-08 15:18 | 0:22 | S/O |  | 0 | 0 | No interruption
Palashbari | 132 kV Bus-2 | 2020-08-11 06:43 | 2020-08-11 08:55 | 2:12 | S/O | Due to C/M work | 5 | 11 | Power interruption
Niyamatpur | 132/33 kV Transformer-T1 | 2020-08-11 12:01 | 2020-08-11 21:30 | 9:29 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 |  | 2020-08-12 17:28 |  | S/O | After maintenance work | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T3 |  | 2020-08-12 17:37 |  | S/O |  | 0 | 0 | No interruption
Niyamatpur | 132/33 kV Transformer-T1 |  | 2020-08-13 11:34 |  | S/O | After maintenance work | 0 | 0 | No interruption
Bogura | 230/132 kV Transformer-T02 | 2020-08-19 10:11 | 2020-08-19 12:30 | 2:19 | S/O | Due to changing work | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformer-T1 | 2020-08-21 14:20 | 2020-08-21 15:45 | 1:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformer-T2 | 2020-08-22 07:08 | 2020-08-22 09:36 | 2:28 | S/O | Due to C/M work | 18 | 44.4 | Power interruption
Bogura | 132/33 kV Transformer-T3 | 2020-08-22 09:45 | 2020-08-22 11:20 | 1:35 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2020-08-22 11:21 | 2020-08-22 15:27 | 4:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | 132 kV main Bus-A | 2020-08-22 09:20 | 2020-08-22 15:15 | 5:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Ruppur | 132/33 kV Transformer-T2 | 2020-08-25 10:03 | 2020-08-26 18:02 | 31:59 | S/O | Due to C/M work | 0 | 0 | No interruption
Lalmonirhat | 132/33 kV Transformer-T1 | 2020-08-28 07:10 | 2020-08-28 07:10 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformer-T3 | 2020-08-30 07:13 | 2020-08-30 08:14 | 1:01 | S/O | Due to C/M work | 12 | 12.2 | Power interruption
|  |  | Total : | 78:58 |  | Unserved Energy : |  | 112.9333
Others :Nil
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 475:16 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/2 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:August 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mymensingh | Mymensingh-Kishoreganj 132 kV line-1 | 2020-08-04 15:31 | 2020-08-04 17:08 | 1:37 | S/O | Due to removing kite | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-1 | 2020-08-05 09:35 | 2020-08-05 12:10 | 2:35 | S/O | Due to C/M work | 0 | 0 | No interruption
| Mymensingh-Netrakona 132 kV line-2 | 2020-08-05 12:18 | 2020-08-05 14:47 | 2:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Tongi 132 kV line-1 | 2020-08-12 06:40 | 2020-08-12 08:24 | 1:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj 160 MW P/S 132 kV line-1 | 2020-08-13 08:06 | 2020-08-13 16:59 | 8:53 | S/O | Due to D/W work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV line-2 | 2020-08-14 06:12 | 2020-08-14 06:58 | 0:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj 162 MW P/S 132 kV line-1 | 2020-08-14 08:57 | 2020-08-14 16:57 | 8:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Gazipur Summit | Gazipur Summit-Kaliakoir 230 kV line | 2020-08-14 12:20 | 2020-08-14 17:23 | 5:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV line-1 | 2020-08-17 13:10 | 2020-08-17 15:33 | 2:23 | S/O | Due to D/W work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV line-1 | 2020-08-28 06:16 | 2020-08-28 08:05 | 1:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi(O) | Tongi(O)-Tongi (N) 132 kV line-1 | 2020-08-28 08:30 | 2020-08-28 09:35 | 1:05 | S/O | Due to C/M work | 0 | 0 | No interruption
| Tongi(O)-Tongi (N) 132 kV line-2 | 2020-08-28 09:37 | 2020-08-28 10:55 | 1:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-1 | 2020-08-30 08:53 | 2020-08-30 10:32 | 1:39 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 39:21 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Ghorashal | Ghorashal-Ashuganj(S) 230 kV line-1 | 2020-08-13 15:36 | 2020-08-13 15:36 | 0:00 | S/O | Due to replacement work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Lalbagh 132 kV line-2 | 2020-08-14 07:34 | 2020-08-14 18:09 | 10:35 | S/O | Due to C/M work | 0 | 0 | No interruption
| Hasnabad-Lalbagh 132 kV line | 2020-08-16 09:51 | 2020-08-16 17:53 | 8:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Aurahati 132 kV line | 2020-08-17 09:24 | 2020-08-17 16:51 | 7:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 230 kV line-1 | 2020-08-18 17:30 | 2020-08-18 19:16 | 1:46 | S/O | Due to C/M work | 0 | 0 | No interruption
| Haripur-Bhulta 230 kV line-2 | 2020-08-18 18:00 | 2020-08-18 21:02 | 3:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Narsinghdi | Narsinghdi-B.Baria 132 kV line-1 | 2020-08-19 14:24 | 2020-08-19 16:38 | 2:14 | S/O | Due to C/M work | 0 | 0 | No interruption
| Narsinghdi-B.Baria 132 kV line-2 | 2020-08-19 17:02 | 2020-08-19 17:50 | 0:48 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Aminbazar 230 kV line-2 | 2020-08-26 07:13 | 2020-08-26 07:13 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 132 kV line | 2020-08-28 12:35 | 2020-08-28 16:35 | 4:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Haripur-Madanganj 132 kV line | 2020-08-29 09:01 | 2020-08-29 21:36 | 12:35 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 50:29 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Kulshi | Kulshi-Baraulia 132 kV line | 2020-08-10 08:24 | 2020-08-10 12:10 | 3:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Rangamati 132 kV line-2 | 2020-08-13 10:01 | 2020-08-13 10:59 | 0:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Kulshi | Kulshi-Rampur 132 kV line-2 | 2020-08-28 09:55 | 2020-08-30 14:30 | 52:35 | S/O | Due to D/W work | 0 | 0 | No interruption
| Khulshi-Madunaghat 132 kV line | 2020-08-29 21:18 | 2020-08-29 22:31 | 1:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Dohazari 132 kV line-1 | 2020-08-30 11:44 | 2020-08-30 13:29 | 1:45 | S/O | Due to tree trimming | 0 | 0 | No interruption
|  |  | Total : | 60:17 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Ashuganj | Ashuganj-B.Baria 132 kV line-1 | 2020-08-04 08:36 | 2020-08-04 11:16 | 2:40 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 kV line-1 | 2020-08-04 09:25 | 2020-08-04 13:02 | 3:37 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ashuganj-B.Baria 132 kV line-2 | 2020-08-04 11:17 | 2020-08-04 14:42 | 3:25 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ashuganj-B.Baria 132 kV line-2 | 2020-08-04 13:07 | 2020-08-04 15:44 | 2:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sreemongal 132 kV line-1 |  | 2020-08-06 20:01 |  | S/O | After maintenance work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorashal 230 kV line-1 | 2020-08-13 06:32 | 2020-08-13 06:32 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Chattak 132 kV line | 2020-08-18 07:42 | 2020-08-18 10:13 | 2:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ashuganj(S) 230 kV line-2 | 2020-08-20 13:09 | 2020-08-20 21:11 | 8:02 | S/O | Due to CT checking | 0 | 0 | No interruption
| Ashuganj-Shahjibazar 132 kV line-3 | 2020-08-22 09:17 | 2020-08-22 17:06 | 7:49 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV line-2 | 2020-08-24 17:24 | 2020-08-24 17:31 | 0:07 | S/O | Due to changing work | 0 | 0 | No interruption
| Ashuganj-Ghorashal 132 kV line-1 | 2020-08-25 09:47 | 2020-08-25 12:28 | 2:41 | S/O | Due to C/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Chattak 132 kV line-2 | 2020-08-26 06:29 | 2020-08-26 08:11 | 1:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ashuganj(S) 230 kV line-1 | 2020-08-29 09:45 | 2020-08-29 13:01 | 3:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj(S) | Ashuganj(S)-Ghorashal 230 kV line-1 |  | 2020-08-29 18:12 |  | S/O | After maintenance work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-2 | 2020-08-31 08:45 | 2020-08-31 13:35 | 4:50 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 43:17 |  | Unserved Energy: |  | 0
Page: 2/2 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:August 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Khulna(C) | Khulna©-KPCL-2 132 kV line | 2020-08-06 07:26 | 2020-08-06 07:26 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Khulna(S)-Khulna© 132 kV line-1 | 2020-08-08 12:45 | 2020-08-08 15:57 | 3:12 | S/O | Due to protection test | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Khulna© 132 kV line-2 | 2020-08-09 11:35 | 2020-08-09 12:56 | 1:21 | S/O | Due to protection test | 0 | 0 | No interruption
Barishal(N) | Barishal(N)-Barishal (S) 132 kV line | 2020-08-25 10:32 | 2020-08-25 11:11 | 0:39 | S/O | Due to trr trimming | 0 | 0 | No interruption
|  |  | Total : | 5:12 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Ishurdi | Ishurdi-Natore 132 kV line-2 | 2020-08-04 14:45 | 2020-08-04 14:55 | 0:42 | S/O | Due to D/W work | 0 | 0 | No interruption
| Ishurdi-Natore 132 kV line-2 | 2020-08-14 09:30 | 2020-08-14 11:47 | 2:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Pabna | Pabna-Shahjadpur 132 kV line | 2020-08-25 10:03 | 2020-08-25 10:42 | 0:39 | S/O | Due to C/M work | 0 | 0 | No interruption
Jessore | Jessore-Noapara 132 kV line-1 | 2020-08-30 06:08 | 2020-08-30 08:30 | 2:22 | S/O | Due to replacement work | 0 | 0 | No interruption
|  |  | Total : | 6:00 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Bogura | Bogura -Natore 132 kV line-2 | 2020-08-05 13:48 | 2020-08-05 15:20 | 1:32 | S/O | Due to line checking | 0 | 0
Sirajganj | Sirajganj -Ashuganj 230 kV line-2 | 2020-08-09 08:11 | 2020-08-09 11:58 | 3:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Baghabari | Baghabari-Bogura 132 kV (new) line | 2020-08-12 09:12 | 2020-08-12 15:39 | 6:27 | S/O | Due to CT connection | 0 | 0 | No interruption
Rajshahi(N) | Rajshahi(N)-C.nawabganj 132 kV line | 2020-08-16 09:12 | 2020-08-16 10:35 | 1:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Natore | Natore-Bogura 132 132 kV line-2 | 2020-08-20 09:30 | 2020-08-20 12:12 | 2:42 | S/O | Due to C/M work | 0 | 0 | No interruption
| Natore-Bogura 132 132 kV line-1 | 2020-08-20 12:14 | 2020-08-20 12:50 | 0:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV line-2 | 2020-08-21 06:55 | 2020-08-21 09:20 | 2:25 | S/O | Due to replacement work | 0 | 0 | No interruption
Rangpur | Rangpur-Rangpur confidence 132 k line-2 | 2020-08-21 06:50 | 2020-08-21 09:55 | 3:05 | S/O | Due to C/M work | 0 | 0 | No interruption
| Rangpur-Rangpur confidence 132 k line-2 | 2020-08-21 10:33 | 2020-08-21 12:37 | 2:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Natore | Natore-Bogura 132 132 kV line-1 | 2020-08-23 08:57 | 2020-08-23 17:39 | 8:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Purbasadipur | Purbasadipur-Thakurgaon 132 kV line-1 | 2020-08-23 11:09 | 2020-08-23 16:15 | 5:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Mohasthangarth | Mohasthangarth -Palshbari 132 kV line-2 |  | 2020-08-24 15:02 |  | S/O | After maintenance work | 0 | 0 | No interruption
Rajshahi(S) | Rajshahi(S)-Katakhali P/S 132 kV line | 2020-08-25 09:45 | 2020-08-25 12:27 | 2:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | Bogura-Naogaon 132 kV line-1 | 2020-08-29 10:01 | 2020-08-29 12:48 | 2:47 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 43:18 |  | Unserved Energy: |  | 0
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 247:54 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:August' 2020
| Area | Previous Month (July 2020) |  |  |  | Current Month (August 2020)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 11 | 5 | 55 | 71 | 23 | 6 | 45 | 74
2 | Dhaka (South) Grid Circle. | 13 | 1 | 31 | 45 | 20 | 8 | 24 | 52
3 | Chattogram Grid Circle. | 8 | 7 | 28 | 43 | 14 | 6 | 12 | 32
4 | Cumilla Grid Circle. | 28 | 9 | 31 | 68 | 23 | 10 | 30 | 63
5 | Khulna Grid Circle. | 23 | 8 | 16 | 47 | 11 | 24 | 17 | 52
6 | HVDC Grid Circle | 11 | 4 | 15 | 30 | 15 | 6 | 7 | 28
7 | Bogura Grid Circle. | 23 | 15 | 16 | 54 | 17 | 25 | 32 | 74
8 | Others | 1 |  | 1 | 2 | 1 |  |  | 1
9 | Total | 118 | 49 | 193 | 360 | 124 | 85 | 167 | 376
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:August' 2020
| Area | Previous Month (July 2020) |  |  |  | Current Month (August 2020)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 118.5 | 163.83 | 859.17 | 1141.5 | 449.08 |  | 647.98 | 1097.06
2 | Dhaka (South) Grid Circle. | 199.5 |  |  | 199.5 | 95.7 | 308.98 | 70 | 474.68
3 | Chattogram Grid Circle. | 258.9 | 171 | 142.3333 | 572.2333 | 24.6 | 304.17 | 485.67 | 814.44
4 | Cumilla Grid Circle. | 106.43 | 80 | 231.75 | 418.18 | 1089.5167 | 306.84 | 171.77 | 1568.1267
5 | Khulna Grid Circle. | 837 | 120.42 | 150.63 | 1108.05 | 5686.77 | 544.87 | 90.56 | 6322.2
6 | HVDC Grid Circle | 6 | 74.12 |  | 80.12 | 0.63 | 173.1 | 23.43 | 197.16
7 | Bogura Grid Circle. | 281.19 | 191.83 | 642.92 | 1115.94 | 1973.93 | 347.75 | 112.93 | 2434.61
8 | Others | Energy unserved ( MWH ) due to Total: 0; Energy unserved ( MWH ) due to Total: 0
9 | Total | 1807.52 | 801.2 | 2026.8033 | 4635.5233 | 9320.2267 | 1985.71 | 1602.34 | 12908.2767
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:August' 2020
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 3 | 9 | 12 | 4 |  | 9 | 772.4833
2 | Dhaka (South) | 5031.6 | 3 | 1 | 4 |  | 1 | 3 | 383.0167
3 | Chattogram | 2042 | 5 | 2 | 7 | 3 |  | 4 | 812.4333
4 | Khulna | 2434 | 14 | 3 | 17 | 4 | 1 | 12 | 593.2308
5 | HVDC | 5913.3 | 4 | 1 | 5 | 1 |  | 3 | 197.1667
6 | Bogura | 3145.6 | 12 | 4 | 16 | 1 | 2 | 13 | 487.4667
7 | Cumilla | 2981 | 14 | 5 | 20 | 5 | 4 | 9 | 866.6
8 | Others | -
| Total | 30349.1 | [6 empty] | 4112.3975
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.97%
2 | Dhaka (South) | 99.97%
3 | Chattogram | 99.93%
4 | Khulna | 99.4%
5 | HVDC | 99.96% | [6 empty] | Executive Engineer
6 | Bogura | 99.97% | [6 empty] | Information Management Division
7 | Cumilla | 99.88% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:August' 2020
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 3 |  | 3 | 1 |  |  | 324.58
2 | Dhaka (South) | 990.29 |  | 2 | - | 2 | - | 1 | 1 | 91.67
3 | Chattogram | 917 | - | 1 |  | 1 | 1 |  |  | 2
4 | Khulna | 1238.4 | - | 5 |  | 3 | 2 |  | 3 | 5728.97
5 | HVDC | 1324 | 501 | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | - | 2 | - | 2 | 1 | - | 1 | 1947.15
7 | Cumilla | 1648.16 | - | 5 |  | 5 | 4 |  | 1 | 701.52
7 | Others | - |  | - | - | - | - | - | - | -
| Total | 10175.6215 | 501 | [6 empty] | 8795.89
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.9%
3 | Chattogram | 99.61%
4 | Khulna | 99.97%
5 | Bheramara (HVDC) | 99.74% | [7 empty] | Executive Engineer
6 | Bogura | 100% | [7 empty] | Information Management Division
7 | Cumilla | 99.69% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:August' 2020
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2020-08-18 | 25 | - | 16 | 24hour 34 min | 3 | 05hour 43 min | - | - | 1 | 3hour 25 min | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/2 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:August' 2020
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Dhamrai | 1 | 0:19 | 38 | 12.0333 | Due to tripping of 132/33 kV Transformer-T1
Joydevpur |  | 5:27 | 10 | 54.5 | Due to tripping of 132/33 kV Transformer-GT3
| 2 | 0:10 | 74 | 57.9667 | Due to tripping of 132/33 kV Transformer-T3
Tongi |  | 0:27 | 300 | 135 | Due to tripping of Tongi-Kabirpur 132 kV line-1
|  | 0:21 | 325 | 113.75 | Due to tripping of Tongi-Kabirpur 132 kV line-1 & 2
| 2 | 0:13 | 350 | 75.8333
Netrakona | 1 | 0:23 | 20 | 7.6667 | Due to S/D of132/33 kV Transformer-T1
Tangail |  | 3:44 | 20 | 74.6667 | Due to S/D of132/33 kV Transformer-T2
Kishoreganj | 1 | 1:33 | 10 | 15.5 | Due to tripping of 132/33 kV Transformer-T2
Netrakona | 2 | 10:47 | 30 | 323.5 | Due to tripping of 132/33 kV Transformer-T2
|  | 10:28 | 5 | 52.3333 | Due to S/D of132/33 kV Transformer-T1
Mymensingh | 1 | 1:05 | 35 | 37.9167
Sylhet | 1 | 4:00 | 30 | 120 | Due to S/D of132/33 kV Transformer-T1
Kishoreganj | 1 | 0:18 | 8 | 2.4 | Due to S/D of132/33 kV Transformer-T3
Joydevpur | 1 | 1:10 | 12 | 14
Maniknagar | 1 | 2:18 | 88 | 202.4 | Due to tripping of 132/33 kV Transformer-T2
Munshiganj | 1 | 0:31 | 82 | 42.3667 | Due to tripping of 132/33 kV Transformer-T1
Narsinghdi | 1 | 1:31 | 45 | 68.25 | Due to red-hot maintenance of 132/33 kV Transformer T3
Haripur | 1 | 0:32 | 100 | 53.3333 | Due to tripping of Haripur-Bhulta 132 kV line
Bhulta | 1 | 0:46 | 50 | 38.3333 | Due to red-hot maintenance of Bhulta -Haripur 132 kV line
Munshiganj | 1 | 2:00 | 35 | 70 | Due to S/D of 132/33 kV Transformer T1
Cox'sbazar |  | 0:18 | 25 | 7.5 | Due to tripping of 132/33 kV Transformer-T3
Dohazari | 2 | 0:30 | 14 | 7 | Due to tripping of 132/33 kV Transformer-T1
|  | 0:27 | 18 | 8.1
Halishahar | 2 | 1:59 | 50 | 99.1667 | Due to red-hot maintenance 33 kV Bus
|  | 2:03 | 100 | 205
Dohazari | 2 | 0:03 | 40 | 2 | Due to tripping of Dohazari-Sikalbaha 132 kV line
|  | 2:38 | 50 | 131.6667 | Due to S/D of 132 kV Bus
Khulshi | 1 | 5:54 | 60 | 354
Ramganj | 2 | 0:05 | 120 | 10 | Due to tripping of 132/33 kV Transformers-T1 & T2
|  | 0:05 | 116 | 9.6667
Chowmuhani | 1 | 0:15 | 136 | 34 | Due to tripping of 132/33 kV Transformers-T1 & T3
Comilla(N) | 1 | 0:14 | 15 | 3.5 | Due to tripping of 132/33 kV Transformer-T3
Kulaura | 1 | 7:14 | 23 | 166.3667 | Due to tripping of 132/33 kV Transformer-T1
Sreemongal | 1 | 1:10 | 52 | 60.6667 | Due to red-hot maintenance of 132/33 kV Transformer T1
Daudkandi | 1 | 1:59 | 20 | 39.6667 | Due to red-hot maintenance of 132/33 kV Transformer T3
Kulaura | 1 | 1:00 | 29 | 29 | Due to red-hot maintenance of 132/33 kV Transformer T1
Comilla(N) | 1 | 0:31 | 20 | 10.3333 | Due to tripping of 132/33 kV Transformer-T3
Kulaura | 1 | 3:35 | 22 | 78.8333 | Due to tripping of 132/33 kV Transformer-T1
Sreemongal | 1 | 17:40 | 12 | 7 | Due to tripping of 132/33 kV Transformer-T3
Comilla(N) | 1 | 0:20 | 50 | 16.6667 | Due to tripping of 132/33 kV Transformers-T3 & T4
| 1 | 0:32 | 15 | 8 | Due to tripping of 132/33 kV Transformer-T3
Kulaura | 1 | 7:08 | 31 | 221.1333 | Due to tripping of 132/33 kV Transformer-T1
S.M. Nagar | 1 | 0:46 | 146 | 111.9333 | Due to tripping of S.M.Nagar-Cumilla(S) 132 kV line-1 & 2
Cumilla(S) | 1 | 0:43 | 160 | 114.6667 | Due to de-loaded at black out at Surjamoninagar
Ashuganj | 1 | 0:37 | 700 | 396.6667 | Due to tripping of Ashuganj-Kishoreganj 132 kV line
Fenchuganj | 1 | 0:34 | 25 | 15.4167 | Due to tripping of Fenchuganj-Kulaura 132 kV line
Cumilla(S) | 1 | 1:02 | 130 | 62.8333 | Due to tripping of Cumilla(S)-Tripura 132 kV line-1 & 2
B.Baria | 1 | 0:21 | 120 | 42 | Due to S/D of 132/33 kV Transformers T1 & T2
Ramganj | 1 | 1:49 | 12 | 21.8 | Due to S/D of 132/33 kV Transformer T2
Kulaura | 1 | 0:16 | 18 | 4.8 | Due to S/D of 132/33 kV Transformer T1
Sylhet | 1 | 4:01 | 30 | 69.5 | Due to S/D of 132/33 kV Transformer T1
Shahjibazar | 1 | 0:53 | 20 | 17.6667 | Due to S/D of 132/33 kV Transformer T2
Cumilla (N) | 1 | 1:36 | 10 | 16 | Due to S/D of 132/33 kV Transformer T3 & T4 | Cumilla (N) | Cumilla (N)
Patuakhali | 1 | 0:30 | 55 | 27.5 | Due to bursting of Y-phase PT
Bagerhat | 1 | 1:42 | 22 | 37.4 | Due to red-hot maintenance of 132/33 kV Transformer T1
Madaripur | 1 | 1:17 | 15 | 19.25 | Due to red-hot maintenance of 132/33 kV Transformer T2
Khulna(C) | 1 | 1:18 | 5 | 6.5 | Due to red-hot maintenance of 132/33 kV Transformer T3
Satkhira | 1 | 15:05 | 10 | 150.8333 | Due to red-hot maintenance of 132/33 kV Transformer T2
Faridpur | 1 | 1:01 | 35 | 35.5833 | Due to Oil leakage of 132/33 kV Transformer T2
Norail |  | 1:47 | 15 | 26.75 | Due to red-hot maintenance of 132/33 kV Transformer T1
| 2 | 0:26 | 6 | 2.6 | Due to red-hot maintenance of 132/33 kV Transformer T2
Bagerhat | 2 | 3:04 | 18 | 55.2 | Due to red-hot maintenance of 132/33 kV Transformer T1
|  | 1:22 | 9 | 12.3 | Due to red-hot maintenance of 132/33 kV Transformer T2
Barishal(S) | 1 | 0:15 | 70 | 17.5 | Due to flashing of 33 kV Bus
Bagerhat | 1 | 1:34 | 40 | 62.6667 | Due to red-hot maintenance of 132/33 kV Transformers T1 & T3
Gopalganj(O) | 1 | 0:47 | 25 | 19.5833 | Due to red-hot maintenance of 132/33 kV Transformer T1
Mongla | 1 | 1:39 | 16 | 26.4 | Due to red-hot maintenance of 132/33 kV Transformer T1
Bagerhat | 1 | 0:06 | 26 | 2.6 | Due to tripping of 132/33 kV Transformers-T1 & T2
Magura | 1 | 1:36 | 28 | 44.8 | Due to red-hot maintenance of Magura-Narail 132 kV line-2
Bagerhat | 2 | 0:30 | 26 | 13 | Due to tripping of Bagerhat-Mongla 132 kV line
|  | 0:09 | 185 | 27.75 | Due to tripping of Bagerhat-Goalpara132 kV line
Khulna | 1 | 5:05 | 965 | 4905.4167 | Due to tripping of all 230 kV and 132 Ckts at Khulna Zone
Barishal | 1 | 3:25 | 216 | 738 | Due to tripping of all 230 kV and 132 Ckts at Barishal Zone
Gopalganj(O) | 1 | 2:58 | 20 | 59.3333 | Due to S/D of 132/33 kV Transformer T1
Faridpur | 1 | 1:30 | 20 | 30
Page: 2/2 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:August' 2020
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Goalpara | 1 | 3:31 | 0.35 | 1.2308 | Due to S/D of 132/33 kV Transformer T6
Bottail |  | 1:10 | 15 | 17.5 | Due to red-hot maintenance of 132/33 kV Transformer T1
Jhenidah | 2 | 2:36 | 36 | 93.6
|  | 2:04 | 30 | 62 | Due to red-hot maintenance of 132/33 kV Transformer T1
Gallamari | 2 | 0:01 | 38 | 0.63333 | Due to tripping of 33 kV feeder fault
Ishurdi | 1 | 0:37 | 38 | 23.4333 | Due to S/D of 132 kV Bus-2
Rajshahi | 1 | 1:06 | 35 | 38.5 | Due to red-hot maintenance of 132/33 kV Transformer T2
Juldhaka | 1 | 0:55 | 16 | 14.6667 | Due to red-hot maintenance of 132/33 kV Transformer T1
Amnura | 1 | 0:12 | 34 | 6.8 | Due to tripping of 132/33 kV Transformer-T1
Purbasadipur | 1 | 0:50 | 20 | 16.6667 | Due to red-hot maintenance of 132/33 kV Transformer T1
Bogura | 1 | 1:15 | 45 | 56.25 | Due to red-hot maintenance of 132/33 kV Transformers T3 & T4
Palashbari | 1 | 1:18 | 20 | 26 | Due to red-hot maintenance of 132/33 kV Transformer T4
Barapukuria | 1 | 1:35 | 37 | 58.5833 | Due to red-hot maintenance of 132/33 kV Transformer T3
Palashbari | 2 | 1:02 | 7 | 7.2333
|  | 1:28 | 5 | 7.3333 | Due to Oil leakage of 132/33 kV Transformer T3
Natore | 1 | 1:27 | 58 | 84.1 | Due to red-hot maintenance of 132/33 kV Transformers T1 & T2
Palashbari | 1 | 1:05 | 20 | 21.6667 | Due to red-hot maintenance of 132/33 kV Transformer T3
Naogaon | 1 | 1:16 | 29 | 36.7333 | Due to tripping of 132/33 kV Transformer-T3
Rangpur | 1 | 3:21 | 5 | 16.75 | Due to Oil leakage of Rangpur-Rangpur confifence 132 kV line
Palashbari | 5 | 0:06 | 762 | 1930.4 | Due to tripping of Palshbari-Mahasthangarth 132 kV line-1 & 2
|  | 2:16 | 20 | 45.3333 | Due to S/D of 132/33 kV Transformer T1
|  | 2:12 | 5 | 11 | Due to S/D of 132 kV Bus
|  | 2:28 | 18 | 44.4 | Due to S/D of 132/33 kV Transformer T2
|  | 1:01 | 12 | 12.2 | Due to S/D of 132/33 kV Transformer T3
| Total Unserved energy : |  |  | 12908.2808 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:August'2020
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 132 | 23 | 2020-08-01 | 12:00
2 | Munsiganj | 130 | 11 | 2020-08-01 | 22:00
3 | Sonargaon | 89 | 29 | 2020-08-01 | 23:00
4 | Shyampur | 204 | 18 | 2020-08-01 | 24:00
5 | Bhulta | 223 | 16 | 2020-08-01 | 17:00
6 | Madanganj | 68 | 13 | 2020-08-01 | 23:00
7 | Shitalakhya | 117 | 27 | 2020-08-01 | 11:00
8 | Rahim steel | 25 | 24 | 2020-08-01 | 12:00
9 | Matuail | 82 | 9 | 2020-08-01 | 18:30
10 | Ghorasal | 86 | 10 | 2020-08-01 | 23:00
11 | Narsingdi | 169 | 23 | 2020-08-01 | 22:00
12 | Haripur (SBU) | 112 | 24 | 2020-08-01 | 10:00
13 | Ullon | 72 | 9 | 2020-08-01 | 14:00
14 | Hasnabad | 211 | 31 | 2020-08-01 | 22:00
15 | Magbazar | 108 | 31 | 2020-08-01 | 12:00
16 | Maniknagar | 106 | 31 | 2020-08-01 | 16:00
17 | Bangabhaban | 40 | 12 | 2020-08-01 | 11:00
18 | Narinda | 92 | 13 | 2020-08-01 | 13:00
19 | Dhanmondi | 190 | 12 | 2020-08-01 | 12:00
20 | Lalbag | 90 | 19 | 2020-08-01 | 13:00
21 | Madartek | 74 | 30 | 2020-08-01 | 22:00
22 | Dhaka University | - | - | - | -
23 | Fatullah | 37 | 31 | 2020-08-01 | 10:00
24 | Mirpur | 109 | 31 | 2020-08-01 | 19:00
25 | Kalyanpur | 114 | 31 | 2020-08-01 | 18:30
26 | Gulshan | 144 | 31 | 2020-08-01 | 13:00
27 | Uttara | 87 | 13 | 2020-08-01 | 15:00
28 | Uttara(new) | 33 | 31 | 2020-08-01 | 14:00
29 | Kamrangirchar | 91 | 25 | 2020-08-01 | 19:00
30 | Savar | 146 | 23 | 2020-08-01 | 12:00
31 | Bhasantec | 162 | 31 | 2020-08-01 | 13:00
32 | Agargaon | 78 | 31 | 2020-08-01 | 13:00
33 | Satmosjid | 103 | 12 | 2020-08-01 | 19:00
34 | Tongi | 153 | 31 | 2020-08-01 | 11:00
35 | Kabirpur | 263 | 31 | 2020-08-01 | 16:00
36 | Basundhara | 144 | 31 | 2020-08-01 | 18:30
37 | Manikganj | 79 | 3 | 2020-08-01 | 21:00
38 | Joydevpur | 190 | 27 | 2020-08-01 | 12:00
39 | New Tongi | 134 | 12 | 2020-08-01 | 1:00
40 | Kodda | 258 | 18 | 2020-08-01 | 15:00
41 | Dhamrai | 102 | 31 | 2020-08-01 | 20:00
42 | Rajendrapur | 108 | 29 | 2020-08-01 | 21:00
43 | Valuka | 114 | 13 | 2020-08-01 | 16:00
44 | Tangail | 205 | 31 | 2020-08-01 | 19:30
45 | Mymensing | 244 | 14 | 2020-08-01 | 21:00
46 | Kishorganj | 164 | 3 | 2020-08-01 | 22:00
47 | Netrokona | 122 | 4 | 2020-08-01 | 21:00
48 | Jamalpur | 151 | 14 | 2020-08-01 | 23:00
49 | Sherpur | 126 | 14 | 2020-08-01 | 22:00
50 | Srimongal | 64 | 24 | 2020-08-01 | 19:00
51 | Shahjibazar | 132 | 24 | 2020-08-01 | 21:00
52 | Fenchuganj | 49 | 3 | 2020-08-01 | 19:30
53 | Kulawara | 51 | 4 | 2020-08-01 | 19:00
54 | Sylhet | 139 | 13 | 2020-08-01 | 19:00
55 | Chatak | 33 | 3 | 2020-08-01 | 21:00
56 | Sunamganj | 50 | 4 | 2020-08-01 | 23:00
57 | Bianibazar | 75 | 24 | 2020-08-01 | 19:00
58 | Cumilla (S) | 178 | 13 | 2020-08-01 | 22:00
59 | Cumilla(N) | 153 | 10 | 2020-08-01 | 0:00
60 | Chandpur | 121 | 2 | 2020-08-01 | 22:00
61 | Feni | 138 | 1 | 2020-08-01 | 22:00
62 | Chowmuhani | 186 | 13 | 2020-08-01 | 22:00
63 | Ashuganj | 69 | 31 | 2020-08-01 | 23:00
64 | Daudkandi | 152 | 3 | 2020-08-01 | 22:00
65 | B.Baria | 170 | 5 | 2020-08-01 | 21:00
66 | Ramganj | 128 | 3 | 2020-08-01 | 22:00
67 | Chaddagram | 56 | 10 | 2020-08-01 | 23:00
68 | PHP | 12 | 14 | 2020-08-01 | 18:30
69 | Madanhat | 67 | 13 | 2020-08-01 | 21:00
70 | Hathazari | 106 | 29 | 2020-08-01 | 19:00
71 | Khulshi | 205 | 12 | 2020-08-01 | 15:00
Page: 2/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:August'2020
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
72 | Halishahar | 147 | 31 | 2020-08-01 | 11:00
73 | Baraulia | 160 | 22 | 2020-08-01 | 9:00
74 | Sikalbaha | 30 | 15 | 2020-08-01 | 21:00
75 | Dohazari | 102 | 2 | 2020-08-01 | 19:00
76 | Cox'sbazar | 106 | 29 | 2020-08-01 | 19:30
77 | Chandraghona | 38 | 2 | 2020-08-01 | 13:00
78 | Kaptai | 5.4 | 19 | 2020-08-01 | 19:00
79 | A. Khaer Stl. | 18 | 27 | 2020-08-01 | 13:00
80 | Bakulia | 103 | 29 | 2020-08-01 | 18:30
81 | Julda | 26 | 13 | 2020-08-01 | 15:00
82 | TK chemical | 30.4 | 29 | 2020-08-01 | 19:00
83 | Modern Steel | 17 | 25 | 2020-08-01 | 2:00
84 | Shahmirpur | 31 | 8 | 2020-08-01 | 14:00
85 | Khagrachhari | 26 | 1 | 2020-08-01 | 19:30
86 | Matarbari | 37 | 2 | 2020-08-01 | 21:00
87 | Baroiar Hat | 46 | 3 | 2020-08-01 | 22:00
88 | Rangamati | 12 | 1 | 2020-08-01 | 19:00
89 | Abul Khair 230 | 151 | 15 | 2020-08-01 | 11:00
90 | BSRM | 163 | 4 | 2020-08-01 | 10:00
91 | GPH Ispat | 91 | 29 | 2020-08-01 | 10:00
92 | Goalpara | 31 | 31 | 2020-08-01 | 23:00
93 | Central s/s | 102 | 12 | 2020-08-01 | 220:00
94 | Noapara | 65 | 11 | 2020-08-01 | 21:00
95 | Jashore | 126 | 7 | 2020-08-01 | 22:00
96 | Benapol | 52 | 1 | 2020-08-01 | 21:00
97 | Jhenidah | 118 | 31 | 2020-08-01 | 22:00
98 | Bottail | 141 | 11 | 2020-08-01 | 19:30
99 | G.K Project | 62 | 13 | 2020-08-01 | 19:30
100 | Faridpur | 204 | 12 | 2020-08-01 | 21:00
101 | Madaripur | 118 | 3 | 2020-08-01 | 22:00
102 | Sariatpur | 80 | 3 | 2020-08-01 | 22:00
103 | Gopalganj | 106 | 2 | 2020-08-01 | 23:00
104 | Bagerhat | 108 | 31 | 2020-08-01 | 20:00
105 | Mongla | 54 | 31 | 2020-08-01 | 11:00
106 | Satkhira | 121 | 3 | 2020-08-01 | 21:00
107 | Gallamari | 51 | 12 | 2020-08-01 | 13:00
108 | Magura | 58 | 3 | 2020-08-01 | 21:00
109 | Norail | 42 | 1 | 2020-08-01 | 20:00
110 | Chuadanga | 94 | 25 | 2020-08-01 | 20:00
111 | Barsal(N) | 54 | 2 | 2020-08-01 | 21:00
112 | Barsal(S) | 112 | 31 | 2020-08-01 | 19:30
113 | Patuakhali | 139 | 3 | 2020-08-01 | 23:00
114 | Bhandaria | 64 | 1 | 2020-08-01 | 21:00
115 | Borhan Uddin | 46 | 11 | 2020-08-01 | 21:00
116 | Ishurdi | 68 | 25 | 2020-08-01 | 19:30
117 | Ruppur Paromanobik | 2 | 2 | 2020-08-01 | 18:00
118 | Natore | 141 | 13 | 2020-08-01 | 21:00
119 | Bogura | 187 | 31 | 2020-08-01 | 21:00
120 | Naogaon | 143 | 31 | 2020-08-01 | 21:00
121 | Rajshahi | 163 | 31 | 2020-08-01 | 21:00
122 | Rajshahi New | 12 | 2 | 2020-08-01 | 23:00
123 | C.Nawabganj | 81 | 10 | 2020-08-01 | 19:00
124 | Amnura | 56 | 3 | 2020-08-01 | 22:00
125 | Pabna | 128 | 31 | 2020-08-01 | 20:00
126 | Shahjadpur | 110 | 3 | 2020-08-01 | 21:00
127 | Serajganj | 117 | 31 | 2020-08-01 | 21:00
128 | Niyamatpur | 64 | 1 | 2020-08-01 | 21:00
129 | Joypurhat | 59 | 12 | 2020-08-01 | 20:00
130 | Sherpur(Bogura) | 50 | 11 | 2020-08-01 | 19:30
131 | Mohastangar | 55 | 3 | 2020-08-01 | 24:00
132 | Rangpur | 163 | 13 | 2020-08-01 | 20:00
133 | Lalmonirhat | 68 | 16 | 2020-08-01 | 19:30
134 | Saidpur | 112 | 27 | 2020-08-01 | 19:00
135 | Purbasadipur | 109 | 10 | 2020-08-01 | 20:00
136 | Thakurgaon | 86 | 5 | 2020-08-01 | 21:00
137 | Palshbari | 132 | 2 | 2020-08-01 | 22:00
138 | Barapukuria | 54 | 24 | 2020-08-01 | 21:00
139 | Panchugar | 56 | 15 | 2020-08-01 | 20:00
140 | Joldhaka | 32 | 2 | 2020-08-01 | 22:00
141 | Kurigram | 62 | 25 | 2020-08-01 | 19:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:August' 2020
Area | MW | Date | Hour | Remarks
Dhaka | 4346 | 31.08.2020 | 15:00
Chattogram | 1325 | 13.08.2020 | 23:00
Khulna | 1605 | 12.08.2020 | 22:00
Rajshahi | 1361 | 31.08.2020 | 21:00
Cumilla | 1241 | 03.08.2020 | 21:00
Mymensingh | 1029 | 14.08.2020 | 20:00
Sylhet | 559 | 13.08.2020 | 20:00
Barisal | 386 | 03.08.2020 | 21:00
Rangpur | 815 | 13.08.2020 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: August'2020
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 405 | 19 | 2020-08-01 | 24:00 | 380 | 2 | 2020-08-01 | 4:00
2 | Bheramara | 400 | 410 | 23 | 2020-08-01 | 7:00 | 383 | 31 | 2020-08-01 | 23:00
3 | Ashuganj(N) | 400 | 402 | 3 | 2020-08-01 | 16:00 | 378 | 7 | 2020-08-01 | 13:00
4 | Payra | 400 | 420 | 23 | 2020-08-01 | 9:00 | 380 | 23 | 2020-08-01 | 12:00
5 | Kaliakoir | 400 | 390 | 19 | 2020-08-01 | 8:00 | 358 | 16 | 2020-08-01 | 10:00
6 | Bhulta | 400 | 413 | 4 | 2020-08-01 | 5:00 | 371 | 16 | 2020-08-01 | 10:00
7 | Gopalganj | 400 | 420 | 29 | 2020-08-01 | 18:00 | 370 | 19 | 2020-08-01 | 15:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 240 | 3 | 2020-08-01 | 18:00 | 230 | 2 | 2020-08-01 | 8:00
2 | Ishurdi | 230 | 238 | 2 | 2020-08-01 | 18:00 | 224 | 9 | 2020-08-01 | 21:00
3 | Ashuganj | 230 | 241 | 3 | 2020-08-01 | 11:00 | 226 | 10 | 2020-08-01 | 10:00
4 | Serajganj | 230 | 234 | 1 | 2020-08-01 | 11:00 | 225 | 1 | 2020-08-01 | 21:00
5 | Baghabari | 230 | 246 | 30 | 2020-08-01 | 18:00 | 232 | 3 | 2020-08-01 | 19:00
6 | Barapukuria | 230 | 236 | 12 | 2020-08-01 | 10:00 | 220 | 3 | 2020-08-01 | 21:00
7 | Bogura | 230 | 231 | 4 | 2020-08-01 | 15:00 | 209 | 14 | 2020-08-01 | 21:00
8 | Rajshahi | 230 | 235 | 20 | 2020-08-01 | 18:30 | 212 | 30 | 2020-08-01 | 22:00
9 | Khulna South | 230 | 240 | 18 | 2020-08-01 | 18:30 | 207 | 23 | 2020-08-01 | 17:00
10 | Rampura | 230 | 230 | 2 | 2020-08-01 | 16:00 | 219 | 16 | 2020-08-01 | 9:00
11 | Haripur | 230 | 232 | 3 | 2020-08-01 | 13:00 | 216 | 16 | 2020-08-01 | 10:00
12 | Hasnabad | 230 | 236 | 29 | 2020-08-01 | 1:00 | 215 | 16 | 2020-08-01 | 10:00
13 | Shyampur | 230 | 230 | 3 | 2020-08-01 | 9:00 | 212 | 16 | 2020-08-01 | 10:00
14 | Aminbazar | 230 | 232 | 3 | 2020-08-01 | 6:00 | 213 | 16 | 2020-08-01 | 10:00
15 | Tongi | 230 | 233 | 3 | 2020-08-01 | 11:00 | 208 | 16 | 2020-08-01 | 10:00
16 | Comilla (N) | 230 | 238 | 23 | 2020-08-01 | 19:00 | 223 | 9 | 2020-08-01 | 2:00
17 | Hathazari | 230 | 234 | 30 | 2020-08-01 | 19:00 | 210 | 4 | 2020-08-01 | 15:00
18 | Megnaghat | 230 | 238 | 3 | 2020-08-01 | 18:00 | 223 | 20 | 2020-08-01 | 12:00
19 | Fenchuganj | 230 | 240 | 18 | 2020-08-01 | 7:00 | 227 | 2 | 2020-08-01 | 24:00
20 | Siddhirganj | 230 | 236 | 19 | 2020-08-01 | 5:00 | 218 | 16 | 2020-08-01 | 10:00
21 | Maniknagar | 230 | 234 | 3 | 2020-08-01 | 9:00 | 216 | 16 | 2020-08-01 | 10:00
22 | Old Airport | 230 | 231 | 3 | 2020-08-01 | 9:00 | 211 | 16 | 2020-08-01 | 10:00
23 | Barisal | 230 | 250 | 12 | 2020-08-01 | 18:00 | 219 | 19 | 2020-08-01 | 12:00
24 | AKSML | 230 | 247 | 19 | 2020-08-01 | 13:00 | 207 | 4 | 2020-08-01 | 15:00
25 | BSRM | 230 | 231 | 28 | 2020-08-01 | 19:00 | 212 | 4 | 2020-08-01 | 16:00
26 | Bibiyana | 230 | 240 | 28 | 2020-08-01 | 13:00 | 216 | 19 | 2020-08-01 | 9:00
27 | Bhulta | 230 | 236 | 3 | 2020-08-01 | 11:00 | 221 | 25 | 2020-08-01 | 17:00
28 | Ashuganj (S) | 230 | 240 | 3 | 2020-08-01 | 11:00 | 218 | 16 | 2020-08-01 | 10:00
29 | Kaliakoir | 230 | 237 | 16 | 2020-08-01 | 19:00 | 218 | 25 | 2020-08-01 | 12:00
30 | GPH | 230 | 229 | 21 | 2020-08-01 | 1:00 | 207 | 5 | 2020-08-01 | 17:00
132 kV Substation
1 | Siddhirganj | 132 | 137 | 3 | 2020-08-01 | 0.79167 | 121 | 16 | 2020-08-01 | 0.375
2 | Munsiganj | 132 | 141 | 29 | 2020-08-01 | 0.45833 | 119 | 16 | 2020-08-01 | 0.41667
3 | Sonargaon | 132 | 138 | 28 | 2020-08-01 | 0.083333 | 120 | 16 | 2020-08-01 | 0.41667
4 | Shyampur | 132 | 136 | 2 | 2020-08-01 | 0.75 | 122 | 16 | 2020-08-01 | 0.41667
5 | Bhulta | 132 | 130 | 3 | 2020-08-01 | 0.45833 | 112 | 16 | 2020-08-01 | 0.33333
6 | Madanganj | 132 | 140 | 29 | 2020-08-01 | 0.875 | 117 | 16 | 2020-08-01 | 0.41667
7 | Shitalakhya | 132 | 143 | 2 | 2020-08-01 | 0.95833 | 127 | 16 | 2020-08-01 | 0.375
8 | Rahim Steal | 132 | 136 | 3 | 2020-08-01 | 0.20833 | 122 | 16 | 2020-08-01 | 0.375
9 | Matuail | 132 | 137 | 3 | 2020-08-01 | 0.79167 | 121 | 16 | 2020-08-01 | 0.375
10 | Ghorasal | 132 | 140 | 1 | 2020-08-01 | 0.33333 | 130 | 23 | 2020-08-01 | 0.625
11 | Narsinghdi | 132 | 132 | 3 | 2020-08-01 | 0.45833 | 117 | 16 | 2020-08-01 | 0.41667
12 | Haripur (SBU) | 132 | 139 | 10 | 2020-08-01 | 0.66667 | 121 | 16 | 2020-08-01 | 0.41667
13 | Ullon | 132 | 135 | 1 | 2020-08-01 | 0.41667 | 124 | 16 | 2020-08-01 | 0.33333
14 | Hasnabad | 132 | 140 | 3 | 2020-08-01 | 0.79167 | 127 | 16 | 2020-08-01 | 0.375
15 | Magbazar | 132 | 136 | 3 | 2020-08-01 | 0.20833 | 125 | 16 | 2020-08-01 | 0.41667
16 | Maniknagar | 132 | 136 | 3 | 2020-08-01 | 0.20833 | 124 | 16 | 2020-08-01 | 0.41667
17 | Bangabhaban | 132 | 136 | 3 | 2020-08-01 | 0.20833 | 124 | 16 | 2020-08-01 | 0.41667
18 | Narinda | 132 | 136 | 3 | 2020-08-01 | 0.20833 | 124 | 16 | 2020-08-01 | 0.41667
19 | Dhanmondi | 132 | 135 | 1 | 2020-08-01 | 0.41667 | 124 | 16 | 2020-08-01 | 0.33333
20 | Lalbag | 132 | 141 | 3 | 2020-08-01 | 0.8125 | 118 | 16 | 2020-08-01 | 0.41667
21 | Madartek | 132 | 135 | 2 | 2020-08-01 | 0.75 | 124 | 16 | 2020-08-01 | 0.41667
22 | Dhaka University | 132 | - | - | - | - | - | - | - | -
23 | Fatullah | 132 | 137 | 3 | 2020-08-01 | 0.45833 | 122 | 16 | 2020-08-01 | 0.41667
24 | Mirpur | 132 | 136 | 3 | 2020-08-01 | 0.375 | 119 | 16 | 2020-08-01 | 0.41667
25 | Kalyanpur | 132 | 136 | 3 | 2020-08-01 | 0.375 | 120 | 16 | 2020-08-01 | 0.41667
26 | Gulshan | 132 | 135 | 3 | 2020-08-01 | 0.125 | 124 | 16 | 2020-08-01 | 0.41667
27 | Uttara | 132 | 137 | 3 | 2020-08-01 | 0.5 | 120 | 16 | 2020-08-01 | 0.41667
28 | Uttara(New) | 132 | 137 | 3 | 2020-08-01 | 0.20833 | 124 | 16 | 2020-08-01 | 0.41667
29 | Kamrangirchar | 132 | 139 | 8 | 2020-08-01 | 0.8125 | 122 | 17 | 2020-08-01 | 0.625
30 | Savar | 132 | 135 | 3 | 2020-08-01 | 0.083333 | 121 | 25 | 2020-08-01 | 0.5
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: August'2020
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
31 | Bhasantec | 132 | 134 | 3 | 2020-08-01 | 0.125 | 123 | 16 | 2020-08-01 | 0.41667
32 | Agargaon | 132 | 136 | 23 | 2020-08-01 | 0.16667 | 123 | 16 | 2020-08-01 | 0.41667
33 | Satmosjid | 132 | 135 | 3 | 2020-08-01 | 0.25 | 124 | 16 | 2020-08-01 | 0.41667
34 | Tongi | 132 | 139 | 2 | 2020-08-01 | 0.875 | 125 | 16 | 2020-08-01 | 0.41667
35 | Kabirpur | 132 | 137 | 4 | 2020-08-01 | 0.77083 | 124 | 12 | 2020-08-01 | 0.91667
36 | Basundhara | 132 | 138 | 24 | 2020-08-01 | 0.77083 | 124 | 16 | 2020-08-01 | 0.41667
37 | Manikganj | 132 | 142 | 3 | 2020-08-01 | 0.79167 | 125 | 24 | 2020-08-01 | 0.625
38 | Joydevpur | 132 | 143 | 1 | 2020-08-01 | 0.79167 | 133 | 10 | 2020-08-01 | 0.41667
39 | New Tongi | 132 | 139 | 3 | 2020-08-01 | 0.45833 | 123 | 16 | 2020-08-01 | 0.41667
40 | Kodda | 132 | 142 | 7 | 2020-08-01 | 0.875 | 118 | 16 | 2020-08-01 | 0.41667
41 | Dhamrai | 132 | 137 | 21 | 2020-08-01 | 0.77083 | 124 | 10 | 2020-08-01 | 0.91667
42 | Rajendrapur | 132 | 139 | 28 | 2020-08-01 | 0.20833 | 117 | 16 | 2020-08-01 | 0.41667
43 | Valuka | 132 | 131 | 30 | 2020-08-01 | 0.16667 | 107 | 10 | 2020-08-01 | 0.8125
44 | Tangail | 132 | 139 | 22 | 2020-08-01 | 0.25 | 120 | 12 | 2020-08-01 | 0.95833
45 | Mymensing | 132 | 131 | 8 | 2020-08-01 | 0.75 | 112 | 10 | 2020-08-01 | 0.95833
46 | Kishorganj | 132 | 134 | 14 | 2020-08-01 | 0.70833 | 114 | 10 | 2020-08-01 | 0.91667
47 | Netrokona | 132 | 131 | 30 | 2020-08-01 | 0.16667 | 107 | 13 | 2020-08-01 | 0.83333
48 | Jamalpur | 132 | 140 | 7 | 2020-08-01 | 0.66667 | 119 | 24 | 2020-08-01 | 0.95833
49 | Sherpur | 132 | 139 | 7 | 2020-08-01 | 0.66667 | 119 | 24 | 2020-08-01 | 0.95833
50 | Srimongal | 132 | 138 | 28 | 2020-08-01 | 0.54167 | 127 | 8 | 2020-08-01 | 0.875
51 | Shahjibazar | 132 | 138 | 28 | 2020-08-01 | 0.54167 | 125 | 10 | 2020-08-01 | 0.91667
52 | Fenchuganj | 132 | 136 | 18 | 2020-08-01 | 0.29167 | 125 | 2 | 2020-08-01 | 1899-12-31
53 | Khulawara | 132 | 136 | 10 | 2020-08-01 | 0.79167 | 124 | 2 | 2020-08-01 | 0.95833
54 | Sylhet | 132 | 133 | 22 | 2020-08-01 | 0.29167 | 119 | 5 | 2020-08-01 | 0.95833
55 | Chattak | 132 | 132 | 21 | 2020-08-01 | 0.41667 | 118 | 4 | 2020-08-01 | 0.95833
56 | Sunamganj | 132 | 131 | 10 | 2020-08-01 | 0.54167 | 113 | 2 | 2020-08-01 | 0.91667
57 | Biani Bazar | 132 | 133 | 28 | 2020-08-01 | 0.66667 | 115 | 2 | 2020-08-01 | 0.91667
58 | Comilla(South) | 132 | 129 | 15 | 2020-08-01 | 0.29167 | 118 | 30 | 2020-08-01 | 0.77083
59 | Comilla (North) | 132 | 141 | 24 | 2020-08-01 | 0.875 | 128 | 16 | 2020-08-01 | 0.45833
60 | Chandpur | 132 | 142 | 25 | 2020-08-01 | 0.79167 | 118 | 3 | 2020-08-01 | 0.66667
61 | Feni | 132 | 140 | 25 | 2020-08-01 | 0.79167 | 121 | 3 | 2020-08-01 | 0.625
62 | Chowmuhani | 132 | 139 | 24 | 2020-08-01 | 0.8125 | 115 | 4 | 2020-08-01 | 0.8125
63 | Ashuganj | 132 | 137 | 28 | 2020-08-01 | 0.29167 | 126 | 10 | 2020-08-01 | 0.95833
64 | Daudkandi | 132 | 140 | 25 | 2020-08-01 | 0.79167 | 120 | 6 | 2020-08-01 | 0.41667
65 | Brahminbaria | 132 | 136 | 28 | 2020-08-01 | 0.29167 | 121 | 10 | 2020-08-01 | 0.91667
66 | Ramganj | 132 | 138 | 24 | 2020-08-01 | 0.83333 | 113 | 4 | 2020-08-01 | 0.79167
67 | Chaddagram | 132 | 140 | 31 | 2020-08-01 | 0.83333 | 117 | 5 | 2020-08-01 | 0.625
68 | PHP | 132 | 139 | 31 | 2020-08-01 | 0.41667 | 122 | 5 | 2020-08-01 | 0.70833
69 | Madanhat | 132 | 141 | 29 | 2020-08-01 | 0 | 128 | 4 | 2020-08-01 | 0.625
70 | Hathazari | 132 | 139 | 30 | 2020-08-01 | 0.79167 | 123 | 29 | 2020-08-01 | 0.29167
71 | Khulshi | 132 | 138 | 30 | 2020-08-01 | 0.79167 | 124 | 4 | 2020-08-01 | 0.625
72 | Halishahar | 132 | 141 | 29 | 2020-08-01 | 0.8125 | 126 | 4 | 2020-08-01 | 0.625
73 | Baraulia | 132 | 139 | 30 | 2020-08-01 | 0.83333 | 126 | 4 | 2020-08-01 | 0.58333
74 | Sikalbaha | 132 | 141 | 30 | 2020-08-01 | 0.79167 | 127 | 1 | 2020-08-01 | 0.58333
75 | Dohazari | 132 | 139 | 31 | 2020-08-01 | 0.54167 | 121 | 5 | 2020-08-01 | 0.77083
76 | Cox'sbazar | 132 | 135 | 16 | 2020-08-01 | 0.25 | 113 | 5 | 2020-08-01 | 0.75
77 | Chandraghona | 132 | 139 | 30 | 2020-08-01 | 0.79167 | 127 | 4 | 2020-08-01 | 0.625
78 | Kaptai | 132 | 137 | 25 | 2020-08-01 | 0.75 | 128 | 5 | 2020-08-01 | 0.54167
79 | A. Khaer Stl. | 132 | 136 | 30 | 2020-08-01 | 0.77083 | 125 | 4 | 2020-08-01 | 0.66667
80 | Bakulia | 132 | 139 | 29 | 2020-08-01 | 0.70833 | 125 | 4 | 2020-08-01 | 0.625
81 | Julda | 132 | 141 | 30 | 2020-08-01 | 0.041667 | 126 | 4 | 2020-08-01 | 0.58333
82 | TK Chemical | 132 | 140 | 30 | 2020-08-01 | 0.79167 | 123 | 24 | 2020-08-01 | 0.375
83 | Modern Steel | 132 | 139 | 29 | 2020-08-01 | 0 | 127 | 1 | 2020-08-01 | 0.625
84 | Shahmirpur | 132 | 141 | 30 | 2020-08-01 | 0.79167 | 126 | 4 | 2020-08-01 | 0.54167
85 | Khagrachhari | 132 | 137 | 30 | 2020-08-01 | 0.8125 | 126 | 4 | 2020-08-01 | 0.625
86 | Matarbari | 132 | 135 | 15 | 2020-08-01 | 0.8125 | 115 | 5 | 2020-08-01 | 0.77083
87 | Baroiar Hat | 132 | 138 | 23 | 2020-08-01 | 0.41667 | 120 | 4 | 2020-08-01 | 0.625
88 | Rangamati | 132 | 138 | 29 | 2020-08-01 | 0.70833 | 127 | 4 | 2020-08-01 | 0.58333
89 | Goalpara | 132 | 140 | 3 | 2020-08-01 | 0.625 | 122 | 30 | 2020-08-01 | 0.91667
90 | Khulna Central | 132 | 139 | 2 | 2020-08-01 | 0.75 | 123 | 2 | 2020-08-01 | 0.54167
91 | Noapara | 132 | 139 | 29 | 2020-08-01 | 0.5 | 120 | 2 | 2020-08-01 | 0.54167
92 | Jessore | 132 | 135 | 4 | 2020-08-01 | 0.54167 | 114 | 30 | 2020-08-01 | 0.91667
93 | Benapol | 132 | 137 | 29 | 2020-08-01 | 0.5 | 113 | 30 | 2020-08-01 | 0.91667
94 | Jhenida | 132 | 133 | 4 | 2020-08-01 | 0.54167 | 106 | 3 | 2020-08-01 | 0.8125
95 | Bottail | 132 | 136 | 4 | 2020-08-01 | 0.54167 | 120 | 3 | 2020-08-01 | 0.8125
96 | G.K Project | 132 | 142 | 30 | 2020-08-01 | 0.75 | 127 | 29 | 2020-08-01 | 0.58333
97 | Faridpur | 132 | 135 | 4 | 2020-08-01 | 0.75 | 121 | 3 | 2020-08-01 | 0.83333
98 | Madaripur | 132 | 140 | 5 | 2020-08-01 | 0.58333 | 125 | 3 | 2020-08-01 | 0.83333
99 | Sariatpur | 132 | 140 | 5 | 2020-08-01 | 0.58333 | 120 | 15 | 2020-08-01 | 0.95833
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: August'2020
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
100 | Gopalganj | 132 | 144 | 29 | 2020-08-01 | 0.625 | 120 | 3 | 2020-08-01 | 0.8125
101 | Bagerhat | 132 | 138 | 3 | 2020-08-01 | 0.75 | 113 | 30 | 2020-08-01 | 0.91667
102 | Mongla | 132 | 135 | 3 | 2020-08-01 | 0.625 | 113 | 30 | 2020-08-01 | 0.91667
103 | Satkhira | 132 | 138 | 2 | 2020-08-01 | 0.75 | 118 | 30 | 2020-08-01 | 0.91667
104 | Gallamari | 132 | 141 | 3 | 2020-08-01 | 0.75 | 123 | 30 | 2020-08-01 | 0.91667
105 | Magura | 132 | 134 | 5 | 2020-08-01 | 0.66667 | 105 | 3 | 2020-08-01 | 0.8125
106 | Norail | 132 | 133 | 0 | 2020-08-01 | 0.83333 | 100 | 3 | 2020-08-01 | 0.83333
107 | Chuadanga | 132 | 130 | 4 | 2020-08-01 | 0.58333 | 95 | 3 | 2020-08-01 | 0.8125
108 | Barisal(N) | 132 | 142 | 3 | 2020-08-01 | 0.45833 | 125 | 3 | 2020-08-01 | 0.875
109 | Barisal(S) | 132 | 140 | 3 | 2020-08-01 | 0.33333 | 124 | 5 | 2020-08-01 | 0.91667
110 | Patuakhali | 132 | 140 | 5 | 2020-08-01 | 0.54167 | 115 | 3 | 2020-08-01 | 0.875
111 | Bhandaria | 132 | 140 | 5 | 2020-08-01 | 0.54167 | 109 | 30 | 2020-08-01 | 0.91667
112 | Ishurdi | 132 | 139 | 19 | 2020-08-01 | 0.77083 | 129 | 3 | 2020-08-01 | 0.8125
113 | Ruppur paromanobik | 132 | 140 | 30 | 2020-08-01 | 0.75 | 121 | 30 | 2020-08-01 | 0.875
114 | Natore | 132 | 138 | 19 | 2020-08-01 | 0.77083 | 117 | 29 | 2020-08-01 | 0.5
115 | Bogra | 132 | 138 | 19 | 2020-08-01 | 0.77083 | 122 | 5 | 2020-08-01 | 0.95833
116 | Noagaon | 132 | 134 | 4 | 2020-08-01 | 0.625 | 115 | 10 | 2020-08-01 | 0.875
117 | Rajshahi | 132 | 137 | 30 | 2020-08-01 | 0.75 | 114 | 29 | 2020-08-01 | 0.5
118 | Rajshahi New | 132 | 138 | 30 | 2020-08-01 | 0.75 | 113 | 29 | 2020-08-01 | 0.5
119 | C.Nawabganj | 132 | 135 | 29 | 2020-08-01 | 0.75 | 110 | 29 | 2020-08-01 | 0.5
120 | Amnura | 132 | 137 | 30 | 2020-08-01 | 0.75 | 107 | 29 | 2020-08-01 | 0.45833
121 | Pabna | 132 | 136 | 1 | 2020-08-01 | 0.41667 | 125 | 25 | 2020-08-01 | 0.875
122 | Shahjadpur | 132 | 140 | 7 | 2020-08-01 | 0.75 | 131 | 5 | 2020-08-01 | 0.91667
123 | Serajganj | 132 | 136 | 19 | 2020-08-01 | 0.77083 | 124 | 2 | 2020-08-01 | 0.875
124 | Niyamatpur | 132 | 133 | 25 | 2020-08-01 | 0.75 | 110 | 10 | 2020-08-01 | 0.875
125 | Joypurhat | 132 | 135 | 28 | 2020-08-01 | 0.75 | 112 | 10 | 2020-08-01 | 0.875
126 | Sherpur(Bogura) | 132 | 137 | 19 | 2020-08-01 | 0.77083 | 123 | 5 | 2020-08-01 | 0.95833
127 | Mohastangor | 132 | 136 | 18 | 2020-08-01 | 0.77083 | 118 | 10 | 2020-08-01 | 0.875
128 | Rangpur | 132 | 133 | 4 | 2020-08-01 | 0.625 | 110 | 10 | 2020-08-01 | 0.875
129 | Lalmonirhat | 132 | 129 | 30 | 2020-08-01 | 0.25 | 105 | 10 | 2020-08-01 | 0.875
130 | Saidpur | 132 | 130 | 4 | 2020-08-01 | 0.625 | 106 | 10 | 2020-08-01 | 0.875
131 | Purbasadipur | 132 | 128 | 4 | 2020-08-01 | 0.77083 | 101 | 3 | 2020-08-01 | 0.875
132 | Thakurgaon | 132 | 128 | 4 | 2020-08-01 | 0.625 | 100 | 14 | 2020-08-01 | 0.875
133 | Palashbari | 132 | 130 | 12 | 2020-08-01 | 0.45833 | 110 | 2 | 2020-08-01 | 0.875
134 | Barapukuria | 132 | 136 | 12 | 2020-08-01 | 0.41667 | 120 | 3 | 2020-08-01 | 0.875
135 | Panchagar | 132 | 127 | 4 | 2020-08-01 | 0.77083 | 92 | 3 | 2020-08-01 | 0.91667
136 | Joldhaka | 132 | 130 | 19 | 2020-08-01 | 0.75 | 103 | 10 | 2020-08-01 | 0.875
137 | Kurigram | 132 | 132 | 31 | 2020-08-01 | 0.875 | 101 | 14 | 2020-08-01 | 0.875
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:August' 2020
Name of the | Auto transofrmer |  | Recorded maximum load
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kV side ) | Date | Time | Remarks
| TR1 | 225 | 125 | 370
Hasnabad | TR2 | 225 | 110 | 370 | 15.08.2020 | 12:00 |  | 1
| TR3 | 225 | 108 | 370
| TR1 | 225 | 190 | 540 |  |  |  | 2
Tongi | TR2 | 225 | 190 | 540 | 05.07.2020 | 12:00
| TR3 | 225 | 190 | 540
Haripur | TR1 | 225 | 141 | 400 | 16.08.2020 | 09:00
| TR3 | 225 | 141 | 400
| TR1 | 225 | 178 | 500
Rampura | TR2 | 225 | 178 | 500 | 31.08.2020 | 14:00 |  | 4
| TR3 | 225 | 178 | 500
| TR1 | 225 | 145 | 416
Aminbazar | TR2 | 225 | 145 | 416 | 16.08.2020 | 16:00 |  | 5
| TR3 | 225 | 151 | 437
Maniknagar | TR1 | 300 | 110 | 330 | 13.08.2020 | 13:00 |  | 6
| TR2 | 300 | 110 | 330
Cumilla (N) | TR1 | 225 | 173 | 516 | 01.08.2020 | 14:00 |  | 7
| TR2 | 225 | 171 | 512
Fenchuganj | AT2 | 300 | 212 | 577 | 09.08.2020 | 19:00 |  | 8
| MT1 | 150 | 74 | 210 |  |  |  | 9
Hathazari | MT2 | 150 | 74 | 210 | 01.08.2020 | 13:00
| MT3 | 150 | 74 | 210
| MT4 | 150 | 74 | 210
| TR1 | 225 | 100 | 270
Ishurdi | TR2 | 225 | 100 | 270 | 02.08.2020 | 21:00 |  | 10
| TR3 | 225 | 100 | 270
Khulna(S) | TR1 | 225 | 122 | 332
| TR2 | 225 | 122 | 332 | 30.08.2020 | 03:00 |  | 11
| TR3 | 300 | 157 | 318
Bogra | TR1 | 225 | 126 | 381 | 29.08.2020 | 12:00 |  | 12
| TR2 | 225 | 126 | 381
| TR3 | 225 | 172 | 502
Baghabari | TR1 | 300 | 155 | 440 | 04.08.2020 | 22:00 |  | 13
| TR2 | 225 | 115 | 320
Barapukuria | TR1 | 225 | 191 | 950 | 21.08.2020 | 21:00 | Due to unavailability of 230 kV side meters
| TR2 | 225 | 168 | 840 |  |  | 132 kV current is being provided | 14
| TR6 | 300 | 217 | 1082
Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:August' 2020
Name of the | Transofrmer |  | Recorded maximum load |  |  |  | Remarks
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 400 kV side ) | Date | Time
Kaliakoir | TR1(400/230 kV) | 520 | 147 | 237 | 02.08.2020 | 22:00
| TR2(400/230 kV) | 520 | 147 | 237
| TR1(400/132 kV) | 325 | 270 | 465 | 31.08.2020 | 20:30
| TR2(400/132 kV) | 325 | 270 | 465
Bibiyana | ICT1(400/230 kV) | 520 | 99 | 172 | 01.08.2020 | 23:00
| ICT2(400/230kV) | 520 | 98 | 170
Bhulta | ATR1(400/230 kV) | 520 | 231 | 401 | 18.08.2020 | 9:00
| ATR2(400/230kV) | 520 | 231 | 401
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:August' 2020 | [6 empty] | (For Evening Peak) | [7 empty] | Month:August' 2020 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-08-20 | 10778 | 10778 | - | - | - | - | - | - | - | - | - | - | - | - | 01-08-20 | 6948.7 | 6948.7 | - | - | - | - | - | - | - | - | - | - | - | -
02-08-20 | 10872 | 10872 | - | - | - | - | - | - | - | - | - | - | - | - | 02-08-20 | 8016.67 | 8016.67 | - | - | - | - | - | - | - | - | - | - | - | -
03-08-20 | 11454 | 11454 | - | - | - | - | - | - | - | - | - | - | - | - | 03-08-20 | 8854.6 | 8854.6 | - | - | - | - | - | - | - | - | - | - | - | -
04-08-20 | 10910 | 10910 | - | - | - | - | - | - | - | - | - | - | - | - | 04-08-20 | 8472.3 | 8472.3 | - | - | - | - | - | - | - | - | - | - | - | -
05-08-20 | 10538 | 10538 | - | - | - | - | - | - | - | - | - | - | - | - | 05-08-20 | 8171.6 | 8171.6 | - | - | - | - | - | - | - | - | - | - | - | -
06-08-20 | 11137 | 11137 | - | - | - | - | - | - | - | - | - | - | - | - | 06-08-20 | 8725.8 | 8725.8 | - | - | - | - | - | - | - | - | - | - | - | -
07-08-20 | 11323 | 11323 | - | - | - | - | - | - | - | - | - | - | - | - | 07-08-20 | 8458.31 | 8458.31 | - | - | - | - | - | - | - | - | - | - | - | -
08-08-20 | 12023 | 12023 | - | - | - | - | - | - | - | - | - | - | - | - | 08-08-20 | 9665.7 | 9665.7 | - | - | - | - | - | - | - | - | - | - | - | -
09-08-20 | 11974 | 11974 | - | - | - | - | - | - | - | - | - | - | - | - | 09-08-20 | 10271.6 | 10271.6 | - | - | - | - | - | - | - | - | - | - | - | -
10-08-20 | 12246 | 12246 | - | - | - | - | - | - | - | - | - | - | - | - | 10-08-20 | 10363.3 | 10363.3 | - | - | - | - | - | - | - | - | - | - | - | -
11-08-20 | 12246 | 12246 | - | - | - | - | - | - | - | - | - | - | - | - | 11-08-20 | 10051.7 | 10051.7 | - | - | - | - | - | - | - | - | - | - | - | -
12-08-20 | 12238 | 12238 | - | - | - | - | - | - | - | - | - | - | - | - | 12-08-20 | 10458.18 | 10458.18 | - | - | - | - | - | - | - | - | - | - | - | -
13-08-20 | 12484 | 12484 | - | - | - | - | - | - | - | - | - | - | - | - | 13-08-20 | 10627.1 | 10627.1 | - | - | - | - | - | - | - | - | - | - | - | -
14-08-20 | 11501 | 11501 | - | - | - | - | - | - | - | - | - | - | - | - | 14-08-20 | 9399.3 | 9399.3 | - | - | - | - | - | - | - | - | - | - | - | -
15-08-20 | 10589 | 10589 | - | - | - | - | - | - | - | - | - | - | - | - | 15-08-20 | 8063.2 | 8063.2 | - | - | - | - | - | - | - | - | - | - | - | -
16-08-20 | 11346 | 11346 | - | - | - | - | - | - | - | - | - | - | - | - | 16-08-20 | 9527.7 | 9527.7 | - | - | - | - | - | - | - | - | - | - | - | -
17-08-20 | 11682 | 11682 | - | - | - | - | - | - | - | - | - | - | - | - | 17-08-20 | 9705.76 | 9705.76 | - | - | - | - | - | - | - | - | - | - | - | -
18-08-20 | 11793 | 11793 | - | - | - | - | - | - | - | - | - | - | - | - | 18-08-20 | 9724.8 | 9724.8 | - | - | - | - | - | - | - | - | - | - | - | -
19-08-20 | 11429 | 11429 | - | - | - | - | - | - | - | - | - | - | - | - | 19-08-20 | 9744.8 | 9744.8 | - | - | - | - | - | - | - | - | - | - | - | -
20-08-20 | 11132 | 11132 | - | - | - | - | - | - | - | - | - | - | - | - | 20-08-20 | 9170.8 | 9170.8 | - | - | - | - | - | - | - | - | - | - | - | -
21-08-20 | 10401 | 10401 | - | - | - | - | - | - | - | - | - | - | - | - | 21-08-20 | 7789.9 | 7789.9 | - | - | - | - | - | - | - | - | - | - | - | -
22-08-20 | 11429 | 11429 | - | - | - | - | - | - | - | - | - | - | - | - | 22-08-20 | 8925.8 | 8925.8 | - | - | - | - | - | - | - | - | - | - | - | -
23-08-20 | 11804 | 11804 | - | - | - | - | - | - | - | - | - | - | - | - | 23-08-20 | 9620.2 | 9620.2 | - | - | - | - | - | - | - | - | - | - | - | -
24-08-20 | 11975 | 11975 | - | - | - | - | - | - | - | - | - | - | - | - | 24-08-20 | 10151.1 | 10151.1 | - | - | - | - | - | - | - | - | - | - | - | -
25-08-20 | 11563 | 11563 | - | - | - | - | - | - | - | - | - | - | - | - | 25-08-20 | 10076.8 | 10076.8 | - | - | - | - | - | - | - | - | - | - | - | -
26-08-20 | 11239 | 11239 | - | - | - | - | - | - | - | - | - | - | - | - | 26-08-20 | 9440.5 | 9440.5 | - | - | - | - | - | - | - | - | - | - | - | -
27-08-20 | 11595 | 11595 | - | - | - | - | - | - | - | - | - | - | - | - | 27-08-20 | 10145.1 | 10145.1 | - | - | - | - | - | - | - | - | - | - | - | -
28-08-20 | 11251 | 11251 | - | - | - | - | - | - | - | - | - | - | - | - | 28-08-20 | 10012.9 | 10012.9 | - | - | - | - | - | - | - | - | - | - | - | -
29-08-20 | 12081 | 12081 | - | - | - | - | - | - | - | - | - | - | - | - | 29-08-20 | 9395.9 | 9395.9 | - | - | - | - | - | - | - | - | - | - | - | -
30-08-20 | 12177 | 12177 | - | - | - | - | - | - | - | - | - | - | - | - | 30-08-20 | 9575.3 | 9575.3
31-08-20 | 12577 | 12577 | - | - | - | - | - | - | - | - | - | - | - | - | 31-08-20 | 10843.5 | 10843.5

## QF-LDC-38
page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:August' 2020
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 12577 | 31/08/20 | 19:30
2 | Maximum Day Peak Genaration | MW | 10843.5 | 31/08/20 | 12:00
3 | Maximum Evening Peak Demand | MW | 12577 | 31/08/20 | 19:30
4 | Minimum Generation | MW | 6840.9 | 01/08/20 | 9:00
5 | Average of the daily evening peak Genaration | MW | 11541.5161
6 | Average of the daily day peak Genaration | MW | 9323.5619
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW | -
11 | Total Generation | MKWH | 7425.8474
12 | Total Generation by BPDB | MKWH | 3338.6684 | % of total Gen. | 44.96%
13 | Total Generation by IPP | MKWH | 2461.3125 | '' | 33.15%
14 | A) Total Generation by RPCL | MKWH | 129.8741 | '' | 1.749%
| B) Total Generation by REB | MKWH | 150.3385 | " | 2.025%
| C) Total Generation by RENTAL | MKWH | 569.7029 | " | 7.672%
| D) Total Imported from India (BIPTC) | MKWH | 681.4909 | " | 9.177%
| E) Total Imported from Tripura, India (A.C) | MKWH | 94.4602 | " | 1.272%
15 | Fuel wise Generation.
| A) Gas | MKWH | 4031.1453 | % of total Gen. | 54.29%
| B) Oil | MKWH | 2050.4803 | '' | 27.61%
| C) Hydro | MKWH | 89.1242 | '' | 1.2%
| D) Solar | MKWH | 4.5842 | '' | 0.06173%
| E) Coal | MKWH | 474.5624 | '' | 6.391%
| F) BIPTC (Import from India) | MKWH | 681.4909 | '' | 9.177%
| G) A.C (Import from Tripura, India) | MKWH | 94.4602 | '' | 1.272%
16 | Maximun of the daily total Generation . | MKWH | 267.1465 | 31-08-2020
17 | Monthly Load factor | % | 79.359
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 23421.0571
| A) Gas | M.Taka | 4644.7108
| B) Liquid fuel | M.Taka | 16576.2336
| C) Coal | M.Taka | 2200.1126
| D) BIPTC (Import from India) | M.Taka | 3475.6036
| E) Tripura(Import from India) | M.Taka | 708.4512
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 1019.5576 | 31/08/2020
| A) Gas | M.Taka | 162.1536 | 10/08/2020
| B) Liquid fuel | M.Taka | 800.1625 | 31/08/2020
| C) Coal | M.Taka | 80.8234 | 13/08/2020
| D) BIPTC (Import from India) | M.Taka | 115.1487 | 04-08-2020
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 3.4858
| B) Excluding Hydro & Solar | Taka/KWHR | 3.53
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 99 | 31/08/2020 | 06:00
b) | Actual | FT (MSL) | 93.18 | 31/08/2020 | 06:00
22 | Peak Genaration of August 2019 | MW | 12738 | 05/08/19 | 19:30
23 | Peak Demand of August 2019 | MW | 12738 | 05/08/19 | 19:30
24 | Maximum peak Generation recorded upto 31/08/2020 | MW | 12893 | 29/05/19 | 21:00
25 | Maximum peak Demand recorded upto 31/08/2020 | MW | 12893 | 29/05/19 | 21:00
26 | Maximum load shed recorded upto 31/08/2020 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.