## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-09-21 | Monday
|  |  | Date (day): | 2020-09-21 |  | Monday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13325.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14346 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-09-20 | 2020-09-21 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 115 | 115 | 115 | 75 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 200 | 200 | 165 |  | Machine problem
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 65 | 66 | 71 | 71
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 92 | 95 | 100 | 100
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 356 | 353 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 341 | 351 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 420 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 7 | 7 | 7 | 93 |  | Fuel shortage
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 80 | 96 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 53 | 65 | 0 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 0 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 7 | 7 | 7 | 93 |  | Fuel shortage
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 287 | 232 | 335 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 85 | 93 | 93 | 93
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 133 | 133 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 45 | 41 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 50 | 46 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 286 | 300 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 68 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 98 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 61 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 132 | 146 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 85 | 85 | 85 | 85 |  | 20 | Engine problem
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 3242 | 3467 | 3701 | 4051 | 1205 | 615
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 8 | 16 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 14 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 42 | 117 | 40 | 150 | 80 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 64 | 51 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 50 | 85 | 100 | 100
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 70 | 60 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 100 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 10 | 9 | 30
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 72 | 78 | 85 | 85 |  | 23 | Engine problem
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 307 | 307 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 11 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 1068 | 1179 | 1338 | 1444 | 470 | 346
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 100 | 100 | 130 | 130
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 210 | 200 | 225 | 225
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 305 | 360 | 360
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 32 | 32 | 32 | 32 | 13 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 20 | 20 | 25 | 25 | 30 |  | Gas shortage
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 16 | 26 | 8 | 8 | 187 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 122 | 123 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 42 | 0 | 42
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 81 | 90 | 90 |  | 73 | ST under shut down
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 42 | 153 | 200 | 200
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 15 | 18 | 18 | 18 |  | 4 | Engine problem
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 2 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 152 | 170 | 162 | 173
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 46 | 52 | 43 | 43 |  | 9 | Engine problem
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 21 | 21
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 80 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 114 | 114 | 114 | 114
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 104 | 113 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1474 | 1727 | 1778 | 2031 | 494 | 454
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 147 | 153 | 150 | 160 | 42 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 17 | 19 | 19 |  | 3 | Engine problem
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 0 | 0 | 0 |  | 95 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 190 | 200 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 473 | 485 | 485.6 | 494 | 42 | 98
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 85 | 86 | 90 | 90
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 29 | 29 | 30 | 30 |  | 35 | Unit-4 under shut down
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 236 | 256 | 250 | 250
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 53 | 53 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 43 | 40 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 0 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 62 | 52 | 65 | 65
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 87 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 213 | 213 | 213 | 213
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 17 | 18 | 18
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 21 | 24 | 25 | 25
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 280 | 341 | 341
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1316 | 1310 | 1397 | 1397 | 0 | 435
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 929 | 918 | 932 | 932
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 58 | 99 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 180 | 225 | 225
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 370 | 330 | 380 | 380
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 81 | 50 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 90 | 105 | 105
| 108 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1477 | 1738 | 1947 | 2103 | 0 | 0
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 20 | 32 | 33 | 33
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 60 | 52 | 60 | 80 |  | 134 | GT-2 & STG under shut down
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 55 | 78 | 90 | 90
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 310 | 470 | 580 | 580
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 445 | 742 | 873 | 893 | 0 | 134
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 34 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 50 | 50 | 50 | 50
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 27 | 43 | 43
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | ST Under maint & gas shoratge
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 190 | 179 | 200 | 200 |  |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 196 | 186 | 220 | 220 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 398 | 374 | 414 | 414 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 32
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 14 | 17 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 10 | 10 | 10 | 10
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 43 | 46 | 52 | 52
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 12 | 94 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 50 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 94 | 69 | 113 | 113
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 109 | 100 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 1127 | 1329 | 1548 | 1670 | 221 | 210
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 110 | 93 | 100 | 113
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 266 | 243 | 258 | 263 | 294 | 40
|  | Total |  |  |  |  | 20383 | 19892 | 10888 | 12220 | 13325.6 | 14346 | 2726 | 2332
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10419.3349 | 11694 | 12752.0103 | 13728.4881
| A. |  | 2020-09-20 | (Yesterday) |  |  |  |  | Sunday
| 1 | Highest Generation : |  |  | 12220 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 9325 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12220 | MW
| 3 | Day peak Generation : |  |  | 10888 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11694 | MW
| 4 | Evening peak Generation : |  |  | 12220 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 266.7719 | MKWHr | By Solar | 0.19067 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 137.9403 | MKWHr |  | By Oil: | 86.058 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 15.0901 | MKWHr |  | By Hydro: | 1.3819 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2726 | MW | Dhaka | 4274 | 4274 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2332 | MW | Chittagong | 1170 | 1170 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5058 | MW | Khulna | 1534 | 1534 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1075.4 | MMCFD |  |  | Rajshahi | 1305 | 1305 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 161041147.732 | ii) Oil : | Taka | 740023207.02 | Comilla | 840 | 840 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 70038205 | Total | Taka | 971102559.752 | Mymensingh | 971 | 971 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.109 | MKWHr. | Sylhet | 506 | 506 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -91 | MW (E to W) at | 19:00 | hrs | Barisal | 321 | 321 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -94 | MW at | 19:30 | hrs | Rangpur | 773 | 773 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 35.7° C |  |  | Total | 11694 | 11694 |  | 0
| B. |  | 2020-09-21 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 33.8° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14346 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10300 | MW
| 4 | Reserve(Generation end) |  |  |  | 2146 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 266.3353 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8954 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.2065 | MKWHr. | ii) HVDC Flow at Peak Time |  | 918 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.9043 | MKWHr. | iii) Maximum HVDC Flow : |  | 929 | MW at | 8:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 95.1 |  | (b) Today: | 95.15 |  | (c) Rule Curve: |  | 103.6
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-09-20
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 115 | 200 | 95 | 71 | 343 | 324 |  | 0 | 390 | 0 | 7 | 85 | 40 | 286 | 0 | 0 | 0 | 7 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 33 | 50 | 0 | 42 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 68 | 0 | 0 | 50 | 20 | 34 | 0 | 0 | 130 | 310 | 0 | 207 | 45 | 90 | 32 | 45 | 0 | 51 | 0 | 41 | 52 | 18 | 5 | 33 | 20 | 180 | 154 | 0 | 18 | 0 | 88 | 30 | 53 | 45 | 110 | 235 | 63 | 84 | 0 | 212 | 18 | 0 | 9 | 290 | 24 | 8 | 0 | 300 | 0 | 50 | 48 | 101 | 149 | 0 | 100 | 200 | 80 | 0 | 38 | 84 | 34 | 0 | 307 | 54 | 0 | 114 | 113 | 90 | 0 | 104 |  | 928 | 0 | 270 | 0 | 99 | 230 | 0 | 0 | 24 | 0 | 40 | 16 | 38 | 110 | 0 | 0 | 0 | 50 | 34 | 96 | 0 | 50 | 21 | 52 | 31 | 15 | 9 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 160 | 0 | 78 | 100 | 130 | 0 | 411 | 35 | 0 | 113 | 0 | 113 | 0 | 0 | 109 | 600 |  | 7553 | 4123 | 11676 | 3499 | 928 | 2197 | 3335 | 750 | 42 | 745 | 180 | 0 | 0 | 95.1
2:00 | 0 | 0 | 0 | 115 | 200 | 95 | 71 | 341 | 323 |  | 0 | 390 | 0 | 7 | 85 | 40 | 271 | 0 | 0 | 0 | 7 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 33 | 51 | 0 | 42 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 68 | 0 | 0 | 50 | 20 | 38 | 0 | 0 | 130 | 310 | 0 | 190 | 45 | 84 | 32 | 45 | 0 | 51 | 0 | 41 | 52 | 18 | 5 | 33 | 20 | 178 | 154 | 0 | 18 | 0 | 88 | 30 | 53 | 45 | 130 | 237 | 63 | 84 | 0 | 212 | 18 | 0 | 9 | 290 | 24 | 8 | 0 | 300 | 0 | 0 | 48 | 0 | 149 | 0 | 100 | 200 | 86 | 0 | 38 | 84 | 34 | 0 | 307 | 54 | 0 | 114 | 113 | 100 | 0 | 104 |  | 928 | 0 | 290 | 0 | 99 | 200 | 0 | 0 | 24 | 0 | 40 | 60 | 38 | 110 | 0 | 0 | 0 | 50 | 34 | 96 | 0 | 50 | 21 | 52 | 31 | 15 | 9 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 150 | 0 | 76 | 100 | 130 | 0 | 398 | 35 | 0 | 113 | 0 | 112 | 0 | 0 | 109 | 580 |  | 7402 | 4111 | 11513 | 3515 | 928 | 2205 | 3200 | 730 | 42 | 715 | 178 | 0 | 0 | 95.1
3:00 | 0 | 0 | 0 | 115 | 200 | 95 | 71 | 345 | 324 |  | 0 | 360 | 0 | 7 | 96 | 40 | 262 | 0 | 0 | 0 | 7 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 33 | 51 | 0 | 40 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 68 | 0 | 25 | 50 | 20 | 38 | 0 | 0 | 130 | 310 | 0 | 177 | 45 | 83 | 32 | 45 | 0 | 51 | 0 | 41 | 52 | 18 | 5 | 33 | 20 | 178 | 154 | 0 | 18 | 0 | 89 | 30 | 53 | 45 | 130 | 235 | 63 | 84 | 0 | 212 | 18 | 0 | 9 | 295 | 24 | 8 | 0 | 300 | 0 | 0 | 48 | 0 | 149 | 0 | 100 | 50 | 88 | 0 | 38 | 84 | 34 | 0 | 307 | 54 | 0 | 114 | 108 | 100 | 0 | 104 |  | 928 | 0 | 305 | 0 | 99 | 200 | 0 | 0 | 24 | 0 | 40 | 60 | 38 | 110 | 0 | 0 | 0 | 50 | 34 | 96 | 0 | 0 | 21 | 52 | 31 | 15 | 9 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 150 | 0 | 77 | 100 | 130 | 0 | 392 | 35 | 0 | 113 | 0 | 113 | 0 | 0 | 109 | 580 |  | 7239 | 4072 | 11311 | 3510 | 928 | 2176 | 3034 | 730 | 40 | 715 | 178 | 0 | 0 | 95.1
4:00 | 0 | 0 | 0 | 115 | 200 | 95 | 71 | 339 | 323 |  | 0 | 360 | 0 | 7 | 96 | 40 | 267 | 0 | 0 | 0 | 7 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 33 | 51 | 0 | 40 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 68 | 0 | 84 | 50 | 20 | 42 | 0 | 0 | 130 | 310 | 0 | 173 | 45 | 82 | 32 | 45 | 0 | 51 | 0 | 32 | 52 | 18 | 5 | 25 | 20 | 174 | 154 | 0 | 18 | 0 | 88 | 30 | 50 | 45 | 130 | 236 | 63 | 84 | 0 | 213 | 18 | 0 | 9 | 280 | 24 | 5 | 0 | 300 | 0 | 0 | 48 | 0 | 149 | 0 | 100 | 0 | 100 | 0 | 38 | 84 | 34 | 0 | 307 | 54 | 0 | 114 | 108 | 100 | 0 | 104 |  | 928 | 0 | 320 | 0 | 99 | 200 | 0 | 0 | 4 | 0 | 40 | 60 | 10 | 0 | 0 | 0 | 0 | 50 | 10 | 96 | 0 | 0 | 21 | 52 | 31 | 15 | 9 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 150 | 0 | 76 | 20 | 130 | 0 | 393 | 35 | 0 | 113 | 0 | 113 | 0 | 0 | 109 | 560 |  | 7216 | 3805 | 11021 | 3509 | 928 | 2133 | 2865 | 710 | 40 | 662 | 174 | 0 | 0 | 95.1
5:00 | 0 | 0 | 0 | 115 | 200 | 95 | 70 | 339 | 304 |  | 0 | 360 | 0 | 7 | 96 | 40 | 287 | 0 | 0 | 0 | 7 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 33 | 51 | 0 | 40 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 68 | 0 | 84 | 50 | 20 | 42 | 0 | 0 | 130 | 310 | 0 | 170 | 45 | 85 | 32 | 44 | 0 | 51 | 0 | 0 | 52 | 15 | 5 | 25 | 20 | 166 | 154 | 0 | 18 | 0 | 89 | 30 | 47 | 45 | 130 | 234 | 63 | 84 | 0 | 213 | 18 | 0 | 9 | 280 | 24 | 8 | 0 | 300 | 0 | 0 | 62 | 0 | 149 | 0 | 100 | 0 | 100 | 0 | 38 | 84 | 34 | 0 | 307 | 54 | 0 | 70 | 107 | 100 | 0 | 104 |  | 928 | 0 | 330 | 0 | 99 | 135 | 0 | 0 | 0 | 0 | 40 | 60 | 20 | 0 | 0 | 0 | 0 | 50 | 0 | 96 | 0 | 0 | 21 | 52 | 0 | 15 | 9 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 150 | 0 | 76 | 0 | 130 | 0 | 383 | 0 | 0 | 113 | 0 | 113 | 0 | 0 | 109 | 450 |  | 7140 | 3537 | 10677 | 3535 | 928 | 2109 | 2779 | 600 | 40 | 520 | 166 | 0 | 0 | 95.1
6:00 | 0 | 0 | 0 | 115 | 200 | 95 | 70 | 343 | 278 |  | 0 | 360 | 0 | 7 | 96 | 40 | 274 | 0 | 0 | 0 | 7 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 22 | 25 | 20 | 33 | 33 | 0 | 0 | 40 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 65 | 30 | 20 | 42 | 0 | 0 | 130 | 310 | 0 | 170 | 45 | 86 | 32 | 45 | 0 | 51 | 0 | 0 | 0 | 15 | 5 | 25 | 20 | 152 | 154 | 0 | 19 | 0 | 88 | 30 | 47 | 45 | 130 | 235 | 63 | 84 | 0 | 213 | 18 | 0 | 9 | 285 | 24 | 8 | 0 | 300 | 0 | 0 | 188 | 0 | 149 | 0 | 100 | 0 | 50 | 0 | 38 | 34 | 17 | 0 | 307 | 0 | 0 | 0 | 108 | 100 | 0 | 104 |  | 928 | 0 | 350 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 15 | 9 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 150 | 0 | 78 | 0 | 130 | 0 | 312 | 0 | 0 | 35 | 0 | 113 | 0 | 0 | 109 | 450 |  | 6737 | 3192 | 9929 | 3548 | 928 | 2023 | 2315 | 600 | 40 | 323 | 152 | 0 | 0 | 95.1
7:00 | 0 | 0 | 0 | 115 | 200 | 95 | 70 | 347 | 272 |  | 0 | 360 | 0 | 7 | 48 | 15 | 296 | 0 | 0 | 0 | 7 | 85 | 150 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 25 | 20 | 25 | 33 | 0 | 0 | 40 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 27 | 0 | 0 | 130 | 345 | 0 | 204 | 8 | 90 | 32 | 20 | 0 | 51 | 0 | 0 | 0 | 17 | 5 | 25 | 20 | 138 | 151 | 0 | 19 | 0 | 88 | 30 | 47 | 45 | 130 | 234 | 61 | 84 | 0 | 213 | 18 | 0 | 9 | 300 | 24 | 5 | 0 | 200 | 0 | 0 | 197 | 0 | 149 | 2 | 100 | 0 | 10 | 0 | 56 | 0 | 0 | 1 | 307 | 0 | 0 | 0 | 105 | 100 | 0 | 104 |  | 928 | 0 | 360 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 9 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 53 | 0 | 140 | 0 | 347 | 0 | 0 | 0 | 0 | 80 | 0 | 1 | 109 | 380 |  | 6294 | 3031 | 9325 | 3612 | 928 | 1962 | 1841 | 530 | 40 | 270 | 138 | 4 | 0 | 95.1
8:00 | 0 | 0 | 0 | 115 | 200 | 95 | 68 | 345 | 274 |  | 0 | 360 | 0 | 7 | 48 | 15 | 288 | 0 | 0 | 0 | 7 | 85 | 150 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 22 | 25 | 20 | 25 | 33 | 0 | 0 | 40 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 9 | 0 | 0 | 130 | 310 | 0 | 213 | 8 | 90 | 32 | 20 | 0 | 43 | 0 | 0 | 0 | 18 | 5 | 25 | 20 | 136 | 150 | 0 | 19 | 1 | 89 | 30 | 47 | 45 | 130 | 234 | 62 | 83 | 0 | 213 | 18 | 0 | 9 | 310 | 24 | 0 | 0 | 200 | 0 | 0 | 198 | 0 | 149 | 6 | 100 | 0 | 10 | 0 | 75 | 0 | 0 | 2 | 307 | 0 | 0 | 0 | 103 | 100 | 0 | 104 |  | 929 | 0 | 365 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 163 | 0 | 53 | 0 | 179 | 0 | 346 | 0 | 0 | 0 | 0 | 52 | 0 | 3 | 109 | 380 |  | 6297 | 3062 | 9359 | 3653 | 929 | 1943 | 1846 | 530 | 40 | 270 | 136 | 12 | 0 | 95.1
9:00 | 0 | 0 | 0 | 115 | 200 | 91 | 68 | 355 | 323 |  | 0 | 400 | 0 | 7 | 60 | 30 | 292 | 0 | 0 | 0 | 7 | 85 | 150 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 22 | 25 | 20 | 25 | 33 | 0 | 0 | 40 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 78 | 1 | 20 | 4 | 0 | 0 | 100 | 330 | 0 | 211 | 8 | 91 | 32 | 20 | 0 | 43 | 0 | 0 | 0 | 15 | 5 | 25 | 20 | 136 | 149 | 0 | 19 | 2 | 88 | 30 | 47 | 45 | 130 | 236 | 63 | 83 | 0 | 214 | 17 | 0 | 9 | 300 | 24 | 0 | 0 | 208 | 0 | 0 | 200 | 0 | 149 | 5 | 100 | 0 | 10 | 0 | 75 | 50 | 0 | 2 | 307 | 0 | 0 | 0 | 104 | 100 | 0 | 104 |  | 928 | 0 | 290 | 0 | 85 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 10 | 11 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 171 | 0 | 50 | 0 | 192 | 0 | 401 | 0 | 0 | 0 | 0 | 58 | 0 | 4 | 109 | 380 |  | 6528 | 3051 | 9579 | 3620 | 928 | 2063 | 1978 | 531 | 40 | 270 | 136 | 13 | 0 | 95.1
10:00 | 0 | 0 | 0 | 115 | 200 | 92 | 68 | 381 | 343 |  | 0 | 420 | 0 | 7 | 80 | 55 | 278 | 0 | 0 | 0 | 7 | 85 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 25 | 33 | 4 | 0 | 42 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 30 | 80 | 28 | 20 | 3 | 0 | 0 | 100 | 355 | 0 | 211 | 8 | 90 | 32 | 20 | 0 | 51 | 0 | 0 | 2 | 15 | 5 | 25 | 20 | 142 | 149 | 0 | 19 | 2 | 88 | 29 | 47 | 44 | 163 | 234 | 63 | 84 | 0 | 214 | 18 | 0 | 9 | 310 | 24 | 0 | 0 | 275 | 0 | 0 | 190 | 0 | 149 | 19 | 90 | 0 | 35 | 0 | 109 | 84 | 19 | 4 | 308 | 28 | 0 | 0 | 104 | 100 | 0 | 104 |  | 928 | 0 | 300 | 0 | 32 | 120 | 0 | 0 | 0 | 0 | 0 | 40 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 15 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 190 | 0 | 23 | 0 | 206 | 0 | 399 | 0 | 0 | 24 | 0 | 109 | 0 | 5 | 109 | 310 |  | 7088 | 3013 | 10101 | 3674 | 928 | 2127 | 2428 | 460 | 42 | 270 | 142 | 30 | 0 | 95.1
11:00 | 0 | 0 | 0 | 115 | 200 | 92 | 66 | 365 | 341 |  | 0 | 420 | 0 | 9 | 80 | 55 | 290 | 0 | 0 | 0 | 7 | 85 | 133 | 52 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 25 | 33 | 27 | 0 | 42 | 0 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 70 | 70 | 50 | 20 | 2 | 0 | 0 | 100 | 345 | 0 | 206 | 8 | 90 | 32 | 20 | 0 | 51 | 0 | 0 | 18 | 15 | 5 | 25 | 20 | 142 | 149 | 0 | 19 | 2 | 84 | 29 | 47 | 44 | 163 | 236 | 61 | 83 | 0 | 213 | 18 | 0 | 9 | 300 | 24 | 0 | 0 | 286 | 0 | 0 | 179 | 0 | 130 | 20 | 100 | 0 | 103 | 0 | 109 | 84 | 51 | 6 | 307 | 54 | 0 | 34 | 104 | 100 | 0 | 104 |  | 928 | 0 | 320 | 0 | 32 | 120 | 0 | 0 | 0 | 0 | 0 | 50 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 14 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 202 | 0 | 40 | 0 | 197 | 0 | 396 | 0 | 0 | 73 | 0 | 112 | 0 | 6 | 109 | 310 |  | 7337 | 3131 | 10468 | 3683 | 928 | 2125 | 2801 | 460 | 42 | 253 | 142 | 34 | 0 | 95.1
12:00 | 0 | 0 | 0 | 115 | 200 | 92 | 65 | 356 | 341 |  | 0 | 420 | 0 | 7 | 80 | 55 | 287 | 0 | 0 | 0 | 7 | 85 | 133 | 53 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 25 | 50 | 0 | 42 | 0 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 50 | 70 | 72 | 50 | 20 | 3 | 0 | 0 | 100 | 310 | 0 | 210 | 16 | 90 | 32 | 20 | 0 | 51 | 0 | 0 | 46 | 15 | 5 | 25 | 20 | 152 | 147 | 0 | 19 | 2 | 85 | 29 | 53 | 43 | 163 | 236 | 62 | 84 | 0 | 213 | 18 | 0 | 9 | 295 | 21 | 5 | 0 | 286 | 0 | 0 | 190 | 0 | 132 | 14 | 90 | 42 | 122 | 0 | 115 | 85 | 64 | 4 | 307 | 54 | 0 | 114 | 104 | 100 | 0 | 104 |  | 929 | 0 | 370 | 0 | 58 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 50 | 0 | 43 | 0 | 14 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 190 | 0 | 55 | 0 | 196 | 0 | 398 | 0 | 0 | 94 | 0 | 110 | 0 | 6 | 109 | 310 |  | 7573 | 3315 | 10888 | 3692 | 929 | 2152 | 3120 | 460 | 42 | 315 | 152 | 26 | 0 | 95.11
13:00 | 0 | 0 | 0 | 115 | 200 | 92 | 65 | 360 | 341 |  | 0 | 420 | 0 | 7 | 80 | 55 | 254 | 0 | 0 | 0 | 7 | 93 | 133 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 33 | 50 | 0 | 74 | 0 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 51 | 70 | 67 | 50 | 20 | 8 | 0 | 0 | 100 | 310 | 0 | 210 | 26 | 82 | 32 | 20 | 0 | 51 | 0 | 0 | 52 | 15 | 2 | 25 | 20 | 156 | 147 | 0 | 19 | 2 | 87 | 29 | 53 | 43 | 163 | 235 | 64 | 84 | 0 | 203 | 18 | 0 | 9 | 300 | 21 | 0 | 0 | 286 | 0 | 0 | 179 | 0 | 132 | 20 | 100 | 87 | 120 | 0 | 95 | 85 | 68 | 2 | 307 | 54 | 0 | 114 | 105 | 100 | 0 | 104 |  | 928 | 0 | 385 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 50 | 0 | 43 | 0 | 14 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 191 | 0 | 75 | 0 | 195 | 0 | 390 | 0 | 0 | 94 | 0 | 105 | 0 | 6 | 109 | 310 |  | 7623 | 3379 | 11002 | 3663 | 928 | 2184 | 3156 | 460 | 74 | 351 | 156 | 30 | 0 | 95.11
14:00 | 0 | 0 | 0 | 115 | 200 | 95 | 65 | 353 | 323 |  | 0 | 360 | 0 | 7 | 86 | 55 | 290 | 0 | 0 | 0 | 7 | 93 | 133 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 25 | 50 | 0 | 40 | 0 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 68 | 70 | 77 | 50 | 20 | 2 | 0 | 0 | 100 | 320 | 0 | 209 | 26 | 91 | 32 | 20 | 0 | 43 | 0 | 0 | 52 | 18 | 2 | 25 | 20 | 168 | 144 | 0 | 19 | 2 | 85 | 30 | 53 | 43 | 110 | 237 | 61 | 86 | 0 | 214 | 18 | 0 | 9 | 270 | 0 | 0 | 0 | 286 | 0 | 0 | 179 | 0 | 137 | 19 | 100 | 142 | 123 | 0 | 95 | 85 | 68 | 0 | 307 | 54 | 0 | 114 | 104 | 100 | 0 | 104 |  | 923 | 0 | 365 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 21 | 64 | 0 | 0 | 0 | 40 | 0 | 48 | 0 | 50 | 0 | 43 | 0 | 14 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 187 | 0 | 78 | 0 | 196 | 0 | 390 | 27 | 0 | 94 | 0 | 103 | 0 | 5 | 109 | 310 |  | 7550 | 3517 | 11067 | 3667 | 923 | 2018 | 3356 | 460 | 40 | 409 | 168 | 26 | 0 | 95.11
15:00 | 0 | 0 | 0 | 115 | 200 | 95 | 64 | 366 | 338 |  | 0 | 400 | 0 | 7 | 96 | 55 | 290 | 0 | 0 | 0 | 7 | 93 | 133 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 33 | 50 | 0 | 40 | 0 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 68 | 70 | 77 | 50 | 20 | 5 | 0 | 0 | 100 | 330 | 0 | 208 | 26 | 90 | 32 | 20 | 0 | 43 | 0 | 0 | 52 | 18 | 2 | 17 | 20 | 170 | 144 | 0 | 17 | 1 | 82 | 30 | 53 | 43 | 163 | 195 | 59 | 86 | 0 | 212 | 17 | 0 | 9 | 310 | 0 | 0 | 0 | 291 | 0 | 25 | 174 | 26 | 146 | 13 | 100 | 195 | 122 | 0 | 106 | 85 | 68 | 0 | 307 | 54 | 0 | 114 | 107 | 100 | 30 | 104 |  | 928 | 0 | 345 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 25 | 80 | 0 | 0 | 0 | 50 | 0 | 47 | 0 | 50 | 0 | 43 | 0 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 194 | 0 | 79 | 0 | 203 | 0 | 403 | 53 | 0 | 94 | 0 | 104 | 0 | 3 | 109 | 317 |  | 7830 | 3595 | 11425 | 3660 | 928 | 2190 | 3535 | 467 | 40 | 418 | 170 | 17 | 0 | 95.11
16:00 | 0 | 0 | 0 | 115 | 200 | 95 | 64 | 350 | 343 |  | 0 | 400 | 0 | 7 | 96 | 55 | 251 | 0 | 0 | 0 | 7 | 93 | 133 | 76 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 33 | 50 | 0 | 40 | 0 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 68 | 70 | 77 | 50 | 20 | 5 | 0 | 0 | 100 | 310 | 0 | 210 | 26 | 80 | 32 | 20 | 0 | 51 | 0 | 0 | 52 | 18 | 5 | 25 | 20 | 160 | 148 | 0 | 17 | 1 | 83 | 29 | 52 | 43 | 163 | 196 | 60 | 86 | 0 | 213 | 17 | 0 | 9 | 290 | 16 | 5 | 0 | 296 | 0 | 25 | 173 | 0 | 137 | 4 | 100 | 200 | 122 | 0 | 115 | 85 | 68 | 0 | 307 | 52 | 0 | 114 | 113 | 100 | 100 | 104 |  | 928 | 0 | 335 | 0 | 83 | 120 | 0 | 0 | 0 | 0 | 0 | 59 | 19 | 80 | 0 | 0 | 0 | 50 | 0 | 47 | 0 | 50 | 0 | 43 | 0 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 184 | 0 | 77 | 0 | 193 | 0 | 353 | 53 | 0 | 94 | 0 | 96 | 0 | 2 | 80 | 380 |  | 7842 | 3515 | 11357 | 3655 | 928 | 2124 | 3495 | 530 | 40 | 418 | 160 | 7 | 0 | 95.12
17:00 | 0 | 0 | 0 | 115 | 200 | 95 | 60 | 342 | 348 |  | 0 | 400 | 0 | 7 | 96 | 55 | 271 | 0 | 0 | 0 | 7 | 93 | 98 | 100 | 0 | 0 | 0 | 17 | 55 | 35 | 22 | 25 | 20 | 33 | 25 | 16 | 0 | 40 | 0 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 68 | 20 | 78 | 50 | 20 | 9 | 0 | 0 | 100 | 310 | 0 | 210 | 26 | 83 | 32 | 20 | 0 | 51 | 0 | 0 | 52 | 18 | 5 | 25 | 20 | 156 | 150 | 0 | 17 | 0 | 83 | 29 | 28 | 20 | 110 | 140 | 40 | 40 | 0 | 213 | 17 | 0 | 9 | 280 | 16 | 8 | 0 | 286 | 0 | 0 | 174 | 0 | 146 | 1 | 100 | 100 | 122 | 0 | 115 | 85 | 68 | 0 | 255 | 53 | 0 | 70 | 85 | 100 | 40 | 104 |  | 928 | 0 | 330 | 0 | 99 | 120 | 0 | 0 | 0 | 4 | 0 | 60 | 21 | 80 | 0 | 0 | 0 | 50 | 5 | 47 | 0 | 25 | 0 | 25 | 0 | 17 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 180 | 0 | 61 | 0 | 189 | 0 | 347 | 35 | 0 | 35 | 0 | 84 | 0 | 1 | 70 | 380 |  | 7160 | 3364 | 10524 | 3519 | 928 | 1952 | 3005 | 530 | 40 | 392 | 156 | 2 | 0 | 95.12
18:00 | 0 | 0 | 0 | 115 | 200 | 95 | 40 | 342 | 284 |  | 0 | 300 | 0 | 7 | 97 | 55 | 290 | 0 | 0 | 0 | 7 | 93 | 98 | 100 | 0 | 0 | 0 | 17 | 55 | 35 | 22 | 25 | 20 | 33 | 33 | 16 | 0 | 38 | 35 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 82 | 20 | 77 | 50 | 20 | 13 | 0 | 0 | 100 | 325 | 0 | 208 | 26 | 91 | 32 | 20 | 0 | 51 | 0 | 29 | 52 | 18 | 2 | 25 | 20 | 134 | 149 | 0 | 17 | 0 | 83 | 30 | 28 | 20 | 110 | 231 | 50 | 40 | 0 | 213 | 17 | 0 | 10 | 270 | 24 | 8 | 17 | 293 | 0 | 25 | 185 | 26 | 146 | 0 | 100 | 100 | 122 | 0 | 85 | 85 | 51 | 0 | 254 | 54 | 0 | 70 | 85 | 100 | 0 | 104 |  | 920 | 0 | 335 | 0 | 83 | 125 | 0 | 0 | 0 | 10 | 16 | 60 | 30 | 80 | 0 | 0 | 0 | 50 | 34 | 55 | 0 | 25 | 12 | 25 | 21 | 17 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 155 | 0 | 44 | 2 | 160 | 0 | 376 | 35 | 20 | 35 | 0 | 66 | 0 | 0 | 70 | 400 |  | 7177 | 3432 | 10609 | 3584 | 920 | 1784 | 3048 | 550 | 73 | 516 | 134 | 0 | 0 | 95.12
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 115 | 200 | 95 | 66 | 353 | 351 |  | 0 | 420 | 0 | 7 | 96 | 55 | 232 | 0 | 0 | 0 | 7 | 93 | 133 | 65 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 16 | 33 | 33 | 46 | 0 | 82 | 35 | 120 | 0 | 16 | 0 | 0 | 0 | 0 |  | 0 | 0 | 85 | 60 | 78 | 50 | 20 | 10 | 0 | 0 | 100 | 305 | 0 | 200 | 26 | 81 | 32 | 20 | 0 | 51 | 0 | 42 | 52 | 18 | 2 | 25 | 20 | 170 | 153 | 0 | 17 | 0 | 86 | 29 | 53 | 40 | 163 | 256 | 52 | 87 | 0 | 213 | 17 | 0 | 10 | 280 | 24 | 0 | 80 | 300 | 68 | 98 | 200 | 61 | 146 | 0 | 100 | 153 | 123 | 0 | 115 | 85 | 51 | 0 | 307 | 54 | 11 | 114 | 113 | 100 | 0 | 104 |  | 918 | 0 | 330 | 0 | 99 | 180 | 0 | 0 | 0 | 0 | 40 | 52 | 32 | 110 | 0 | 0 | 0 | 50 | 34 | 94 | 0 | 50 | 27 | 46 | 32 | 17 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 179 | 0 | 78 | 81 | 186 | 0 | 374 | 90 | 50 | 69 | 0 | 93 | 0 | 0 | 100 | 470 |  | 8168 | 4052 | 12220 | 3535 | 918 | 2183 | 4000 | 620 | 117 | 677 | 170 | 0 | 0 | 95.12
19:30 | 0 | 0 | 0 | 115 | 200 | 95 | 67 | 339 | 353 |  | 0 | 420 | 0 | 7 | 97 | 55 | 281 | 0 | 0 | 0 | 7 | 93 | 133 | 27 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 16 | 33 | 33 | 50 | 0 | 82 | 35 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 0 | 85 | 60 | 84 | 50 | 20 | 14 | 0 | 0 | 100 | 305 | 0 | 195 | 26 | 81 | 32 | 25 | 0 | 51 | 0 | 42 | 52 | 18 | 2 | 25 | 20 | 174 | 153 | 0 | 17 | 0 | 86 | 29 | 53 | 45 | 130 | 257 | 52 | 87 | 0 | 193 | 17 | 0 | 10 | 285 | 24 | 5 | 0 | 300 | 0 | 0 | 200 | 0 | 147 | 0 | 100 | 180 | 123 | 0 | 115 | 85 | 51 | 0 | 307 | 54 | 17 | 114 | 113 | 100 | 0 | 104 |  | 918 | 0 | 330 | 0 | 99 | 180 | 0 | 0 | 0 | 0 | 40 | 57 | 34 | 110 | 0 | 0 | 0 | 50 | 34 | 98 | 0 | 50 | 42 | 52 | 32 | 19 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 176 | 0 | 78 | 100 | 188 | 0 | 387 | 90 | 0 | 69 | 0 | 110 | 0 | 0 | 109 | 470 |  | 7886 | 4093 | 11979 | 3555 | 918 | 2189 | 3710 | 620 | 117 | 696 | 174 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 115 | 200 | 95 | 69 | 338 | 354 |  | 0 | 380 | 0 | 7 | 97 | 55 | 290 | 0 | 0 | 0 | 7 | 93 | 114 | 26 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 16 | 28 | 33 | 25 | 0 | 82 | 35 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 0 | 68 | 30 | 84 | 50 | 20 | 22 | 0 | 0 | 100 | 305 | 0 | 191 | 26 | 80 | 32 | 25 | 0 | 51 | 0 | 42 | 52 | 18 | 2 | 25 | 21 | 178 | 153 | 0 | 17 | 0 | 86 | 29 | 53 | 48 | 130 | 263 | 52 | 87 | 0 | 192 | 17 | 0 | 10 | 255 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 146 | 0 | 100 | 150 | 125 | 0 | 115 | 85 | 51 | 0 | 306 | 54 | 17 | 114 | 113 | 100 | 0 | 104 |  | 918 | 0 | 325 | 0 | 99 | 180 | 0 | 0 | 0 | 0 | 40 | 59 | 31 | 110 | 0 | 0 | 0 | 50 | 34 | 94 | 0 | 50 | 47 | 52 | 32 | 17 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 176 | 0 | 78 | 100 | 185 | 0 | 394 | 90 | 0 | 94 | 0 | 111 | 0 | 0 | 109 | 514 |  | 7722 | 4160 | 11882 | 3559 | 918 | 2135 | 3650 | 664 | 117 | 661 | 178 | 0 | 0 | 95.13
21:00 | 0 | 0 | 0 | 115 | 200 | 92 | 69 | 340 | 353 |  | 0 | 450 | 0 | 7 | 97 | 55 | 284 | 0 | 0 | 0 | 7 | 93 | 82 | 26 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 28 | 0 | 33 | 25 | 0 | 83 | 35 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 0 | 51 | 30 | 84 | 50 | 20 | 36 | 0 | 0 | 100 | 290 | 0 | 217 | 26 | 80 | 32 | 25 | 0 | 51 | 0 | 42 | 52 | 18 | 2 | 25 | 21 | 176 | 153 | 0 | 18 | 0 | 87 | 29 | 53 | 48 | 163 | 258 | 64 | 87 | 0 | 201 | 17 | 0 | 10 | 290 | 16 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 145 | 0 | 100 | 68 | 125 | 0 | 115 | 85 | 51 | 0 | 306 | 54 | 17 | 90 | 113 | 100 | 0 | 104 |  | 918 | 0 | 320 | 0 | 99 | 200 | 0 | 0 | 0 | 0 | 40 | 58 | 35 | 96 | 0 | 0 | 0 | 50 | 34 | 94 | 0 | 50 | 36 | 52 | 32 | 20 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 180 | 0 | 78 | 100 | 190 | 0 | 406 | 90 | 0 | 94 | 0 | 111 | 0 | 0 | 109 | 590 |  | 7714 | 4253 | 11967 | 3563 | 918 | 2302 | 3529 | 740 | 118 | 621 | 176 | 0 | 0 | 95.13
22:00 | 0 | 0 | 0 | 115 | 200 | 94 | 70 | 339 | 354 |  | 0 | 450 | 0 | 7 | 97 | 40 | 284 | 0 | 0 | 0 | 7 | 93 | 82 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 25 | 0 | 84 | 35 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 0 | 51 | 30 | 84 | 50 | 20 | 38 | 0 | 0 | 100 | 290 | 0 | 210 | 26 | 82 | 32 | 25 | 0 | 51 | 0 | 42 | 52 | 18 | 2 | 25 | 21 | 176 | 156 | 0 | 18 | 0 | 87 | 29 | 53 | 48 | 163 | 260 | 64 | 84 | 0 | 213 | 17 | 0 | 10 | 285 | 16 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 146 | 0 | 100 | 68 | 125 | 0 | 115 | 85 | 51 | 0 | 306 | 54 | 17 | 90 | 113 | 100 | 0 | 104 |  | 918 | 0 | 315 | 0 | 99 | 200 | 0 | 0 | 0 | 0 | 40 | 59 | 36 | 96 | 0 | 0 | 0 | 50 | 34 | 94 | 0 | 50 | 36 | 52 | 32 | 20 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 182 | 0 | 78 | 100 | 188 | 0 | 396 | 90 | 0 | 94 | 0 | 111 | 0 | 0 | 109 | 600 |  | 7761 | 4250 | 12011 | 3622 | 918 | 2291 | 3514 | 750 | 119 | 621 | 176 | 0 | 0 | 95.13
23:00 | 0 | 0 | 0 | 115 | 200 | 94 | 69 | 340 | 352 |  | 0 | 420 | 0 | 7 | 96 | 40 | 265 | 0 | 0 | 0 | 7 | 94 | 82 | 27 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 25 | 0 | 84 | 35 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 0 | 51 | 30 | 84 | 50 | 20 | 40 | 0 | 0 | 85 | 315 | 0 | 216 | 8 | 91 | 32 | 25 | 0 | 51 | 0 | 42 | 43 | 18 | 2 | 25 | 21 | 176 | 156 | 0 | 18 | 0 | 86 | 29 | 53 | 49 | 163 | 260 | 63 | 84 | 0 | 211 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 143 | 0 | 100 | 34 | 125 | 0 | 105 | 67 | 51 | 0 | 307 | 54 | 17 | 90 | 113 | 100 | 0 | 104 |  | 918 | 0 | 305 | 0 | 99 | 200 | 0 | 0 | 0 | 0 | 40 | 60 | 24 | 80 | 0 | 0 | 0 | 50 | 34 | 86 | 0 | 50 | 36 | 52 | 31 | 20 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 173 | 0 | 78 | 100 | 188 | 0 | 399 | 90 | 0 | 94 | 0 | 113 | 0 | 0 | 109 | 580 |  | 7652 | 4180 | 11832 | 3619 | 918 | 2229 | 3429 | 730 | 119 | 612 | 176 | 0 | 0 | 95.13
24:00 | 0 | 0 | 0 | 115 | 200 | 94 | 68 | 368 | 350 |  | 0 | 420 | 0 | 7 | 77 | 55 | 271 | 0 | 0 | 0 | 7 | 93 | 114 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 33 | 0 | 85 | 35 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 0 | 51 | 30 | 84 | 50 | 20 | 40 | 0 | 0 | 80 | 320 | 0 | 215 | 8 | 91 | 32 | 25 | 0 | 51 | 0 | 42 | 43 | 18 | 2 | 25 | 21 | 170 | 156 | 0 | 14 | 0 | 86 | 30 | 53 | 49 | 163 | 260 | 64 | 85 | 0 | 205 | 18 | 0 | 10 | 310 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 145 | 0 | 100 | 34 | 127 | 0 | 105 | 67 | 51 | 0 | 307 | 54 | 17 | 105 | 113 | 100 | 0 | 104 |  | 918 | 0 | 305 | 0 | 99 | 200 | 0 | 0 | 0 | 0 | 40 | 60 | 34 | 80 | 0 | 0 | 0 | 50 | 34 | 89 | 0 | 50 | 36 | 52 | 24 | 20 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 164 | 0 | 78 | 100 | 200 | 0 | 407 | 90 | 0 | 94 | 0 | 112 | 0 | 0 | 109 | 580 |  | 7746 | 4196 | 11942 | 3641 | 918 | 2275 | 3448 | 730 | 120 | 640 | 170 | 0 | 0 | 95.13
KWH | 0 | 0 | 0 | 2772000 | 4776027 | 2215318 | 1560160 | 8497150 | 7790000 |  | 0 | 9095500 | 0 | 199680 | 2134008 | 1130481 | 6802567 | 0 | 0 | 0 | 194880 | 2183328 | 3150240 | 755211 | 0 | 0 | 0 | 1164960 | 1216417 | 1181311 | 390672 | 600000 | 507780 | 699600 | 788700 | 772020 | 0 | 1145907 | 236000 | 2800000 | 0 | 220678 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1176581 | 768360 | 1561920 | 1042560 | 460272 | 502080 | 0 | 0 | 2644752 | 7860000 | 0 | 4885000 | 669090 | 2064540 | 740952 | 688800 | 0 | 1162341 | 0 | 423968 | 979550 | 391212 | 98280 | 622300 | 507540 | 3904320 | 3548560 | 0 | 380196 | 15250 | 2033000 | 702600 | 1186800 | 1049976 | 3477600 | 5275000 | 1460352 | 1960320 | 0 | 5099250 | 404000 | 0 | 211500 | 7257000 | 478080 | 119096 | 76032 | 6889961 | 153742 | 239217 | 3705600 | 277134 | 3490990 | 108945 | 2395200 | 2001600 | 2400363 | 0 | 2056800 | 1761720 | 1114867 | 20280 | 7288909 | 1092797 | 102872 | 1934580 | 2585520 | 2409600 | 0 | 2612160 |  | 22206545 | 0 | 8121024 | 0 | 2094720 | 3786240 | 0 | 0 | 87390 | 6784 | 463500 | 1325000 | 614188 | 1312704 | 0 | 0 | 0 | 769808 | 355040 | 1388576 | 0 | 665900 | 310640 | 885600 | 331471 | 368880 | 225828 | 245016 | 0 | 0 | 3682200 | 0 | 0 | 0 | 0 | 4359336 | 0 | 1625782 | 955200 | 4506409 | 0 | 9312909 | 906240 | 66470 | 1902048 | 0 | 2442240 | 0 | 46198 | 2481600 | 11407900 |  | 177512482 | 89259386 | 266771868 | 86966263 | 22206545 | 50974072 | 74271250 | 15090100 | 1381907 | 11786738 | 3904320 | 190673 | 0
Fuel Cost | 0 | 0 | 0 | 4074840 | 5301389.97 | 2924219.76 | 2652272 | 8582121.5 | 8023700 |  | 0 | 9914095 | 0 | 1515571.2 | 14703315.12 | 9563869.26 | 7074669.68 | 0 | 0 | 0 | 1467446.4 | 19911951.36 | 30998361.6 | 6963045.42 | 0 | 0 | 0 | 8504208 | 9402903.41 | 11647726.46 | 293004 | 450000 | 0 | 0 | 0 | 7465433.4 | 0 | 309394.89 | 63720 | 5068000 | 0 | 2050098.62 | 0 | 0 | 0 | 0 |  | 0 | 0 | 11412835.7 | 7337838 | 13588704 | 8257075.2 | 579942.72 | 1491177.6 | 0 | 0 | 3887785.44 | 5816400 | 0 | 4494200 | 863126.1 | 2374221 | 837275.76 | 964320 | 0 | 1987603.11 | 0 | 4282076.8 | 9354702.5 | 496839.24 | 73710 | 1089025 | 380655 | 29282400 | 3761473.6 | 0 | 482848.92 | 243085 | 3334120 | 1124160 | 2112504 | 1637962.56 | 3964464 | 5486000 | 2876893.44 | 3744211.2 | 0 | 8821702.5 | 884760 | 0 | 431460 | 7329570 | 358560 | 90512.96 | 1293304.32 | 52088105.16 | 2610539.16 | 3999708.24 | 19269120 | 4633680.48 | 34351341.6 | 1273567.05 | 19520880 | 21717360 | 16922559.15 | 0 | 18758016 | 16648254 | 9710491.57 | 0 | 55104152.04 | 9518261.87 | 904244.88 | 19307108.4 | 22157906.4 | 16047936 | 0 | 0 |  | 127909699.2 | 0 | 8527075.2 | 0 | 16464499.2 | 52477286.4 | 0 | 0 | 916721.1 | 71096.32 | 4829670 | 1497250 | 951991.4 | 12811991.04 | 0 | 0 | 0 | 7574910.72 | 3607206.4 | 12288897.6 | 0 | 9002968 | 3010101.6 | 8581464 | 3215268.7 | 708249.6 | 350033.4 | 185477.112 | 0 | 0 | 19957524 | 0 | 0 | 0 | 0 | 5754323.52 | 0 | 2438673 | 16247952 | 5272498.53 | 0 | 9219779.91 | 9461145.6 | 1130654.7 | 18050435.52 | 0 | 18951782.4 | 0 | 510487.9 | 18339024 | 50080681 |  | 680298094.72 | 450396819.072 | 1130694913.792 | 99331735.092 | 127909699.2 | 61709412.64 | 610168444.08 | 70038205 | 373114.89 | 129854762.94 | 29282400 | 2027139.95 | 0
Yesterday Day Peak | 0 | 0 | 0 | 115 | 200 | 92 | 65 | 356 | 341 |  | 0 | 420 | 0 | 7 | 80 | 55 | 287 | 0 | 0 | 0 | 7 | 85 | 133 | 53 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 25 | 50 | 0 | 42 | 0 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 50 | 70 | 72 | 50 | 20 | 3 | 0 | 0 | 100 | 310 | 0 | 210 | 16 | 90 | 32 | 20 | 0 | 51 | 0 | 0 | 46 | 15 | 5 | 25 | 20 | 152 | 147 | 0 | 19 | 2 | 85 | 29 | 53 | 43 | 163 | 236 | 62 | 84 | 0 | 213 | 18 | 0 | 9 | 295 | 21 | 5 | 0 | 286 | 0 | 0 | 190 | 0 | 132 | 14 | 90 | 42 | 122 | 0 | 115 | 85 | 64 | 4 | 307 | 54 | 0 | 114 | 104 | 100 | 0 | 104 |  | 929 | 0 | 370 | 0 | 58 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 50 | 0 | 43 | 0 | 14 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 190 | 0 | 55 | 0 | 196 | 0 | 398 | 0 | 0 | 94 | 0 | 110 | 0 | 6 | 109 | 310 |  | 10888 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 115 | 200 | 95 | 66 | 353 | 351 | 0 | 0 | 420 | 0 | 7 | 96 | 55 | 232 | 0 | 0 | 0 | 7 | 93 | 133 | 65 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 16 | 33 | 33 | 46 | 0 | 82 | 35 | 120 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 60 | 78 | 50 | 20 | 10 | 0 | 0 | 100 | 305 | 0 | 200 | 26 | 81 | 32 | 20 | 0 | 51 | 0 | 42 | 52 | 18 | 2 | 25 | 20 | 170 | 153 | 0 | 17 | 0 | 86 | 29 | 53 | 40 | 163 | 256 | 52 | 87 | 0 | 213 | 17 | 0 | 10 | 280 | 24 | 0 | 80 | 300 | 68 | 98 | 200 | 61 | 146 | 0 | 100 | 153 | 123 | 0 | 115 | 85 | 51 | 0 | 307 | 54 | 11 | 114 | 113 | 100 | 0 | 104 |  | 918 | 0 | 330 | 0 | 99 | 180 | 0 | 0 | 0 | 0 | 40 | 52 | 32 | 110 | 0 | 0 | 0 | 50 | 34 | 94 | 0 | 50 | 27 | 46 | 32 | 17 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 179 | 0 | 78 | 81 | 186 | 0 | 374 | 90 | 50 | 69 | 0 | 93 | 0 | 0 | 100 | 470 |  | 12220 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 115 | 200 | 100 | 71 | 412 | 360 | 0 | 0 | 450 | 0 | 7 | 100 | 55 | 335 | 0 | 0 | 0 | 7 | 93 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 80 | 70 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 100 | 85 | 50 | 20 | 30 | 0 | 0 | 130 | 360 | 0 | 225 | 8 | 90 | 32 | 25 | 0 | 51 | 0 | 42 | 43 | 18 | 11 | 25 | 21 | 173 | 160 | 0 | 19 | 0 | 90 | 30 | 51 | 44 | 163 | 250 | 65 | 86 | 0 | 213 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 85 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 104 |  | 932 | 16 | 380 | 0 | 115 | 225 | 0 | 0 | 30 | 60 | 40 | 80 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 0 | 50 | 43 | 52 | 32 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 200 | 0 | 90 | 100 | 220 | 0 | 414 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 580
Forecast for Day | 0 | 0 | 0 | 115 | 200 | 100 | 71 | 412 | 360 | 0 | 0 | 450 | 0 | 7 | 100 | 55 | 335 | 0 | 0 | 0 | 7 | 93 | 149 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 40 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 100 | 85 | 50 | 20 | 9 | 0 | 0 | 130 | 360 | 0 | 225 | 8 | 90 | 32 | 25 | 0 | 51 | 0 | 0 | 43 | 18 | 11 | 25 | 21 | 162 | 150 | 0 | 19 | 1.6 | 90 | 30 | 51 | 44 | 163 | 250 | 65 | 86 | 0 | 213 | 18 | 0 | 10 | 341 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 100 | 200 | 150 | 0 | 115 | 85 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 104 |  | 932 | 0 | 380 | 0 | 115 | 225 | 0 | 0 | 0 | 0 | 40 | 60 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 50 | 43 | 52 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 200 |  | 90 | 50 | 220 | 0 | 414 | 105 | 100 | 113 | 100 | 100 | 0 | 8 | 113 | 580
Generation at 08:00(Today) | 0 | 0 | 0 | 115 | 200 | 95 | 67 | 350 | 353 | 0 | 0 | 320 | 0 |  | 50 | 35 | 0 | 0 | 0 | 0 | 7 | 85 | 0 | 10 | 0 | 0 | 0 | 54 | 48 | 17 | 22 | 25 | 28 | 33 | 16 | 0 | 0 | 40 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 19 | 20 | 6 | 0 | 0 | 80 | 260 | 0 | 180 | 8 | 81 | 32 | 25 | 0 | 51 | 0 | 0 | 0 | 18 | 2 | 25 | 20 | 84 | 158 | 0 | 11 | 1 | 87 | 3 | 53 | 49 | 110 | 257 | 64 | 83 | 0 | 205 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 299 | 0 | 0 | 200 | 0 | 115 | 0 | 100 | 0 | 93 | 0 | 25 | 17 | 0 | 1 | 275 | 0 | 0 | 0 | 113 | 100 | 0 | 17 | 0 | 923 | 0 | 370 | 0 | 80 | 120 | 0 | 0 | 0 | 0 | 0 | 57 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 147 | 0 | 77 | 0 | 161 | 0 | 283 | 0 | 0 | 35 | 0 | 113 | 0 | 1 | 109 | 440 | 0
199
| Minimum Generation |  | 9325 | 7:00
| Highest Generation |  | 12220 | 19:00
| Day Peak Generation |  | 10888 | 12:00
| Evening Peak Generation |  | 12220 | 19:00
| HVDC Max Flow |  | 929 | 8:00
| HVDC EvPeak Flow |  | 918 | 19:00
| Load factor L.F |  | 90.96%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-09-21
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-09-20 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10888 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 8954 | MW
Evening Peak Generation : |  | 12220 | MW Hour : | 19:00 | Available Max Generation : |  | 14346 | MW
E.P. Demand (at gen end) : |  | 12220 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 12200 | MW
Maximum Generation : |  | 12220 | MW Hour : | 19:00 | Reserve(Generation end) |  | 2146 | MW
Total Gen. (MKWH) : |  | 266.7719 | System Load Factor : | 90.96% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -94 | MW at | 19:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-09-21
Actual : | 95.15 | Ft.(MSL) , | Rule curve : | 103.6 | Ft.( MSL )
Gas Consumed : | Total = | 1075.4 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 161041147.732
: |  | Coal : | 70038205 | Oil : | 740023207.02 | Total : | 971102559.752
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4341.4475 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1479.1854 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1325.8094 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1198.1611 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1082.6613 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 873.6766 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 484.8457 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 224.8511 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 673.8403 |  |  | 0 | 0%
Total | 0 |  | 11684.4784 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 9) Meghnaghat summit
|  |  |  | 2) Bibiyana #3 | 10) Ashuganj (S)-360 MW
|  |  |  | 3) Ghorasal Unit-1,2,3,4 | 11) Sikalbaha-225 MW.
|  |  |  | 4) Ashuganj unit-3,4 | 12) Sikalbaha-150 MW.
5) Kaptai-2,3,4,5
6) Raozan #1,2
7) Sirajganj #1
8) Baghabari-71 MW & 100 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Mirpur- Uttara sector-18 132 kV Ckt was under shut down from 10:26 to 14:33 for C/M.
b) Ghorasal-Joydebpur 132 kV Ckt-2 was under shut down from 08:45 to 11:42 for Safety Outage.
c) Chapai 132/33 kV T2 transformer was under shut down from 10:05 to 11:44 for R/H.
d) Barisal north 132/33 kV T4 transformer shut down at 10:32 for R/H maintenance at R-phase clamp.
e) Noapara-Jessore 132 kV Ckt-1 tripped from 07:50 to 08:17 showing Dist. AB-phase, Z1 and Dist. 3-Phase
earth fault respectively.
f) Ishwardi-Bheramara 132 kV Ckt-1 tripped from 08:55 to 11:19 showing Dist. O/C ,Z2, B & C-phase respectively.
g) Ishwardi-Bheramara 132 kV Ckt-2 tripped from 08:59 to 10:28 showing Dist. B-phase and Dist. O/C ,
Z2, & C-phase respectively.
h) Bheramara(HVDC)-Bheramara 230kV Ckt-1 tripped from 08:59 to 09:28 showing DT and CT received.
i) Noapara-Jessore 132 kV Ckt-1 shut down at 10:59 to cheek CT (R-phase) problem.
j) Bashundhara 132/33 kV T1 Transformer shifted to Tongi at 15:11.
k) Bheramara(HVDC)-Rajshahi(New) 230 kV Ckt-1 was switched on at 20:57.
l) Rajshahi 230/132 kV T2 transformer was charged 230kV side at 21:03 and 132 kV side at 21:24.
m) Bibiyana 400kV-Bibiyana-3 400kV ST line Switched on at 14:07 and GT line switched on at 14:14.
n) Netrokona 132/33 kV T3 transformer was under shut down from 15:34 to 16:36 due to 33 kV bus |  |  |  |  | About 35 MW power interruption occurred Netrokona area from 15:34
work (PBS-work). |  |  |  |  | to 16:36
o) Shahjibazar 132/33 kV T2 , T4 transformer was tripped from 18:11 to 18:16 ,T4 showing O/C. |  |  |  |  | About 104 MW power interruption occurred Shahjibazar area from 18:11
to18.16
p) Shahjibazar 132/33 kV T2 transformer was switched on at 21:16.
q) Ramganj 132/33 kV T2 transformer along with 33 kV bus shut down at 21:30 due to R/H. |  |  |  |  | About 30 MW power interruption occurred Ramganj area from 21:30
to 23:18.
r) Rajshahi 230/132 kV T2 transformer was under shut down from 22:01 to 00:15(21/09/2020) due to
CT, R-phase, R/H.
s) Siddirganj 335 MW shut down at 07:09(21/9/2020) due to Maintenance for 10 Hours.
t) Mymensing T1 transformer shut down at 06:25(21/9/2020) due to C/M. |  |  |  |  | About 80 MW power interruption occurred Mymensing area since 06:25
(21/09/2020)
u) Mymensing- Kisargonj Ckt-1 was shut down at 06:45(21/9/2020) sue to C/M.
v) Bogura-Sirajganj 230 kV Ckt-1 was shut down at 07:20 due to C/M.
Rangpur T2 transformer was shut down at 06:32 due to C/M. |  |  |  |  | About 60 MW power interruption occurred Rangpur area since 06:32
(21/09/2020)

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-09-20 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 115 | 2772000 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 4776027 | Gas shortage
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 66 | 1560160 | Engine problem
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 95 | 2215318 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 353 | 8497150 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 351 | 7790000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9095500 | Frequency control
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 7 | 199680 | Fuel Shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shorage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 96 | 2134008
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1130481
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 65 | 755211 | Fuel Shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 390672 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 7 | 194880 | Fuel Shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 232 | 6802567 | FGMO
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 2183328 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel Shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1164960
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 133 | 3150240 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1216417
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1181311
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Machine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 41 | 1107780 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 699600
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 788700
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 46 | 772020
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 6889961
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 68 | 153742 | Low demand.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 98 | 239217
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 61 | 277134 | Fuel Shortage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 146 | 3490990
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 85 | 1761720 | Engine problem
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2612160
| Dhaka area Total |  |  |  | 5895 | 3467 | 76002934
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2800000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 16 | 220678 | Low demand.
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 108945
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1042560
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 117 | 1381907 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Gas shortage
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 51 | 1114867 | Transformer O/L
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 1176581
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 60 | 768360 | High voltage
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2395200
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 460272
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 10 | 502080
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 78 | 1561920 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 20280
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 307 | 7288909
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1092797
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 11 | 102872 | Low demand.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2409600
| Chattogram area Total |  |  |  | 2266 | 1179 | 24447828
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 100 | 2644752 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 200 | 4885000 | Gas shortage
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 305 | 7860000 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Gas shortage
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 32 | 740952 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 20 | 688800 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 26 | 669090 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1162341
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 123 | 2400363 | Engine problem
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 42 | 423968 | Engine problem
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 81 | 2064540
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 153 | 2001600 | High voltage
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 391212 | Engine problem
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 2 | 98280 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 170 | 3904320
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 622300 | Engine problem
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 979550
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 507540 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 80 | 76032 | Low demand.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1934580
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 2585520
| Cumilla Area Total |  |  |  | 2980 | 1727 | 36640740
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 153 | 3548560 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 380196 | Engine problem
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 0 | 0
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 15250
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 3705600
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2056800 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 485 | 9706406
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 86 | 2033000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 29 | 702600 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3477600
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 256 | 5275000
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1186800
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 40 | 1049976
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 119096 | Engine problem
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 52 | 1460352 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 87 | 1960320
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 213 | 5099250
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 404000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 478080
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7257000 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 211500
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1310 | 30714574
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 918 | 22206545
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 2094720 | Engine problem
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 87390 | Reserve.
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 180 | 3786240 | Low demand.
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 6784 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 330 | 8121024 | Gas Shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 463500
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 81 | 955200 | Low demand.
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 90 | 906240 | Engine problem
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1738 | 38627643
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1312704
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 32 | 614188
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 52 | 1325000 | GT-2 Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 78 | 1625782 | Engine problem
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 470 | 11407900
| Barisal Area Total |  |  |  | 1054 | 742 | 16285574
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 769808
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 34 | 355040 | Engine problem
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 665900
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 27 | 310640
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas Shortage
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 179 | 4359336 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 186 | 4506409 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 374 | 9312909 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 331471
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 17 | 368880 | Engine problem
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 10 | 225828
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 245016
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 46 | 885600
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 1388576
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 50 | 66470 | Low demand.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 69 | 1902048 | Low demand.
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 100 | 2481600
| Rajshahi Area Total |  |  |  | 2183 | 1329 | 28175531
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3682200 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 93 | 2442240 | Engine problem
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 46198
| Rangpur Area Total |  |  |  | 605 | 243 | 6170638
| Total |  |  |  | 19892 | 12220 | 266771868
| Eastern Grid Total |  |  |  | 13766 | 8168 | 177512482
| Western Grid Total |  |  |  | 6126 | 4052 | 89259386
| National Grid Total |  |  |  | 19892 | 12220 | 266771868
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-09-20
| (a) ENTIRE EASTERN GRID : |  | 7761 | MW | (b) ENTIRE WESTERN GRID : |  | 3933 | MW
| i) Dhaka area |  | 4274 | MW | i) Khulna area |  | 1534 | MW
| ii) Chittagong area |  | 1170 | MW | ii) Rajshahi area |  | 1305 | MW
| iii) Comilla area |  | 840 | MW | iii) Barisal area |  | 321 | MW
| iv) Mymensingh area |  | 971 | MW | iv) Rangpur area |  | 773 | MW
| v) Sylhet area |  | 506 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11694 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 128 | 11:00 | Sherpur | 112 | 19:00 | Jhenida | 116 | 19:00
| Munsiganj | 124 | 18:30 | Srimongal | 54 | 18:30 | Bottail | 132 | 19:00
| Sonargaon | 84 | 24:00 | Shahjibazar | 125 | 1:00 | G.K Project | 59 | 20:00
| Shyampur | 188 | 6:00 | Fenchuganj | 42 | 18:30 | Faridpur | 201 | 0.875
| Bhulta | 195 | 24:00 | Kulawara | 45 | 18:30 | Madaripur | 106 | 0.875
| Madanganj | 50 | 1:00 | Sylhet | 145 | 19:30 | Sariatpur | 66 | 21:00
| Shitalakhya | 122 | 12:00 | Chatak | 33 | 21:00 | Gopalganj | 91 | 19:00
| Rahim steel | 6 | 9:00 | Sunamganj | 46 | 20:00 | Bagerhat | 104 | 21:00
| Matuail | 85 | 16:00 | Biani Bazar | 74 | 20:00 | Mongla | 34 | 13:00
| Ghorasal | 85 | 18:30 | Comilla (S) | 178 | 20:00 | Satkhira | 109 | 0.8125
| Narsingdi | 165 | 1:00 | Comilla(N) | 97 | 22:00 | Gallamari | 45 | 23:00
| Haripur (SBU) | 103 | 12:00 | Chandpur | 111 | 22:00 | Magura | 54 | 0.83333
| Ullon | 62 | 19:00 | Feni | 118 | 22:00 | Norail | 41 | 18:30
| Hasnabad | 220 | 19:00 | Chowmuhani | 190 | 23:00 | Chuadanga | 90 | 19:00
| Magbazar | 119 | 15:00 | Ashuganj | 57 | 13:00 | Barisal(N) | 49 | 0.8125
| Maniknagar | 104 | 15:00 | Daudkandi | 123 | 0:00 | Barisal (S) | 104 | 0.79167
| Bangabhaban | 40 | 13:00 | B.Baria | 128 | 14:00 | Patuakhali | 126 | 0.041667
| Narinda | 94 | 13:00 | Ramganj | 106 | 0:00 | Bhandaria | 54 | 0.041667
| Dhanmondi | 191 | 12:00 | Chaddagram | 30 | 14:00 | Borhan Uddin | 44 | 20:00
| Lalbag | 90 | 13:00 | PHP | 10 | 16:00 | Ishurdi | 64 | 18:30
| Madartek | 76 | 1:00 | Madunaghat | 88 | 8:00 | Ruppur Paromanobik | 2 | 1:00
| Dhaka University | 0 | #NUM! | Hathazari | 97 | 0.875 | Natore | 136 | 21:00
| Fatullah | 39 | 0.41667 | Khulshi | 185 | 0.79167 | Bogra | 180 | 19:00
| Mirpur | 109 | 12:00 | Halishahar | 141 | 0.45833 | Noagaon | 127 | 19:30
| Kalyanpur | 105 | 21:00 | Baraulia | 149 | 0 | Rajshahi | 154 | 21:00
| Gulshan | 144 | 13:00 | Sikalbaha | 25 | 0.77083 | Rajshahi New | 12 | 19:00
| Uttara | 89 | 19:30 | Dohazari | 92 | 0.041667 | C.Nawabganj | 74 | 20:00
| Uttara New | 33 | 19:30 | Cox'sbazar | 104 | 0.83333 | Amnura | 50 | 21:00
| Kamrangirchar | 92 | 16:00 | Chandraghona | 30 | 0.77083 | Pabna | 124 | 21:00
| Savar | 142 | 19:00 | Kaptai | 4.6 | 0.77083 | Shahjadpur | 110 | 20:00
| Bhasantec | 158 | 15:00 | A. Khaer Stl. | 0 | 0.041667 | Serajganj | 113 | 20:00
| Agargaon | 78 | 14:00 | Bakulia | 108 | 0.5 | Niyamatpur | 61 | 21:00
| Satmosjid | 109 | 18:30 | Julda | 20 | 0.041667 | Joypurhat | 60 | 20:00
| Tongi | 103 | 0.41667 | TK chemical | 28.6 | 0.91667 | Sherpur(Bogura) | 52 | 21:00
| Kabirpur | 239 | 15:00 | Modern Steel | 15 | 0.041667 | Mohastangor | 54 | 19:00
| Basundhara | 149 | 14:00 | Shahmirpur | 24 | 0.041667 | Rangpur | 160 | 21:00
| Manikganj | 72 | 0.041667 | Khagrachhari | 26 | 0.70833 | Lalmonirhat | 59 | 18:30
| Joydevpur | 156 | 15:00 | Matarbari | 31 | 0.875 | Saidpur | 99 | 18:30
| New Tongi | 123 | 14:00 | Baroiar Hat | 56 | 0.79167 | Purbasadipur | 102 | 18:30
| Korda | 286 | 19:00 | Rangamati | 12 | 0.54167 | Thakurgaon | 88 | 19:30
| Dhamrai | 96 | 21:00 | Abul Khair 230 | 137 | 0.58333 | Palashbari | 124 | 20:00
| Rajendrapur | 102 | 18:30 | BSRM | 108 | 0.25 | Barapukuria | 55 | 20:00
| Valuka | 132 | 19:30 | GPH Ispat | 75 | 0.25 | Panchagar | 54 | 19:00
| Tangail | 210 | 20:00 | Goalpara | 24 | 0.041667 | Joldhaka | 34 | 20:00
| Mymensing | 156 | 18:00 | Central s/s | 93 | 19:00 | Kurigram | 54 | 1:00
| Kishorganj | 150 | 18:30 | Noapara | 55 | 1:00
| Netrokona | 110 | 19:30 | Jessore | 126 | 19:00
| Jamalpur | 151 | 21:00 | Benapol | 42 | 19:00
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-09-20 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 394 | 5:00 | 386 | 11:00 | Kaliakoir | 375 | 0.25 | 362 | 0.5
| Bheramara | 395 | 3:00 | 386 | 21:00 | Bhulta | 387 | 0.125 | 375 | 0.375
| Ashuganj(N) | 392 | 5:00 | 380 | 9:00 | Gopalganj | 418 | 0.25 | 394 | 0.91667
| Payra | 416 | 1:00 | 404 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 232 | 1:00 | 230 | 7:00 | Comilla (N) | 234 | 20:00 | 227 | 6:00
| Ishurdi | 234 | 8:00 | 223 | 20:00 | Hathazari | 232 | 19:00 | 220 | 9:00
| Ashuganj | 238 | 5:00 | 229 | 9:00 | Megnaghat | 228 | 19:00 | 221 | 11:00
| Serajganj | 231 | 4:00 | 226 | 18:30 | Fenchuganj | 236 | 5:00 | 232 | 18:00
| Baghabari | 240 | 17:00 | 235 | 19:30 | Siddhirganj | 229 | 5:00 | 221 | 11:00
| Barapukuria | 236 | 6:00 | 225 | 20:00 | Maniknagar | 226 | 1:00 | 219 | 9:00
| Bogra | 225 | 6:00 | 212 | 20:00 | Agargaon | 224 | 5:00 | 215 | 9:00
| Rajshahi | 226 | 18:00 | 217 | 18:30 | Barisal | 250 | 4:00 | 234 | 10:00
| Khulna South | 237 | 8:00 | 225 | 4:00 | AKSML | 227 | 19:00 | 217 | 8:00
| Rampura | 224 | 1:00 | 220 | 9:00 | BSRM | 228 | 21:00 | 218 | 8:00
| Haripur | 225 | 3:00 | 219 | 9:00 | Bibiyana | 235 | 21:00 | 231 | 9:00
| Hasnabad | 225 | 1:00 | 218 | 11:00 | Bhulta | 229 | 19:00 | 221 | 17:00
| Shyampur | 223 | 1:00 | 215 | 9:00 | Ashuganj (S) | 234 | 1:00 | 226 | 9:00
| Aminbazar | 225 | 3:00 | 217 | 9:00 | Kaliakoir | 230 | 3:00 | 221 | 8:00
| Tongi | 226 | 20:00 | 215 | 7:00 | GPH | 224 | 3:00 | 218 | 6:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 129 | 1:00 | 125 | 9:00 | Hathazari | 138 | 0.79167 | 132 | 0.20833
| Munsiganj | 132 | 22:00 | 126 | 9:00 | Khulshi | 137 | 0.54167 | 130 | 0.33333
| Sonargaon | 130 | 1:00 | 126 | 9:00 | Halishahar | 140 | 0.625 | 131 | 0.375
| Shyampur | 131 | 1:00 | 126 | 9:00 | Baraulia | 137 | 0.70833 | 129 | 0.375
| Bhulta | 125 | 19:30 | 118 | 12:00 | Sikalbaha | 140 | 4:00 | 133 | 0.29167
| Madanganj | 131 | 9:00 | 128 | 13:00 | Dohazari | 138 | 17:00 | 127 | 0.375
| Shitalakhya | 140 | 18:30 | 132 | 9:00 | Cox'sbazar | 132 | 0.70833 | 119 | 0.25
| Rahim steal | 130 | 4:00 | 125 | 12:00 | Chandraghona | 139 | 0.041667 | 132 | 0.33333
| Matuail | 129 | 1:00 | 125 | 9:00 | Kaptai | 136 | 19:30 | 135 | 0.041667
| Ghorasal | 138 | 1:00 | 135 | 8:00 | A. Khaer Stl. | 135 | 0.041667 | 130 | 7:00
| Narsinghdi | 128 | 19:00 | 119 | 10:00 | Bakulia | 139 | 0.58333 | 131 | 0.375
| Haripur (SBU) | 130 | 5:00 | 125 | 11:00 | Julda | 140 | 0.79167 | 133 | 0.33333
| Ullon | 132 | 4:00 | 124 | 10:00 | TK Chemical | 139 | 0.70833 | 135 | 6:00
| Hasnabad | 136 | 1:00 | 128 | 7:00 | Modern Steel | 139 | 0.041667 | 131 | 0.29167
| Magbazar | 132 | 4:00 | 123 | 15:00 | Shahmirpur | 139 | 0.041667 | 131 | 0.29167
| Maniknagar | 132 | 1:00 | 125 | 11:00 | Khagrachhari | 138 | 0.70833 | 130 | 0.29167
| Bangabhaban | 132 | 1:00 | 125 | 11:00 | Matarbari | 135 | 0.70833 | 125 | 0.29167
| Narinda | 132 | 1:00 | 125 | 11:00 | Baroiar Hat | 135 | 0.5 | 127 | 0.33333
| Dhanmondi | 132 | 4:00 | 124 | 10:00 | Rangamati | 138 | 0.041667 | 131 | 7:00
| Lalbag | 136 | 18:30 | 127 | 9:00 | Goalpara S/S | 139 | 8:00 | 130 | 12:00
| Madartek | 131 | 23:00 | 123 | 11:00 | Khulna Central S/S | 139 | 0.33333 | 130 | 12:00
| Dhaka University |  |  |  |  | Noapara | 138 | 8:00 | 126 | 12:00
| Fatuiiah | 132 | 0.25 | 127 | 9:00 | Jessore | 136 | 8:00 | 118 | 12:00
| Mirpur | 133 | 6:00 | 125 | 12:00 | Benapol | 134 | 8:00 | 119 | 18:30
| Kalyanpur | 134 | 6:00 | 128 | 12:00 | Jhenida | 131 | 0.33333 | 111 | 20:00
| Gulshan | 130 | 6:00 | 123 | 12:00 | Bottail | 135 | 8:00 | 123 | 20:00
| Uttara | 133 | 6:00 | 126 | 12:00 | G.K Project | 140 | 0.33333 | 134 | 19:30
| Uttara New | 136 | 6:00 | 129 | 12:00 | Faridpur | 132 | 6:00 | 123 | 22:00
| Kamrangirchar | 130 | 6:00 | 124 | 12:00 | Madaripur | 136 | 0.375 | 130 | 1:00
| Savar | 134 | 6:00 | 126 | 12:00 | Shariyatpur S/S | 136 | 0.25 | 128 | 1:00
| Bhasantec | 135 | 6:00 | 127 | 12:00 | Gopalganj | 138 | 7:00 | 125 | 21:00
| Agargaon | 136 | 6:00 | 129 | 12:00 | Bagerhat | 140 | 7:00 | 124 | 1:00
| Satmosjid | 136 | 6:00 | 127 | 12:00 | Mongla | 137 | 0.33333 | 121 | 1:00
| Tongi | 136 | 0.041667 | 130 | 8:00 | Satkhira | 138 | 0.29167 | 126 | 1:00
| Kabirpur | 131 | 6:00 | 124 | 14:00 | Gallamari | 138 | 7:00 | 130 | 1:00
| Basundhara | 131 | 23:00 | 122 | 14:00 | Magura | 134 | 8:00 | 110 | 20:00
| Manikganj | 139 | 3:00 | 130 | 8:00 | Norail | 131 | 0.33333 | 107 | 20:00
| Joydevpur | 141 | 1:00 | 132 | 9:00 | Chuadanga | 129 | 9:00 | 100 | 20:00
| New Tongi | 137 | 0.083333 | 128 | 9:00 | Barisal(N) | 142 | 5:00 | 132 | 10:00
| Kodda | 137 | 4:00 | 124 | 0.375 | Barisal (S) | 140 | 0.20833 | 130 | 11:00
| Dhamrai | 131 | 6:00 | 124 | 18:30 | Patuakhali(S) | 135 | 0.16667 | 125 | 1:00
| Rajendrapur | 137 | 4:00 | 123 | 8:00 | Bhandaria | 138 | 8:00 | 116 | 1:00
| Valuka | 117 | 7:00 | 108 | 19:00 | Ishurdi | 137 | 5:00 | 131 | 20:00
| Tangail | 129 | 6:00 | 121 | 19:30 | Ruppur Paromanobik | 136 | 18:00 | 131 | 20:00
| Mymensing | 121 | 6:00 | 113 | 21:00 | Natore | 136 | 16:00 | 130 | 20:00
| Kishorganj | 125 | 19:30 | 118 | 21:00 | Bogra | 136 | 6:00 | 127 | 19:30
| Netrokona | 120 | 16:00 | 109 | 21:00 | Noagaon | 131 | 6:00 | 119 | 20:00
| Jamalpur | 131 | 10:00 | 112 | 3:00 | Rajshahi | 137 | 18:00 | 130 | 20:0
| Sherpur | 130 | 9:00 | 110 | 1:00 | Rajshahi New | 138 | 16:00 | 130 | 18:30
| Srimongal | 135 | 6:00 | 133 | 0.375 | C.Nawabganj | 135 | 17:00 | 129 | 20:00
| Shahjibazar | 135 | 20:00 | 131 | 0.58333 | Amnura | 136 | 18:00 | 129 | 9:00
| Fenchuganj | 134 | 5:00 | 132 | 0.75 | Pabna | 133 | 6:00 | 127 | 20:0
| Khulawara | 133 | 1:00 | 131 | 0.79167 | Shahjadpur | 137 | 3:00 | 133 | 9:00
| Sylhet | 133 | 5:00 | 130 | 0.58333 | Serajganj | 133 | 5:00 | 127 | 20:00
| Chatak | 131 | 6:00 | 127 | 19:30 | Niyamatpur | 130 | 7:00 | 115 | 20:00
| Sunamganj | 130 | 8:00 | 125 | 0.8125 | Joypurhat | 131 | 6:00 | 117 | 20:00
| Biani Bazar | 130 | 5:00 | 126 | 0.041667 | Sherpur(Bogura) | 134 | 6:00 | 126 | 20:00
| Comilla(s) | 126 | 18:00 | 119 | 13:00 | Mohastangor | 134 | 6:00 | 123 | 20:00
| Comilla(n) | 138 | 18:30 | 133 | 11:00 | Rangpur | 130 | 5:00 | 114 | 20:00
| Chandpur | 140 | 15:00 | 130 | 8:00 | Lalmonirhat | 128 | 6:00 | 112 | 18:30
| Feni | 137 | 12:00 | 129 | 9:00 | Saidpur | 130 | 6:00 | 113 | 21:00
| Chowmuhani | 134 | 19:00 | 128 | 9:00 | Purbasadipur | 127 | 6:00 | 110 | 20:00
| Ashuganj | 135 | 6:00 | 131 | 10:00 | Thakurgaon | 128 | 6:00 | 109 | 20:00
| Daudkandi | 137 | 19:00 | 126 | 11:00 | Palashbari | 130 | 10:00 | 122 | 2:00
| B.Baria | 132 | 19:00 | 128 | 8:00 | Barapukuria | 136 | 6:00 | 125 | 20:00
| Ramganj | 132 | 12:00 | 124 | 0:00 | Panchagar | 126 | 6:00 | 104 | 21:00
| Chaddagram | 137 | 19:30 | 128 | 6:00 | Joldhaka | 128 | 6:00 | 111 | 20:00
| PHP | 138 | 19:00 | 127 | 8:00 | Kurigram | 127 | 6:00 | 110
| Madanhat | 141 | 19:00 | 133 | 9:00

## L-Curve
Date | 2020-09-20
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 96 | 7746 | 4196 | 11942 |  |  |  | QF-LDC-11
0:30 | 89 | 7649.5 | 4159.5 | 11809 | Date: | 2020-09-20
1:00 | 82 | 7553 | 4123 | 11676
1:30 | 94.5 | 7477.5 | 4117 | 11594.5
2:00 | 107 | 7402 | 4111 | 11513
2:30 | 112 | 7320.5 | 4091.5 | 11412 | [5 empty] | Gen. at Eve. Peak | 12220 | 9500 MW (19:30 )
3:00 | 117 | 7239 | 4072 | 11311 | [6 empty] | 19:00
3:30 | 128.5 | 7227.5 | 3938.5 | 11166 | [5 empty] | Gen. at Day Peak | 10888 | 7952.5 MW (12:00 )
4:00 | 140 | 7216 | 3805 | 11021 | [6 empty] | 12:00
4:30 | 167.5 | 7178 | 3671 | 10849 | [5 empty] | Highest Generation | 12220
5:00 | 195 | 7140 | 3537 | 10677 | [6 empty] | 19:00
5:30 | 263 | 6938.5 | 3364.5 | 10303
6:00 | 331 | 6737 | 3192 | 9929
6:30 | 375.5 | 6515.5 | 3111.5 | 9627
7:00 | 420 | 6294 | 3031 | 9325
7:30 | 530 | 6295.5 | 3046.5 | 9342
8:00 | 640 | 6297 | 3062 | 9359
8:30 | 600 | 6412.5 | 3056.5 | 9469
9:00 | 560 | 6528 | 3051 | 9579
9:30 | 505.5 | 6808 | 3032 | 9840
10:00 | 451 | 7088 | 3013 | 10101
10:30 | 404.5 | 7212.5 | 3072 | 10284.5
11:00 | 358 | 7337 | 3131 | 10468
11:30 | 320.5 | 7455 | 3223 | 10678
12:00 | 283 | 7573 | 3315 | 10888
12:30 | 229.5 | 7598 | 3347 | 10945
13:00 | 176 | 7623 | 3379 | 11002
13:30 | 263.5 | 7586.5 | 3448 | 11034.5
14:00 | 351 | 7550 | 3517 | 11067
14:30 | 311.5 | 7690 | 3556 | 11246
15:00 | 272 | 7830 | 3595 | 11425
15:30 | 292 | 7836 | 3555 | 11391
16:00 | 312 | 7842 | 3515 | 11357
16:30 | 373.5 | 7501 | 3439.5 | 10940.5
17:00 | 435 | 7160 | 3364 | 10524
17:30 | 443.5 | 7168.5 | 3398 | 10566.5
18:00 | 452 | 7177 | 3432 | 10609
18:30 | 271.5 | 7672.5 | 3742 | 11414.5
19:00 | 91 | 8168 | 4052 | 12220
19:30 | 94 | 7886 | 4093 | 11979
20:00 | 59 | 7722 | 4160 | 11882 |  |  |  | Executive Engineer
20:30 | 43 | 7718 | 4206.5 | 11924.5 |  |  |  | Network Operation Division
21:00 | 27 | 7714 | 4253 | 11967
21:30 | 15.5 | 7737.5 | 4251.5 | 11989
22:00 | 4 | 7761 | 4250 | 12011 |  |  |  |  | Page 6 of 7
22:30 | 42 | 7706.5 | 4215 | 11921.5
23:00 | 80 | 7652 | 4180 | 11832
23:30 | 88 | 7699 | 4188 | 11887
24:00 | 96 | 7746 | 4196 | 11942
9500 MW (19:30 )
7952.5 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-09-20 |  | Energy | 266771868
[10 empty] | 2020-09-20 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3641 | 918 | 2275 | 3429 | 730 | 120 | 640 | 0 | 170
0:30 | 3570 | 923 | 2236 | 3382 | 740 | 81 | 692.5 | 0 | 175 | Date: | 2020-09-20
1:00 | 3499 | 928 | 2197 | 3335 | 750 | 42 | 745 | 0 | 180
1:30 | 3507 | 928 | 2201 | 3267.5 | 740 | 42 | 730 | 0 | 179 | [7 empty] | Total Energy | 266.7719 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 3515 | 928 | 2205 | 3200 | 730 | 42 | 715 | 0 | 178 | [7 empty] | Energy not Served | 0
2:30 | 3512.5 | 928 | 2190.5 | 3117 | 730 | 41 | 715 | 0 | 178 | [7 empty] | Energy Requirement | 266.7719
3:00 | 3510 | 928 | 2176 | 3034 | 730 | 40 | 715 | 0 | 178
3:30 | 3509.5 | 928 | 2154.5 | 2949.5 | 720 | 40 | 688.5 | 0 | 176 | [6 empty] | Shortage
4:00 | 3509 | 928 | 2133 | 2865 | 710 | 40 | 662 | 0 | 174
4:30 | 3522 | 928 | 2121 | 2822 | 655 | 40 | 591 | 0 | 170
5:00 | 3535 | 928 | 2109 | 2779 | 600 | 40 | 520 | 0 | 166
5:30 | 3541.5 | 928 | 2066 | 2547 | 600 | 40 | 421.5 | 0 | 159
6:00 | 3548 | 928 | 2023 | 2315 | 600 | 40 | 323 | 0 | 152
6:30 | 3580 | 928 | 1992.5 | 2078 | 565 | 40 | 296.5 | 0 | 145 |  |  |  |  | Coal
7:00 | 3612 | 928 | 1962 | 1841 | 530 | 40 | 270 | 0 | 138
7:30 | 3632.5 | 928.5 | 1952.5 | 1843.5 | 530 | 40 | 270 | 0 | 137 |  |  |  | Oil |  |  |  | ,
8:00 | 3653 | 929 | 1943 | 1846 | 530 | 40 | 270 | 0 | 136
8:30 | 3636.5 | 928.5 | 2003 | 1912 | 530.5 | 40 | 270 | 0 | 136
9:00 | 3620 | 928 | 2063 | 1978 | 531 | 40 | 270 | 0 | 136
9:30 | 3647 | 928 | 2095 | 2203 | 495.5 | 41 | 270 | 0 | 139
10:00 | 3674 | 928 | 2127 | 2428 | 460 | 42 | 270 | 0 | 142
10:30 | 3678.5 | 928 | 2126 | 2614.5 | 460 | 42 | 261.5 | 0 | 142
11:00 | 3683 | 928 | 2125 | 2801 | 460 | 42 | 253 | 0 | 142
11:30 | 3687.5 | 928.5 | 2138.5 | 2960.5 | 460 | 42 | 284 | 0 | 147
12:00 | 3692 | 929 | 2152 | 3120 | 460 | 42 | 315 | 0 | 152
12:30 | 3677.5 | 928.5 | 2168 | 3138 | 460 | 58 | 333 | 0 | 154
13:00 | 3663 | 928 | 2184 | 3156 | 460 | 74 | 351 | 0 | 156
13:30 | 3663 | 928 | 2184 | 3156 | 460 | 74 | 351 | 0 | 156
14:00 | 3663 | 928 | 2184 | 3156 | 460 | 74 | 351 | 0 | 156
14:30 | 3661.5 | 928 | 2187 | 3345.5 | 463.5 | 57 | 384.5 | 0 | 163
15:00 | 3660 | 928 | 2190 | 3535 | 467 | 40 | 418 | 0 | 170
15:30 | 3657.5 | 928 | 2157 | 3515 | 498.5 | 40 | 418 | 0 | 165
16:00 | 3655 | 928 | 2124 | 3495 | 530 | 40 | 418 | 0 | 160
16:30 | 3587 | 928 | 2038 | 3250 | 530 | 40 | 405 | 0 | 158
17:00 | 3519 | 928 | 1952 | 3005 | 530 | 40 | 392 | 0 | 156
17:30 | 3551.5 | 924 | 1868 | 3026.5 | 540 | 56.5 | 454 | 0 | 145
18:00 | 3584 | 920 | 1784 | 3048 | 550 | 73 | 516 | 0 | 134
18:30 | 3559.5 | 919 | 1983.5 | 3524 | 585 | 95 | 596.5 | 0 | 152
19:00 | 3535 | 918 | 2183 | 4000 | 620 | 117 | 677 | 0 | 170
19:30 | 3555 | 918 | 2189 | 3710 | 620 | 117 | 696 | 0 | 174
20:00 | 3559 | 918 | 2135 | 3650 | 664 | 117 | 661 | 0 | 178
20:30 | 3561 | 918 | 2218.5 | 3589.5 | 702 | 117.5 | 641 | 0 | 177
21:00 | 3563 | 918 | 2302 | 3529 | 740 | 118 | 621 | 0 | 176
21:30 | 3592.5 | 918 | 2296.5 | 3521.5 | 745 | 118.5 | 621 | 0 | 176
22:00 | 3622 | 918 | 2291 | 3514 | 750 | 119 | 621 | 0 | 176
22:30 | 3620.5 | 918 | 2260 | 3471.5 | 740 | 119 | 616.5 | 0 | 176
23:00 | 3619 | 918 | 2229 | 3429 | 730 | 119 | 612 | 0 | 176
23:30 | 3630 | 918 | 2252 | 3429 | 730 | 119.5 | 626 | 0 | 173 | Max Temp. in Dhaka |  | 35.7° C
24:00 | 3641 | 918 | 2275 | 3429 | 730 | 120 | 640 | 0 | 170
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
Note on W13: Author:

## Generation
g | 2020-09-20
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 42 | 42 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 42 | 42 | 42 | 74 | 40 | 40 | 40 | 40 | 38 |  | 82 | 82 | 82 | 83 | 84 | 84 | 85 | 1145907
2 | Karnaphuli Hydro PP Unit-4 & 5 | [17 empty] | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 236000
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [9 empty] | 0 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 16 | 25 | 25 | 25 | 25 | 25 | 25 | 220678
| Teknaf 20MW PP (Solartech) | [6 empty] | 2 | 6 | 5 | 19 | 20 | 14 | 20 | 19 | 13 | 4 | 1 | [9 empty] | 108945
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 68 | 68 | 68 | 68 | 68 | [6 empty] | 50 | 51 | 68 | 68 | 68 | 68 | 82 |  | 85 | 85 | 68 | 51 | 51 | 51 | 51 | 1176581
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 34 | 34 | 34 | 34 | 34 | 17 |  |  |  | 19 | 51 | 64 | 68 | 68 | 68 | 68 | 68 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1114867
| Daudkandi 200 MW PP (B.Trac) | [17 empty] | 17 |  | 80 | [6 empty] | 76032
14 | Titas 50 MW Peaking PP | 41 | 41 | 41 | 32 | [13 empty] | 29 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 423968
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 286 | 271 | 262 | 267 | 287 | 274 | 296 | 288 | 292 | 278 | 290 | 287 | 254 | 290 | 290 | 251 | 271 | 290 |  | 232 | 281 | 290 | 284 | 284 | 265 | 271 | 6802567
18 | Kodda 300 MW PP Unit-2 (Summit) | 300 | 300 | 300 | 300 | 300 | 300 | 200 | 200 | 208 | 275 | 286 | 286 | 286 | 286 | 291 | 296 | 286 | 293 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 6889961
19 | Ashuganj 195MW PP (APSCL-United) | 45 | 45 | 45 | 45 | 45 | 45 | 8 | 8 | 8 | 8 | 8 | 16 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 8 | 8 | 669090
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2772000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4776027
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 85 | 80 | 2644752
32 | Ashuganj 50 MW PP | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 740952
33 | Ashuganj 225 MW CCPP | 207 | 190 | 177 | 173 | 170 | 170 | 204 | 213 | 211 | 211 | 206 | 210 | 210 | 209 | 208 | 210 | 210 | 208 |  | 200 | 195 | 191 | 217 | 210 | 216 | 215 | 4885000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 310 | 310 | 310 | 310 | 345 | 310 | 330 | 355 | 345 | 310 | 310 | 320 | 330 | 310 | 310 | 325 |  | 305 | 305 | 305 | 290 | 290 | 315 | 320 | 7860000
35 | Ashuganj 55 MW PP (Precision) | 45 | 45 | 45 | 45 | 44 | 45 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 25 | 25 | 25 | 25 | 25 | 25 | 688800
36 | Chandpur 150 MW CCPP | 90 | 84 | 83 | 82 | 85 | 86 | 90 | 90 | 91 | 90 | 90 | 90 | 82 | 91 | 90 | 80 | 83 | 91 |  | 81 | 81 | 80 | 80 | 82 | 91 | 91 | 2064540
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 343 | 341 | 345 | 339 | 339 | 343 | 347 | 345 | 355 | 381 | 365 | 356 | 360 | 353 | 366 | 350 | 342 | 342 |  | 353 | 339 | 338 | 340 | 339 | 340 | 368 | 8497150
40 | Meghnaghat 450 MW CCPP(MPL) | 390 | 390 | 360 | 360 | 360 | 360 | 360 | 360 | 400 | 420 | 420 | 420 | 420 | 360 | 400 | 400 | 400 | 300 |  | 420 | 420 | 380 | 450 | 450 | 420 | 420 | 9095500
41 | Haripur 360MW CCPP(HPL) | 324 | 323 | 324 | 323 | 304 | 278 | 272 | 274 | 323 | 343 | 341 | 341 | 341 | 323 | 338 | 343 | 348 | 284 |  | 351 | 353 | 354 | 353 | 354 | 352 | 350 | 7790000
42 | RPCL 210MW CCPP | 154 | 154 | 154 | 154 | 154 | 154 | 151 | 150 | 149 | 149 | 149 | 147 | 147 | 144 | 144 | 148 | 150 | 149 |  | 153 | 153 | 153 | 153 | 156 | 156 | 156 | 3548560
43
44 | Fenchugonj CCPP Phase-1 | 88 | 88 | 89 | 88 | 89 | 88 | 88 | 89 | 88 | 88 | 84 | 85 | 87 | 85 | 82 | 83 | 83 | 83 |  | 86 | 86 | 86 | 87 | 87 | 86 | 86 | 2033000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 29 | 29 | 29 | 30 | 30 | 29 | 29 | 30 |  | 29 | 29 | 29 | 29 | 29 | 29 | 30 | 702600
46 | Shajibazar 330 MW CCPP | 235 | 237 | 235 | 236 | 234 | 235 | 234 | 234 | 236 | 234 | 236 | 236 | 235 | 237 | 195 | 196 | 140 | 231 |  | 256 | 257 | 263 | 258 | 260 | 260 | 260 | 5275000
47 | Shahjibazar GTPP Unit- 8 & 9 | 63 | 63 | 63 | 63 | 63 | 63 | 61 | 62 | 63 | 63 | 61 | 62 | 64 | 61 | 59 | 60 | 40 | 50 |  | 52 | 52 | 52 | 64 | 64 | 63 | 64 | 1460352
48 | Shahjibazar 86MW PP (Shahjibazar) | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 83 | 83 | 84 | 83 | 84 | 84 | 86 | 86 | 86 | 40 | 40 |  | 87 | 87 | 87 | 87 | 84 | 84 | 85 | 1960320
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 212 | 212 | 212 | 213 | 213 | 213 | 213 | 213 | 214 | 214 | 213 | 213 | 203 | 214 | 212 | 213 | 213 | 213 |  | 213 | 193 | 192 | 201 | 213 | 211 | 205 | 5099250
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 18 | 18 | 404000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 211500
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 5 | 8 | 8 | 5 |  |  |  |  | 5 |  |  |  | 5 | 8 | 8 |  |  | 5 | 11 | 11 | 8 | 11 | 11 | 119096
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 50 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 53 | 53 | 53 | 53 | 52 | 28 | 28 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1186800
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 21 | 21 |  |  | 16 | 16 | 24 |  | 24 | 24 | 24 | 16 | 16 | 24 | 24 | 478080
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 290 | 295 | 280 | 280 | 285 | 300 | 310 | 300 | 310 | 300 | 295 | 300 | 270 | 310 | 290 | 280 | 270 |  | 280 | 285 | 255 | 290 | 285 | 280 | 310 | 7257000
| Bibiyana South 400 MW | [14 empty] | 30 | 100 | 40
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 17 | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1181311
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 460272
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | [5 empty] | 22 | 22 | 22 | 390672
62 | Tangail 22 MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 18 | 18 | 18 | 14 | 380196
63 | Impoprt (Tripura) | 180 | 178 | 178 | 174 | 166 | 152 | 138 | 136 | 136 | 142 | 142 | 152 | 156 | 168 | 170 | 160 | 156 | 134 |  | 170 | 174 | 178 | 176 | 176 | 176 | 170 | 3904320
64 | Malancha, Ctg. EPZ (United) | 34 | 38 | 38 | 42 | 42 | 42 | 27 | 9 | 4 | 3 | 2 | 3 | 8 | 2 | 5 | 5 | 9 | 13 |  | 10 | 14 | 22 | 36 | 38 | 40 | 40 | 502080
65 | Feni 22MW PP (Doreen) | 18 | 18 | 18 | 18 | 15 | 15 | 17 | 18 | 15 | 15 | 15 | 15 | 15 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 391212
66 | Feni 11 MW PP (Doreen) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 2 | 2 | 2 | 5 | 5 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 98280
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 17 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 622300
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 507540
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 16 | 16 | 16 | 28 | 28 | 28 | 22 | 507780
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 28 |  | 33 | 33 | 33 | 699600
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 33 | 25 | 33 | 33 | 25 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 788700
73 | Ghorashal 108MW PP (Regent) | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 91 | 92 | 92 | 92 | 92 | 95 | 95 | 95 | 95 | 95 |  | 95 | 95 | 95 | 92 | 94 | 94 | 94 | 2215318
| Feni Lanka Power | 114 | 114 | 114 | 114 | 70 | [5 empty] | 34 | 114 | 114 | 114 | 114 | 114 | 70 | 70 |  | 114 | 114 | 114 | 90 | 90 | 90 | 105 | 1934580
| Chowmuhani 113 MW | 113 | 113 | 108 | 108 | 107 | 108 | 105 | 103 | 104 | 104 | 104 | 104 | 105 | 104 | 107 | 113 | 85 | 85 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2585520
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 194880
78 | Gazipur 52 MW PP | 50 | 51 | 51 | 51 | 51 |  |  |  |  | 4 | 27 | 50 | 50 | 50 | 50 | 50 | 16 | 16 |  | 46 | 50 | 25 | 25 | 25 | 25 | 33 | 772020
79 | Kodda 150MW PP | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 133 | 133 | 133 | 133 | 133 | 133 | 98 | 98 |  | 133 | 133 | 114 | 82 | 82 | 82 | 114 | 3150240
80 | Jamalpur 95 MW PP(Powerpac) | [25 empty] | 0 | 0
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | 52 | 52 |  |  |  |  | 2 | 18 | 46 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 43 | 43 | 979550
| Gazipur 100 MW PP | 84 | 84 | 84 | 84 | 84 | 34 |  |  | 50 | 84 | 84 | 85 | 85 | 85 | 85 | 85 | 85 | 85 |  | 85 | 85 | 85 | 85 | 85 | 67 | 67 | 1761720
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 2 | 4 | 6 | 4 | 2 | 0 | 0 | 0 | 0 | [9 empty] | 20280
| Jodiac Power | 54 | 54 | 54 | 54 | 54 |  |  |  |  | 28 | 54 | 54 | 54 | 54 | 54 | 52 | 53 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1092797
| Karnaphuli Power Ltd. | [19 empty] | 11 | 17 | 17 | 17 | 17 | 17 | 17 | 102872
82 | Madanganj 102 PP(Summit) | 85 | 85 | 96 | 96 | 96 | 96 | 48 | 48 | 60 | 80 | 80 | 80 | 80 | 86 | 96 | 96 | 96 | 97 |  | 96 | 97 | 97 | 97 | 97 | 96 | 77 | 2134008
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [10 empty] | 52 | 53 | 50 | 50 | 50 | 76 | 100 | 100 |  | 65 | 27 | 26 | 26 | 25 | 27 | 25 | 755211
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 9 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 199680
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 2612160
88 | Ghorashal 78.5 MW PP(MAX) | 71 | 71 | 71 | 71 | 70 | 70 | 70 | 68 | 68 | 68 | 66 | 65 | 65 | 65 | 64 | 64 | 60 | 40 |  | 66 | 67 | 69 | 69 | 70 | 69 | 68 | 1560160
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [9 empty] | 30 | 70 | 70 | 70 | 70 | 70 | 70 | 20 | 20 |  | 60 | 60 | 30 | 30 | 30 | 30 | 30 | 768360
92 | Fenchuganj 44MW (Energyprima) | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 44 | 44 | 43 | 43 | 43 | 43 | 43 | 20 | 20 |  | 40 | 45 | 48 | 48 | 48 | 49 | 49 | 1049976
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 51 | 51 | 51 | 51 | 43 | 43 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1162341
94 | Gagnagar 102 MW PP (Digital Power) | 93 | 93 | 93 | 93 | 93 | 93 | 85 | 85 | 85 | 85 | 85 | 85 | 93 | 93 | 93 | 93 | 93 | 93 |  | 93 | 93 | 93 | 93 | 93 | 94 | 93 | 2183328
95 | Patenga 50MW PP (Baraka) | 50 | 50 | 50 | 50 | 50 | 30 |  |  | 1 | 28 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1042560
96 | Chattogram 108 MW PP (ECPV) |  | 0 | 25 | 84 | 84 | 65 | 12 | 27 | 78 | 80 | 70 | 72 | 67 | 77 | 77 | 77 | 78 | 77 |  | 78 | 84 | 84 | 84 | 84 | 84 | 84 | 1561920
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | 40 | 40 | 40 | 40 | 40 | 40 | 15 | 15 | 30 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 40 | 40 | 55 | 1130481
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1216417
101 | Kushiara 163 MW CCPP (KP) | 110 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 163 | 163 | 163 | 163 | 110 | 163 | 163 | 110 | 110 |  | 163 | 130 | 130 | 163 | 163 | 163 | 163 | 3477600
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 15250
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 17 | 17 | 17 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 17 | 17 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1164960
104 | Keranigonj 300 MW PP (APR) | [19 empty] | 68 | [5 empty] | 0 | 153742
105 | Bramhangoan 100 MW PP (Aggreko) | 50 | [13 empty] | 25 | 25 |  | 25 |  | 98 | [5 empty] | 0 | 239217
106 | Mymensingh 200 MW PP (United) | 48 | 48 | 48 | 48 | 62 | 188 | 197 | 198 | 200 | 190 | 179 | 190 | 179 | 179 | 174 | 173 | 174 | 185 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 3705600
112 | Aurahati 100MW PP (Aggreko) | 101 | [13 empty] | 26 |  |  | 26 |  | 61 | [5 empty] | 0 | 277134
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 130 | 132 | 132 | 137 | 146 | 137 | 146 | 146 |  | 146 | 147 | 146 | 145 | 146 | 143 | 145 | 3490990
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 100 | 90 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2395200
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 50 | [8 empty] | 42 | 87 | 142 | 195 | 200 | 100 | 100 |  | 153 | 180 | 150 | 68 | 68 | 34 | 34 | 2001600
117 | Ashuganj 150MW PP (Midland) | 80 | 86 | 88 | 100 | 100 | 50 | 10 | 10 | 10 | 35 | 103 | 122 | 120 | 123 | 122 | 122 | 122 | 122 |  | 123 | 123 | 125 | 125 | 125 | 125 | 127 | 2400363
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 38 | 38 | 38 | 38 | 38 | 38 | 56 | 75 | 75 | 109 | 109 | 115 | 95 | 95 | 106 | 115 | 115 | 85 |  | 115 | 115 | 115 | 115 | 115 | 105 | 105 | 2056800
| Anwara 300 MW PP (United) | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 308 | 307 | 307 | 307 | 307 | 307 | 307 | 255 | 254 |  | 307 | 307 | 306 | 306 | 306 | 307 | 307 | 7288909
| Juldah unit-2 (Acorn) | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2409600
120 | Eastern Zone Total | 7553 | 7402 | 7239 | 7216 | 7140 | 6737 | 6294 | 6297 | 6528 | 7088 | 7337 | 7573 | 7623 | 7550 | 7830 | 7842 | 7160 | 7177 |  | 8168 | 7886 | 7722 | 7714 | 7761 | 7652 | 7746 | 177512482
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 85 | 32 | 32 | 58 | 66 | 99 | 99 | 83 | 99 | 83 |  | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 2094720
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 24 | 24 | 24 | 4 | [22 empty] | 87390
| Khulna 225 MW CCPP | 230 | 200 | 200 | 200 | 135 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 125 |  | 180 | 180 | 180 | 200 | 200 | 200 | 200 | 3786240
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | 35 | 35 | 35 | [9 empty] | 27 | 53 | 53 | 35 | 35 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 906240
130
131
132
133
| Barisal 110 MW PP (Summit ) | 110 | 110 | 110 | [10 empty] | 64 | 80 | 80 | 80 | 80 |  | 110 | 110 | 110 | 96 | 96 | 80 | 80 | 1312704
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 78 | 76 | 77 | 76 | 76 | 78 | 53 | 53 | 50 | 23 | 40 | 55 | 75 | 78 | 79 | 77 | 61 | 44 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 1625782
| Bhola 225 MW CCPP | 16 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 40 | 50 | 60 | 60 | 60 | 60 | 59 | 60 | 60 |  | 52 | 57 | 59 | 58 | 59 | 60 | 60 | 1325000
140 | Bhola 33 MW PP (Venture) | 38 | 38 | 38 | 10 | 20 | 23 | 20 | 18 | 16 | 18 | 19 | 20 | 20 | 21 | 25 | 19 | 21 | 30 |  | 32 | 34 | 31 | 35 | 36 | 24 | 34 | 614188
141 | Noapara 100 MW PP (Bangla Trac) | 100 | 100 | 100 | 20 | [13 empty] | 2 |  | 81 | 100 | 100 | 100 | 100 | 100 | 100 | 955200
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 40 | 40 | 40 | [12 empty] | 16 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 463500
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 4 | 10 | [8 empty] | 6784
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 928 | 928 | 928 | 928 | 928 | 928 | 928 | 929 | 928 | 928 | 928 | 929 | 928 | 923 | 928 | 928 | 928 | 920 |  | 918 | 918 | 918 | 918 | 918 | 918 | 918 | 22206545
147 | Bheramara 410 MW CCPP | 270 | 290 | 305 | 320 | 330 | 350 | 360 | 365 | 290 | 300 | 320 | 370 | 385 | 365 | 345 | 335 | 330 | 335 |  | 330 | 330 | 325 | 320 | 315 | 305 | 305 | 8121024
148 | Payra 1320 MW | 600 | 580 | 580 | 560 | 450 | 450 | 380 | 380 | 380 | 310 | 310 | 310 | 310 | 310 | 317 | 380 | 380 | 400 |  | 470 | 470 | 514 | 590 | 600 | 580 | 580 | 11407900
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 151 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3682200
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 50 | 50 | 50 | 50 | 50 | [8 empty] | 40 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 769808
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 160 | 150 | 150 | 150 | 150 | 150 | 152 | 163 | 171 | 190 | 202 | 190 | 191 | 187 | 194 | 184 | 180 | 155 |  | 179 | 176 | 176 | 180 | 182 | 173 | 164 | 4359336
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 130 | 130 | 130 | 130 | 130 | 130 | 140 | 179 | 192 | 206 | 197 | 196 | 195 | 196 | 203 | 193 | 189 | 160 |  | 186 | 188 | 185 | 190 | 188 | 188 | 200 | 4506409
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 411 | 398 | 392 | 393 | 383 | 312 | 347 | 346 | 401 | 399 | 396 | 398 | 390 | 390 | 403 | 353 | 347 | 376 |  | 374 | 387 | 394 | 406 | 396 | 399 | 407 | 9312909
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 34 | 34 | 34 | 10 | [12 empty] | 5 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 355040
162 | Bogra 22 MW PP (GBB) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 14 | 14 | 14 | 14 | 18 | 18 | 17 | 17 |  | 17 | 19 | 17 | 20 | 20 | 20 | 20 | 368880
163 | Bogura 20 MW PP (Energyprima) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 225828
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 11 | 11 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 245016
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 50 | 50 | [9 empty] | 50 | 50 | 50 | 50 | 50 | 25 | 25 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 665900
167 | Katakhali 50 MW Peaking PP | 21 | 21 | 21 | 21 | 21 | [12 empty] | 12 |  | 27 | 42 | 47 | 36 | 36 | 36 | 36 | 310640
168 | Santahar 50 MW Peaking PP | 31 | 31 | 31 | 31 | [13 empty] | 21 |  | 32 | 32 | 32 | 32 | 32 | 31 | 24 | 331471
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 52 | 52 |  |  |  |  | 17 | 35 | 43 | 43 | 43 | 43 | 43 | 25 | 25 |  | 46 | 52 | 52 | 52 | 52 | 52 | 52 | 885600
170 | Chapainawabganj 100 MW Peaking PP | 96 | 96 | 96 | 96 | 96 | 53 | [5 empty] | 12 | 47 | 48 | 47 | 47 | 47 | 55 |  | 94 | 98 | 94 | 94 | 94 | 86 | 89 | 1388576
171 | Baghabari 200 MW PP (Paramount) | [17 empty] | 20 |  | 50 | [5 empty] | 0 | 66470
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 113 | 35 |  |  |  | 24 | 73 | 94 | 94 | 94 | 94 | 94 | 35 | 35 |  | 69 | 69 | 94 | 94 | 94 | 94 | 94 | 1902048
172 | Confidence Power Bogura Unit-1 113 MW | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 80 | 70 | 70 |  | 100 | 109 | 109 | 109 | 109 | 109 | 109 | 2481600
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 113 | 112 | 113 | 113 | 113 | 113 | 80 | 52 | 58 | 109 | 112 | 110 | 105 | 103 | 104 | 96 | 84 | 66 |  | 93 | 110 | 111 | 111 | 111 | 113 | 112 | 2442240
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 3 | 4 | 5 | 6 | 6 | 6 | 5 | 3 | 2 | 1 | 0 | [8 empty] | 46198
178
178