## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-09-24 | Thursday
|  |  | Date (day): | 2020-09-24 |  | Thursday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12729.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13620 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-09-23 | 2020-09-24 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 115 | 115 | 115 | 75 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 200 | 200 | 165 |  | Machine problem
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 66 | 68 | 68 | 68 |  | 10 | Engine problem
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 90 | 94 | 94 | 94 |  | 14 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 340 | 339 | 412 | 412 |  |  | FGMO
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 310 | 353 | 0 | 0 |  | 360 | Under maint
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 380 | 350 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 20 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 97 | 95 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 41 | 41 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 90 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 273 | 300 | 335 | 335 |  |  | FGMO
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 93 | 93 | 93 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 150 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 52 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 52 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 300 | 300 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 130 | 131 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 50 | 84 | 85 | 85 |  | 20 | Engine problem
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 17 | 17 | 17 | 87 |  | Fuel shortage
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 2873 | 3296 | 3491 | 3781 | 1106 | 1008
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 8 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 11 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 2 | 18 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 42 | 75 | 40 | 105 | 125 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 17 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 100 | 100
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 100 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 19 | 20 | 20
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 8 | 17 | 8 | 30
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 39 | 90 | 90 | 90 |  | 18 | Engine problem
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 306 | 307 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 54 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 720 | 1010 | 1342 | 1404 | 515 | 341
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 100 | 80 | 80 | 80 | 54 |  | Gas shortage
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 182 | 189 | 225 | 225 |  |  | FGMO
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 260 | 360 | 360 |  |  | FGMO
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 29 | 30 | 30 | 15 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 20 | 27 | 50 | 50
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 20 | 105 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 36 | 0 | 42
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 85 | 96 | 100 | 100 |  | 63 | ST under shut down
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 101 | 200 | 200
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 120 | 158 | 162 | 173
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 34 | 34 | 34 |  | 18 | Engine problem
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 20 | 21 | 21
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 100 | 114 | 114
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 113 | 113 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1064 | 1458 | 1749 | 2002 | 520 | 456
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 145 | 125 | 160 | 160 | 42 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 16 | 16 | 16 |  | 6 | Engine problem
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 0 | 0 | 0 |  | 95 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 195 | 195 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 24 | 90 | 115 | 115
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 381 | 426 | 492.6 | 491 | 42 | 101
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 89 | 89 | 90 | 90
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 35 | Unit-4 under shut down
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 110 | 163 | 163
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 211 | 140 | 250 | 250
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 49 | 50 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 46 | 49 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 66 | 65 | 65 | 65
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 50 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 205 | 219 | 0 | 0 |  | 231 | Engine problem
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 300 | 341 | 341 |  |  | FGMO
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1292 | 1164 | 1184 | 1184 | 0 | 666
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 921 | 921 | 931 | 931
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 99 | 115 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 12 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 180 | 225 | 225
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 310 | 330 | 315 | 315
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 53 | 105 | 105
| 108 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1450 | 1751 | 1881 | 2037 | 0 | 0
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 64 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 15 | 32 | 33 | 33
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 60 | 60 | 60 | 60 |  | 134 | GT-2 & STG under shut down
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 78 | 76 | 76 | 76 |  | 19 | Engine problem
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 430 | 540 | 580 | 580
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 583 | 772 | 859 | 859 | 0 | 153
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 35 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 43 | 43 | 43
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | ST Under maint & gas shoratge
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 184 | 135 | 200 | 200 |  |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 196 | 160 | 220 | 220 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 354 | 412 | 414 | 414 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 33 | 0 | 34
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 17 | 15 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 10 | 10 | 10 | 10
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 9 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 52 | 52 | 52
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 96 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 90 | 90 | 90 |  | 23 | Engine problem
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 109 | 109 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 875 | 1244 | 1473 | 1599 | 271 | 233
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 80 | 113 | 100 | 113
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 0 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 230 | 263 | 258 | 263 | 294 | 40
|  | Total |  |  |  |  | 20383 | 19892 | 9468 | 11384 | 12729.6 | 13620 | 2748 | 2998
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9097.8963 | 10939 | 12232.0006 | 13087.5949
| A. |  | 2020-09-23 | (Yesterday) |  |  |  |  | Wednesday
| 1 | Highest Generation : |  |  | 11384 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
| 2 | Minimum Generation : |  |  | 8503 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11384 | MW
| 3 | Day peak Generation : |  |  | 9468 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10939 | MW
| 4 | Evening peak Generation : |  |  | 11384 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 237.0147 | MKWHr | By Solar | 0.093853 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 133.5401 | MKWHr |  | By Oil: | 60.8929 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 16.0101 | MKWHr |  | By Hydro: | 1.1354 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2748 | MW | Dhaka | 3981 | 3981 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2998 | MW | Chittagong | 1103 | 1103 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5746 | MW | Khulna | 1382 | 1382 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1048.69 | MMCFD |  |  | Rajshahi | 1162 | 1162 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 155009748.264 | ii) Oil : | Taka | 505271819.12 | Comilla | 1071 | 1071 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 74087717 | Total | Taka | 734369284.384 | Mymensingh | 842 | 842 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 466 | 466 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 324 | MW (E to W) at | 19:30 | hrs | Barisal | 322 | 322 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 193 | MW at | 24:00 | hrs | Rangpur | 610 | 610 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 30.7° C |  |  | Total | 10939 | 10939 |  | 0
| B. |  | 2020-09-24 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 31.7° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 11400 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13620 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 9200 | MW
| 4 | Reserve(Generation end) |  |  |  | 2220 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 237.3478 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7827 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.1178 | MKWHr. | ii) HVDC Flow at Peak Time |  | 921 | MW at | 19:30 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.2246 | MKWHr. | iii) Maximum HVDC Flow : |  | 937 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 95.35 |  | (b) Today: | 95.61 |  | (c) Rule Curve: |  | 104.32
.

## YesterdayGen
2020-09-23
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 115 | 200 | 95 | 68 | 355 | 351 |  | 0 | 420 | 0 | 7 | 97 | 55 | 290 | 0 | 0 | 0 | 0 | 93 | 0 | 24 | 0 | 0 | 0 | 17 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 84 | 50 | 20 | 42 | 0 | 0 | 100 | 320 | 0 | 189 | 8 | 90 | 29 | 20 | 0 | 51 | 0 | 0 | 43 | 15 | 8 | 25 | 21 | 152 | 158 | 0 | 16 | 0 | 89 | 30 | 50 | 49 | 130 | 210 | 66 | 87 | 0 | 205 | 17 | 0 | 9 | 310 | 24 | 8 | 0 | 300 | 0 | 0 | 194 | 0 | 130 | 0 | 100 | 0 | 107 | 0 | 105 | 84 | 17 | 0 | 307 | 54 | 0 | 0 | 113 | 100 | 0 | 17 |  | 937 | 0 | 235 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 80 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 168 | 0 | 77 | 0 | 178 | 0 | 395 | 0 | 0 | 113 | 0 | 101 | 0 | 0 | 109 | 560 |  | 6945 | 3499 | 10444 | 3442 | 937 | 2227 | 2726 | 710 | 42 | 208 | 152 | 0 | 0 | 95.33
2:00 | 0 | 0 | 0 | 115 | 200 | 95 | 68 | 335 | 355 |  | 0 | 420 | 0 | 7 | 97 | 55 | 290 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 82 | 10 | 20 | 42 | 0 | 0 | 100 | 320 | 0 | 182 | 8 | 95 | 29 | 20 | 0 | 51 | 0 | 0 | 0 | 15 | 8 | 25 | 21 | 150 | 158 | 0 | 16 | 0 | 89 | 30 | 50 | 49 | 130 | 212 | 66 | 87 | 0 | 205 | 18 | 0 | 9 | 290 | 24 | 8 | 0 | 300 | 0 | 0 | 194 | 0 | 131 | 0 | 100 | 0 | 107 | 0 | 105 | 0 | 0 | 0 | 307 | 54 | 0 | 0 | 113 | 100 | 0 | 17 |  | 936 | 0 | 245 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 30 | 32 | 80 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 5 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 168 | 0 | 77 | 0 | 179 | 0 | 365 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 109 | 560 |  | 6699 | 3379 | 10078 | 3461 | 936 | 2180 | 2403 | 711 | 42 | 195 | 150 | 0 | 0 | 95.33
3:00 | 0 | 0 | 0 | 115 | 200 | 95 | 68 | 344 | 352 |  | 0 | 420 | 0 | 7 | 97 | 55 | 287 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 45 | 0 | 20 | 36 | 0 | 0 | 100 | 320 | 0 | 182 | 8 | 91 | 26 | 20 | 0 | 51 | 0 | 0 | 0 | 15 | 8 | 25 | 21 | 150 | 158 | 0 | 16 | 0 | 89 | 30 | 50 | 49 | 130 | 211 | 65 | 87 | 0 | 205 | 18 | 0 | 9 | 295 | 24 | 8 | 0 | 300 | 0 | 0 | 194 | 0 | 130 | 0 | 100 | 0 | 107 | 0 | 105 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 113 | 100 | 0 | 17 |  | 922 | 0 | 255 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 29 | 32 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 168 | 0 | 77 | 0 | 179 | 0 | 395 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 109 | 520 |  | 6514 | 3323 | 9837 | 3498 | 922 | 2203 | 2182 | 670 | 42 | 170 | 150 | 0 | 0 | 95.34
4:00 | 0 | 0 | 0 | 115 | 200 | 95 | 68 | 340 | 353 |  | 0 | 420 | 0 | 7 | 97 | 55 | 297 | 0 | 0 | 0 | 5 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 38 | 0 | 0 | 100 | 325 | 0 | 184 | 8 | 96 | 26 | 20 | 0 | 51 | 0 | 0 | 0 | 15 | 8 | 25 | 21 | 148 | 158 | 0 | 16 | 0 | 89 | 30 | 50 | 49 | 130 | 210 | 65 | 88 | 0 | 205 | 18 | 0 | 9 | 300 | 24 | 8 | 0 | 300 | 0 | 0 | 193 | 0 | 120 | 0 | 100 | 0 | 50 | 0 | 45 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 113 | 100 | 0 | 17 |  | 921 | 0 | 270 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 29 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 161 | 0 | 76 | 0 | 175 | 0 | 395 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 109 | 520 |  | 6319 | 3255 | 9574 | 3519 | 921 | 2211 | 1943 | 670 | 42 | 120 | 148 | 0 | 0 | 95.34
5:00 | 0 | 0 | 0 | 115 | 200 | 95 | 68 | 348 | 352 |  | 0 | 400 | 0 | 7 | 64 | 55 | 301 | 0 | 0 | 0 | 7 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 0 | 0 | 100 | 330 | 0 | 195 | 8 | 96 | 26 | 20 | 0 | 51 | 0 | 0 | 0 | 15 | 8 | 25 | 21 | 140 | 158 | 0 | 16 | 0 | 89 | 30 | 50 | 49 | 163 | 210 | 65 | 88 | 0 | 205 | 18 | 0 | 9 | 310 | 24 | 8 | 0 | 145 | 0 | 0 | 193 | 0 | 110 | 0 | 100 | 0 | 10 | 0 | 45 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 113 | 100 | 0 | 17 |  | 922 | 0 | 285 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 159 | 0 | 76 | 0 | 181 | 0 | 395 | 0 | 0 | 0 | 0 | 74 | 0 | 0 | 109 | 520 |  | 6129 | 3230 | 9359 | 3566 | 922 | 2235 | 1664 | 670 | 42 | 120 | 140 | 0 | 0 | 95.35
6:00 | 0 | 0 | 0 | 115 | 200 | 95 | 67 | 343 | 309 |  | 0 | 400 | 0 | 7 | 55 | 30 | 263 | 0 | 0 | 0 | 7 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 9 | 0 | 0 | 100 | 320 | 0 | 182 | 8 | 86 | 26 | 20 | 0 | 51 | 0 | 0 | 0 | 15 | 8 | 25 | 21 | 132 | 160 | 0 | 16 | 0 | 89 | 30 | 50 | 49 | 163 | 211 | 65 | 88 | 0 | 205 | 18 | 0 | 9 | 300 | 24 | 8 | 0 | 145 | 0 | 0 | 200 | 0 | 110 | 0 | 100 | 0 | 10 | 0 | 8 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 98 | 100 | 0 | 17 |  | 921 | 0 | 295 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 159 | 0 | 77 | 0 | 182 | 0 | 345 | 0 | 0 | 0 | 0 | 61 | 0 | 0 | 109 | 479 |  | 5790 | 3081 | 8871 | 3504 | 921 | 2092 | 1431 | 629 | 42 | 120 | 132 | 0 | 0 | 95.35
7:00 | 0 | 0 | 0 | 115 | 200 | 95 | 50 | 339 | 289 |  | 0 | 350 | 0 | 7 | 48 | 30 | 288 | 0 | 0 | 0 | 7 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 40 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 31 | 0 | 0 | 100 | 285 | 0 | 182 | 8 | 85 | 22 | 20 | 0 | 51 | 0 | 0 | 0 | 15 | 8 | 25 | 17 | 120 | 160 | 0 | 16 | 0 | 89 | 30 | 50 | 49 | 100 | 210 | 65 | 88 | 0 | 205 | 18 | 0 | 9 | 290 | 24 | 8 | 0 | 145 | 0 | 0 | 200 | 0 | 110 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 199 | 0 | 0 | 0 | 47 | 100 | 0 | 17 |  | 921 | 0 | 310 | 0 | 32 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 147 | 0 | 78 | 0 | 167 | 0 | 380 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 50 | 470 |  | 5523 | 2980 | 8503 | 3468 | 921 | 1989 | 1224 | 620 | 40 | 120 | 120 | 1 | 0 | 95.36
8:00 | 0 | 0 | 0 | 115 | 200 | 95 | 40 | 340 | 289 |  | 0 | 350 | 0 | 7 | 48 | 30 | 305 | 0 | 0 | 0 | 10 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 40 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 0 | 0 | 100 | 295 | 0 | 194 | 8 | 96 | 26 | 20 | 0 | 51 | 0 | 0 | 0 | 15 | 8 | 25 | 15 | 120 | 160 | 0 | 16 | 1 | 89 | 30 | 50 | 49 | 100 | 211 | 66 | 88 | 0 | 205 | 18 | 0 | 9 | 290 | 24 | 8 | 0 | 145 | 0 | 0 | 200 | 0 | 112 | 1 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 197 | 0 | 0 | 0 | 46 | 100 | 0 | 17 |  | 921 | 0 | 315 | 0 | 32 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 76 | 0 | 163 | 0 | 399 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 50 | 450 |  | 5549 | 2977 | 8526 | 3529 | 921 | 1971 | 1222 | 600 | 40 | 120 | 120 | 3 | 0 | 95.36
9:00 | 0 | 0 | 0 | 115 | 200 | 91 | 40 | 351 | 289 |  | 0 | 350 | 0 | 7 | 54 | 34 | 307 | 0 | 0 | 0 | 18 | 93 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 40 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 1 | 0 | 20 | 5 | 0 | 0 | 100 | 270 | 0 | 182 | 8 | 88 | 29 | 20 | 0 | 51 | 0 | 0 | 0 | 15 | 8 | 25 | 15 | 120 | 157 | 0 | 16 | 2 | 89 | 30 | 50 | 49 | 163 | 210 | 67 | 85 | 0 | 205 | 18 | 0 | 9 | 300 | 24 | 8 | 0 | 163 | 0 | 0 | 200 | 0 | 129 | 5 | 100 | 0 | 2 | 0 | 12 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 88 | 100 | 0 | 17 |  | 921 | 0 | 315 | 0 | 32 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 162 | 0 | 78 | 0 | 171 | 0 | 368 | 0 | 0 | 0 | 0 | 34 | 0 | 1 | 50 | 430 |  | 5863 | 2946 | 8809 | 3523 | 921 | 2005 | 1492 | 580 | 40 | 120 | 120 | 8 | 0 | 95.37
10:00 | 0 | 0 | 0 | 115 | 200 | 91 | 50 | 340 | 310 |  | 0 | 350 | 0 | 7 | 90 | 41 | 298 | 0 | 0 | 0 | 72 | 93 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 40 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 20 | 5 | 0 | 0 | 100 | 270 | 0 | 188 | 8 | 96 | 29 | 20 | 0 | 51 | 0 | 0 | 0 | 15 | 8 | 25 | 15 | 122 | 156 | 0 | 16 | 1 | 89 | 30 | 47 | 46 | 163 | 210 | 66 | 84 | 0 | 205 | 18 | 0 | 9 | 290 | 24 | 8 | 0 | 261 | 0 | 0 | 200 | 0 | 130 | 9 | 100 | 0 | 10 | 0 | 24 | 30 | 0 | 2 | 304 | 0 | 0 | 0 | 113 | 100 | 0 | 17 |  | 921 | 0 | 310 | 0 | 32 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 154 | 0 | 77 | 0 | 163 | 0 | 399 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 70 | 430 |  | 6155 | 2975 | 9130 | 3494 | 921 | 2049 | 1792 | 580 | 40 | 120 | 122 | 12 | 0 | 95.38
11:00 | 0 | 0 | 0 | 115 | 200 | 90 | 67 | 345 | 310 |  | 0 | 350 | 0 | 9 | 97 | 41 | 317 | 0 | 0 | 0 | 92 | 93 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 41 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 20 | 5 | 0 | 0 | 100 | 270 | 0 | 184 | 8 | 94 | 29 | 20 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 25 | 15 | 128 | 155 | 0 | 16 | 2 | 89 | 30 | 47 | 46 | 163 | 212 | 66 | 84 | 0 | 205 | 18 | 0 | 9 | 310 | 24 | 8 | 0 | 298 | 0 | 0 | 200 | 0 | 130 | 9 | 90 | 0 | 10 | 0 | 24 | 50 | 0 | 2 | 307 | 0 | 0 | 0 | 105 | 100 | 0 | 17 |  | 921 | 0 | 310 | 0 | 58 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 164 | 0 | 78 | 0 | 174 | 0 | 400 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 109 | 430 |  | 6284 | 3062 | 9346 | 3529 | 921 | 2083 | 1931 | 580 | 41 | 120 | 128 | 13 | 0 | 95.39
12:00 | 0 | 0 | 0 | 115 | 200 | 90 | 66 | 340 | 310 |  | 0 | 380 | 0 | 7 | 97 | 41 | 273 | 0 | 0 | 0 | 100 | 93 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 39 | 2 | 0 | 8 | 0 | 0 | 100 | 270 | 0 | 182 | 8 | 85 | 29 | 20 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 25 | 15 | 120 | 145 | 0 | 16 | 1 | 89 | 30 | 49 | 46 | 163 | 211 | 66 | 84 | 0 | 205 | 18 | 0 | 9 | 290 | 24 | 8 | 0 | 300 | 0 | 0 | 195 | 0 | 130 | 11 | 90 | 0 | 20 | 0 | 24 | 50 | 0 | 2 | 306 | 0 | 0 | 0 | 113 | 100 | 0 | 17 |  | 921 | 0 | 310 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 10 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 184 | 0 | 78 | 0 | 196 | 0 | 354 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 109 | 430 |  | 6330 | 3138 | 9468 | 3485 | 921 | 2048 | 2138 | 580 | 42 | 120 | 120 | 14 | 0 | 95.4
13:00 | 0 | 0 | 0 | 115 | 200 | 91 | 50 | 338 | 265 |  | 0 | 340 | 0 | 7 | 97 | 41 | 253 | 0 | 0 | 0 | 100 | 93 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 74 | 24 | 17 | 8 | 0 | 0 | 100 | 260 | 0 | 182 | 8 | 86 | 26 | 20 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 25 | 15 | 122 | 125 | 0 | 16 | 0 | 89 | 30 | 50 | 46 | 110 | 212 | 67 | 84 | 0 | 151 | 18 | 0 | 9 | 270 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 131 | 9 | 95 | 0 | 40 | 0 | 8 | 50 | 0 | 2 | 306 | 0 | 0 | 0 | 113 | 100 | 110 | 17 |  | 921 | 0 | 280 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 164 | 0 | 78 | 0 | 173 | 0 | 284 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 109 | 430 |  | 6250 | 3012 | 9262 | 3433 | 921 | 1792 | 2241 | 580 | 42 | 120 | 122 | 11 | 9262 | 95.42
14:00 | 0 | 0 | 0 | 115 | 200 | 91 | 40 | 339 | 250 |  | 0 | 310 | 0 | 7 | 80 | 41 | 302 | 0 | 0 | 0 | 100 | 93 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 19 | 25 | 23 | 33 | 33 | 0 | 0 | 43 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 64 | 24 | 19 | 7 | 0 | 0 | 80 | 270 | 0 | 198 | 8 | 96 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 25 | 15 | 130 | 124 | 0 | 16 | 0 | 89 | 30 | 50 | 49 | 110 | 138 | 50 | 40 | 0 | 151 | 18 | 0 | 9 | 280 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 130 | 13 | 100 | 0 | 10 | 0 | 8 | 33 | 0 | 2 | 306 | 0 | 0 | 0 | 107 | 100 | 180 | 17 |  | 921 | 0 | 250 | 0 | 49 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 77 | 0 | 130 | 0 | 340 | 0 | 0 | 0 | 0 | 38 | 0 | 1 | 109 | 430 |  | 6051 | 2837 | 8888 | 3367 | 921 | 1744 | 1967 | 580 | 43 | 120 | 130 | 16 | 0 | 95.44
15:00 | 0 | 0 | 0 | 115 | 200 | 91 | 40 | 362 | 310 |  | 0 | 310 | 0 | 7 | 80 | 41 | 286 | 0 | 0 | 0 | 100 | 93 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 19 | 25 | 23 | 33 | 33 | 0 | 0 | 44 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 64 | 19 | 19 | 3 | 0 | 0 | 80 | 355 | 0 | 184 | 8 | 95 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 25 | 15 | 132 | 124 | 0 | 16 | 0 | 89 | 30 | 47 | 49 | 110 | 140 | 65 | 40 | 0 | 152 | 18 | 0 | 9 | 300 | 24 | 8 | 0 | 300 | 0 | 0 | 170 | 0 | 131 | 5 | 100 | 0 | 10 | 0 | 8 | 33 | 0 | 4 | 307 | 0 | 0 | 0 | 107 | 100 | 230 | 17 |  | 921 | 0 | 255 | 0 | 49 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 77 | 0 | 130 | 0 | 417 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 109 | 430 |  | 6236 | 2915 | 9151 | 3520 | 921 | 1895 | 1930 | 580 | 44 | 120 | 132 | 9 | 0 | 95.46
16:00 | 0 | 0 | 0 | 115 | 200 | 87 | 40 | 342 | 310 |  | 0 | 420 | 0 | 7 | 80 | 41 | 274 | 0 | 0 | 0 | 100 | 93 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 19 | 25 | 27 | 33 | 33 | 0 | 0 | 44 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 73 | 12 | 18 | 5 | 0 | 0 | 80 | 260 | 0 | 182 | 8 | 85 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 2 | 25 | 15 | 134 | 125 | 0 | 16 | 0 | 89 | 30 | 47 | 49 | 130 | 200 | 65 | 40 | 0 | 152 | 18 | 0 | 9 | 290 | 24 | 8 | 0 | 300 | 0 | 0 | 170 | 0 | 133 | 2 | 100 | 0 | 10 | 0 | 8 | 33 | 0 | 1 | 307 | 0 | 0 | 0 | 105 | 100 | 0 | 17 |  | 921 | 0 | 335 | 0 | 49 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 142 | 0 | 76 | 0 | 153 | 0 | 388 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 109 | 430 |  | 6041 | 3004 | 9045 | 3324 | 921 | 1983 | 1936 | 580 | 44 | 120 | 134 | 3 | 0 | 95.48
17:00 | 0 | 0 | 0 | 115 | 200 | 87 | 40 | 350 | 330 |  | 0 | 330 | 0 | 7 | 80 | 41 | 301 | 0 | 0 | 0 | 100 | 93 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 19 | 25 | 27 | 33 | 33 | 0 | 0 | 43 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 84 | 12 | 19 | 6 | 0 | 0 | 80 | 270 | 0 | 193 | 8 | 95 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 25 | 15 | 122 | 123 | 0 | 16 | 0 | 89 | 30 | 50 | 49 | 110 | 202 | 64 | 40 | 0 | 152 | 18 | 0 | 9 | 285 | 24 | 8 | 0 | 300 | 0 | 0 | 150 | 0 | 131 | 2 | 100 | 0 | 10 | 0 | 8 | 33 | 0 | 0 | 307 | 0 | 0 | 0 | 112 | 100 | 0 | 17 |  | 921 | 0 | 340 | 0 | 49 | 120 | 0 | 0 | 4 | 7 | 0 | 60 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 130 | 0 | 78 | 0 | 166 | 0 | 412 | 0 | 0 | 0 | 0 | 34 | 0 | 1 | 109 | 430 |  | 6004 | 3047 | 9051 | 3405 | 921 | 1919 | 1928 | 579 | 43 | 131 | 122 | 3 | 0 | 95.5
18:00 | 0 | 0 | 0 | 115 | 200 | 93 | 40 | 341 | 270 |  | 0 | 300 | 0 | 7 | 80 | 41 | 301 | 0 | 0 | 0 | 100 | 93 | 16 | 27 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 25 | 22 | 33 | 33 | 24 | 0 | 42 | 35 | 120 | 0 | 6 | 0 | 0 | 0 | 0 |  | 0 | 0 | 85 | 10 | 84 | 17 | 19 | 3 | 0 | 0 | 80 | 265 | 0 | 199 | 8 | 96 | 29 | 5 | 0 | 51 | 0 | 22 | 3 | 18 | 8 | 25 | 15 | 146 | 124 | 0 | 16 | 0 | 87 | 30 | 50 | 49 | 110 | 143 | 40 | 10 | 0 | 152 | 18 | 0 | 9 | 285 | 24 | 8 | 0 | 300 | 0 | 0 | 170 | 0 | 131 | 0 | 100 | 6 | 18 | 0 | 12 | 43 | 4 | 0 | 307 | 16 | 0 | 80 | 113 | 100 | 0 | 17 |  | 922 | 0 | 290 | 0 | 115 | 120 | 0 | 0 | 8 | 10 | 40 | 60 | 26 | 80 | 0 | 0 | 0 | 27 | 5 | 50 | 0 | 0 | 40 | 16 | 24 | 0 | 10 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 130 | 0 | 77 | 0 | 130 | 0 | 348 | 35 | 0 | 12 | 0 | 42 | 0 | 0 | 109 | 430 |  | 6287 | 3313 | 9600 | 3223 | 922 | 1744 | 2502 | 579 | 77 | 407 | 146 | 0 | 0 | 95.51
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 115 | 200 | 94 | 67 | 355 | 353 |  | 0 | 350 | 0 | 7 | 95 | 41 | 286 | 0 | 0 | 0 | 100 | 93 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 27 | 33 | 33 | 52 | 0 | 41 | 35 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 0 | 85 | 10 | 87 | 50 | 19 | 13 | 0 | 0 | 80 | 260 | 0 | 182 | 8 | 88 | 29 | 27 | 0 | 51 | 0 | 32 | 25 | 18 | 8 | 25 | 15 | 154 | 124 | 0 | 16 | 0 | 89 | 30 | 50 | 49 | 110 | 140 | 55 | 50 | 0 | 219 | 18 | 0 | 9 | 290 | 24 | 11 | 0 | 300 | 0 | 40 | 194 | 51 | 131 | 0 | 100 | 101 | 76 | 0 | 90 | 84 | 17 | 0 | 307 | 54 | 0 | 100 | 113 | 100 | 0 | 17 |  | 921 | 0 | 330 | 0 | 115 | 160 | 0 | 0 | 9 | 0 | 40 | 60 | 31 | 80 | 0 | 0 | 0 | 43 | 35 | 98 | 0 | 0 | 43 | 52 | 26 | 0 | 10 | 11 | 0 | 0 | 150 | 0 | 12 | 0 | 0 | 168 | 0 | 77 | 89 | 160 | 0 | 386 | 53 | 0 | 55 | 0 | 100 | 0 | 0 | 109 | 520 |  | 7405 | 3943 | 11348 | 3392 | 921 | 2025 | 3417 | 670 | 76 | 693 | 154 | 0 | 0 | 95.52
19:30 | 0 | 0 | 0 | 115 | 200 | 94 | 68 | 339 | 353 |  | 0 | 350 | 0 | 20 | 95 | 41 | 300 | 0 | 0 | 0 | 100 | 93 | 150 | 90 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 33 | 52 | 0 | 40 | 35 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 85 | 0 | 90 | 18 | 19 | 17 | 0 | 0 | 80 | 260 | 0 | 189 | 8 | 96 | 29 | 27 | 0 | 51 | 0 | 36 | 34 | 18 | 8 | 25 | 20 | 158 | 125 | 0 | 16 | 0 | 89 | 30 | 50 | 49 | 110 | 140 | 65 | 50 | 0 | 219 | 18 | 0 | 9 | 300 | 24 | 11 | 0 | 300 | 0 | 0 | 195 | 0 | 131 | 0 | 100 | 101 | 105 | 0 | 90 | 84 | 17 | 0 | 307 | 54 | 0 | 100 | 113 | 100 | 0 | 17 |  | 921 | 0 | 330 | 0 | 115 | 180 | 0 | 0 | 12 | 0 | 40 | 60 | 32 | 64 | 0 | 0 | 0 | 43 | 35 | 96 | 0 | 0 | 43 | 52 | 33 | 15 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 135 | 0 | 76 | 100 | 160 | 0 | 412 | 53 | 0 | 90 | 0 | 113 | 0 | 0 | 109 | 540 |  | 7354 | 4030 | 11384 | 3391 | 921 | 2081 | 3355 | 690 | 75 | 713 | 158 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 115 | 200 | 94 | 67 | 340 | 353 |  | 0 | 350 | 0 | 17 | 95 | 41 | 293 | 0 | 0 | 0 | 100 | 93 | 150 | 86 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 27 | 33 | 33 | 52 | 0 | 40 | 35 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 85 | 0 | 90 | 19 | 19 | 21 | 0 | 0 | 80 | 260 | 0 | 183 | 8 | 90 | 29 | 38 | 0 | 51 | 0 | 41 | 32 | 18 | 8 | 25 | 21 | 160 | 124 | 0 | 16 | 0 | 88 | 30 | 50 | 49 | 110 | 140 | 55 | 50 | 0 | 219 | 18 | 0 | 9 | 290 | 24 | 11 | 0 | 300 | 0 | 0 | 195 | 0 | 131 | 0 | 100 | 101 | 105 | 0 | 90 | 84 | 17 | 0 | 307 | 54 | 0 | 100 | 113 | 100 | 0 | 17 |  | 920 | 0 | 330 | 0 | 115 | 180 | 0 | 0 | 18 | 0 | 40 | 60 | 32 | 64 | 0 | 0 | 0 | 43 | 35 | 96 | 0 | 0 | 47 | 52 | 33 | 20 | 10 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 130 | 0 | 75 | 100 | 160 | 0 | 420 | 53 | 0 | 92 | 0 | 112 | 0 | 0 | 109 | 540 |  | 7306 | 4046 | 11352 | 3335 | 920 | 2097 | 3348 | 689 | 75 | 728 | 160 | 0 | 0 | 95.53
21:00 | 0 | 0 | 0 | 115 | 200 | 94 | 67 | 339 | 354 |  | 0 | 350 | 0 | 41 | 97 | 41 | 286 | 0 | 0 | 0 | 100 | 93 | 150 | 86 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 28 | 33 | 33 | 52 | 0 | 41 | 35 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 85 | 0 | 91 | 19 | 20 | 28 | 0 | 0 | 80 | 275 | 0 | 182 | 8 | 96 | 29 | 48 | 0 | 51 | 0 | 41 | 34 | 18 | 8 | 25 | 21 | 158 | 124 | 0 | 16 | 0 | 89 | 30 | 50 | 49 | 110 | 142 | 67 | 50 | 0 | 219 | 18 | 0 | 9 | 295 | 24 | 11 | 0 | 300 | 0 | 0 | 194 | 0 | 131 | 0 | 100 | 0 | 105 | 0 | 90 | 84 | 17 | 0 | 307 | 54 | 0 | 100 | 113 | 100 | 0 | 17 |  | 921 | 0 | 320 | 0 | 115 | 165 | 0 | 0 | 23 | 0 | 40 | 60 | 32 | 64 | 0 | 0 | 0 | 43 | 26 | 96 | 0 | 0 | 43 | 52 | 32 | 20 | 10 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 130 | 0 | 76 | 60 | 160 | 0 | 404 | 53 | 0 | 94 | 0 | 113 | 0 | 0 | 109 | 540 |  | 7284 | 3961 | 11245 | 3354 | 921 | 2105 | 3238 | 689 | 76 | 704 | 158 | 0 | 0 | 95.54
22:00 | 0 | 0 | 0 | 115 | 200 | 95 | 67 | 339 | 353 |  | 0 | 350 | 0 | 41 | 97 | 55 | 293 | 0 | 0 | 0 | 100 | 93 | 150 | 85 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 28 | 33 | 33 | 52 | 0 | 41 | 35 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 85 | 0 | 90 | 19 | 20 | 32 | 0 | 0 | 80 | 275 | 0 | 182 | 8 | 94 | 29 | 50 | 0 | 51 | 0 | 27 | 34 | 18 | 8 | 28 | 21 | 156 | 124 | 0 | 16 | 0 | 89 | 30 | 50 | 49 | 110 | 140 | 67 | 50 | 0 | 205 | 18 | 0 | 9 | 290 | 24 | 11 | 0 | 300 | 0 | 0 | 195 | 0 | 131 | 0 | 100 | 0 | 105 | 0 | 90 | 84 | 0 | 0 | 307 | 34 | 0 | 100 | 113 | 100 | 0 | 17 |  | 921 | 0 | 315 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 60 | 33 | 48 | 0 | 0 | 0 | 43 | 0 | 96 | 0 | 0 | 43 | 52 | 32 | 22 | 10 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 130 | 0 | 76 | 40 | 160 | 0 | 409 | 35 | 0 | 94 | 0 | 113 | 0 | 0 | 109 | 540 |  | 7229 | 3816 | 11045 | 3341 | 921 | 2114 | 3152 | 689 | 76 | 596 | 156 | 0 | 0 | 95.55
23:00 | 0 | 0 | 0 | 115 | 200 | 95 | 67 | 341 | 354 |  | 0 | 400 | 0 | 16 | 97 | 55 | 283 | 0 | 0 | 0 | 100 | 93 | 133 | 86 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 33 | 33 | 16 | 0 | 41 | 35 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 44 | 0 | 75 | 0 | 20 | 41 | 0 | 0 | 80 | 275 | 0 | 218 | 8 | 86 | 29 | 50 | 0 | 51 | 0 | 0 | 34 | 18 | 8 | 28 | 21 | 152 | 125 | 0 | 16 | 0 | 88 | 30 | 50 | 49 | 163 | 140 | 67 | 86 | 0 | 205 | 18 | 0 | 9 | 285 | 24 | 11 | 0 | 300 | 0 | 0 | 194 | 0 | 131 | 0 | 100 | 0 | 105 | 0 | 105 | 84 | 3 | 0 | 307 | 34 | 0 | 87 | 113 | 100 | 0 | 17 |  | 921 | 0 | 310 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 40 | 59 | 30 | 48 | 0 | 0 | 0 | 43 | 0 | 96 | 0 | 0 | 43 | 52 | 32 | 20 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 148 | 0 | 77 | 10 | 166 | 0 | 400 | 35 | 0 | 94 | 0 | 113 | 0 | 0 | 109 | 468 |  | 7233 | 3704 | 10937 | 3398 | 921 | 2245 | 3016 | 618 | 76 | 511 | 152 | 0 | 0 | 95.56
24:00 | 0 | 0 | 0 | 115 | 200 | 95 | 67 | 339 | 355 |  | 0 | 400 | 0 | 74 | 97 | 55 | 289 | 0 | 0 | 0 | 100 | 93 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 88 | 0 | 20 | 40 | 0 | 0 | 80 | 315 | 0 | 217 | 8 | 96 | 29 | 50 | 0 | 51 | 0 | 0 | 16 | 18 | 8 | 25 | 21 | 144 | 125 | 0 | 16 | 0 | 88 | 30 | 50 | 49 | 163 | 142 | 67 | 86 | 0 | 205 | 18 | 0 | 9 | 285 | 24 | 11 | 0 | 300 | 0 | 0 | 194 | 0 | 131 | 0 | 100 | 0 | 105 | 0 | 115 | 34 | 17 | 0 | 307 | 34 | 0 | 0 | 113 | 100 | 0 | 17 |  | 921 | 0 | 300 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 40 | 60 | 30 | 48 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 179 | 0 | 77 | 0 | 177 | 0 | 395 | 0 | 0 | 35 | 0 | 113 | 0 | 0 | 109 | 500 |  | 6914 | 3443 | 10357 | 3483 | 921 | 2241 | 2660 | 650 | 42 | 216 | 144 | 0 | 0 | 95.57
KWH | 0 | 0 | 0 | 2772000 | 4781200 | 2169318 | 1379840 | 8424888 | 7817000 |  | 0 | 8743750 | 0 | 355200 | 2073600 | 1084599 | 7108049 | 0 | 0 | 0 | 1545600 | 2235744 | 771840 | 560379 | 0 | 0 | 0 | 645120 | 726133 | 651309 | 410112 | 600000 | 628200 | 760300 | 826700 | 261780 | 0 | 951360 | 184000 | 2800000 | 0 | 63340 | 0 | 0 | 0 | 0 |  | 0 | 0 | 466474 | 18480 | 1262400 | 303360 | 451488 | 484800 | 0 | 0 | 2183924 | 7267500 | 0 | 4609000 | 234181 | 2184540 | 643608 | 573120 | 0 | 1264187 | 0 | 156320 | 257784 | 401832 | 164700 | 619000 | 463050 | 3224640 | 3293080 | 0 | 371088 | 6650 | 2088000 | 707160 | 1191000 | 1173888 | 3276245 | 4301000 | 1520064 | 1728960 | 0 | 4709500 | 422000 | 0 | 203580 | 7197800 | 565512 | 210000 | 0 | 6536179 | 0 | 61332 | 4598400 | 58946 | 3077280 | 68715 | 2411520 | 251040 | 1244509 | 0 | 1227600 | 963216 | 125454 | 15360 | 7085673 | 418380 | 0 | 547200 | 2526720 | 2404800 | 479100 | 432960 |  | 22117818 | 0 | 7352352 | 0 | 1988160 | 3107520 | 0 | 0 | 49490 | 12544 | 300750 | 1315000 | 567061 | 664128 | 0 | 0 | 0 | 223041 | 93796 | 805712 | 0 | 0 | 263128 | 264480 | 171380 | 330960 | 226944 | 158922 | 0 | 0 | 3692600 | 0 | 8000 | 0 | 0 | 3911218 | 0 | 1853917 | 383040 | 4268473 | 0 | 9350963 | 315360 | 0 | 674592 | 0 | 1768320 | 0 | 3128 | 2388768 | 12317500 |  | 156065660 | 80949065 | 237014725 | 83772560 | 22117818 | 49767514 | 54763635 | 16010100 | 1135360 | 6129245 | 3224640 | 93853 | 0
Fuel Cost | 0 | 0 | 0 | 4074840 | 5307132 | 2863499.76 | 2345728 | 8509136.88 | 8051510 |  | 0 | 9530687.5 | 0 | 2695968 | 14287104 | 9175707.54 | 7392370.96 | 0 | 0 | 0 | 11638368 | 20389985.28 | 7594905.6 | 5166694.38 | 0 | 0 | 0 | 4709376 | 5613008.09 | 6421906.74 | 307584 | 450000 | 0 | 0 | 0 | 2531412.6 | 0 | 256867.2 | 49680 | 5068000 | 0 | 588428.6 | 0 | 0 | 0 | 0 |  | 0 | 0 | 4524797.8 | 176484 | 10982880 | 2402611.2 | 568874.88 | 1439856 | 0 | 0 | 3210368.28 | 5377950 | 0 | 4240280 | 302093.49 | 2512221 | 727277.04 | 802368 | 0 | 2161759.77 | 0 | 1578832 | 2461837.2 | 510326.64 | 123525 | 1083250 | 347287.5 | 24184800 | 3490664.8 | 0 | 471281.76 | 106001 | 3424320 | 1131456 | 2119980 | 1831265.28 | 3734919.3 | 4473040 | 2994526.08 | 3302313.6 | 0 | 8147435 | 924180 | 0 | 415303.2 | 7269778 | 424134 | 159600 | 0 | 49413513.24 | 0 | 1025471.04 | 23911680 | 985577.12 | 30280435.2 | 803278.35 | 19653888 | 2723784 | 8773788.45 | 0 | 11195712 | 9102391.2 | 1092704.34 | 0 | 53567687.88 | 3644089.8 | 0 | 5461056 | 21653990.4 | 16015968 | 0 | 0 |  | 127398631.68 | 0 | 7719969.6 | 0 | 15626937.6 | 43070227.2 | 0 | 0 | 519150.1 | 131461.12 | 3133815 | 1485950 | 878944.55 | 6481889.28 | 0 | 0 | 0 | 2194723.44 | 952967.36 | 7130551.2 | 0 | 0 | 2549710.32 | 2562811.2 | 1662386 | 635443.2 | 351763.2 | 120303.954 | 0 | 0 | 20013892 | 0 | 228240 | 0 | 0 | 5162807.76 | 0 | 2780875.5 | 6515510.4 | 4994113.41 | 0 | 9257453.37 | 3292358.4 | 0 | 6401878.08 | 0 | 13722163.2 | 0 | 34564.4 | 17652995.52 | 54073825 |  | 518464793.97 | 368738313.044 | 887203107.014 | 94934206.544 | 127398631.68 | 60075541.72 | 433133866.98 | 74087717 | 306547.2 | 72137952.14 | 24184800 | 943843.75 | 0
Yesterday Day Peak | 0 | 0 | 0 | 115 | 200 | 90 | 66 | 340 | 310 |  | 0 | 380 | 0 | 7 | 97 | 41 | 273 | 0 | 0 | 0 | 100 | 93 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 39 | 2 | 0 | 8 | 0 | 0 | 100 | 270 | 0 | 182 | 8 | 85 | 29 | 20 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 25 | 15 | 120 | 145 | 0 | 16 | 1 | 89 | 30 | 49 | 46 | 163 | 211 | 66 | 84 | 0 | 205 | 18 | 0 | 9 | 290 | 24 | 8 | 0 | 300 | 0 | 0 | 195 | 0 | 130 | 11 | 90 | 0 | 20 | 0 | 24 | 50 | 0 | 2 | 306 | 0 | 0 | 0 | 113 | 100 | 0 | 17 |  | 921 | 0 | 310 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 10 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 184 | 0 | 78 | 0 | 196 | 0 | 354 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 109 | 430 |  | 9468 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 115 | 200 | 94 | 68 | 339 | 353 | 0 | 0 | 350 | 0 | 20 | 95 | 41 | 300 | 0 | 0 | 0 | 100 | 93 | 150 | 90 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 33 | 52 | 0 | 40 | 35 | 120 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 90 | 18 | 19 | 17 | 0 | 0 | 80 | 260 | 0 | 189 | 8 | 96 | 29 | 27 | 0 | 51 | 0 | 36 | 34 | 18 | 8 | 25 | 20 | 158 | 125 | 0 | 16 | 0 | 89 | 30 | 50 | 49 | 110 | 140 | 65 | 50 | 0 | 219 | 18 | 0 | 9 | 300 | 24 | 11 | 0 | 300 | 0 | 0 | 195 | 0 | 131 | 0 | 100 | 101 | 105 | 0 | 90 | 84 | 17 | 0 | 307 | 54 | 0 | 100 | 113 | 100 | 0 | 17 |  | 921 | 0 | 330 | 0 | 115 | 180 | 0 | 0 | 12 | 0 | 40 | 60 | 32 | 64 | 0 | 0 | 0 | 43 | 35 | 96 | 0 | 0 | 43 | 52 | 33 | 15 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 135 | 0 | 76 | 100 | 160 | 0 | 412 | 53 | 0 | 90 | 0 | 113 | 0 | 0 | 109 | 540 |  | 11384 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 115 | 200 | 94 | 68 | 412 | 0 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 | 0 | 0 | 100 | 93 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 70 | 35 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 100 | 90 | 50 | 20 | 30 | 0 | 0 | 80 | 360 | 0 | 225 | 8 | 100 | 30 | 50 | 0 | 51 | 0 | 42 | 34 | 18 | 8 | 25 | 21 | 173 | 160 | 0 | 16 | 0 | 90 | 30 | 51 | 44 | 163 | 250 | 65 | 86 | 0 | 0 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 85 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 17 |  | 931 | 16 | 315 | 0 | 115 | 225 | 0 | 0 | 30 | 60 | 40 | 60 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 0 | 0 | 43 | 52 | 34 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 200 | 0 | 76 | 100 | 220 | 0 | 414 | 105 | 200 | 90 | 100 | 113 | 0 | 0 | 113 | 580
Forecast for Day | 0 | 0 | 0 | 115 | 200 | 94 | 68 | 412 | 0 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 | 0 | 0 | 100 | 93 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 40 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 100 | 90 | 50 | 20 | 8 | 0 | 0 | 80 | 360 | 0 | 225 | 8 | 100 | 30 | 50 | 0 | 51 | 0 | 0 | 34 | 18 | 8 | 25 | 21 | 162 | 160 | 0 | 16 | 1.6 | 90 | 30 | 51 | 44 | 163 | 250 | 65 | 86 | 0 | 0 | 18 | 0 | 10 | 341 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 200 | 150 | 0 | 115 | 85 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 17 |  | 931 | 0 | 315 | 0 | 115 | 225 | 0 | 0 | 0 | 0 | 40 | 60 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 52 | 0 | 22 | 10 | 9 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 200 |  | 76 | 50 | 220 | 0 | 414 | 105 | 100 | 90 | 100 | 100 | 0 | 8 | 113 | 580
Generation at 08:00(Today) | 0 | 0 | 0 | 115 | 200 | 94 | 40 | 341 | 0 | 0 | 0 | 350 | 0 |  | 30 | 16 | 270 | 0 | 0 | 0 | 35 | 50 | 0 | 4 | 0 | 0 | 0 | 54 | 17 | 17 | 19 | 25 | 29 | 33 | 33 | 0 | 0 | 40 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 6 | 0 | 0 | 80 | 275 | 0 | 220 | 8 | 85 | 29 | 50 | 0 | 25 | 0 | 0 | 0 | 17 | 5 | 25 | 15 | 106 | 158 | 0 | 16 | 0 | 89 | 3 | 50 | 49 | 110 | 140 | 40 | 20 | 0 | 0 | 18 | 0 | 9 | 290 | 24 | 8 | 0 | 126 | 0 | 0 | 160 | 0 | 91 | 5 | 100 | 0 | 7 | 0 | 2 | 17 | 0 | 1 | 251 | 23 | 0 | 0 | 66 | 100 | 0 | 17 | 0 | 929 | 0 | 310 | 0 | 34 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 161 | 0 | 41 | 0 | 162 | 0 | 334 | 0 | 0 | 0 | 0 | 35 | 0 | 1 | 50 | 400 | 0
199
| Minimum Generation |  | 8503 | 7:00
| Highest Generation |  | 11384 | 19:30
| Day Peak Generation |  | 9468 | 12:00
| Evening Peak Generation |  | 11384 | 19:30
| HVDC Max Flow |  | 937 | 1:00
| HVDC EvPeak Flow |  | 921 | 19:30
| Load factor L.F |  | 86.75%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-09-24
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-09-23 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9468 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 7827 | MW
Evening Peak Generation : |  | 11384 | MW Hour : | 19:30 | Available Max Generation : |  | 13620 | MW
E.P. Demand (at gen end) : |  | 11384 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 11400 | MW
Maximum Generation : |  | 11384 | MW Hour : | 19:30 | Reserve(Generation end) |  | 2220 | MW
Total Gen. (MKWH) : |  | 237.0147 | System Load Factor : | 86.75% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 193 | MW at | 24:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-09-24
Actual : | 95.61 | Ft.(MSL) , | Rule curve : | 104.32 | Ft.( MSL )
Gas Consumed : | Total = | 1048.69 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 155009748.264
: |  | Coal : | 74087717 | Oil : | 505271819.12 | Total : | 734369284.384
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4076.3776 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1387.1252 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1242.9841 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1123.1999 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1014.987 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 819.0609 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 456.7803 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 210.8545 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 631.7062 |  |  | 0 | 0%
Total | 0 |  | 10963.0756 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 9) Meghnaghat summit
|  |  |  | 2) Bibiyana #3 | 10) Ashuganj (S)-360 MW
|  |  |  | 3) Ghorasal Unit-1,2,3,4 | 11) Sikalbaha-225 MW.
|  |  |  | 4) Ashuganj unit-3,4 | 12) Sikalbaha-150 MW.
|  |  |  | 5) Kaptai-2,4,5 | 13) Sylhet-225 MW
|  |  |  | 6) Raozan #1,2 | 14) Haripur-360 MW
7) Sirajganj #1
8) Baghabari-71 MW & 100 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Ruppur-Ishurdi 132 kV Ckt-2 was under shut down from 09:16 to 16:43 for C/M.
b) Benapole 132/33 kV T-1 transformer was under shut down from 07:35 to 08:59 for auxiliary fuse |  |  |  |  | About 10 MW power interruption occurred under Benapole S/S area
problem at 33 kV end. |  |  |  |  | from 07:35 to 08:59.
c) Bhandaria 132/33 kV T-1 transformer was shut down at 08:37 due to red hot maintenance at LT bus |  |  |  |  | About 10 MW power interruption occurred under Bhandaria S/S area
DS and was switched on at 10:12. |  |  |  |  | from 08:37 to 10:12.
d) Rangpur 132/33 kV T-2 transformer was under shut down from 08:02 to 16:45 for D/W. |  |  |  |  | About 60 MW power interruption occurred under Rangpur S/S area
from 08:02 to 16:45.
e) Bogura 132/33 kV T-3 & T-4 transformers tripped at 12:48 showing O/C as Y-phase loop of 33 kV |  |  |  |  | About 55 MW power interruption occurred under Bogura S/S area
Dupchachia feeder got snapped and were switched on at 18:48 & 13:32 respectively. |  |  |  |  | from 12:48 to 13:32.
f) Bibiyana(South)-400 MW tripped at 15:29 due to problem with GBC.
g) Norsingdi 132/33 kV T-2 transformer tripped at 19:49 showing mechanical protection trip and was |  |  |  |  | About 45 MW power interruption occurred under Norsingdi S/S area
switched on at 20:57. |  |  |  |  | from 19:49 to 20:57.
h) Tangail 132/33 kV T-4 transformer was under shut down from 07:10 to 09:28(24/9/20) for C/M.
i) Daudkandi 132/33 kV T-3 transformer along with 33 kV Bus were shut down at 07:05(24/9/20) for C/M
and were switched on at 08:12(24/9/20).
j) Mymensing 132/33 kV T-1 transformer along with 33 kV Bus were shut down at 07:18(24/9/20) due to |  |  |  |  | About 60 MW power interruption occurred under Mymensing S/S area
red hot maintenance at Bus and were switched on at 08:38(24/9/20). |  |  |  |  | from 07:18 to 08:38(24/9/20).
k) Haripur-360 MW CCPP ST & GT were forced shut down at 01:44 & 07:00(24/9/20) for maintenance.
l) Hasnabad 132/33 kV T-1,T-2 & T-5 transformers tripped at 06:49(24/9/20) due to 33 kV Pangaon |  |  |  |  | About 135 MW power interruption occurred under Hasnabad S/S area
feeder fault and were switched on at 07:19(24/9/20). |  |  |  |  | from 06:49 to 07:19(24/9/20).
m) Sylhet-225 MW tripped at 07:47(24/9/20) showing E/F relay.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-09-23 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 115 | 2772000 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 4781200 | Machine problem
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 68 | 1379840
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 94 | 2169318 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 339 | 8424888 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 353 | 7817000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 350 | 8743750 | Frequency control
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 20 | 355200 | Fuel Shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shorage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 95 | 2073600
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 41 | 1084599 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 90 | 560379 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 410112
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 1545600
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 7108049 | FGMO
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 2235744 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel Shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 645120 | High voltage
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 771840
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 726133
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 651309
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Machine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 52 | 1228200 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 760300
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 826700
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 52 | 261780
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 6536179
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 61332 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 58946
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 131 | 3077280 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 84 | 963216 | Engine problem
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 432960
| Dhaka area Total |  |  |  | 5895 | 3296 | 68462574
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2800000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 8 | 63340 | Engine problem
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 68715
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 18 | 303360 | Engine problem
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 75 | 1135360 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Gas shortage
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 17 | 125454 | Transformer O/L
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 466474
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 18480 | Reserve.
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2411520
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 451488
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 17 | 484800
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 90 | 1262400 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 15360
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 307 | 7085673
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 418380
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Transformer O/L
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2404800
| Chattogram area Total |  |  |  | 2266 | 1010 | 19515604
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 2183924 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 189 | 4609000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 260 | 7267500 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 643608 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 27 | 573120 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 234181 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1264187
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 105 | 1244509 | Engine problem
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 36 | 156320 | Engine problem
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 96 | 2184540
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 101 | 251040 | High voltage
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 401832
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 164700
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 158 | 3224640
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 619000
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 34 | 257784
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 463050
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 100 | 547200
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 2526720
| Cumilla Area Total |  |  |  | 2980 | 1458 | 28816855
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 125 | 3293080 | Machine problem & Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 371088 | Engine problem
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 0 | 0
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 6650
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 195 | 4598400 | High voltage
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 90 | 1227600 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 426 | 9496818
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 89 | 2088000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 707160 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 3276245 | Frequency control
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 140 | 4301000 | Gas shortage.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1191000
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 49 | 1173888
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 210000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 65 | 1520064
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 50 | 1728960 | Gas shortage.
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 219 | 4709500
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 422000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 565512
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7197800 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 203580
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 479100 | On test
| Sylhet Area Total |  |  |  | 1988 | 1164 | 29773809
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 921 | 22117818
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 1988160
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 12 | 49490 | Engine problem
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 180 | 3107520 | Low demand.
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 12544 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 330 | 7352352 | Gas Shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 300750
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 383040
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 315360 | Low demand.
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1751 | 35627034
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 64 | 664128 | Low demand.
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 32 | 567061
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 60 | 1315000 | GT-2 Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 76 | 1853917 | Engine problem
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 540 | 12317500 | Under maint unit 1
| Barisal Area Total |  |  |  | 1054 | 772 | 16717606
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 223041
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 35 | 93796 | Engine problem
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 43 | 263128
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | STG U/M & Gas Shortage
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 135 | 3911218 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 160 | 4268473 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 412 | 9350963 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 33 | 171380
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 15 | 330960 | Engine problem
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 10 | 226944
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 158922
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 264480
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 96 | 805712
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 90 | 674592 | Engine problem
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 2388768
| Rajshahi Area Total |  |  |  | 2183 | 1244 | 23132377
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3692600 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 8000
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1768320
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 3128
| Rangpur Area Total |  |  |  | 605 | 263 | 5472048
| Total |  |  |  | 19892 | 11384 | 237014725
| Eastern Grid Total |  |  |  | 13766 | 7354 | 156065660
| Western Grid Total |  |  |  | 6126 | 4030 | 80949065
| National Grid Total |  |  |  | 19892 | 11384 | 237014725
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-09-23
| (a) ENTIRE EASTERN GRID : |  | 7463 | MW | (b) ENTIRE WESTERN GRID : |  | 3476 | MW
| i) Dhaka area |  | 3981 | MW | i) Khulna area |  | 1382 | MW
| ii) Chittagong area |  | 1103 | MW | ii) Rajshahi area |  | 1162 | MW
| iii) Comilla area |  | 1071 | MW | iii) Barisal area |  | 322 | MW
| iv) Mymensingh area |  | 842 | MW | iv) Rangpur area |  | 610 | MW
| v) Sylhet area |  | 466 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 10939 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 122 | 12:00 | Sherpur | 100 | 22:00 | Jhenida | 106 | 20:00
| Munsiganj | 112 | 21:00 | Srimongal | 47 | 18:00 | Bottail | 128 | 19:00
| Sonargaon | 76 | 23:00 | Shahjibazar | 112 | 21:00 | G.K Project | 54 | 19:00
| Shyampur | 190 | 0:00 | Fenchuganj | 35 | 19:30 | Faridpur | 185 | 0.83333
| Bhulta | 194 | 2:00 | Kulawara | 41 | 18:00 | Madaripur | 86 | 0.875
| Madanganj | 48 | 1:00 | Sylhet | 123 | 18:30 | Sariatpur | 58 | 20:00
| Shitalakhya | 107 | 11:00 | Chatak | 27 | 21:00 | Gopalganj | 76 | 22:00
| Rahim steel | 23 | 6:00 | Sunamganj | 40 | 20:00 | Bagerhat | 93 | 19:30
| Matuail | 84 | 11:00 | Biani Bazar | 57 | 19:30 | Mongla | 38 | 16:00
| Ghorasal | 80 | 19:00 | Comilla (S) | 160 | 20:00 | Satkhira | 101 | 0.83333
| Narsingdi | 165 | 23:00 | Comilla(N) | 103 | 21:00 | Gallamari | 44 | 13:00
| Haripur (SBU) | 105 | 19:00 | Chandpur | 95 | 19:30 | Magura | 50 | 0.77083
| Ullon | 57 | 18:30 | Feni | 107 | 20:00 | Norail | 36 | 20:00
| Hasnabad | 193 | 19:00 | Chowmuhani | 166 | 18:30 | Chuadanga | 92 | 20:00
| Magbazar | 102 | 12:00 | Ashuganj | 56 | 19:30 | Barisal(N) | 38 | 0.8125
| Maniknagar | 96 | 12:00 | Daudkandi | 118 | 21:00 | Barisal (S) | 96 | 0.77083
| Bangabhaban | 34 | 10:00 | B.Baria | 146 | 20:00 | Patuakhali | 108 | 0.83333
| Narinda | 88 | 11:00 | Ramganj | 102 | 18:30 | Bhandaria | 52 | 0.83333
| Dhanmondi | 188 | 12:00 | Chaddagram | 33 | 20:00 | Borhan Uddin | 42 | 1:00
| Lalbag | 88 | 12:00 | PHP | 11 | 11:00 | Ishurdi | 59 | 19:00
| Madartek | 67 | 1:00 | Madunaghat | 55 | 18:30 | Ruppur Paromanobik | 2 | 20:00
| Dhaka University |  |  | Hathazari | 95 | 0.77083 | Natore | 110 | 18:30
| Fatullah | 41 | 0.5 | Khulshi | 198 | 0.5 | Bogra | 144 | 20:00
| Mirpur | 102 | 12:00 | Halishahar | 129 | 0.58333 | Noagaon | 105 | 20:00
| Kalyanpur | 90 | 18:30 | Baraulia | 145 | 0 | Rajshahi | 141 | 20:00
| Gulshan | 126 | 11:00 | Sikalbaha | 27 | 0.77083 | Rajshahi New | 12 | 20:00
| Uttara | 77 | 18:30 | Dohazari | 84 | 0.91667 | C.Nawabganj | 68 | 20:00
| Uttara New | 32 | 18:30 | Cox'sbazar | 96 | 0.79167 | Amnura | 42 | 20:00
| Kamrangirchar | 88 | 18:30 | Chandraghona | 30 | 0.77083 | Pabna | 116 | 20:00
| Savar | 141 | 12:00 | Kaptai | 4.2 | 0.77083 | Shahjadpur | 93 | 20:00
| Bhasantec | 149 | 12:00 | A. Khaer Stl. | 0 | 0.041667 | Serajganj | 96 | 19:30
| Agargaon | 70 | 12:00 | Bakulia | 100 | 0.77083 | Niyamatpur | 54 | 20:00
| Satmosjid | 95 | 18:30 | Julda | 21 | 0.041667 | Joypurhat | 56 | 19:30
| Tongi | 98 | 0.625 | TK chemical | 23.4 | 0.20833 | Sherpur(Bogura) | 44 | 20:00
| Kabirpur | 222 | 12:00 | Modern Steel | 15 | 0.083333 | Mohastangor | 50 | 18:30
| Basundhara | 124 | 12:00 | Shahmirpur | 23 | 0.625 | Rangpur | 126 | 20:00
| Manikganj | 64 | 0.875 | Khagrachhari | 26 | 0.75 | Lalmonirhat | 35 | 20:00
| Joydevpur | 147 | 21:00 | Matarbari | 33 | 0.75 | Saidpur | 88 | 18:30
| New Tongi | 117 | 10:00 | Baroiar Hat | 34 | 0.75 | Purbasadipur | 88 | 12:00
| Korda | 232 | 0:00 | Rangamati | 12 | 0.77083 | Thakurgaon | 62 | 19:00
| Dhamrai | 92 | 18:30 | Abul Khair 230 | 54 | 0.58333 | Palashbari | 109 | 19:30
| Rajendrapur | 100 | 21:00 | BSRM | 103 | 0.70833 | Barapukuria | 44 | 20:00
| Valuka | 118 | 21:00 | GPH Ispat | 76 | 0.29167 | Panchagar | 36 | 19:30
| Tangail | 193 | 19:00 | Goalpara | 22 | 0.875 | Joldhaka | 25 | 20:00
| Mymensing | 140 | 21:00 | Central s/s | 87 | 18:30 | Kurigram | 45 | 18:30
| Kishorganj | 132 | 23:00 | Noapara | 57 | 21:00
| Netrokona | 110 | 20:00 | Jessore | 112 | 19:00
| Jamalpur | 129 | 22:00 | Benapol | 40 | 18:30
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-09-23 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 393 | 23:00 | 388 | 16:00 | Kaliakoir | 376 | 0.375 | 365 | 0.33333
| Bheramara | 395 | 23:00 | 388 | 19:30 | Bhulta | 386 | 24:00 | 373 | 0.66667
| Ashuganj(N) | 392 | 24:00 | 380 | 11:00 | Gopalganj | 417 | 0.375 | 400 | 0.041667
| Payra | 415 | 22:00 | 407 | 22:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 230 | 1:00 | Comilla (N) | 232 | 18:00 | 226 | 11:00
| Ishurdi | 233 | 13:00 | 228 | 2:00 | Hathazari | 229 | 18:30 | 220 | 4:00
| Ashuganj | 235 | 1:00 | 230 | 8:00 | Megnaghat | 230 | 9:00 | 222 | 10:00
| Serajganj | 231 | 13:00 | 229 | 10:00 | Fenchuganj | 238 | 23:00 | 234 | 17:00
| Baghabari | 241 | 13:00 | 238 | 1:00 | Siddhirganj | 229 | 21:00 | 221 | 10:00
| Barapukuria | 239 | 13:00 | 235 | 10:00 | Maniknagar | 226 | 23:00 | 218 | 11:00
| Bogra | 229 | 13:00 | 223 | 10:00 | Agargaon | 224 | 7:00 | 215 | 11:00
| Rajshahi | 231 | 19:00 | 218 | 24:00 | Barisal | 249 | 18:30 | 238 | 1:00
| Khulna South | 237 | 18:00 | 226 | 1:00 | AKSML | 226 | 19:00 | 218 | 8:00
| Rampura | 228 | 24:00 | 220 | 11:00 | BSRM | 227 | 20:00 | 219 | 15:00
| Haripur | 224 | 23:00 | 218 | 10:00 | Bibiyana | 236 | 24:00 | 232 | 10:00
| Hasnabad | 225 | 18:00 | 218 | 9:00 | Bhulta | 229 | 19:00 | 220 | 17:00
| Shyampur | 223 | 22:00 | 214 | 11:00 | Ashuganj (S) | 233 | 19:00 | 227 | 11:00
| Aminbazar | 225 | 22:00 | 216 | 11:00 | Kaliakoir | 229 | 23:00 | 221 | 11:00
| Tongi | 224 | 21:00 | 213 | 8:00 | GPH | 224 | 23:00 | 217 | 15:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 130 | 0:00 | 125 | 11:00 | Hathazari | 137 | 0.77083 | 131 | 0.083333
| Munsiganj | 132 | 2:00 | 125 | 8:00 | Khulshi | 137 | 0.79167 | 130 | 0.20833
| Sonargaon | 130 | 20:00 | 125 | 9:00 | Halishahar | 139 | 0.77083 | 130 | 0.33333
| Shyampur | 131 | 19:00 | 126 | 10:00 | Baraulia | 137 | 0.77083 | 131 | 0.20833
| Bhulta | 124 | 18:00 | 118 | 11:00 | Sikalbaha | 140 | 18:00 | 129 | 0.33333
| Madanganj | 134 | 19:00 | 125 | 7:00 | Dohazari | 136 | 18:00 | 126 | 0.33333
| Shitalakhya | 140 | 18:30 | 130 | 11:00 | Cox'sbazar | 127 | 0.375 | 119 | 0.083333
| Rahim steal | 130 | 18:00 | 126 | 7:00 | Chandraghona | 138 | 0.79167 | 130 | 0.33333
| Matuail | 130 | 0:00 | 125 | 11:00 | Kaptai | 137 | 18:00 | 131 | 0.45833
| Ghorasal | 138 | 18:00 | 135 | 11:00 | A. Khaer Stl. | 135 | 0.79167 | 131 | 5:00
| Narsinghdi | 124 | 18:00 | 121 | 10:00 | Bakulia | 138 | 0.75 | 130 | 0.29167
| Haripur (SBU) | 130 | 23:00 | 125 | 11:00 | Julda | 140 | 0.77083 | 132 | 0.16667
| Ullon | 134 | 24:00 | 128 | 10:00 | TK Chemical | 139 | 0.79167 | 132 | 2:00
| Hasnabad | 136 | 19:00 | 128 | 10:00 | Modern Steel | 138 | 0.75 | 130 | 0.45833
| Magbazar | 134 | 1:00 | 127 | 11:00 | Shahmirpur | 139 | 0.79167 | 130 | 0.29167
| Maniknagar | 132 | 24:00 | 126 | 10:00 | Khagrachhari | 136 | 0.75 | 130 | 0.16667
| Bangabhaban | 132 | 24:00 | 126 | 10:00 | Matarbari | 130 | 0.77083 | 121 | 0.125
| Narinda | 132 | 24:00 | 126 | 10:00 | Baroiar Hat | 135 | 0.79167 | 128 | 0
| Dhanmondi | 134 | 24:00 | 128 | 10:00 | Rangamati | 137 | 0.75 | 131 | 4:00
| Lalbag | 136 | 18:30 | 124 | 11:00 | Goalpara S/S | 137 | 18:00 | 131 | 1:00
| Madartek | 134 | 1:00 | 127 | 11:00 | Khulna Central S/S | 138 | 0.75 | 131 | 1:00
| Dhaka University |  |  |  |  | Noapara | 135 | 18:00 | 127 | 2:00
| Fatuiiah | 131 | 0.75 | 126 | 11:00 | Jessore | 132 | 18:00 | 124 | 21:00
| Mirpur | 134 | 24:00 | 127 | 11:00 | Benapol | 132 | 18:00 | 124 | 21:00
| Kalyanpur | 134 | 23:00 | 128 | 10:00 | Jhenida | 129 | 0.375 | 118 | 22:00
| Gulshan | 133 | 3:00 | 127 | 9:00 | Bottail | 135 | 13:00 | 128 | 21:00
| Uttara | 134 | 24:00 | 125 | 11:00 | G.K Project | 140 | 0.375 | 136 | 21:00
| Uttara New | 133 | 21:00 | 125 | 10:00 | Faridpur | 134 | 9:00 | 127 | 1:00
| Kamrangirchar | 136 | 18:30 | 124 | 11:00 | Madaripur | 139 | 0.25 | 132 | 1:00
| Savar | 134 | 24:00 | 126 | 10:00 | Shariyatpur S/S | 139 | 0.29167 | 129 | 1:00
| Bhasantec | 135 | 24:00 | 128 | 11:00 | Gopalganj | 139 | 9:00 | 129 | 22:00
| Agargaon | 136 | 2:00 | 129 | 11:00 | Bagerhat | 135 | 18:00 | 126 | 3:00
| Satmosjid | 136 | 23:00 | 130 | 11:00 | Mongla | 129 | 0.54167 | 120 | 2:00
| Tongi | 135 | 0.875 | 127 | 9:00 | Satkhira | 136 | 0.75 | 127 | 1:00
| Kabirpur | 133 | 24:00 | 128 | 8:00 | Gallamari | 137 | 18:00 | 130 | 1:00
| Basundhara | 133 | 22:00 | 127 | 11:00 | Magura | 128 | 13:0 | 117 | 21:00
| Manikganj | 137 | 22:00 | 130 | 15:00 | Norail | 128 | 0.54167 | 115 | 22:00
| Joydevpur | 141 | 18:30 | 133 | 10:00 | Chuadanga | 126 | 13:00 | 109 | 21:00
| New Tongi | 134 | 0.875 | 127 | 16:00 | Barisal(N) | 141 | 6:00 | 134 | 1:00
| Kodda | 134 | 22:00 | 122 | 1904-01-02 | Barisal (S) | 139 | 0.25 | 133 | 1:00
| Dhamrai | 132 | 24:00 | 127 | 18:00 | Patuakhali(S) | 135 | 0.25 | 127 | 1:00
| Rajendrapur | 131 | 21:00 | 121 | 15:00 | Bhandaria | 130 | 18:00 | 120 | 22:00
| Valuka | 128 | 12:00 | 116 | 21:00 | Ishurdi | 138 | 13:00 | 134 | 2:00
| Tangail | 134 | 14:00 | 126 | 22:00 | Ruppur Paromanobik | 136 | 6:00 | 134 | 20:00
| Mymensing | 131 | 13:00 | 119 | 20:00 | Natore | 138 | 18:00 | 134 | 1:00
| Kishorganj | 131 | 8:00 | 122 | 20:00 | Bogra | 140 | 13:00 | 135 | 8:00
| Netrokona | 130 | 13:00 | 116 | 20:00 | Noagaon | 135 | 18:00 | 129 | 10:00
| Jamalpur | 138 | 12:00 | 130 | 20:00 | Rajshahi | 138 | 18:00 | 132 | 2:00
| Sherpur | 137 | 9:00 | 128 | 20:00 | Rajshahi New | 139 | 18:00 | 133 | 3:00
| Srimongal | 137 | 9:00 | 132 | 0.75 | C.Nawabganj | 136 | 18:00 | 130 | 11:00
| Shahjibazar | 135 | 6:00 | 131 | 0.75 | Amnura | 137 | 18:00 | 131 | 10:00
| Fenchuganj | 136 | 9:00 | 133 | 0.083333 | Pabna | 135 | 13:00 | 132 | 20:00
| Khulawara | 135 | 13:00 | 132 | 0.125 | Shahjadpur | 140 | 18:00 | 136 | 10:00
| Sylhet | 134 | 12:00 | 131 | 0.77083 | Serajganj | 136 | 18:30 | 132 | 20:00
| Chatak | 133 | 6:00 | 129 | 18:00 | Niyamatpur | 134 | 6:00 | 129 | 20:00
| Sunamganj | 133 | 9:00 | 127 | 0.8125 | Joypurhat | 134 | 6:00 | 130 | 20:00
| Biani Bazar | 134 | 13:00 | 128 | 0.77083 | Sherpur(Bogura) | 138 | 13:00 | 133 | 10:00
| Comilla(s) | 127 | 6:00 | 122 | 18:00 | Mohastangor | 138 | 13:00 | 133 | 8:00
| Comilla(n) | 137 | 18:00 | 132 | 10:00 | Rangpur | 135 | 13:00 | 128 | 19:00
| Chandpur | 135 | 19:30 | 130 | 21:00 | Lalmonirhat | 135 | 6:00 | 129 | 20:00
| Feni | 135 | 20:00 | 128 | 17:00 | Saidpur | 135 | 13:00 | 128 | 19:00
| Chowmuhani | 132 | 18:00 | 126 | 23:00 | Purbasadipur | 132 | 13:00 | 124 | 20:00
| Ashuganj | 136 | 14:00 | 133 | 1:00 | Thakurgaon | 130 | 6:00 | 123 | 20:00
| Daudkandi | 130 | 18:00 | 125 | 15:00 | Palashbari | 138 | 15:00 | 127 | 18:30
| B.Baria | 134 | 13:00 | 127 | 22:00 | Barapukuria | 139 | 13:00 | 135 | 18:00
| Ramganj | 130 | 19:00 | 123 | 21:00 | Panchagar | 130 | 13:00 | 120 | 19:30
| Chaddagram | 135 | 19:30 | 130 | 7:00 | Joldhaka | 135 | 13:00 | 126 | 20:00
| PHP | 135 | 18:30 | 127 | 4:00 | Kurigram | 135 | 13:00 | 126 | 18:30
| Madanhat | 140 | 18:00 | 133 | 5:00

## L-Curve
Date | 2020-09-23
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 193 | 6914 | 3443 | 10357 |  |  |  | QF-LDC-11
0:30 | 211.5 | 6929.5 | 3471 | 10400.5 | Date: | 2020-09-23
1:00 | 230 | 6945 | 3499 | 10444
1:30 | 231 | 6822 | 3439 | 10261
2:00 | 232 | 6699 | 3379 | 10078
2:30 | 244 | 6606.5 | 3351 | 9957.5 | [5 empty] | Gen. at Eve. Peak | 11384 | 11384 MW (19:30 )
3:00 | 256 | 6514 | 3323 | 9837 | [6 empty] | 19:30
3:30 | 273 | 6416.5 | 3289 | 9705.5 | [5 empty] | Gen. at Day Peak | 9468 | 9468 MW (12:00 )
4:00 | 290 | 6319 | 3255 | 9574 | [6 empty] | 12:00
4:30 | 315 | 6224 | 3242.5 | 9466.5 | [5 empty] | Highest Generation | 11384
5:00 | 340 | 6129 | 3230 | 9359 | [6 empty] | 19:30
5:30 | 383 | 5959.5 | 3155.5 | 9115
6:00 | 426 | 5790 | 3081 | 8871
6:30 | 441.5 | 5656.5 | 3030.5 | 8687
7:00 | 457 | 5523 | 2980 | 8503
7:30 | 464.5 | 5536 | 2978.5 | 8514.5
8:00 | 472 | 5549 | 2977 | 8526
8:30 | 477.5 | 5706 | 2961.5 | 8667.5
9:00 | 483 | 5863 | 2946 | 8809
9:30 | 500.5 | 6009 | 2960.5 | 8969.5
10:00 | 518 | 6155 | 2975 | 9130
10:30 | 552.5 | 6219.5 | 3018.5 | 9238
11:00 | 587 | 6284 | 3062 | 9346
11:30 | 565 | 6307 | 3100 | 9407
12:00 | 543 | 6330 | 3138 | 9468
12:30 | 535 | 6290 | 3075 | 9365
13:00 | 527 | 6250 | 3012 | 9262
13:30 | 501.5 | 6150.5 | 2924.5 | 9075
14:00 | 476 | 6051 | 2837 | 8888
14:30 | 498 | 6143.5 | 2876 | 9019.5
15:00 | 520 | 6236 | 2915 | 9151
15:30 | 606 | 6138.5 | 2959.5 | 9098
16:00 | 692 | 6041 | 3004 | 9045
16:30 | 638 | 6022.5 | 3025.5 | 9048
17:00 | 584 | 6004 | 3047 | 9051
17:30 | 526.5 | 6145.5 | 3180 | 9325.5
18:00 | 469 | 6287 | 3313 | 9600
18:30 | 377 | 6846 | 3628 | 10474
19:00 | 285 | 7405 | 3943 | 11348
19:30 | 324 | 7354 | 4030 | 11384
20:00 | 333 | 7306 | 4046 | 11352 |  |  |  | Executive Engineer
20:30 | 312.5 | 7295 | 4003.5 | 11298.5 |  |  |  | Network Operation Division
21:00 | 292 | 7284 | 3961 | 11245
21:30 | 281 | 7256.5 | 3888.5 | 11145
22:00 | 270 | 7229 | 3816 | 11045 |  |  |  |  | Page 6 of 7
22:30 | 276.5 | 7231 | 3760 | 10991
23:00 | 283 | 7233 | 3704 | 10937
23:30 | 238 | 7073.5 | 3573.5 | 10647
24:00 | 193 | 6914 | 3443 | 10357
11384 MW (19:30 )
9468 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-09-23 |  | Energy | 237014725
[10 empty] | 2020-09-23 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3483 | 921 | 2241 | 3016 | 650 | 42 | 216 | 0 | 144
0:30 | 3462.5 | 929 | 2234 | 2871 | 680 | 42 | 212 | 0 | 148 | Date: | 2020-09-23
1:00 | 3442 | 937 | 2227 | 2726 | 710 | 42 | 208 | 0 | 152
1:30 | 3451.5 | 936.5 | 2203.5 | 2564.5 | 710.5 | 42 | 201.5 | 0 | 151 | [7 empty] | Total Energy | 237.0147 | Total Energy Gen 237.015 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 237.015 MKWHr
2:00 | 3461 | 936 | 2180 | 2403 | 711 | 42 | 195 | 0 | 150 | [7 empty] | Energy not Served | 0
2:30 | 3479.5 | 929 | 2191.5 | 2292.5 | 690.5 | 42 | 182.5 | 0 | 150 | [7 empty] | Energy Requirement | 237.015
3:00 | 3498 | 922 | 2203 | 2182 | 670 | 42 | 170 | 0 | 150
3:30 | 3508.5 | 921.5 | 2207 | 2062.5 | 670 | 42 | 145 | 0 | 149 | [6 empty] | Shortage
4:00 | 3519 | 921 | 2211 | 1943 | 670 | 42 | 120 | 0 | 148
4:30 | 3542.5 | 921.5 | 2223 | 1803.5 | 670 | 42 | 120 | 0 | 144
5:00 | 3566 | 922 | 2235 | 1664 | 670 | 42 | 120 | 0 | 140
5:30 | 3535 | 921.5 | 2163.5 | 1547.5 | 649.5 | 42 | 120 | 0 | 136
6:00 | 3504 | 921 | 2092 | 1431 | 629 | 42 | 120 | 0 | 132
6:30 | 3486 | 921 | 2040.5 | 1327.5 | 624.5 | 41 | 120 | 0 | 126 |  |  |  |  | Coal
7:00 | 3468 | 921 | 1989 | 1224 | 620 | 40 | 120 | 0 | 120
7:30 | 3498.5 | 921 | 1980 | 1223 | 610 | 40 | 120 | 0 | 120 |  |  |  | Oil |  |  |  | ,
8:00 | 3529 | 921 | 1971 | 1222 | 600 | 40 | 120 | 0 | 120
8:30 | 3526 | 921 | 1988 | 1357 | 590 | 40 | 120 | 0 | 120
9:00 | 3523 | 921 | 2005 | 1492 | 580 | 40 | 120 | 0 | 120
9:30 | 3508.5 | 921 | 2027 | 1642 | 580 | 40 | 120 | 0 | 121
10:00 | 3494 | 921 | 2049 | 1792 | 580 | 40 | 120 | 0 | 122
10:30 | 3511.5 | 921 | 2066 | 1861.5 | 580 | 40.5 | 120 | 0 | 125
11:00 | 3529 | 921 | 2083 | 1931 | 580 | 41 | 120 | 0 | 128
11:30 | 3507 | 921 | 2065.5 | 2034.5 | 580 | 41.5 | 120 | 0 | 124
12:00 | 3485 | 921 | 2048 | 2138 | 580 | 42 | 120 | 0 | 120
12:30 | 3459 | 921 | 1920 | 2189.5 | 580 | 42 | 120 | 0 | 121
13:00 | 3433 | 921 | 1792 | 2241 | 580 | 42 | 120 | 0 | 122
13:30 | 3433 | 921 | 1792 | 2241 | 580 | 42 | 120 | 0 | 122
14:00 | 3433 | 921 | 1792 | 2241 | 580 | 42 | 120 | 0 | 122
14:30 | 3476.5 | 921 | 1843.5 | 2085.5 | 580 | 43 | 120 | 0 | 127
15:00 | 3520 | 921 | 1895 | 1930 | 580 | 44 | 120 | 0 | 132
15:30 | 3422 | 921 | 1939 | 1933 | 580 | 44 | 120 | 0 | 133
16:00 | 3324 | 921 | 1983 | 1936 | 580 | 44 | 120 | 0 | 134
16:30 | 3364.5 | 921 | 1951 | 1932 | 579.5 | 43.5 | 125.5 | 0 | 128
17:00 | 3405 | 921 | 1919 | 1928 | 579 | 43 | 131 | 0 | 122
17:30 | 3314 | 921.5 | 1831.5 | 2215 | 579 | 60 | 269 | 0 | 134
18:00 | 3223 | 922 | 1744 | 2502 | 579 | 77 | 407 | 0 | 146
18:30 | 3307.5 | 921.5 | 1884.5 | 2959.5 | 624.5 | 76.5 | 550 | 0 | 150
19:00 | 3392 | 921 | 2025 | 3417 | 670 | 76 | 693 | 0 | 154
19:30 | 3391 | 921 | 2081 | 3355 | 690 | 75 | 713 | 0 | 158
20:00 | 3335 | 920 | 2097 | 3348 | 689 | 75 | 728 | 0 | 160
20:30 | 3344.5 | 920.5 | 2101 | 3293 | 689 | 75.5 | 716 | 0 | 159
21:00 | 3354 | 921 | 2105 | 3238 | 689 | 76 | 704 | 0 | 158
21:30 | 3347.5 | 921 | 2109.5 | 3195 | 689 | 76 | 650 | 0 | 157
22:00 | 3341 | 921 | 2114 | 3152 | 689 | 76 | 596 | 0 | 156
22:30 | 3369.5 | 921 | 2179.5 | 3084 | 653.5 | 76 | 553.5 | 0 | 154
23:00 | 3398 | 921 | 2245 | 3016 | 618 | 76 | 511 | 0 | 152
23:30 | 3440.5 | 921 | 2243 | 3016 | 634 | 59 | 363.5 | 0 | 148 | Max Temp. in Dhaka |  | 30.7° C
24:00 | 3483 | 921 | 2241 | 3016 | 650 | 42 | 216 | 0 | 144
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
Total Energy Gen 237.015 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 237.015 MKWHr
Note on W13: Author:

## Generation
g | 2020-09-23
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 42 | 42 | 42 | 42 | 42 | 42 | 40 | 40 | 40 | 40 | 41 | 42 | 42 | 43 | 44 | 44 | 43 | 42 |  | 41 | 40 | 40 | 41 | 41 | 41 | 42 | 951360
2 | Karnaphuli Hydro PP Unit-4 & 5 | [17 empty] | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 |  | 184000
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 6 |  | 25 | 8 | 8 | 8 |  |  | 0 | 63340
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 0 | 1 | 5 | 9 | 9 | 11 | 9 | 13 | 5 | 2 | 2 | [9 empty] | 68715
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 85 |  | 85 | 85 | 85 | 85 | 85 | 44 | 0 | 466474
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 0 | [15 empty] | 4 |  | 17 | 17 | 17 | 17 |  | 3 | 17 | 125454
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [17 empty] | 22 |  | 32 | 36 | 41 | 41 | 27 |  |  | 156320
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 290 | 290 | 287 | 297 | 301 | 263 | 288 | 305 | 307 | 298 | 317 | 273 | 253 | 302 | 286 | 274 | 301 | 301 |  | 286 | 300 | 293 | 286 | 293 | 283 | 289 | 7108049
18 | Kodda 300 MW PP Unit-2 (Summit) | 300 | 300 | 300 | 300 | 145 | 145 | 145 | 145 | 163 | 261 | 298 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 6536179
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 234181
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2772000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4781200
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2183924
32 | Ashuganj 50 MW PP | 29 | 29 | 26 | 26 | 26 | 26 | 22 | 26 | 29 | 29 | 29 | 29 | 26 | 26 | 29 | 29 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 643608
33 | Ashuganj 225 MW CCPP | 189 | 182 | 182 | 184 | 195 | 182 | 182 | 194 | 182 | 188 | 184 | 182 | 182 | 198 | 184 | 182 | 193 | 199 |  | 182 | 189 | 183 | 182 | 182 | 218 | 217 | 4609000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 320 | 320 | 320 | 325 | 330 | 320 | 285 | 295 | 270 | 270 | 270 | 270 | 260 | 270 | 355 | 260 | 270 | 265 |  | 260 | 260 | 260 | 275 | 275 | 275 | 315 | 7267500
35 | Ashuganj 55 MW PP (Precision) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 5 | 5 | 5 | 5 | 5 |  | 27 | 27 | 38 | 48 | 50 | 50 | 50 | 573120
36 | Chandpur 150 MW CCPP | 90 | 95 | 91 | 96 | 96 | 86 | 85 | 96 | 88 | 96 | 94 | 85 | 86 | 96 | 95 | 85 | 95 | 96 |  | 88 | 96 | 90 | 96 | 94 | 86 | 96 | 2184540
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 355 | 335 | 344 | 340 | 348 | 343 | 339 | 340 | 351 | 340 | 345 | 340 | 338 | 339 | 362 | 342 | 350 | 341 |  | 355 | 339 | 340 | 339 | 339 | 341 | 339 | 8424888
40 | Meghnaghat 450 MW CCPP(MPL) | 420 | 420 | 420 | 420 | 400 | 400 | 350 | 350 | 350 | 350 | 350 | 380 | 340 | 310 | 310 | 420 | 330 | 300 |  | 350 | 350 | 350 | 350 | 350 | 400 | 400 | 8743750
41 | Haripur 360MW CCPP(HPL) | 351 | 355 | 352 | 353 | 352 | 309 | 289 | 289 | 289 | 310 | 310 | 310 | 265 | 250 | 310 | 310 | 330 | 270 |  | 353 | 353 | 353 | 354 | 353 | 354 | 355 | 7817000
42 | RPCL 210MW CCPP | 158 | 158 | 158 | 158 | 158 | 160 | 160 | 160 | 157 | 156 | 155 | 145 | 125 | 124 | 124 | 125 | 123 | 124 |  | 124 | 125 | 124 | 124 | 124 | 125 | 125 | 3293080
43
44 | Fenchugonj CCPP Phase-1 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 87 |  | 89 | 89 | 88 | 89 | 89 | 88 | 88 | 2088000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 707160
46 | Shajibazar 330 MW CCPP | 210 | 212 | 211 | 210 | 210 | 211 | 210 | 211 | 210 | 210 | 212 | 211 | 212 | 138 | 140 | 200 | 202 | 143 |  | 140 | 140 | 140 | 142 | 140 | 140 | 142 | 4301000
47 | Shahjibazar GTPP Unit- 8 & 9 | 66 | 66 | 65 | 65 | 65 | 65 | 65 | 66 | 67 | 66 | 66 | 66 | 67 | 50 | 65 | 65 | 64 | 40 |  | 55 | 65 | 55 | 67 | 67 | 67 | 67 | 1520064
48 | Shahjibazar 86MW PP (Shahjibazar) | 87 | 87 | 87 | 88 | 88 | 88 | 88 | 88 | 85 | 84 | 84 | 84 | 84 | 40 | 40 | 40 | 40 | 10 |  | 50 | 50 | 50 | 50 | 50 | 86 | 86 | 1728960
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 151 | 151 | 152 | 152 | 152 | 152 |  | 219 | 219 | 219 | 219 | 205 | 205 | 205 | 4709500
51 | Sylhet 20 MW GTPP | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 422000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 203580
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 210000
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 47 | 49 | 50 | 50 | 47 | 47 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1191000
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 565512
57 | Bibiana-II 341 MW CCPP (Summit) | 310 | 290 | 295 | 300 | 310 | 300 | 290 | 290 | 300 | 290 | 310 | 290 | 270 | 280 | 300 | 290 | 285 | 285 |  | 290 | 300 | 290 | 295 | 290 | 285 | 285 | 7197800
| Bibiyana South 400 MW | [12 empty] | 110 | 180 | 230 | [11 empty] | 479100
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 17 | 0 |  |  |  |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 17 | 651309
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 17 | 19 | 19 | 18 | 19 | 19 |  | 19 | 19 | 19 | 20 | 20 | 20 | 20 | 451488
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 22 |  |  |  | 19 | 19 | 410112
62 | Tangail 22 MW PP (Doreen) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 371088
63 | Impoprt (Tripura) | 152 | 150 | 150 | 148 | 140 | 132 | 120 | 120 | 120 | 122 | 128 | 120 | 122 | 130 | 132 | 134 | 122 | 146 |  | 154 | 158 | 160 | 158 | 156 | 152 | 144 | 3224640
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 36 | 38 | 42 | 9 | 31 | 8 | 5 | 5 | 5 | 8 | 8 | 7 | 3 | 5 | 6 | 3 |  | 13 | 17 | 21 | 28 | 32 | 41 | 40 | 484800
65 | Feni 22MW PP (Doreen) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 401832
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 2 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 164700
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 28 | 28 | 25 | 619000
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 17 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 20 | 21 | 21 | 21 | 21 | 21 | 463050
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 23 | 23 | 27 | 27 | 22 |  | 27 | 27 | 27 | 28 | 28 | 28 | 28 | 628200
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 760300
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 826700
73 | Ghorashal 108MW PP (Regent) | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 91 | 91 | 90 | 90 | 91 | 91 | 91 | 87 | 87 | 93 |  | 94 | 94 | 94 | 94 | 95 | 95 | 95 | 2169318
| Feni Lanka Power | [17 empty] | 80 |  | 100 | 100 | 100 | 100 | 100 | 87 | 0 | 547200
| Chowmuhani 113 MW | 113 | 113 | 113 | 113 | 113 | 98 | 47 | 46 | 88 | 113 | 105 | 113 | 113 | 107 | 107 | 105 | 112 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2526720
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) |  |  |  | 5 | 7 | 7 | 7 | 10 | 18 | 72 | 92 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1545600
78 | Gazipur 52 MW PP | [17 empty] | 24 |  | 52 | 52 | 52 | 52 | 52 | 16 |  | 261780
79 | Kodda 150MW PP | [17 empty] | 16 |  | 150 | 150 | 150 | 150 | 150 | 133 | 48 | 771840
80 | Jamalpur 95 MW PP(Powerpac) | [25 empty] | 0 | 0
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 0 | [15 empty] | 3 |  | 25 | 34 | 32 | 34 | 34 | 34 | 16 | 257784
| Gazipur 100 MW PP | 84 | 0 | [7 empty] | 30 | 50 | 50 | 50 | 33 | 33 | 33 | 33 | 43 |  | 84 | 84 | 84 | 84 | 84 | 84 | 34 | 963216
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 1 | 0 | 2 | 2 | 2 | 2 | 2 | 4 | 1 | 0 | [9 empty] | 15360
| Jodiac Power | 54 | 54 | 0 | [14 empty] | 16 |  | 54 | 54 | 54 | 54 | 34 | 34 | 34 | 418380
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | 97 | 97 | 97 | 97 | 64 | 55 | 48 | 48 | 54 | 90 | 97 | 97 | 97 | 80 | 80 | 80 | 80 | 80 |  | 95 | 95 | 95 | 97 | 97 | 97 | 97 | 2073600
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 24 | 0 | [15 empty] | 27 |  | 100 | 90 | 86 | 86 | 85 | 86 | 0 | 560379
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 9 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 20 | 17 | 41 | 41 | 16 | 74 | 355200
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 432960
88 | Ghorashal 78.5 MW PP(MAX) | 68 | 68 | 68 | 68 | 68 | 67 | 50 | 40 | 40 | 50 | 67 | 66 | 50 | 40 | 40 | 40 | 40 | 40 |  | 67 | 68 | 67 | 67 | 67 | 67 | 67 | 1379840
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [17 empty] | 10 |  | 10 | [5 empty] | 0 | 18480
92 | Fenchuganj 44MW (Energyprima) | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 46 | 46 | 46 | 46 | 49 | 49 | 49 | 49 | 49 |  | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1173888
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1264187
94 | Gagnagar 102 MW PP (Digital Power) | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 |  | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 2235744
95 | Patenga 50MW PP (Baraka) | 50 | 10 | 0 | [8 empty] | 2 | 24 | 24 | 19 | 12 | 12 | 17 |  | 50 | 18 | 19 | 19 | 19 |  | 0 | 303360
96 | Chattogram 108 MW PP (ECPV) | 84 | 82 | 45 | 0 |  |  |  |  | 1 | 12 | 12 | 39 | 74 | 64 | 64 | 73 | 84 | 84 |  | 87 | 90 | 90 | 91 | 90 | 75 | 88 | 1262400
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 30 | 30 | 30 | 34 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 55 | 55 | 55 | 1084599
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 17 | 0 |  |  |  |  | 17 | 17 | 17 | 55 | 55 | 17 | 17 | 17 | 17 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 726133
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 163 | 163 | 100 | 100 | 163 | 163 | 163 | 163 | 110 | 110 | 110 | 130 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 163 | 163 | 3276245
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 2 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 6650
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 0 |  |  |  |  | 17 | 17 | 17 | 54 | 54 | 17 | 17 | 17 | 17 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 645120
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko) | [19 empty] | 40 | [6 empty] | 61332
106 | Mymensingh 200 MW PP (United) | 194 | 194 | 194 | 193 | 193 | 200 | 200 | 200 | 200 | 200 | 200 | 195 | 200 | 200 | 170 | 170 | 150 | 170 |  | 194 | 195 | 195 | 194 | 195 | 194 | 194 | 4598400
112 | Aurahati 100MW PP (Aggreko) | [19 empty] | 51 | [5 empty] | 0 | 58946
114 | Kodda 149 MW PP Unit-1 (Summit) | 130 | 131 | 130 | 120 | 110 | 110 | 110 | 112 | 129 | 130 | 130 | 130 | 131 | 130 | 131 | 133 | 131 | 131 |  | 131 | 131 | 131 | 131 | 131 | 131 | 131 | 3077280
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 95 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2411520
116 | Chandpur 200MW (Desh energy) | [17 empty] | 6 |  | 101 | 101 | 101 |  |  |  | 0 | 251040
117 | Ashuganj 150MW PP (Midland) | 107 | 107 | 107 | 50 | 10 | 10 |  |  | 2 | 10 | 10 | 20 | 40 | 10 | 10 | 10 | 10 | 18 |  | 76 | 105 | 105 | 105 | 105 | 105 | 105 | 1244509
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 105 | 105 | 105 | 45 | 45 | 8 |  |  | 12 | 24 | 24 | 24 | 8 | 8 | 8 | 8 | 8 | 12 |  | 90 | 90 | 90 | 90 | 90 | 105 | 115 | 1227600
| Anwara 300 MW PP (United) | 307 | 307 | 307 | 307 | 307 | 215 | 199 | 197 | 307 | 304 | 307 | 306 | 306 | 306 | 307 | 307 | 307 | 307 |  | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 7085673
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2404800
120 | Eastern Zone Total | 6945 | 6699 | 6514 | 6319 | 6129 | 5790 | 5523 | 5549 | 5863 | 6155 | 6284 | 6330 | 6250 | 6051 | 6236 | 6041 | 6004 | 6287 |  | 7405 | 7354 | 7306 | 7284 | 7229 | 7233 | 6914 | 156065660
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 115 | 115 | 115 | 115 | 115 | 66 | 32 | 32 | 32 | 32 | 58 | 99 | 115 | 49 | 49 | 49 | 49 | 115 |  | 115 | 115 | 115 | 115 | 115 | 99 | 99 | 1988160
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 4 | 8 |  | 9 | 12 | 18 | 23 |  |  |  | 49490
| Khulna 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 160 | 180 | 180 | 165 | 120 | 120 | 120 | 3107520
129 | Rupsha 105 MW PP (Orion rupsha) | [17 empty] | 35 |  | 53 | 53 | 53 | 53 | 35 | 35 | 0 | 315360
130
131
132
133
| Barisal 110 MW PP (Summit ) | 80 | 80 | 32 | 16 | 0 | [12 empty] | 80 |  | 80 | 64 | 64 | 64 | 48 | 48 | 48 | 664128
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 77 | 77 | 77 | 76 | 76 | 77 | 78 | 76 | 78 | 77 | 78 | 78 | 78 | 77 | 77 | 76 | 78 | 77 |  | 77 | 76 | 75 | 76 | 76 | 77 | 77 | 1853917
| Bhola 225 MW CCPP |  | 30 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 59 | 60 | 1315000
140 | Bhola 33 MW PP (Venture) | 33 | 32 | 29 | 29 | 28 | 24 | 19 | 18 | 18 | 18 | 17 | 15 | 18 | 17 | 18 | 18 | 19 | 26 |  | 31 | 32 | 32 | 32 | 33 | 30 | 30 | 567061
141 | Noapara 100 MW PP (Bangla Trac) | [19 empty] | 89 | 100 | 100 | 60 | 40 | 10 | 0 | 383040
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 300750
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 7 | 10 | [8 empty] | 12544
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 937 | 936 | 922 | 921 | 922 | 921 | 921 | 921 | 921 | 921 | 921 | 921 | 921 | 921 | 921 | 921 | 921 | 922 |  | 921 | 921 | 920 | 921 | 921 | 921 | 921 | 22117818
147 | Bheramara 410 MW CCPP | 235 | 245 | 255 | 270 | 285 | 295 | 310 | 315 | 315 | 310 | 310 | 310 | 280 | 250 | 255 | 335 | 340 | 290 |  | 330 | 330 | 330 | 320 | 315 | 310 | 300 | 7352352
148 | Payra 1320 MW | 560 | 560 | 520 | 520 | 520 | 479 | 470 | 450 | 430 | 430 | 430 | 430 | 430 | 430 | 430 | 430 | 430 | 430 |  | 520 | 540 | 540 | 540 | 540 | 468 | 500 | 12317500
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 151 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 149 |  | 150 | 150 | 149 | 149 | 149 | 150 | 150 | 3692600
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 27 |  | 43 | 43 | 43 | 43 | 43 | 43 | 0 | 223041
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 168 | 168 | 168 | 161 | 159 | 159 | 147 | 152 | 162 | 154 | 164 | 184 | 164 | 130 | 130 | 142 | 130 | 130 |  | 168 | 135 | 130 | 130 | 130 | 148 | 179 | 3911218
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 178 | 179 | 179 | 175 | 181 | 182 | 167 | 163 | 171 | 163 | 174 | 196 | 173 | 130 | 130 | 153 | 166 | 130 |  | 160 | 160 | 160 | 160 | 160 | 166 | 177 | 4268473
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 395 | 365 | 395 | 395 | 395 | 345 | 380 | 399 | 368 | 399 | 400 | 354 | 284 | 340 | 417 | 388 | 412 | 348 |  | 386 | 412 | 420 | 404 | 409 | 400 | 395 | 9350963
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 5 |  | 35 | 35 | 35 | 26 |  |  |  | 93796
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 21 | 18 | 22 | 21 | 21 | 21 | 18 | 17 | 0 | [7 empty] | 15 | 20 | 20 | 22 | 20 | 21 | 330960
163 | Bogura 20 MW PP (Energyprima) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 226944
164 | Ullapara 11 MW PP (Summit) | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 158922
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [17 empty] | 40 |  | 43 | 43 | 47 | 43 | 43 | 43 | 0 | 263128
168 | Santahar 50 MW Peaking PP | [17 empty] | 24 |  | 26 | 33 | 33 | 32 | 32 | 32 |  | 171380
169 | Natore 52 MW PP (Rajlanka) | [17 empty] | 16 |  | 52 | 52 | 52 | 52 | 52 | 52 | 0 | 264480
170 | Chapainawabganj 100 MW Peaking PP | 88 | 75 | 50 | 0 | [13 empty] | 50 |  | 98 | 96 | 96 | 96 | 96 | 96 | 48 | 805712
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 0 | [15 empty] | 12 |  | 55 | 90 | 92 | 94 | 94 | 94 | 35 | 674592
172 | Confidence Power Bogura Unit-1 113 MW | 109 | 109 | 109 | 109 | 109 | 109 | 50 | 50 | 50 | 70 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 |  | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 2388768
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | [19 empty] | 12 | [6 empty] | 8000
176 | Rangpur 113 MW PP (Confidence) | 101 | 100 | 105 | 101 | 74 | 61 | 39 | 35 | 34 | 35 | 38 | 80 | 95 | 38 | 34 | 38 | 34 | 42 |  | 100 | 113 | 112 | 113 | 113 | 113 | 113 | 1768320
177 | Sympa Solar Power 8MW | [7 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | [9 empty] | 3128
178
178