## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-09-25 | Friday
|  |  | Date (day): | 2020-09-25 |  | Friday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13286.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14153 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-09-24 | 2020-09-25 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 115 | 115 | 115 | 75 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 200 | 200 | 165 |  | Machine problem
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 66 | 66 | 68 | 68 |  | 10 | Engine problem
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 88 | 90 | 94 | 94 |  | 14 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 341 | 344 | 412 | 412 |  |  | FGMO
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 353 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 380 | 420 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 100 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 95 | 97 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 40 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 50 | 50 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 0 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 302 | 262 | 335 | 335 |  |  | FGMO
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 90 | 93 | 93 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 150 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 54 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 52 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 293 | 300 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 149 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 84 | 93 | 85 | 85 |  | 20 | Engine problem
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 104 | 104 | 104 | 0 |  | Fuel shortage
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 2779 | 3462 | 3938 | 4228 | 1019 | 648
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 8 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 14 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 42 | 43 | 42 | 105 | 125 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 34 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 100 | 100
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 20 | 20 | 20
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 25 | 40 | 40
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 57 | 79 | 90 | 90 |  | 18 | Engine problem
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 270 | 307 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 813 | 1042 | 1376 | 1414 | 515 | 341
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 80 | 80 | 80 | 54 |  | Gas shortage
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 190 | 182 | 225 | 225 |  |  | FGMO
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 295 | 290 | 360 | 360 |  |  | FGMO
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 29 | 30 | 30 | 15 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 47 | 50 | 50 | 50
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 100 | 98 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 49 | 0 | 42
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 94 | 85 | 100 | 100 |  | 63 | ST under shut down
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 32 | 200 | 200
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 8 | 8 |  | 3 | Engine problem
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 120 | 150 | 162 | 173
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 25 | 25 | 25 |  | 8 | Engine problem
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 25 | 52 | 34 | 34 |  | 18 | Engine problem
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 17 | 21 | 21 | 21
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 100 | 114 | 114
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 113 | 113 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1225 | 1441 | 1749 | 2002 | 520 | 456
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 123 | 125 | 160 | 160 | 42 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 16 | 16 | 16 |  | 6 | Engine problem
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 0 | 0 | 0 |  | 95 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 200 | 200 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 8 | 105 | 115 | 115
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 348 | 446 | 492.6 | 491 | 42 | 101
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 89 | 90 | 90 | 90
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 35 | Unit-4 under shut down
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 142 | 142 | 142 | 142 |  |  | Gas shortage
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 44 | 53 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 46 | 47 | 47 | 47
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 51 | 68 | 65 | 65
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 84 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 145 | 145 | 145
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 280 | 341 | 341 |  |  | FGMO
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 962 | 1165 | 1224 | 1224 | 0 | 435
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 927 | 930 | 939 | 939
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 99 | 115 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 200 | 225 | 225
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 285 | 265 | 315 | 315
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 20 | 50 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 90 | 105 | 105
| 108 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1431 | 1660 | 1889 | 2045 | 0 | 0
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 48 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 17 | 29 | 33 | 33
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 15 | 86 | 86 | 86 |  | 134 | GT-2 & STG under shut down
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 78 | 78 | 78 | 78 |  | 17 | Engine problem
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 440 | 520 | 580 | 580
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 550 | 761 | 887 | 887 | 0 | 151
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 39 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 43 | 43 | 43
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | ST Under maint & gas shoratge
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 177 | 147 | 200 | 200 |  |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 201 | 156 | 220 | 220 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 388 | 365 | 414 | 414 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 33 | 0 | 34
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 18 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 10 | 10 | 10 | 10
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 9 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 16 | 52 | 52 | 52
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 98 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 60 | 110 | 90 | 90 |  | 23 | Engine problem
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 109 | 109 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 987 | 1241 | 1473 | 1599 | 271 | 233
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 146 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 91 | 113 | 100 | 113
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 244 | 259 | 258 | 263 | 294 | 40
|  | Total |  |  |  |  | 20383 | 19892 | 9339 | 11477 | 13286.6 | 14153 | 2661 | 2405
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8932.9565 | 10978 | 12708.9217 | 13537.6522
| A. |  | 2020-09-24 | (Yesterday) |  |  |  |  | Thursday
| 1 | Highest Generation : |  |  | 11477 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 7827 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11477 | MW
| 3 | Day peak Generation : |  |  | 9339 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10978 | MW
| 4 | Evening peak Generation : |  |  | 11477 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 232.1527 | MKWHr | By Solar | 0.12702 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 126.3466 | MKWHr |  | By Oil: | 63.8339 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 15.551 | MKWHr |  | By Hydro: | 0.95856 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2661 | MW | Dhaka | 4062 | 4062 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2405 | MW | Chittagong | 1076 | 1076 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5066 | MW | Khulna | 1407 | 1407 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1016.89 | MMCFD |  |  | Rajshahi | 1101 | 1101 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 145934313.366 | ii) Oil : | Taka | 519504200.96 | Comilla | 1018 | 1018 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 72060526 | Total | Taka | 737499040.326 | Mymensingh | 892 | 892 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.0165 | MKWHr. | Sylhet | 430 | 430 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 187 | MW (E to W) at | 19:00 | hrs | Barisal | 294 | 294 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 150 | MW at | 22:00 | hrs | Rangpur | 698 | 698 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 31.0° C |  |  | Total | 10978 | 10978 |  | 0
| B. |  | 2020-09-25 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 32.2° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 10500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14153 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 8500 | MW
| 4 | Reserve(Generation end) |  |  |  | 3653 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 212.3903 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7803 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.2713 | MKWHr. | ii) HVDC Flow at Peak Time |  | 930 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.0643 | MKWHr. | iii) Maximum HVDC Flow : |  | 930 | MW at | 19:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 95.61 |  | (b) Today: | 96.17 |  | (c) Rule Curve: |  | 104.56
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-09-24
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 115 | 200 | 95 | 68 | 338 | 354 |  | 0 | 400 | 0 | 85 | 97 | 55 | 298 | 0 | 0 | 0 | 100 | 93 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 43 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 91 | 0 | 20 | 41 | 0 | 0 | 80 | 315 | 0 | 217 | 8 | 96 | 29 | 50 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 25 | 21 | 140 | 125 | 0 | 16 | 0 | 87 | 30 | 50 | 49 | 163 | 141 | 67 | 86 | 0 | 205 | 18 | 0 | 9 | 290 | 24 | 11 | 0 | 268 | 0 | 0 | 194 | 0 | 131 | 0 | 100 | 0 | 50 | 0 | 85 | 0 | 17 | 0 | 307 | 17 | 0 | 0 | 107 | 100 | 0 | 17 |  | 928 | 0 | 300 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 176 | 0 | 77 | 0 | 176 | 0 | 410 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 109 | 500 |  | 6607 | 3324 | 9931 | 3485 | 928 | 2255 | 2285 | 650 | 43 | 145 | 140 | 0 | 0 | 95.58
2:00 | 0 | 0 | 0 | 115 | 200 | 94 | 68 | 352 | 174 |  | 0 | 420 | 0 | 87 | 48 | 55 | 304 | 0 | 0 | 0 | 100 | 93 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 43 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 51 | 0 | 20 | 41 | 0 | 0 | 80 | 335 | 0 | 216 | 8 | 85 | 29 | 50 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 25 | 21 | 130 | 143 | 0 | 16 | 0 | 87 | 30 | 50 | 49 | 163 | 142 | 67 | 86 | 0 | 205 | 18 | 0 | 9 | 295 | 24 | 8 | 0 | 200 | 0 | 0 | 193 | 0 | 111 | 0 | 100 | 0 | 10 | 0 | 85 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 106 | 100 | 0 | 17 |  | 928 | 0 | 300 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 187 | 0 | 76 | 0 | 187 | 0 | 409 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 109 | 500 |  | 6234 | 3295 | 9529 | 3548 | 928 | 2099 | 2011 | 650 | 43 | 120 | 130 | 0 | 0 | 95.59
3:00 | 0 | 0 | 0 | 115 | 200 | 95 | 68 | 343 | 184 |  | 0 | 420 | 0 | 93 | 30 | 55 | 295 | 0 | 0 | 0 | 100 | 93 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 44 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 41 | 0 | 0 | 80 | 315 | 0 | 217 | 8 | 93 | 29 | 50 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 25 | 21 | 116 | 145 | 0 | 16 | 0 | 87 | 30 | 50 | 46 | 163 | 140 | 67 | 87 | 0 | 205 | 18 | 0 | 9 | 290 | 24 | 8 | 0 | 200 | 0 | 0 | 183 | 0 | 98 | 0 | 100 | 0 | 5 | 0 | 24 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 107 | 100 | 0 | 17 |  | 928 | 0 | 295 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 183 | 0 | 76 | 0 | 182 | 0 | 407 | 0 | 0 | 0 | 0 | 71 | 0 | 0 | 109 | 480 |  | 6028 | 3238 | 9266 | 3505 | 928 | 2099 | 1824 | 630 | 44 | 120 | 116 | 0 | 0 | 95.6
4:00 | 0 | 0 | 0 | 115 | 200 | 95 | 68 | 340 | 184 |  | 0 | 420 | 0 | 98 | 30 | 30 | 292 | 0 | 0 | 0 | 92 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 44 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 0 | 0 | 80 | 315 | 0 | 219 | 8 | 90 | 29 | 51 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 25 | 21 | 116 | 161 | 0 | 16 | 0 | 87 | 30 | 50 | 49 | 163 | 140 | 67 | 87 | 0 | 205 | 18 | 0 | 9 | 290 | 24 | 8 | 0 | 145 | 0 | 0 | 200 | 0 | 86 | 0 | 100 | 0 | 5 | 0 | 24 | 0 | 0 | 0 | 254 | 0 | 0 | 0 | 84 | 100 | 0 | 17 |  | 928 | 0 | 295 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 182 | 0 | 76 | 0 | 181 | 0 | 400 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 109 | 480 |  | 5871 | 3200 | 9071 | 3512 | 928 | 2097 | 1624 | 630 | 44 | 120 | 116 | 0 | 0 | 95.6
5:00 | 0 | 0 | 0 | 115 | 200 | 94 | 68 | 341 | 184 |  | 0 | 420 | 0 | 100 | 30 | 30 | 295 | 0 | 0 | 0 | 60 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 43 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 0 | 0 | 80 | 315 | 0 | 218 | 8 | 94 | 29 | 51 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 25 | 21 | 112 | 160 | 0 | 16 | 0 | 87 | 30 | 50 | 49 | 163 | 143 | 67 | 87 | 0 | 205 | 18 | 0 | 9 | 285 | 24 | 8 | 0 | 145 | 0 | 0 | 200 | 0 | 86 | 0 | 100 | 0 | 5 | 0 | 8 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 84 | 100 | 0 | 17 |  | 928 | 0 | 295 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 169 | 0 | 75 | 0 | 172 | 0 | 405 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 109 | 480 |  | 5784 | 3125 | 8909 | 3499 | 928 | 2094 | 1483 | 630 | 43 | 120 | 112 | 0 | 0 | 95.61
6:00 | 0 | 0 | 0 | 115 | 200 | 94 | 68 | 340 | 184 |  | 0 | 420 | 0 | 75 | 30 | 15 | 285 | 0 | 0 | 0 | 7 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 41 | 0 | 0 | 80 | 275 | 0 | 218 | 8 | 88 | 29 | 50 | 0 | 51 | 0 | 0 | 0 | 17 | 8 | 25 | 21 | 108 | 160 | 0 | 16 | 0 | 88 | 30 | 50 | 49 | 163 | 140 | 67 | 87 | 0 | 205 | 18 | 0 | 9 | 280 | 24 | 8 | 0 | 145 | 0 | 0 | 200 | 0 | 86 | 0 | 100 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 55 | 100 | 0 | 17 |  | 928 | 0 | 295 | 0 | 32 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 160 | 0 | 76 | 0 | 158 | 0 | 330 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 470 |  | 5516 | 2909 | 8425 | 3416 | 928 | 2012 | 1179 | 620 | 42 | 120 | 108 | 0 | 0 | 95.61
7:00 | 0 | 0 | 0 | 115 | 200 | 94 | 40 | 338 | 14 |  | 0 | 380 | 0 | 22 | 30 | 15 | 287 | 0 | 0 | 0 | 7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 24 | 0 | 0 | 80 | 275 | 0 | 219 | 8 | 94 | 29 | 51 | 0 | 10 | 0 | 0 | 0 | 17 | 5 | 25 | 15 | 88 | 160 | 0 | 16 | 0 | 88 | 30 | 50 | 49 | 163 | 140 | 40 | 20 | 0 | 205 | 18 | 0 | 9 | 290 | 24 | 8 | 0 | 115 | 0 | 0 | 160 | 0 | 86 | 1 | 100 | 0 | 5 | 0 | 0 | 0 | 0 | 1 | 215 | 0 | 0 | 0 | 55 | 100 | 0 | 17 |  | 928 | 0 | 315 | 0 | 32 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 50 | 0 | 159 | 0 | 340 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 35 | 400 |  | 5007 | 2835 | 7842 | 3403 | 928 | 1641 | 1068 | 550 | 42 | 120 | 88 | 2 | 0 | 95.62
8:00 | 0 | 0 | 0 | 115 | 200 | 94 | 40 | 341 | 0 |  | 0 | 350 | 0 | 77 | 30 | 16 | 270 | 0 | 0 | 0 | 35 | 50 | 0 | 4 | 0 | 0 | 0 | 54 | 17 | 17 | 19 | 25 | 29 | 33 | 33 | 0 | 0 | 40 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 6 | 0 | 0 | 80 | 275 | 0 | 220 | 8 | 85 | 29 | 50 | 0 | 25 | 0 | 0 | 0 | 17 | 5 | 25 | 15 | 106 | 158 | 0 | 16 | 0 | 89 | 30 | 50 | 49 | 110 | 140 | 40 | 20 | 0 | 0 | 18 | 0 | 9 | 290 | 24 | 8 | 0 | 126 | 0 | 0 | 160 | 0 | 91 | 5 | 100 | 0 | 7 | 0 | 2 | 17 | 0 | 1 | 251 | 23 | 0 | 0 | 66 | 100 | 0 | 17 |  | 929 | 0 | 310 | 0 | 34 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 161 | 0 | 41 | 0 | 162 | 0 | 334 | 0 | 0 | 0 | 0 | 35 | 0 | 1 | 50 | 400 |  | 4992 | 2835 | 7827 | 3177 | 929 | 1519 | 1379 | 550 | 40 | 120 | 106 | 7 | 0 | 95.62
9:00 | 0 | 0 | 0 | 115 | 200 | 94 | 40 | 338 | 0 |  | 0 | 350 | 0 | 92 | 40 | 40 | 290 | 0 | 0 | 0 | 90 | 64 | 0 | 10 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 28 | 33 | 17 | 0 | 0 | 40 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 54 | 16 | 20 | 5 | 0 | 0 | 80 | 275 | 0 | 182 | 8 | 92 | 29 | 50 | 0 | 43 | 0 | 0 | 4 | 17 | 5 | 25 | 8 | 112 | 159 | 0 | 16 | 0 | 89 | 30 | 50 | 49 | 110 | 142 | 40 | 84 | 0 | 0 | 18 | 0 | 9 | 260 | 24 | 8 | 0 | 282 | 0 | 0 | 100 | 0 | 142 | 14 | 100 | 0 | 56 | 0 | 8 | 34 | 0 | 1 | 214 | 54 | 0 | 0 | 113 | 100 | 0 | 17 |  | 928 | 0 | 310 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 157 | 0 | 22 | 0 | 160 | 0 | 360 | 0 | 0 | 0 | 0 | 52 | 0 | 1 | 100 | 370 |  | 5518 | 2904 | 8422 | 3136 | 928 | 1578 | 1973 | 519 | 40 | 120 | 112 | 16 | 0 | 95.63
10:00 | 0 | 0 | 0 | 115 | 200 | 89 | 40 | 350 | 0 |  | 0 | 350 | 0 | 100 | 48 | 40 | 318 | 0 | 0 | 0 | 98 | 76 | 0 | 10 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 28 | 33 | 17 | 0 | 0 | 40 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 55 | 19 | 20 | 4 | 0 | 0 | 80 | 310 | 0 | 203 | 8 | 94 | 29 | 50 | 0 | 43 | 0 | 0 | 8 | 17 | 8 | 32 | 17 | 120 | 142 | 0 | 16 | 1 | 89 | 30 | 47 | 46 | 110 | 142 | 51 | 84 | 0 | 0 | 18 | 0 | 9 | 295 | 24 | 8 | 0 | 300 | 0 | 0 | 106 | 0 | 149 | 14 | 100 | 0 | 70 | 0 | 8 | 34 | 0 | 2 | 214 | 54 | 0 | 0 | 113 | 100 | 0 | 17 |  | 928 | 0 | 305 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 168 | 0 | 35 | 0 | 171 | 0 | 364 | 0 | 0 | 0 | 0 | 61 | 0 | 1 | 109 | 380 |  | 5751 | 2968 | 8719 | 3267 | 928 | 1616 | 2080 | 530 | 40 | 120 | 120 | 18 | 0 | 95.63
11:00 | 0 | 0 | 0 | 115 | 200 | 89 | 67 | 366 | 0 |  | 0 | 350 | 0 | 100 | 60 | 40 | 302 | 0 | 0 | 0 | 100 | 85 | 0 | 18 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 0 | 33 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 55 | 29 | 21 | 3 | 0 | 0 | 80 | 290 | 0 | 194 | 8 | 94 | 29 | 50 | 0 | 51 | 0 | 0 | 8 | 18 | 8 | 33 | 17 | 120 | 124 | 0 | 16 | 1 | 89 | 30 | 47 | 46 | 110 | 142 | 40 | 81 | 0 | 0 | 18 | 0 | 9 | 310 | 24 | 5 | 0 | 291 | 0 | 0 | 132 | 0 | 149 | 20 | 100 | 0 | 83 | 0 | 8 | 48 | 0 | 1 | 252 | 54 | 0 | 0 | 104 | 90 | 0 | 17 |  | 928 | 0 | 285 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 0 | 16 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 195 | 0 | 65 | 0 | 192 | 0 | 382 | 0 | 0 | 4 | 0 | 65 | 0 | 1 | 109 | 370 |  | 5872 | 3030 | 8902 | 3176 | 928 | 1709 | 2264 | 520 | 42 | 120 | 120 | 23 | 0 | 95.64
12:00 | 0 | 0 | 0 | 115 | 200 | 88 | 66 | 341 | 0 |  | 0 | 380 | 0 | 100 | 95 | 40 | 302 | 0 | 0 | 0 | 100 | 90 | 0 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 0 | 33 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 57 | 50 | 0 | 4 | 0 | 0 | 80 | 295 | 0 | 190 | 8 | 94 | 29 | 47 | 0 | 51 | 0 | 0 | 25 | 18 | 5 | 33 | 17 | 120 | 123 | 0 | 16 | 1 | 89 | 30 | 44 | 46 | 130 | 142 | 51 | 84 | 0 | 0 | 18 | 0 | 9 | 290 | 24 | 5 | 0 | 293 | 0 | 0 | 200 | 0 | 149 | 14 | 100 | 0 | 100 | 0 | 8 | 84 | 0 | 2 | 270 | 54 | 0 | 0 | 113 | 100 | 0 | 17 |  | 927 | 0 | 285 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 0 | 15 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 18 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 177 | 0 | 78 | 0 | 201 | 0 | 388 | 0 | 0 | 60 | 0 | 91 | 0 | 3 | 109 | 440 |  | 6127 | 3212 | 9339 | 3128 | 927 | 1758 | 2634 | 590 | 42 | 120 | 120 | 20 | 0 | 95.64
13:00 | 0 | 0 | 0 | 115 | 200 | 88 | 65 | 343 | 100 |  | 0 | 380 | 0 | 100 | 97 | 40 | 265 | 0 | 0 | 0 | 100 | 93 | 16 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 27 | 33 | 33 | 25 | 0 | 43 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 25 | 30 | 57 | 50 | 20 | 7 | 0 | 0 | 80 | 290 | 0 | 182 | 8 | 94 | 29 | 47 | 0 | 51 | 0 | 0 | 25 | 18 | 8 | 33 | 16 | 122 | 121 | 0 | 16 | 1 | 89 | 30 | 47 | 46 | 130 | 140 | 52 | 82 | 0 | 0 | 18 | 0 | 9 | 290 | 24 | 5 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 10 | 100 | 0 | 100 | 0 | 8 | 84 | 0 | 1 | 305 | 54 | 0 | 34 | 105 | 100 | 0 | 21 |  | 929 | 0 | 265 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 40 | 15 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 20 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 176 | 0 | 77 | 0 | 196 | 0 | 338 | 0 | 0 | 89 | 0 | 105 | 0 | 4 | 109 | 460 |  | 6404 | 3279 | 9683 | 3105 | 929 | 1812 | 2885 | 610 | 43 | 161 | 122 | 16 | 9683 | 95.65
14:00 | 0 | 0 | 0 | 115 | 200 | 88 | 65 | 339 | 195 |  | 0 | 350 | 0 | 100 | 87 | 40 | 248 | 0 | 0 | 0 | 100 | 93 | 0 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 27 | 33 | 33 | 25 | 0 | 43 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 51 | 10 | 55 | 50 | 20 | 5 | 0 | 0 | 80 | 285 | 0 | 182 | 8 | 85 | 29 | 45 | 0 | 51 | 0 | 0 | 34 | 18 | 8 | 25 | 16 | 128 | 101 | 0 | 16 | 1 | 89 | 30 | 47 | 49 | 110 | 141 | 40 | 40 | 0 | 50 | 18 | 0 | 9 | 255 | 24 | 3 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 100 | 0 | 8 | 84 | 0 | 2 | 306 | 54 | 0 | 0 | 107 | 100 | 0 | 36 |  | 928 | 0 | 250 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 40 | 15 | 19 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 20 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 168 | 0 | 77 | 0 | 175 | 0 | 326 | 0 | 0 | 70 | 0 | 109 | 0 | 2 | 109 | 470 |  | 6313 | 3188 | 9501 | 3035 | 928 | 1759 | 2787 | 620 | 43 | 196 | 128 | 5 | 0 | 95.65
15:00 | 0 | 0 | 0 | 115 | 200 | 88 | 65 | 339 | 300 |  | 0 | 350 | 0 | 100 | 97 | 40 | 274 | 0 | 0 | 0 | 100 | 93 | 0 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 27 | 33 | 33 | 0 | 0 | 44 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 34 | 10 | 50 | 50 | 20 | 3 | 0 | 0 | 80 | 260 | 0 | 182 | 8 | 96 | 29 | 46 | 0 | 51 | 0 | 0 | 16 | 18 | 5 | 25 | 16 | 132 | 101 | 0 | 16 | 0 | 89 | 30 | 47 | 47 | 110 | 140 | 40 | 40 | 0 | 100 | 18 | 0 | 9 | 260 | 24 | 5 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 20 | 0 | 8 | 34 | 0 | 2 | 307 | 54 | 0 | 0 | 107 | 100 | 0 | 45 |  | 928 | 0 | 250 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 8 | 86 | 17 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 20 | 10 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 152 | 0 | 77 | 0 | 168 | 0 | 342 | 0 | 0 | 35 | 0 | 113 | 0 | 2 | 109 | 470 |  | 6309 | 3196 | 9505 | 3143 | 928 | 1890 | 2566 | 619 | 44 | 179 | 132 | 4 | 0 | 95.66
16:00 | 0 | 0 | 0 | 115 | 200 | 85 | 65 | 351 | 351 |  | 0 | 330 | 0 | 100 | 97 | 40 | 282 | 0 | 0 | 0 | 100 | 93 | 0 | 10 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 27 | 33 | 33 | 0 | 0 | 44 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 6 | 0 | 13 | 18 | 0 | 12 | 0 | 0 | 80 | 260 | 0 | 182 | 8 | 91 | 29 | 46 | 0 | 43 | 0 | 0 | 0 | 18 | 8 | 25 | 16 | 122 | 102 | 0 | 16 | 0 | 90 | 30 | 52 | 47 | 110 | 143 | 40 | 40 | 0 | 150 | 18 | 0 | 9 | 280 | 24 | 5 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 6 | 100 | 0 | 20 | 0 | 8 | 34 | 0 | 0 | 307 | 54 | 0 | 0 | 106 | 100 | 0 | 72 |  | 928 | 0 | 250 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 0 | 86 | 20 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 152 | 0 | 78 | 0 | 171 | 0 | 354 | 0 | 0 | 0 | 0 | 113 | 0 | 1 | 109 | 450 |  | 6235 | 3140 | 9375 | 3196 | 928 | 1960 | 2368 | 599 | 44 | 151 | 122 | 7 | 0 | 95.66
17:00 | 0 | 0 | 0 | 115 | 200 | 84 | 65 | 352 | 351 |  | 0 | 380 | 0 | 100 | 97 | 15 | 280 | 0 | 0 | 0 | 70 | 93 | 10 | 10 | 0 | 0 | 0 | 17 | 17 | 17 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 46 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 18 | 18 | 19 | 15 | 0 | 0 | 80 | 260 | 0 | 182 | 8 | 86 | 29 | 48 | 0 | 43 | 0 | 0 | 0 | 18 | 8 | 25 | 16 | 118 | 125 | 0 | 16 | 0 | 90 | 30 | 50 | 47 | 163 | 144 | 45 | 40 | 0 | 150 | 18 | 0 | 9 | 290 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 2 | 100 | 0 | 20 | 0 | 8 | 34 | 0 | 0 | 215 | 54 | 0 | 0 | 84 | 100 | 0 | 104 |  | 928 | 0 | 250 | 0 | 32 | 120 | 0 | 0 | 0 | 2 | 0 | 86 | 16 | 0 | 0 | 0 | 0 | 25 | 9 | 40 | 0 | 0 | 0 | 0 | 7 | 20 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 151 | 0 | 78 | 0 | 174 | 0 | 351 | 0 | 0 | 0 | 0 | 60 | 0 | 1 | 109 | 420 |  | 6204 | 3047 | 9251 | 3247 | 928 | 2068 | 2041 | 570 | 46 | 230 | 118 | 3 | 0 | 95.67
18:00 | 0 | 0 | 0 | 115 | 200 | 89 | 66 | 325 | 286 |  | 0 | 360 | 0 | 100 | 97 | 28 | 296 | 0 | 0 | 0 | 75 | 93 | 84 | 35 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 28 | 33 | 33 | 40 | 0 | 44 | 0 | 120 | 0 | 15 | 0 | 0 | 0 | 0 |  | 0 | 0 | 71 | 10 | 30 | 50 | 0 | 24 | 0 | 0 | 80 | 280 | 0 | 186 | 8 | 94 | 29 | 45 | 0 | 51 | 0 | 18 | 16 | 18 | 8 | 25 | 18 | 140 | 125 | 0 | 16 | 0 | 89 | 30 | 53 | 47 | 110 | 142 | 68 | 40 | 0 | 135 | 18 | 0 | 10 | 270 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 46 | 43 | 0 | 19 | 60 | 18 | 0 | 280 | 54 | 0 | 52 | 103 | 100 | 0 | 104 |  | 928 | 0 | 260 | 0 | 66 | 150 | 0 | 0 | 0 | 7 | 40 | 86 | 25 | 16 | 0 | 0 | 0 | 33 | 39 | 80 | 0 | 0 | 29 | 43 | 33 | 20 | 10 | 8 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 142 | 0 | 77 | 0 | 130 | 0 | 283 | 50 | 0 | 70 | 0 | 62 | 0 | 0 | 109 | 400 |  | 6746 | 3344 | 10090 | 3213 | 928 | 1874 | 2799 | 548 | 44 | 544 | 140 | 0 | 0 | 95.69
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 115 | 200 | 90 | 66 | 344 | 353 |  | 0 | 420 | 0 | 100 | 97 | 40 | 262 | 0 | 0 | 0 | 100 | 93 | 150 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 29 | 33 | 33 | 52 | 0 | 43 | 0 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 102 | 0 | 79 | 50 | 20 | 25 | 0 | 0 | 80 | 290 | 0 | 182 | 8 | 85 | 29 | 50 | 0 | 51 | 0 | 49 | 52 | 18 | 8 | 25 | 21 | 150 | 125 | 0 | 16 | 0 | 90 | 30 | 53 | 47 | 163 | 142 | 68 | 84 | 0 | 145 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 32 | 98 | 0 | 105 | 93 | 34 | 0 | 307 | 54 | 0 | 100 | 113 | 100 | 0 | 104 |  | 930 | 0 | 265 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 86 | 29 | 48 | 0 | 0 | 0 | 50 | 39 | 98 | 0 | 0 | 43 | 52 | 33 | 18 | 10 | 11 | 0 | 0 | 146 | 0 | 0 | 0 | 0 | 147 | 0 | 78 | 20 | 156 | 0 | 365 | 90 | 0 | 110 | 0 | 113 | 0 | 0 | 109 | 520 |  | 7556 | 3921 | 11477 | 3253 | 930 | 2200 | 3471 | 666 | 43 | 764 | 150 | 0 | 0 | 95.71
19:30 | 0 | 0 | 0 | 115 | 200 | 90 | 66 | 339 | 353 |  | 0 | 420 | 0 | 100 | 97 | 40 | 298 | 0 | 0 | 0 | 100 | 93 | 115 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 29 | 33 | 33 | 52 | 0 | 43 | 0 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 102 | 0 | 89 | 19 | 20 | 25 | 0 | 0 | 80 | 290 | 0 | 188 | 8 | 95 | 29 | 50 | 0 | 51 | 0 | 0 | 52 | 18 | 8 | 25 | 21 | 148 | 125 | 0 | 16 | 0 | 90 | 30 | 53 | 47 | 163 | 140 | 60 | 84 | 0 | 145 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 98 | 0 | 95 | 103 | 17 | 0 | 307 | 54 | 0 | 50 | 113 | 100 | 0 | 104 |  | 929 | 0 | 265 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 86 | 30 | 48 | 0 | 0 | 0 | 50 | 4 | 96 | 0 | 0 | 43 | 25 | 33 | 21 | 10 | 11 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 144 | 0 | 78 | 20 | 184 | 0 | 410 | 90 | 0 | 113 | 0 | 113 | 0 | 0 | 109 | 520 |  | 7407 | 3932 | 11339 | 3315 | 929 | 2269 | 3327 | 665 | 43 | 643 | 148 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 115 | 200 | 90 | 66 | 339 | 353 |  | 0 | 420 | 0 | 98 | 97 | 40 | 295 | 0 | 0 | 0 | 100 | 92 | 115 | 52 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 29 | 33 | 33 | 52 | 0 | 41 | 0 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 102 | 0 | 90 | 19 | 20 | 30 | 0 | 0 | 80 | 280 | 0 | 184 | 8 | 95 | 29 | 48 | 0 | 51 | 0 | 0 | 52 | 18 | 8 | 28 | 21 | 150 | 124 | 0 | 17 | 0 | 90 | 30 | 53 | 47 | 163 | 140 | 60 | 84 | 0 | 145 | 18 | 0 | 10 | 275 | 24 | 11 | 0 | 290 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 98 | 0 | 95 | 103 | 17 | 0 | 307 | 54 | 0 | 50 | 113 | 100 | 0 | 104 |  | 929 | 0 | 265 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 86 | 31 | 48 | 0 | 0 | 0 | 50 | 0 | 96 | 0 | 0 | 47 | 25 | 33 | 21 | 10 | 11 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 147 | 0 | 78 | 20 | 186 | 0 | 418 | 90 | 0 | 113 | 0 | 113 | 0 | 0 | 109 | 560 |  | 7361 | 3988 | 11349 | 3306 | 929 | 2256 | 3317 | 707 | 41 | 643 | 150 | 0 | 0 | 95.73
21:00 | 0 | 0 | 0 | 115 | 200 | 89 | 66 | 339 | 354 |  | 0 | 420 | 0 | 100 | 97 | 40 | 275 | 0 | 0 | 0 | 100 | 93 | 115 | 74 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 29 | 33 | 33 | 52 | 0 | 41 | 0 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 102 | 0 | 90 | 19 | 20 | 37 | 0 | 0 | 80 | 280 | 0 | 182 | 8 | 85 | 29 | 48 | 0 | 51 | 0 | 0 | 52 | 18 | 8 | 28 | 21 | 148 | 122 | 0 | 17 | 0 | 89 | 30 | 53 | 47 | 163 | 140 | 60 | 84 | 0 | 145 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 285 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 98 | 0 | 95 | 93 | 17 | 0 | 307 | 54 | 0 | 50 | 113 | 100 | 0 | 104 |  | 929 | 0 | 255 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 86 | 32 | 32 | 0 | 0 | 0 | 50 | 0 | 96 | 0 | 0 | 43 | 25 | 33 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 144 | 0 | 77 | 20 | 176 | 0 | 394 | 90 | 0 | 113 | 0 | 108 | 0 | 0 | 109 | 560 |  | 7346 | 3919 | 11265 | 3248 | 929 | 2244 | 3306 | 710 | 41 | 639 | 148 | 0 | 0 | 95.76
22:00 | 0 | 0 | 0 | 115 | 200 | 89 | 66 | 339 | 354 |  | 0 | 420 | 0 | 100 | 97 | 40 | 270 | 0 | 0 | 0 | 100 | 93 | 98 | 79 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 29 | 33 | 33 | 25 | 0 | 41 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 40 | 0 | 91 | 19 | 20 | 40 | 0 | 0 | 80 | 280 | 0 | 182 | 8 | 86 | 29 | 54 | 0 | 51 | 0 | 0 | 52 | 18 | 8 | 33 | 21 | 144 | 121 | 0 | 17 | 0 | 89 | 30 | 53 | 47 | 163 | 140 | 60 | 84 | 0 | 145 | 18 | 0 | 10 | 275 | 24 | 11 | 0 | 293 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 98 | 0 | 95 | 85 | 17 | 0 | 307 | 54 | 0 | 0 | 113 | 100 | 0 | 104 |  | 930 | 0 | 250 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 86 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 144 | 0 | 78 | 20 | 175 | 0 | 393 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 109 | 560 |  | 7188 | 3783 | 10971 | 3242 | 930 | 2248 | 3222 | 710 | 41 | 434 | 144 | 0 | 0 | 95.79
23:00 | 0 | 0 | 0 | 115 | 200 | 89 | 66 | 340 | 324 |  | 0 | 350 | 0 | 97 | 97 | 40 | 304 | 0 | 0 | 0 | 95 | 93 | 84 | 83 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 29 | 33 | 33 | 0 | 0 | 40 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 91 | 19 | 20 | 42 | 0 | 0 | 80 | 300 | 0 | 197 | 8 | 96 | 29 | 55 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 21 | 144 | 123 | 0 | 17 | 0 | 89 | 30 | 53 | 47 | 130 | 140 | 57 | 84 | 0 | 145 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 102 | 0 | 95 | 85 | 17 | 0 | 307 | 54 | 0 | 0 | 113 | 100 | 0 | 104 |  | 929 | 0 | 250 | 0 | 115 | 165 | 0 | 0 | 0 | 0 | 40 | 86 | 31 | 16 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 151 | 0 | 79 | 0 | 170 | 0 | 414 | 70 | 0 | 0 | 0 | 113 | 0 | 0 | 109 | 560 |  | 7051 | 3586 | 10637 | 3323 | 929 | 2144 | 2968 | 710 | 40 | 379 | 144 | 0 | 0 | 95.83
24:00 | 0 | 0 | 0 | 115 | 200 | 87 | 66 | 361 | 349 |  | 0 | 420 | 0 | 100 | 97 | 40 | 291 | 0 | 0 | 0 | 95 | 93 | 48 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 29 | 33 | 33 | 0 | 0 | 41 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 91 | 0 | 0 | 42 | 0 | 0 | 80 | 280 | 0 | 182 | 8 | 94 | 29 | 55 | 0 | 51 | 0 | 0 | 0 | 18 | 5 | 33 | 21 | 140 | 123 | 0 | 17 | 0 | 89 | 30 | 53 | 47 | 110 | 140 | 63 | 84 | 0 | 145 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 98 | 0 | 95 | 50 | 17 | 0 | 307 | 54 | 0 | 0 | 113 | 100 | 0 | 104 |  | 929 | 0 | 250 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 86 | 31 | 16 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 162 | 0 | 78 | 0 | 168 | 0 | 416 | 53 | 0 | 0 | 0 | 113 | 0 | 0 | 109 | 560 |  | 6971 | 3531 | 10502 | 3283 | 929 | 2238 | 2863 | 710 | 41 | 298 | 140 | 0 | 0 | 95.87
KWH | 0 | 0 | 0 | 2740500 | 4793600 | 2142136 | 1464512 | 8369150 | 5009000 |  | 0 | 8874750 | 0 | 2269440 | 1784352 | 925611 | 7020858 | 0 | 0 | 0 | 2082240 | 2071008 | 691200 | 704392 | 0 | 0 | 0 | 872280 | 913882 | 776183 | 339984 | 600000 | 637560 | 767300 | 818800 | 303720 | 0 | 958560 | 0 | 2900000 | 0 | 55949 | 0 | 0 | 0 | 0 |  | 0 | 0 | 579472 | 67920 | 1170240 | 480480 | 413658 | 564000 | 0 | 0 | 1923456 | 7304000 | 0 | 4800000 | 267636 | 2177060 | 660456 | 1189920 | 0 | 1168242 | 0 | 59296 | 406997 | 418608 | 153900 | 637500 | 456480 | 3064320 | 3073640 | 0 | 362124 | 5650 | 2096000 | 726000 | 1201800 | 1157760 | 3449372 | 3150000 | 1286 | 1709760 | 0 | 2972160 | 425000 | 0 | 213660 | 7023500 | 576696 | 184000 | 0 | 6127198 | 0 | 0 | 4478400 | 0 | 3182690 | 89910 | 2402880 | 126720 | 1445236 | 0 | 994800 | 1128360 | 178981 | 12000 | 6553745 | 936693 | 0 | 307800 | 2455320 | 2389440 | 0 | 1261440 |  | 22271272 | 0 | 6920640 | 0 | 2034240 | 3363840 | 0 | 0 | 0 | 5248 | 371250 | 1832908 | 493328 | 320640 | 0 | 0 | 0 | 277949 | 76924 | 672008 | 0 | 0 | 167856 | 231360 | 145740 | 466560 | 220860 | 184428 | 0 | 0 | 3681200 | 0 | 0 | 0 | 0 | 4130618 | 0 | 1696781 | 100800 | 4425655 | 0 | 9039000 | 526560 | 0 | 941568 | 0 | 1978560 | 0 | 19461 | 2435040 | 11869800 |  | 151250629 | 80902094 | 232152723 | 78994025 | 22271272 | 47352577 | 57794415 | 15551000 | 958560 | 6039533 | 3064320 | 127021 | 0
Fuel Cost | 0 | 0 | 0 | 4028535 | 5320896 | 2827619.52 | 2489670.4 | 8452841.5 | 5159270 |  | 0 | 9673477.5 | 0 | 17225049.6 | 12294185.28 | 7830669.06 | 7301692.32 | 0 | 0 | 0 | 15679267.2 | 18887592.96 | 6801408 | 6494494.24 | 0 | 0 | 0 | 6367644 | 7064307.86 | 7653164.38 | 254988 | 450000 | 0 | 0 | 0 | 2936972.4 | 0 | 258811.2 | 0 | 5249000 | 0 | 519766.21 | 0 | 0 | 0 | 0 |  | 0 | 0 | 5620878.4 | 648636 | 10181088 | 3805401.6 | 521209.08 | 1675080 | 0 | 0 | 2827480.32 | 5404960 | 0 | 4416000 | 345250.44 | 2503619 | 746315.28 | 1665888 | 0 | 1997693.82 | 0 | 598889.6 | 3886821.35 | 531632.16 | 115425 | 1115625 | 342360 | 22982400 | 3258058.4 | 0 | 459897.48 | 90061 | 3437440 | 1161600 | 2139204 | 1806105.6 | 3932284.08 | 3276000 | 2533.42 | 3265641.6 | 0 | 5141836.8 | 930750 | 0 | 435866.4 | 7093735 | 432522 | 139840 | 0 | 46321616.88 | 0 | 0 | 23287680 | 0 | 31317669.6 | 1051047.9 | 19583472 | 1374912 | 10188913.8 | 0 | 9072576 | 10663002 | 1558924.51 | 0 | 49546312.2 | 8158596.03 | 0 | 3071844 | 21042092.4 | 15913670.4 | 0 | 0 |  | 128282526.72 | 0 | 7266672 | 0 | 15989126.4 | 46622822.4 | 0 | 0 | 0 | 54999.04 | 3868425 | 2071186.04 | 764658.4 | 3129446.4 | 0 | 0 | 0 | 2735018.16 | 781547.84 | 5947270.8 | 0 | 0 | 1626524.64 | 2241878.4 | 1413678 | 895795.2 | 342333 | 139611.996 | 0 | 0 | 19952104 | 0 | 0 | 0 | 0 | 5452415.76 | 0 | 2545171.5 | 1714608 | 5178016.35 | 0 | 8948610 | 5497286.4 | 0 | 8935480.32 | 0 | 15353625.6 | 0 | 215044.05 | 17994945.6 | 52108422 |  | 522309681.18 | 368069250.016 | 890378931.196 | 87930958.906 | 128282526.72 | 58003354.46 | 447301164.08 | 72060526 | 258811.2 | 72203036.88 | 22982400 | 1356152.95 | 0
Yesterday Day Peak | 0 | 0 | 0 | 115 | 200 | 88 | 66 | 341 | 0 |  | 0 | 380 | 0 | 100 | 95 | 40 | 302 | 0 | 0 | 0 | 100 | 90 | 0 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 0 | 33 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 57 | 50 | 0 | 4 | 0 | 0 | 80 | 295 | 0 | 190 | 8 | 94 | 29 | 47 | 0 | 51 | 0 | 0 | 25 | 18 | 5 | 33 | 17 | 120 | 123 | 0 | 16 | 1 | 89 | 30 | 44 | 46 | 130 | 142 | 51 | 84 | 0 | 0 | 18 | 0 | 9 | 290 | 24 | 5 | 0 | 293 | 0 | 0 | 200 | 0 | 149 | 14 | 100 | 0 | 100 | 0 | 8 | 84 | 0 | 2 | 270 | 54 | 0 | 0 | 113 | 100 | 0 | 17 |  | 927 | 0 | 285 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 0 | 15 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 18 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 177 | 0 | 78 | 0 | 201 | 0 | 388 | 0 | 0 | 60 | 0 | 91 | 0 | 3 | 109 | 440 |  | 9339 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 115 | 200 | 90 | 66 | 344 | 353 | 0 | 0 | 420 | 0 | 100 | 97 | 40 | 262 | 0 | 0 | 0 | 100 | 93 | 150 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 29 | 33 | 33 | 52 | 0 | 43 | 0 | 120 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 79 | 50 | 20 | 25 | 0 | 0 | 80 | 290 | 0 | 182 | 8 | 85 | 29 | 50 | 0 | 51 | 0 | 49 | 52 | 18 | 8 | 25 | 21 | 150 | 125 | 0 | 16 | 0 | 90 | 30 | 53 | 47 | 163 | 142 | 68 | 84 | 0 | 145 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 32 | 98 | 0 | 105 | 93 | 34 | 0 | 307 | 54 | 0 | 100 | 113 | 100 | 0 | 104 |  | 930 | 0 | 265 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 86 | 29 | 48 | 0 | 0 | 0 | 50 | 39 | 98 | 0 | 0 | 43 | 52 | 33 | 18 | 10 | 11 | 0 | 0 | 146 | 0 | 0 | 0 | 0 | 147 | 0 | 78 | 20 | 156 | 0 | 365 | 90 | 0 | 110 | 0 | 113 | 0 | 0 | 109 | 520 |  | 11477 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 115 | 200 | 94 | 68 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 | 0 | 0 | 100 | 93 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 70 | 35 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 100 | 90 | 50 | 20 | 40 | 0 | 0 | 80 | 360 | 0 | 225 | 8 | 100 | 30 | 50 | 0 | 51 | 0 | 42 | 34 | 18 | 8 | 25 | 21 | 173 | 160 | 0 | 16 | 0 | 90 | 30 | 51 | 47 | 163 | 142 | 65 | 86 | 0 | 145 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 85 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 104 |  | 939 | 16 | 315 | 0 | 115 | 225 | 0 | 0 | 30 | 60 | 40 | 86 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 0 | 0 | 43 | 52 | 34 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 200 | 0 | 78 | 100 | 220 | 0 | 414 | 105 | 200 | 90 | 100 | 113 | 0 | 0 | 113 | 580
Forecast for Day | 0 | 0 | 0 | 115 | 200 | 94 | 68 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 | 0 | 0 | 100 | 93 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 42 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 100 | 90 | 50 | 20 | 40 | 0 | 0 | 80 | 360 | 0 | 225 | 8 | 100 | 30 | 50 | 0 | 51 | 0 | 0 | 34 | 18 | 8 | 25 | 21 | 162 | 160 | 0 | 16 | 1.6 | 90 | 30 | 51 | 47 | 163 | 142 | 65 | 86 | 0 | 145 | 18 | 0 | 10 | 341 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 200 | 150 | 0 | 115 | 85 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 104 |  | 939 | 0 | 315 | 0 | 115 | 225 | 0 | 0 | 0 | 0 | 40 | 86 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 52 | 0 | 22 | 10 | 9 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 200 |  | 78 | 50 | 220 | 0 | 414 | 105 | 100 | 90 | 100 | 100 | 0 | 8 | 113 | 580
Generation at 08:00(Today) | 0 | 0 | 0 | 115 | 200 | 43 | 40 | 338 | 255 | 0 | 0 | 300 | 0 |  | 46 | 0 | 285 | 0 | 0 | 0 | 0 | 8 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 37 | 0 | 0 | 80 | 260 | 0 | 144 | 8 | 89 | 29 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 5 | 33 | 18 | 96 | 158 | 0 | 14 | 1 | 89 | 30 | 50 | 47 | 110 | 140 | 40 | 85 | 0 | 80 | 18 | 0 | 9 | 280 | 24 | 8 | 0 | 250 | 0 | 0 | 170 | 0 | 146 | 4 | 100 | 0 | 5 | 0 | 16 | 34 | 0 | 1 | 197 | 0 | 0 | 0 | 8 | 100 | 0 | 17 | 0 | 929 | 0 | 240 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 86 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 130 | 0 | 78 | 0 | 130 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 430 | 0
199
| Minimum Generation |  | 7827 | 8:00
| Highest Generation |  | 11477 | 19:00
| Day Peak Generation |  | 9339 | 12:00
| Evening Peak Generation |  | 11477 | 19:00
| HVDC Max Flow |  | 930 | 19:00
| HVDC EvPeak Flow |  | 930 | 19:00
| Load factor L.F |  | 84.28%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-09-25
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-09-24 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9339 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 7803 | MW
Evening Peak Generation : |  | 11477 | MW Hour : | 19:00 | Available Max Generation : |  | 14153 | MW
E.P. Demand (at gen end) : |  | 11477 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 10500 | MW
Maximum Generation : |  | 11477 | MW Hour : | 19:00 | Reserve(Generation end) |  | 3653 | MW
Total Gen. (MKWH) : |  | 232.1527 | System Load Factor : | 84.28% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 150 | MW at | 22:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-09-25
Actual : | 96.17 | Ft.(MSL) , | Rule curve : | 104.56 | Ft.( MSL )
Gas Consumed : | Total = | 1016.89 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 145934313.366
: |  | Coal : | 72060526 | Oil : | 519504200.96 | Total : | 737499040.326
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3742.1174 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1271.0348 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1138.5391 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1028.6717 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 929.6478 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 750.1891 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 421.3891 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 193.2043 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 578.5739 |  |  | 0 | 0%
Total | 0 |  | 10053.3674 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 9) Meghnaghat summit
|  |  |  | 2) Bibiyana #3 | 10) Ashuganj (S)-360 MW
|  |  |  | 3) Ghorasal Unit-1,2,3,4 | 11) Sikalbaha-225 MW.
|  |  |  | 4) Ashuganj unit-3,4 | 12) Sikalbaha-150 MW.
5) Kaptai-2,4,5
6) Raozan #1,2
7) Sirajganj #1
8) Baghabari-71 MW & 100 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Aminbazar 230/132 kV T-2 transformer was under shut down from 10:07 to 13:54 for A/M.
b) Bibiyana-Kaliakoir 400 kV Ckt-1 was under shut down from 08:22 to 16:41 for C/M.
c) Barapukuria 132/33 kV T-4 transformer tripped at 11:15 due to HV CB trip and was switched
on at 12:15.
d) After maintenance AES Haripur 360 MW GT & ST were synchronized at 12:15,13:26 respectively.
e) Bogura 132/33 kV T-2 transformer was under shut down from 12:01 to 12:54 due to 33 kV |  |  |  |  | About 10 MW power interruption occurred under Bogura S/S area
Dupchachia feeder DS problem. |  |  |  |  | from 12:01 to 12:54.
f) After maintenance Sylhet 225 MW CCPP GT was synchronized at 13:29.
g) Bogura 132/33 kV T-1 & T2 transformer tripped at 13:33 due to 33 kV Dupchachia feeder CT burst |  |  |  |  | About 60 MW power interruption occurred under Bogura S/S area
and were switched on at 14:08 |  |  |  |  | from 13:33 to 14:08.
h) Mymensing 132/33 kV T-2 transformer was under shut down from 15:30 to 17:40 for C/M.
i) After maintenance Bhola 225 MW CCPP STG was synchronized at 14:30.
j) After maintenance Shahjadpur 132/33 kV T1 transformer was switched on at 18:05.
k) Hasnabad 132/33 kV T-2 transformer was under shut down from 14:13 to 19:22 for C/M.
l) Bagerhat 132/33 kV T-1 transformer tripped at 22:23 from both side showing O/C relay at 132 kV side |  |  |  |  | About 50 MW power interruption occurred under Bagerhat S/S area
& E/F relay at 33 kV side due to 33 kV B-phase cable burst and was switched on at 09:34. |  |  |  |  | from 22:23 to 09:34(25-09-2020).
m) Bagerhat 132/33 kV T-2 transformer tripped at 22:23 from both side showing E/F relay from both side
and was switched on at 23:05.
n) Ashuganj 132 kV bus-2 was under shut down since 07:08 for C/M.
o) Ashuganj 225 MW CCPP ST was under shut down since 06:26 due to C/M maint of 132 kV bus-2.
p) Benapole 132/33 kV T1 transformer was under shut down from 07:27 to 10:03 for dropout fuse |  |  |  |  | About 10 MW power interruption occurred under Benapole S/S area
replacement of Auxiliary (33/0.4 kV) transformer . |  |  |  |  | from 07:27 to 10:03(25-09-2020).
q) AKSML S/S 230 kV bus coupler tripped at 05:28 showing O/C & L/O relay and was switched on at 07:02.
r) Ghorasal 230/132 bus-2 was shut down from 06:36 to 09:28(25-09-2020) for red hot maintenance.
s) BSRM- GPH 230 kV Ckt-2 tripped at 05:28 from BSRM end showing dist Z-2 and was switched on at
07:07(25-09-2020)
t) AKSML 230/33 kV transformer tripped at 05:30 due to bus PT fault and was switched on at 12:00(25-09-2020).
07:07(25-09-2020)
u) AKSML 230/33 kV transformer tripped at 05:30 due to bus PT fault and was switched on at 12:00(25-09-2020).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-09-24 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 115 | 2740500 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 4793600 | Machine problem
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 66 | 1464512 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 90 | 2142136 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 344 | 8369150 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 353 | 5009000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 8874750 | Frequency control
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 2269440
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shorage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 97 | 1784352 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 40 | 925611 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 50 | 704392 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 339984 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 2082240
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 262 | 7020858 | FGMO
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 2071008 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel Shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 872280
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 691200
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 913882
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 776183
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Machine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 54 | 1237560 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 767300
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 818800
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 52 | 303720
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 6127198
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3182690
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 93 | 1128360 | Engine problem
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 1261440
| Dhaka area Total |  |  |  | 5895 | 3462 | 68672146
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2900000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 8 | 55949 | Low demand.
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 89910
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 480480
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 43 | 958560 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Gas shortage
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 34 | 178981 | Transformer O/L
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 579472
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 67920 | Reserve.
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2402880
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 413658
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 25 | 564000
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 79 | 1170240 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 12000
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 307 | 6553745
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 936693
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Transformer O/L
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2389440
| Chattogram area Total |  |  |  | 2266 | 1042 | 19753928
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 1923456 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 182 | 4800000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 290 | 7304000 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 660456 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 50 | 1189920 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 267636 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1168242
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 98 | 1445236 | Engine problem
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 49 | 59296
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 85 | 2177060
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 32 | 126720 | High voltage
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 418608
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 153900
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 150 | 3064320
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 637500
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 406997
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 456480
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 100 | 307800
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 2455320
| Cumilla Area Total |  |  |  | 2980 | 1441 | 29022947
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 125 | 3073640 | Machine problem & Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 362124 | Engine problem
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 0 | 0 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 5650
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 4478400 | High voltage
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 105 | 994800 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 446 | 8914614
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 90 | 2096000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 726000 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3449372
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 142 | 3150000 | Gas shortage.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1201800
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 47 | 1157760
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 184000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 68 | 1286
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1709760 | Gas shortage.
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 145 | 2972160
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 425000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 576696
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7023500 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 213660
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1165 | 24886994
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 930 | 22271272
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 2034240
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine problem
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 200 | 3363840
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 5248 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 265 | 6920640 | Gas Shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 371250
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 20 | 100800 | Low demand.
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 90 | 526560 | Engine problem
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1660 | 35593850
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 320640 | Low demand.
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 29 | 493328
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 86 | 1832908 | GT-2 Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 78 | 1696781 | Engine problem
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 520 | 11869800 | Under maint unit 1
| Barisal Area Total |  |  |  | 1054 | 761 | 16213457
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 277949
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 39 | 76924 | Engine problem
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 43 | 167856
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | STG U/M & Gas Shortage
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 147 | 4130618 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 156 | 4425655 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 365 | 9039000 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 33 | 145740
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 18 | 466560 | Engine problem
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 10 | 220860
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 184428
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 231360
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 98 | 672008 | Engine problem
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 110 | 941568 | Engine problem
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 2435040
| Rajshahi Area Total |  |  |  | 2183 | 1241 | 23415566
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 146 | 3681200 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1978560
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 19461
| Rangpur Area Total |  |  |  | 605 | 259 | 5679221
| Total |  |  |  | 19892 | 11477 | 232152723
| Eastern Grid Total |  |  |  | 13766 | 7556 | 151250629
| Western Grid Total |  |  |  | 6126 | 3921 | 80902094
| National Grid Total |  |  |  | 19892 | 11477 | 232152723
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-09-24
| (a) ENTIRE EASTERN GRID : |  | 7478 | MW | (b) ENTIRE WESTERN GRID : |  | 3500 | MW
| i) Dhaka area |  | 4062 | MW | i) Khulna area |  | 1407 | MW
| ii) Chittagong area |  | 1076 | MW | ii) Rajshahi area |  | 1101 | MW
| iii) Comilla area |  | 1018 | MW | iii) Barisal area |  | 294 | MW
| iv) Mymensingh area |  | 892 | MW | iv) Rangpur area |  | 698 | MW
| v) Sylhet area |  | 430 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 10978 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 124 | 0:00 | Sherpur | 98 | 1:00 | Jhenida | 109 | 18:30
| Munsiganj | 114 | 21:00 | Srimongal | 45 | 18:30 | Bottail | 124 | 19:00
| Sonargaon | 79 | 18:30 | Shahjibazar | 107 | 22:00 | G.K Project | 54 | 19:00
| Shyampur | 192 | 10:00 | Fenchuganj | 33 | 19:00 | Faridpur | 180 | 0.77083
| Bhulta | 198 | 21:00 | Kulawara | 38 | 21:00 | Madaripur | 89 | 0.91667
| Madanganj | 39 | 1:00 | Sylhet | 111 | 20:00 | Sariatpur | 58 | 21:00
| Shitalakhya | 106 | 16:00 | Chatak | 24 | 21:00 | Gopalganj | 83 | 20:00
| Rahim steel | 12 | 6:00 | Sunamganj | 37 | 1:00 | Bagerhat | 88 | 19:00
| Matuail | 80 | 10:00 | Biani Bazar | 52 | 20:00 | Mongla | 38 | 14:00
| Ghorasal | 79 | 18:30 | Comilla (S) | 154 | 18:30 | Satkhira | 99 | 0.875
| Narsingdi | 157 | 1:00 | Comilla(N) | 94 | 20:00 | Gallamari | 44 | 14:00
| Haripur (SBU) | 97 | 10:00 | Chandpur | 87 | 23:00 | Magura | 50 | 0.79167
| Ullon | 57 | 11:00 | Feni | 102 | 18:30 | Norail | 37 | 18:30
| Hasnabad | 199 | 19:30 | Chowmuhani | 156 | 18:30 | Chuadanga | 91 | 18:30
| Magbazar | 96 | 14:00 | Ashuganj | 55 | 23:00 | Barisal(N) | 40 | 0.875
| Maniknagar | 88 | 13:00 | Daudkandi | 128 | 20:00 | Barisal (S) | 92 | 0.875
| Bangabhaban | 34 | 11:00 | B.Baria | 136 | 20:00 | Patuakhali | 108 | 0.91667
| Narinda | 84 | 18:00 | Ramganj | 104 | 19:00 | Bhandaria | 52 | 0.875
| Dhanmondi | 181 | 12:00 | Chaddagram | 31 | 19:00 | Borhan Uddin | 41 | 21:00
| Lalbag | 88 | 13:00 | PHP | 11 | 22:00 | Ishurdi | 62 | 19:00
| Madartek | 67 | 21:00 | Madunaghat | 48 | 12:00 | Ruppur Paromanobik | 2 | 20:00
| Dhaka University |  |  | Hathazari | 81 | 0.875 | Natore | 109 | 19:00
| Fatullah | 40 | 0.5 | Khulshi | 195 | 0.45833 | Bogra | 137 | 19:30
| Mirpur | 102 | 18:00 | Halishahar | 131 | 0.77083 | Noagaon | 103 | 20:00
| Kalyanpur | 90 | 18:00 | Baraulia | 143 | 0.041667 | Rajshahi | 132 | 21:00
| Gulshan | 126 | 13:00 | Sikalbaha | 27 | 0.77083 | Rajshahi New | 12 | 21:00
| Uttara | 80 | 18:30 | Dohazari | 80 | 0.79167 | C.Nawabganj | 63 | 19:30
| Uttara New | 33 | 18:30 | Cox'sbazar | 102 | 0.75 | Amnura | 40 | 21:00
| Kamrangirchar | 82 | 18:30 | Chandraghona | 26 | 0.75 | Pabna | 120 | 19:30
| Savar | 135 | 15:00 | Kaptai | 4.2 | 0.77083 | Shahjadpur | 93 | 20:00
| Bhasantec | 146 | 13:00 | A. Khaer Stl. | 0 | 0.041667 | Serajganj | 86 | 20:00
| Agargaon | 68 | 13:00 | Bakulia | 106 | 0.75 | Niyamatpur | 50 | 20:00
| Satmosjid | 93 | 18:30 | Julda | 21 | 0.66667 | Joypurhat | 54 | 20:00
| Tongi | 93 | 0.625 | TK chemical | 26.1 | 0.875 | Sherpur(Bogura) | 44 | 19:00
| Kabirpur | 221 | 15:00 | Modern Steel | 13 | 0.125 | Mohastangor | 48 | 1:00
| Basundhara | 131 | 18:30 | Shahmirpur | 22.5 | 0.79167 | Rangpur | 134 | 19:00
| Manikganj | 64 | 0.875 | Khagrachhari | 24 | 0.77083 | Lalmonirhat | 50 | 18:30
| Joydevpur | 157 | 18:30 | Matarbari | 38 | 0.79167 | Saidpur | 91 | 19:00
| New Tongi | 117 | 15:00 | Baroiar Hat | 26 | 0.041667 | Purbasadipur | 89 | 19:00
| Korda | 226 | 19:00 | Rangamati | 12 | 0.77083 | Thakurgaon | 71 | 19:00
| Dhamrai | 94 | 19:00 | Abul Khair 230 | 46 | 0.041667 | Palashbari | 104 | 20:00
| Rajendrapur | 100 | 21:00 | BSRM | 106 | 0.16667 | Barapukuria | 45 | 19:30
| Valuka | 120 | 21:00 | GPH Ispat | 87 | 0.77083 | Panchagar | 47 | 19:00
| Tangail | 189 | 22:00 | Goalpara | 21 | 0.54167 | Joldhaka | 30 | 19:00
| Mymensing | 156 | 22:00 | Central s/s | 87 | 19:00 | Kurigram | 52 | 18:30
| Kishorganj | 125 | 20:00 | Noapara | 52 | 18:30
| Netrokona | 109 | 19:30 | Jessore | 114 | 18:30
| Jamalpur | 127 | 20:00 | Benapol | 38 | 18:30
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-09-24 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 396 | 22:00 | 389 | 15:00 | Kaliakoir | 378 | 0.20833 | 356 | 0.625
| Bheramara | 395 | 8:00 | 386 | 18:30 | Bhulta | 387 | 0.91667 | 376 | 0.41667
| Ashuganj(N) | 393 | 8:00 | 381 | 16:00 | Gopalganj | 417 | 0.375 | 390 | 0.83333
| Payra | 416 | 8:00 | 402 | 20:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 1:00 | 230 | 10:00 | Comilla (N) | 234 | 18:30 | 228 | 16:00
| Ishurdi | 234 | 14:00 | 227 | 1:00 | Hathazari | 232 | 19:00 | 220 | 4:00
| Ashuganj | 236 | 8:00 | 230 | 16:00 | Megnaghat | 230 | 19:00 | 223 | 15:00
| Serajganj | 233 | 18:00 | 229 | 2:00 | Fenchuganj | 239 | 1:00 | 234 | 15:00
| Baghabari | 241 | 19:00 | 237 | 23:00 | Siddhirganj | 228 | 1:00 | 222 | 10:00
| Barapukuria | 239 | 14:00 | 231 | 19:00 | Maniknagar | 226 | 20:00 | 221 | 10:00
| Bogra | 231 | 14:00 | 222 | 1:00 | Agargaon | 226 | 6:00 | 216 | 16:00
| Rajshahi | 229 | 18:00 | 218 | 1:00 | Barisal | 248 | 21:00 | 229 | 23:00
| Khulna South | 239 | 19:00 | 226 | 1:00 | AKSML | 226 | 18:30 | 218 | 6:00
| Rampura | 228 | 1:00 | 222 | 10:00 | BSRM | 228 | 18:30 | 219 | 4:00
| Haripur | 227 | 21:00 | 220 | 16:00 | Bibiyana | 236 | 19:00 | 231 | 15:00
| Hasnabad | 226 | 24:00 | 220 | 13:00 | Bhulta | 230 | 19:00 | 223 | 17:00
| Shyampur | 224 | 8:00 | 216 | 16:00 | Ashuganj (S) | 234 | 18:30 | 228 | 10:00
| Aminbazar | 227 | 8:00 | 215 | 12:00 | Kaliakoir | 231 | 8:00 | 219 | 16:00
| Tongi | 225 | 21:00 | 216 | 15:00 | GPH | 228 | 8:00 | 213 | 17:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 131 | 18:00 | 127 | 10:00 | Hathazari | 139 | 0.79167 | 131 | 0.16667
| Munsiganj | 133 | 18:30 | 127 | 4:00 | Khulshi | 138 | 0.79167 | 131 | 0.041667
| Sonargaon | 133 | 18:00 | 126 | 3:00 | Halishahar | 141 | 0.875 | 132 | 0.25
| Shyampur | 132 | 8:00 | 127 | 10:00 | Baraulia | 140 | 0.79167 | 130 | 0.20833
| Bhulta | 125 | 18:00 | 120 | 10:00 | Sikalbaha | 141 | 19:00 | 131 | 0.16667
| Madanganj | 135 | 21:00 | 128 | 16:00 | Dohazari | 137 | 19:00 | 125 | 0.20833
| Shitalakhya | 140 | 21:00 | 131 | 15:00 | Cox'sbazar | 128 | 0.375 | 119 | 0.25
| Rahim steal | 132 | 18:00 | 127 | 11:00 | Chandraghona | 139 | 0.875 | 130 | 0.16667
| Matuail | 131 | 18:00 | 127 | 10:00 | Kaptai | 138 | 18:30 | 132 | 0.041667
| Ghorasal | 138 | 1:00 | 136 | 10:00 | A. Khaer Stl. | 135 | 0.79167 | 130 | 6:00
| Narsinghdi | 127 | 8:00 | 122 | 1:00 | Bakulia | 140 | 0.79167 | 129 | 0.25
| Haripur (SBU) | 131 | 9:00 | 127 | 10:00 | Julda | 141 | 0.79167 | 130 | 0.625
| Ullon | 134 | 1:00 | 128 | 16:00 | TK Chemical | 138 | 0.8125 | 130 | 6:00
| Hasnabad | 135 | 4:00 | 130 | 17:00 | Modern Steel | 140 | 0.79167 | 129 | 0.70833
| Magbazar | 135 | 7:00 | 128 | 12:00 | Shahmirpur | 140 | 0.79167 | 133 | 0.41667
| Maniknagar | 132 | 1:00 | 127 | 11:00 | Khagrachhari | 137 | 0.77083 | 129 | 0.20833
| Bangabhaban | 132 | 1:00 | 127 | 11:00 | Matarbari | 130 | 0.29167 | 121 | 0.041667
| Narinda | 132 | 1:00 | 127 | 11:00 | Baroiar Hat | 137 | 0.79167 | 128 | 0.041667
| Dhanmondi | 134 | 1:00 | 128 | 16:00 | Rangamati | 138 | 0.875 | 129 | 6:00
| Lalbag | 136 | 21:00 | 125 | 16:00 | Goalpara S/S | 137 | 18:00 | 132 | 1:00
| Madartek | 134 | 8:00 | 128 | 16:00 | Khulna Central S/S | 137 | 0.75 | 131 | 1:00
| Dhaka University |  |  |  |  | Noapara | 134 | 9:00 | 128 | 1:00
| Fatuiiah | 133 | 0.875 | 128 | 10:00 | Jessore | 130 | 18:00 | 123 | 18:30
| Mirpur | 133 | 6:00 | 126 | 12:00 | Benapol | 132 | 9:00 | 124 | 1:00
| Kalyanpur | 134 | 6:00 | 127 | 12:00 | Jhenida | 130 | 0.375 | 117 | 20:00
| Gulshan | 133 | 6:00 | 128 | 12:00 | Bottail | 134 | 9:00 | 127 | 20:00
| Uttara | 133 | 6:00 | 126 | 12:00 | G.K Project | 140 | 0.375 | 136 | 20:00
| Uttara New | 134 | 18:00 | 128 | 10:00 | Faridpur | 133 | 9:00 | 124 | 21:00
| Kamrangirchar | 134 | 6:00 | 127 | 12:00 | Madaripur | 138 | 0.375 | 129 | 20:00
| Savar | 134 | 1:00 | 125 | 12:00 | Shariyatpur S/S | 137 | 0.29167 | 125 | 20:00
| Bhasantec | 136 | 8:00 | 129 | 12:00 | Gopalganj | 138 | 8:00 | 125 | 19:00
| Agargaon | 137 | 8:00 | 130 | 16:00 | Bagerhat | 130 | 8:00 | 123 | 1:00
| Satmosjid | 137 | 8:00 | 130 | 12:00 | Mongla | 130 | 0.33333 | 123 | 1:00
| Tongi | 136 | 0.875 | 130 | 15:00 | Satkhira | 135 | 0.33333 | 128 | 1:00
| Kabirpur | 135 | 8:00 | 124 | 15:00 | Gallamari | 137 | 12:00 | 130 | 1:00
| Basundhara | 134 | 22:00 | 127 | 16:00 | Magura | 128 | 9:00 | 115 | 21:00
| Manikganj | 138 | 21:00 | 130 | 15:00 | Norail | 127 | 0.33333 | 115 | 18:30
| Joydevpur | 142 | 18:30 | 134 | 16:00 | Chuadanga | 123 | 9:00 | 108 | 20:00
| New Tongi | 136 | 0.875 | 128 | 15:00 | Barisal(N) | 141 | 6:00 | 128 | 22:00
| Kodda | 137 | 20:00 | 124 | 0.66667 | Barisal (S) | 138 | 0.25 | 128 | 22:00
| Dhamrai | 134 | 8:00 | 124 | 15:00 | Patuakhali(S) | 137 | 0.25 | 120 | 23:00
| Rajendrapur | 133 | 19:00 | 121 | 15:00 | Bhandaria | 131 | 9:00 | 122 | 21:00
| Valuka | 131 | 8:00 | 116 | 19:00 | Ishurdi | 139 | 18:00 | 133 | 23:00
| Tangail | 135 | 7:00 | 126 | 21:00 | Ruppur Paromanobik | 137 | 18:00 | 133 | 23:00
| Mymensing | 135 | 8:00 | 121 | 19:00 | Natore | 139 | 18:00 | 132 | 23:00
| Kishorganj | 133 | 8:00 | 123 | 19:30 | Bogra | 140 | 18:00 | 133 | 23:00
| Netrokona | 134 | 8:00 | 117 | 18:30 | Noagaon | 135 | 18:00 | 127 | 23:00
| Jamalpur | 138 | 8:00 | 130 | 9:00 | Rajshahi | 139 | 18:00 | 130 | 23:00
| Sherpur | 138 | 8:00 | 128 | 9:00 | Rajshahi New | 141 | 18:00 | 130 | 1:00
| Srimongal | 138 | 8:00 | 134 | 0.875 | C.Nawabganj | 139 | 18:00 | 128 | 1:00
| Shahjibazar | 137 | 9:00 | 133 | 0.041667 | Amnura | 139 | 18:00 | 126 | 3:00
| Fenchuganj | 136 | 14:00 | 134 | 0.041667 | Pabna | 135 | 18:00 | 130 | 20:00
| Khulawara | 135 | 8:00 | 133 | 0.041667 | Shahjadpur | 140 | 18:00 | 134 | 23:00
| Sylhet | 134 | 6:00 | 130 | 0.41667 | Serajganj | 136 | 18:00 | 131 | 24:00
| Chatak | 133 | 4:00 | 128 | 11:00 | Niyamatpur | 135 | 14:00 | 125 | 23:00
| Sunamganj | 132 | 6:00 | 128 | 0.041667 | Joypurhat | 135 | 18:00 | 126 | 23:00
| Biani Bazar | 132 | 5:00 | 129 | 0.041667 | Sherpur(Bogura) | 139 | 18:00 | 132 | 23:00
| Comilla(s) | 128 | 7:00 | 120 | 19:00 | Mohastangor | 139 | 14:00 | 131 | 23:00
| Comilla(n) | 138 | 19:00 | 134 | 12:00 | Rangpur | 137 | 14:00 | 124 | 20:00
| Chandpur | 134 | 7:00 | 129 | 1:00 | Lalmonirhat | 135 | 14:0 | 120 | 20:00
| Feni | 136 | 19:00 | 128 | 23:00 | Saidpur | 134 | 6:00 | 124 | 20:00
| Chowmuhani | 133 | 18:00 | 125 | 24:00 | Purbasadipur | 131 | 14:00 | 118 | 19:00
| Ashuganj | 138 | 8:00 | 135 | 22:00 | Thakurgaon | 132 | 14:00 | 117 | 19:00
| Daudkandi | 133 | 18:00 | 128 | 11:00 | Palashbari | 135 | 14:00 | 127 | 20:00
| B.Baria | 135 | 7:00 | 129 | 21:00 | Barapukuria | 139 | 14:00 | 131 | 19:00
| Ramganj | 131 | 18:00 | 125 | 17:00 | Panchagar | 128 | 6:00 | 115 | 19:00
| Chaddagram | 137 | 19:00 | 129 | 23:00 | Joldhaka | 135 | 14:00 | 119 | 19:00
| PHP | 137 | 19:00 | 128 | 2:00 | Kurigram | 134 | 14:00 | 119 | 18:30
| Madanhat | 142 | 18:30 | 131 | 5:00

## L-Curve
Date | 2020-09-24
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 172 | 6971 | 3531 | 10502 |  |  |  | QF-LDC-11
0:30 | 195 | 6789 | 3427.5 | 10216.5 | Date: | 2020-09-24
1:00 | 218 | 6607 | 3324 | 9931
1:30 | 235.5 | 6420.5 | 3309.5 | 9730
2:00 | 253 | 6234 | 3295 | 9529
2:30 | 271.5 | 6131 | 3266.5 | 9397.5 | [5 empty] | Gen. at Eve. Peak | 11477 | 11477 MW (19:00 )
3:00 | 290 | 6028 | 3238 | 9266 | [6 empty] | 19:00
3:30 | 313 | 5949.5 | 3219 | 9168.5 | [5 empty] | Gen. at Day Peak | 9339 | 9339 MW (12:00 )
4:00 | 336 | 5871 | 3200 | 9071 | [6 empty] | 12:00
4:30 | 342.5 | 5827.5 | 3162.5 | 8990 | [5 empty] | Highest Generation | 11477
5:00 | 349 | 5784 | 3125 | 8909 | [6 empty] | 19:00
5:30 | 399.5 | 5650 | 3017 | 8667
6:00 | 450 | 5516 | 2909 | 8425
6:30 | 448 | 5261.5 | 2872 | 8133.5
7:00 | 446 | 5007 | 2835 | 7842
7:30 | 460.5 | 4999.5 | 2835 | 7834.5
8:00 | 475 | 4992 | 2835 | 7827
8:30 | 515.5 | 5255 | 2869.5 | 8124.5
9:00 | 556 | 5518 | 2904 | 8422
9:30 | 583.5 | 5634.5 | 2936 | 8570.5
10:00 | 611 | 5751 | 2968 | 8719
10:30 | 625.5 | 5811.5 | 2999 | 8810.5
11:00 | 640 | 5872 | 3030 | 8902
11:30 | 623.5 | 5999.5 | 3121 | 9120.5
12:00 | 607 | 6127 | 3212 | 9339
12:30 | 569 | 6265.5 | 3245.5 | 9511
13:00 | 531 | 6404 | 3279 | 9683
13:30 | 563 | 6358.5 | 3233.5 | 9592
14:00 | 595 | 6313 | 3188 | 9501
14:30 | 593 | 6311 | 3192 | 9503
15:00 | 591 | 6309 | 3196 | 9505
15:30 | 611.5 | 6272 | 3168 | 9440
16:00 | 632 | 6235 | 3140 | 9375
16:30 | 559 | 6219.5 | 3093.5 | 9313
17:00 | 486 | 6204 | 3047 | 9251
17:30 | 409 | 6475 | 3195.5 | 9670.5
18:00 | 332 | 6746 | 3344 | 10090
18:30 | 259.5 | 7151 | 3632.5 | 10783.5
19:00 | 187 | 7556 | 3921 | 11477
19:30 | 214 | 7407 | 3932 | 11339
20:00 | 212 | 7361 | 3988 | 11349 |  |  |  | Executive Engineer
20:30 | 196 | 7353.5 | 3953.5 | 11307 |  |  |  | Network Operation Division
21:00 | 180 | 7346 | 3919 | 11265
21:30 | 165 | 7267 | 3851 | 11118
22:00 | 150 | 7188 | 3783 | 10971 |  |  |  |  | Page 6 of 7
22:30 | 165.5 | 7119.5 | 3684.5 | 10804
23:00 | 181 | 7051 | 3586 | 10637
23:30 | 176.5 | 7011 | 3558.5 | 10569.5
24:00 | 172 | 6971 | 3531 | 10502
11477 MW (19:00 )
9339 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-09-24 |  | Energy | 232152723
[10 empty] | 2020-09-24 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3283 | 929 | 2238 | 2968 | 710 | 41 | 298 | 0 | 140
0:30 | 3384 | 928.5 | 2246.5 | 2626.5 | 680 | 42 | 221.5 | 0 | 140 | Date: | 2020-09-24
1:00 | 3485 | 928 | 2255 | 2285 | 650 | 43 | 145 | 0 | 140
1:30 | 3516.5 | 928 | 2177 | 2148 | 650 | 43 | 132.5 | 0 | 135 | [7 empty] | Total Energy | 232.1527 | Total Energy Gen 232.153 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 232.153 MKWHr
2:00 | 3548 | 928 | 2099 | 2011 | 650 | 43 | 120 | 0 | 130 | [7 empty] | Energy not Served | 0
2:30 | 3526.5 | 928 | 2099 | 1917.5 | 640 | 43.5 | 120 | 0 | 123 | [7 empty] | Energy Requirement | 232.1527
3:00 | 3505 | 928 | 2099 | 1824 | 630 | 44 | 120 | 0 | 116
3:30 | 3508.5 | 928 | 2098 | 1724 | 630 | 44 | 120 | 0 | 116 | [6 empty] | Shortage
4:00 | 3512 | 928 | 2097 | 1624 | 630 | 44 | 120 | 0 | 116
4:30 | 3505.5 | 928 | 2095.5 | 1553.5 | 630 | 43.5 | 120 | 0 | 114
5:00 | 3499 | 928 | 2094 | 1483 | 630 | 43 | 120 | 0 | 112
5:30 | 3457.5 | 928 | 2053 | 1331 | 625 | 42.5 | 120 | 0 | 110
6:00 | 3416 | 928 | 2012 | 1179 | 620 | 42 | 120 | 0 | 108
6:30 | 3409.5 | 928 | 1826.5 | 1123.5 | 585 | 42 | 120 | 0 | 98 |  |  |  |  | Coal
7:00 | 3403 | 928 | 1641 | 1068 | 550 | 42 | 120 | 0 | 88
7:30 | 3290 | 928.5 | 1580 | 1223.5 | 550 | 41 | 120 | 0 | 97 |  |  |  | Oil |  |  |  | ,
8:00 | 3177 | 929 | 1519 | 1379 | 550 | 40 | 120 | 0 | 106
8:30 | 3156.5 | 928.5 | 1548.5 | 1676 | 534.5 | 40 | 120 | 0 | 109
9:00 | 3136 | 928 | 1578 | 1973 | 519 | 40 | 120 | 0 | 112
9:30 | 3201.5 | 928 | 1597 | 2026.5 | 524.5 | 40 | 120 | 0 | 116
10:00 | 3267 | 928 | 1616 | 2080 | 530 | 40 | 120 | 0 | 120
10:30 | 3221.5 | 928 | 1662.5 | 2172 | 525 | 41 | 120 | 0 | 120
11:00 | 3176 | 928 | 1709 | 2264 | 520 | 42 | 120 | 0 | 120
11:30 | 3152 | 927.5 | 1733.5 | 2449 | 555 | 42 | 120 | 0 | 120
12:00 | 3128 | 927 | 1758 | 2634 | 590 | 42 | 120 | 0 | 120
12:30 | 3116.5 | 928 | 1785 | 2759.5 | 600 | 42.5 | 140.5 | 0 | 121
13:00 | 3105 | 929 | 1812 | 2885 | 610 | 43 | 161 | 0 | 122
13:30 | 3105 | 929 | 1812 | 2885 | 610 | 43 | 161 | 0 | 122
14:00 | 3105 | 929 | 1812 | 2885 | 610 | 43 | 161 | 0 | 122
14:30 | 3124 | 928.5 | 1851 | 2725.5 | 614.5 | 43.5 | 170 | 0 | 127
15:00 | 3143 | 928 | 1890 | 2566 | 619 | 44 | 179 | 0 | 132
15:30 | 3169.5 | 928 | 1925 | 2467 | 609 | 44 | 165 | 0 | 127
16:00 | 3196 | 928 | 1960 | 2368 | 599 | 44 | 151 | 0 | 122
16:30 | 3221.5 | 928 | 2014 | 2204.5 | 584.5 | 45 | 190.5 | 0 | 120
17:00 | 3247 | 928 | 2068 | 2041 | 570 | 46 | 230 | 0 | 118
17:30 | 3230 | 928 | 1971 | 2420 | 559 | 45 | 387 | 0 | 129
18:00 | 3213 | 928 | 1874 | 2799 | 548 | 44 | 544 | 0 | 140
18:30 | 3233 | 929 | 2037 | 3135 | 607 | 43.5 | 654 | 0 | 145
19:00 | 3253 | 930 | 2200 | 3471 | 666 | 43 | 764 | 0 | 150
19:30 | 3315 | 929 | 2269 | 3327 | 665 | 43 | 643 | 0 | 148
20:00 | 3306 | 929 | 2256 | 3317 | 707 | 41 | 643 | 0 | 150
20:30 | 3277 | 929 | 2250 | 3311.5 | 708.5 | 41 | 641 | 0 | 149
21:00 | 3248 | 929 | 2244 | 3306 | 710 | 41 | 639 | 0 | 148
21:30 | 3245 | 929.5 | 2246 | 3264 | 710 | 41 | 536.5 | 0 | 146
22:00 | 3242 | 930 | 2248 | 3222 | 710 | 41 | 434 | 0 | 144
22:30 | 3282.5 | 929.5 | 2196 | 3095 | 710 | 40.5 | 406.5 | 0 | 144
23:00 | 3323 | 929 | 2144 | 2968 | 710 | 40 | 379 | 0 | 144
23:30 | 3303 | 929 | 2191 | 2968 | 710 | 40.5 | 338.5 | 0 | 142 | Max Temp. in Dhaka |  | 31.0° C
24:00 | 3283 | 929 | 2238 | 2968 | 710 | 41 | 298 | 0 | 140
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 232.153 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 232.153 MKWHr
Note on W13: Author:

## Generation
g | 2020-09-24
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 43 | 43 | 44 | 44 | 43 | 42 | 42 | 40 | 40 | 40 | 42 | 42 | 43 | 43 | 44 | 44 | 46 | 44 |  | 43 | 43 | 41 | 41 | 41 | 40 | 41 | 958560
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2900000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 15 |  | 8 | 8 | 8 | 8 |  |  |  | 55949
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 1 | 5 | 14 | 14 | 20 | 14 | 10 | 0 |  | 6 | 2 | [9 empty] | 89910
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [12 empty] | 25 | 51 | 34 | 6 | 17 | 71 |  | 102 | 102 | 102 | 102 | 40 | 34 | 34 | 579472
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | [16 empty] | 18 |  | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 178981
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [17 empty] | 18 |  | 49 | [6 empty] | 59296
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 298 | 304 | 295 | 292 | 295 | 285 | 287 | 270 | 290 | 318 | 302 | 302 | 265 | 248 | 274 | 282 | 280 | 296 |  | 262 | 298 | 295 | 275 | 270 | 304 | 291 | 7020858
18 | Kodda 300 MW PP Unit-2 (Summit) | 268 | 200 | 200 | 145 | 145 | 145 | 115 | 126 | 282 | 300 | 291 | 293 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 290 | 285 | 293 | 300 | 300 | 6127198
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 267636
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2740500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4793600
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1923456
32 | Ashuganj 50 MW PP | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 660456
33 | Ashuganj 225 MW CCPP | 217 | 216 | 217 | 219 | 218 | 218 | 219 | 220 | 182 | 203 | 194 | 190 | 182 | 182 | 182 | 182 | 182 | 186 |  | 182 | 188 | 184 | 182 | 182 | 197 | 182 | 4800000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 315 | 335 | 315 | 315 | 315 | 275 | 275 | 275 | 275 | 310 | 290 | 295 | 290 | 285 | 260 | 260 | 260 | 280 |  | 290 | 290 | 280 | 280 | 280 | 300 | 280 | 7304000
35 | Ashuganj 55 MW PP (Precision) | 50 | 50 | 50 | 51 | 51 | 50 | 51 | 50 | 50 | 50 | 50 | 47 | 47 | 45 | 46 | 46 | 48 | 45 |  | 50 | 50 | 48 | 48 | 54 | 55 | 55 | 1189920
36 | Chandpur 150 MW CCPP | 96 | 85 | 93 | 90 | 94 | 88 | 94 | 85 | 92 | 94 | 94 | 94 | 94 | 85 | 96 | 91 | 86 | 94 |  | 85 | 95 | 95 | 85 | 86 | 96 | 94 | 2177060
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 338 | 352 | 343 | 340 | 341 | 340 | 338 | 341 | 338 | 350 | 366 | 341 | 343 | 339 | 339 | 351 | 352 | 325 |  | 344 | 339 | 339 | 339 | 339 | 340 | 361 | 8369150
40 | Meghnaghat 450 MW CCPP(MPL) | 400 | 420 | 420 | 420 | 420 | 420 | 380 | 350 | 350 | 350 | 350 | 380 | 380 | 350 | 350 | 330 | 380 | 360 |  | 420 | 420 | 420 | 420 | 420 | 350 | 420 | 8874750
41 | Haripur 360MW CCPP(HPL) | 354 | 174 | 184 | 184 | 184 | 184 | 14 | [5 empty] | 100 | 195 | 300 | 351 | 351 | 286 |  | 353 | 353 | 353 | 354 | 354 | 324 | 349 | 5009000
42 | RPCL 210MW CCPP | 125 | 143 | 145 | 161 | 160 | 160 | 160 | 158 | 159 | 142 | 124 | 123 | 121 | 101 | 101 | 102 | 125 | 125 |  | 125 | 125 | 124 | 122 | 121 | 123 | 123 | 3073640
43
44 | Fenchugonj CCPP Phase-1 | 87 | 87 | 87 | 87 | 87 | 88 | 88 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 90 | 90 | 89 |  | 90 | 90 | 90 | 89 | 89 | 89 | 89 | 2096000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 726000
46 | Shajibazar 330 MW CCPP | 141 | 142 | 140 | 140 | 143 | 140 | 140 | 140 | 142 | 142 | 142 | 142 | 140 | 141 | 140 | 143 | 144 | 142 |  | 142 | 140 | 140 | 140 | 140 | 140 | 140 | 3150000
47 | Shahjibazar GTPP Unit- 8 & 9 | 67 | 67 | 67 | 67 | 67 | 67 | 40 | 40 | 40 | 51 | 40 | 51 | 52 | 40 | 40 | 40 | 45 | 68 |  | 68 | 60 | 60 | 60 | 60 | 57 | 63 | 1286
48 | Shahjibazar 86MW PP (Shahjibazar) | 86 | 86 | 87 | 87 | 87 | 87 | 20 | 20 | 84 | 84 | 81 | 84 | 82 | 40 | 40 | 40 | 40 | 40 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 1709760
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 205 | 205 | 205 | 205 | 205 | 205 | 205 | [6 empty] | 50 | 100 | 150 | 150 | 135 |  | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 2972160
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 425000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 213660
54 | Hobiganj 11MW PP Cofidence-E | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 3 | 5 | 5 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 184000
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 47 | 44 | 47 | 47 | 47 | 52 | 50 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1201800
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576696
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 295 | 290 | 290 | 285 | 280 | 290 | 290 | 260 | 295 | 310 | 290 | 290 | 255 | 260 | 280 | 290 | 270 |  | 280 | 300 | 275 | 280 | 275 | 280 | 300 | 7023500
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | [7 empty] | 17 | 35 | 35 | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 17 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 776183
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 21 |  | 20 | 20 | 20 |  | 19 |  |  | 20 | 20 | 20 | 20 | 20 | 20 |  | 413658
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | [8 empty] | 339984
62 | Tangail 22 MW PP (Doreen) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 17 | 17 | 17 | 17 | 17 | 362124
63 | Impoprt (Tripura) | 140 | 130 | 116 | 116 | 112 | 108 | 88 | 106 | 112 | 120 | 120 | 120 | 122 | 128 | 132 | 122 | 118 | 140 |  | 150 | 148 | 150 | 148 | 144 | 144 | 140 | 3064320
64 | Malancha, Ctg. EPZ (United) | 41 | 41 | 41 | 42 | 42 | 41 | 24 | 6 | 5 | 4 | 3 | 4 | 7 | 5 | 3 | 12 | 15 | 24 |  | 25 | 25 | 30 | 37 | 40 | 42 | 42 | 564000
65 | Feni 22MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 418608
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 8 | 8 | 5 | 8 | 8 | 5 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 153900
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 32 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 28 | 28 | 33 | 33 | 33 | 637500
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 15 | 15 | 8 | 17 | 17 | 17 | 16 | 16 | 16 | 16 | 16 | 18 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 456480
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 29 | 28 | 28 | 28 | 28 | 27 | 27 | 27 | 27 | 28 | 28 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 637560
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 |  | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 767300
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 17 | 17 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 818800
73 | Ghorashal 108MW PP (Regent) | 95 | 94 | 95 | 95 | 94 | 94 | 94 | 94 | 94 | 89 | 89 | 88 | 88 | 88 | 88 | 85 | 84 | 89 |  | 90 | 90 | 90 | 89 | 89 | 89 | 87 | 2142136
| Feni Lanka Power | [12 empty] | 34 |  |  |  |  | 52 |  | 100 | 50 | 50 | 50 |  |  |  | 307800
| Chowmuhani 113 MW | 107 | 106 | 107 | 84 | 84 | 55 | 55 | 66 | 113 | 113 | 104 | 113 | 105 | 107 | 107 | 106 | 84 | 103 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2455320
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 100 | 100 | 92 | 60 | 7 | 7 | 35 | 90 | 98 | 100 | 100 | 100 | 100 | 100 | 100 | 70 | 75 |  | 100 | 100 | 100 | 100 | 100 | 95 | 95 | 2082240
78 | Gazipur 52 MW PP | [12 empty] | 25 | 25 |  |  |  | 40 |  | 52 | 52 | 52 | 52 | 25 |  |  | 303720
79 | Kodda 150MW PP | [12 empty] | 16 |  |  |  | 10 | 84 |  | 150 | 115 | 115 | 115 | 98 | 84 | 48 | 691200
80 | Jamalpur 95 MW PP(Powerpac) | [26 empty] | 0
81 | Jangalia 52 MW PP (Lakdanavi) | [8 empty] | 4 | 8 | 8 | 25 | 25 | 34 | 16 |  |  | 16 |  | 52 | 52 | 52 | 52 | 52 |  |  | 406997
| Gazipur 100 MW PP | [7 empty] | 17 | 34 | 34 | 48 | 84 | 84 | 84 | 34 | 34 | 34 | 60 |  | 93 | 103 | 103 | 93 | 85 | 85 | 50 | 1128360
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 1 | 1 | 2 | 1 | 2 | 1 | 2 | 2 | 0 | 0 | [9 empty] | 12000
| Jodiac Power | 17 | [6 empty] | 23 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 936693
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | 97 | 48 | 30 | 30 | 30 | 30 | 30 | 30 | 40 | 48 | 60 | 95 | 97 | 87 | 97 | 97 | 97 | 97 |  | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 1784352
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [7 empty] | 4 | 10 | 10 | 18 | 50 | 50 | 50 | 50 | 10 | 10 | 35 |  | 50 | 50 | 52 | 74 | 79 | 83 | 50 | 704392
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | 85 | 87 | 93 | 98 | 100 | 75 | 22 | 77 | 92 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 98 | 100 | 100 | 97 | 100 | 2269440
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 21 | 36 | 45 | 72 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 1261440
88 | Ghorashal 78.5 MW PP(MAX) | 68 | 68 | 68 | 68 | 68 | 68 | 40 | 40 | 40 | 40 | 67 | 66 | 65 | 65 | 65 | 65 | 65 | 66 |  | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 1464512
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [12 empty] | 30 | 10 | 10 |  |  | 10 | [8 empty] | 67920
92 | Fenchuganj 44MW (Energyprima) | 49 | 49 | 46 | 49 | 49 | 49 | 49 | 49 | 49 | 46 | 46 | 46 | 46 | 49 | 47 | 47 | 47 | 47 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 1157760
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 10 | 25 | 43 | 43 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1168242
94 | Gagnagar 102 MW PP (Digital Power) | 93 | 93 | 93 | 93 | 93 | 64 | 40 | 50 | 64 | 76 | 85 | 90 | 93 | 93 | 93 | 93 | 93 | 93 |  | 93 | 93 | 92 | 93 | 93 | 93 | 93 | 2071008
95 | Patenga 50MW PP (Baraka) | [8 empty] | 16 | 19 | 29 | 50 | 50 | 50 | 50 | 18 | 18 | 50 |  | 50 | 19 | 19 | 19 | 19 | 19 |  | 480480
96 | Chattogram 108 MW PP (ECPV) | 91 | 51 | [6 empty] | 54 | 55 | 55 | 57 | 57 | 55 | 50 | 13 | 18 | 30 |  | 79 | 89 | 90 | 90 | 91 | 91 | 91 | 1170240
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 30 | 30 | 15 | 15 | 16 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 15 | 28 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 925611
100 | Manikganj 55 MW PP (Northern) | 17 | 17 | [5 empty] | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 17 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 913882
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 110 | 110 | 110 | 110 | 130 | 130 | 110 | 110 | 110 | 163 | 110 |  | 163 | 163 | 163 | 163 | 163 | 130 | 110 | 3449372
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | [9 empty] | 5650
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 |  |  |  |  | 54 | 35 | 35 | 54 | 54 | 54 | 54 | 54 | 54 | 17 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 872280
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 194 | 193 | 183 | 200 | 200 | 200 | 160 | 160 | 100 | 106 | 132 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4478400
112 | Aurahati 100MW PP (Aggreko) | [26 empty] | 0
114 | Kodda 149 MW PP Unit-1 (Summit) | 131 | 111 | 98 | 86 | 86 | 86 | 86 | 91 | 142 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3182690
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2402880
116 | Chandpur 200MW (Desh energy) | [17 empty] | 46 |  | 32 | [6 empty] | 126720
117 | Ashuganj 150MW PP (Midland) | 50 | 10 | 5 | 5 | 5 | 5 | 5 | 7 | 56 | 70 | 83 | 100 | 100 | 100 | 20 | 20 | 20 | 43 |  | 98 | 98 | 98 | 98 | 98 | 102 | 98 | 1445236
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 85 | 85 | 24 | 24 | 8 |  |  | 2 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 19 |  | 105 | 95 | 95 | 95 | 95 | 95 | 95 | 994800
| Anwara 300 MW PP (United) | 307 | 307 | 307 | 254 | 215 | 178 | 215 | 251 | 214 | 214 | 252 | 270 | 305 | 306 | 307 | 307 | 215 | 280 |  | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 6553745
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2389440
120 | Eastern Zone Total | 6607 | 6234 | 6028 | 5871 | 5784 | 5516 | 5007 | 4992 | 5518 | 5751 | 5872 | 6127 | 6404 | 6313 | 6309 | 6235 | 6204 | 6746 |  | 7556 | 7407 | 7361 | 7346 | 7188 | 7051 | 6971 | 151250629
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 99 | 99 | 99 | 99 | 66 | 32 | 32 | 34 | 66 | 66 | 99 | 99 | 99 | 99 | 99 | 99 | 32 | 66 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2034240
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
| Khulna 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 150 |  | 200 | 200 | 200 | 200 | 200 | 165 | 120 | 3363840
129 | Rupsha 105 MW PP (Orion rupsha) | [17 empty] | 50 |  | 90 | 90 | 90 | 90 | 105 | 70 | 53 | 526560
130
131
132
133
| Barisal 110 MW PP (Summit ) | 16 | 16 | 16 | 16 | [13 empty] | 16 |  | 48 | 48 | 48 | 32 | 32 | 16 | 16 | 320640
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 77 | 76 | 76 | 76 | 75 | 76 | 50 | 41 | 22 | 35 | 65 | 78 | 77 | 77 | 77 | 78 | 78 | 77 |  | 78 | 78 | 78 | 77 | 78 | 79 | 78 | 1696781
| Bhola 225 MW CCPP | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 16 | 15 | 15 | 15 | 86 | 86 | 86 | 86 |  | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 1832908
140 | Bhola 33 MW PP (Venture) | 22 | 24 | 22 | 22 | 21 | 20 | 17 | 11 | 12 | 12 | 13 | 17 | 17 | 19 | 17 | 20 | 16 | 25 |  | 29 | 30 | 31 | 32 | 32 | 31 | 31 | 493328
141 | Noapara 100 MW PP (Bangla Trac) | [19 empty] | 20 | 20 | 20 | 20 | 20 |  |  | 100800
142 | Noapara 40 MW PP (Khanjahan Ali) | [12 empty] | 40 | 40 | 8 |  |  | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 371250
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 2 | 7 | [8 empty] | 5248
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 928 | 928 | 928 | 928 | 928 | 928 | 928 | 929 | 928 | 928 | 928 | 927 | 929 | 928 | 928 | 928 | 928 | 928 |  | 930 | 929 | 929 | 929 | 930 | 929 | 929 | 22271272
147 | Bheramara 410 MW CCPP | 300 | 300 | 295 | 295 | 295 | 295 | 315 | 310 | 310 | 305 | 285 | 285 | 265 | 250 | 250 | 250 | 250 | 260 |  | 265 | 265 | 265 | 255 | 250 | 250 | 250 | 6920640
148 | Payra 1320 MW | 500 | 500 | 480 | 480 | 480 | 470 | 400 | 400 | 370 | 380 | 370 | 440 | 460 | 470 | 470 | 450 | 420 | 400 |  | 520 | 520 | 560 | 560 | 560 | 560 | 560 | 11869800
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 150 | 150 | 150 | 150 | 150 | 149 | 149 | 150 | 148 |  | 146 | 145 | 147 | 150 | 150 | 150 | 150 | 3681200
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [13 empty] | 25 | 25 | 25 | 25 | 33 |  | 50 | 50 | 50 | 50 |  |  |  | 277949
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 176 | 187 | 183 | 182 | 169 | 160 | 158 | 161 | 157 | 168 | 195 | 177 | 176 | 168 | 152 | 152 | 151 | 142 |  | 147 | 144 | 147 | 144 | 144 | 151 | 162 | 4130618
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 176 | 187 | 182 | 181 | 172 | 158 | 159 | 162 | 160 | 171 | 192 | 201 | 196 | 175 | 168 | 171 | 174 | 130 |  | 156 | 184 | 186 | 176 | 175 | 170 | 168 | 4425655
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 410 | 409 | 407 | 400 | 405 | 330 | 340 | 334 | 360 | 364 | 382 | 388 | 338 | 326 | 342 | 354 | 351 | 283 |  | 365 | 410 | 418 | 394 | 393 | 414 | 416 | 9039000
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 9 | 39 |  | 39 | 4 | [5 empty] | 76924
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 18 | 18 | 20 | 20 | 20 | 20 | 20 | 20 |  | 18 | 21 | 21 | 21 | 21 | 21 | 21 | 466560
163 | Bogura 20 MW PP (Energyprima) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 220860
164 | Ullapara 11 MW PP (Summit) | 11 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 184428
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [17 empty] | 29 |  | 43 | 43 | 47 | 43 |  |  |  | 167856
168 | Santahar 50 MW Peaking PP | [16 empty] | 7 | 33 |  | 33 | 33 | 33 | 33 |  |  |  | 145740
169 | Natore 52 MW PP (Rajlanka) | [11 empty] | 16 | 52 | 8 | 8 |  |  | 43 |  | 52 | 25 | 25 | 25 |  |  |  | 231360
170 | Chapainawabganj 100 MW Peaking PP | 25 | [15 empty] | 40 | 80 |  | 98 | 96 | 96 | 96 | 96 | 96 | 96 | 672008
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [10 empty] | 4 | 60 | 89 | 70 | 35 |  |  | 70 |  | 110 | 113 | 113 | 113 | 113 |  |  | 941568
172 | Confidence Power Bogura Unit-1 113 MW | 109 | 109 | 109 | 109 | 109 | 35 | 35 | 50 | 100 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 |  | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 2435040
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 113 | 90 | 71 | 42 | 35 | 35 | 34 | 35 | 52 | 61 | 65 | 91 | 105 | 109 | 113 | 113 | 60 | 62 |  | 113 | 113 | 113 | 108 | 113 | 113 | 113 | 1978560
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 1 | 1 | 1 | 1 | 3 | 4 | 2 | 2 | 1 | 1 | [9 empty] | 19461
178
178