## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-09-26 | Saturday
|  |  | Date (day): | 2020-09-26 |  | Saturday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13304.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14271 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-09-25 | 2020-09-26 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 100 | 100
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 115 | 115 | 180 | 10
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 0 | 0 | 365 |  | Machine problem
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 40 | 40 | 68 | 68 |  | 10 | Engine problem
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 85 | 92 | 94 | 94 |  | 14 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 348 | 343 | 412 | 412 |  |  | FGMO
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 324 | 352 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 420 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 1 | 100 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 30 | 90 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 40 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 302 | 308 | 335 | 335 |  |  | FGMO
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 93 | 93 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 84 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 41 | 54 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 25 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 70 | 270 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 80 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 85 | 85 |  | 20 | Engine problem
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 104 | 104 | 104
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 2145 | 3143 | 3838 | 4193 | 1154 | 468
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 7 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 42 | 113 | 40 | 110 | 120 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 100 | 100
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 21 | 20 | 20
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 39 | 41 | 12 | 40
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 48 | 90 | 90 |  | 18 | Engine problem
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 161 | 306 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 591 | 849 | 1346 | 1419 | 510 | 341
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 130 | 80 | 80 | 54 |  | Gas shortage
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 139 | 97 | 225 | 225 |  |  | FGMO
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 290 | 335 | 360 | 360 |  |  | FGMO
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 29 | 30 | 30 | 15 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 54 | 55 | 55
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 45 | 8 | 8 | 187 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 5 | 5 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 42
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 96 | 96 | 100 | 100 |  | 63 | ST under shut down
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 200 | 200
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 8 | 8 |  | 3 | Engine problem
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 106 | 142 | 162 | 173
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 25 | 25 |  | 8 | Engine problem
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 34 | 34 |  | 18 | Engine problem
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 21 | 18 | 21 | 21
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 113 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 881 | 1174 | 1754 | 2007 | 520 | 456
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 152 | 157 | 160 | 160 | 42 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 14 | 17 | 16 | 16 |  | 6 | Engine problem
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 0 | 0 | 0 |  | 95 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 170 | 200 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 16 | 8 | 115 | 115
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 354 | 382 | 492.6 | 491 | 42 | 101
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 89 | 87 | 90 | 90
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 35 | Unit-4 under shut down
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 142 | 202 | 200 | 200 |  |  | Gas shortage
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 50 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 44 | 47 | 47 | 47
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 66 | 65 | 65
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 85 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 120 | 136 | 145 | 145
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 300 | 341 | 341 |  |  | FGMO
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1107 | 1229 | 1282 | 1282 | 0 | 435
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 928 | 919 | 929 | 929
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 99 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 120 | 225 | 225
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 290 | 370 | 410 | 410
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105
| 108 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1338 | 1548 | 1974 | 2130 | 0 | 0
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 48 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 15 | 30 | 33 | 33
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 86 | 80 | 86 | 86 |  | 134 | GT-2 & STG under shut down
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 33 | 77 | 78 | 78 |  | 17 | Engine problem
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 400 | 500 | 580 | 580
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 534 | 735 | 887 | 887 | 0 | 151
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 43 | 43
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | ST Under maint & gas shoratge
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 151 | 190 | 200 | 200 |  |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 160 | 197 | 220 | 220 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 404 | 408 | 414 | 414 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 34
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 21 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 10 | 10 | 10 | 10
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 9 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 90 | 90 |  | 23 | Engine problem
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 109 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 753 | 943 | 1473 | 1599 | 271 | 233
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 109 | 100 | 113
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 0 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 150 | 259 | 258 | 263 | 294 | 40
|  | Total |  |  |  |  | 20383 | 19892 | 7853 | 10262 | 13304.6 | 14271 | 2791 | 2225
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7474.201 | 9767 | 12662.8365 | 13582.621
| A. |  | 2020-09-25 | (Yesterday) |  |  |  |  | Friday
| 1 | Highest Generation : |  |  | 10262 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 7634 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10262 | MW
| 3 | Day peak Generation : |  |  | 7853 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9767 | MW
| 4 | Evening peak Generation : |  |  | 10262 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 212.6303 | MKWHr | By Solar | 0.066741 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 128.3377 | MKWHr |  | By Oil: | 42.6272 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 14.921 | MKWHr |  | By Hydro: | 1.4779 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2791 | MW | Dhaka | 3350 | 3350 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2225 | MW | Chittagong | 986 | 986 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5016 | MW | Khulna | 1302 | 1302 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1026.24 | MMCFD |  |  | Rajshahi | 1048 | 1048 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 150046671.032 | ii) Oil : | Taka | 334532732.69 | Comilla | 963 | 963 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 69204186 | Total | Taka | 553783589.722 | Mymensingh | 810 | 810 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.016 | MKWHr. | Sylhet | 437 | 437 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 73 | MW (E to W) at | 21:00 | hrs | Barisal | 287 | 287 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -63 | MW at | 19:30 | hrs | Rangpur | 584 | 584 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 31.8° C |  |  | Total | 9767 | 9767 |  | 0
| B. |  | 2020-09-26 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 31.5° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 11000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14271 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 9000 | MW
| 4 | Reserve(Generation end) |  |  |  | 3271 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 227.9218 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7804 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.2516 | MKWHr. | ii) HVDC Flow at Peak Time |  | 919 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.9482 | MKWHr. | iii) Maximum HVDC Flow : |  | 936 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 96.17 |  | (b) Today: | 96.76 |  | (c) Rule Curve: |  | 104.8
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-09-25
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 115 | 200 | 87 | 66 | 339 | 351 |  | 0 | 380 | 0 | 100 | 97 | 40 | 285 | 0 | 0 | 0 | 100 | 93 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 29 | 33 | 33 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 91 | 0 | 0 | 42 | 0 | 0 | 80 | 280 | 0 | 182 | 8 | 85 | 29 | 55 | 0 | 51 | 0 | 0 | 0 | 18 | 5 | 33 | 21 | 138 | 123 | 0 | 17 | 0 | 89 | 30 | 53 | 47 | 110 | 140 | 64 | 84 | 0 | 145 | 18 | 0 | 10 | 285 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 100 | 0 | 95 | 0 | 0 | 0 | 307 | 54 | 0 | 0 | 113 | 100 | 0 | 104 |  | 936 | 0 | 250 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 24 | 86 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 165 | 0 | 78 | 0 | 169 | 0 | 414 | 17 | 0 | 0 | 0 | 113 | 0 | 0 | 109 | 560 |  | 6721 | 3415 | 10136 | 3267 | 936 | 2182 | 2685 | 710 | 42 | 176 | 138 | 0 | 0 | 95.92
2:00 | 0 | 0 | 0 | 115 | 200 | 87 | 66 | 339 | 351 |  | 0 | 350 | 0 | 100 | 97 | 40 | 285 | 0 | 0 | 0 | 100 | 93 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 29 | 33 | 33 | 0 | 0 | 43 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 80 | 280 | 0 | 182 | 8 | 89 | 29 | 55 | 0 | 51 | 0 | 0 | 0 | 18 | 5 | 33 | 21 | 134 | 142 | 0 | 17 | 0 | 89 | 30 | 53 | 47 | 110 | 141 | 64 | 85 | 0 | 145 | 18 | 0 | 10 | 285 | 24 | 8 | 0 | 286 | 0 | 0 | 200 | 0 | 145 | 0 | 100 | 0 | 50 | 0 | 95 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 113 | 100 | 0 | 104 |  | 935 | 0 | 255 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 86 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 167 | 0 | 78 | 0 | 171 | 0 | 405 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 109 | 540 |  | 6445 | 3312 | 9757 | 3300 | 935 | 2143 | 2376 | 690 | 43 | 136 | 134 | 0 | 0 | 95.97
3:00 | 0 | 0 | 0 | 115 | 200 | 87 | 66 | 339 | 352 |  | 0 | 350 | 0 | 100 | 97 | 40 | 301 | 0 | 0 | 0 | 100 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 29 | 33 | 0 | 0 | 0 | 44 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 80 | 280 | 0 | 184 | 8 | 95 | 29 | 56 | 0 | 51 | 0 | 0 | 0 | 18 | 5 | 33 | 21 | 132 | 144 | 0 | 17 | 0 | 89 | 30 | 53 | 47 | 110 | 141 | 64 | 85 | 0 | 145 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 280 | 0 | 0 | 200 | 0 | 125 | 0 | 100 | 0 | 5 | 0 | 35 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 113 | 100 | 0 | 104 |  | 936 | 0 | 260 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 86 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 165 | 0 | 78 | 0 | 164 | 0 | 410 | 0 | 0 | 0 | 0 | 112 | 0 | 0 | 109 | 540 |  | 6188 | 3312 | 9500 | 3289 | 936 | 2154 | 2135 | 690 | 44 | 120 | 132 | 0 | 0 | 96.02
4:00 | 0 | 0 | 0 | 115 | 200 | 87 | 66 | 345 | 350 |  | 0 | 350 | 0 | 100 | 48 | 40 | 301 | 0 | 0 | 0 | 100 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 29 | 33 | 33 | 0 | 0 | 44 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 80 | 280 | 0 | 191 | 8 | 96 | 29 | 55 | 0 | 51 | 0 | 0 | 0 | 18 | 5 | 33 | 21 | 132 | 156 | 0 | 17 | 0 | 89 | 30 | 50 | 47 | 110 | 138 | 64 | 85 | 0 | 145 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 100 | 0 | 0 | 200 | 0 | 117 | 0 | 100 | 0 | 5 | 0 | 16 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 113 | 100 | 0 | 104 |  | 936 | 0 | 270 | 0 | 105 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 165 | 0 | 77 | 0 | 175 | 0 | 414 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 109 | 520 |  | 5992 | 3244 | 9236 | 3367 | 936 | 2160 | 1807 | 670 | 44 | 120 | 132 | 0 | 0 | 96.07
5:00 | 0 | 0 | 0 | 115 | 200 | 87 | 66 | 339 | 352 |  | 0 | 350 | 0 | 100 | 48 | 40 | 285 | 0 | 0 | 0 | 100 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 29 | 33 | 33 | 0 | 0 | 44 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 42 | 0 | 0 | 80 | 280 | 0 | 182 | 8 | 96 | 29 | 55 | 0 | 51 | 0 | 0 | 0 | 18 | 5 | 33 | 21 | 128 | 157 | 0 | 17 | 0 | 89 | 30 | 50 | 47 | 110 | 142 | 64 | 85 | 0 | 145 | 18 | 0 | 10 | 285 | 24 | 8 | 0 | 95 | 0 | 0 | 200 | 0 | 112 | 0 | 100 | 0 | 5 | 0 | 16 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 113 | 100 | 0 | 104 |  | 935 | 0 | 275 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 161 | 0 | 77 | 0 | 175 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 520 |  | 5955 | 3195 | 9150 | 3360 | 935 | 2138 | 1755 | 670 | 44 | 120 | 128 | 0 | 0 | 96.12
6:00 | 0 | 0 | 0 | 115 | 200 | 87 | 66 | 341 | 309 |  | 0 | 350 | 0 | 75 | 48 | 0 | 271 | 0 | 0 | 0 | 48 | 50 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 25 | 33 | 33 | 0 | 0 | 43 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 42 | 0 | 0 | 80 | 280 | 0 | 182 | 8 | 85 | 29 | 55 | 0 | 51 | 0 | 0 | 0 | 18 | 5 | 33 | 21 | 116 | 158 | 0 | 17 | 0 | 89 | 30 | 50 | 47 | 110 | 140 | 64 | 85 | 0 | 145 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 117 | 0 | 0 | 200 | 0 | 112 | 0 | 100 | 0 | 5 | 0 | 16 | 0 | 0 | 0 | 252 | 0 | 0 | 0 | 35 | 100 | 0 | 53 |  | 930 | 0 | 290 | 0 | 29 | 120 | 0 | 0 | 0 | 0 | 0 | 86 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 157 | 0 | 77 | 0 | 170 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520 |  | 5606 | 2912 | 8518 | 3337 | 930 | 2002 | 1240 | 670 | 43 | 180 | 116 | 0 | 0 | 96.17
7:00 | 0 | 0 | 0 | 115 | 200 | 86 | 65 | 338 | 254 |  | 0 | 300 | 0 | 15 | 32 | 0 | 265 | 0 | 0 | 0 | 0 | 8 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 39 | 0 | 0 | 80 | 260 | 0 | 144 | 8 | 86 | 29 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 5 | 33 | 21 | 100 | 160 | 0 | 17 | 0 | 89 | 30 | 50 | 47 | 110 | 140 | 55 | 85 | 0 | 120 | 18 | 0 | 9 | 270 | 24 | 8 | 0 | 215 | 0 | 0 | 170 | 0 | 117 | 2 | 100 | 0 | 5 | 0 | 16 | 4 | 0 | 0 | 252 | 0 | 0 | 0 | 8 | 100 | 0 | 17 |  | 929 | 0 | 240 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 86 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 149 | 0 | 77 | 0 | 140 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 |  | 5206 | 2737 | 7943 | 3151 | 929 | 1812 | 1059 | 630 | 42 | 218 | 100 | 2 | 0 | 96.22
8:00 | 0 | 0 | 0 | 115 | 200 | 43 | 40 | 338 | 255 |  | 0 | 300 | 0 | 0 | 46 | 0 | 285 | 0 | 0 | 0 | 0 | 8 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 37 | 0 | 0 | 80 | 260 | 0 | 144 | 8 | 89 | 29 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 5 | 33 | 18 | 96 | 158 | 0 | 14 | 1 | 89 | 30 | 50 | 47 | 110 | 140 | 40 | 85 | 0 | 80 | 18 | 0 | 9 | 280 | 24 | 8 | 0 | 250 | 0 | 0 | 170 | 0 | 146 | 4 | 100 | 0 | 5 | 0 | 16 | 34 | 0 | 1 | 197 | 0 | 0 | 0 | 8 | 100 | 0 | 17 |  | 929 | 0 | 240 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 86 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 130 | 0 | 78 | 0 | 130 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 430 |  | 5146 | 2657 | 7803 | 3083 | 929 | 1752 | 1097 | 579 | 42 | 218 | 96 | 7 | 0 | 96.26
9:00 | 0 | 0 | 0 | 115 | 200 | 43 | 40 | 339 | 255 |  | 0 | 300 | 0 | 0 | 30 | 0 | 283 | 0 | 0 | 0 | 0 | 8 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 41 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 39 | 0 | 0 | 80 | 260 | 0 | 143 | 8 | 95 | 29 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 5 | 33 | 15 | 100 | 156 | 0 | 14 | 1 | 89 | 30 | 50 | 47 | 110 | 143 | 40 | 40 | 0 | 80 | 18 | 0 | 9 | 270 | 24 | 8 | 0 | 250 | 0 | 0 | 170 | 0 | 149 | 2 | 100 | 0 | 5 | 0 | 16 | 34 | 0 | 2 | 161 | 0 | 0 | 0 | 0 | 100 | 0 | 17 |  | 929 | 0 | 245 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 86 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 130 | 0 | 33 | 0 | 130 | 0 | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 |  | 5040 | 2594 | 7634 | 3093 | 929 | 1659 | 1040 | 549 | 41 | 218 | 100 | 5 | 0 | 96.3
10:00 | 0 | 0 | 0 | 115 | 200 | 42 | 40 | 340 | 254 |  | 0 | 300 | 0 | 0 | 30 | 0 | 293 | 0 | 0 | 0 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 25 | 33 | 8 | 0 | 0 | 41 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 39 | 0 | 0 | 80 | 260 | 0 | 142 | 8 | 94 | 29 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 21 | 108 | 155 | 0 | 14 | 2 | 89 | 30 | 47 | 44 | 110 | 142 | 40 | 40 | 0 | 80 | 18 | 0 | 9 | 285 | 24 | 8 | 0 | 250 | 0 | 0 | 170 | 0 | 149 | 4 | 100 | 0 | 5 | 0 | 16 | 34 | 0 | 1 | 160 | 0 | 0 | 0 | 0 | 100 | 0 | 17 |  | 930 | 0 | 245 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 86 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 130 | 0 | 34 | 0 | 130 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 |  | 5003 | 2622 | 7625 | 3074 | 930 | 1693 | 1039 | 549 | 41 | 184 | 108 | 7 | 0 | 96.34
11:00 | 0 | 0 | 0 | 115 | 200 | 42 | 40 | 356 | 323 |  | 0 | 400 | 0 | 0 | 30 | 0 | 307 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 25 | 33 | 33 | 0 | 0 | 41 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 39 | 0 | 0 | 80 | 310 | 0 | 139 | 8 | 96 | 29 | 0 | 0 | 51 | 0 | 0 | 0 | 15 | 5 | 33 | 21 | 112 | 152 | 0 | 14 | 2 | 89 | 30 | 47 | 44 | 130 | 142 | 40 | 40 | 0 | 120 | 18 | 0 | 9 | 300 | 24 | 8 | 0 | 120 | 0 | 0 | 170 | 0 | 105 | 6 | 100 | 0 | 5 | 0 | 16 | 0 | 0 | 2 | 160 | 0 | 0 | 0 | 0 | 100 | 0 | 17 |  | 929 | 0 | 245 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 86 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 33 | 0 | 130 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 |  | 5085 | 2632 | 7717 | 3217 | 929 | 1907 | 831 | 550 | 41 | 120 | 112 | 10 | 0 | 96.38
12:00 | 0 | 0 | 0 | 115 | 200 | 85 | 40 | 348 | 324 |  | 0 | 400 | 0 | 1 | 30 | 0 | 302 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 16 | 33 | 33 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 39 | 0 | 0 | 80 | 290 | 0 | 139 | 8 | 96 | 29 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 5 | 33 | 21 | 106 | 152 | 0 | 14 | 2 | 89 | 30 | 47 | 44 | 130 | 142 | 60 | 85 | 0 | 120 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 70 | 0 | 0 | 170 | 0 | 80 | 7 | 100 | 0 | 5 | 0 | 16 | 0 | 0 | 2 | 161 | 0 | 0 | 0 | 0 | 100 | 0 | 17 |  | 928 | 0 | 290 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 86 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 151 | 0 | 33 | 0 | 160 | 0 | 404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 |  | 5078 | 2775 | 7853 | 3294 | 928 | 2045 | 757 | 550 | 42 | 120 | 106 | 11 | 0 | 96.4
13:00 | 0 | 0 | 0 | 115 | 200 | 91 | 50 | 368 | 343 |  | 0 | 400 | 0 | 14 | 37 | 0 | 285 | 0 | 0 | 0 | 2 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 13 | 33 | 33 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 0 | 0 | 80 | 310 | 0 | 142 | 8 | 86 | 26 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 21 | 112 | 156 | 0 | 14 | 2 | 88 | 30 | 50 | 47 | 163 | 142 | 61 | 85 | 0 | 130 | 17 | 0 | 10 | 300 | 24 | 8 | 0 | 70 | 0 | 0 | 180 | 0 | 74 | 2 | 100 | 0 | 5 | 0 | 16 | 0 | 0 | 1 | 161 | 0 | 0 | 0 | 0 | 100 | 0 | 23 |  | 930 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 80 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 172 | 0 | 43 | 0 | 178 | 0 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 |  | 5225 | 2822 | 8047 | 3386 | 930 | 2105 | 798 | 549 | 42 | 120 | 112 | 5 | 8047 | 96.42
14:00 | 0 | 0 | 0 | 115 | 200 | 91 | 64 | 340 | 285 |  | 0 | 340 | 0 | 53 | 48 | 0 | 261 | 0 | 0 | 0 | 7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 13 | 33 | 33 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 37 | 0 | 0 | 80 | 260 | 0 | 143 | 8 | 85 | 23 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 0 | 104 | 142 | 0 | 0 | 1 | 88 | 30 | 50 | 47 | 110 | 140 | 40 | 84 | 0 | 80 | 17 | 0 | 10 | 260 | 24 | 8 | 0 | 70 | 0 | 0 | 197 | 0 | 72 | 9 | 100 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 100 | 0 | 53 |  | 928 | 0 | 285 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 80 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 5 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 179 | 0 | 43 | 0 | 177 | 0 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 |  | 4917 | 2715 | 7632 | 3127 | 928 | 1830 | 923 | 548 | 42 | 120 | 104 | 10 | 0 | 96.44
15:00 | 0 | 0 | 0 | 115 | 200 | 91 | 64 | 339 | 273 |  | 0 | 300 | 0 | 55 | 30 | 0 | 292 | 0 | 0 | 0 | 7 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 13 | 25 | 33 | 0 | 0 | 42 | 35 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 34 | 0 | 0 | 80 | 260 | 0 | 141 | 8 | 85 | 29 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 5 | 33 | 18 | 108 | 142 | 0 | 0 | 0 | 87 | 30 | 48 | 47 | 110 | 140 | 52 | 85 | 0 | 20 | 17 | 0 | 10 | 260 | 24 | 8 | 0 | 70 | 0 | 0 | 100 | 0 | 63 | 8 | 100 | 0 | 5 | 0 | 0 | 0 | 0 | 1 | 161 | 0 | 0 | 0 | 0 | 100 | 0 | 53 |  | 929 | 0 | 240 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 80 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 5 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 148 | 0 | 43 | 0 | 130 | 0 | 284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 |  | 4770 | 2477 | 7247 | 2997 | 929 | 1756 | 801 | 450 | 77 | 120 | 108 | 9 | 0 | 96.46
16:00 | 0 | 0 | 0 | 115 | 200 | 91 | 66 | 343 | 273 |  | 0 | 300 | 0 | 38 | 30 | 0 | 308 | 0 | 0 | 0 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 6 | 25 | 33 | 0 | 0 | 42 | 35 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 21 | 41 | 0 | 0 | 80 | 285 | 0 | 140 | 8 | 94 | 29 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 5 | 33 | 18 | 106 | 159 | 0 | 0 | 0 | 90 | 30 | 50 | 47 | 110 | 142 | 66 | 84 | 0 | 20 | 18 | 0 | 0 | 280 | 24 | 8 | 0 | 60 | 0 | 0 | 32 | 0 | 21 | 2 | 100 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 0 | 100 | 0 | 38 |  | 929 | 0 | 240 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 80 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 5 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 137 | 0 | 33 | 0 | 130 | 0 | 253 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 290 |  | 4628 | 2384 | 7012 | 3069 | 929 | 1723 | 548 | 420 | 77 | 137 | 106 | 3 | 0 | 96.48
17:00 | 0 | 0 | 0 | 115 | 200 | 91 | 66 | 360 | 274 |  | 0 | 300 | 0 | 24 | 30 | 0 | 317 | 0 | 0 | 0 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 6 | 25 | 33 | 0 | 0 | 42 | 35 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 21 | 38 | 0 | 0 | 80 | 295 | 0 | 139 | 8 | 96 | 29 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 0 | 18 | 108 | 158 | 0 | 0 | 0 | 89 | 30 | 53 | 47 | 110 | 142 | 65 | 84 | 0 | 30 | 17 | 0 | 10 | 300 | 8 | 8 | 0 | 45 | 0 | 0 | 32 | 0 | 22 | 2 | 100 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 0 | 0 | 0 | 100 | 0 | 17 |  | 929 | 0 | 240 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 80 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 5 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 146 | 0 | 34 | 0 | 151 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 290 |  | 4599 | 2515 | 7114 | 3096 | 929 | 1855 | 489 | 420 | 77 | 137 | 108 | 3 | 0 | 96.5
18:00 | 0 | 0 | 0 | 115 | 200 | 91 | 65 | 385 | 273 |  | 0 | 380 | 0 | 36 | 30 | 0 | 310 | 0 | 0 | 0 | 12 | 24 | 25 | 4 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 25 | 13 | 25 | 33 | 0 | 0 | 42 | 35 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 51 | 10 | 0 | 1 | 21 | 39 | 0 | 0 | 80 | 285 | 0 | 140 | 53 | 95 | 29 | 10 | 0 | 51 | 0 | 0 | 1 | 18 | 8 | 27 | 18 | 130 | 158 | 0 | 0 | 0 | 90 | 30 | 53 | 47 | 110 | 144 | 65 | 84 | 0 | 49 | 18 | 0 | 10 | 320 | 24 | 8 | 0 | 50 | 0 | 0 | 53 | 0 | 37 | 0 | 100 | 0 | 8 | 0 | 6 | 1 | 0 | 0 | 199 | 0 | 0 | 0 | 42 | 100 | 0 | 40 |  | 918 | 0 | 310 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 8 | 80 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 30 | 0 | 0 | 20 | 10 | 5 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 169 | 0 | 39 | 0 | 180 | 0 | 348 | 0 | 0 | 4 | 0 | 23 | 0 | 0 | 90 | 350 |  | 5283 | 2961 | 8244 | 3299 | 918 | 2027 | 1061 | 490 | 77 | 242 | 130 | 0 | 0 | 96.52
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 115 | 200 | 92 | 40 | 348 | 355 |  | 0 | 370 | 0 | 82 | 68 | 28 | 253 | 0 | 0 | 0 | 65 | 70 | 84 | 30 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 20 | 25 | 25 | 0 | 0 | 43 | 70 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 51 | 10 | 39 | 18 | 21 | 29 | 0 | 0 | 130 | 260 | 0 | 144 | 45 | 86 | 29 | 46 | 0 | 51 | 0 | 0 | 8 | 18 | 8 | 33 | 18 | 138 | 160 | 0 | 17 | 0 | 90 | 30 | 53 | 47 | 110 | 142 | 40 | 84 | 0 | 86 | 18 | 0 | 10 | 270 | 24 | 8 | 0 | 195 | 0 | 0 | 199 | 0 | 92 | 0 | 100 | 0 | 62 | 0 | 36 | 41 | 0 | 0 | 303 | 19 | 0 | 0 | 113 | 100 | 0 | 104 |  | 918 | 0 | 345 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 16 | 80 | 26 | 48 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 44 | 8 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 174 | 0 | 78 | 0 | 196 | 0 | 282 | 35 | 0 | 30 | 0 | 101 | 0 | 0 | 109 | 430 |  | 6429 | 3400 | 9829 | 3318 | 918 | 2019 | 2388 | 580 | 113 | 355 | 138 | 0 | 0 | 96.54
19:30 | 0 | 0 | 0 | 115 | 200 | 92 | 40 | 339 | 355 |  | 0 | 370 | 0 | 100 | 80 | 40 | 290 | 0 | 0 | 0 | 100 | 85 | 84 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 20 | 25 | 33 | 0 | 0 | 43 | 70 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 82 | 10 | 21 | 40 | 0 | 0 | 130 | 260 | 0 | 143 | 45 | 92 | 29 | 52 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 18 | 140 | 160 | 0 | 17 | 0 | 90 | 30 | 53 | 47 | 110 | 202 | 40 | 84 | 0 | 103 | 18 | 0 | 10 | 285 | 24 | 11 | 0 | 280 | 0 | 0 | 199 | 0 | 130 | 0 | 100 | 0 | 80 | 0 | 8 | 50 | 0 | 0 | 306 | 34 | 0 | 0 | 113 | 100 | 0 | 104 |  | 919 | 0 | 340 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 16 | 80 | 27 | 48 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 44 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 170 | 0 | 76 | 0 | 190 | 0 | 303 | 35 | 0 | 0 | 0 | 103 | 0 | 0 | 109 | 440 |  | 6803 | 3381 | 10184 | 3424 | 919 | 2071 | 2571 | 590 | 113 | 356 | 140 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 115 | 197 | 92 | 40 | 338 | 353 |  | 0 | 420 | 0 | 100 | 80 | 40 | 288 | 0 | 0 | 0 | 100 | 85 | 84 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 20 | 25 | 33 | 0 | 0 | 43 | 70 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 86 | 6 | 21 | 40 | 0 | 0 | 130 | 310 | 0 | 142 | 45 | 92 | 29 | 52 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 18 | 140 | 160 | 0 | 17 | 0 | 88 | 30 | 50 | 47 | 163 | 200 | 52 | 85 | 0 | 125 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 286 | 0 | 0 | 200 | 0 | 132 | 0 | 100 | 0 | 15 | 0 | 8 | 14 | 0 | 0 | 303 | 0 | 0 | 0 | 113 | 100 | 0 | 104 |  | 919 | 0 | 340 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 16 | 80 | 30 | 48 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 173 | 0 | 76 | 0 | 196 | 0 | 344 | 17 | 0 | 0 | 0 | 105 | 0 | 0 | 109 | 490 |  | 6790 | 3394 | 10184 | 3506 | 919 | 2209 | 2426 | 640 | 113 | 231 | 140 | 0 | 0 | 96.56
21:00 | 0 | 0 | 0 | 115 | 200 | 92 | 40 | 343 | 352 |  | 0 | 420 | 0 | 100 | 90 | 40 | 308 | 0 | 0 | 0 | 100 | 93 | 84 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 22 | 25 | 29 | 25 | 33 | 0 | 0 | 43 | 70 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 48 | 0 | 21 | 41 | 0 | 0 | 130 | 335 | 0 | 97 | 45 | 96 | 29 | 54 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 18 | 142 | 157 | 0 | 17 | 0 | 87 | 30 | 50 | 47 | 163 | 202 | 66 | 85 | 0 | 136 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 270 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 5 | 0 | 8 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 113 | 100 | 0 | 104 |  | 919 | 0 | 370 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 40 | 80 | 30 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 190 | 0 | 77 | 0 | 197 | 0 | 408 | 0 | 0 | 0 | 0 | 109 | 0 | 0 | 109 | 500 |  | 6777 | 3485 | 10262 | 3598 | 919 | 2296 | 2340 | 650 | 113 | 204 | 142 | 0 | 0 | 96.58
22:00 | 0 | 0 | 0 | 115 | 200 | 92 | 50 | 353 | 350 |  | 0 | 420 | 0 | 100 | 97 | 40 | 299 | 0 | 0 | 0 | 100 | 93 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 22 | 25 | 29 | 25 | 33 | 0 | 0 | 43 | 70 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 13 | 0 | 21 | 42 | 0 | 0 | 130 | 315 | 0 | 34 | 45 | 96 | 26 | 54 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 18 | 142 | 158 | 0 | 17 | 0 | 89 | 30 | 50 | 47 | 163 | 200 | 67 | 84 | 0 | 105 | 18 | 0 | 10 | 300 | 0 | 11 | 0 | 293 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 5 | 0 | 56 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 105 | 100 | 0 | 104 |  | 920 | 0 | 350 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 40 | 80 | 32 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 201 | 0 | 78 | 0 | 197 | 0 | 412 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 109 | 500 |  | 6713 | 3488 | 10201 | 3451 | 920 | 2311 | 2379 | 650 | 113 | 235 | 142 | 0 | 0 | 96.6
23:00 | 0 | 0 | 0 | 115 | 200 | 92 | 66 | 341 | 351 |  | 0 | 420 | 0 | 100 | 97 | 40 | 297 | 0 | 0 | 0 | 100 | 93 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 22 | 25 | 29 | 25 | 33 | 0 | 0 | 40 | 70 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 21 | 42 | 0 | 0 | 130 | 310 | 0 | 37 | 45 | 96 | 26 | 54 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 18 | 140 | 158 | 0 | 17 | 0 | 89 | 30 | 50 | 47 | 163 | 200 | 67 | 85 | 0 | 96 | 18 | 0 | 9 | 300 | 0 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 5 | 0 | 80 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 108 | 100 | 0 | 104 |  | 920 | 0 | 340 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 40 | 80 | 31 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 190 | 0 | 78 | 0 | 192 | 0 | 414 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 109 | 500 |  | 6700 | 3447 | 10147 | 3400 | 920 | 2329 | 2396 | 650 | 110 | 202 | 140 | 0 | 0 | 96.62
24:00 | 0 | 0 | 0 | 115 | 200 | 92 | 65 | 339 | 351 |  | 0 | 420 | 0 | 100 | 97 | 40 | 266 | 0 | 0 | 0 | 100 | 93 | 64 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 22 | 25 | 29 | 25 | 33 | 0 | 0 | 40 | 70 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 0 | 0 | 130 | 310 | 0 | 50 | 45 | 94 | 26 | 54 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 20 | 134 | 160 | 0 | 17 | 0 | 89 | 30 | 50 | 47 | 163 | 200 | 67 | 85 | 0 | 97 | 18 | 0 | 10 | 290 | 8 | 11 | 0 | 245 | 0 | 0 | 194 | 0 | 144 | 0 | 100 | 0 | 5 | 0 | 103 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 113 | 100 | 0 | 104 |  | 919 | 0 | 340 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 80 | 31 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 184 | 0 | 77 | 0 | 187 | 0 | 370 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 109 | 500 |  | 6554 | 3390 | 9944 | 3380 | 919 | 2274 | 2293 | 650 | 110 | 184 | 134 | 0 | 0 | 96.64
KWH | 0 | 0 | 0 | 2803500 | 4860800 | 1911090 | 1351616 | 8430690 | 7523000 |  | 0 | 8553750 | 0 | 1432320 | 1437720 | 446281 | 7031521 | 0 | 0 | 0 | 1187520 | 1332432 | 1016160 | 53451 | 0 | 0 | 0 | 466200 | 482427 | 276894 | 442944 | 600000 | 506880 | 779400 | 786100 | 0 | 0 | 949860 | 528000 | 2900000 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 155023 | 19920 | 336000 | 33120 | 389328 | 997920 | 0 | 0 | 2223996 | 7234400 | 0 | 3395000 | 434909 | 2182300 | 657648 | 660480 | 0 | 1244739 | 0 | 0 | 9994 | 412596 | 140040 | 767600 | 448730 | 2948160 | 3583080 | 0 | 284616 | 9500 | 2066000 | 713760 | 1211400 | 1116576 | 3074890 | 3503000 | 1352544 | 1847040 | 0 | 2483450 | 422000 | 0 | 225180 | 7070200 | 475152 | 210000 | 0 | 4571562 | 0 | 0 | 4149600 | 0 | 2642260 | 44010 | 2424000 | 0 | 466690 | 0 | 781200 | 238224 | 12545 | 10000 | 5570182 | 121255 | 0 | 0 | 1376760 | 2428800 | 0 | 1652160 |  | 22251636 | 0 | 7007040 | 0 | 1273920 | 2954880 | 0 | 0 | 0 | 0 | 220125 | 2032126 | 521207 | 275520 | 0 | 0 | 0 | 0 | 0 | 184920 | 0 | 0 | 74838 | 9120 | 0 | 492720 | 190152 | 169506 | 0 | 0 | 3593200 | 0 | 0 | 0 | 0 | 4085027 | 0 | 1473405 | 0 | 4318745 | 0 | 8737909 | 92160 | 0 | 45984 | 0 | 1068480 | 0 | 3231 | 1306560 | 11327800 |  | 138920095 | 73710211 | 212630306 | 79699519 | 22251636 | 48638183 | 38241386 | 14921000 | 1477860 | 4385821 | 2948160 | 66741 | 0
Fuel Cost | 0 | 0 | 0 | 4121145 | 5395488 | 2522638.8 | 2297747.2 | 8514996.9 | 7748690 |  | 0 | 9323587.5 | 0 | 10871308.8 | 9905890.8 | 3775537.26 | 7312781.84 | 0 | 0 | 0 | 8942025.6 | 12151779.84 | 9999014.4 | 492818.22 | 0 | 0 | 0 | 3403260 | 3729160.71 | 2730174.84 | 332208 | 450000 | 0 | 0 | 0 | 0 | 0 | 256462.2 | 142560 | 5249000 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1503723.1 | 190236 | 2923200 | 262310.4 | 490553.28 | 2963822.4 | 0 | 0 | 3269274.12 | 5353456 | 0 | 3123400 | 561032.61 | 2509645 | 743142.24 | 924672 | 0 | 2128503.69 | 0 | 0 | 95442.7 | 523996.92 | 105030 | 1343300 | 336547.5 | 22111200 | 3798064.8 | 0 | 361462.32 | 151430 | 3388240 | 1142016 | 2156292 | 1741858.56 | 3505374.6 | 3643120 | 2664511.68 | 3527846.4 | 0 | 4296368.5 | 924180 | 0 | 459367.2 | 7140902 | 356364 | 159600 | 0 | 34561008.72 | 0 | 0 | 21577920 | 0 | 25999838.4 | 514476.9 | 19755600 | 0 | 3290164.5 | 0 | 7124544 | 2251216.8 | 109266.95 | 0 | 42110575.92 | 1056131.05 | 0 | 0 | 11798833.2 | 16175808 | 0 | 0 |  | 128169423.36 | 0 | 7357392 | 0 | 10013011.2 | 40954636.8 | 0 | 0 | 0 | 0 | 2293702.5 | 2296302.38 | 807870.85 | 2689075.2 | 0 | 0 | 0 | 0 | 0 | 1636542 | 0 | 0 | 725180.22 | 88372.8 | 0 | 946022.4 | 294735.6 | 128316.042 | 0 | 0 | 19475144 | 0 | 0 | 0 | 0 | 5392235.64 | 0 | 2210107.5 | 0 | 5052931.65 | 0 | 8650529.91 | 962150.4 | 0 | 436388.16 | 0 | 8291404.8 | 0 | 35702.55 | 9655478.4 | 49729042 |  | 396873146.37 | 308291698.362 | 705164844.732 | 90135069.812 | 128169423.36 | 59911601.22 | 279713636.17 | 69204186 | 399022.2 | 54819096.52 | 22111200 | 701609.45 | 0
Yesterday Day Peak | 0 | 0 | 0 | 115 | 200 | 85 | 40 | 348 | 324 |  | 0 | 400 | 0 | 1 | 30 | 0 | 302 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 16 | 33 | 33 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 39 | 0 | 0 | 80 | 290 | 0 | 139 | 8 | 96 | 29 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 5 | 33 | 21 | 106 | 152 | 0 | 14 | 2 | 89 | 30 | 47 | 44 | 130 | 142 | 60 | 85 | 0 | 120 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 70 | 0 | 0 | 170 | 0 | 80 | 7 | 100 | 0 | 5 | 0 | 16 | 0 | 0 | 2 | 161 | 0 | 0 | 0 | 0 | 100 | 0 | 17 |  | 928 | 0 | 290 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 86 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 151 | 0 | 33 | 0 | 160 | 0 | 404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 |  | 7853 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 115 | 200 | 92 | 40 | 343 | 352 | 0 | 0 | 420 | 0 | 100 | 90 | 40 | 308 | 0 | 0 | 0 | 100 | 93 | 84 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 22 | 25 | 29 | 25 | 33 | 0 | 0 | 43 | 70 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 21 | 41 | 0 | 0 | 130 | 335 | 0 | 97 | 45 | 96 | 29 | 54 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 18 | 142 | 157 | 0 | 17 | 0 | 87 | 30 | 50 | 47 | 163 | 202 | 66 | 85 | 0 | 136 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 270 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 5 | 0 | 8 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 113 | 100 | 0 | 104 |  | 919 | 0 | 370 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 40 | 80 | 30 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 190 | 0 | 77 | 0 | 197 | 0 | 408 | 0 | 0 | 0 | 0 | 109 | 0 | 0 | 109 | 500 |  | 10262 | EvPeak
Forecast for Evening | 0 | 0 | 100 | 180 | 0 | 94 | 68 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 | 0 | 0 | 100 | 93 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 40 | 70 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 100 | 90 | 50 | 20 | 40 | 0 | 0 | 80 | 360 | 0 | 225 | 8 | 100 | 30 | 55 | 0 | 51 | 0 | 42 | 34 | 18 | 8 | 25 | 21 | 173 | 160 | 0 | 16 | 0 | 90 | 30 | 51 | 47 | 163 | 200 | 65 | 86 | 0 | 145 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 85 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 104 |  | 929 | 16 | 410 | 0 | 115 | 225 | 0 | 0 | 30 | 60 | 40 | 86 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 0 | 0 | 43 | 52 | 34 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 200 | 0 | 78 | 100 | 220 | 0 | 414 | 105 | 200 | 90 | 100 | 113 | 0 | 0 | 113 | 580
Forecast for Day | 0 | 0 | 100 | 115 | 0 | 94 | 68 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 | 0 | 0 | 100 | 93 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 40 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 100 | 90 | 50 | 20 | 12 | 0 | 0 | 80 | 360 | 0 | 225 | 8 | 100 | 30 | 55 | 0 | 51 | 0 | 0 | 34 | 18 | 8 | 25 | 21 | 162 | 160 | 0 | 16 | 1.6 | 90 | 30 | 51 | 47 | 163 | 200 | 65 | 86 | 0 | 145 | 18 | 0 | 10 | 341 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 200 | 150 | 0 | 115 | 85 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 104 |  | 929 | 0 | 410 | 0 | 115 | 225 | 0 | 0 | 0 | 0 | 40 | 86 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 52 | 0 | 22 | 10 | 9 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 200 |  | 78 | 50 | 220 | 0 | 414 | 105 | 100 | 90 | 100 | 100 | 0 | 8 | 113 | 580
Generation at 08:00(Today) | 0 | 0 | 0 | 115 | 0 | 92 | 66 | 349 | 303 | 0 | 0 | 350 | 0 |  | 30 | 0 | 306 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 25 | 14 | 25 | 33 | 0 | 0 | 40 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 12 | 0 | 0 | 80 | 295 | 0 | 191 | 8 | 96 | 22 | 55 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 33 | 18 | 102 | 157 | 0 | 17 | 1 | 89 | 30 | 50 | 47 | 130 | 202 | 63 | 83 | 0 | 96 | 18 | 0 | 10 | 300 | 15 | 8 | 0 | 0 | 0 | 0 | 200 | 0 | 81 | 11 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 3 | 161 | 0 | 0 | 0 | 67 | 100 | 0 | 104 | 0 | 920 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 81 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 163 | 0 | 77 | 0 | 170 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 440 | 0
199
| Minimum Generation |  | 7634 | 9:00
| Highest Generation |  | 10262 | 21:00
| Day Peak Generation |  | 7853 | 12:00
| Evening Peak Generation |  | 10262 | 21:00
| HVDC Max Flow |  | 936 | 1:00
| HVDC EvPeak Flow |  | 919 | 21:00
| Load factor L.F |  | 86.33%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-09-26
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-09-25 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7853 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 7804 | MW
Evening Peak Generation : |  | 10262 | MW Hour : | 21:00 | Available Max Generation : |  | 14271 | MW
E.P. Demand (at gen end) : |  | 10262 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 11000 | MW
Maximum Generation : |  | 10262 | MW Hour : | 21:00 | Reserve(Generation end) |  | 3271 | MW
Total Gen. (MKWH) : |  | 212.6303 | System Load Factor : | 86.33% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -63 | MW at | 19:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-09-26
Actual : | 96.76 | Ft.(MSL) , | Rule curve : | 104.8 | Ft.( MSL )
Gas Consumed : | Total = | 1026.24 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 150046671.032
: |  | Coal : | 69204186 | Oil : | 334532732.69 | Total : | 553783589.722
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3899.0387 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1325.5344 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1187.5717 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1073.0488 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 969.711 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 782.5216 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 438.0038 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 201.4903 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 603.5173 |  |  | 0 | 0%
Total | 0 |  | 10480.4376 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 9) Meghnaghat summit
|  |  |  | 2) Bibiyana #3 | 10) Ashuganj (S)-360 MW
|  |  |  | 3) Ghorasal Unit-1,2,3,7 | 11) Sikalbaha-225 MW.
|  |  |  | 4) Ashuganj unit-3,4 | 12) Sikalbaha-150 MW.
5) Kaptai-2,4,5
6) Raozan #1,2
7) Sirajganj #1
8) Baghabari-100 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Maniknagar 230/132 kV Tr-1 transformer was under shut down from 08:36 to 17:38 for C/M.
b) Ishurdi 230/132 kV Tr-1 transformer was under shut down from 07:50 to 12:07 for C/M.
c) Kaliakoir-Bibiyana 400 kV Ckt-1 was under shut down from 08:20 to 16:26 for C/M.
d) Thakurgaon-Purbasadipur 132 kV Ckts 1 & 2 tripped at 11:34 showing Dist. B,Z1 at Thakurgaon end |  |  |  |  | About 50 MW power interruption occurred under Thakurgaon and Panchagarh
and were switched on at 11:45. |  |  |  |  | S/S areas from 11:34 to 11:45.
e) Barapukuria 132/33 kV T-4 transformer tripped at 12:50 and was switched on at 15:15.
f) Saidpur-Jaldhaka 132 kV Ckts 1 & 2 tripped at 13:20 showing Dist. R,Y,Z1 at Saidpur end and was |  |  |  |  | About 9 MW power interruption occurred under Jaldhaka S/S areas
switched on at 13:30. |  |  |  |  | from 13:20 to 13:30.
g) Kaliakoir-Tangail 132 kV Ckt-1 tripped at 14:13 showing Dist Z1 at both ends and was switched on
at 14:33.
h) Ishurdi-Ghorashal 230 kV Ckt-1 was under shut down from 14:44 to 17:49 for kite removing.
i) Bogura 33 kV Bus of 132/33 kV T-1 transformer was under shut down from 15:09 to 15:38 for PBS work.
j) Comilla(N)-Chandpur 132 kV Ckt-1 tripped at 20:48 showing Dist A at Cumilla(N) end and Dist. A,B,Z1
at Chandpur end and was switched on at 21:05.
k) Sylhet 132/33 kV T-2 transformer tripped at 21:04 due to 33 kV CB burst.
l) Ghorashal unit-7 tripped at 00:56(23/9/2020) due to generator protection trip.
m) Ashuganj 225 STG was synchronized at 01:46(26/9/2020).
n) Manikganj 132/33 kV T-3 transformer was under shut down from 06:26(26/9/2020) to 12:06 for D/W. |  |  |  |  | About 5 MW power interruption occurred under Manikganj S/S areas
from 06:26(26/9/2020) to 12:06.
o) Pabna 132/33 kV T-3 transformer was under shut down from 06:52(26/9/2020) to 08:56 for C/M.
p) Jamalpur 132/33 kV T-3 & T-4 transformer was shut down at 07:37(26/9/2020) and was switched on
at 09:45 & 09:34 respectively.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-09-25 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 115 | 2803500 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 4860800 | Machine problem
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 40 | 1351616 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 92 | 1911090 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 343 | 8430690 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 352 | 7523000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 8553750 | Frequency control
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 1432320
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shorage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 90 | 1437720 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 40 | 446281 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 53451 | High voltage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 442944
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 1187520
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 308 | 7031521 | FGMO
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 1332432 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel Shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 466200
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 84 | 1016160 | Low demand.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 482427
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 276894 | Low demand.
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Machine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 54 | 1106880 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 779400 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 786100
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 270 | 4571562 | Low demand.
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 2642260
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 238224 | Reserve.
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 1652160
| Dhaka area Total |  |  |  | 5895 | 3143 | 62816902
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2900000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve.
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 44010
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 33120 | Reserve.
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 113 | 1477860 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Gas shortage
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 12545 | Transformer O/L
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 155023 | Reserve.
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 19920 | Reserve.
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2424000
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 389328
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 41 | 997920
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 48 | 336000 | Low demand.
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 10000
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 306 | 5570182
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 121255 | Reserve.
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Transformer O/L
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2428800
| Chattogram area Total |  |  |  | 2266 | 849 | 16919963
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 130 | 2223996
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 97 | 3395000 | ST Synchronized process
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 335 | 7234400 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 657648 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 54 | 660480
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 45 | 434909 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1244739
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 5 | 466690 | Low demand.
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 96 | 2182300
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | High voltage
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 412596 | Engine problem
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 140040 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 142 | 2948160
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 767600
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 9994 | Reserve.
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 18 | 448730 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 1376760
| Cumilla Area Total |  |  |  | 2980 | 1174 | 24604042
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 157 | 3583080 | Machine problem & Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 284616 | Engine problem
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 0 | 0 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9500
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 4149600 | High voltage
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 8 | 781200 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 382 | 8807996
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 87 | 2066000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 713760 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3074890
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 202 | 3503000 | Gas shortage.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1211400
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 47 | 1116576
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 210000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 66 | 1352544
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1847040
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 136 | 2483450
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 422000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 475152
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7070200 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 225180
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1229 | 25771192
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 919 | 22251636
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 1273920 | Engine problem
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 120 | 2954880 | Low demand.
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 370 | 7007040 | Gas Shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 220125
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 92160 | Reserve.
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1548 | 33799761
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 275520 | High voltage
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 30 | 521207
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 80 | 2032126 | GT-2 Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 77 | 1473405 | Engine problem
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 500 | 11327800 | Under maint unit 1
| Barisal Area Total |  |  |  | 1054 | 735 | 15630058
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Reserve.
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve.
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 74838
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | STG U/M & Gas Shortage
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 190 | 4085027 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 197 | 4318745 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 408 | 8737909 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 492720
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 10 | 190152
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 169506 | Engine problem
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 9120
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 184920 | Reserve.
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 45984 | Reserve.
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 1306560
| Rajshahi Area Total |  |  |  | 2183 | 943 | 19615481
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3593200 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 109 | 1068480
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 3231
| Rangpur Area Total |  |  |  | 605 | 259 | 4664911
| Total |  |  |  | 19892 | 10262 | 212630306
| Eastern Grid Total |  |  |  | 13766 | 6777 | 138920095
| Western Grid Total |  |  |  | 6126 | 3485 | 73710211
| National Grid Total |  |  |  | 19892 | 10262 | 212630306
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-09-25
| (a) ENTIRE EASTERN GRID : |  | 6546 | MW | (b) ENTIRE WESTERN GRID : |  | 3221 | MW
| i) Dhaka area |  | 3350 | MW | i) Khulna area |  | 1302 | MW
| ii) Chittagong area |  | 986 | MW | ii) Rajshahi area |  | 1048 | MW
| iii) Comilla area |  | 963 | MW | iii) Barisal area |  | 287 | MW
| iv) Mymensingh area |  | 810 | MW | iv) Rangpur area |  | 584 | MW
| v) Sylhet area |  | 437 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 9767 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 110 | 2:00 | Sherpur | 84 | 23:00 | Jhenida | 101 | 18:30
| Munsiganj | 114 | 22:00 | Srimongal | 44 | 19:30 | Bottail | 110 | 1:00
| Sonargaon | 73 | 20:00 | Shahjibazar | 104 | 19:30 | G.K Project | 51 | 19:30
| Shyampur | 182 | 1:00 | Fenchuganj | 35 | 19:30 | Faridpur | 171 | 0.041667
| Bhulta | 192 | 1:00 | Kulawara | 40 | 20:00 | Madaripur | 88 | 0.91667
| Madanganj | 43 | 23:00 | Sylhet | 106 | 19:00 | Sariatpur | 58 | 20:00
| Shitalakhya | 77 | 1:00 | Chatak | 28 | 20:00 | Gopalganj | 85 | 19:00
| Rahim steel | 4 | 7:00 | Sunamganj | 38 | 20:00 | Bagerhat | 80 | 20:00
| Matuail | 84 | 12:00 | Biani Bazar | 55 | 22:00 | Mongla | 32 | 1:00
| Ghorasal | 71 | 22:00 | Comilla (S) | 142 | 18:30 | Satkhira | 94 | 0.77083
| Narsingdi | 154 | 1:00 | Comilla(N) | 85 | 19:00 | Gallamari | 38 | 12:00
| Haripur (SBU) | 93 | 1:00 | Chandpur | 85 | 19:00 | Magura | 48 | 0.875
| Ullon | 62 | 13:00 | Feni | 98 | 19:30 | Norail | 38 | 19:00
| Hasnabad | 169 | 1:00 | Chowmuhani | 162 | 20:00 | Chuadanga | 44048 | 19:30
| Magbazar | 72 | 13:00 | Ashuganj | 55 | 22:00 | Barisal(N) | 36 | 0.79167
| Maniknagar | 72 | 1:00 | Daudkandi | 124 | 19:00 | Barisal (S) | 80 | 0.041667
| Bangabhaban | 14 | 1:00 | B.Baria | 139 | 20:00 | Patuakhali | 106 | 0.875
| Narinda | 68 | 23:00 | Ramganj | 106 | 19:00 | Bhandaria | 50 | 0.8125
| Dhanmondi | 124 | 13:00 | Chaddagram | 31 | 19:00 | Borhan Uddin | 41 | 21:00
| Lalbag | 68 | 1:00 | PHP | 11 | 18:00 | Ishurdi | 60 | 21:00
| Madartek | 65 | 22:00 | Madunaghat | 43 | 20:00 | Ruppur Paromanobik | 2 | 1:00
| Dhaka University |  |  | Hathazari | 77 | 0.8125 | Natore | 106 | 20:00
| Fatullah | 36 | 0.041667 | Khulshi | 160 | 0.45833 | Bogra | 136 | 19:00
| Mirpur | 91 | 19:00 | Halishahar | 112 | 0.77083 | Noagaon | 100 | 21:00
| Kalyanpur | 84 | 19:00 | Baraulia | 121 | 0.125 | Rajshahi | 131 | 20:00
| Gulshan | 92 | 18:30 | Sikalbaha | 24 | 0.77083 | Rajshahi New | 12 | 21:00
| Uttara | 72 | 18:00 | Dohazari | 84 | 0.77083 | C.Nawabganj | 65 | 21:00
| Uttara New | 26 | 19:00 | Cox'sbazar | 96 | 0.77083 | Amnura | 34 | 21:00
| Kamrangirchar | 67 | 19:00 | Chandraghona | 28 | 0.79167 | Pabna | 106 | 19:00
| Savar | 101 | 21:00 | Kaptai | 4.3 | 0.79167 | Shahjadpur | 90 | 20:00
| Bhasantec | 128 | 19:00 | A. Khaer Stl. | 8 | 0.45833 | Serajganj | 76 | 20:00
| Agargaon | 59 | 18:00 | Bakulia | 82 | 0.8125 | Niyamatpur | 43 | 1:00
| Satmosjid | 87 | 13:00 | Julda | 20 | 0.041667 | Joypurhat | 51 | 20:00
| Tongi | 82 | 0.45833 | TK chemical | 22.2 | 0.041667 | Sherpur(Bogura) | 41 | 19:30
| Kabirpur | 169 | 21:00 | Modern Steel | 13 | 0.083333 | Mohastangor | 42 | 19:00
| Basundhara | 115 | 18:30 | Shahmirpur | 20.5 | 0.041667 | Rangpur | 114 | 19:30
| Manikganj | 64 | 0.875 | Khagrachhari | 24 | 0.79167 | Lalmonirhat | 43 | 19:00
| Joydevpur | 133 | 1:00 | Matarbari | 33.5 | 0.79167 | Saidpur | 74 | 19:30
| New Tongi | 93 | 1:00 | Baroiar Hat | 40 | 0.75 | Purbasadipur | 86 | 19:00
| Korda | 187 | 9:00 | Rangamati | 10 | 0.75 | Thakurgaon | 63 | 19:00
| Dhamrai | 74 | 1:00 | Abul Khair 230 | 56 | 0.625 | Palashbari | 108 | 20:00
| Rajendrapur | 86 | 1:00 | BSRM | 102 | 0.041667 | Barapukuria | 39 | 1:00
| Valuka | 102 | 23:00 | GPH Ispat | 72 | 0 | Panchagar | 40 | 19:00
| Tangail | 174 | 21:00 | Goalpara | 25 | 0.91667 | Joldhaka | 24 | 21:00
| Mymensing | 145 | 1:00 | Central s/s | 72 | 19:30 | Kurigram | 45 | 19:00
| Kishorganj | 126 | 21:00 | Noapara | 46 | 19:00
| Netrokona | 103 | 22:00 | Jessore | 108 | 19:00
| Jamalpur | 126 | 23:00 | Benapol | 36 | 19:30
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-09-25 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 401 | 19:00 | 390 | 4:00 | Kaliakoir | 382 | 0.66667 | 359 | 0.5
| Bheramara | 392 | 18:30 | 388 | 11:00 | Bhulta | 395 | 0.77083 | 376 | 0.5
| Ashuganj(N) | 397 | 7:00 | 383 | 12:00 | Gopalganj | 417 | 0.625 | 394 | 0.875
| Payra | 417 | 19:00 | 404 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 7:00 | 230 | 13:00 | Comilla (N) | 235 | 19:30 | 226 | 12:00
| Ishurdi | 233 | 14:00 | 225 | 21:00 | Hathazari | 231 | 19:00 | 219 | 17:00
| Ashuganj | 238 | 18:30 | 230 | 12:00 | Megnaghat | 232 | 19:00 | 225 | 11:00
| Serajganj | 232 | 18:30 | 229 | 1:00 | Fenchuganj | 241 | 18:30 | 234 | 3:00
| Baghabari | 241 | 14:00 | 236 | 21:00 | Siddhirganj | 232 | 5:00 | 223 | 12:00
| Barapukuria | 239 | 14:00 | 233 | 20:00 | Maniknagar | 226 | 18:30 | 221 | 12:00
| Bogra | 229 | 18:00 | 221 | 20:00 | Agargaon | 228 | 8:00 | 217 | 12:00
| Rajshahi | 225 | 9:00 | 215 | 22:00 | Barisal | 246 | 19:00 | 231 | 1:00
| Khulna South | 234 | 17:00 | 223 | 22:00 | AKSML | 225 | 19:00 | 217 | 17:00
| Rampura | 229 | 18:30 | 222 | 12:00 | BSRM | 227 | 1:00 | 218 | 17:00
| Haripur | 230 | 19:00 | 221 | 12:00 | Bibiyana | 241 | 18:30 | 234 | 2:00
| Hasnabad | 230 | 19:30 | 220 | 12:00 | Bhulta | 233 | 19:00 | 223 | 17:00
| Shyampur | 227 | 19:00 | 217 | 12:00 | Ashuganj (S) | 235 | 20:00 | 228 | 12:00
| Aminbazar | 230 | 19:00 | 220 | 11:00 | Kaliakoir | 235 | 19:00 | 219 | 12:00
| Tongi | 230 | 18:00 | 217 | 11:00 | GPH | 222 | 19:00 | 216 | 6:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 135 | 24:00 | 127 | 11:00 | Hathazari | 137 | 0.77083 | 132 | 0.54167
| Munsiganj | 135 | 18:30 | 125 | 11:00 | Khulshi | 136 | 0.79167 | 129 | 0.66667
| Sonargaon | 135 | 19:30 | 126 | 8:00 | Halishahar | 139 | 0.79167 | 130 | 0.70833
| Shyampur | 135 | 19:00 | 128 | 12:00 | Baraulia | 137 | 0.79167 | 129 | 0.70833
| Bhulta | 127 | 18:30 | 122 | 5:00 | Sikalbaha | 140 | 19:00 | 130 | 0.70833
| Madanganj | 136 | 2:00 | 127 | 9:00 | Dohazari | 135 | 19:00 | 126 | 0.625
| Shitalakhya | 142 | 18:30 | 128 | 12:00 | Cox'sbazar | 129 | 0.79167 | 118 | 0.91667
| Rahim steal | 133 | 18:30 | 127 | 9:00 | Chandraghona | 137 | 0.77083 | 131 | 0.70833
| Matuail | 135 | 24:00 | 127 | 11:00 | Kaptai | 135 | 18:30 | 130 | 0.20833
| Ghorasal | 140 | 18:00 | 136 | 1:00 | A. Khaer Stl. | 135 | 0.79167 | 130 | 13:00
| Narsinghdi | 128 | 18:00 | 123 | 1:00 | Bakulia | 138 | 0.79167 | 129 | 0.20833
| Haripur (SBU) | 133 | 18:30 | 127 | 12:00 | Julda | 139 | 0.79167 | 131 | 0.66667
| Ullon | 136 | 22:00 | 129 | 13:00 | TK Chemical | 140 | 0.79167 | 130 | 13:00
| Hasnabad | 138 | 19:30 | 127 | 12:00 | Modern Steel | 138 | 0.77083 | 130 | 0.5
| Magbazar | 135 | 4:00 | 130 | 12:00 | Shahmirpur | 137 | 0.77083 | 132 | 0.25
| Maniknagar | 135 | 19:00 | 127 | 12:00 | Khagrachhari | 136 | 0.79167 | 131 | 0.083333
| Bangabhaban | 135 | 19:00 | 127 | 12:00 | Matarbari | 130 | 0.75 | 121 | 0.041667
| Narinda | 135 | 19:00 | 127 | 12:00 | Baroiar Hat | 131 | 0.875 | 128 | 0.625
| Dhanmondi | 135 | 19:00 | 129 | 13:00 | Rangamati | 137 | 0.79167 | 130 | 17:00
| Lalbag | 138 | 18:30 | 127 | 12:00 | Goalpara S/S | 135 | 11:00 | 130 | 21:00
| Madartek | 134 | 2:00 | 129 | 12:00 | Khulna Central S/S | 135 | 0.45833 | 130 | 21:00
| Dhaka University |  |  |  |  | Noapara | 134 | 18:00 | 127 | 2:00
| Fatuiiah | 135 | 0.77083 | 128 | 12:00 | Jessore | 132 | 14:00 | 121 | 21:00
| Mirpur | 136 | 19:00 | 129 | 13:00 | Benapol | 132 | 17:00 | 122 | 21:00
| Kalyanpur | 136 | 19:00 | 130 | 12:00 | Jhenida | 130 | 0.58333 | 116 | 21:00
| Gulshan | 134 | 19:00 | 129 | 12:00 | Bottail | 135 | 9:00 | 126 | 21:00
| Uttara | 135 | 19:00 | 128 | 12:00 | G.K Project | 141 | 0.70833 | 135 | 1:00
| Uttara New | 137 | 19:00 | 127 | 12:00 | Faridpur | 135 | 16:00 | 124 | 1:00
| Kamrangirchar | 137 | 19:00 | 125 | 12:00 | Madaripur | 137 | 0.66667 | 128 | 22:00
| Savar | 136 | 19:00 | 127 | 12:00 | Shariyatpur S/S | 138 | 0.33333 | 125 | 22:00
| Bhasantec | 138 | 19:00 | 130 | 12:00 | Gopalganj | 139 | 16:00 | 125 | 21:00
| Agargaon | 139 | 19:00 | 130 | 12:00 | Bagerhat | 134 | 11:00 | 121 | 2:00
| Satmosjid | 138 | 19:00 | 131 | 12:00 | Mongla | 131 | 0.5 | 121 | 1:00
| Tongi | 138 | 0.8125 | 130 | 15:00 | Satkhira | 135 | 0.8375 | 126 | 21:00
| Kabirpur | 137 | 15:00 | 128 | 12:00 | Gallamari | 136 | 18:00 | 130 | 1:00
| Basundhara | 135 | 18:30 | 129 | 12:00 | Magura | 130 | 14:00 | 115 | 21:00
| Manikganj | 140 | 19:00 | 131 | 16:00 | Norail | 129 | 0.58333 | 112 | 21:00
| Joydevpur | 143 | 19:00 | 136 | 13:00 | Chuadanga | 126 | 16:00 | 107 | 21:00
| New Tongi | 137 | 0.77083 | 128 | 12:00 | Barisal(N) | 140 | 8:00 | 130 | 21:00
| Kodda | 136 | 19:00 | 123 | 0.66667 | Barisal (S) | 137 | 0.25 | 127 | 1:00
| Dhamrai | 135 | 19:00 | 128 | 14:00 | Patuakhali(S) | 136 | 0.33333 | 121 | 1:00
| Rajendrapur | 134 | 19:00 | 122 | 16:00 | Bhandaria | 131 | 12:00 | 117 | 23:00
| Valuka | 131 | 15:00 | 119 | 21:00 | Ishurdi | 138 | 9:00 | 132 | 20:00
| Tangail | 136 | 7:00 | 126 | 21:00 | Ruppur Paromanobik | 137 | 15:00 | 132 | 20:00
| Mymensing | 135 | 16:00 | 121 | 21:00 | Natore | 138 | 18:00 | 130 | 21:00
| Kishorganj | 133 | 7:00 | 1255 | 22:00 | Bogra | 139 | 18:00 | 132 | 20:00
| Netrokona | 134 | 16:00 | 118 | 21:00 | Noagaon | 135 | 18:00 | 126 | 20:00
| Jamalpur | 139 | 15:00 | 127 | 20:00 | Rajshahi | 137 | 18:00 | 129 | 21:00
| Sherpur | 140 | 15:00 | 126 | 20:00 | Rajshahi New | 138 | 18:00 | 129 | 21:00
| Srimongal | 139 | 15:00 | 135 | 0.041667 | C.Nawabganj | 135 | 17:00 | 127 | 21:00
| Shahjibazar | 137 | 14:00 | 133 | 0.041667 | Amnura | 136 | 18:00 | 126 | 21:00
| Fenchuganj | 137 | 14:00 | 133 | 0.125 | Pabna | 136 | 18:00 | 129 | 21:00
| Khulawara | 135 | 7:00 | 133 | 0.041667 | Shahjadpur | 140 | 14:00 | 136 | 1:00
| Sylhet | 134 | 7:00 | 132 | 0.041667 | Serajganj | 136 | 14:00 | 130 | 21:00
| Chatak | 132 | 6:00 | 130 | 1:00 | Niyamatpur | 134 | 9:00 | 124 | 20:00
| Sunamganj | 132 | 8:00 | 129 | 0.041667 | Joypurhat | 136 | 18:00 | 126 | 20:00
| Biani Bazar | 133 | 7:00 | 129 | 0.91667 | Sherpur(Bogura) | 138 | 14:00 | 131 | 21:00
| Comilla(s) | 127 | 8:00 | 122 | 18:00 | Mohastangor | 138 | 18:00 | 131 | 20:00
| Comilla(n) | 136 | 18:30 | 131 | 12:00 | Rangpur | 136 | 14:00 | 126 | 20:00
| Chandpur | 132 | 18:00 | 129 | 17:00 | Lalmonirhat | 138 | 14:00 | 126 | 19:30
| Feni | 130 | 18:00 | 125 | 13:00 | Saidpur | 136 | 14:00 | 127 | 21:00
| Chowmuhani | 128 | 7:00 | 123 | 13:00 | Purbasadipur | 133 | 14:00 | 122 | 19:30
| Ashuganj | 138 | 7:00 | 135 | 1:00 | Thakurgaon | 130 | 15:00 | 123 | 19:00
| Daudkandi | 132 | 18:30 | 127 | 12:00 | Palashbari | 133 | 18:00 | 125 | 21:00
| B.Baria | 136 | 7:00 | 130 | 22:00 | Barapukuria | 139 | 14:00 | 133 | 21:00
| Ramganj | 128 | 8:00 | 118 | 16:00 | Panchagar | 134 | 14:00 | 123 | 20:00
| Chaddagram | 134 | 21:00 | 128 | 5:00 | Joldhaka | 132 | 15:00 | 123 | 20:00
| PHP | 132 | 19:00 | 126 | 12:00 | Kurigram
| Madanhat | 139 | 19:00 | 132 | 12:00

## L-Curve
Date | 2020-09-25
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 168 | 6554 | 3390 | 9944 |  |  |  | QF-LDC-11
0:30 | 140 | 6637.5 | 3402.5 | 10040 | Date: | 2020-09-25
1:00 | 112 | 6721 | 3415 | 10136
1:30 | 117.5 | 6583 | 3363.5 | 9946.5
2:00 | 123 | 6445 | 3312 | 9757
2:30 | 200.5 | 6316.5 | 3312 | 9628.5 | [5 empty] | Gen. at Eve. Peak | 10262 | 10262 MW (21:00 )
3:00 | 278 | 6188 | 3312 | 9500 | [6 empty] | 21:00
3:30 | 280.5 | 6090 | 3278 | 9368 | [5 empty] | Gen. at Day Peak | 7853 | 7853 MW (12:00 )
4:00 | 283 | 5992 | 3244 | 9236 | [6 empty] | 12:00
4:30 | 288.5 | 5973.5 | 3219.5 | 9193 | [5 empty] | Highest Generation | 10262
5:00 | 294 | 5955 | 3195 | 9150 | [6 empty] | 21:00
5:30 | 330.5 | 5780.5 | 3053.5 | 8834
6:00 | 367 | 5606 | 2912 | 8518
6:30 | 314.5 | 5406 | 2824.5 | 8230.5
7:00 | 262 | 5206 | 2737 | 7943
7:30 | 305.5 | 5176 | 2697 | 7873
8:00 | 349 | 5146 | 2657 | 7803
8:30 | 377 | 5093 | 2625.5 | 7718.5
9:00 | 405 | 5040 | 2594 | 7634
9:30 | 442.5 | 5021.5 | 2608 | 7629.5
10:00 | 480 | 5003 | 2622 | 7625
10:30 | 451 | 5044 | 2627 | 7671
11:00 | 422 | 5085 | 2632 | 7717
11:30 | 472 | 5081.5 | 2703.5 | 7785
12:00 | 522 | 5078 | 2775 | 7853
12:30 | 546.5 | 5151.5 | 2798.5 | 7950
13:00 | 571 | 5225 | 2822 | 8047
13:30 | 590.5 | 5071 | 2768.5 | 7839.5
14:00 | 610 | 4917 | 2715 | 7632
14:30 | 505 | 4843.5 | 2596 | 7439.5
15:00 | 400 | 4770 | 2477 | 7247
15:30 | 350 | 4699 | 2430.5 | 7129.5
16:00 | 300 | 4628 | 2384 | 7012
16:30 | 350 | 4613.5 | 2449.5 | 7063
17:00 | 400 | 4599 | 2515 | 7114
17:30 | 341 | 4941 | 2738 | 7679
18:00 | 282 | 5283 | 2961 | 8244
18:30 | 167.5 | 5856 | 3180.5 | 9036.5
19:00 | 53 | 6429 | 3400 | 9829
19:30 | 63 | 6803 | 3381 | 10184
20:00 | 2 | 6790 | 3394 | 10184 |  |  |  | Executive Engineer
20:30 | 37.5 | 6783.5 | 3439.5 | 10223 |  |  |  | Network Operation Division
21:00 | 73 | 6777 | 3485 | 10262
21:30 | 92 | 6745 | 3486.5 | 10231.5
22:00 | 111 | 6713 | 3488 | 10201 |  |  |  |  | Page 6 of 7
22:30 | 138.5 | 6706.5 | 3467.5 | 10174
23:00 | 166 | 6700 | 3447 | 10147
23:30 | 167 | 6627 | 3418.5 | 10045.5
24:00 | 168 | 6554 | 3390 | 9944
10262 MW (21:00 )
7853 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-09-25 |  | Energy | 212630306
[10 empty] | 2020-09-25 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3380 | 919 | 2274 | 2396 | 650 | 110 | 184 | 0 | 134
0:30 | 3323.5 | 927.5 | 2228 | 2540.5 | 680 | 76 | 180 | 0 | 136 | Date: | 2020-09-25
1:00 | 3267 | 936 | 2182 | 2685 | 710 | 42 | 176 | 0 | 138
1:30 | 3283.5 | 935.5 | 2162.5 | 2530.5 | 700 | 42.5 | 156 | 0 | 136 | [7 empty] | Total Energy | 212.6303 | Total Energy Gen 212.630 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 212.630 MKWHr
2:00 | 3300 | 935 | 2143 | 2376 | 690 | 43 | 136 | 0 | 134 | [7 empty] | Energy not Served | 0
2:30 | 3294.5 | 935.5 | 2148.5 | 2255.5 | 690 | 43.5 | 128 | 0 | 133 | [7 empty] | Energy Requirement | 212.6303
3:00 | 3289 | 936 | 2154 | 2135 | 690 | 44 | 120 | 0 | 132
3:30 | 3328 | 936 | 2157 | 1971 | 680 | 44 | 120 | 0 | 132 | [6 empty] | Shortage
4:00 | 3367 | 936 | 2160 | 1807 | 670 | 44 | 120 | 0 | 132
4:30 | 3363.5 | 935.5 | 2149 | 1781 | 670 | 44 | 120 | 0 | 130
5:00 | 3360 | 935 | 2138 | 1755 | 670 | 44 | 120 | 0 | 128
5:30 | 3348.5 | 932.5 | 2070 | 1497.5 | 670 | 43.5 | 150 | 0 | 122
6:00 | 3337 | 930 | 2002 | 1240 | 670 | 43 | 180 | 0 | 116
6:30 | 3244 | 929.5 | 1907 | 1149.5 | 650 | 42.5 | 199 | 0 | 108 |  |  |  |  | Coal
7:00 | 3151 | 929 | 1812 | 1059 | 630 | 42 | 218 | 0 | 100
7:30 | 3117 | 929 | 1782 | 1078 | 604.5 | 42 | 218 | 0 | 98 |  |  |  | Oil |  |  |  | ,
8:00 | 3083 | 929 | 1752 | 1097 | 579 | 42 | 218 | 0 | 96
8:30 | 3088 | 929 | 1705.5 | 1068.5 | 564 | 41.5 | 218 | 0 | 98
9:00 | 3093 | 929 | 1659 | 1040 | 549 | 41 | 218 | 0 | 100
9:30 | 3083.5 | 929.5 | 1676 | 1039.5 | 549 | 41 | 201 | 0 | 104
10:00 | 3074 | 930 | 1693 | 1039 | 549 | 41 | 184 | 0 | 108
10:30 | 3145.5 | 929.5 | 1800 | 935 | 549.5 | 41 | 152 | 0 | 110
11:00 | 3217 | 929 | 1907 | 831 | 550 | 41 | 120 | 0 | 112
11:30 | 3255.5 | 928.5 | 1976 | 794 | 550 | 41.5 | 120 | 0 | 109
12:00 | 3294 | 928 | 2045 | 757 | 550 | 42 | 120 | 0 | 106
12:30 | 3340 | 929 | 2075 | 777.5 | 549.5 | 42 | 120 | 0 | 109
13:00 | 3386 | 930 | 2105 | 798 | 549 | 42 | 120 | 0 | 112
13:30 | 3386 | 930 | 2105 | 798 | 549 | 42 | 120 | 0 | 112
14:00 | 3386 | 930 | 2105 | 798 | 549 | 42 | 120 | 0 | 112
14:30 | 3191.5 | 929.5 | 1930.5 | 799.5 | 499.5 | 59.5 | 120 | 0 | 110
15:00 | 2997 | 929 | 1756 | 801 | 450 | 77 | 120 | 0 | 108
15:30 | 3033 | 929 | 1739.5 | 674.5 | 435 | 77 | 128.5 | 0 | 107
16:00 | 3069 | 929 | 1723 | 548 | 420 | 77 | 137 | 0 | 106
16:30 | 3082.5 | 929 | 1789 | 518.5 | 420 | 77 | 137 | 0 | 107
17:00 | 3096 | 929 | 1855 | 489 | 420 | 77 | 137 | 0 | 108
17:30 | 3197.5 | 923.5 | 1941 | 775 | 455 | 77 | 189.5 | 0 | 119
18:00 | 3299 | 918 | 2027 | 1061 | 490 | 77 | 242 | 0 | 130
18:30 | 3308.5 | 918 | 2023 | 1724.5 | 535 | 95 | 298.5 | 0 | 134
19:00 | 3318 | 918 | 2019 | 2388 | 580 | 113 | 355 | 0 | 138
19:30 | 3424 | 919 | 2071 | 2571 | 590 | 113 | 356 | 0 | 140
20:00 | 3506 | 919 | 2209 | 2426 | 640 | 113 | 231 | 0 | 140
20:30 | 3552 | 919 | 2252.5 | 2383 | 645 | 113 | 217.5 | 0 | 141
21:00 | 3598 | 919 | 2296 | 2340 | 650 | 113 | 204 | 0 | 142
21:30 | 3524.5 | 919.5 | 2303.5 | 2359.5 | 650 | 113 | 219.5 | 0 | 142
22:00 | 3451 | 920 | 2311 | 2379 | 650 | 113 | 235 | 0 | 142
22:30 | 3425.5 | 920 | 2320 | 2387.5 | 650 | 111.5 | 218.5 | 0 | 141
23:00 | 3400 | 920 | 2329 | 2396 | 650 | 110 | 202 | 0 | 140
23:30 | 3390 | 919.5 | 2301.5 | 2396 | 650 | 110 | 193 | 0 | 137 | Max Temp. in Dhaka |  | 31.8° C
24:00 | 3380 | 919 | 2274 | 2396 | 650 | 110 | 184 | 0 | 134
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 212.630 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 212.630 MKWHr
Note on W13: Author:

## Generation
g | 2020-09-25
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 42 | 43 | 44 | 44 | 44 | 43 | 42 | 42 | 41 | 41 | 41 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 43 | 43 | 43 | 43 | 43 | 40 | 40 | 949860
2 | Karnaphuli Hydro PP Unit-4 & 5 | [14 empty] | 35 | 35 | 35 | 35 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 528000
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2900000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 2 | 4 | 2 | 4 | 6 | 7 | 2 | 9 | 8 | 2 | 2 | [9 empty] | 44010
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [15 empty] | 17 | 17 | 51 |  | 51 | 51 |  |  |  |  | 0 | 155023
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 12545
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 285 | 285 | 301 | 301 | 285 | 271 | 265 | 285 | 283 | 293 | 307 | 302 | 285 | 261 | 292 | 308 | 317 | 310 |  | 253 | 290 | 288 | 308 | 299 | 297 | 266 | 7031521
18 | Kodda 300 MW PP Unit-2 (Summit) | 300 | 286 | 280 | 100 | 95 | 117 | 215 | 250 | 250 | 250 | 120 | 70 | 70 | 70 | 70 | 60 | 45 | 50 |  | 195 | 280 | 286 | 270 | 293 | 300 | 245 | 4571562
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 53 |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 434909
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2803500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 197 | 200 | 200 | 200 | 200 | 4860800
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 2223996
32 | Ashuganj 50 MW PP | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 26 | 23 | 29 | 29 | 29 | 29 |  | 29 | 29 | 29 | 29 | 26 | 26 | 26 | 657648
33 | Ashuganj 225 MW CCPP | 182 | 182 | 184 | 191 | 182 | 182 | 144 | 144 | 143 | 142 | 139 | 139 | 142 | 143 | 141 | 140 | 139 | 140 |  | 144 | 143 | 142 | 97 | 34 | 37 | 50 | 3395000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 260 | 260 | 260 | 260 | 310 | 290 | 310 | 260 | 260 | 285 | 295 | 285 |  | 260 | 260 | 310 | 335 | 315 | 310 | 310 | 7234400
35 | Ashuganj 55 MW PP (Precision) | 55 | 55 | 56 | 55 | 55 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 10 |  | 46 | 52 | 52 | 54 | 54 | 54 | 54 | 660480
36 | Chandpur 150 MW CCPP | 85 | 89 | 95 | 96 | 96 | 85 | 86 | 89 | 95 | 94 | 96 | 96 | 86 | 85 | 85 | 94 | 96 | 95 |  | 86 | 92 | 92 | 96 | 96 | 96 | 94 | 2182300
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 339 | 339 | 339 | 345 | 339 | 341 | 338 | 338 | 339 | 340 | 356 | 348 | 368 | 340 | 339 | 343 | 360 | 385 |  | 348 | 339 | 338 | 343 | 353 | 341 | 339 | 8430690
40 | Meghnaghat 450 MW CCPP(MPL) | 380 | 350 | 350 | 350 | 350 | 350 | 300 | 300 | 300 | 300 | 400 | 400 | 400 | 340 | 300 | 300 | 300 | 380 |  | 370 | 370 | 420 | 420 | 420 | 420 | 420 | 8553750
41 | Haripur 360MW CCPP(HPL) | 351 | 351 | 352 | 350 | 352 | 309 | 254 | 255 | 255 | 254 | 323 | 324 | 343 | 285 | 273 | 273 | 274 | 273 |  | 355 | 355 | 353 | 352 | 350 | 351 | 351 | 7523000
42 | RPCL 210MW CCPP | 123 | 142 | 144 | 156 | 157 | 158 | 160 | 158 | 156 | 155 | 152 | 152 | 156 | 142 | 142 | 159 | 158 | 158 |  | 160 | 160 | 160 | 157 | 158 | 158 | 160 | 3583080
43
44 | Fenchugonj CCPP Phase-1 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 88 | 88 | 87 | 90 | 89 | 90 |  | 90 | 90 | 88 | 87 | 89 | 89 | 89 | 2066000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 713760
46 | Shajibazar 330 MW CCPP | 140 | 141 | 141 | 138 | 142 | 140 | 140 | 140 | 143 | 142 | 142 | 142 | 142 | 140 | 140 | 142 | 142 | 144 |  | 142 | 202 | 200 | 202 | 200 | 200 | 200 | 3503000
47 | Shahjibazar GTPP Unit- 8 & 9 | 64 | 64 | 64 | 64 | 64 | 64 | 55 | 40 | 40 | 40 | 40 | 60 | 61 | 40 | 52 | 66 | 65 | 65 |  | 40 | 40 | 52 | 66 | 67 | 67 | 67 | 1352544
48 | Shahjibazar 86MW PP (Shahjibazar) | 84 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 40 | 40 | 40 | 85 | 85 | 84 | 85 | 84 | 84 | 84 |  | 84 | 84 | 85 | 85 | 84 | 85 | 85 | 1847040
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 145 | 145 | 145 | 145 | 145 | 145 | 120 | 80 | 80 | 80 | 120 | 120 | 130 | 80 | 20 | 20 | 30 | 49 |  | 86 | 103 | 125 | 136 | 105 | 96 | 97 | 2483450
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 18 | 17 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 422000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 10 |  | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 9 | 10 | 225180
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 210000
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 47 | 47 | 50 | 50 | 48 | 50 | 53 | 53 |  | 53 | 53 | 50 | 50 | 50 | 50 | 50 | 1211400
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 8 | 24 |  | 24 | 24 | 24 | 24 |  |  | 8 | 475152
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 285 | 290 | 300 | 285 | 280 | 270 | 280 | 270 | 285 | 300 | 300 | 300 | 260 | 260 | 280 | 300 | 320 |  | 270 | 285 | 280 | 300 | 300 | 300 | 290 | 7070200
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 55 | [12 empty] | 17 | 17 | 17 | 17 | 35 |  | 35 | 35 | 35 |  |  |  | 0 | 276894
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) |  |  |  |  | 18 | 18 | 18 | 19 | 19 | 20 | 20 | 20 | 20 | 20 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 389328
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 442944
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 14 | 14 | 14 | 14 | 14 | 14 | [6 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 284616
63 | Impoprt (Tripura) | 138 | 134 | 132 | 132 | 128 | 116 | 100 | 96 | 100 | 108 | 112 | 106 | 112 | 104 | 108 | 106 | 108 | 130 |  | 138 | 140 | 140 | 142 | 142 | 140 | 134 | 2948160
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 39 | 37 | 39 | 39 | 39 | 39 | 42 | 37 | 34 | 41 | 38 | 39 |  | 29 | 40 | 40 | 41 | 42 | 42 | 42 | 997920
65 | Feni 22MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 15 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 412596
66 | Feni 11 MW PP (Doreen) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 8 | 8 | 5 | 5 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 140040
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 27 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 767600
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 15 | 21 | 21 | 21 | 21 |  | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 448730
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 29 | 29 | 29 | 29 | 29 | 25 | 28 | 28 | 28 | 25 | 25 | 16 | 13 | 13 | 13 | 6 | 6 | 13 |  | 20 | 20 | 20 | 29 | 29 | 29 | 29 | 506880
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 779400
72 | Rupganj 33 MW PP(Summit) | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 8 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 786100
73 | Ghorashal 108MW PP (Regent) | 87 | 87 | 87 | 87 | 87 | 87 | 86 | 43 | 43 | 42 | 42 | 85 | 91 | 91 | 91 | 91 | 91 | 91 |  | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 1911090
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | 113 | 113 | 113 | 113 | 113 | 35 | 8 | 8 | [9 empty] | 42 |  | 113 | 113 | 113 | 113 | 105 | 108 | 113 | 1376760
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 100 | 100 | 100 | 100 | 48 | [6 empty] | 2 | 7 | 7 | 7 | 7 | 12 |  | 65 | 100 | 100 | 100 | 100 | 100 | 100 | 1187520
78 | Gazipur 52 MW PP
79 | Kodda 150MW PP | 16 | 16 |  |  |  | 60 | 98 | 98 | 98 | 64 | [7 empty] | 25 |  | 84 | 84 | 84 | 84 | 115 | 82 | 64 | 1016160
80 | Jamalpur 95 MW PP(Powerpac) | [25 empty] | 0 | 0
81 | Jangalia 52 MW PP (Lakdanavi) | [17 empty] | 1 |  | 8 | [6 empty] | 9994
| Gazipur 100 MW PP | [6 empty] | 4 | 34 | 34 | 34 | [7 empty] | 1 |  | 41 | 50 | 14 |  |  |  | 0 | 238224
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 1 | 2 | 1 | 2 | 2 | 1 | 0 | 1 | 0 | 0 | [9 empty] | 10000
| Jodiac Power | 54 | [18 empty] | 19 | 34 |  |  |  |  | 0 | 121255
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | 97 | 97 | 97 | 48 | 48 | 48 | 32 | 46 | 30 | 30 | 30 | 30 | 37 | 48 | 30 | 30 | 30 | 30 |  | 68 | 80 | 80 | 90 | 97 | 97 | 97 | 1437720
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [17 empty] | 4 |  | 30 | [5 empty] | 0 | 53451
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | 100 | 100 | 100 | 100 | 100 | 75 | 15 |  |  |  |  | 1 | 14 | 53 | 55 | 38 | 24 | 36 |  | 82 | 100 | 100 | 100 | 100 | 100 | 100 | 1432320
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 104 | 104 | 53 | 17 | 17 | 17 | 17 | 17 | 17 | 23 | 53 | 53 | 38 | 17 | 40 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 1652160
88 | Ghorashal 78.5 MW PP(MAX) | 66 | 66 | 66 | 66 | 66 | 66 | 65 | 40 | 40 | 40 | 40 | 40 | 50 | 64 | 64 | 66 | 66 | 65 |  | 40 | 40 | 40 | 40 | 50 | 66 | 65 | 1351616
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [17 empty] | 10 |  | 10 | [5 empty] | 0 | 19920
92 | Fenchuganj 44MW (Energyprima) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 44 | 44 | 44 | 47 | 47 | 47 | 47 | 47 | 47 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 1116576
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1244739
94 | Gagnagar 102 MW PP (Digital Power) | 93 | 93 | 93 | 93 | 93 | 50 | 8 | 8 | 8 | 8 | 8 | 7 | 16 | 40 | 40 | 16 | 16 | 24 |  | 70 | 85 | 85 | 93 | 93 | 93 | 93 | 1332432
95 | Patenga 50MW PP (Baraka) | [17 empty] | 1 |  | 18 | 10 | 6 |  |  |  | 0 | 33120
96 | Chattogram 108 MW PP (ECPV) | 91 | [18 empty] | 39 | 82 | 86 | 48 | 13 | 12 | 0 | 336000
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | 40 | 40 | 40 | 40 | 40 | [14 empty] | 28 | 40 | 40 | 40 | 40 | 40 | 40 | 446281
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | [15 empty] | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 482427
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 130 | 130 | 163 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 163 | 163 | 163 | 163 | 163 | 3074890
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | 0 | [9 empty] | 9500
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | [15 empty] | 35 |  | 54 | 54 | 54 | 54 | 54 | 54 | 0 | 466200
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 200 | 200 | 200 | 200 | 200 | 200 | 170 | 170 | 170 | 170 | 170 | 170 | 180 | 197 | 100 | 32 | 32 | 53 |  | 199 | 199 | 200 | 200 | 200 | 200 | 194 | 4149600
112 | Aurahati 100MW PP (Aggreko) | [25 empty] | 0 | 0
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 145 | 125 | 117 | 112 | 112 | 117 | 146 | 149 | 149 | 105 | 80 | 74 | 72 | 63 | 21 | 22 | 37 |  | 92 | 130 | 132 | 149 | 149 | 149 | 144 | 2642260
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2424000
116 | Chandpur 200MW (Desh energy) | [25 empty] | 0 | 0
117 | Ashuganj 150MW PP (Midland) | 100 | 50 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 |  | 62 | 80 | 15 | 5 | 5 | 5 | 5 | 466690
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 95 | 95 | 35 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  |  |  |  | 6 |  | 36 | 8 | 8 | 8 | 56 | 80 | 103 | 781200
| Anwara 300 MW PP (United) | 307 | 307 | 307 | 307 | 305 | 252 | 252 | 197 | 161 | 160 | 160 | 161 | 161 | 161 | 161 | 84 | 74 | 199 |  | 303 | 306 | 303 | 306 | 306 | 306 | 307 | 5570182
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2428800
120 | Eastern Zone Total | 6721 | 6445 | 6188 | 5992 | 5955 | 5606 | 5206 | 5146 | 5040 | 5003 | 5085 | 5078 | 5225 | 4917 | 4770 | 4628 | 4599 | 5283 |  | 6429 | 6803 | 6790 | 6777 | 6713 | 6700 | 6554 | 138920095
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 115 | 115 | 115 | 105 | 115 | 29 | [11 empty] | 66 |  | 115 | 115 | 115 | 99 | 99 | 99 | 115 | 1273920
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
| Khulna 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2954880
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | [18 empty] | 35 | 35 | 17 |  |  |  | 0 | 92160
130
131
132
133
| Barisal 110 MW PP (Summit ) | [17 empty] | 11 |  | 48 | 48 | 48 | 48 | 48 | 32 | 16 | 275520
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 78 | 78 | 78 | 77 | 77 | 77 | 77 | 78 | 33 | 34 | 33 | 33 | 43 | 43 | 43 | 33 | 34 | 39 |  | 78 | 76 | 76 | 77 | 78 | 78 | 77 | 1473405
| Bhola 225 MW CCPP | 86 | 86 | 86 | 87 | 87 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2032126
140 | Bhola 33 MW PP (Venture) | 30 | 29 | 28 | 27 | 27 | 24 | 20 | 18 | 17 | 18 | 15 | 15 | 16 | 18 | 18 | 16 | 17 | 24 |  | 26 | 27 | 30 | 30 | 32 | 31 | 31 | 521207
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | 24 | [16 empty] | 8 |  | 16 | 16 | 16 | 40 | 40 | 40 | 40 | 220125
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 936 | 935 | 936 | 936 | 935 | 930 | 929 | 929 | 929 | 930 | 929 | 928 | 930 | 928 | 929 | 929 | 929 | 918 |  | 918 | 919 | 919 | 919 | 920 | 920 | 919 | 22251636
147 | Bheramara 410 MW CCPP | 250 | 255 | 260 | 270 | 275 | 290 | 240 | 240 | 245 | 245 | 245 | 290 | 320 | 285 | 240 | 240 | 240 | 310 |  | 345 | 340 | 340 | 370 | 350 | 340 | 340 | 7007040
148 | Payra 1320 MW | 560 | 540 | 540 | 520 | 520 | 520 | 480 | 430 | 400 | 400 | 400 | 400 | 400 | 400 | 320 | 290 | 290 | 350 |  | 430 | 440 | 490 | 500 | 500 | 500 | 500 | 11327800
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 149 | 149 | 150 | 150 | 149 | 148 | 130 | 130 | 130 | 140 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3593200
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 165 | 167 | 165 | 165 | 161 | 157 | 149 | 130 | 130 | 130 | 130 | 151 | 172 | 179 | 148 | 137 | 146 | 169 |  | 174 | 170 | 173 | 190 | 201 | 190 | 184 | 4085027
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 169 | 171 | 164 | 175 | 175 | 170 | 140 | 130 | 130 | 130 | 130 | 160 | 178 | 177 | 130 | 130 | 151 | 180 |  | 196 | 190 | 196 | 197 | 197 | 192 | 187 | 4318745
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 414 | 405 | 410 | 414 | 405 | 320 | 310 | 310 | 326 | 352 | 365 | 404 | 376 | 302 | 284 | 253 | 342 | 348 |  | 282 | 303 | 344 | 408 | 412 | 414 | 370 | 8737909
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 492720
163 | Bogura 20 MW PP (Energyprima) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  |  |  | 10 | 10 | 10 | 10 |  | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 190152
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 169506
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [17 empty] | 30 |  | 44 | 44 | [5 empty] | 74838
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [19 empty] | 8 | [5 empty] | 0 | 9120
170 | Chapainawabganj 100 MW Peaking PP | 40 | [16 empty] | 16 |  | 56 | 57 | 27 |  |  |  |  | 184920
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [17 empty] | 4 |  | 30 | [5 empty] | 0 | 45984
172 | Confidence Power Bogura Unit-1 113 MW | 109 | 109 | 109 | 109 | 109 | [12 empty] | 90 |  | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 1306560
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 112 | 50 | [13 empty] | 23 |  | 101 | 103 | 105 | 109 | 113 | 113 | 113 | 1068480
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [9 empty] | 3231
178
178