## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-08-19 | Monday
|  | Date (day): | 2019-08-19 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13422 | MW |  |  | (b) At Evening Peak Hour : |  | 15140 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-08-18 | 2019-08-19 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 70 | 70 | 70 | 70 |  | 15
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 189 | 189 | 190 | 190
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 380 | 320 | 350 | 350
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 40 | 74 | 50 | 75
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 47 | 84 | 90 | 90
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 20 | 20 | 20 | 20 | 20 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 371 | 316 | 350 | 350 |  |  | FGMO
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 303 | 300 | 300 | 300
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 360 | 360 | 350 | 350 |  |  | Machine problem
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 285 | 265 | 280 | 280 |  |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 0 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 152 | 120 | 100 | 150 | 60 |  | Gas shortage
| Siddhirganj Desh |  | HSD | QRPP | 96*1.2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217 | 217 | 217 | 50 | 0 | 0 | 0 |  | 217 | Under maint.
| Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 24 | 47 | 46 | 46 |  | 5 | Engine problem
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 35 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 100 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 43 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 72 | 72 | 72 |  | 36 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 32 | 43 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 45 | 51 | 51 | 51 |  | 10 | Engine problem
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 30 | 33 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 105 | 105 | 100 | 100
| Dhaka area Total |  |  |  |  | 5929 | 5693 | 2591 | 2730 | 3781 | 4456 | 185 | 791
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Under maint.
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 12 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 45 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 212 | 214 | 215 | 215
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 179 | 204 | 215 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 130 | 130 | 130 | 150
44 | Sikalbaha 51 MW PP(Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | Contract expired
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 50 | 100
46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D
47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 25 | 50 | 80
48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 10 | 100 | 100
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 10 | 100 | 100 | 100
50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 13 | 45 | 10 | 25
51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 97 | 95 | 97 |  | 11 | Engine problem
52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5.94 | 0 | 4.4 | 0
53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 16 | 105 | 230 | 260
| Jodiac Power |  | HFO | IPP | 54.36 | 0 | 0 | 18 | 0 | 0 | 0
| Karnaphuli Power Lid. |  | HFO | IPP | 110 | 0 | 0 | 113 | 50 | 113 | 113 |  |  | RRT
| Chattogram area Total |  |  |  |  | 2113 | 2053 | 840.94 | 1172 | 1529.4 | 1652 | 260 | 109
54 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 80 | 120 | 120 |  |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 80 | 100 | 100 |  |  | Gas shortage
55 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 193 | 181 | 220 | 220 |  |  | FGMO
56 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 240 | 250 | 250 | 360 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 305 | 360 | 360 |  |  | FGMO
58 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 30 | 33 | 33 | 33 |  | 12 | Engine problem
59 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 10 | 10 | 52 | 52
60 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract expired
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 68 | 68 | 127 |  | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 10 | 43 | 43 | 43 |  | 8 | Engine problem
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 55 | 150 | 150
64 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract expired
65 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
66 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 138 | 140 | 140 | 140
67 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 200 | 200 | 200
68 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 15 | 21 | 22 | 22
69 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 140 | 168 | 131 | 185
70 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 29 | 33 | 33
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 52 | 52 | 52
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 21 | 20 | 20 |  | 5 | Engine problem
73 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1232 | 1687 | 2005 | 2419 | 256 | 25
74 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 151 | 172 | 204 | 204
75 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
76 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 90 | 95 | 95
77 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.6 | 0 | 1.6 | 0
78 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 7 | 195 | 200 | 200
79 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 65 | 115 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 253.6 | 592 | 635.6 | 634 | 0 | 0
80 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 56 | 60 | 60 | 60
81 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 58 | 58 | 58 | 58
82 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 130 | 163 | 163
83 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 154 | 152 | 160 | 160 |  |  | FGMO
84 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 16 | 50 | 51 | 51
85 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 15 | 50 | 44 | 44
86 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
87 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 59 | 64 | 63 | 63 |  |  | FGMO
88 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 75 | 73 | 75
89 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 43 | 43 | 44 | 44 |  | 6 | Engine problem
90 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 110 | 70 | 120 | 120
91 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 17 | 17 | 17 |  | 3 | Engine problem
92 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 42 | 33 | 42 | 43 |  | 7 | Engine problem
93 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
94 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 285 | 300 | 320 |  |  | FGMO
95 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285 MW | 285 | 285 | 0 | 0 | 0 | 0 |  |  | Under maint.
96 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1879 | 1834 | 1055 | 1129 | 1240 | 1263 | 0 | 16
97 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 32
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 926 | 932 | 943 | 943
| Khulna 115 MW PP (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
98 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 115 | 115 | 115
99 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 40 | 0 | 42
100 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 200 | 200
101 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 56 | 0 | 75
102 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 280 | 330 | 320 | 410
103 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
104 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 80 | 100
105 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 105 | 105 | 105
106 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 88 | 88 | 50 | 100 |  | 5 | Engine problem
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 1311 | 1806 | 1853 | 2162 | 0 | 5
107 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 70 | 110
108 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
109 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 24 | 37 | 25 | 35
110 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 83 | 153 | 135 | 135
111 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 90 | 97 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 197 | 397 | 325 | 405 | 0 | 0
112 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 55 | 60 | 60 | 60
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
113 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
114 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 30
115 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 12 | 50 | 40 | 50
116 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 24 | 50 | 50
117 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 47 | 47
118 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 205 | 190 | 215 | 215 |  |  | FGMO
119 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas Shortage
120 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 210 | 186 | 205 | 215 |  |  | FGMO
121 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 386 | 334 | 400 | 400
122 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 0 | 35
123 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
124 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 16 | 14 | 16 | 15
125 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
126 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 25 | 52 | 52
127 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 94 | 80 | 100
128 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
129 | Bagura 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 36 | 113 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 947 | 1201 | 1561 | 1665 | 220 | 100
130 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 93 | 91 | 90 | 90
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
131 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 250 | 270 | 280 | 280
132 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
133 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  |  | Under maint.
| Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 0 | 0 | 0 | 113 | 114 | 114
| Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 8.4 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 572 | 492 | 351.4 | 474 | 492 | 484 | 0 | 105
| Total |  |  |  |  | 18969 | 18446 | 8778.94 | 11188 | 13422 | 15140 | 921 | 1151
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8396.8034 | 10701 | 12837.7567 | 14480.9743
A. |  | 2019-08-18 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 11188 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 7667.61 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11188 | MW
3 | Day peak Generation : |  |  | 8778.94 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10701 | MW
4 | Evening peak Generation : |  |  | 11188 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 221.0269 | MKWHr | By Solar | 0.17625 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 145.6372 | MKWHr |  | By Oil: | 36.8784 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 8.5479 | MKWHr |  | By Hydro: | 4.8475 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 921 | MW | Dhaka | 3376 | 3376 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1151 | MW | Chittagong | 1074 | 1074 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2072 | MW | Khulna | 1418 | 1418 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1325.99 | MMCFD |  |  | Rajshahi | 1184 | 1184 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 141369656.554 | ii) Oil : | Taka | 275134971 | Comilla | 1085 | 1085 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 39972121.68 | Total | Taka | 456476749.234 | Mymensingh | 972 | 972 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.655 | MKWHr. | Sylhet | 495 | 495 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -12 | MW (E to W) at | 21:00 | hrs | Barisal | 340 | 340 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -170 | MW at | 4:00 | hrs | Rangpur | 757 | 757 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.0° C |  |  | Total | 10701 | 10701 |  | 0
B. |  | 2019-08-19 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 33.9° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15140 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9500 | MW
4 | Reserve(Generation end) |  |  |  | 3240 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 235.093 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8108.7 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.4625 | MKWHr. | ii) HVDC Flow at Peak Time |  | 932 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.4771 | MKWHr. | iii) Maximum HVDC Flow : |  | 934 | MW at | 16:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 105.71 |  | (b) Today: | 105.76 |  | (c) Rule Curve: |  | 94.76
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-08-18
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Lid. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence) | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 70 | 190 | 0 | 0 | 350 | 87 | 40 | 345 | 355 |  | 20 | 350 | 272 | 0 | 0 | 0 | 207 | 0 | 120 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 46 | 35 | 0 | 0 | 22 | 25 | 13 | 33 | 33 | 0 | 0 | 123 | 90 | 100 | 0 | 0 | 204 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 46 | 22 | 42 | 135 | 0 | 0 | 0 | 260 | 181 | 55 | 140 | 27 | 54 | 0 | 43 | 0 | 0 | 43 | 21 | 11 | 25 | 20 | 160 | 157 | 91 | 20 | 0 | 60 | 58 | 48 | 50 | 130 | 152 | 63 | 70 | 45 | 48 | 0 | 31 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 100 | 199 | 0 | 0 | 108 | 53 | 0 | 0 | 15 | 0 | 113 |  | 834 | 0 | 320 | 0 | 32 | 0 | 0 | 0 | 35 | 23 | 16 | 134 | 35 | 16 | 0 | 0 | 60 | 50 | 0 | 95 | 12 | 8 | 0 | 26 | 0 | 22 | 16 | 11 | 91 | 0 | 251 | 0 | 0 | 193 | 0 | 0 | 0 | 96 | 0 | 157 | 0 | 361 | 105 | 0 | 75 | 88 | 113 | 0 | 0 |  | 6614 | 3275 | 9889 | 4169 | 834 | 2240 | 1712 | 342 | 213 | 219 | 160 | 0 | 0 | 105.64
2:00 | 70 | 190 | 0 | 0 | 350 | 87 | 40 | 345 | 354 |  | 20 | 350 | 285 | 0 | 0 | 0 | 207 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 35 | 0 | 0 | 22 | 25 | 13 | 33 | 33 | 0 | 0 | 122 | 90 | 100 | 0 | 0 | 205 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 41 | 135 | 0 | 0 | 0 | 260 | 181 | 55 | 140 | 27 | 54 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 25 | 20 | 156 | 157 | 91 | 20 | 0 | 60 | 58 | 48 | 50 | 130 | 149 | 62 | 70 | 45 | 48 | 0 | 31 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 70 | 165 | 0 | 0 | 115 | 35 | 0 | 0 | 15 | 0 | 113 |  | 834 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 35 | 23 | 0 | 136 | 34 | 16 | 0 | 0 | 60 | 25 | 0 | 80 | 12 | 8 | 0 | 26 | 0 | 22 | 16 | 11 | 92 | 0 | 250 | 0 | 0 | 186 | 0 | 0 | 0 | 82 | 0 | 156 | 0 | 394 | 78 | 0 | 75 | 88 | 113 | 0 | 0 |  | 6442 | 3172 | 9614 | 4165 | 834 | 2256 | 1486 | 342 | 212 | 163 | 156 | 0 | 0 | 105.66
3:00 | 70 | 190 | 0 | 0 | 350 | 87 | 40 | 345 | 355 |  | 20 | 350 | 290 | 0 | 0 | 0 | 207 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 17 | 0 | 0 | 22 | 25 | 13 | 33 | 33 | 0 | 0 | 120 | 90 | 100 | 0 | 0 | 204 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 41 | 135 | 0 | 0 | 0 | 260 | 187 | 55 | 140 | 27 | 55 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 25 | 20 | 150 | 157 | 91 | 20 | 0 | 60 | 58 | 48 | 50 | 130 | 150 | 63 | 70 | 45 | 48 | 0 | 31 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 20 | 60 | 0 | 0 | 115 | 35 | 0 | 0 | 15 | 0 | 113 |  | 835 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 35 | 23 | 0 | 136 | 35 | 16 | 0 | 0 | 60 | 25 | 0 | 80 | 12 | 8 | 0 | 26 | 0 | 22 | 16 | 11 | 91 | 0 | 249 | 0 | 0 | 187 | 0 | 0 | 0 | 82 | 0 | 157 | 0 | 395 | 17 | 0 | 36 | 88 | 37 | 0 | 0 |  | 6235 | 2999 | 9234 | 4174 | 835 | 2260 | 1102 | 340 | 210 | 163 | 150 | 0 | 0 | 105.68
4:00 | 70 | 190 | 0 | 0 | 350 | 87 | 40 | 348 | 354 |  | 20 | 350 | 280 | 0 | 0 | 0 | 209 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 17 | 0 | 0 | 22 | 25 | 13 | 33 | 33 | 0 | 0 | 117 | 90 | 100 | 0 | 0 | 204 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 42 | 135 | 0 | 0 | 0 | 260 | 181 | 55 | 140 | 27 | 55 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 25 | 20 | 148 | 157 | 74 | 20 | 0 | 60 | 58 | 48 | 50 | 130 | 151 | 63 | 70 | 45 | 48 | 0 | 31 | 10 | 310 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 10 | 17 | 0 | 0 | 115 | 35 | 0 | 0 | 15 | 0 | 113 |  | 834 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 35 | 23 | 0 | 136 | 26 | 16 | 0 | 0 | 60 | 25 | 0 | 80 | 12 | 8 | 0 | 17 | 0 | 22 | 16 | 11 | 90 | 0 | 249 | 0 | 0 | 193 | 0 | 0 | 0 | 82 | 0 | 160 | 0 | 361 | 17 | 0 | 36 | 88 | 35 | 0 | 0 |  | 6112 | 2952 | 9064 | 4178 | 834 | 2227 | 968 | 339 | 207 | 163 | 148 | 0 | 0 | 105.69
5:00 | 70 | 190 | 0 | 0 | 350 | 87 | 40 | 345 | 356 |  | 20 | 350 | 290 | 0 | 0 | 0 | 208 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 17 | 0 | 0 | 22 | 25 | 13 | 33 | 33 | 0 | 0 | 115 | 90 | 100 | 0 | 0 | 204 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 42 | 135 | 0 | 0 | 0 | 260 | 181 | 55 | 140 | 27 | 55 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 25 | 20 | 144 | 157 | 50 | 20 | 0 | 60 | 58 | 48 | 50 | 130 | 153 | 63 | 70 | 45 | 48 | 0 | 31 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 10 | 17 | 0 | 0 | 115 | 35 | 0 | 0 | 15 | 0 | 113 |  | 834 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 136 | 25 | 16 | 0 | 0 | 60 | 0 | 0 | 48 | 12 | 8 | 0 | 8 | 0 | 22 | 15 | 8 | 88 | 0 | 249 | 0 | 0 | 192 | 0 | 0 | 0 | 82 | 0 | 156 | 0 | 382 | 17 | 0 | 36 | 88 | 34 | 0 | 0 |  | 6082 | 2859 | 8941 | 4168 | 834 | 2238 | 944 | 337 | 205 | 71 | 144 | 0 | 0 | 105.7
6:00 | 70 | 190 | 0 | 0 | 350 | 12 | 40 | 345 | 355 |  | 20 | 350 | 262 | 0 | 0 | 0 | 120 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 22 | 25 | 13 | 33 | 33 | 0 | 0 | 117 | 90 | 100 | 0 | 0 | 203 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 42 | 135 | 0 | 0 | 0 | 260 | 181 | 55 | 140 | 27 | 10 | 0 | 10 | 0 | 0 | 0 | 21 | 11 | 25 | 20 | 124 | 161 | 8 | 20 | 0 | 60 | 58 | 11 | 10 | 130 | 150 | 60 | 10 | 10 | 48 | 0 | 10 | 10 | 280 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 115 | 0 | 0 | 0.1 | 15 | 0 | 113 |  | 834 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 136 | 24 | 16 | 0 | 0 | 60 | 0 | 0 | 24 | 12 | 0 | 0 | 0 | 0 | 22 | 15 | 8 | 86 | 0 | 249 | 0 | 0 | 190 | 0 | 0 | 0 | 51 | 0 | 164 | 0 | 356 | 17 | 0 | 36 | 55 | 34 | 0 | 0 |  | 5397.1 | 2732 | 8129.1 | 4013 | 834 | 1813 | 756 | 335 | 207 | 47 | 124 | 0.1 | 0 | 105.71
7:00 | 70 | 188 | 0 | 0 | 300 | 12 | 40 | 345 | 303 |  | 20 | 350 | 265 | 0 | 0 | 0 | 56 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 22 | 25 | 13 | 33 | 33 | 0 | 0 | 118 | 90 | 100 | 0 | 0 | 178 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 42 | 100 | 0 | 0 | 0 | 260 | 181 | 8 | 140 | 27 | 10 | 0 | 10 | 0 | 0 | 0 | 21 | 11 | 25 | 20 | 116 | 204 | 8 | 20 | 0.2 | 60 | 58 | 11 | 10 | 100 | 151 | 59 | 10 | 10 | 48 | 0 | 12 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 1.2 | 10 | 0 | 0 | 0 | 65 | 0 | 0 | 0.3 | 15 | 0 | 113 |  | 835 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 133 | 21 | 16 | 0 | 0 | 60 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 15 | 5 | 86 | 0 | 249 | 0 | 0 | 178 | 0 | 0 | 0 | 22 | 0 | 166 | 0 | 361 | 0 | 0 | 36 | 53 | 34 | 0 | 1.1 |  | 5082.7 | 2648.1 | 7730.8 | 3864 | 835 | 1679 | 668 | 335 | 208 | 23 | 116 | 2.8 | 0 | 0
8:00 | 70 | 189 | 0 | 0 | 300 | 12 | 40 | 344 | 273 |  | 20 | 350 | 265 | 0 | 0 | 0 | 50 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 22 | 25 | 13 | 33 | 33 | 11 | 0 | 119 | 90 | 100 | 0 | 0 | 178 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 32 | 100 | 0 | 0 | 0 | 260 | 181 | 8 | 140 | 24 | 10 | 0 | 10 | 0 | 0 | 0 | 21 | 11 | 25 | 15 | 118 | 189 | 8 | 20 | 0.4 | 60 | 58 | 11 | 10 | 100 | 150 | 62 | 10 | 10 | 48 | 0 | 18 | 10 | 290 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 65 | 52 | 0 | 2.61 | 15 | 0 | 113 |  | 834 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 128 | 19 | 16 | 0 | 0 | 60 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 16 | 5 | 91 | 0 | 250 | 0 | 0 | 160 | 0 | 0 | 0 | 22 | 0 | 158 | 0 | 364 | 0 | 0 | 36 | 54 | 35 | 0 | 3.6 |  | 5079.01 | 2588.6 | 7667.61 | 3766 | 834 | 1637 | 733 | 341 | 209 | 23 | 118 | 6.61 | 0 | 0
9:00 | 70 | 189 | 0 | 0 | 330 | 12 | 40 | 361 | 303 |  | 20 | 350 | 295 | 0 | 0 | 0 | 50 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 22 | 25 | 10 | 33 | 33 | 25 | 0 | 119 | 90 | 100 | 0 | 0 | 182 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 8 | 100 | 0 | 0 | 0 | 275 | 196 | 8 | 140 | 27 | 10 | 0 | 10 | 0 | 0 | 0 | 21 | 8 | 25 | 15 | 122 | 170 | 8 | 20 | 2 | 60 | 58 | 11 | 10 | 100 | 154 | 61 | 10 | 10 | 48 | 0 | 17 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 1 | 10 | 0 | 0 | 0 | 65 | 52 | 0 | 2 | 15 | 0 | 113 |  | 842 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 23 | 16 | 0 | 0 | 60 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 16 | 5 | 89 | 0 | 250 | 0 | 0 | 172 | 0 | 0 | 0 | 85 | 0 | 168 | 0 | 385 | 0 | 0 | 36 | 54 | 41 | 0 | 2 |  | 5206 | 2689 | 7895 | 3853 | 842 | 1740 | 783 | 339 | 209 | 0 | 122 | 7 | 0 | 0
10:00 | 70 | 189 | 0 | 0 | 380 | 12 | 40 | 364 | 303 |  | 20 | 350 | 280 | 0 | 0 | 0 | 50 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 22 | 25 | 10 | 33 | 33 | 26 | 0 | 119 | 90 | 100 | 0 | 0 | 179 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 13 | 100 | 0 | 0 | 210 | 320 | 196 | 8 | 140 | 27 | 10 | 0 | 10 | 0 | 0 | 0 | 18 | 8 | 25 | 15 | 130 | 170 | 8 | 20 | 2.5 | 58 | 58 | 11 | 10 | 100 | 152 | 59 | 10 | 43 | 47 | 0 | 17 | 10 | 315 | 16 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 8 | 10 | 0 | 0 | 0 | 65 | 90 | 0 | 4.05 | 15 | 0 | 113 |  | 931 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 22 | 16 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 16 | 5 | 93 | 0 | 250 | 0 | 0 | 176 | 0 | 0 | 0 | 97 | 0 | 172 | 0 | 385 | 0 | 0 | 36 | 88 | 20 | 0 | 2.3 |  | 5587.55 | 2762.3 | 8349.85 | 4096 | 931 | 1804 | 820 | 343 | 209 | 0 | 130 | 16.85 | 0 | 0
11:00 | 70 | 189 | 0 | 0 | 380 | 12 | 40 | 353 | 303 |  | 20 | 350 | 285 | 0 | 0 | 0 | 50 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 22 | 25 | 10 | 33 | 33 | 36 | 0 | 121 | 90 | 100 | 0 | 0 | 180 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 13 | 100 | 0 | 0 | 240 | 320 | 195 | 8 | 140 | 27 | 10 | 0 | 10 | 0 | 0 | 0 | 18 | 8 | 25 | 15 | 134 | 152 | 8 | 20 | 2.5 | 58 | 58 | 11 | 10 | 100 | 153 | 60 | 10 | 43 | 85 | 0 | 15 | 10 | 315 | 16 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 8 | 10 | 10 | 0 | 0 | 0 | 65 | 90 | 0 | 5.92 | 16 | 10 | 113 |  | 927 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 22 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 16 | 5 | 91 | 0 | 250 | 0 | 0 | 174 | 0 | 0 | 0 | 95 | 0 | 167 | 0 | 385 | 0 | 0 | 36 | 88 | 0 | 0 | 8.64 |  | 5670.42 | 2716.64 | 8387.06 | 4129 | 927 | 1800 | 818 | 341 | 211 | 0 | 134 | 27.06 | 0 | 0
12:00 | 70 | 189 | 0 | 0 | 380 | 47 | 40 | 371 | 303 |  | 20 | 360 | 285 | 0 | 0 | 0 | 50 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 22 | 25 | 7 | 33 | 33 | 45 | 0 | 122 | 90 | 100 | 0 | 0 | 179 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 13 | 80 | 0 | 0 | 240 | 320 | 193 | 8 | 138 | 30 | 10 | 0 | 10 | 0 | 0 | 0 | 15 | 8 | 25 | 15 | 140 | 151 | 8 | 20 | 2.6 | 56 | 58 | 16 | 15 | 130 | 154 | 59 | 10 | 43 | 110 | 0 | 42 | 10 | 320 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 30 | 12 | 10 | 0 | 0 | 0 | 65 | 105 | 0 | 5.94 | 16 | 18 | 113 |  | 926 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 24 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 16 | 5 | 93 | 0 | 250 | 0 | 0 | 205 | 0 | 0 | 0 | 90 | 0 | 210 | 0 | 386 | 17 | 0 | 36 | 88 | 0 | 0 | 8.4 |  | 5972.54 | 2806.4 | 8778.94 | 4325 | 926 | 1915 | 889 | 343 | 212 | 0 | 140 | 28.94 | 0 | 0
13:00 | 70 | 189 | 0 | 0 | 380 | 82 | 72 | 348 | 303 |  | 20 | 360 | 270 | 0 | 0 | 0 | 70 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 22 | 25 | 12 | 33 | 33 | 51 | 0 | 122 | 90 | 100 | 0 | 0 | 178 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 21 | 80 | 0 | 0 | 245 | 305 | 181 | 8 | 140 | 30 | 10 | 0 | 20 | 0 | 0 | 0 | 16 | 8 | 25 | 0 | 130 | 135 | 8 | 20 | 2.4 | 56 | 58 | 50 | 50 | 100 | 152 | 60 | 55 | 43 | 110 | 0 | 42 | 10 | 295 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 30 | 12 | 10 | 0 | 0 | 0 | 65 | 105 | 0 | 3.85 | 16 | 13 | 113 |  | 926 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 24 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 24 | 0 | 0 | 0 | 22 | 14 | 5 | 92 | 0 | 265 | 0 | 0 | 180 | 0 | 0 | 0 | 95 | 0 | 190 | 0 | 368 | 35 | 0 | 37 | 88 | 0 | 0 | 2 |  | 6003.25 | 2797 | 8800.25 | 4193 | 926 | 2044 | 918 | 357 | 212 | 0 | 130 | 20.25 | 0 | 0
14:00 | 70 | 189 | 0 | 0 | 380 | 83 | 71 | 356 | 303 |  | 20 | 360 | 280 | 0 | 0 | 0 | 70 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 22 | 25 | 12 | 33 | 33 | 0 | 0 | 122 | 90 | 100 | 0 | 0 | 180 | 0 | 140 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 16 | 80 | 0 | 0 | 80 | 330 | 198 | 8 | 140 | 30 | 10 | 0 | 43 | 0 | 0 | 0 | 17 | 5 | 33 | 15 | 136 | 135 | 8 | 20 | 0.2 | 60 | 58 | 50 | 50 | 100 | 160 | 60 | 71 | 43 | 97 | 16 | 45 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 30 | 17 | 10 | 0 | 0 | 0 | 65 | 105 | 0 | 5.17 | 16 | 18 | 113 |  | 930 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 24 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 24 | 0 | 0 | 0 | 22 | 15 | 5 | 92 | 0 | 280 | 0 | 0 | 190 | 0 | 0 | 0 | 96 | 0 | 198 | 0 | 383 | 70 | 0 | 37 | 87 | 0 | 0 | 7.2 |  | 5913.37 | 2929.2 | 8842.57 | 4144 | 930 | 2103 | 916 | 372 | 212 | 0 | 136 | 29.57 | 0 | 0
15:00 | 70 | 189 | 0 | 0 | 380 | 83 | 71 | 382 | 333 |  | 20 | 360 | 280 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 27 | 0 | 0 | 0 | 22 | 25 | 6 | 33 | 17 | 6 | 0 | 119 | 90 | 100 | 0 | 0 | 210 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 3 | 22 | 16 | 80 | 0 | 42 | 20 | 330 | 199 | 8 | 140 | 30 | 10 | 0 | 43 | 0 | 0 | 0 | 17 | 8 | 33 | 15 | 144 | 139 | 8 | 20 | 0.5 | 60 | 58 | 50 | 50 | 130 | 153 | 59 | 71 | 43 | 47 | 17 | 33 | 10 | 325 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 32 | 16 | 50 | 16 | 10 | 0 | 115 | 105 | 0 | 3.95 | 27 | 18 | 113 |  | 931 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 24 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 24 | 0 | 0 | 0 | 22 | 15 | 5 | 91 | 0 | 280 | 0 | 0 | 202 | 0 | 0 | 0 | 96 | 0 | 208 | 0 | 385 | 70 | 0 | 67 | 88 | 35 | 0 | 5.9 |  | 6151.45 | 3107.9 | 9259.35 | 4227 | 931 | 2178 | 1173 | 371 | 209 | 0 | 144 | 26.35 | 0 | 0
16:00 | 70 | 189 | 0 | 0 | 380 | 83 | 72 | 355 | 332 |  | 20 | 360 | 240 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 41 | 0 | 0 | 0 | 22 | 25 | 6 | 33 | 33 | 29 | 0 | 117 | 90 | 100 | 0 | 0 | 205 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 12 | 22 | 16 | 80 | 0 | 55 | 10 | 305 | 180 | 8 | 140 | 30 | 10 | 0 | 43 | 0 | 0 | 0 | 18 | 8 | 33 | 15 | 140 | 158 | 8 | 20 | 0.4 | 60 | 58 | 50 | 50 | 130 | 151 | 63 | 73 | 44 | 48 | 17 | 31 | 10 | 310 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 32 | 10 | 50 | 34 | 10 | 0 | 115 | 105 | 0 | 2.65 | 47 | 0 | 113 |  | 934 | 0 | 340 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 24 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 24 | 0 | 0 | 0 | 22 | 15 | 5 | 90 | 0 | 280 | 0 | 0 | 192 | 0 | 0 | 0 | 97 | 0 | 207 | 0 | 349 | 70 | 0 | 74 | 88 | 35 | 0 | 4.8 |  | 6116.05 | 3085.8 | 9201.85 | 4182 | 934 | 2129 | 1222 | 370 | 207 | 0 | 140 | 17.85 | 0 | 0
17:00 | 70 | 189 | 0 | 0 | 300 | 83 | 60 | 267 | 303 |  | 0 | 360 | 240 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 47 | 0 | 0 | 0 | 22 | 25 | 7 | 33 | 33 | 42 | 0 | 117 | 90 | 100 | 0 | 0 | 205 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 12 | 22 | 27 | 80 | 0 | 55 | 70 | 305 | 180 | 8 | 132 | 33 | 10 | 0 | 43 | 0 | 0 | 0 | 18 | 8 | 33 | 15 | 136 | 158 | 8 | 20 | 0.2 | 60 | 58 | 50 | 50 | 130 | 152 | 63 | 69 | 42 | 47 | 17 | 31 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 32 | 2 | 50 | 34 | 10 | 0 | 115 | 105 | 0 | 1.36 | 52 | 0 | 113 |  | 934 | 0 | 300 | 0 | 16 | 0 | 0 | 0 | 0 | 5 | 0 | 150 | 20 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 24 | 0 | 0 | 0 | 22 | 15 | 5 | 90 | 0 | 280 | 0 | 0 | 187 | 0 | 0 | 0 | 95 | 0 | 201 | 0 | 330 | 70 | 0 | 75 | 88 | 35 | 0 | 2.2 |  | 5908.56 | 3011.2 | 8919.76 | 3957 | 934 | 2058 | 1247 | 370 | 207 | 5 | 136 | 5.76 | 0 | 0
18:00 | 70 | 189 | 0 | 0 | 270 | 83 | 50 | 176 | 303 |  | 20 | 300 | 245 | 0 | 0 | 5 | 0 | 0 | 73 | 0 | 0 | 3 | 0 | 0 | 50 | 0 | 47 | 0 | 0 | 0 | 22 | 25 | 11 | 33 | 33 | 42 | 0 | 121 | 90 | 100 | 0 | 0 | 205 | 0 | 80 | 0 |  | 0 | 0 | 0 | 10 | 1 | 0 | 22 | 34 | 80 | 0 | 70 | 155 | 250 | 180 | 8 | 135 | 33 | 10 | 0 | 43 | 0 | 0 | 1 | 21 | 11 | 33 | 15 | 130 | 160 | 8 | 20 | 0.1 | 60 | 58 | 11 | 10 | 100 | 112 | 64 | 40 | 42 | 48 | 17 | 33 | 10 | 275 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 32 | 0 | 50 | 34 | 10 | 0 | 115 | 105 | 0 | 0.14 | 52 | 0 | 113 |  | 934 | 0 | 270 | 0 | 16 | 0 | 0 | 0 | 6 | 17 | 0 | 152 | 23 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 24 | 0 | 0 | 0 | 22 | 15 | 5 | 90 | 0 | 280 | 0 | 0 | 156 | 0 | 0 | 0 | 53 | 0 | 169 | 0 | 290 | 35 | 0 | 75 | 88 | 35 | 0 | 0.4 |  | 5506.24 | 2822.4 | 8328.64 | 3690 | 934 | 1755 | 1215 | 370 | 211 | 23 | 130 | 0.64 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 70 | 189 | 0 | 0 | 320 | 83 | 50 | 52 | 334 |  | 20 | 360 | 290 | 6 | 0 | 15 | 0 | 0 | 125 | 0 | 0 | 10 | 60 | 0 | 66 | 0 | 47 | 53 | 55 | 17 | 22 | 25 | 11 | 33 | 25 | 51 | 0 | 123 | 90 | 100 | 0 | 12 | 205 | 0 | 130 | 0 |  | 0 | 0 | 48 | 10 | 36 | 16 | 22 | 39 | 80 | 0 | 70 | 240 | 290 | 189 | 8 | 140 | 33 | 10 | 0 | 43 | 0 | 0 | 18 | 21 | 11 | 33 | 20 | 164 | 164 | 51 | 20 | 0 | 60 | 58 | 24 | 25 | 130 | 144 | 63 | 60 | 42 | 47 | 17 | 33 | 10 | 290 | 24 | 8 | 0 | 14 | 0 | 0 | 48 | 0 | 34 | 0 | 100 | 77 | 50 | 0 | 115 | 105 | 0 | 0 | 77 | 0 | 55 |  | 932 | 0 | 300 | 0 | 97 | 0 | 0 | 0 | 39 | 60 | 40 | 154 | 32 | 64 | 0 | 0 | 60 | 50 | 10 | 96 | 50 | 24 | 47 | 23 | 27 | 22 | 16 | 5 | 92 | 0 | 279 | 0 | 0 | 165 | 0 | 0 | 0 | 97 | 6 | 160 | 0 | 358 | 105 | 0 | 113 | 88 | 110 | 0 | 0 |  | 6535 | 3721 | 10256 | 3925 | 932 | 2066 | 2148 | 371 | 213 | 437 | 164 | 0 | 0 | 0
19:30 | 70 | 189 | 0 | 0 | 320 | 84 | 70 | 180 | 334 |  | 20 | 360 | 245 | 16 | 0 | 15 | 0 | 0 | 120 | 0 | 0 | 32 | 110 | 0 | 72 | 0 | 47 | 40 | 55 | 17 | 22 | 25 | 11 | 33 | 25 | 51 | 0 | 123 | 90 | 100 | 0 | 25 | 204 | 0 | 130 | 0 |  | 0 | 0 | 51 | 10 | 96 | 45 | 22 | 39 | 80 | 0 | 70 | 245 | 305 | 180 | 8 | 131 | 33 | 10 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 29 | 20 | 170 | 164 | 90 | 20 | 0 | 60 | 58 | 50 | 47 | 130 | 150 | 65 | 73 | 42 | 48 | 17 | 33 | 10 | 280 | 24 | 8 | 0 | 14 | 0 | 0 | 185 | 0 | 40 | 0 | 100 | 150 | 100 | 0 | 115 | 105 | 0 | 0 | 105 | 0 | 55 |  | 932 | 0 | 300 | 0 | 115 | 0 | 0 | 0 | 40 | 57 | 40 | 145 | 34 | 87 | 0 | 0 | 60 | 50 | 24 | 96 | 50 | 24 | 47 | 25 | 30 | 22 | 13 | 11 | 93 | 0 | 279 | 0 | 0 | 212 | 0 | 0 | 0 | 96 | 90 | 168 | 0 | 305 | 105 | 0 | 113 | 88 | 111 | 0 | 0 |  | 7244 | 3862 | 11106 | 4106 | 932 | 2083 | 2725 | 372 | 213 | 505 | 170 | 0 | 0 | 0
20:00 | 70 | 189 | 0 | 0 | 320 | 84 | 74 | 168 | 303 |  | 20 | 360 | 260 | 24 | 0 | 15 | 0 | 0 | 70 | 0 | 0 | 32 | 118 | 0 | 72 | 0 | 47 | 53 | 55 | 17 | 22 | 25 | 11 | 33 | 33 | 51 | 0 | 124 | 90 | 100 | 0 | 25 | 204 | 0 | 130 | 0 |  | 0 | 0 | 51 | 10 | 97 | 43 | 22 | 39 | 80 | 0 | 80 | 250 | 305 | 181 | 8 | 135 | 33 | 10 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 28 | 21 | 170 | 164 | 90 | 20 | 0 | 60 | 58 | 50 | 50 | 130 | 150 | 64 | 75 | 42 | 67 | 17 | 33 | 10 | 270 | 24 | 8 | 0 | 14 | 0 | 0 | 185 | 0 | 47 | 0 | 100 | 198 | 100 | 0 | 115 | 105 | 0 | 0 | 105 | 0 | 50 |  | 931 | 0 | 300 | 0 | 115 | 0 | 0 | 0 | 40 | 56 | 40 | 152 | 36 | 110 | 0 | 0 | 60 | 50 | 10 | 94 | 50 | 24 | 0 | 16 | 29 | 22 | 13 | 11 | 90 | 0 | 280 | 0 | 0 | 202 | 0 | 0 | 0 | 96 | 88 | 172 | 0 | 314 | 105 | 0 | 113 | 88 | 111 | 0 | 0 |  | 7290 | 3818 | 11108 | 4091 | 931 | 2062 | 2822 | 370 | 214 | 448 | 170 | 0 | 0 | 0
21:00 | 70 | 189 | 0 | 0 | 320 | 84 | 74 | 316 | 300 |  | 20 | 360 | 265 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 100 | 0 | 72 | 0 | 47 | 35 | 43 | 17 | 0 | 25 | 18 | 33 | 33 | 51 | 0 | 124 | 90 | 100 | 0 | 25 | 204 | 0 | 130 | 0 |  | 0 | 0 | 25 | 10 | 97 | 45 | 22 | 45 | 80 | 0 | 80 | 250 | 305 | 181 | 8 | 140 | 33 | 10 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 29 | 21 | 168 | 172 | 90 | 20 | 0 | 60 | 58 | 50 | 50 | 130 | 152 | 64 | 75 | 43 | 70 | 17 | 33 | 10 | 285 | 24 | 8 | 0 | 0 | 0 | 0 | 195 | 0 | 33 | 0 | 100 | 200 | 55 | 0 | 115 | 105 | 0 | 0 | 105 | 0 | 50 |  | 932 | 0 | 330 | 0 | 115 | 0 | 0 | 0 | 40 | 56 | 40 | 153 | 37 | 110 | 0 | 0 | 60 | 50 | 0 | 94 | 50 | 24 | 0 | 25 | 28 | 22 | 14 | 11 | 91 | 0 | 270 | 0 | 0 | 190 | 0 | 0 | 0 | 97 | 100 | 186 | 0 | 334 | 105 | 0 | 113 | 88 | 113 | 0 | 0 |  | 7310 | 3878 | 11188 | 4326 | 932 | 2104 | 2690 | 361 | 214 | 393 | 168 | 0 | 0 | 0
22:00 | 70 | 189 | 0 | 0 | 320 | 84 | 74 | 338 | 300 |  | 20 | 360 | 260 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 65 | 0 | 40 | 0 | 47 | 0 | 18 | 0 | 22 | 25 | 18 | 33 | 33 | 51 | 0 | 125 | 90 | 100 | 0 | 8 | 204 | 0 | 130 | 0 |  | 0 | 0 | 17 | 10 | 50 | 50 | 22 | 42 | 80 | 0 | 80 | 250 | 305 | 181 | 8 | 131 | 33 | 10 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 29 | 21 | 172 | 172 | 90 | 20 | 0 | 60 | 58 | 50 | 50 | 130 | 152 | 64 | 75 | 43 | 68 | 17 | 32 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 200 | 0 | 16 | 0 | 100 | 200 | 10 | 0 | 115 | 105 | 0 | 0 | 105 | 0 | 50 |  | 932 | 0 | 330 | 0 | 99 | 0 | 0 | 0 | 40 | 56 | 40 | 154 | 37 | 96 | 0 | 0 | 55 | 50 | 0 | 94 | 50 | 8 | 0 | 25 | 22 | 22 | 16 | 11 | 94 | 0 | 270 | 0 | 0 | 200 | 0 | 0 | 0 | 97 | 100 | 194 | 0 | 341 | 105 | 0 | 113 | 88 | 113 | 0 | 0 |  | 7086 | 3852 | 10938 | 4373 | 932 | 2124 | 2414 | 364 | 215 | 344 | 172 | 0 | 0 | 0
23:00 | 70 | 190 | 0 | 0 | 320 | 84 | 74 | 343 | 300 |  | 20 | 360 | 272 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 65 | 0 | 40 | 0 | 47 | 0 | 0 | 0 | 22 | 25 | 18 | 33 | 33 | 51 | 0 | 125 | 90 | 100 | 0 | 8 | 204 | 0 | 130 | 0 |  | 0 | 0 | 17 | 10 | 50 | 50 | 22 | 38 | 80 | 0 | 100 | 250 | 305 | 182 | 8 | 138 | 33 | 10 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 29 | 20 | 170 | 174 | 91 | 20 | 0 | 60 | 58 | 50 | 50 | 130 | 152 | 64 | 76 | 45 | 67 | 17 | 32 | 10 | 285 | 24 | 8 | 0 | 0 | 0 | 0 | 200 | 0 | 16 | 0 | 100 | 200 | 10 | 0 | 115 | 105 | 0 | 0 | 105 | 0 | 50 |  | 933 | 0 | 330 | 0 | 85 | 0 | 0 | 0 | 41 | 56 | 40 | 154 | 36 | 96 | 0 | 0 | 55 | 0 | 0 | 94 | 50 | 8 | 0 | 25 | 22 | 22 | 16 | 11 | 93 | 0 | 270 | 0 | 0 | 194 | 0 | 0 | 0 | 96 | 100 | 201 | 0 | 351 | 105 | 0 | 113 | 88 | 113 | 0 | 0 |  | 7097 | 3798 | 10895 | 4408 | 933 | 2116 | 2395 | 363 | 215 | 295 | 170 | 0 | 0 | 0
24:00 | 70 | 190 | 0 | 0 | 320 | 84 | 75 | 344 | 300 |  | 20 | 360 | 245 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 48 | 0 | 40 | 0 | 47 | 0 | 0 | 0 | 22 | 25 | 18 | 33 | 33 | 51 | 0 | 125 | 90 | 100 | 0 | 8 | 205 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 50 | 50 | 22 | 38 | 80 | 0 | 100 | 210 | 305 | 181 | 8 | 131 | 33 | 30 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 29 | 20 | 168 | 190 | 91 | 20 | 0 | 60 | 58 | 50 | 50 | 130 | 151 | 64 | 75 | 45 | 82 | 17 | 45 | 10 | 280 | 24 | 8 | 0 | 0 | 0 | 0 | 192 | 0 | 12 | 0 | 100 | 200 | 10 | 0 | 115 | 105 | 0 | 0 | 105 | 0 | 50 |  | 932 | 0 | 330 | 0 | 66 | 0 | 0 | 0 | 40 | 56 | 40 | 152 | 35 | 82 | 0 | 0 | 55 | 0 | 0 | 94 | 50 | 32 | 0 | 25 | 22 | 22 | 16 | 11 | 95 | 0 | 270 | 0 | 0 | 181 | 0 | 0 | 0 | 97 | 80 | 194 | 0 | 327 | 105 | 0 | 113 | 88 | 113 | 0 | 0 |  | 7034 | 3723 | 10757 | 4370 | 932 | 2120 | 2327 | 365 | 215 | 260 | 168 | 0 | 0 | 0
KWH | 1534000 | 4803000 | 0 | 0 | 8295672 | 1573409 | 1345344 | 7762940 | 7600000 |  | 475500 | 8440125 | 6636044 | 48000 | 0 | 43882 | 1781455 | 0 | 2789000 | 0 | 0 | 58320 | 438240 | 0 | 475200 | 0 | 943104 | 288360 | 157007 | 67703 | 462960 | 600000 | 311580 | 811600 | 811600 | 654840 | 0 | 2691475 | 2156000 | 2400000 | 0 | 87411 | 4667027 | 0 | 2863652 | 0 |  | 0 | 0 | 171373 | 260040 | 398400 | 355200 | 5172960 | 770400 | 2422070 | 0 | 681224 | 2788400 | 7088000 | 4488000 | 501818 | 3265490 | 676368 | 539040 | 0 | 855510 | 0 | 0 | 326851 | 466776 | 229680 | 681500 | 447570 | 3477120 | 3788080 | 1056000 | 441936 | 12850 | 1412000 | 1375800 | 860400 | 922104 | 3158067 | 3375000 | 1452672 | 1273920 | 894240 | 1458250 | 192600 | 691200 | 252180 | 7372000 | 566064 | 192384 | 0 | 35127 | 0 | 0 | 1418400 | 0 | 406080 | 85050 | 1129920 | 1685280 | 291054 | 0 | 2388000 | 1824684 | 0 | 35500 | 1003636 | 65650 | 2402862 |  | 21462545 | 0 | 7824960 | 0 | 666240 | 0 | 0 | 0 | 383040 | 518144 | 240375 | 3753000 | 653336 | 716160 | 0 | 0 | 138000 | 369856 | 28602 | 971344 | 522590 | 310938 | 58643 | 259200 | 134263 | 511440 | 359748 | 191412 | 2197964 | 0 | 6349900 | 0 | 0 | 4784164 | 0 | 0 | 0 | 1961005 | 495360 | 4503564 | 0 | 874000 | 1228320 | 0 | 1580448 | 1969776 | 1308480 | 0 | 42849 |  | 153657230 | 67369666 | 221026896 | 104227910 | 21462545 | 41409286 | 33804942 | 8547864 | 4847475 | 3073505 | 3477120 | 176249 | 0
Fuel Cost | 1718080 | 5187240 | 0 | 0 | 6138797.28 | 1526206.73 | 1964202.24 | 5589316.8 | 5776000 |  | 841635 | 6752100 | 5972439.6 | 489600 | 0 | 450229.32 | 2209004.2 | 0 | 3486250 | 0 | 0 | 592531.2 | 4342958.4 | 0 | 4324320 | 0 | 8827453.44 | 2765372.4 | 1497846.78 | 674321.88 | 347220 | 450000 | 0 | 0 | 0 | 6273367.2 | 0 | 699783.5 | 560560 | 3672000 | 0 | 840019.71 | 4900378.35 | 0 | 3636838.04 | 0 |  | 0 | 0 | 1797702.77 | 2675811.6 | 3788784 | 3324672 | 4759123.2 | 2141712 | 2543173.5 | 0 | 715285.2 | 2063416 | 5953920 | 4128960 | 491781.64 | 4343101.7 | 554621.76 | 555211.2 | 0 | 1223379.3 | 0 | 0 | 3072399.4 | 476111.52 | 172260 | 1288035 | 335677.5 | 23992128 | 3106225.6 | 10042560 | 450774.72 | 210740 | 1920320 | 1871088 | 1170144 | 1152630 | 3916003.08 | 3105000 | 2164481.28 | 2242099.2 | 992606.4 | 2216540 | 306234 | 808704 | 592623 | 5234120 | 424548 | 146211.84 | 0 | 367779.69 | 0 | 0 | 13645008 | 0 | 4097347.2 | 981477 | 10530854.4 | 15807926.4 | 2727175.98 | 0 | 20942760 | 16257934.44 | 0 | 0 | 9253523.92 | 0 | 0 |  | 57948871.5 | 0 | 6103468.8 | 0 | 6422553.6 | 0 | 0 | 0 | 4443264 | 6787686.4 | 2377308.75 | 3002400 | 1012670.8 | 7691558.4 | 0 | 0 | 259440 | 4120195.84 | 350374.5 | 9616305.6 | 5419258.3 | 3641083.98 | 706648.15 | 2581632 | 1322490.55 | 562584 | 593584.2 | 144898.884 | 14001030.68 | 0 | 25971091 | 0 | 0 | 4210064.32 | 0 | 0 | 0 | 3117997.95 | 8371584 | 3963136.32 | 0 | 638020 | 11619907.2 | 0 | 14508512.64 | 17550704.16 | 12221203.2 | 0 | 0 |  | 299588779.51 | 241281529.724 | 540870309.234 | 98905276.814 | 57948871.5 | 42464379.74 | 241647344.79 | 39972121.68 | 1260343.5 | 33487626.21 | 23992128 | 1192217 | 0
Yesterday Day Peak | 70 | 189 | 0 | 0 | 380 | 47 | 40 | 371 | 303 |  | 20 | 360 | 285 | 0 | 0 | 0 | 50 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 22 | 25 | 7 | 33 | 33 | 45 | 0 | 122 | 90 | 100 | 0 | 0 | 179 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 13 | 80 | 0 | 0 | 240 | 320 | 193 | 8 | 138 | 30 | 10 | 0 | 10 | 0 | 0 | 0 | 15 | 8 | 25 | 15 | 140 | 151 | 8 | 20 | 2.6 | 56 | 58 | 16 | 15 | 130 | 154 | 59 | 10 | 43 | 110 | 0 | 42 | 10 | 320 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 30 | 12 | 10 | 0 | 0 | 0 | 65 | 105 | 0 | 5.94 | 16 | 18 | 113 |  | 926 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 24 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 16 | 5 | 93 | 0 | 250 | 0 | 0 | 205 | 0 | 0 | 0 | 90 | 0 | 210 | 0 | 386 | 17 | 0 | 36 | 88 | 0 | 0 | 8.4 |  | 8778.94 | DayPeak
Yesterday Evening Peak | 70 | 189 | 0 | 0 | 320 | 84 | 74 | 316 | 300 | 0 | 20 | 360 | 265 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 100 | 0 | 72 | 0 | 47 | 35 | 43 | 17 | 0 | 25 | 18 | 33 | 33 | 51 | 0 | 124 | 90 | 100 | 0 | 25 | 204 | 0 | 130 | 0 | 0 | 0 | 0 | 25 | 10 | 97 | 45 | 22 | 45 | 80 | 0 | 80 | 250 | 305 | 181 | 8 | 140 | 33 | 10 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 29 | 21 | 168 | 172 | 90 | 20 | 0 | 60 | 58 | 50 | 50 | 130 | 152 | 64 | 75 | 43 | 70 | 17 | 33 | 10 | 285 | 24 | 8 | 0 | 0 | 0 | 0 | 195 | 0 | 33 | 0 | 100 | 200 | 55 | 0 | 115 | 105 | 0 | 0 | 105 | 0 | 50 |  | 932 | 0 | 330 | 0 | 115 | 0 | 0 | 0 | 40 | 56 | 40 | 153 | 37 | 110 | 0 | 0 | 60 | 50 | 0 | 94 | 50 | 24 | 0 | 25 | 28 | 22 | 14 | 11 | 91 | 0 | 270 | 0 | 0 | 190 | 0 | 0 | 0 | 97 | 100 | 186 | 0 | 334 | 105 | 0 | 113 | 88 | 113 | 0 | 0 |  | 11188 | EvPeak
Forecast for Evening | 70 | 190 | 0 | 0 | 350 | 90 | 75 | 350 | 300 | 0 | 20 | 350 | 280 | 100 | 100 | 55 | 0 | 0 | 150 | 0 | 100 | 100 | 149 | 100 | 72 | 0 | 46 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 125 | 90 | 100 | 0 | 25 | 215 | 0 | 150 | 0 | 0 | 0 | 0 | 80 | 100 | 97 | 50 | 22 | 25 | 120 | 0 | 100 | 360 | 360 | 220 | 68 | 140 | 33 | 52 | 0 | 43 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 185 | 204 | 95 | 20 | 0 | 60 | 58 | 51 | 44 | 163 | 160 | 63 | 75 | 44 | 120 | 17 | 43 | 10 | 320 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 0 | 260 |  | 113 |  | 943 | 32 | 410 | 0 | 115 | 200 | 0 | 0 | 42 | 75 | 40 | 135 | 35 | 110 | 30 | 0 | 60 | 50 | 30 | 100 | 50 | 50 | 47 | 52 | 35 | 22 | 15 | 11 | 90 | 0 | 280 | 0 | 0 | 215 | 0 | 0 | 0 | 95 | 100 | 215 | 0 | 400 | 105 | 200 | 113 | 100 | 114 | 0
Forecast for Day | 70 | 190 | 0 | 0 | 350 | 90 | 50 | 350 | 300 | 0 | 20 | 350 | 280 | 100 | 100 | 55 | 0 | 0 | 100 | 0 | 100 | 100 | 149 | 100 | 72 | 0 | 46 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 125 | 90 | 100 | 0 | 25 | 215 | 0 | 130 | 0 | 0 | 0 | 0 | 50 | 100 | 95 | 50 | 22 | 10 | 120 | 0 | 100 | 250 | 360 | 220 | 68 | 140 | 33 | 52 | 0 | 43 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 131 | 204 | 95 | 20 | 1.6 | 60 | 58 | 51 | 44 | 163 | 160 | 63 | 73 | 44 | 120 | 17 | 42 | 10 | 300 | 24 | 11 | 0 | 200 | 0 | 0 | 200 | 0 | 149 | 20 | 100 | 200 | 150 | 0 | 115 | 100 | 50 | 4.4 | 230 |  | 113 |  | 943 | 0 | 320 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 135 | 25 | 70 | 0 | 0 | 60 | 50 | 0 | 80 | 40 | 50 | 47 | 52 | 0 | 22 | 16 | 11 | 90 | 0 | 280 | 0 | 0 | 215 | 0 | 0 | 0 | 95 | 80 | 205 | 0 | 400 | 105 | 100 | 113 | 50 | 114 | 0 | 8
Generation at 08:00(Today) | 70 | 189 | 0 | 0 | 270 | 13 | 25 | 346 | 240 | 0 | 20 | 300 | 265 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 25 | 13 | 33 | 33 | 0 | 0 | 124 | 90 | 100 | 0 | 0 | 206 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 4 | 80 | 0 | 100 | 225 | 310 | 186 | 8 | 138 | 33 | 54 | 0 | 5 | 0 | 0 | 0 | 21 | 11 | 29 | 17 | 124 | 173 | 8 | 20 | 0.6 | 60 | 58 | 5 | 5 | 100 | 152 | 62 | 10 | 10 | 118 | 17 | 15 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 10 | 10 | 17 | 0 | 0 | 80 | 53 | 0 | 2.68 | 15 | 0 | 50 | 0 | 929 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 153 | 10 | 0 | 0 | 0 | 60 | 0 | 0 | 24 | 12 | 24 | 0 | 0 | 0 | 22 | 16 | 8 | 92 | 0 | 280 | 0 | 0 | 162 | 0 | 0 | 0 | 97 | 0 | 173 | 0 | 382 | 17 | 0 | 37 | 35 | 35 | 0 | 0 | 0
199
| Minimum Generation |  | 7667.61 | 8:00
| Highest Generation |  | 11188 | 21:00
| Day Peak Generation |  | 8778.94 | 12:00
| Evening Peak Generation |  | 11188 | 21:00
| HVDC Max Flow |  | 934 | 16:00
| HVDC EvPeak Flow |  | 932 | 21:00
| Load factor L.F |  | 82.32%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-08-19
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-08-18 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8778.94 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 8108.7 | MW
Evening Peak Generation : |  | 11188 | MW Hour : | 21:00 | Available Max Generation : |  | 15140 | MW
E.P. Demand (at gen end) : |  | 11188 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 11900 | MW
Maximum Generation : |  | 11188 | MW Hour : | 21:00 | Reserve(Generation end) |  | 3240 | MW
Total Gen. (MKWH) : |  | 221.0269 | System Load Factor : | 82.32% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -170 | MW at | 4:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-08-19
Actual : | 105.76 | Ft.(MSL) , | Rule curve : | 94.76 | Ft.( MSL )
Gas Consumed : | Total = | 1325.99 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 141369656.554
|  | Coal : | 39972121.68 | Oil : | 275134971 | Total : | 456476749.234
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4233.8977 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1441.8327 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1292.2037 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1167.7462 |  |  | 0 | 0%
) | 0 | 0:00 | 1055.2031 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 851.5168 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 473.4584 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 219.1721 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 656.7448 |  |  | 0 | 0%
Total | 0 |  | 11391.7754 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit- 2. | 7) Ghorasal Unit-5
|  |  |  | 2) Khulna ST 110 MW | 8) Ghorashal Unit-4
|  |  |  | 3) Sikalbaha ST 60 MW | 9) Sirajganj Unit-2
|  |  |  | 4) Siddhirganj ST | 10) Siddhirganj 335 MW.
5) Ashuganj #4
6) Baghabari 100 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Faridpur-Madaripur 132 kV Ckt-1 was shut down at 08:31 for D/W.
b) Ashuganj(N) 450 MW CCPP GT was synchronized at 09:06.
c) Khulna 132/33 kV T2 transformer was shut down from 10:56 to 11:25 due to red hot maintenance at 33 kV
breaker.
d) Bhola 225 MW CCPP ST was synchronized at 13:25.
e) Siddhirganj 335 MW was shut down at 15:00 due to maintenance work.
f) Haripur 412 MW EGCB STG tripped at 16:20 due to diverter damper fault and was synchronized at 18:57.
g) Jessore 132/33 kV T3 transformer was under shut down from 16:36 to 17:09 due to 33 kv PBS-1 feeder |  |  |  |  | About 24 MW power interruption occurred under Jessore S/S
fault. |  |  |  |  | area from 16:36 to 17:09.
h) Rajshahi 33 kV Bus was under shut down from 21:22 to 22:35 due to red hot maintenance at 33 kV |  |  |  |  | About 14 MW power interruption occurred under Rajshahi S/S
feeder bus isolator. |  |  |  |  | area from 22:22 to 22:35.
i) Chandpur 132/33 kv T1 transformer along with 33 kV Bus section were shut down from 00:44(19/08/2019) |  |  |  |  | About 25 MW power interruption occurred under Chandpur S/S
to 01:54(19/08/2019) due to 33 kV Lakshipur feeder loop maintenance. |  |  |  |  | area from 00:40 to 01:54(19/08/2019).
j) Naogaon 33 KV Bus section-1 & 2 along with T1 & T2 transformers were shut down at 07:42(19/08/2019) |  |  |  |  | About 45 MW power interruption occurred under Naogaon S/S
due to red hot maintenance at 33 kV bus coupler. |  |  |  |  | area from 07:42(18/08/2019) to till.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-08-18 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 70 | 1534000
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 189 | 4803000
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 320 | 8295672 | Gas shortage
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 74 | 1345344 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 84 | 1573409 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 20 | 475500 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 316 | 7762940 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 300 | 7600000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 360 | 8440125 | Machine problem
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 48000 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 265 | 6636044 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 0 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 43882 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 462960 | Under shut down
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 120 | 2789000 | Frequency control
| Siddhirganj Desh |  | QRPP | 96*1.2 | 0 | 0 | 0 | Contract Expired
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217 | 217 | 0 | 1781455 | Testing
| Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 58320 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 47 | 943104
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 288360 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 100 | 438240 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 43 | 157007 | Low demand
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 67703 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 72 | 475200 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 43 | 911580 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 811600
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 811600
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 654840
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 35127 | Reserve
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 33 | 406080 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 1824684
| Dhaka area Total |  |  |  | 5693 | 2730 | 61474776
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 87411
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 85050
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 45 | 355200
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 214 | 4847475
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4667027 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 130 | 2863652 | FGMO
44 | Sikalbaha 51 MW PP(Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 0 | 0 | Contract Expired
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
46 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
47 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 25 | 171373 | Low demand
48 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 260040 | Low demand
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1129920
50 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 5172960
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 45 | 770400
51 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 97 | 398400
52 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 35500
53 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 105 | 1003636 | Transformer overload.
| Jodiac Power |  | IPP | 54.36 | 0 | 0 | 65650 | on test
| Karnaphuli Power Lid. |  | IPP | 110 | 0 | 50 | 2402862 | RRT
| Chattogram area Total |  |  |  | 2053 | 1172 | 26716556
54 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 2422070
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 681224 | Gas shortage
55 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 181 | 4488000 | FGMO
56 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 250 | 2788400 | Under maint.
57 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 7088000 | FGMO
58 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 33 | 676368 | Engine problem
59 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 10 | 539040 | Low demand
60 | Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
61 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 501818 | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 855510 | Engine problem
63 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 55 | 291054 | Transformer overload.
64 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
65 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
66 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 140 | 3265490
67 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 1685280
68 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 466776
69 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 229680
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 168 | 3477120
70 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 29 | 681500 | Engine problem
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 326851
72 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 447570 | Engine problem
73 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1687 | 30911751
74 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 172 | 3788080 | Gas shortage
75 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 441936
76 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 90 | 1056000
77 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12850
78 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 195 | 1418400
79 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2388000
| Mymensingh Area Total |  |  |  | 637 | 592 | 9105266
80 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1412000
81 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 58 | 1375800
82 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3158067
83 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 152 | 3375000 | GT-2 under maint.
84 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 860400
85 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 922104
86 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 192384 | Engine problem
87 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 64 | 1452672 | FGMO
88 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 75 | 1273920 | Engine problem
89 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 43 | 894240 | Engine problem
90 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 70 | 1458250 | Gas shortage
91 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 192600 | Engine problem
92 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 33 | 691200 | Gas shortage
93 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 566064
94 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 7372000 | FGMO
95 | Bibiyana-III 400 MW CCPP |  | PDB | 285 MW | 285 | 0 | 0 | Under shut down
96 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 252180
| Sylhet Area Total |  |  |  | 1834 | 1129 | 25448881
97 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 932 | 21462545
| Khulna 115 MW PP (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
98 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 666240
99 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 40 | 383040
100 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
101 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 56 | 518144
102 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 330 | 7824960 | Line O/L
103 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 240375
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
104 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 495360 | Low demand
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1228320
106 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 88 | 1969776 | Engine problem
| Khulna Area Total |  |  |  | 2314 | 1806 | 34788760
107 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 716160
108 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
109 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 37 | 653336
110 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 153 | 3753000 | ST under maint.
111 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 97 | 1961005
| Barisal Area Total |  |  |  | 462 | 397 | 7083501
112 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 60 | 138000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
113 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 369856
114 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 28602 | Reserve
115 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 522590
116 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 24 | 310938 | Low demand
117 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 58643
118 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 190 | 4784164 | FGMO
119 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
120 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 186 | 4503564 | FGMO
121 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 334 | 874000 | FGMO
122 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 134263
123 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 511440
124 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 14 | 359748
125 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 191412
126 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 25 | 259200
127 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 971344
128 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
129 | Bagura 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1580448
| Rajshahi Area Total |  |  |  | 2070 | 1201 | 15598212
130 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 91 | 2197964
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
131 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 270 | 6349900
132 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
133 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
| Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 0 | 113 | 1308480 | On test
| Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 42849
| Rangpur Area Total |  |  |  | 492 | 474 | 9899193
| Total |  |  |  | 18446 | 11188 | 221026896
| Eastern Grid Total |  |  |  | 13108 | 7310 | 153657230
| Western Grid Total |  |  |  | 5338 | 3878 | 67369666
| National Grid Total |  |  |  | 18446 | 11188 | 221026896
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2019-08-18
(a) ENTIRE EASTERN GRID : |  | 7002 | MW | (b) ENTIRE WESTERN GRID : |  | 3699 | MW
i) Dhaka area |  | 3376 | MW | i) Khulna area |  | 1418 | MW
ii) Chittagong area |  | 1074 | MW | ii) Rajshahi area |  | 1184 | MW
iii) Comilla area |  | 1085 | MW | iii) Barisal area |  | 340 | MW
iv) Mymensingh area |  | 972 | MW | iv) Rangpur area |  | 757 | MW
v) Sylhet area |  | 495 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 10701 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 86 | 1930 | Sherpur | 108 | 2100 | Jhenida | 112 | 1930
Munsiganj | 130 | 2100 | Srimongal | 39 | 1930 | Bottail | 122 | 1930
Sonargaon | 72 | 2000 | Shahjibazar | 119 | 2100 | G.K Project | 58 | 1930
Shyampur | 132 | 1500 | Fenchuganj | 42 | 1930 | Faridpur | 74 | 2100
Bhulta | 113 | 1200 | Kulawara | 47 | 2000 | Madaripur | 112 | 2200
Madanganj | 48 | 100 | Sylhet | 134 | 2000 | Sariatpur | 46 | 2100
Shitalakhya | 85 | 1600 | Chatak | 31 | 2000 | Gopalganj | 89 | 1930
Rahim steel | 5 | 900 | Sunamganj | 39 | 2100 | Bagerhat | 81 | 2100
Matuail | 60 | 1600 | Biani Bazar | 52 | 1930 | Mongla | 28 | 1600
Ghorasal | 67 | 100 | Comilla (S) | 172 | 2200 | Satkhira | 95 | 1930
Narsingdi | 119 | 2000 | Comilla(N) | 110 | 2300 | Gallamari | 43 | 1400
Haripur (SBU) | 70 | 1700 | Chandpur | 105 | 2000 | Magura | 52 | 1930
Ullon | 77 | 1830 | Feni | 125 | 2100 | Norail | 24 | 2100
Hasnabad | 170 | 2100 | Chowmuhani | 176 | 2100 | Chuadanga | 89 | 1930
Magbazar | 121 | 1300 | Ashuganj | 58 | 2300 | Barisal(N) | 43 | 2200
Maniknagar | 106 | 1700 | Daudkandi | 120 | 2300 | Barisal (S) | 100 | 2000
Bangabhaban | 36 | 1300 | B.Baria | 138 | 2000 | Patuakhali | 113 | 2200
Narinda | 70 | 1600 | Ramganj | 100 | 2200 | Bhandaria | 56 | 2000
Dhanmondi | 129 | 1200 | Madunaghat | 54 | 2100 | Borhan Uddin | 38 | 2000
Lalbag | 42 | 1300 | Hathazari | 90 | 1930 | Ishurdi | 62 | 1930
Madartek | 50 | 2100 | Khulshi | 184 | 1700 | Ruppur Paromanobik | 2 | 1100
Mirpur | 91 | 1900 | Halishahar | 117 | 2000 | Natore | 125 | 2100
Kalyanpur | 99 | 2000 | Baraulia | 124 | 2100 | Bogra | 233 | 2000
Gulshan | 140 | 1300 | Sikalbaha | 20 | 1930 | Noagaon | 113 | 2000
Uttara | 74 | 1300 | Dohazari | 90 | 1900 | Rajshahi | 147 | 1930
Uttara New | 12 | 1900 | Cox'sbazar | 87 | 1930 | C.Nawabganj | 68 | 1930
Kamrangirchar | 54 | 1900 | Chandraghona | 30 | 1900 | Amnura | 38 | 2100
Savar | 108 | 2100 | Kaptai | 4 | 1900 | Pabna | 108 | 2100
Bhasantec | 152 | 1300 | A. Khaer Stl. | 0 | 0 | Shahjadpur | 91 | 1830
Agargaon | 56 | 1300 | Bakulia | 91 | 1930 | Serajganj | 91 | 2100
Satmosjid | 93 | 1900 | Julda | 17 | 1200 | Niyamatpur | 64 | 2100
Tongi | 108 | 1600 | TK chemical | 16 | 2000 | Joypurhat | 51 | 2000
Kabirpur | 169 | 1930 | Modern Steel | 8 | 1500 | Mohastangor | 16 | 2000
Basundhara | 130 | 1400 | Shahmirpur | 29 | 2100 | Rangpur | 148 | 2100
Manikganj | 88 | 2100 | Khagrachhari | 20 | 1930 | Lalmonirhat | 65 | 2000
Joydevpur | 190 | 2000 | Matarbari | 26 | 2100 | Saidpur | 112 | 2100
New Tongi | 78 | 1200 | Baroiar Hat | 34 | 1900 | Purbasadipur | 92 | 1930
Korda | 199 | 2100 | Rangamati | 12 | 1900 | Thakurgaon | 70 | 2100
Dhamrai | 58 | 2100 | Abul Khair 230 | 132 | 1000 | Palashbari | 120 | 2100
Valuka | 78 | 1930 | BSRM | 129 | 1500 | Barapukuria | 50 | 2000
Tangail | 188 | 2100 | Goalpara | 27 | 1930 | Panchagar | 43 | 1900
Mymensing | 244 | 2100 | Central s/s | 90 | 1930 | Joldhaka | 27 | 2100
Kishorganj | 126 | 2000 | Noapara | 75 | 2100 | Kurigram | 38 | 1900
Netrokona | 101 | 2300 | Jessore | 104 | 2000
Jamalpur | 131 | 2000 | Benapol | 38 | 1930
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-08-18
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | 126
Bibiyana | 391 | 8:00 | 382 | 15:00 | Kaliakoir | 371 | 6:00 | 360
Bheramara | 401 | 7:00 | 385 | 21:00 | Bhulta | 384 | 20:00 | 369
Ashuganj(N) | 387 | 20:00 | 369 | 15:00
230 KV | KV |  | KV |  | 230 KV | KV |  | 15:00
Ghorasal | 230 | 1:00 | 226 | 15:00 | Hathazari | 220 | 21:00 | 216
Ishurdi | 235 | 8:00 | 224 | 1:00 | Megnaghat | 225 | 4:00 | 219
Ashuganj | 236 | 20:00 | 230 | 15:00 | Fenchuganj | 236 | 6:00 | 232
Serajganj | 230 | 6:00 | 225 | 21:00 | Siddhirganj | 225 | 4:00 | 216
Baghabari | 233 | 18:00 | 230 | 1:00 | Maniknagar | 223 | 6:00 | 215
Barapukuria | 234 | 18:00 | 223 | 21:00 | Old Airport | 222 | 6:00 | 213
Bogra | 227 | 18:30 | 213 | 21:00 | Barisal | 232 | 8:00 | 223
Khulna South | 226 | 18:30 | 212 | 2:00 | AKSML | 217 | 20:00 | 212
Rampura | 222 | 4:00 | 217 | 11:00 | BSRM | 220 | 7:00 | 214
Haripur | 222 | 6:00 | 217 | 16:00 | Bibiyana | 233 | 7:00 | 229
Hasnabad | 224 | 3:00 | 215 | 13:00 | Bhulta | 224 | 6:00 | 216
Aminbazar | 223 | 5:00 | 215 | 15:00 | Ashuganj (S) | 234 | 20:00 | 227
Tongi | 222 | 7:00 | 215 | 15:00 | Kaliakoir | 224 | 7:00 | 215
Comilla (N) | 230 | 6:00 | 224 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 134 | 200 | 129 | 1500 | Khulshi | 129 | 1900 | 125
Munsiganj | 134 | 2000 | 127 | 1600 | Halishahar | 133 | 1930 | 128
Megnaghat | 132 | 1800 | 128 | 1100 | Baraulia | 130 | 2000 | 126
Shyampur | 132 | 700 | 127 | 1400 | Sikalbaha | 133 | 1930 | 129
Bhulta | 129 | 700 | 123 | 1500 | Dohazari | 130 | 1930 | 124
Madanganj | 131 | 700 | 126 | 1400 | Cox'sbazar | 124 | 600 | 116
Shitalakhya | 134 | 2000 | 126 | 1400 | Chandraghona | 132 | 2000 | 129
Rahim steal | 134 | 100 | 130 | 1500 | Kaptai | 132 | 1830 | 130
Matuail | 134 | 700 | 128 | 1500 | A. Khaer Stl. | 130 | 300 | 126
Ghorasal | 135 | 100 | 133 | 1100 | Bakulia | 131 | 1930 | 127
Narsinghdi | 131 | 1800 | 125 | 100 | Julda | 132 | 1930 | 127
Haripur (SBU) | 134 | 100 | 130 | 1500 | TK Chemical | 135 | 2100 | 128
Ullon | 134 | 600 | 127 | 1200 | Modern Steel | 132 | 2000 | 128
Hasnabad | 132 | 600 | 127 | 1400 | Shahmirpur | 132 | 2100 | 128
Magbazar | 135 | 600 | 126 | 1500 | Khagrachhari | 130 | 600 | 127
Maniknagar | 138 | 600 | 132 | 1500 | Matarbari | 126 | 600 | 119
Bangabhaban | 138 | 600 | 132 | 1500 | Baroiar Hat | 126 | 700 | 123
Narinda | 138 | 600 | 132 | 1500 | Rangamati | 131 | 600 | 129
Dhanmondi | 138 | 600 | 132 | 1500 | Goalpara | 137 | 1700 | 128
Lalbag | 134 | 600 | 127 | 1400 | Central s/s | 136 | 1700 | 126
Madartek | 133 | 600 | 126 | 1500 | Noapara | 134 | 2000 | 122
Mirpur | 137 | 600 | 130 | 1200 | Jessore | 128 | 900 | 119
Kalyanpur | 137 | 600 | 131 | 1600 | Benapol | 130 | 800 | 120
Gulshan | 133 | 600 | 126 | 1500 | Jhenida | 129 | 800 | 117
Uttara | 136 | 600 | 126 | 1400 | Bottail | 135 | 900 | 126
Uttara New | 132 | 2000 | 128 | 1400 | G.K Project | 142 | 1800 | 135
Kamrangirchar | 132 | 200 | 125 | 1600 | Faridpur | 132 | 700 | 123
Savar | 134 | 1930 | 126 | 1500 | Madaripur | 134 | 1700 | 128
Bhasantec | 132 | 700 | 124 | 1600 | Sariatpur | 133 | 800 | 123
Agargaon | 132 | 400 | 125 | 1500 | Gopalganj | 141 | 1000 | 135
Satmosjid | 132 | 600 | 125 | 1400 | Bagerhat | 136 | 900 | 126
Tongi | 135 | 1930 | 131 | 1500 | Mongla | 133 | 800 | 125
Kabirpur | 134 | 700 | 128 | 2100 | Satkhira | 136 | 900 | 126
Basundhara | 131 | 2100 | 126 | 1400 | Gallamari | 138 | 1800 | 125
Manikganj | 137 | 1830 | 132 | 200 | Magura | 129 | 900 | 115
Joydevpur | 138 | 2000 | 131 | 1600 | Norail | 126 | 800 | 115
New Tongi | 134 | 2000 | 128 | 1500 | Chuadanga | 124 | 800 | 109
Kodda | 135 | 2000 | 126 | 900 | Barisal(N) | 138 | 800 | 132
Dhamrai | 133 | 1800 | 127 | 2100 | Barisal (S) | 139 | 900 | 130
Valuka | 128 | 1800 | 117 | 2100 | Patuakhali | 136 | 700 | 126
Tangail | 132 | 800 | 122 | 2100 | Bhandaria | 135 | 800 | 126
Mymensing | 129 | 1800 | 120 | 100 | Ishurdi | 140 | 1830 | 133
Kishorganj | 129 | 1800 | 121 | 2100 | Ruppur Paromanobik | 139 | 1800 | 133
Netrokona | 128 | 1800 | 116 | 2100 | Natore | 138 | 1830 | 127
Jamalpur | 137 | 2300 | 124 | 1200 | Bogra | 137 | 1830 | 127
Sherpur | 134 | 1830 | 122 | 1400 | Noagaon | 131 | 1830 | 121
Srimongal | 136 | 1800 | 132 | 2100 | Rajshahi | 134 | 1800 | 123
Shahjibazar | 134 | 1800 | 130 | 2000 | C.Nawabganj | 134 | 1830 | 120
Fenchuganj | 135 | 600 | 132 | 1930 | Amnura | 139 | 1830 | 121
Khulawara | 134 | 1800 | 131 | 2100 | Pabna | 138 | 1800 | 131
Sylhet | 134 | 800 | 131 | 1900 | Shahjadpur | 140 | 700 | 135
Chatak | 132 | 700 | 128 | 2000 | Serajganj | 136 | 1830 | 129
Sunamganj | 132 | 700 | 127 | 2000 | Niyamatpur | 131 | 1830 | 116
Biani Bazar | 133 | 900 | 127 | 2100 | Joypurhat | 134 | 1830 | 118
Comilla(s) | 124 | 700 | 121 | 1100 | Mohastangor | 135 | 1830 | 125
Comilla(n) | 134 | 700 | 130 | 300 | Rangpur | 128 | 900 | 116
Chandpur | 130 | 2400 | 125 | 1500 | Lalmonirhat | 124 | 1830 | 110
Feni | 125 | 800 | 122 | 1600 | Saidpur | 127 | 1800 | 115
Chowmuhani | 124 | 700 | 119 | 2200 | Purbasadipur | 127 | 900 | 112
Ashuganj | 135 | 1800 | 131 | 1000 | Thakurgaon | 123 | 1800 | 103
Daudkandi | 130 | 700 | 126 | 1300 | Palashbari | 131 | 1830 | 121
B.Baria | 132 | 700 | 126 | 2100 | Barapukuria | 134 | 1800 | 123

## L-Curve
Date | 2019-08-18
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 10 | 7034 | 3723 | 10757 |  |  |  | QF-LDC-12
0:30 | 70 | 6824 | 3499 | 10323 | Date: | 2019-08-18
1:00 | 130 | 6614 | 3275 | 9889
1:30 | 145 | 6528 | 3223.5 | 9751.5
2:00 | 160 | 6442 | 3172 | 9614
2:30 | 161 | 6338.5 | 3085.5 | 9424 | [5 empty] | Gen. at Eve. Peak | 11188 | 11188 MW (21:00 )
3:00 | 162 | 6235 | 2999 | 9234 | [6 empty] | 21:00
3:30 | 166 | 6173.5 | 2975.5 | 9149 | [5 empty] | Gen. at Day Peak | 8778.94 | 8778.94 MW (12:00 )
4:00 | 170 | 6112 | 2952 | 9064 | [6 empty] | 12:00
4:30 | 151 | 6097 | 2905.5 | 9002.5 | [5 empty] | Highest Generation | 11188
5:00 | 132 | 6082 | 2859 | 8941 | [6 empty] | 21:00
5:30 | 75 | 5739.55 | 2795.5 | 8535.05
6:00 | 18 | 5397.1 | 2732 | 8129.1
6:30 | 49 | 5239.9 | 2690.05 | 7929.95
7:00 | 80 | 5082.7 | 2648.1 | 7730.8
7:30 | 130 | 5080.855 | 2618.35 | 7699.205
8:00 | 180 | 5079.01 | 2588.6 | 7667.61
8:30 | 290 | 5142.505 | 2638.8 | 7781.305
9:00 | 400 | 5206 | 2689 | 7895
9:30 | 385 | 5396.775 | 2725.65 | 8122.425
10:00 | 370 | 5587.55 | 2762.3 | 8349.85
10:30 | 361 | 5628.985 | 2739.47 | 8368.455
11:00 | 352 | 5670.42 | 2716.64 | 8387.06
11:30 | 308 | 5821.48 | 2761.52 | 8583
12:00 | 264 | 5972.54 | 2806.4 | 8778.94
12:30 | 206 | 5987.895 | 2801.7 | 8789.595
13:00 | 148 | 6003.25 | 2797 | 8800.25
13:30 | 191 | 5958.31 | 2863.1 | 8821.41
14:00 | 234 | 5913.37 | 2929.2 | 8842.57
14:30 | 272 | 6032.41 | 3018.55 | 9050.96
15:00 | 310 | 6151.45 | 3107.9 | 9259.35
15:30 | 325 | 6133.75 | 3096.85 | 9230.6
16:00 | 340 | 6116.05 | 3085.8 | 9201.85
16:30 | 385 | 6012.305 | 3048.5 | 9060.805
17:00 | 430 | 5908.56 | 3011.2 | 8919.76
17:30 | 405 | 5707.4 | 2916.8 | 8624.2
18:00 | 380 | 5506.24 | 2822.4 | 8328.64
18:30 | 265 | 6020.62 | 3271.7 | 9292.32
19:00 | 150 | 6535 | 3721 | 10256
19:30 | 34 | 7244 | 3862 | 11106
20:00 | 60 | 7290 | 3818 | 11108 |  |  |  | Executive Engineer
20:30 | 36 | 7300 | 3848 | 11148 |  |  |  | Network Operation Division
21:00 | 12 | 7310 | 3878 | 11188
21:30 | 29 | 7198 | 3865 | 11063
22:00 | 46 | 7086 | 3852 | 10938 |  |  |  |  | Page 6 of 7
22:30 | 28 | 7091.5 | 3825 | 10916.5
23:00 | 10 | 7097 | 3798 | 10895
23:30 | 10 | 7065.5 | 3760.5 | 10826
24:00 | 10 | 7034 | 3723 | 10757
11188 MW (21:00 )
8778.94 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-08-18 |  | Energy | 221026896
[10 empty] | 2019-08-18 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4370 | 932 | 2120 | 2327 | 365 | 215 | 260 | 0 | 168
0:30 | 4269.5 | 883 | 2180 | 2019.5 | 353.5 | 214 | 239.5 | 0 | 164 | Date: | 2019-08-18
1:00 | 4169 | 834 | 2240 | 1712 | 342 | 213 | 219 | 0 | 160
1:30 | 4167 | 834 | 2248 | 1599 | 342 | 212.5 | 191 | 0 | 158 | [7 empty] | Total Energy | 221.0269 | Total Energy Gen 187.552 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 187.552 MKWHr
2:00 | 4165 | 834 | 2256 | 1486 | 342 | 212 | 163 | 0 | 156 | [7 empty] | Energy not Served | 0
2:30 | 4169.5 | 834.5 | 2258 | 1294 | 341 | 211 | 163 | 0 | 153 | [7 empty] | Energy Requirement | 221.0269
3:00 | 4174 | 835 | 2260 | 1102 | 340 | 210 | 163 | 0 | 150
3:30 | 4176 | 834.5 | 2243.5 | 1035 | 339.5 | 208.5 | 163 | 0 | 149 | [6 empty] | Shortage
4:00 | 4178 | 834 | 2227 | 968 | 339 | 207 | 163 | 0 | 148
4:30 | 4173 | 834 | 2232.5 | 956 | 338 | 206 | 117 | 0 | 146
5:00 | 4168 | 834 | 2238 | 944 | 337 | 205 | 71 | 0 | 144
5:30 | 4090.5 | 834 | 2025.5 | 850 | 336 | 206 | 59 | 0 | 134
6:00 | 4013 | 834 | 1813 | 756 | 335 | 207 | 47 | 0 | 124
6:30 | 3938.5 | 834.5 | 1746 | 712 | 335 | 207.5 | 35 | 0 | 120 |  |  |  |  | Coal
7:00 | 3864 | 835 | 1679 | 668 | 335 | 208 | 23 | 0 | 116
7:30 | 3815 | 834.5 | 1658 | 700.5 | 338 | 208.5 | 23 | 0 | 117 |  |  |  | Oil |  |  |  | ,
8:00 | 3766 | 834 | 1637 | 733 | 341 | 209 | 23 | 0 | 118
8:30 | 3809.5 | 838 | 1688.5 | 758 | 340 | 209 | 11.5 | 0 | 120
9:00 | 3853 | 842 | 1740 | 783 | 339 | 209 | 0 | 0 | 122
9:30 | 3974.5 | 886.5 | 1772 | 801.5 | 341 | 209 | 0 | 0 | 126
10:00 | 4096 | 931 | 1804 | 820 | 343 | 209 | 0 | 0 | 130
10:30 | 4112.5 | 929 | 1802 | 819 | 342 | 210 | 0 | 0 | 132
11:00 | 4129 | 927 | 1800 | 818 | 341 | 211 | 0 | 0 | 134
11:30 | 4227 | 926.5 | 1857.5 | 853.5 | 342 | 211.5 | 0 | 0 | 137
12:00 | 4325 | 926 | 1915 | 889 | 343 | 212 | 0 | 0 | 140
12:30 | 4259 | 926 | 1979.5 | 903.5 | 350 | 212 | 0 | 0 | 135
13:00 | 4193 | 926 | 2044 | 918 | 357 | 212 | 0 | 0 | 130
13:30 | 4193 | 926 | 2044 | 918 | 357 | 212 | 0 | 0 | 130
14:00 | 4193 | 926 | 2044 | 918 | 357 | 212 | 0 | 0 | 130
14:30 | 4210 | 928.5 | 2111 | 1045.5 | 364 | 210.5 | 0 | 0 | 137
15:00 | 4227 | 931 | 2178 | 1173 | 371 | 209 | 0 | 0 | 144
15:30 | 4204.5 | 932.5 | 2153.5 | 1197.5 | 370.5 | 208 | 0 | 0 | 142
16:00 | 4182 | 934 | 2129 | 1222 | 370 | 207 | 0 | 0 | 140
16:30 | 4069.5 | 934 | 2093.5 | 1234.5 | 370 | 207 | 2.5 | 0 | 138
17:00 | 3957 | 934 | 2058 | 1247 | 370 | 207 | 5 | 0 | 136
17:30 | 3823.5 | 934 | 1906.5 | 1231 | 370 | 209 | 14 | 0 | 133
18:00 | 3690 | 934 | 1755 | 1215 | 370 | 211 | 23 | 0 | 130
18:30 | 3807.5 | 933 | 1910.5 | 1681.5 | 370.5 | 212 | 230 | 0 | 147
19:00 | 3925 | 932 | 2066 | 2148 | 371 | 213 | 437 | 0 | 164
19:30 | 4106 | 932 | 2083 | 2725 | 372 | 213 | 505 | 0 | 170
20:00 | 4091 | 931 | 2062 | 2822 | 370 | 214 | 448 | 0 | 170
20:30 | 4208.5 | 931.5 | 2083 | 2756 | 365.5 | 214 | 420.5 | 0 | 169
21:00 | 4326 | 932 | 2104 | 2690 | 361 | 214 | 393 | 0 | 168
21:30 | 4349.5 | 932 | 2114 | 2552 | 362.5 | 214.5 | 368.5 | 0 | 170
22:00 | 4373 | 932 | 2124 | 2414 | 364 | 215 | 344 | 0 | 172
22:30 | 4390.5 | 932.5 | 2120 | 2404.5 | 363.5 | 215 | 319.5 | 0 | 171
23:00 | 4408 | 933 | 2116 | 2395 | 363 | 215 | 295 | 0 | 170
23:30 | 4389 | 932.5 | 2118 | 2361 | 364 | 215 | 277.5 | 0 | 169 | Max Temp. in Dhaka |  | 33.0° C
24:00 | 4370 | 932 | 2120 | 2327 | 365 | 215 | 260 | 0 | 168
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 187.552 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 187.552 MKWHr
Note on W13: Author:

## Generation
2019-08-18
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 123 | 122 | 120 | 117 | 115 | 117 | 118 | 119 | 119 | 119 | 121 | 122 | 122 | 122 | 119 | 117 | 117 | 121 |  | 123 | 123 | 124 | 124 | 125 | 125 | 125 | 2691475
2 | Karnaphuli Hydro PP Unit-4 & 5 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2156000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [19 empty] | 12 | 25 | 25 | 25 | 8 | 8 | 8 | 87411
| Teknaf 20MW PP (Solartech) | [6 empty] | 1.2 | 0 | 1 | 8 | 10 | 12 | 12 | 17 | 16 | 10 | 2 | 0 | [8 empty] | 85050
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 205 | 204 | 204 | 204 | 203 | 178 | 178 | 182 | 179 | 180 | 179 | 178 | 180 | 210 | 205 | 205 | 205 |  | 205 | 204 | 204 | 204 | 204 | 204 | 205 | 4667027
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 130 | 130 | 130 | 130 | 130 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 130 | 140 | 130 | 130 | 130 | 80 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 2863652
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 48 | 51 | 51 | 25 | 17 | 17 | 0 | 171373
12 | Hathazari 100 MW peaking PP
Sikalbaha 105 MW PP (Baraka Sikalbaha)
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 120 | 125 | 125 | 120 | 120 | 80 | 80 | 80 | 80 | 80 | 80 | 152 | 115 | 76 | 160 | 160 | 120 | 73 |  | 125 | 120 | 70 | 120 | 120 | 120 | 120 | 2789000
17 | Siddhirganj 335 MW CCPP | 207 | 207 | 207 | 209 | 208 | 120 | 56 | 50 | 50 | 50 | 50 | 50 | 70 | 70 | 0 | [11 empty] | 1781455
18 | Kodda 300 MW PP Unit-2 (Summit) | [19 empty] | 14 | 14 | 14 | 0 |  |  |  | 35127
19 | Ashuganj 195MW PP (APSCL-United) | 55 | 55 | 55 | 55 | 55 | 55 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 501818
20 | Ghorasal TPP (Unit-1&2) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1534000
21 | Ghorasal Repowered CCPP Unit-3 | 190 | 190 | 190 | 190 | 190 | 190 | 188 | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 189 |  | 189 | 189 | 189 | 189 | 189 | 190 | 190 | 4803000
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 350 | 350 | 350 | 350 | 350 | 350 | 300 | 300 | 330 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 300 | 270 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 8295672
26
28 | Ashuganj TPP Unit- 3 | 135 | 135 | 135 | 135 | 135 | 135 | 100 | 100 | 100 | 100 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2422070
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | [14 empty] | 42 | 55 | 55 | 70 |  | 70 | 70 | 80 | 80 | 80 | 100 | 100 | 681224
32 | Ashuganj 50 MW PP | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 27 | 27 | 27 | 30 | 30 | 30 | 30 | 30 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 676368
33 | Ashuganj 225 MW CCPP | 181 | 181 | 187 | 181 | 181 | 181 | 181 | 181 | 196 | 196 | 195 | 193 | 181 | 198 | 199 | 180 | 180 | 180 |  | 189 | 180 | 181 | 181 | 181 | 182 | 181 | 4488000
34 | Ashuganj 450 MW CCPP(South) | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 275 | 320 | 320 | 320 | 305 | 330 | 330 | 305 | 305 | 250 |  | 290 | 305 | 305 | 305 | 305 | 305 | 305 | 7088000
| Ashuganj 450 MW CCPP(North) | [9 empty] | 210 | 240 | 240 | 245 | 80 | 20 | 10 | 70 | 155 |  | 240 | 245 | 250 | 250 | 250 | 250 | 210 | 2788400
35 | Ashuganj 55 MW PP (Precision) | 54 | 54 | 55 | 55 | 55 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 30 | 539040
36 | Chandpur 150 MW CCPP | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 138 | 140 | 140 | 140 | 140 | 132 | 135 |  | 140 | 131 | 135 | 140 | 131 | 138 | 131 | 3265490
37 | Tongi 80 MW GTPP
38 | Haripur GTPP | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 475500
39 | Haripur 412 MW CCPP | 345 | 345 | 345 | 348 | 345 | 345 | 345 | 344 | 361 | 364 | 353 | 371 | 348 | 356 | 382 | 355 | 267 | 176 |  | 52 | 180 | 168 | 316 | 338 | 343 | 344 | 7762940
40 | Meghnaghat 450 MW CCPP(MPL) | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 360 | 360 | 360 | 360 | 360 | 360 | 300 |  | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 8440125
41 | Haripur 360MW CCPP(HPL) | 355 | 354 | 355 | 354 | 356 | 355 | 303 | 273 | 303 | 303 | 303 | 303 | 303 | 303 | 333 | 332 | 303 | 303 |  | 334 | 334 | 303 | 300 | 300 | 300 | 300 | 7600000
42 | RPCL 210MW CCPP | 157 | 157 | 157 | 157 | 157 | 161 | 204 | 189 | 170 | 170 | 152 | 151 | 135 | 135 | 139 | 158 | 158 | 160 |  | 164 | 164 | 164 | 172 | 172 | 174 | 190 | 3788080
43
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 58 | 58 | 56 | 56 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1412000
45 | Fenchugonj CCPP Phase-2 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 |  | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 1375800
46 | Shajibazar 330 MW CCPP | 152 | 149 | 150 | 151 | 153 | 150 | 151 | 150 | 154 | 152 | 153 | 154 | 152 | 160 | 153 | 151 | 152 | 112 |  | 144 | 150 | 150 | 152 | 152 | 152 | 151 | 3375000
47 | Shahjibazar GTPP Unit- 8 & 9 | 63 | 62 | 63 | 63 | 63 | 60 | 59 | 62 | 61 | 59 | 60 | 59 | 60 | 60 | 59 | 63 | 63 | 64 |  | 63 | 65 | 64 | 64 | 64 | 64 | 64 | 1452672
48 | Shahjibazar 86MW PP (Shahjibazar) | 70 | 70 | 70 | 70 | 70 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 55 | 71 | 71 | 73 | 69 | 40 |  | 60 | 73 | 75 | 75 | 75 | 76 | 75 | 1273920
49 | Shahjibazar 50MW PP (EPL) | 45 | 45 | 45 | 45 | 45 | 10 | 10 | 10 | 10 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 42 | 42 |  | 42 | 42 | 42 | 43 | 43 | 45 | 45 | 894240
50 | Sylhet 150 MW CCPP | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 47 | 85 | 110 | 110 | 97 | 47 | 48 | 47 | 48 |  | 47 | 48 | 67 | 70 | 68 | 67 | 82 | 1458250
51 | Sylhet 20 MW GTPP | [13 empty] | 16 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 192600
52 | Sylhet 50MW PP (EPL) | 31 | 31 | 31 | 31 | 31 | 10 | 12 | 18 | 17 | 17 | 15 | 42 | 42 | 45 | 33 | 31 | 31 | 33 |  | 33 | 33 | 33 | 33 | 32 | 32 | 45 | 691200
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 252180
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 192384
55 | Fenchugonj 51 MW PP (Barakatullah) | 48 | 48 | 48 | 48 | 48 | 11 | 11 | 11 | 11 | 11 | 11 | 16 | 50 | 50 | 50 | 50 | 50 | 11 |  | 24 | 50 | 50 | 50 | 50 | 50 | 50 | 860400
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 566064
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 300 | 300 | 310 | 300 | 280 | 300 | 290 | 300 | 315 | 315 | 320 | 295 | 300 | 325 | 310 | 300 | 275 |  | 290 | 280 | 270 | 285 | 300 | 285 | 280 | 7372000
58 | Nababganj 55 MW PP (Southern power ) | [19 empty] | 17 | 17 | 17 | 17 |  |  |  | 67703
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 5172960
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 |  | 22 | 22 | 22 | 462960
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 441936
63 | Impoprt (Tripura) | 160 | 156 | 150 | 148 | 144 | 124 | 116 | 118 | 122 | 130 | 134 | 140 | 130 | 136 | 144 | 140 | 136 | 130 |  | 164 | 170 | 170 | 168 | 172 | 170 | 168 | 3477120
64 | Malancha, Ctg. EPZ (United) | 42 | 41 | 41 | 42 | 42 | 42 | 42 | 32 | 8 | 13 | 13 | 13 | 21 | 16 | 16 | 16 | 27 | 34 |  | 39 | 39 | 39 | 45 | 42 | 38 | 38 | 770400
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 18 | 15 | 16 | 17 | 17 | 18 | 18 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 466776
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 5 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 229680
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 |  | 33 | 29 | 28 | 29 | 29 | 29 | 29 | 681500
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 15 | 15 | 15 | 15 | 15 | 0 | 15 | 15 | 15 | 15 | 15 |  | 20 | 20 | 21 | 21 | 21 | 20 | 20 | 447570
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 10 | 10 | 10 | 7 | 12 | 12 | 6 | 6 | 7 | 11 |  | 11 | 11 | 11 | 18 | 18 | 18 | 18 | 311580
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 811600
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 17 | 33 | 33 | 33 |  | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 811600
73 | Ghorashal 108MW PP (Regent) | 87 | 87 | 87 | 87 | 87 | 12 | 12 | 12 | 12 | 12 | 12 | 47 | 82 | 83 | 83 | 83 | 83 | 83 |  | 83 | 84 | 84 | 84 | 84 | 84 | 84 | 1573409
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [7 empty] | 11 | 25 | 26 | 36 | 45 | 51 | 0 | 6 | 29 | 42 | 42 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 654840
79 | Kodda 150MW PP | 16 | [18 empty] | 60 | 110 | 118 | 100 | 65 | 65 | 48 | 438240
80 | Jamalpur 95 MW PP(Powerpac) | 91 | 91 | 91 | 74 | 50 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 51 | 90 | 90 | 90 | 90 | 91 | 91 | 1056000
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 0 | [15 empty] | 1 |  | 18 | 52 | 52 | 52 | 52 | 52 | 52 | 326851
| Gazipur 100 MW PP | 53 | 35 | 35 | 35 | 35 |  |  | 52 | 52 | 90 | 90 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1824684
| Kaptai 7 MW Solar PP |  |  |  |  | 0 | 0.1 | 0.3 | 2.61 | 2 | 4.05 | 5.92 | 5.94 | 3.85 | 5.17 | 3.95 | 2.65 | 1.36 | 0.14 | [8 empty] | 35500
| Jodiac Power | [10 empty] | 10 | 18 | 13 | 18 | 18 | [11 empty] | 65650
| Karnaphuli Power Lid. | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 55 | 55 | 50 | 50 | 50 | 50 | 50 | 2402862
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP(Summit) | 272 | 285 | 290 | 280 | 290 | 262 | 265 | 265 | 295 | 280 | 285 | 285 | 270 | 280 | 280 | 240 | 240 | 245 |  | 290 | 245 | 260 | 265 | 260 | 272 | 245 | 6636044
87 | Meghnaghat 100 MW(IEL) | [19 empty] | 6 | 16 | 24 |  |  |  |  | 48000
88 | Ghorashal 78.5 MW PP(MAX) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 72 | 71 | 71 | 72 | 60 | 50 |  | 50 | 70 | 74 | 74 | 74 | 74 | 75 | 1345344
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 260040
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 50 | 50 | 50 | 10 | 10 | 10 | 10 | 10 | 10 | 15 | 50 | 50 | 50 | 50 | 50 | 10 |  | 25 | 47 | 50 | 50 | 50 | 50 | 50 | 922104
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 20 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 855510
94 | Gagnagar 102 MW PP (Digital Power) | [17 empty] | 3 |  | 10 | 32 | 32 | 0 |  |  |  | 58320
95 | Patenga 50MW PP (Baraka) | 46 | [13 empty] | 3 | 12 | 12 |  |  | 16 | 45 | 43 | 45 | 50 | 50 | 50 | 355200
96 | Chattogram 108 MW PP (ECPV) | [17 empty] | 1 |  | 36 | 96 | 97 | 97 | 50 | 50 | 50 | 398400
97 | Katpotti 52 MW PP (Sinha) | 46 | 46 | 46 | 46 | 46 | 46 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 41 | 47 | 47 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 943104
98 | Bosila 108MW PP(CLC) | [14 empty] | 50 | 50 | 50 | 50 |  | 66 | 72 | 72 | 72 | 40 | 40 | 40 | 475200
99 | Madanganj-55 MW PP(Summit) | [17 empty] | 5 |  | 15 | 15 | 15 | 0 |  |  |  | 43882
100 | Manikganj 55 MW PP (Northern) | [19 empty] | 55 | 55 | 55 | 43 | 18 |  |  | 157007
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 130 | 100 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 130 | 130 | 130 | 100 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3158067
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0.2 | 0.4 | 2 | 2.5 | 2.5 | 2.6 | 2.4 | 0.2 | 0.5 | 0.4 | 0.2 | 0.1 | [8 empty] | 12850
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 17 | 17 | 17 | [14 empty] | 53 | 40 | 53 | 35 |  |  |  | 288360
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 90 | 90 | 50 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 48 | 185 | 185 | 195 | 200 | 200 | 192 | 1418400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [10 empty] | 8 | 30 | 30 | 30 | 32 | 32 | 32 | 32 |  | 34 | 40 | 47 | 33 | 16 | 16 | 12 | 406080
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 70 | 20 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 50 | 50 | 50 | 50 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1129920
116 | Chandpur 200MW (Desh energy) | 199 | 165 | 60 | 17 | 17 | 0 | 0 | [7 empty] | 16 | 34 | 34 | 34 |  | 77 | 150 | 198 | 200 | 200 | 200 | 200 | 1685280
117 | Ashuganj 150MW PP (Midland) | [14 empty] | 10 | 10 | 10 | 10 |  | 50 | 100 | 100 | 55 | 10 | 10 | 10 | 291054
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 108 | 115 | 115 | 115 | 115 | 115 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2388000
| Anwara 300 MW PP (United) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 16 | 16 | 16 | 16 | 27 | 47 | 52 | 52 |  | 77 | 105 | 105 | 105 | 105 | 105 | 105 | 1003636
120 | Eastern Zone Total | 6614 | 6442 | 6235 | 6112 | 6082 | 5397.1 | 5082.7 | 5079.01 | 5206 | 5587.55 | 5670.42 | 5972.54 | 6003.25 | 5913.37 | 6151.45 | 6116.05 | 5908.56 | 5506.24 |  | 6535 | 7244 | 7290 | 7310 | 7086 | 7097 | 7034 | 153657230
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 32 | 0 | [13 empty] | 16 | 16 | 16 |  | 97 | 115 | 115 | 115 | 99 | 85 | 66 | 666240
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 35 | 35 | 35 | 35 | 0 | [12 empty] | 6 |  | 39 | 40 | 40 | 40 | 40 | 41 | 40 | 383040
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 78 | 17 | 17 | 17 | 17 | 0 |  |  |  |  | 17 | 35 | 70 | 70 | 70 | 70 | 35 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1228320
130
131
132
133
| Barisal 110 MW PP (Summit ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 0 | [6 empty] | 0 |  | 64 | 87 | 110 | 110 | 96 | 96 | 82 | 716160
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 96 | 82 | 82 | 82 | 82 | 51 | 22 | 22 | 85 | 97 | 95 | 90 | 95 | 96 | 96 | 97 | 95 | 53 |  | 97 | 96 | 96 | 97 | 97 | 96 | 97 | 1961005
| Bhola 225 MW CCPP | 134 | 136 | 136 | 136 | 136 | 136 | 133 | 128 | 131 | 84 | 83 | 83 | 83 | 152 | 152 | 152 | 150 | 152 |  | 154 | 145 | 152 | 153 | 154 | 154 | 152 | 3753000
140 | Bhola 33 MW PP (Venture) | 35 | 34 | 35 | 26 | 25 | 24 | 21 | 19 | 23 | 22 | 22 | 24 | 24 | 24 | 24 | 24 | 20 | 23 |  | 32 | 34 | 36 | 37 | 37 | 36 | 35 | 653336
141 | Noapara 100 MW PP (Bangla Trac) | [19 empty] | 6 | 90 | 88 | 100 | 100 | 100 | 80 | 495360
142 | Noapara 40 MW PP (Khanjahan Ali) | 16 | 0 | [17 empty] | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 240375
143 | Gopalganj 100 MW Peaking PP | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 0 | [7 empty] | 5 | 17 |  | 60 | 57 | 56 | 56 | 56 | 56 | 56 | 518144
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | 88 | 88 | 88 | 88 | 88 | 55 | 53 | 54 | 54 | 88 | 88 | 88 | 88 | 87 | 88 | 88 | 88 | 88 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 1969776
146 | Bheramara HVDC | 834 | 834 | 835 | 834 | 834 | 834 | 835 | 834 | 842 | 931 | 927 | 926 | 926 | 930 | 931 | 934 | 934 | 934 |  | 932 | 932 | 931 | 932 | 932 | 933 | 932 | 21462545
147 | Bheramara 360 MW CCPP | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 280 | 280 | 280 | 280 | 280 | 280 | 250 | 340 | 340 | 300 | 270 |  | 300 | 300 | 300 | 330 | 330 | 330 | 330 | 7824960
148
149
150 | Barapukuria TPP Unit-1 | 91 | 92 | 91 | 90 | 88 | 86 | 86 | 91 | 89 | 93 | 91 | 93 | 92 | 92 | 91 | 90 | 90 | 90 |  | 92 | 93 | 90 | 91 | 94 | 93 | 95 | 2197964
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 251 | 250 | 249 | 249 | 249 | 249 | 249 | 250 | 250 | 250 | 250 | 250 | 265 | 280 | 280 | 280 | 280 | 280 |  | 279 | 279 | 280 | 270 | 270 | 270 | 270 | 6349900
153 | Baghabari 71 MW GTPP | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 60 | 60 | 60 | 60 | 55 | 55 | 55 | 138000
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 50 | 25 | 25 | 25 | 0 | 0 | [13 empty] | 50 | 50 | 50 | 50 | 50 | 0 | 0 | 369856
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 193 | 186 | 187 | 193 | 192 | 190 | 178 | 160 | 172 | 176 | 174 | 205 | 180 | 190 | 202 | 192 | 187 | 156 |  | 165 | 212 | 202 | 190 | 200 | 194 | 181 | 4784164
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 157 | 156 | 157 | 160 | 156 | 164 | 166 | 158 | 168 | 172 | 167 | 210 | 190 | 198 | 208 | 207 | 201 | 169 |  | 160 | 168 | 172 | 186 | 194 | 201 | 194 | 4503564
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 361 | 394 | 395 | 361 | 382 | 356 | 361 | 364 | 385 | 385 | 385 | 386 | 368 | 383 | 385 | 349 | 330 | 290 |  | 358 | 305 | 314 | 334 | 341 | 351 | 327 | 874000
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [19 empty] | 10 | 24 | 10 | 0 | 0 |  |  | 28602
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 511440
163 | Bogura 20 MW PP (Energyprima) | 16 | 16 | 16 | 16 | 15 | 15 | 15 | 16 | 16 | 16 | 16 | 16 | 14 | 15 | 15 | 15 | 15 | 15 |  | 16 | 13 | 13 | 14 | 16 | 16 | 16 | 359748
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 191412
165 | Amnura 50 MW PP(Sinha) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 522590
166 | Katakhali 50 MW PP (Northern) | 8 | 8 | 8 | 8 | 8 | 0 | 0 | [5 empty] | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 8 | 8 | 32 | 310938
167 | Katakhali 50 MW Peaking PP | [19 empty] | 47 | 47 | 0 |  |  |  |  | 58643
168 | Santahar 50 MW Peaking PP | 0 | [18 empty] | 27 | 30 | 29 | 28 | 22 | 22 | 22 | 134263
169 | Natore 52 MW PP (Rajlanka) | 26 | 26 | 26 | 17 | 8 | 0 | 0 | [12 empty] | 23 | 25 | 16 | 25 | 25 | 25 | 25 | 259200
170 | Chapainawabganj 100 MW Peaking PP | 95 | 80 | 80 | 80 | 48 | 24 | 0 | [12 empty] | 96 | 96 | 94 | 94 | 94 | 94 | 94 | 971344
171 | Baghabari 200 MW PP (Paramount)
172 | Bagura 113 MW PP (Confidence) | 75 | 75 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 37 | 37 | 67 | 74 | 75 | 75 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1580448
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 37 | 35 | 34 | 34 | 34 | 35 | 41 | 20 | 0 |  |  |  | 35 | 35 | 35 | 35 |  | 110 | 111 | 111 | 113 | 113 | 113 | 113 | 1308480
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1.1 | 3.6 | 2 | 2.3 | 8.64 | 8.4 | 2 | 7.2 | 5.9 | 4.8 | 2.2 | 0.4 | [8 empty] | 42849
178
178