## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-09-28 | Monday
|  |  | Date (day): | 2020-09-28 |  | Monday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13619.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14458 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-09-27 | 2020-09-28 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 200 | 199 | 220 | 220
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 115 | 115 | 115 | 75
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 365 |  | Machine problem
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 65 | 0 | 0 | 0 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 86 | 43 | 94 | 94 |  | 14 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  |  | Under maint.
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 350 | 348 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 360 | 400 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 93 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 5 | 110 | 150 | 150 | 155 |  | GT-2 S/D for Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 48 | 97 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 40 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 65 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 100 | 92 | 100 | 100 | 110 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 318 | 301 | 335 | 335 |  |  | FGMO
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 93 | 93 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 115 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 35 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 46 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 25 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 195 | 300 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 139 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 34 | 86 | 85 | 85 |  | 20 | Engine problem
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 2572 | 3153 | 3728 | 4018 | 1047 | 458
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 8 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 12 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 44 | 44 | 44 | 186 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 223 | 203 | 221 | 221
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 142 | 139 | 140 | 145
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 100 | 100
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 10 | 100 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 20 | 20
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 20 | 10 | 40
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 90 | 90 | 90 |  | 18 | Engine problem
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 72 | 140 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 52 | 54 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 821 | 1174 | 1709 | 1719 | 426 | 116
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 80 | 80 | 80 | 54 |  | Engine problem
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 217 | 177 | 225 | 225 |  |  | FGMO
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 330 | 260 | 360 | 360 |  |  | FGMO
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 29 | 30 | 30 | 15 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 51 | 52 | 55 | 55
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 55 | 55 | 65 | 65 | 130 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 50 | 100 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 42
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 96 | 94 | 100 | 100 |  | 63 | ST under shut down
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 200 | 200
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 8 | 8 | 8 |  | 3 | Engine problem
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 128 | 146 | 162 | 173
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33 |  | 8 | Engine problem
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 43 | 34 | 34 |  | 18 | Engine problem
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 15 | 21 | 21
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 101 | 114 | 114
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 111 | 113 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1264 | 1375 | 1819 | 2072 | 463 | 456
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 150 | 157 | 160 | 160 | 42 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 16 | 16 |  | 6 | Engine problem
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 0 | 0 | 0 |  | 95 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 185 | 186 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 115 | 115 | 115
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 352 | 475 | 492.6 | 491 | 42 | 101
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 89 | 89 | 90 | 90
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 35 | Unit-4 under shut down
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 200 | 186 | 200 | 200 |  |  | Gas shortage
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 44 | 53 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 41 | 47 | 47 | 47
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 65 | 64 | 65 | 65
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 87 | 88 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 97 | 97 | 97 | 97
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 280 | 341 | 341 |  |  | FGMO
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1177 | 1149 | 1234 | 1234 | 0 | 435
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 926 | 926 | 934 | 934
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 105 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 230 | 225 | 225
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 320 | 345 | 410 | 410
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 90 | 105 | 105
| 108 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1383 | 1836 | 1979 | 2135 | 0 | 0
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 32 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 19 | 29 | 33 | 33
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 81 | 81 | 86 | 86 |  | 134 | GT-2 & STG under shut down
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 76 | 76 | 78 | 78 |  | 17 | Engine problem
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 470 | 622 | 620 | 620
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 646 | 840 | 927 | 927 | 0 | 151
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 47 | 43 | 43
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | ST Under maint & gas shoratge
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 198 | 174 | 200 | 200 |  |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 203 | 184 | 220 | 220 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 393 | 389 | 414 | 414 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 34
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 21 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 10 | 10
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 9 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 52 | 52 | 52
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 98 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 90 | 90 |  | 23 | Engine problem
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 70 | 109 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 893 | 1241 | 1473 | 1599 | 271 | 233
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 106 | 100 | 113
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 2 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 152 | 256 | 258 | 263 | 294 | 40
|  | Total |  |  |  |  | 20383 | 19892 | 9260 | 11499 | 13619.6 | 14458 | 2543 | 1990
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8841.2505 | 10979 | 13003.7037 | 13804.1901
| A. |  | 2020-09-27 | (Yesterday) |  |  |  |  | Sunday
| 1 | Highest Generation : |  |  | 11499 | MW at | 20:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
| 2 | Minimum Generation : |  |  | 7876 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11499 | MW
| 3 | Day peak Generation : |  |  | 9260 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10979 | MW
| 4 | Evening peak Generation : |  |  | 11499 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 230.5335 | MKWHr | By Solar | 0.16427 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 136.591 | MKWHr |  | By Oil: | 50.8711 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 16.6368 | MKWHr |  | By Hydro: | 0.948 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2543 | MW | Dhaka | 3863 | 3863 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 1990 | MW | Chittagong | 1127 | 1127 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4533 | MW | Khulna | 1439 | 1439 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1148.49 | MMCFD |  |  | Rajshahi | 1230 | 1230 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 163015105.324 | ii) Oil : | Taka | 407294147.7 | Comilla | 1039 | 1039 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 76844492 | Total | Taka | 647153745.024 | Mymensingh | 930 | 930 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 449 | 449 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 330 | MW (E to W) at | 20:00 | hrs | Barisal | 321 | 321 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 248 | MW at | 22:00 | hrs | Rangpur | 581 | 581 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 30.9° C |  |  | Total | 10979 | 10979 |  | 0
| B. |  | 2020-09-28 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 33.1° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 11900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14458 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 9800 | MW
| 4 | Reserve(Generation end) |  |  |  | 2558 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 238.5728 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8201 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.2167 | MKWHr. | ii) HVDC Flow at Peak Time |  | 926 | MW at | 20:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.1056 | MKWHr. | iii) Maximum HVDC Flow : |  | 927 | MW at | 10:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 97.24 |  | (b) Today: | 97.86 |  | (c) Rule Curve: |  | 105.04
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-09-27
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 200 | 115 | 0 | 87 | 65 | 0 | 354 |  | 0 | 400 | 0 | 100 | 97 | 15 | 292 | 0 | 85 | 0 | 100 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 41 | 0 | 120 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 31 | 0 | 0 | 80 | 310 | 0 | 219 | 45 | 88 | 29 | 53 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 18 | 132 | 159 | 0 | 17 | 0 | 89 | 30 | 50 | 47 | 163 | 202 | 64 | 88 | 0 | 97 | 18 | 0 | 10 | 280 | 16 | 8 | 0 | 95 | 0 | 0 | 193 | 0 | 149 | 0 | 0 | 0 | 100 | 0 | 55 | 0 | 0 | 0 | 102 | 54 | 0 | 0 | 113 | 100 | 0 | 104 |  | 926 | 0 | 340 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 81 | 29 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 183 | 0 | 76 | 0 | 185 | 0 | 399 | 70 | 0 | 0 | 0 | 47 | 0 | 0 | 70 | 560 |  | 6164 | 3329 | 9493 | 3656 | 926 | 2249 | 1659 | 710 | 41 | 120 | 132 | 0 | 0 | 97.14
2:00 | 0 | 0 | 200 | 115 | 0 | 87 | 66 | 0 | 354 |  | 0 | 400 | 0 | 100 | 97 | 15 | 273 | 0 | 80 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 41 | 0 | 120 | 0 | 0 | 203 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 0 | 0 | 80 | 310 | 0 | 221 | 45 | 90 | 29 | 53 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 18 | 128 | 160 | 0 | 17 | 0 | 89 | 30 | 50 | 47 | 163 | 202 | 64 | 88 | 0 | 97 | 18 | 0 | 10 | 280 | 16 | 8 | 0 | 95 | 0 | 0 | 200 | 0 | 120 | 0 | 0 | 0 | 50 | 0 | 55 | 0 | 0 | 0 | 34 | 54 | 0 | 0 | 111 | 100 | 0 | 104 |  | 926 | 0 | 340 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 81 | 29 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 183 | 0 | 77 | 0 | 186 | 0 | 347 | 70 | 0 | 0 | 0 | 62 | 0 | 0 | 70 | 520 |  | 5988 | 3233 | 9221 | 3634 | 926 | 2210 | 1492 | 670 | 41 | 120 | 128 | 0 | 0 | 97.16
3:00 | 0 | 0 | 200 | 115 | 0 | 87 | 65 | 0 | 354 |  | 0 | 400 | 0 | 100 | 48 | 15 | 282 | 0 | 92 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 0 | 0 | 80 | 310 | 0 | 219 | 45 | 95 | 29 | 52 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 18 | 122 | 160 | 0 | 17 | 0 | 89 | 30 | 50 | 47 | 163 | 202 | 64 | 88 | 0 | 97 | 18 | 0 | 10 | 280 | 16 | 8 | 0 | 95 | 0 | 0 | 193 | 0 | 105 | 0 | 0 | 0 | 50 | 0 | 35 | 0 | 0 | 0 | 15 | 54 | 0 | 0 | 98 | 100 | 0 | 104 |  | 926 | 0 | 340 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 81 | 27 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 183 | 0 | 77 | 0 | 185 | 0 | 353 | 53 | 0 | 0 | 0 | 43 | 0 | 0 | 35 | 480 |  | 5843 | 3125 | 8968 | 3656 | 926 | 2212 | 1260 | 630 | 42 | 120 | 122 | 0 | 0 | 97.18
4:00 | 0 | 0 | 200 | 115 | 0 | 88 | 65 | 0 | 353 |  | 0 | 400 | 0 | 74 | 48 | 15 | 288 | 0 | 94 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 0 | 0 | 80 | 310 | 0 | 219 | 45 | 96 | 29 | 51 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 18 | 118 | 160 | 0 | 17 | 0 | 89 | 30 | 50 | 47 | 163 | 203 | 64 | 88 | 0 | 97 | 18 | 0 | 10 | 285 | 24 | 8 | 0 | 95 | 0 | 0 | 160 | 0 | 101 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 15 | 34 | 0 | 0 | 75 | 70 | 0 | 85 |  | 926 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 81 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 184 | 0 | 77 | 0 | 187 | 0 | 358 | 35 | 0 | 0 | 0 | 34 | 0 | 0 | 35 | 480 |  | 5601 | 3085 | 8686 | 3657 | 926 | 2220 | 973 | 630 | 42 | 120 | 118 | 0 | 0 | 97.2
5:00 | 0 | 0 | 200 | 115 | 0 | 88 | 65 | 0 | 351 |  | 0 | 400 | 0 | 53 | 48 | 15 | 321 | 0 | 97 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 43 | 0 | 120 | 0 | 0 | 215 | 0 | 141 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 0 | 0 | 80 | 340 | 0 | 197 | 45 | 96 | 29 | 52 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 18 | 114 | 157 | 0 | 17 | 0 | 89 | 30 | 50 | 47 | 163 | 200 | 63 | 40 | 0 | 97 | 18 | 0 | 10 | 295 | 24 | 8 | 0 | 95 | 0 | 0 | 140 | 0 | 100 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 15 | 34 | 0 | 0 | 55 | 50 | 0 | 70 |  | 926 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 81 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 175 | 0 | 78 | 0 | 181 | 0 | 358 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 |  | 5493 | 2981 | 8474 | 3690 | 926 | 2182 | 769 | 630 | 43 | 120 | 114 | 0 | 0 | 97.22
6:00 | 0 | 0 | 200 | 115 | 0 | 88 | 65 | 0 | 354 |  | 0 | 400 | 0 | 41 | 48 | 14 | 289 | 0 | 32 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 43 | 0 | 120 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 0 | 0 | 80 | 310 | 0 | 177 | 45 | 86 | 29 | 52 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 18 | 110 | 160 | 0 | 17 | 0 | 89 | 30 | 22 | 20 | 163 | 200 | 64 | 40 | 0 | 97 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 95 | 0 | 0 | 140 | 0 | 100 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 15 | 34 | 0 | 0 | 55 | 50 | 0 | 70 |  | 926 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 81 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 155 | 0 | 78 | 0 | 165 | 0 | 360 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 |  | 5252 | 2911 | 8163 | 3487 | 926 | 2122 | 756 | 599 | 43 | 120 | 110 | 0 | 0 | 97.24
7:00 | 0 | 0 | 200 | 115 | 0 | 88 | 40 | 0 | 302 |  | 0 | 370 | 0 | 41 | 48 | 14 | 303 | 0 | 32 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 25 | 28 | 33 | 33 | 0 | 0 | 44 | 0 | 120 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 21 | 0 | 0 | 80 | 270 | 0 | 177 | 45 | 91 | 29 | 52 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 18 | 106 | 158 | 0 | 17 | 0 | 89 | 30 | 22 | 20 | 110 | 202 | 40 | 40 | 0 | 97 | 18 | 0 | 10 | 285 | 24 | 8 | 0 | 95 | 0 | 0 | 140 | 0 | 100 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 1 | 15 | 34 | 0 | 0 | 55 | 30 | 0 | 70 |  | 926 | 0 | 385 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 81 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 144 | 0 | 53 | 0 | 154 | 0 | 372 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 |  | 4977 | 2899 | 7876 | 3423 | 926 | 1920 | 736 | 600 | 44 | 120 | 106 | 1 | 0 | 97.26
8:00 | 0 | 0 | 200 | 115 | 0 | 88 | 40 | 0 | 302 |  | 0 | 370 | 0 | 42 | 48 | 15 | 315 | 0 | 35 | 0 | 40 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 25 | 28 | 33 | 33 | 0 | 0 | 44 | 0 | 120 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 6 | 0 | 0 | 80 | 280 | 0 | 189 | 55 | 96 | 29 | 52 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 18 | 102 | 157 | 0 | 17 | 0 | 89 | 30 | 22 | 20 | 110 | 202 | 40 | 40 | 0 | 97 | 18 | 0 | 10 | 295 | 24 | 8 | 0 | 95 | 0 | 0 | 140 | 0 | 100 | 7 | 10 | 0 | 20 | 0 | 0 | 0 | 0 | 2 | 16 | 34 | 0 | 0 | 55 | 30 | 0 | 72 |  | 926 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 81 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 150 | 0 | 53 | 0 | 161 | 0 | 375 | 17 | 0 | 0 | 0 | 0 | 0 | 1 | 20 | 440 |  | 5076 | 2895 | 7971 | 3453 | 926 | 1922 | 804 | 590 | 44 | 120 | 102 | 10 | 0 | 97.28
9:00 | 0 | 0 | 200 | 115 | 0 | 88 | 40 | 0 | 303 |  | 0 | 370 | 0 | 82 | 74 | 25 | 307 | 0 | 35 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 45 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 44 | 0 | 120 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 10 | 2 | 21 | 8 | 0 | 0 | 80 | 270 | 0 | 184 | 55 | 94 | 29 | 51 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 18 | 112 | 156 | 0 | 17 | 1 | 89 | 30 | 22 | 20 | 110 | 202 | 40 | 40 | 0 | 97 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 110 | 0 | 0 | 140 | 0 | 135 | 9 | 10 | 0 | 40 | 0 | 0 | 50 | 0 | 4 | 16 | 34 | 0 | 0 | 55 | 30 | 0 | 103 |  | 926 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 81 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 161 | 0 | 52 | 0 | 165 | 0 | 376 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 450 |  | 5385 | 2939 | 8324 | 3463 | 926 | 1934 | 1111 | 600 | 44 | 120 | 112 | 14 | 0 | 97.3
10:00 | 0 | 0 | 200 | 115 | 0 | 85 | 40 | 0 | 333 |  | 0 | 370 | 0 | 100 | 97 | 40 | 293 | 0 | 32 | 0 | 90 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 43 | 0 | 120 | 0 | 0 | 204 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 13 | 12 | 21 | 2 | 0 | 0 | 80 | 270 | 0 | 183 | 55 | 86 | 26 | 50 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 18 | 118 | 155 | 0 | 17 | 2 | 89 | 30 | 22 | 20 | 110 | 202 | 40 | 40 | 0 | 97 | 18 | 0 | 9 | 300 | 24 | 8 | 0 | 195 | 0 | 0 | 168 | 0 | 149 | 8 | 10 | 0 | 95 | 0 | 0 | 51 | 0 | 4 | 16 | 34 | 0 | 0 | 79 | 80 | 0 | 104 |  | 927 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 81 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 167 | 0 | 52 | 0 | 160 | 0 | 412 | 17 | 0 | 0 | 0 | 0 | 0 | 1 | 70 | 450 |  | 5743 | 3013 | 8756 | 3436 | 927 | 1989 | 1508 | 600 | 43 | 120 | 118 | 15 | 0 | 97.32
11:00 | 0 | 0 | 200 | 115 | 0 | 90 | 50 | 0 | 354 |  | 0 | 420 | 6 | 100 | 48 | 40 | 313 | 0 | 80 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 41 | 0 | 120 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 21 | 3 | 0 | 0 | 80 | 275 | 0 | 192 | 55 | 93 | 26 | 50 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 15 | 122 | 154 | 0 | 17 | 2 | 89 | 30 | 33 | 30 | 130 | 200 | 65 | 88 | 0 | 97 | 18 | 0 | 9 | 290 | 24 | 0 | 0 | 195 | 0 | 0 | 185 | 0 | 149 | 7 | 10 | 0 | 50 | 0 | 0 | 51 | 0 | 3 | 16 | 34 | 0 | 0 | 94 | 100 | 0 | 104 |  | 926 | 0 | 335 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 81 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 181 | 0 | 72 | 0 | 168 | 0 | 412 | 17 | 0 | 0 | 0 | 0 | 0 | 1 | 35 | 450 |  | 5953 | 2994 | 8947 | 3532 | 926 | 2175 | 1418 | 600 | 41 | 120 | 122 | 13 | 0 | 97.34
12:00 | 0 | 0 | 200 | 115 | 0 | 86 | 65 | 0 | 350 |  | 0 | 360 | 5 | 100 | 48 | 40 | 318 | 0 | 100 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 40 | 0 | 120 | 0 | 0 | 223 | 0 | 142 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 21 | 4 | 0 | 0 | 80 | 330 | 0 | 217 | 55 | 96 | 29 | 51 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 15 | 128 | 150 | 0 | 17 | 0 | 89 | 30 | 44 | 41 | 163 | 200 | 65 | 87 | 0 | 97 | 18 | 0 | 9 | 310 | 24 | 0 | 0 | 195 | 0 | 0 | 185 | 0 | 139 | 20 | 10 | 0 | 50 | 0 | 0 | 34 | 0 | 5 | 72 | 52 | 0 | 0 | 111 | 100 | 0 | 104 |  | 926 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 81 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 198 | 0 | 76 | 0 | 203 | 0 | 393 | 17 | 0 | 0 | 0 | 0 | 0 | 2 | 70 | 470 |  | 6186 | 3074 | 9260 | 3698 | 926 | 2185 | 1516 | 620 | 40 | 120 | 128 | 27 | 0 | 97.36
13:00 | 0 | 0 | 200 | 115 | 0 | 90 | 64 | 0 | 351 |  | 0 | 360 | 5 | 100 | 60 | 40 | 316 | 0 | 100 | 0 | 100 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 40 | 0 | 120 | 0 | 0 | 205 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 21 | 10 | 0 | 0 | 80 | 285 | 0 | 196 | 55 | 95 | 29 | 49 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 15 | 126 | 153 | 0 | 17 | 2 | 89 | 30 | 49 | 44 | 163 | 200 | 55 | 87 | 0 | 97 | 18 | 0 | 9 | 310 | 24 | 5 | 0 | 195 | 0 | 0 | 185 | 0 | 133 | 9 | 50 | 0 | 65 | 0 | 0 | 34 | 0 | 2 | 100 | 54 | 0 | 0 | 107 | 100 | 0 | 104 |  | 926 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 81 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 199 | 0 | 76 | 0 | 190 | 0 | 405 | 53 | 0 | 0 | 0 | 33 | 0 | 2 | 109 | 500 |  | 6200 | 3192 | 9392 | 3575 | 926 | 2213 | 1727 | 650 | 40 | 120 | 126 | 15 | 9392 | 97.38
14:00 | 0 | 0 | 200 | 115 | 0 | 91 | 64 | 0 | 347 |  | 0 | 360 | 6 | 100 | 87 | 40 | 306 | 0 | 99 | 0 | 100 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 41 | 0 | 120 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 14 | 0 | 0 | 12 | 21 | 5 | 0 | 0 | 80 | 270 | 0 | 188 | 55 | 96 | 29 | 52 | 0 | 51 | 0 | 0 | 0 | 18 | 5 | 33 | 15 | 134 | 153 | 0 | 17 | 1 | 88 | 30 | 47 | 44 | 163 | 202 | 55 | 88 | 0 | 97 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 195 | 0 | 0 | 185 | 0 | 133 | 12 | 50 | 0 | 93 | 0 | 0 | 34 | 0 | 0 | 104 | 54 | 0 | 0 | 102 | 100 | 0 | 104 |  | 927 | 0 | 285 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 24 | 81 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 184 | 0 | 76 | 0 | 175 | 0 | 410 | 53 | 0 | 0 | 0 | 36 | 0 | 2 | 109 | 500 |  | 6251 | 3183 | 9434 | 3507 | 927 | 2193 | 1833 | 650 | 41 | 134 | 134 | 15 | 0 | 97.4
15:00 | 0 | 0 | 200 | 115 | 0 | 88 | 64 | 0 | 348 |  | 0 | 380 | 6 | 100 | 97 | 40 | 294 | 0 | 100 | 0 | 100 | 50 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 204 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 4 | 12 | 21 | 3 | 0 | 0 | 80 | 270 | 0 | 182 | 55 | 87 | 29 | 53 | 0 | 51 | 0 | 0 | 0 | 18 | 5 | 33 | 15 | 132 | 153 | 0 | 17 | 1 | 89 | 30 | 46 | 47 | 163 | 187 | 64 | 88 | 0 | 97 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 209 | 0 | 0 | 185 | 0 | 138 | 14 | 90 | 0 | 105 | 0 | 14 | 70 | 0 | 1 | 139 | 54 | 0 | 0 | 104 | 100 | 0 | 104 |  | 927 | 0 | 340 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 24 | 81 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 186 | 0 | 76 | 0 | 176 | 0 | 405 | 53 | 0 | 0 | 0 | 68 | 0 | 2 | 109 | 480 |  | 6445 | 3248 | 9693 | 3535 | 927 | 2207 | 2082 | 630 | 42 | 120 | 132 | 18 | 0 | 97.43
16:00 | 0 | 0 | 200 | 115 | 0 | 88 | 0 | 0 | 349 |  | 0 | 380 | 6 | 100 | 97 | 15 | 305 | 0 | 100 | 0 | 100 | 40 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 10 | 0 | 11 | 12 | 21 | 5 | 0 | 0 | 80 | 270 | 0 | 184 | 55 | 93 | 29 | 52 | 0 | 51 | 0 | 0 | 0 | 18 | 5 | 33 | 15 | 128 | 153 | 0 | 17 | 0 | 89 | 30 | 50 | 47 | 130 | 190 | 63 | 88 | 0 | 97 | 18 | 0 | 10 | 270 | 24 | 8 | 0 | 239 | 0 | 0 | 194 | 0 | 149 | 6 | 70 | 0 | 50 | 0 | 16 | 51 | 0 | 2 | 140 | 17 | 0 | 0 | 113 | 40 | 0 | 104 |  | 927 | 0 | 340 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 81 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 76 | 0 | 162 | 0 | 380 | 17 | 0 | 0 | 0 | 93 | 0 | 2 | 109 | 470 |  | 6195 | 3135 | 9330 | 3513 | 927 | 2070 | 1890 | 620 | 42 | 130 | 128 | 10 | 0 | 97.46
17:00 | 0 | 0 | 200 | 115 | 0 | 88 | 0 | 0 | 348 |  | 0 | 390 | 15 | 100 | 97 | 15 | 282 | 0 | 92 | 0 | 100 | 40 | 10 | 5 | 0 | 0 | 0 | 17 | 55 | 17 | 22 | 25 | 28 | 33 | 25 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 204 | 0 | 138 | 0 |  | 0 | 0 | 17 | 0 | 11 | 12 | 21 | 6 | 0 | 0 | 80 | 260 | 0 | 183 | 55 | 85 | 29 | 54 | 0 | 51 | 0 | 0 | 1 | 18 | 5 | 33 | 15 | 120 | 153 | 0 | 17 | 0 | 90 | 30 | 51 | 47 | 110 | 185 | 40 | 20 | 0 | 97 | 18 | 0 | 10 | 285 | 24 | 8 | 0 | 199 | 0 | 0 | 194 | 0 | 149 | 1 | 70 | 0 | 55 | 0 | 16 | 51 | 0 | 0 | 140 | 17 | 0 | 50 | 113 | 40 | 0 | 104 |  | 927 | 0 | 340 | 0 | 9 | 120 | 0 | 0 | 0 | 0 | 0 | 81 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 163 | 0 | 76 | 0 | 163 | 0 | 300 | 17 | 0 | 0 | 0 | 76 | 0 | 2 | 109 | 450 |  | 6063 | 3045 | 9108 | 3433 | 927 | 1929 | 1894 | 601 | 42 | 159 | 120 | 3 | 0 | 97.49
18:00 | 0 | 0 | 185 | 115 | 0 | 43 | 0 | 0 | 280 |  | 0 | 320 | 50 | 100 | 97 | 29 | 307 | 0 | 50 | 0 | 100 | 64 | 80 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 23 | 0 | 43 | 0 | 120 | 0 | 19 | 203 | 0 | 104 | 0 |  | 0 | 0 | 77 | 0 | 63 | 16 | 21 | 10 | 0 | 0 | 80 | 260 | 0 | 187 | 55 | 96 | 29 | 52 | 0 | 51 | 0 | 0 | 36 | 18 | 8 | 33 | 15 | 148 | 156 | 0 | 17 | 0 | 89 | 30 | 50 | 47 | 110 | 192 | 67 | 20 | 0 | 98 | 18 | 0 | 10 | 260 | 24 | 8 | 0 | 262 | 0 | 0 | 195 | 0 | 149 | 0 | 100 | 0 | 85 | 0 | 19 | 70 | 0 | 0 | 140 | 19 | 0 | 50 | 113 | 90 | 0 | 104 |  | 926 | 0 | 310 | 0 | 100 | 170 | 0 | 0 | 0 | 6 | 40 | 81 | 23 | 48 | 0 | 0 | 0 | 25 | 0 | 36 | 0 | 0 | 45 | 25 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 76 | 0 | 135 | 0 | 270 | 70 | 0 | 54 | 0 | 79 | 0 | 2 | 109 | 430 |  | 6534 | 3382 | 9916 | 3348 | 926 | 1698 | 2732 | 580 | 43 | 439 | 148 | 2 | 0 | 97.52
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 200 | 115 | 0 | 43 | 0 | 0 | 348 |  | 0 | 400 | 70 | 95 | 97 | 40 | 267 | 0 | 92 | 0 | 100 | 93 | 150 | 79 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 43 | 0 | 43 | 0 | 120 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 102 | 0 | 90 | 48 | 21 | 14 | 0 | 0 | 80 | 310 | 0 | 177 | 55 | 87 | 29 | 53 | 0 | 51 | 0 | 0 | 43 | 18 | 8 | 33 | 10 | 154 | 158 | 0 | 17 | 0 | 89 | 30 | 53 | 47 | 163 | 186 | 67 | 88 | 0 | 97 | 18 | 0 | 10 | 270 | 24 | 0 | 0 | 300 | 0 | 0 | 186 | 0 | 149 | 0 | 100 | 0 | 100 | 0 | 90 | 86 | 0 | 0 | 141 | 52 | 0 | 101 | 113 | 100 | 0 | 104 |  | 926 | 0 | 355 | 0 | 99 | 230 | 0 | 0 | 0 | 0 | 40 | 81 | 27 | 48 | 0 | 0 | 0 | 30 | 0 | 97 | 0 | 0 | 46 | 52 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 199 | 0 | 76 | 70 | 190 | 0 | 375 | 90 | 0 | 94 | 0 | 101 | 0 | 0 | 109 | 570 |  | 7384 | 4087 | 11471 | 3567 | 926 | 2094 | 3312 | 720 | 43 | 655 | 154 | 0 | 0 | 97.55
19:30 | 0 | 0 | 200 | 115 | 0 | 43 | 0 | 0 | 348 |  | 0 | 400 | 95 | 93 | 97 | 40 | 298 | 0 | 92 | 0 | 100 | 93 | 115 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 25 | 0 | 43 | 0 | 120 | 0 | 8 | 204 | 0 | 139 | 0 |  | 0 | 0 | 102 | 0 | 90 | 50 | 21 | 16 | 0 | 0 | 80 | 260 | 0 | 177 | 55 | 88 | 29 | 53 | 0 | 51 | 0 | 0 | 43 | 18 | 8 | 33 | 15 | 154 | 157 | 0 | 17 | 0 | 89 | 30 | 52 | 47 | 163 | 185 | 67 | 88 | 0 | 97 | 18 | 0 | 10 | 295 | 24 | 0 | 0 | 300 | 0 | 0 | 186 | 0 | 149 | 0 | 100 | 0 | 100 | 0 | 115 | 86 | 0 | 0 | 141 | 54 | 0 | 101 | 113 | 100 | 0 | 104 |  | 925 | 0 | 350 | 0 | 99 | 230 | 0 | 0 | 0 | 0 | 40 | 81 | 27 | 32 | 0 | 0 | 0 | 43 | 0 | 98 | 0 | 0 | 46 | 52 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 188 | 0 | 76 | 100 | 192 | 0 | 345 | 90 | 0 | 113 | 0 | 105 | 0 | 0 | 109 | 590 |  | 7354 | 4113 | 11467 | 3544 | 925 | 2090 | 3337 | 740 | 43 | 634 | 154 | 0 | 0 | 0
20:00 | 0 | 0 | 199 | 115 | 0 | 43 | 0 | 0 | 348 |  | 0 | 400 | 110 | 93 | 97 | 40 | 301 | 0 | 92 | 0 | 100 | 93 | 115 | 65 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 21 | 33 | 33 | 25 | 0 | 44 | 0 | 120 | 0 | 8 | 203 | 0 | 139 | 0 |  | 0 | 0 | 85 | 0 | 90 | 50 | 21 | 20 | 0 | 0 | 80 | 260 | 0 | 177 | 55 | 94 | 29 | 52 | 0 | 51 | 0 | 0 | 43 | 18 | 8 | 33 | 15 | 146 | 157 | 0 | 17 | 0 | 89 | 30 | 53 | 47 | 163 | 186 | 64 | 88 | 0 | 97 | 18 | 0 | 10 | 280 | 24 | 0 | 0 | 300 | 0 | 0 | 186 | 0 | 149 | 0 | 100 | 0 | 100 | 0 | 115 | 86 | 0 | 0 | 140 | 54 | 0 | 101 | 113 | 100 | 0 | 104 |  | 926 | 0 | 345 | 0 | 105 | 230 | 0 | 0 | 0 | 0 | 40 | 81 | 29 | 32 | 0 | 0 | 0 | 43 | 0 | 98 | 0 | 0 | 47 | 52 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 174 | 0 | 76 | 100 | 184 | 0 | 389 | 90 | 0 | 113 | 0 | 106 | 0 | 0 | 109 | 622 |  | 7326 | 4173 | 11499 | 3515 | 926 | 2125 | 3353 | 772 | 44 | 618 | 146 | 0 | 0 | 97.58
21:00 | 0 | 0 | 200 | 115 | 0 | 43 | 0 | 0 | 348 |  | 0 | 400 | 120 | 93 | 97 | 40 | 293 | 0 | 92 | 0 | 100 | 93 | 98 | 28 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 44 | 0 | 120 | 0 | 8 | 203 | 0 | 139 | 0 |  | 0 | 0 | 85 | 0 | 90 | 50 | 21 | 25 | 0 | 0 | 80 | 260 | 0 | 180 | 55 | 86 | 29 | 53 | 0 | 51 | 0 | 0 | 43 | 18 | 8 | 33 | 15 | 148 | 158 | 0 | 17 | 0 | 89 | 30 | 53 | 47 | 163 | 184 | 64 | 88 | 0 | 97 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 300 | 0 | 0 | 185 | 0 | 149 | 0 | 100 | 0 | 100 | 0 | 115 | 87 | 0 | 0 | 141 | 54 | 0 | 70 | 113 | 100 | 0 | 104 |  | 926 | 0 | 345 | 0 | 115 | 230 | 0 | 0 | 0 | 0 | 40 | 81 | 29 | 32 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 153 | 0 | 75 | 100 | 168 | 0 | 358 | 90 | 0 | 113 | 0 | 105 | 0 | 0 | 109 | 622 |  | 7260 | 3997 | 11257 | 3483 | 926 | 2100 | 3273 | 772 | 44 | 511 | 148 | 0 | 0 | 97.61
22:00 | 0 | 0 | 199 | 115 | 0 | 43 | 0 | 0 | 348 |  | 0 | 400 | 145 | 93 | 97 | 40 | 298 | 0 | 60 | 0 | 100 | 93 | 82 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 44 | 0 | 120 | 0 | 8 | 203 | 0 | 139 | 0 |  | 0 | 0 | 68 | 0 | 90 | 19 | 21 | 34 | 0 | 0 | 80 | 260 | 0 | 180 | 55 | 87 | 29 | 53 | 0 | 51 | 0 | 0 | 43 | 18 | 8 | 33 | 21 | 150 | 158 | 0 | 17 | 0 | 89 | 30 | 53 | 47 | 163 | 189 | 64 | 88 | 0 | 97 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 300 | 0 | 0 | 195 | 0 | 149 | 0 | 100 | 0 | 100 | 0 | 115 | 70 | 0 | 0 | 141 | 54 | 0 | 34 | 113 | 100 | 0 | 104 |  | 926 | 0 | 350 | 0 | 115 | 230 | 0 | 0 | 0 | 0 | 40 | 81 | 31 | 32 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 153 | 0 | 77 | 100 | 161 | 0 | 371 | 90 | 0 | 70 | 0 | 105 | 0 | 0 | 109 | 622 |  | 7118 | 3914 | 11032 | 3465 | 926 | 2136 | 3091 | 772 | 44 | 448 | 150 | 0 | 0 | 97.64
23:00 | 0 | 0 | 200 | 115 | 0 | 43 | 0 | 0 | 348 |  | 0 | 400 | 150 | 93 | 97 | 30 | 311 | 0 | 60 | 0 | 100 | 24 | 48 | 0 | 0 | 0 | 0 | 17 | 17 | 55 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 42 | 0 | 120 | 0 | 8 | 204 | 0 | 139 | 0 |  | 0 | 0 | 34 | 0 | 91 | 19 | 21 | 35 | 0 | 0 | 80 | 300 | 0 | 186 | 65 | 96 | 29 | 53 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 21 | 150 | 158 | 0 | 17 | 0 | 89 | 30 | 53 | 47 | 163 | 194 | 63 | 88 | 0 | 97 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 145 | 0 | 0 | 189 | 0 | 149 | 0 | 100 | 0 | 100 | 0 | 105 | 0 | 0 | 0 | 141 | 54 | 0 | 0 | 113 | 100 | 0 | 104 |  | 927 | 0 | 350 | 0 | 115 | 230 | 0 | 0 | 0 | 0 | 40 | 81 | 31 | 16 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 155 | 0 | 76 | 100 | 181 | 0 | 414 | 90 | 0 | 70 | 0 | 105 | 0 | 0 | 109 | 622 |  | 6704 | 3963 | 10667 | 3561 | 927 | 2189 | 2646 | 772 | 42 | 380 | 150 | 0 | 0 | 97.67
24:00 | 0 | 0 | 200 | 115 | 0 | 43 | 0 | 0 | 348 |  | 0 | 400 | 140 | 92 | 97 | 15 | 310 | 0 | 60 | 0 | 100 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 42 | 0 | 120 | 0 | 8 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 91 | 0 | 21 | 40 | 0 | 0 | 80 | 290 | 0 | 179 | 65 | 89 | 29 | 53 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 21 | 142 | 158 | 0 | 17 | 0 | 89 | 30 | 53 | 47 | 163 | 185 | 64 | 88 | 0 | 97 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 145 | 0 | 0 | 183 | 0 | 149 | 0 | 100 | 0 | 50 | 0 | 105 | 0 | 0 | 0 | 142 | 54 | 0 | 0 | 113 | 100 | 0 | 104 |  | 927 | 0 | 345 | 0 | 115 | 210 | 0 | 0 | 0 | 0 | 40 | 81 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 155 | 0 | 75 | 0 | 195 | 0 | 426 | 90 | 0 | 35 | 0 | 100 | 0 | 0 | 109 | 580 |  | 6468 | 3735 | 10203 | 3537 | 927 | 2204 | 2356 | 729 | 42 | 266 | 142 | 0 | 0 | 97.7
KWH | 0 | 0 | 4759000 | 2772000 | 0 | 1794000 | 890624 | 0 | 8122000 |  | 0 | 8780800 | 740684 | 2117760 | 1920384 | 711505 | 7248349 | 0 | 1979000 | 0 | 2119680 | 836208 | 624000 | 242109 | 0 | 0 | 0 | 304560 | 583265 | 1024714 | 465660 | 600000 | 645120 | 809400 | 825000 | 104544 | 0 | 948000 | 0 | 2800000 | 0 | 95691 | 4906681 | 0 | 3315056 | 0 |  | 0 | 0 | 468799 | 0 | 666240 | 317760 | 492240 | 485760 | 0 | 0 | 1923456 | 7296900 | 0 | 4651000 | 1388363 | 2164470 | 662544 | 1252800 | 0 | 1259710 | 0 | 0 | 234754 | 426996 | 69660 | 809900 | 396910 | 3105600 | 3672160 | 0 | 378396 | 9200 | 2109000 | 714840 | 1062600 | 1031544 | 3616854 | 4469000 | 1406592 | 1755840 | 0 | 2337450 | 427000 | 0 | 238140 | 7092250 | 559752 | 165000 | 0 | 4426034 | 0 | 0 | 4279200 | 0 | 3223728 | 110295 | 1149120 | 0 | 1722909 | 0 | 904800 | 853608 | 0 | 24324 | 1994727 | 1061240 | 0 | 408120 | 2325120 | 1935360 | 0 | 2448960 |  | 22216727 | 0 | 8513280 | 0 | 735360 | 3597120 | 0 | 0 | 0 | 4736 | 282375 | 1949072 | 554108 | 206976 | 0 | 136000 | 0 | 100342 | 0 | 490952 | 0 | 0 | 130719 | 169440 | 0 | 489840 | 0 | 240732 | 0 | 0 | 3698000 | 0 | 0 | 0 | 0 | 4312091 | 0 | 1730311 | 546240 | 4506864 | 0 | 9128900 | 1224000 | 0 | 634080 | 0 | 1196160 | 0 | 20450 | 1706976 | 12938800 |  | 149072819 | 81460651 | 230533470 | 85916571 | 22216727 | 50674444 | 45454391 | 16636800 | 948000 | 5416668 | 3105600 | 164269 | 0
Fuel Cost | 0 | 0 | 6948140 | 4074840 | 0 | 2368080 | 1514060.8 | 0 | 8365660 |  | 0 | 9571072 | 822159.24 | 16073798.4 | 13231445.76 | 6019332.3 | 7538282.96 | 0 | 3423670 | 0 | 15961190.4 | 7626216.96 | 6140160 | 2232244.98 | 0 | 0 | 0 | 2223288 | 4508638.45 | 10103680.04 | 349245 | 450000 | 0 | 0 | 0 | 1010940.48 | 0 | 255960 | 0 | 5068000 | 0 | 888969.39 | 5348282.29 | 0 | 5635595.2 | 0 |  | 0 | 0 | 4547350.3 | 0 | 5796288 | 2516659.2 | 620222.4 | 1442707.2 | 0 | 0 | 2827480.32 | 5399706 | 0 | 4278920 | 1790988.27 | 2489140.5 | 748674.72 | 1753920 | 0 | 2154104.1 | 0 | 0 | 2241900.7 | 542284.92 | 52245 | 1417325 | 297682.5 | 23292000 | 3892489.6 | 0 | 480562.92 | 146648 | 3458760 | 1143744 | 1891428 | 1609208.64 | 4123213.56 | 4647760 | 2770986.24 | 3353654.4 | 0 | 4043788.5 | 935130 | 0 | 485805.6 | 7163172.5 | 419814 | 125400 | 0 | 33460817.04 | 0 | 0 | 22251840 | 0 | 31721483.52 | 1289348.55 | 9365328 | 0 | 12146508.45 | 0 | 8251776 | 8066595.6 | 0 | 0 | 15080136.12 | 9243400.4 | 0 | 4073037.6 | 19926278.4 | 12889497.6 | 0 | 0 |  | 127968347.52 | 0 | 8938944 | 0 | 5779929.6 | 49856083.2 | 0 | 0 | 0 | 49633.28 | 2942347.5 | 2202451.36 | 858867.4 | 2020085.76 | 0 | 278800 | 0 | 987365.28 | 0 | 4344925.2 | 0 | 0 | 1266667.11 | 1641873.6 | 0 | 940492.8 | 0 | 182234.124 | 0 | 0 | 20043160 | 0 | 0 | 0 | 0 | 5691960.12 | 0 | 2595466.5 | 9291542.4 | 5273030.88 | 0 | 9037611 | 12778560 | 0 | 6017419.2 | 0 | 9282201.6 | 0 | 225972.5 | 12614552.64 | 56801332 |  | 440420165.02 | 359911856.574 | 800332021.594 | 101995592.554 | 127968347.52 | 61019512.77 | 340101963.33 | 76844492 | 255960 | 67192184.37 | 23292000 | 1661969.05 | 0
Yesterday Day Peak | 0 | 0 | 200 | 115 | 0 | 86 | 65 | 0 | 350 |  | 0 | 360 | 5 | 100 | 48 | 40 | 318 | 0 | 100 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 40 | 0 | 120 | 0 | 0 | 223 | 0 | 142 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 21 | 4 | 0 | 0 | 80 | 330 | 0 | 217 | 55 | 96 | 29 | 51 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 15 | 128 | 150 | 0 | 17 | 0 | 89 | 30 | 44 | 41 | 163 | 200 | 65 | 87 | 0 | 97 | 18 | 0 | 9 | 310 | 24 | 0 | 0 | 195 | 0 | 0 | 185 | 0 | 139 | 20 | 10 | 0 | 50 | 0 | 0 | 34 | 0 | 5 | 72 | 52 | 0 | 0 | 111 | 100 | 0 | 104 |  | 926 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 81 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 198 | 0 | 76 | 0 | 203 | 0 | 393 | 17 | 0 | 0 | 0 | 0 | 0 | 2 | 70 | 470 |  | 9260 | DayPeak
Yesterday Evening Peak | 0 | 0 | 199 | 115 | 0 | 43 | 0 | 0 | 348 | 0 | 0 | 400 | 110 | 93 | 97 | 40 | 301 | 0 | 92 | 0 | 100 | 93 | 115 | 65 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 21 | 33 | 33 | 25 | 0 | 44 | 0 | 120 | 0 | 8 | 203 | 0 | 139 | 0 | 0 | 0 | 0 | 85 | 0 | 90 | 50 | 21 | 20 | 0 | 0 | 80 | 260 | 0 | 177 | 55 | 94 | 29 | 52 | 0 | 51 | 0 | 0 | 43 | 18 | 8 | 33 | 15 | 146 | 157 | 0 | 17 | 0 | 89 | 30 | 53 | 47 | 163 | 186 | 64 | 88 | 0 | 97 | 18 | 0 | 10 | 280 | 24 | 0 | 0 | 300 | 0 | 0 | 186 | 0 | 149 | 0 | 100 | 0 | 100 | 0 | 115 | 86 | 0 | 0 | 140 | 54 | 0 | 101 | 113 | 100 | 0 | 104 |  | 926 | 0 | 345 | 0 | 105 | 230 | 0 | 0 | 0 | 0 | 40 | 81 | 29 | 32 | 0 | 0 | 0 | 43 | 0 | 98 | 0 | 0 | 47 | 52 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 174 | 0 | 76 | 100 | 184 | 0 | 389 | 90 | 0 | 113 | 0 | 106 | 0 | 0 | 109 | 622 |  | 11499 | EvPeak
Forecast for Evening | 0 | 0 | 220 | 115 | 0 | 94 | 0 | 0 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 335 | 0 | 100 | 0 | 100 | 93 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 44 | 0 | 120 | 0 | 25 | 221 | 0 | 145 | 0 | 0 | 0 |  | 100 | 100 | 90 | 50 | 20 | 40 | 0 | 0 | 80 | 360 | 0 | 225 | 65 | 100 | 30 | 55 | 0 | 51 | 0 | 42 | 34 | 18 | 8 | 33 | 21 | 173 | 160 | 0 | 16 | 0 | 90 | 30 | 51 | 47 | 163 | 200 | 65 | 86 | 0 | 97 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 85 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 104 |  | 934 | 16 | 410 | 0 | 115 | 225 | 0 | 0 | 30 | 60 | 40 | 86 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 0 | 0 | 43 | 52 | 34 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 200 | 0 | 78 | 100 | 220 | 0 | 414 | 105 | 200 | 90 | 100 | 113 | 0 | 0 | 113 | 620
Forecast for Day | 0 | 0 | 220 | 115 | 0 | 94 | 0 | 0 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 335 | 0 | 100 | 0 | 100 | 93 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 44 | 0 | 120 | 0 | 25 | 221 | 0 | 140 | 0 | 0 | 0 |  | 100 | 100 | 90 | 50 | 20 | 10 | 0 | 0 | 80 | 360 | 0 | 225 | 65 | 100 | 30 | 55 | 0 | 51 | 0 | 0 | 34 | 18 | 8 | 33 | 21 | 162 | 160 | 0 | 16 | 1.6 | 90 | 30 | 51 | 47 | 163 | 200 | 65 | 86 | 0 | 97 | 18 | 0 | 10 | 341 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 200 | 150 | 0 | 115 | 85 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 104 |  | 934 | 0 | 410 | 0 | 115 | 225 | 0 | 0 | 0 | 0 | 40 | 86 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 52 | 0 | 22 | 10 | 9 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 200 |  | 78 | 50 | 220 | 0 | 414 | 105 | 100 | 90 | 100 | 100 | 0 | 8 | 113 | 620
Generation at 08:00(Today) | 0 | 0 | 200 | 115 | 0 | 42 | 0 | 0 | 302 | 0 | 0 | 340 | 150 |  | 48 | 15 | 313 | 0 | 60 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 22 | 25 | 28 | 18 | 33 | 0 | 0 | 44 | 0 | 120 | 0 | 0 | 215 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 2 | 0 | 0 | 80 | 285 | 0 | 197 | 65 | 95 | 26 | 52 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 18 | 110 | 157 | 0 | 17 | 0 | 60 | 30 | 28 | 0 | 130 | 204 | 63 | 88 | 0 | 97 | 18 | 0 | 10 | 310 | 24 | 8 | 0 | 0 | 0 | 0 | 100 | 0 | 149 | 13 | 0 | 0 | 10 | 0 | 0 | 50 | 0 | 2 | 15 | 17 | 0 | 0 | 55 | 55 | 0 | 104 | 0 | 924 | 0 | 345 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 81 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 186 | 0 | 77 | 0 | 173 | 0 | 360 | 0 | 0 | 0 | 0 | 34 | 0 | 2 | 35 | 450 | 0
199
| Minimum Generation |  | 7876 | 7:00
| Highest Generation |  | 11499 | 20:00
| Day Peak Generation |  | 9260 | 12:00
| Evening Peak Generation |  | 11499 | 20:00
| HVDC Max Flow |  | 927 | 10:00
| HVDC EvPeak Flow |  | 926 | 20:00
| Load factor L.F |  | 83.53%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-09-28
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-09-27 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9260 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 8201 | MW
Evening Peak Generation : |  | 11499 | MW Hour : | 20:00 | Available Max Generation : |  | 14458 | MW
E.P. Demand (at gen end) : |  | 11499 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 11900 | MW
Maximum Generation : |  | 11499 | MW Hour : | 20:00 | Reserve(Generation end) |  | 2558 | MW
Total Gen. (MKWH) : |  | 230.5335 | System Load Factor : | 83.53% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 248 | MW at | 22:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-09-28
Actual : | 97.86 | Ft.(MSL) , | Rule curve : | 105.04 | Ft.( MSL )
Gas Consumed : | Total = | 1148.49 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 163015105.324
: |  | Coal : | 76844492 | Oil : | 407294147.7 | Total : | 647153745.024
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4226.6532 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1439.3167 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1289.9401 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1165.6975 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1053.3535 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 850.0241 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 472.6914 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 218.7895 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 655.5932 |  |  | 0 | 0%
Total | 0 |  | 11372.0593 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Bibiyana #3
3) Ghorasal Unit-1,2,3,7
4) Ashuganj unit-3,4
5) Kaptai-2,4,5
6) Raozan #1,2
7) Sirajganj #1
8) Baghabari-71 MW,100 MW
9) Ashuganj (S)-360 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Rangpur-Kurigram 132 kV Ckt tripped at 08:07 showing Dist. Z1, SOTF relay and was switched on at |  |  |  |  | About 10 MW power interruption occurred under Kurigram S/S area
12:35. |  |  |  |  | from 08:07 to 12:35.
b) Mymensingh-Netrokona 132 kV Ckt-2 was under shut down from 09:15 to 15:27 for insulator disc replacement.
c) Sherpur(Bogura) 132/33 kV T-1 transformer was under shut down from 10:28 to 17:30 for A/M.
d) Sirajganj 132/33 kV T-1 transformer was under shut down from 12:25 to 15:59 for D/W.
e) Mymensingh-Kishoreganj 132 kV Ckt-1 was under shut down from 09:01 to 12:56 for problem with micro
switch of air compressor of CB.
f) Khulna(C)-Noapara 132 kV Ckt-1 was under shut down from 10:30 to 14:54 for protection work.
g) Meghnaghat Summit CCPP GT_1 was synchronized at 10:12 and ST was synchronized at 16:28.
h) Rajendrapur 132/33 kV T-2 transformer was under shut down from 10:00 to 13:37 for project work.
i) Shahjibazar 132/33 kV T-4 & T-6 transformers were under shut down from 11:09 to 13:45 for protection work.
j) Sirajganj 132/33 kV T-2 transformer was under shut down from 16:21 to 18:05 for D/w.
k) Ghorashal unit-7 GT was synchronized at 20:02 ant ST was synchronized at 21:56
l) Matarbari S/S 132/33 kV T-1 transformer was under shut down from 18:53 to 21:35 for R/H maintenance
at Y-phase,CT clamp of 33 kV feeder.
m) Halishahar 132/33 kV T-1 transformer was under shut down from 21:45 to 22:14 for CT loop maintenance
at 33 kV side.
n) Kabirpur-Kaliakoir 132 kV Ckt-1 was under shut down from 06:15(28/9/2020) to 10:03 for C/M.
o) Mymensingh-Netrokona 132 kV Ckt-1 was shut down at 07:15(28/9/2020) for C/M.
p) Manikganj 132/33 kV GT-3 transformer was under shut down from 06:20(28/9/2020) to 07:55 for C/M.
q) Bogura 3 kV Bus under 132/33 kV T-1 transformer was under shut down from 07:10(28/9/2020) to 08:41
for R/H maintenance at EPL 33 kV feeder.
r) Hathazari 132/33 kV T-1 transformer was under shut down from 23:05 to 00:05(28/9/2020) for R/H |  |  |  |  | About 25 MW power interruption occurred under Hathazari S/S area
maintenance at CT. |  |  |  |  | from 23:05 to 00:05(28/9/2020).
s) Pabna-Ishurdi 132 kV Ckt was under shut down from 07:47(28/9/2020) to 09:52 for C/M.
t)Joydevpur-Kodda 132 kV Ckt-1 tripped at 07:43(28/9/2020) showing Dist. A,B,C at Joydevpur end
and was switched on at 08:04.
u) Fenchuganj-Kulaura 132 kV Ckts 1 & 2 tripped at 07:43(28/9/2020) due to Kulaura 132 kV Bus-coupler |  |  |  |  | About 22 MW power interruption occurred under Fenchuganj S/S area
PT burst and were switched on at 08:40. |  |  |  |  | from 07:43(28/9/2020) to 08:40.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-09-27 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 199 | 4759000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 115 | 2772000 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Machine problem
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 890624 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 43 | 1794000 | Low demand.
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 348 | 8122000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 8780800 | Frequency control
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 93 | 2117760 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 110 | 740684 | Gas shorage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 97 | 1920384 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 40 | 711505 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 65 | 242109 | Low demand.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 465660
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 92 | 1979000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 2119680
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 301 | 7248349 | FGMO
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 836208 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel Shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 304560
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 115 | 624000 | Low demand.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 583265 | Low demand.
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1024714
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 46 | 1245120 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 809400
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 825000
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 25 | 104544 | Low demand.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 4426034
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3223728
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 86 | 853608 | Low demand.
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2448960
| Dhaka area Total |  |  |  | 5895 | 3153 | 61972696
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2800000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 8 | 95691 | Low demand.
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 110295
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 317760
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 44 | 948000 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4906681
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 139 | 3315056
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 468799
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1149120
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 492240
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 20 | 485760
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 90 | 666240 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 24324
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 140 | 1994727 | Low demand.
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1061240
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1935360
| Chattogram area Total |  |  |  | 2266 | 1174 | 20771293
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 1923456
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 177 | 4651000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 260 | 7296900 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 662544 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 52 | 1252800
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 55 | 1388363 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1259710
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 100 | 1722909 | Low demand.
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 94 | 2164470
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve.
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 426996 | Engine problem
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 69660 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 146 | 3105600
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 809900
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 234754
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 15 | 396910 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 101 | 408120 | Engine problem
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 2325120
| Cumilla Area Total |  |  |  | 2980 | 1375 | 30099212
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 157 | 3672160 | Machine problem & Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 378396 | Engine problem
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 0 | 0 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9200
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 186 | 4279200
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 904800 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 475 | 9243756
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 89 | 2109000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 714840 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3616854 | Frequency control
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 186 | 4469000 | Gas shortage.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1062600
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 47 | 1031544
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 165000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 64 | 1406592
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 88 | 1755840
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 97 | 2337450
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 427000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 559752
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7092250 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 238140
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1149 | 26985862
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 926 | 22216727
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 105 | 735360
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 230 | 3597120
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 4736 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 345 | 8513280 | Frequency control
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 282375
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 546240
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 90 | 1224000 | Engine problem
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1836 | 37119838
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 206976 | High voltage
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 29 | 554108
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 81 | 1949072 | GT-2 Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 76 | 1730311 | Engine problem
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 622 | 12938800 | Under maint unit 1
| Barisal Area Total |  |  |  | 1054 | 840 | 17379267
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 136000
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 100342
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel Shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel Shortage
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 47 | 130719
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | STG U/M & Gas Shortage
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 174 | 4312091 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 184 | 4506864 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 389 | 9128900 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 489840
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 240732
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 169440
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 98 | 490952
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 634080
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 1706976
| Rajshahi Area Total |  |  |  | 2183 | 1241 | 22046936
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3698000 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 106 | 1196160
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 20450
| Rangpur Area Total |  |  |  | 605 | 256 | 4914610
| Total |  |  |  | 19892 | 11499 | 230533470
| Eastern Grid Total |  |  |  | 13766 | 7326 | 149072819
| Western Grid Total |  |  |  | 6126 | 4173 | 81460651
| National Grid Total |  |  |  | 19892 | 11499 | 230533470
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-09-27
| (a) ENTIRE EASTERN GRID : |  | 7408 | MW | (b) ENTIRE WESTERN GRID : |  | 3571 | MW
| i) Dhaka area |  | 3863 | MW | i) Khulna area |  | 1439 | MW
| ii) Chittagong area |  | 1127 | MW | ii) Rajshahi area |  | 1230 | MW
| iii) Comilla area |  | 1039 | MW | iii) Barisal area |  | 321 | MW
| iv) Mymensingh area |  | 930 | MW | iv) Rangpur area |  | 581 | MW
| v) Sylhet area |  | 449 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 10979 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 120 | 16:00 | Sherpur | 94 | 21:00 | Jhenida | 106 | 18:30
| Munsiganj | 114 | 21:00 | Srimongal | 62 | 18:30 | Bottail | 130 | 19:00
| Sonargaon | 86 | 19:30 | Shahjibazar | 110 | 20:00 | G.K Project | 57 | 20:00
| Shyampur | 194 | 23:00 | Fenchuganj | 28 | 19:00 | Faridpur | 188 | 0.875
| Bhulta | 193 | 24:00 | Kulawara | 40 | 18:30 | Madaripur | 88 | 0.8125
| Madanganj | 50 | 21:00 | Sylhet | 116 | 18:30 | Sariatpur | 56 | 21:00
| Shitalakhya | 95 | 13:00 | Chatak | 24 | 19:30 | Gopalganj | 91 | 19:30
| Rahim steel | 22 | 16:00 | Sunamganj | 40 | 20:00 | Bagerhat | 87 | 22:00
| Matuail | 82 | 16:00 | Biani Bazar | 54 | 18:00 | Mongla | 38 | 9:00
| Ghorasal | 75 | 23:00 | Comilla (S) | 156 | 18:30 | Satkhira | 105 | 0.79167
| Narsingdi | 154 | 19:30 | Comilla(N) | 99 | 20:00 | Gallamari | 41 | 23:00
| Haripur (SBU) | 98 | 18:00 | Chandpur | 90 | 21:00 | Magura | 54 | 0.79167
| Ullon | 57 | 18:00 | Feni | 103 | 18:30 | Norail | 40 | 18:30
| Hasnabad | 193 | 19:30 | Chowmuhani | 156 | 18:30 | Chuadanga | 94 | 20:00
| Magbazar | 103 | 13:00 | Ashuganj | 56 | 0:00 | Barisal(N) | 39 | 0.83333
| Maniknagar | 86 | 12:00 | Daudkandi | 124 | 19:30 | Barisal (S) | 88 | 0.77083
| Bangabhaban | 34 | 13:00 | B.Baria | 145 | 20:00 | Patuakhali | 111 | 0.91667
| Narinda | 88 | 18:00 | Ramganj | 100 | 18:30 | Bhandaria | 52 | 0.875
| Dhanmondi | 164 | 12:00 | Chaddagram | 32 | 18:00 | Borhan Uddin | 42 | 21:00
| Lalbag | 86 | 13:00 | PHP | 10 | 21:00 | Ishurdi | 61 | 18:30
| Madartek | 65 | 21:00 | Madunaghat | 58 | 23:00 | Ruppur Paromanobik | 2 | 9:00
| Dhaka University |  |  | Hathazari | 94 | 0.75 | Natore | 117 | 18:30
| Fatullah | 41 | 0.41667 | Khulshi | 197 | 0.5 | Bogra | 161 | 18:30
| Mirpur | 99 | 18:30 | Halishahar | 133 | 0.83333 | Noagaon | 104 | 19:30
| Kalyanpur | 99 | 18:00 | Baraulia | 140 | 0.041667 | Rajshahi | 140 | 21:00
| Gulshan | 120 | 13:00 | Sikalbaha | 24 | 0.77083 | Rajshahi New | 13 | 20:00
| Uttara | 87 | 13:00 | Dohazari | 78 | 0.8125 | C.Nawabganj | 70 | 21:00
| Uttara New | 31 | 11:00 | Cox'sbazar | 100 | 0.77083 | Amnura | 42 | 20:00
| Kamrangirchar | 85 | 18:30 | Chandraghona | 28 | 0.75 | Pabna | 120 | 20:00
| Savar | 130 | 15:00 | Kaptai | 4.4 | 0.75 | Shahjadpur | 98 | 20:00
| Bhasantec | 142 | 13:00 | A. Khaer Stl. | 8 | 0.41667 | Serajganj | 108 | 20:00
| Agargaon | 71 | 13:00 | Bakulia | 95 | 0.8125 | Niyamatpur | 55 | 21:00
| Satmosjid | 79 | 14:00 | Julda | 21 | 0.083333 | Joypurhat | 62 | 20:00
| Tongi | 99 | 0.625 | TK chemical | 27 | 0.77083 | Sherpur(Bogura) | 47 | 18:30
| Kabirpur | 231 | 15:00 | Modern Steel | 12 | 0.95833 | Mohastangor | 48 | 19:00
| Basundhara | 126 | 18:30 | Shahmirpur | 21 | 0.625 | Rangpur | 95 | 19:00
| Manikganj | 64 | 0.875 | Khagrachhari | 24 | 0.79167 | Lalmonirhat | 43 | 21:00
| Joydevpur | 153 | 19:00 | Matarbari | 36 | 0.77083 | Saidpur | 81 | 19:00
| New Tongi | 119 | 12:00 | Baroiar Hat | 44 | 0.8125 | Purbasadipur | 92 | 20:00
| Korda | 232 | 15:00 | Rangamati | 12 | 0.77083 | Thakurgaon | 68 | 19:00
| Dhamrai | 88 | 21:00 | Abul Khair 230 | 54 | 0.125 | Palashbari | 106 | 21:00
| Rajendrapur | 100 | 19:00 | BSRM | 107 | 0.66667 | Barapukuria | 47 | 21:00
| Valuka | 120 | 18:30 | GPH Ispat | 25 | 0.70833 | Panchagar | 45 | 18:30
| Tangail | 198 | 20:00 | Goalpara | 26 | 0.041667 | Joldhaka | 22 | 19:00
| Mymensing | 172 | 20:00 | Central s/s | 90 | 18:30 | Kurigram | 48 | 19:00
| Kishorganj | 118 | 23:00 | Noapara | 55 | 19:30
| Netrokona | 114 | 19:00 | Jessore | 114 | 19:00
| Jamalpur | 135 | 21:00 | Benapol | 48 | 19:00
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-09-27 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 394 | 19:00 | 387 | 16:00 | Kaliakoir | 374 | 0.75 | 363 | 0.5
| Bheramara | 399 | 19:00 | 389 | 19:00 | Bhulta | 387 | 0.91667 | 375 | 0.5
| Ashuganj(N) | 392 | 22:00 | 383 | 11:00 | Gopalganj | 415 | 0.25 | 394 | 0.83333
| Payra | 415 | 21:00 | 402 | 20:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 232 | 1:00 | 230 | 8:00 | Comilla (N) | 233 | 20:00 | 228 | 10:00
| Ishurdi | 231 | 6:00 | 225 | 12:00 | Hathazari | 227 | 18:30 | 219 | 9:00
| Ashuganj | 235 | 1:00 | 230 | 8:00 | Megnaghat | 231 | 6:00 | 224 | 11:00
| Serajganj | 232 | 2:00 | 227 | 21:00 | Fenchuganj | 239 | 1:00 | 234 | 11:00
| Baghabari | 238 | 1:00 | 235 | 23:00 | Siddhirganj | 228 | 2:00 | 222 | 9:00
| Barapukuria | 239 | 1:00 | 234 | 22:00 | Maniknagar | 226 | 22:00 | 220 | 12:00
| Bogra | 229 | 18:00 | 222 | 22:00 | Agargaon | 225 | 18:00 | 216 | 12:00
| Rajshahi | 229 | 18:00 | 214 | 1:00 | Barisal | 245 | 18:00 | 233 | 20:00
| Khulna South | 232 | 19:30 | 224 | 12:00 | AKSML | 223 | 18:00 | 217 | 10:00
| Rampura | 227 | 5:00 | 220 | 12:00 | BSRM | 225 | 19:00 | 218 | 8:00
| Haripur | 228 | 22:00 | 218 | 12:00 | Bibiyana | 237 | 19:00 | 231 | 12:00
| Hasnabad | 228 | 17:00 | 219 | 11:00 | Bhulta | 230 | 19:00 | 222 | 17:00
| Shyampur | 224 | 21:00 | 215 | 12:00 | Ashuganj (S) | 234 | 19:30 | 228 | 11:00
| Aminbazar | 224 | 1:00 | 218 | 12:00 | Kaliakoir | 229 | 22:00 | 221 | 11:00
| Tongi | 223 | 4:00 | 215 | 11:00 | GPH | 223 | 22:00 | 216 | 9:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 131 | 21:00 | 125 | 12:00 | Hathazari | 135 | 0.77083 | 130 | 0.29167
| Munsiganj | 133 | 18:00 | 123 | 12:00 | Khulshi | 133 | 0.79167 | 127 | 0.375
| Sonargaon | 132 | 18:00 | 125 | 7:00 | Halishahar | 136 | 0.875 | 128 | 0.375
| Shyampur | 133 | 21:00 | 126 | 12:00 | Baraulia | 134 | 0.875 | 128 | 0.083333
| Bhulta | 125 | 18:00 | 119 | 11:00 | Sikalbaha | 136 | 22:00 | 129 | 0.29167
| Madanganj | 135 | 21:00 | 124 | 12:00 | Dohazari | 132 | 18:00 | 126 | 0.041667
| Shitalakhya | 140 | 21:00 | 127 | 12:00 | Cox'sbazar | 125 | 0.29167 | 117 | 0
| Rahim steal | 131 | 21:00 | 125 | 12:00 | Chandraghona | 134 | 0.75 | 129 | 0.45833
| Matuail | 131 | 21:00 | 125 | 12:00 | Kaptai | 135 | 1:00 | 130 | 0.29167
| Ghorasal | 136 | 1:00 | 136 | 1:00 | A. Khaer Stl. | 132 | 0.75 | 128 | 9:00
| Narsinghdi | 127 | 22:00 | 120 | 12:00 | Bakulia | 135 | 0.79167 | 128 | 0.29167
| Haripur (SBU) | 132 | 1:00 | 125 | 12:00 | Julda | 135 | 0.75 | 129 | 0.29167
| Ullon | 134 | 3:00 | 127 | 12:00 | TK Chemical | 135 | 0.875 | 129 | 11:00
| Hasnabad | 135 | 18:30 | 129 | 10:00 | Modern Steel | 135 | 0.77083 | 128 | 0.45833
| Magbazar | 135 | 2:00 | 127 | 12:00 | Shahmirpur | 135 | 0.8125 | 129 | 0.33333
| Maniknagar | 133 | 21:00 | 126 | 12:00 | Khagrachhari | 133 | 0.79167 | 128 | 0.45833
| Bangabhaban | 133 | 21:00 | 126 | 12:00 | Matarbari | 126 | 0.58333 | 120 | 0.041667
| Narinda | 133 | 21:00 | 126 | 12:00 | Baroiar Hat | 135 | 0.75 | 128 | 0.45833
| Dhanmondi | 134 | 3:00 | 127 | 12:00 | Rangamati | 133 | 0.75 | 129 | 8:00
| Lalbag | 135 | 19:00 | 123 | 12:00 | Goalpara S/S | 134 | 8:00 | 129 | 12:00
| Madartek | 133 | 1:00 | 127 | 11:00 | Khulna Central S/S | 137 | 0.75 | 129 | 12:00
| Dhaka University |  |  |  |  | Noapara | 135 | 18:00 | 124 | 12:00
| Fatuiiah | 133 | 0.91667 | 126 | 11:00 | Jessore | 132 | 18:00 | 120 | 13:00
| Mirpur | 136 | 5:00 | 128 | 12:00 | Benapol | 132 | 18:00 | 122 | 12:00
| Kalyanpur | 135 | 21:00 | 129 | 12:00 | Jhenida | 127 | 0.75 | 116 | 20:00
| Gulshan | 133 | 1:00 | 127 | 11:00 | Bottail | 134 | 7:00 | 126 | 19:00
| Uttara | 132 | 6:00 | 126 | 12:00 | G.K Project | 141 | 0.75 | 135 | 20:00
| Uttara New | 133 | 3:00 | 126 | 14:00 | Faridpur | 133 | 7:00 | 125 | 19:00
| Kamrangirchar | 133 | 19:30 | 126 | 17:00 | Madaripur | 138 | 0.41667 | 130 | 19:00
| Savar | 133 | 4:00 | 127 | 12:00 | Shariyatpur S/S | 137 | 0.29167 | 127 | 19:00
| Bhasantec | 136 | 6:00 | 129 | 12:00 | Gopalganj | 137 | 7:00 | 125 | 19:00
| Agargaon | 137 | 2:00 | 130 | 12:00 | Bagerhat | 132 | 18:00 | 122 | 16:00
| Satmosjid | 137 | 6:00 | 130 | 12:00 | Mongla | 128 | 0.33333 | 120 | 12:00
| Tongi | 135 | 0.91667 | 129 | 11:00 | Satkhira | 135 | 0.75 | 127 | 16:00
| Kabirpur | 132 | 7:00 | 125 | 12:00 | Gallamari | 137 | 18:00 | 129 | 12:00
| Basundhara | 133 | 22:00 | 127 | 13:00 | Magura | 126 | 7:00 | 115 | 18:30
| Manikganj | 138 | 19:30 | 131 | 14:00 | Norail | 127 | 0.29167 | 113 | 22:00
| Joydevpur | 140 | 22:00 | 134 | 13:00 | Chuadanga | 127 | 8:00 | 105 | 20:00
| New Tongi | 134 | 0.91667 | 127 | 14:00 | Barisal(N) | 139 | 6:00 | 130 | 20:00
| Kodda | 135 | 19:30 | 122 | 0.58333 | Barisal (S) | 138 | 0.75 | 127 | 20:00
| Dhamrai | 131 | 18:00 | 125 | 12:00 | Patuakhali(S) | 136 | 0.75 | 123 | 20:00
| Rajendrapur | 133 | 18:00 | 122 | 14:00 | Bhandaria | 130 | 7:00 | 121 | 15:00
| Valuka | 125 | 17:00 | 112 | 21:00 | Ishurdi | 139 | 18:00 | 133 | 12:00
| Tangail | 131 | 6:00 | 123 | 18:30 | Ruppur Paromanobik | 138 | 18:00 | 133 | 12:00
| Mymensing | 129 | 17:00 | 118 | 21:00 | Natore | 137 | 18:00 | 130 | 2:00
| Kishorganj | 130 | 7:00 | 122 | 21:00 | Bogra | 139 | 18:00 | 133 | 1:00
| Netrokona | 127 | 8:00 | 114 | 18:30 | Noagaon | 135 | 18:00 | 127 | 21:00
| Jamalpur | 134 | 17:00 | 125 | 4:00 | Rajshahi | 138 | 18:00 | 130 | 1:00
| Sherpur | 135 | 17:00 | 124 | 18:00 | Rajshahi New | 139 | 18:00 | 130 | 1:00
| Srimongal | 139 | 14:00 | 135 | 0.95833 | C.Nawabganj | 138 | 18:00 | 128 | 2:00
| Shahjibazar | 137 | 15:00 | 133 | 0.83333 | Amnura | 137 | 18:00 | 126 | 3:00
| Fenchuganj | 135 | 6:00 | 134 | 0.041667 | Pabna | 136 | 7:00 | 130 | 19:30
| Khulawara | 135 | 5:00 | 133 | 0.41667 | Shahjadpur | 140 | 5:00 | 135 | 12:00
| Sylhet | 134 | 4:00 | 132 | 0.95833 | Serajganj | 135 | 18:00 | 130 | 10:00
| Chatak | 133 | 17:00 | 130 | 18:00 | Niyamatpur | 132 | 17:00 | 123 | 18:30
| Sunamganj | 132 | 4:00 | 127 | 0.91667 | Joypurhat | 135 | 18:00 | 128 | 19:00
| Biani Bazar | 133 | 6:00 | 129 | 0.75 | Sherpur(Bogura) | 138 | 18:00 | 132 | 5:00
| Comilla(s) | 125 | 5:00 | 119 | 18:00 | Mohastangor | 137 | 18:00 | 132 | 1:00
| Comilla(n) | 137 | 19:30 | 132 | 11:00 | Rangpur | 137 | 4:00 | 128 | 18:30
| Chandpur | 133 | 14:00 | 130 | 23:00 | Lalmonirhat | 140 | 4:00 | 126 | 18:30
| Feni | 133 | 20:00 | 128 | 7:00 | Saidpur | 136 | 7:00 | 125 | 18:30
| Chowmuhani | 131 | 19:00 | 122 | 11:00 | Purbasadipur | 134 | 6:00 | 124 | 18:30
| Ashuganj | 137 | 8:00 | 135 | 0:00 | Thakurgaon | 134 | 5:00 | 123 | 20:00
| Daudkandi | 132 | 17:00 | 127 | 11:00 | Palashbari | 135 | 10:00 | 127 | 21:00
| B.Baria | 134 | 15:00 | 129 | 21:00 | Barapukuria | 139 | 1:00 | 135 | 19:00
| Ramganj | 129 | 17:00 | 124 | 20:00 | Panchagar | 133 | 5:00 | 120 | 21:00
| Chaddagram | 135 | 17:00 | 132 | 15:00 | Joldhaka | 136 | 4:00 | 124 | 18:30
| PHP | 134 | 20:00 | 128 | 8:00 | Kurigram | 135 | 5:00 | 127 | 19:00
| Madanhat | 136 | 19:30 | 130 | 11:00

## L-Curve
Date | 2020-09-27
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 273 | 6468 | 3735 | 10203 |  |  |  | QF-LDC-11
0:30 | 340 | 6316 | 3532 | 9848 | Date: | 2020-09-27
1:00 | 407 | 6164 | 3329 | 9493
1:30 | 408 | 6076 | 3281 | 9357
2:00 | 409 | 5988 | 3233 | 9221
2:30 | 420 | 5915.5 | 3179 | 9094.5 | [5 empty] | Gen. at Eve. Peak | 11499 | 9500 MW (19:30 )
3:00 | 431 | 5843 | 3125 | 8968 | [6 empty] | 20:00
3:30 | 468 | 5722 | 3105 | 8827 | [5 empty] | Gen. at Day Peak | 9260 | 7952.5 MW (12:00 )
4:00 | 505 | 5601 | 3085 | 8686 | [6 empty] | 12:00
4:30 | 507.5 | 5547 | 3033 | 8580 | [5 empty] | Highest Generation | 11499
5:00 | 510 | 5493 | 2981 | 8474 | [6 empty] | 20:00
5:30 | 546.5 | 5372.5 | 2946 | 8318.5
6:00 | 583 | 5252 | 2911 | 8163
6:30 | 613.5 | 5114.5 | 2905 | 8019.5
7:00 | 644 | 4977 | 2899 | 7876
7:30 | 686.5 | 5026.5 | 2897 | 7923.5
8:00 | 729 | 5076 | 2895 | 7971
8:30 | 694.5 | 5230.5 | 2917 | 8147.5
9:00 | 660 | 5385 | 2939 | 8324
9:30 | 666 | 5564 | 2976 | 8540
10:00 | 672 | 5743 | 3013 | 8756
10:30 | 655 | 5848 | 3003.5 | 8851.5
11:00 | 638 | 5953 | 2994 | 8947
11:30 | 579 | 6069.5 | 3034 | 9103.5
12:00 | 520 | 6186 | 3074 | 9260
12:30 | 520 | 6193 | 3133 | 9326
13:00 | 520 | 6200 | 3192 | 9392
13:30 | 515.5 | 6225.5 | 3187.5 | 9413
14:00 | 511 | 6251 | 3183 | 9434
14:30 | 509.5 | 6348 | 3215.5 | 9563.5
15:00 | 508 | 6445 | 3248 | 9693
15:30 | 518.5 | 6320 | 3191.5 | 9511.5
16:00 | 529 | 6195 | 3135 | 9330
16:30 | 550.5 | 6129 | 3090 | 9219
17:00 | 572 | 6063 | 3045 | 9108
17:30 | 580.5 | 6298.5 | 3213.5 | 9512
18:00 | 589 | 6534 | 3382 | 9916
18:30 | 474.5 | 6959 | 3734.5 | 10693.5
19:00 | 360 | 7384 | 4087 | 11471
19:30 | 263 | 7354 | 4113 | 11467
20:00 | 330 | 7326 | 4173 | 11499 |  |  |  | Executive Engineer
20:30 | 370 | 7293 | 4085 | 11378 |  |  |  | Network Operation Division
21:00 | 410 | 7260 | 3997 | 11257
21:30 | 329 | 7189 | 3955.5 | 11144.5
22:00 | 248 | 7118 | 3914 | 11032 |  |  |  |  | Page 6 of 7
22:30 | 319 | 6911 | 3938.5 | 10849.5
23:00 | 390 | 6704 | 3963 | 10667
23:30 | 331.5 | 6586 | 3849 | 10435
24:00 | 273 | 6468 | 3735 | 10203
9500 MW (19:30 )
7952.5 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-09-27 |  | Energy | 230533470
[10 empty] | 2020-09-27 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3537 | 927 | 2204 | 2646 | 729 | 42 | 266 | 0 | 142
0:30 | 3596.5 | 926.5 | 2226.5 | 2152.5 | 719.5 | 41.5 | 193 | 0 | 137 | Date: | 2020-09-27
1:00 | 3656 | 926 | 2249 | 1659 | 710 | 41 | 120 | 0 | 132
1:30 | 3645 | 926 | 2229.5 | 1575.5 | 690 | 41 | 120 | 0 | 130 | [7 empty] | Total Energy | 230.5335 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 3634 | 926 | 2210 | 1492 | 670 | 41 | 120 | 0 | 128 | [7 empty] | Energy not Served | 0
2:30 | 3645 | 926 | 2211 | 1376 | 650 | 41.5 | 120 | 0 | 125 | [7 empty] | Energy Requirement | 230.5335
3:00 | 3656 | 926 | 2212 | 1260 | 630 | 42 | 120 | 0 | 122
3:30 | 3656.5 | 926 | 2216 | 1116.5 | 630 | 42 | 120 | 0 | 120 | [6 empty] | Shortage
4:00 | 3657 | 926 | 2220 | 973 | 630 | 42 | 120 | 0 | 118
4:30 | 3673.5 | 926 | 2201 | 871 | 630 | 42.5 | 120 | 0 | 116
5:00 | 3690 | 926 | 2182 | 769 | 630 | 43 | 120 | 0 | 114
5:30 | 3588.5 | 926 | 2152 | 762.5 | 614.5 | 43 | 120 | 0 | 112
6:00 | 3487 | 926 | 2122 | 756 | 599 | 43 | 120 | 0 | 110
6:30 | 3455 | 926 | 2021 | 746 | 599.5 | 43.5 | 120 | 0 | 108 |  |  |  |  | Coal
7:00 | 3423 | 926 | 1920 | 736 | 600 | 44 | 120 | 0 | 106
7:30 | 3438 | 926 | 1921 | 770 | 595 | 44 | 120 | 0 | 104 |  |  |  | Oil |  |  |  | ,
8:00 | 3453 | 926 | 1922 | 804 | 590 | 44 | 120 | 0 | 102
8:30 | 3458 | 926 | 1928 | 957.5 | 595 | 44 | 120 | 0 | 107
9:00 | 3463 | 926 | 1934 | 1111 | 600 | 44 | 120 | 0 | 112
9:30 | 3449.5 | 926.5 | 1961.5 | 1309.5 | 600 | 43.5 | 120 | 0 | 115
10:00 | 3436 | 927 | 1989 | 1508 | 600 | 43 | 120 | 0 | 118
10:30 | 3484 | 926.5 | 2082 | 1463 | 600 | 42 | 120 | 0 | 120
11:00 | 3532 | 926 | 2175 | 1418 | 600 | 41 | 120 | 0 | 122
11:30 | 3615 | 926 | 2180 | 1467 | 610 | 40.5 | 120 | 0 | 125
12:00 | 3698 | 926 | 2185 | 1516 | 620 | 40 | 120 | 0 | 128
12:30 | 3636.5 | 926 | 2199 | 1621.5 | 635 | 40 | 120 | 0 | 127
13:00 | 3575 | 926 | 2213 | 1727 | 650 | 40 | 120 | 0 | 126
13:30 | 3575 | 926 | 2213 | 1727 | 650 | 40 | 120 | 0 | 126
14:00 | 3575 | 926 | 2213 | 1727 | 650 | 40 | 120 | 0 | 126
14:30 | 3555 | 926.5 | 2210 | 1904.5 | 640 | 41 | 120 | 0 | 129
15:00 | 3535 | 927 | 2207 | 2082 | 630 | 42 | 120 | 0 | 132
15:30 | 3524 | 927 | 2138.5 | 1986 | 625 | 42 | 125 | 0 | 130
16:00 | 3513 | 927 | 2070 | 1890 | 620 | 42 | 130 | 0 | 128
16:30 | 3473 | 927 | 1999.5 | 1892 | 610.5 | 42 | 144.5 | 0 | 124
17:00 | 3433 | 927 | 1929 | 1894 | 601 | 42 | 159 | 0 | 120
17:30 | 3390.5 | 926.5 | 1813.5 | 2313 | 590.5 | 42.5 | 299 | 0 | 134
18:00 | 3348 | 926 | 1698 | 2732 | 580 | 43 | 439 | 0 | 148
18:30 | 3457.5 | 926 | 1896 | 3022 | 650 | 43 | 547 | 0 | 151
19:00 | 3567 | 926 | 2094 | 3312 | 720 | 43 | 655 | 0 | 154
19:30 | 3544 | 925 | 2090 | 3337 | 740 | 43 | 634 | 0 | 154
20:00 | 3515 | 926 | 2125 | 3353 | 772 | 44 | 618 | 0 | 146
20:30 | 3499 | 926 | 2112.5 | 3313 | 772 | 44 | 564.5 | 0 | 147
21:00 | 3483 | 926 | 2100 | 3273 | 772 | 44 | 511 | 0 | 148
21:30 | 3474 | 926 | 2118 | 3182 | 772 | 44 | 479.5 | 0 | 149
22:00 | 3465 | 926 | 2136 | 3091 | 772 | 44 | 448 | 0 | 150
22:30 | 3513 | 926.5 | 2162.5 | 2868.5 | 772 | 43 | 414 | 0 | 150
23:00 | 3561 | 927 | 2189 | 2646 | 772 | 42 | 380 | 0 | 150
23:30 | 3549 | 927 | 2196.5 | 2646 | 750.5 | 42 | 323 | 0 | 146 | Max Temp. in Dhaka |  | 30.9° C
24:00 | 3537 | 927 | 2204 | 2646 | 729 | 42 | 266 | 0 | 142
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
Note on W13: Author:

## Generation
g | 2020-09-27
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 41 | 41 | 42 | 42 | 43 | 43 | 44 | 44 | 44 | 43 | 41 | 40 | 40 | 41 | 42 | 42 | 42 | 43 |  | 43 | 43 | 44 | 44 | 44 | 42 | 42 | 948000
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 19 |  | 25 | 8 | 8 | 8 | 8 | 8 | 8 | 95691
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 |  | 7 | 9 | 8 | 7 | 20 | 9 | 12 | 14 | 6 | 1 | [9 empty] | 110295
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 203 | 203 | 203 | 215 | 203 | 203 | 204 | 203 | 204 | 204 | 223 | 205 | 204 | 204 | 204 | 204 | 203 |  | 204 | 204 | 203 | 203 | 203 | 204 | 204 | 4906681
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 139 | 140 | 139 | 139 | 141 | 139 | 139 | 139 | 139 | 140 | 139 | 142 | 140 | 139 | 140 | 139 | 138 | 104 |  | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 3315056
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [13 empty] | 14 |  | 10 | 17 | 77 |  | 102 | 102 | 85 | 85 | 68 | 34 | 0 | 468799
12 | Hathazari 100 MW peaking PP
Sikalbaha 105 MW PP (Baraka Sikalbaha)
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 85 | 80 | 92 | 94 | 97 | 32 | 32 | 35 | 35 | 32 | 80 | 100 | 100 | 99 | 100 | 100 | 92 | 50 |  | 92 | 92 | 92 | 92 | 60 | 60 | 60 | 1979000
17 | Siddhirganj 335 MW CCPP | 292 | 273 | 282 | 288 | 321 | 289 | 303 | 315 | 307 | 293 | 313 | 318 | 316 | 306 | 294 | 305 | 282 | 307 |  | 267 | 298 | 301 | 293 | 298 | 311 | 310 | 7248349
18 | Kodda 300 MW PP Unit-2 (Summit) | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 110 | 195 | 195 | 195 | 195 | 195 | 209 | 239 | 199 | 262 |  | 300 | 300 | 300 | 300 | 300 | 145 | 145 | 4426034
19 | Ashuganj 195MW PP (APSCL-United) | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 65 | 65 | 1388363
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 185 |  | 200 | 200 | 199 | 200 | 199 | 200 | 200 | 4759000
23 | Ghorasal TPP Unit-5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2772000
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1923456
32 | Ashuganj 50 MW PP | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 26 | 26 | 29 | 29 | 29 | 29 | 29 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 662544
33 | Ashuganj 225 MW CCPP | 219 | 221 | 219 | 219 | 197 | 177 | 177 | 189 | 184 | 183 | 192 | 217 | 196 | 188 | 182 | 184 | 183 | 187 |  | 177 | 177 | 177 | 180 | 180 | 186 | 179 | 4651000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 310 | 310 | 340 | 310 | 270 | 280 | 270 | 270 | 275 | 330 | 285 | 270 | 270 | 270 | 260 | 260 |  | 310 | 260 | 260 | 260 | 260 | 300 | 290 | 7296900
35 | Ashuganj 55 MW PP (Precision) | 53 | 53 | 52 | 51 | 52 | 52 | 52 | 52 | 51 | 50 | 50 | 51 | 49 | 52 | 53 | 52 | 54 | 52 |  | 53 | 53 | 52 | 53 | 53 | 53 | 53 | 1252800
36 | Chandpur 150 MW CCPP | 88 | 90 | 95 | 96 | 96 | 86 | 91 | 96 | 94 | 86 | 93 | 96 | 95 | 96 | 87 | 93 | 85 | 96 |  | 87 | 88 | 94 | 86 | 87 | 96 | 89 | 2164470
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 400 | 400 | 400 | 400 | 400 | 400 | 370 | 370 | 370 | 370 | 420 | 360 | 360 | 360 | 380 | 380 | 390 | 320 |  | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 8780800
41 | Haripur 360MW CCPP(HPL) | 354 | 354 | 354 | 353 | 351 | 354 | 302 | 302 | 303 | 333 | 354 | 350 | 351 | 347 | 348 | 349 | 348 | 280 |  | 348 | 348 | 348 | 348 | 348 | 348 | 348 | 8122000
42 | RPCL 210MW CCPP | 159 | 160 | 160 | 160 | 157 | 160 | 158 | 157 | 156 | 155 | 154 | 150 | 153 | 153 | 153 | 153 | 153 | 156 |  | 158 | 157 | 157 | 158 | 158 | 158 | 158 | 3672160
43
44 | Fenchugonj CCPP Phase-1 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 88 | 89 | 89 | 90 | 89 |  | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 2109000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 714840
46 | Shajibazar 330 MW CCPP | 202 | 202 | 202 | 203 | 200 | 200 | 202 | 202 | 202 | 202 | 200 | 200 | 200 | 202 | 187 | 190 | 185 | 192 |  | 186 | 185 | 186 | 184 | 189 | 194 | 185 | 4469000
47 | Shahjibazar GTPP Unit- 8 & 9 | 64 | 64 | 64 | 64 | 63 | 64 | 40 | 40 | 40 | 40 | 65 | 65 | 55 | 55 | 64 | 63 | 40 | 67 |  | 67 | 67 | 64 | 64 | 64 | 63 | 64 | 1406592
48 | Shahjibazar 86MW PP (Shahjibazar) | 88 | 88 | 88 | 88 | 40 | 40 | 40 | 40 | 40 | 40 | 88 | 87 | 87 | 88 | 88 | 88 | 20 | 20 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 1755840
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 98 |  | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 2337450
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 427000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 238140
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  |  | 5 | 8 | 8 | 8 | 8 | 8 |  |  |  |  | 11 | 11 | 11 | 11 | 165000
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 22 | 22 | 22 | 22 | 22 | 33 | 44 | 49 | 47 | 46 | 50 | 51 | 50 |  | 53 | 52 | 53 | 53 | 53 | 53 | 53 | 1062600
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 559752
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 280 | 280 | 285 | 295 | 290 | 285 | 295 | 300 | 300 | 290 | 310 | 310 | 290 | 290 | 270 | 285 | 260 |  | 270 | 295 | 280 | 280 | 290 | 290 | 290 | 7092250
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 17 | 17 | 17 | 17 | 17 | 17 | 45 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 17 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1024714
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 492240
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 465660
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 378396
63 | Impoprt (Tripura) | 132 | 128 | 122 | 118 | 114 | 110 | 106 | 102 | 112 | 118 | 122 | 128 | 126 | 134 | 132 | 128 | 120 | 148 |  | 154 | 154 | 146 | 148 | 150 | 150 | 142 | 3105600
64 | Malancha, Ctg. EPZ (United) | 31 | 42 | 42 | 42 | 42 | 42 | 21 | 6 | 8 | 2 | 3 | 4 | 10 | 5 | 3 | 5 | 6 | 10 |  | 14 | 16 | 20 | 25 | 34 | 35 | 40 | 485760
65 | Feni 22MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 426996
66 | Feni 11 MW PP (Doreen) | [13 empty] | 5 | 5 | 5 | 5 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 69660
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 809900
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 10 | 15 | 15 | 15 | 21 | 21 | 21 | 396910
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 22 | 28 | 21 | 28 | 28 | 28 | 28 | 645120
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 809400
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 825000
73 | Ghorashal 108MW PP (Regent) | 87 | 87 | 87 | 88 | 88 | 88 | 88 | 88 | 88 | 85 | 90 | 86 | 90 | 91 | 88 | 88 | 88 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1794000
| Feni Lanka Power | [16 empty] | 50 | 50 |  | 101 | 101 | 101 | 70 | 34 |  |  | 408120
| Chowmuhani 113 MW | 113 | 111 | 98 | 75 | 55 | 55 | 55 | 55 | 55 | 79 | 94 | 111 | 107 | 102 | 104 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2325120
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 100 | 100 | 60 | 40 | 40 | 40 | 40 | 65 | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2119680
78 | Gazipur 52 MW PP | [17 empty] | 23 |  | 43 | 25 | 25 |  |  |  |  | 104544
79 | Kodda 150MW PP | [16 empty] | 10 | 80 |  | 150 | 115 | 115 | 98 | 82 | 48 | 16 | 624000
80 | Jamalpur 95 MW PP(Powerpac) | [26 empty] | 0
81 | Jangalia 52 MW PP (Lakdanavi) | [16 empty] | 1 | 36 |  | 43 | 43 | 43 | 43 | 43 |  |  | 234754
| Gazipur 100 MW PP | [8 empty] | 50 | 51 | 51 | 34 | 34 | 34 | 70 | 51 | 51 | 70 |  | 86 | 86 | 86 | 87 | 70 |  |  | 853608
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 4 | 4 | 3 | 5 | 2 | 0 | 1 | 2 | 0 | [9 empty] | 24324
| Jodiac Power | 54 | 54 | 54 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 52 | 54 | 54 | 54 | 17 | 17 | 19 |  | 52 | 54 | 54 | 54 | 54 | 54 | 54 | 1061240
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | 97 | 97 | 48 | 48 | 48 | 48 | 48 | 48 | 74 | 97 | 48 | 48 | 60 | 87 | 97 | 97 | 97 | 97 |  | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 1920384
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [16 empty] | 5 | 50 |  | 79 | 50 | 65 | 28 |  |  |  | 242109
86 | Meghnaghat CCPP(Summit) | [10 empty] | 6 | 5 | 5 | 6 | 6 | 6 | 15 | 50 |  | 70 | 95 | 110 | 120 | 145 | 150 | 140 | 740684
87 | Meghnaghat 100 MW(IEL) | 100 | 100 | 100 | 74 | 53 | 41 | 41 | 42 | 82 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 95 | 93 | 93 | 93 | 93 | 93 | 92 | 2117760
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 85 | 70 | 70 | 70 | 72 | 103 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 2448960
88 | Ghorashal 78.5 MW PP(MAX) | 65 | 66 | 65 | 65 | 65 | 65 | 40 | 40 | 40 | 40 | 50 | 65 | 64 | 64 | 64 | [11 empty] | 890624
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44MW (Energyprima) | 47 | 47 | 47 | 47 | 47 | 20 | 20 | 20 | 20 | 20 | 30 | 41 | 44 | 44 | 47 | 47 | 47 | 47 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 1031544
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1259710
94 | Gagnagar 102 MW PP (Digital Power) | 7 | [6 empty] | 16 | 16 | 16 |  |  | 16 | 40 | 50 | 40 | 40 | 64 |  | 93 | 93 | 93 | 93 | 93 | 24 | 7 | 836208
95 | Patenga 50MW PP (Baraka) | [8 empty] | 2 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 16 |  | 48 | 50 | 50 | 50 | 19 | 19 |  | 317760
96 | Chattogram 108 MW PP (ECPV) | [8 empty] | 10 | 13 |  |  |  |  | 4 | 11 | 11 | 63 |  | 90 | 90 | 90 | 90 | 90 | 91 | 91 | 666240
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | 15 | 15 | 15 | 15 | 15 | 14 | 14 | 15 | 25 | 40 | 40 | 40 | 40 | 40 | 40 | 15 | 15 | 29 |  | 40 | 40 | 40 | 40 | 40 | 30 | 15 | 711505
100 | Manikganj 55 MW PP (Northern) | 17 | [6 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 55 | 55 | 55 |  | 55 | 55 | 35 | 55 | 55 | 17 | 17 | 583265
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 163 | 110 | 110 | 110 | 110 | 130 | 163 | 163 | 163 | 163 | 130 | 110 | 110 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3616854
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 2 | 2 |  | 2 | 1 | 1 | 0 | 0 | [9 empty] | 9200
103 | Kamalaghat 54 MW PP(Banco Energy) | [14 empty] | 17 | 17 | 17 | 54 |  | 54 | 54 | 54 | 54 | 17 | 17 |  | 304560
104 | Keranigonj 300 MW PP (APR) | [26 empty] | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 193 | 200 | 193 | 160 | 140 | 140 | 140 | 140 | 140 | 168 | 185 | 185 | 185 | 185 | 185 | 194 | 194 | 195 |  | 186 | 186 | 186 | 185 | 195 | 189 | 183 | 4279200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 120 | 105 | 101 | 100 | 100 | 100 | 100 | 135 | 149 | 149 | 139 | 133 | 133 | 138 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3223728
115 | Juldah 100 MW PP Unit-3 (Acorn) | [7 empty] | 10 | 10 | 10 | 10 | 10 | 50 | 50 | 90 | 70 | 70 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1149120
116 | Chandpur 200MW (Desh energy)
117 | Ashuganj 150MW PP (Midland) | 100 | 50 | 50 | 20 | 20 | 20 | 20 | 20 | 40 | 95 | 50 | 50 | 65 | 93 | 105 | 50 | 55 | 85 |  | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 1722909
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 55 | 55 | 35 | [11 empty] | 14 | 16 | 16 | 19 |  | 90 | 115 | 115 | 115 | 115 | 105 | 105 | 904800
| Anwara 300 MW PP (United) | 102 | 34 | 15 | 15 | 15 | 15 | 15 | 16 | 16 | 16 | 16 | 72 | 100 | 104 | 139 | 140 | 140 | 140 |  | 141 | 141 | 140 | 141 | 141 | 141 | 142 | 1994727
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 70 | 50 | 50 | 30 | 30 | 30 | 80 | 100 | 100 | 100 | 100 | 100 | 40 | 40 | 90 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1935360
120 | Eastern Zone Total | 6164 | 5988 | 5843 | 5601 | 5493 | 5252 | 4977 | 5076 | 5385 | 5743 | 5953 | 6186 | 6200 | 6251 | 6445 | 6195 | 6063 | 6534 |  | 7384 | 7354 | 7326 | 7260 | 7118 | 6704 | 6468 | 149072819
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 16 | [15 empty] | 9 | 100 |  | 99 | 99 | 105 | 115 | 115 | 115 | 115 | 735360
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
| Khulna 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 170 |  | 230 | 230 | 230 | 230 | 230 | 230 | 210 | 3597120
129 | Rupsha 105 MW PP (Orion rupsha) | 70 | 70 | 53 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 53 | 53 | 53 | 17 | 17 | 70 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1224000
130
131
132
133
| Barisal 110 MW PP (Summit ) | [17 empty] | 48 |  | 48 | 32 | 32 | 32 | 32 | 16 |  | 206976
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 76 | 77 | 77 | 77 | 78 | 78 | 53 | 53 | 52 | 52 | 72 | 76 | 76 | 76 | 76 | 76 | 76 | 76 |  | 76 | 76 | 76 | 75 | 77 | 76 | 75 | 1730311
| Bhola 225 MW CCPP | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 1949072
140 | Bhola 33 MW PP (Venture) | 29 | 29 | 27 | 26 | 26 | 21 | 18 | 12 | 17 | 17 | 17 | 19 | 19 | 19 | 19 | 18 | 17 | 23 |  | 27 | 27 | 29 | 29 | 31 | 31 | 31 | 554108
141 | Noapara 100 MW PP (Bangla Trac) | [19 empty] | 70 | 100 | 100 | 100 | 100 | 100 | 0 | 546240
142 | Noapara 40 MW PP (Khanjahan Ali) | [13 empty] | 24 | 24 |  |  | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 282375
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 6 | [8 empty] | 4736
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 926 | 926 | 926 | 926 | 926 | 926 | 926 | 926 | 926 | 927 | 926 | 926 | 926 | 927 | 927 | 927 | 927 | 926 |  | 926 | 925 | 926 | 926 | 926 | 927 | 927 | 22216727
147 | Bheramara 410 MW CCPP | 340 | 340 | 340 | 360 | 360 | 360 | 385 | 360 | 360 | 360 | 335 | 320 | 300 | 285 | 340 | 340 | 340 | 310 |  | 355 | 350 | 345 | 345 | 350 | 350 | 345 | 8513280
148 | Payra 1320 MW | 560 | 520 | 480 | 480 | 480 | 450 | 450 | 440 | 450 | 450 | 450 | 470 | 500 | 500 | 480 | 470 | 450 | 430 |  | 570 | 590 | 622 | 622 | 622 | 622 | 580 | 12938800
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 151 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 3698000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP | 45 | 40 | 40 | [23 empty] | 136000
| Baghabari 50 MW Peaking PP | [17 empty] | 25 |  | 30 | 43 | 43 |  |  |  |  | 100342
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 183 | 183 | 183 | 184 | 175 | 155 | 144 | 150 | 161 | 167 | 181 | 198 | 199 | 184 | 186 | 158 | 163 | 140 |  | 199 | 188 | 174 | 153 | 153 | 155 | 155 | 4312091
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 185 | 186 | 185 | 187 | 181 | 165 | 154 | 161 | 165 | 160 | 168 | 203 | 190 | 175 | 176 | 162 | 163 | 135 |  | 190 | 192 | 184 | 168 | 161 | 181 | 195 | 4506864
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 399 | 347 | 353 | 358 | 358 | 360 | 372 | 375 | 376 | 412 | 412 | 393 | 405 | 410 | 405 | 380 | 300 | 270 |  | 375 | 345 | 389 | 358 | 371 | 414 | 426 | 9128900
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 22 | 22 | 22 | 21 | 489840
163 | Bogura 20 MW PP (Energyprima) | [26 empty] | 0
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 240732
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [16 empty] | 12 | 45 |  | 46 | 46 | 47 |  |  |  |  | 130719
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [17 empty] | 25 |  | 52 | 52 | 52 | 25 |  |  |  | 169440
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 36 |  | 97 | 98 | 98 | 98 | 68 | 68 | 40 | 490952
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [17 empty] | 54 |  | 94 | 113 | 113 | 113 | 70 | 70 | 35 | 634080
172 | Confidence Power Bogura Unit-1 113 MW | 70 | 70 | 35 | 35 |  |  |  | 20 | 35 | 70 | 35 | 70 | 109 | 109 | 109 | 109 | 109 | 109 |  | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 1706976
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 47 | 62 | 43 | 34 | [8 empty] | 33 | 36 | 68 | 93 | 76 | 79 |  | 101 | 105 | 106 | 105 | 105 | 105 | 100 | 1196160
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 20450
178
178