## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-09-30 | Wednesday
|  |  | Date (day): | 2020-09-30 |  | Wednesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13336.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14541 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-09-29 | 2020-09-30 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 200 | 200 | 220 | 220
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 115 | 115 | 115 | 75 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 200 | 200 |  | 365
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 43 | 42 | 42 | 42 | 66 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Dust in gas.
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 347 | 351 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 340 | 280 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 100 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 140 | 130 | 150 | 150 | 155 |  | GT-2 S/D for Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 95 | 97 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 40 | 40 |  | 15 | Engine problem
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 12 | 23 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 180 | 150 | 200 | 200 | 10 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 94 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 93 | 93 | 93 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 150 | 150 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 35 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 51 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 51 | 51 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 286 | 300 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 303 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 99 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 149 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 84 | 84 | 85 | 86 |  | 19 | Engine problem
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 2943 | 3259 | 3626 | 3917 | 648 | 1578
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 42 | 77 | 44 | 44 | 186 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 204 | 203 | 221 | 221
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 139 | 139 | 140 | 145
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 100 | 100
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 60 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 21 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 18 | 10 | 25
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 37 | 90 | 90 | 90 |  | 18 | Engine problem
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 176 | 162 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 1064 | 1321 | 1710 | 1705 | 426 | 116
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 80 | 80 | 80 |  | 54 | Engine problem
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 188 | 179 | 225 | 225 |  |  | FGMO
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 320 | 360 | 360 |  |  | FGMO
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 360 |  | 360
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 29 | 30 | 30 | 15 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 53 | 51 | 55 | 55
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 50 | 55 | 26 | 26 | 169 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 45 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 10 | 10 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 50 | 0 | 50
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 96 | 86 | 100 | 100 |  | 63 | ST under shut down
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 200 | 200 | 200
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 8 | 8 |  | 3 | Engine problem
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 130 | 156 | 162 | 173
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 43 | 52 | 52 |  | 0 | Engine problem
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 21 | 21 | 21 | 21
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 100 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 80 | 100 | 114 | 114
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 113 | 94 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1297 | 1678 | 1798 | 2419 | 448 | 484
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 152 | 155 | 160 | 160 | 42 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 17 | 17 |  | 5 | Engine problem
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 0 | 0 | 0 |  | 95 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 193 | 200 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 96 | 102 | 115 | 115
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 460 | 474 | 493.6 | 492 | 42 | 100
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 59 | 60 | 60 | 60
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 35 | Unit-4 under shut down
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 195 | 185 | 200 | 200 |  | 110 | ST Under maint.
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 53 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 44 | 44 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 5 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 63 | 63 | 65 | 65
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 88 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 16 | 25 | 25
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 285 | 341 | 341 |  |  | FGMO
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 5 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 981 | 1002 | 1104 | 1104 | 0 | 545
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 928 | 916 | 927 | 927
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 83 | 83 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 9 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 225 | 225 | 225
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 325 | 410 | 410 | 410
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 90 | 105 | 90 | 90 |  | 15 | Engine problem
| 108 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1546 | 1888 | 1957 | 2113 | 0 | 15
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 80 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 14 | 38 | 33 | 33
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 50 | 60 | 65 | 65 |  | 134 | GT-2 & STG under shut down
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 77 | 77 | 78 | 78 |  | 17 | Engine problem
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 470 | 622 | 620 | 620
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 627 | 877 | 906 | 906 | 0 | 151
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 41 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 44 | 43 | 43
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | ST Under maint & gas shoratge
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 181 | 196 | 200 | 200 |  |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 169 | 200 | 220 | 220 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 387 | 393 | 414 | 414 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 34
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 21 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 7 | 10 | 10 | 10
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 10 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 52 | 52 | 52
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 97 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 175 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 94 | 94 | 100 | 113
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 109 | 109 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 1031 | 1493 | 1484 | 1622 | 271 | 210
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 109 | 108 | 100 | 113
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 266 | 258 | 258 | 263 | 294 | 40
|  | Total |  |  |  |  | 20383 | 19892 | 10215 | 12250 | 13336.6 | 14541 | 2129 | 3239
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9855.5988 | 11819 | 12867.3694 | 14029.3942
| A. |  | 2020-09-29 | (Yesterday) |  |  |  |  | Tuesday
| 1 | Highest Generation : |  |  | 12250 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 8783 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12250 | MW
| 3 | Day peak Generation : |  |  | 10215 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11819 | MW
| 4 | Evening peak Generation : |  |  | 12250 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 253.641 | MKWHr | By Solar | 0.20405 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 125.4767 | MKWHr |  | By Oil: | 83.906 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 17.405 | MKWHr |  | By Hydro: | 1.0634 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2129 | MW | Dhaka | 4236 | 4236 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3239 | MW | Chittagong | 1239 | 1239 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5368 | MW | Khulna | 1479 | 1479 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1119.61 | MMCFD |  |  | Rajshahi | 1253 | 1253 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 149993003.466 | ii) Oil : | Taka | 695777151.24 | Comilla | 1156 | 1156 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 80209680 | Total | Taka | 925979834.706 | Mymensingh | 944 | 944 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 428 | 428 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 395 | MW (E to W) at | 19:00 | hrs | Barisal | 343 | 343 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 246 | MW at | 20:00 | hrs | Rangpur | 741 | 741 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 33.4° C |  |  | Total | 11819 | 11819 |  | 0
| B. |  | 2020-09-30 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 33.8° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14541 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10800 | MW
| 4 | Reserve(Generation end) |  |  |  | 1741 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 265.0289 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9241 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.1702 | MKWHr. | ii) HVDC Flow at Peak Time |  | 916 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.4157 | MKWHr. | iii) Maximum HVDC Flow : |  | 929 | MW at | 16:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 98.14 |  | (b) Today: | 98.46 |  | (c) Rule Curve: |  | 105.76
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-09-29
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 200 | 115 | 0 | 42 | 0 | 0 | 349 |  | 0 | 380 | 140 | 100 | 85 | 40 | 0 | 0 | 195 | 0 | 100 | 93 | 150 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 25 | 33 | 51 | 0 | 42 | 0 | 120 | 0 | 25 | 204 | 0 | 145 | 0 |  | 0 | 0 | 100 | 0 | 97 | 50 | 21 | 42 | 0 | 0 | 80 | 280 | 0 | 177 | 8 | 88 | 29 | 55 | 0 | 43 | 0 | 0 | 43 | 18 | 8 | 33 | 20 | 156 | 158 | 0 | 17 | 0 | 60 | 30 | 53 | 44 | 163 | 187 | 63 | 85 | 0 | 97 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 300 | 0 | 0 | 194 | 0 | 149 | 0 | 40 | 100 | 93 | 0 | 95 | 86 | 0 | 0 | 16 | 54 | 0 | 82 | 113 | 40 | 0 | 104 |  | 927 | 0 | 330 | 0 | 99 | 190 | 0 | 0 | 0 | 0 | 40 | 50 | 37 | 64 | 0 | 0 | 0 | 50 | 0 | 97 | 0 | 0 | 36 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 157 | 0 | 77 | 100 | 167 | 0 | 399 | 90 | 0 | 113 | 0 | 108 | 0 | 0 | 109 | 600 |  | 7018 | 4084 | 11102 | 3242 | 927 | 2108 | 3254 | 750 | 42 | 623 | 156 | 0 | 0 | 98.09
2:00 | 0 | 0 | 200 | 115 | 0 | 42 | 0 | 0 | 349 |  | 0 | 380 | 140 | 100 | 80 | 44 | 0 | 0 | 195 | 0 | 100 | 93 | 150 | 24 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 51 | 0 | 42 | 0 | 120 | 0 | 25 | 203 | 0 | 144 | 0 |  | 0 | 0 | 68 | 0 | 97 | 50 | 21 | 40 | 0 | 0 | 80 | 280 | 0 | 177 | 8 | 89 | 29 | 55 | 0 | 34 | 0 | 0 | 43 | 18 | 8 | 33 | 21 | 152 | 158 | 0 | 17 | 0 | 60 | 30 | 53 | 44 | 163 | 188 | 62 | 85 | 0 | 97 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 300 | 0 | 0 | 194 | 0 | 149 | 0 | 40 | 0 | 93 | 0 | 95 | 86 | 0 | 0 | 16 | 54 | 0 | 82 | 113 | 40 | 0 | 104 |  | 927 | 0 | 330 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 40 | 50 | 33 | 64 | 0 | 0 | 0 | 25 | 0 | 97 | 0 | 0 | 36 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 157 | 0 | 78 | 30 | 169 | 0 | 406 | 90 | 0 | 113 | 0 | 113 | 0 | 0 | 109 | 580 |  | 6878 | 3910 | 10788 | 3253 | 927 | 2101 | 3087 | 730 | 42 | 496 | 152 | 0 | 0 | 98.1
3:00 | 0 | 0 | 200 | 115 | 0 | 42 | 0 | 0 | 349 |  | 0 | 380 | 140 | 100 | 79 | 44 | 0 | 0 | 195 | 0 | 100 | 93 | 114 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 68 | 0 | 97 | 50 | 21 | 42 | 0 | 0 | 80 | 280 | 0 | 177 | 8 | 89 | 29 | 55 | 0 | 34 | 0 | 0 | 43 | 18 | 8 | 33 | 21 | 148 | 158 | 0 | 17 | 0 | 60 | 30 | 53 | 44 | 163 | 186 | 62 | 85 | 0 | 97 | 18 | 0 | 10 | 285 | 24 | 8 | 0 | 300 | 0 | 0 | 194 | 0 | 149 | 0 | 40 | 0 | 93 | 0 | 95 | 86 | 0 | 0 | 16 | 54 | 0 | 82 | 113 | 40 | 0 | 104 |  | 926 | 0 | 330 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 24 | 50 | 30 | 64 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 77 | 0 | 169 | 0 | 403 | 90 | 0 | 113 | 0 | 113 | 0 | 0 | 109 | 580 |  | 6727 | 3796 | 10523 | 3247 | 926 | 2091 | 2940 | 730 | 42 | 399 | 148 | 0 | 0 | 98.11
4:00 | 0 | 0 | 200 | 115 | 0 | 42 | 0 | 0 | 350 |  | 0 | 380 | 140 | 100 | 80 | 45 | 0 | 0 | 195 | 0 | 100 | 93 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 34 | 0 | 97 | 47 | 21 | 42 | 0 | 0 | 80 | 280 | 0 | 177 | 8 | 88 | 29 | 55 | 0 | 40 | 0 | 0 | 43 | 13 | 8 | 33 | 21 | 146 | 158 | 0 | 17 | 0 | 60 | 30 | 53 | 44 | 163 | 184 | 62 | 85 | 0 | 97 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 300 | 0 | 0 | 194 | 0 | 149 | 0 | 40 | 0 | 93 | 0 | 95 | 86 | 0 | 0 | 16 | 54 | 0 | 36 | 113 | 40 | 0 | 104 |  | 928 | 0 | 330 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 0 | 50 | 30 | 64 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 76 | 0 | 169 | 0 | 406 | 90 | 0 | 113 | 0 | 113 | 0 | 0 | 109 | 580 |  | 6583 | 3724 | 10307 | 3240 | 928 | 2105 | 2817 | 730 | 42 | 299 | 146 | 0 | 0 | 98.12
5:00 | 0 | 0 | 200 | 115 | 0 | 42 | 0 | 0 | 349 |  | 0 | 380 | 140 | 100 | 80 | 52 | 0 | 0 | 195 | 0 | 100 | 93 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 34 | 0 | 97 | 35 | 21 | 42 | 0 | 0 | 80 | 280 | 0 | 177 | 8 | 89 | 29 | 55 | 0 | 51 | 0 | 0 | 43 | 13 | 8 | 33 | 21 | 138 | 158 | 0 | 17 | 0 | 60 | 30 | 53 | 44 | 163 | 184 | 62 | 85 | 0 | 97 | 18 | 0 | 9 | 280 | 24 | 8 | 0 | 300 | 0 | 0 | 194 | 0 | 149 | 0 | 40 | 0 | 93 | 0 | 95 | 50 | 0 | 0 | 16 | 54 | 0 | 17 | 113 | 40 | 0 | 104 |  | 927 | 0 | 335 | 0 | 83 | 120 | 0 | 0 | 0 | 0 | 0 | 50 | 30 | 48 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 157 | 0 | 77 | 0 | 166 | 0 | 405 | 90 | 0 | 50 | 0 | 113 | 0 | 0 | 109 | 580 |  | 6483 | 3596 | 10079 | 3239 | 927 | 2104 | 2662 | 730 | 42 | 237 | 138 | 0 | 0 | 98.13
6:00 | 0 | 0 | 200 | 115 | 0 | 42 | 0 | 0 | 348 |  | 0 | 340 | 120 | 100 | 80 | 15 | 0 | 0 | 190 | 0 | 100 | 93 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 22 | 25 | 28 | 33 | 16 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 64 | 19 | 21 | 42 | 0 | 0 | 80 | 280 | 0 | 177 | 8 | 86 | 29 | 55 | 0 | 51 | 0 | 0 | 25 | 18 | 8 | 33 | 21 | 134 | 160 | 0 | 17 | 0 | 60 | 30 | 53 | 44 | 163 | 184 | 62 | 85 | 0 | 97 | 18 | 0 | 9 | 270 | 24 | 8 | 0 | 230 | 0 | 0 | 200 | 0 | 143 | 0 | 40 | 0 | 93 | 0 | 35 | 16 | 0 | 0 | 16 | 54 | 0 | 0 | 109 | 40 | 0 | 104 |  | 927 | 0 | 340 | 0 | 49 | 120 | 0 | 0 | 0 | 0 | 0 | 50 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 76 | 0 | 163 | 0 | 365 | 90 | 0 | 35 | 0 | 113 | 0 | 0 | 50 | 550 |  | 6010 | 3316 | 9326 | 3224 | 927 | 2007 | 2156 | 700 | 42 | 136 | 134 | 0 | 0 | 98.14
7:00 | 0 | 0 | 200 | 115 | 0 | 42 | 0 | 0 | 353 |  | 0 | 340 | 125 | 100 | 80 | 15 | 0 | 0 | 160 | 0 | 92 | 93 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 203 | 0 | 103 | 0 |  | 0 | 0 | 0 | 0 | 32 | 19 | 21 | 31 | 0 | 0 | 80 | 280 | 0 | 177 | 8 | 85 | 29 | 55 | 0 | 43 | 0 | 0 | 25 | 18 | 8 | 33 | 21 | 122 | 159 | 0 | 17 | 0 | 60 | 30 | 53 | 44 | 110 | 184 | 62 | 85 | 0 | 97 | 18 | 0 | 9 | 260 | 24 | 8 | 0 | 145 | 0 | 0 | 200 | 0 | 27 | 4 | 20 | 0 | 93 | 0 | 8 | 4 | 0 | 0 | 16 | 54 | 0 | 0 | 105 | 40 | 0 | 104 |  | 927 | 0 | 360 | 0 | 32 | 120 | 0 | 0 | 0 | 0 | 0 | 50 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 157 | 0 | 77 | 0 | 160 | 0 | 316 | 90 | 0 | 35 | 0 | 55 | 0 | 2 | 50 | 520 |  | 5606 | 3177 | 8783 | 3188 | 927 | 1878 | 1782 | 670 | 42 | 168 | 122 | 6 | 0 | 98.15
8:00 | 0 | 0 | 200 | 115 | 0 | 42 | 0 | 0 | 348 |  | 0 | 340 | 138 | 93 | 80 | 30 | 0 | 0 | 120 | 0 | 96 | 93 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 0 | 25 | 28 | 25 | 33 | 0 | 0 | 43 | 0 | 120 | 0 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 31 | 19 | 21 | 7 | 0 | 0 | 80 | 280 | 0 | 176 | 8 | 90 | 29 | 55 | 0 | 45 | 0 | 0 | 25 | 18 | 5 | 33 | 21 | 124 | 156 | 0 | 17 | 1 | 60 | 30 | 53 | 44 | 110 | 202 | 62 | 85 | 0 | 97 | 18 | 0 | 9 | 280 | 24 | 8 | 0 | 145 | 0 | 0 | 200 | 0 | 79 | 6 | 20 | 0 | 93 | 0 | 8 | 50 | 0 | 0 | 16 | 54 | 0 | 0 | 113 | 40 | 0 | 104 |  | 927 | 0 | 355 | 0 | 32 | 120 | 0 | 0 | 0 | 0 | 0 | 50 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 161 | 0 | 77 | 0 | 160 | 0 | 337 | 90 | 0 | 35 | 0 | 52 | 0 | 4 | 50 | 470 |  | 5682 | 3140 | 8822 | 3134 | 927 | 1886 | 1909 | 620 | 43 | 168 | 124 | 11 | 0 | 98.16
9:00 | 0 | 0 | 200 | 115 | 0 | 43 | 0 | 0 | 348 |  | 0 | 340 | 140 | 90 | 80 | 32 | 0 | 0 | 120 | 0 | 100 | 93 | 48 | 6 | 0 | 0 | 0 | 40 | 55 | 55 | 0 | 25 | 25 | 25 | 33 | 0 | 0 | 44 | 0 | 120 | 0 | 0 | 204 | 0 | 103 | 0 |  | 0 | 0 | 0 | 0 | 31 | 19 | 21 | 5 | 0 | 0 | 80 | 295 | 0 | 180 | 8 | 95 | 26 | 55 | 0 | 51 | 0 | 0 | 31 | 18 | 5 | 33 | 21 | 122 | 157 | 0 | 17 | 2 | 60 | 30 | 50 | 44 | 163 | 191 | 62 | 85 | 0 | 30 | 18 | 0 | 9 | 300 | 24 | 0 | 0 | 154 | 0 | 0 | 193 | 0 | 144 | 11 | 20 | 0 | 93 | 0 | 32 | 70 | 0 | 2 | 16 | 54 | 0 | 80 | 108 | 100 | 0 | 104 |  | 928 | 0 | 350 | 0 | 43 | 120 | 0 | 0 | 0 | 0 | 0 | 50 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 20 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 170 | 0 | 77 | 0 | 176 | 0 | 418 | 90 | 0 | 50 | 0 | 61 | 0 | 3 | 90 | 460 |  | 6003 | 3318 | 9321 | 3087 | 928 | 2036 | 2308 | 610 | 44 | 168 | 122 | 18 | 0 | 98.17
10:00 | 0 | 0 | 200 | 115 | 0 | 43 | 0 | 0 | 349 |  | 0 | 340 | 135 | 100 | 85 | 55 | 0 | 0 | 120 | 0 | 100 | 93 | 80 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 45 | 0 | 44 | 0 | 120 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 32 | 19 | 18 | 5 | 0 | 0 | 80 | 295 | 0 | 180 | 50 | 85 | 26 | 55 | 0 | 51 | 0 | 0 | 43 | 18 | 5 | 33 | 21 | 124 | 154 | 0 | 17 | 1 | 60 | 30 | 46 | 44 | 163 | 185 | 62 | 85 | 0 | 0 | 0 | 0 | 9 | 285 | 24 | 0 | 0 | 260 | 0 | 0 | 193 | 0 | 149 | 13 | 60 | 0 | 93 | 0 | 75 | 84 | 0 | 5 | 115 | 54 | 0 | 80 | 109 | 100 | 0 | 104 |  | 928 | 0 | 335 | 0 | 83 | 120 | 0 | 0 | 0 | 0 | 0 | 50 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 20 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 155 | 0 | 77 | 0 | 161 | 0 | 403 | 90 | 0 | 90 | 0 | 112 | 0 | 3 | 109 | 470 |  | 6475 | 3412 | 9887 | 3036 | 928 | 2045 | 2868 | 620 | 44 | 200 | 124 | 22 | 0 | 98.19
11:00 | 0 | 0 | 200 | 115 | 0 | 43 | 0 | 0 | 348 |  | 0 | 340 | 135 | 100 | 95 | 55 | 0 | 0 | 180 | 0 | 100 | 93 | 133 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 51 | 0 | 44 | 0 | 120 | 0 | 14 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 32 | 19 | 18 | 5 | 0 | 0 | 80 | 295 | 0 | 179 | 50 | 88 | 29 | 55 | 0 | 43 | 0 | 0 | 43 | 18 | 5 | 33 | 21 | 132 | 153 | 0 | 17 | 2 | 60 | 30 | 47 | 44 | 110 | 191 | 63 | 85 | 0 | 0 | 0 | 0 | 9 | 280 | 24 | 0 | 0 | 275 | 0 | 0 | 183 | 0 | 136 | 20 | 70 | 0 | 10 | 0 | 75 | 84 | 0 | 3 | 167 | 54 | 0 | 80 | 113 | 100 | 10 | 104 |  | 928 | 0 | 330 | 0 | 83 | 120 | 0 | 0 | 0 | 0 | 0 | 50 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 17 | 7 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 156 | 0 | 78 | 0 | 160 | 0 | 359 | 90 | 0 | 94 | 0 | 113 | 0 | 4 | 109 | 465 |  | 6570 | 3386 | 9956 | 3120 | 928 | 1930 | 2905 | 615 | 44 | 253 | 132 | 29 | 0 | 98.21
12:00 | 0 | 0 | 200 | 115 | 0 | 43 | 0 | 0 | 347 |  | 0 | 340 | 140 | 100 | 95 | 55 | 0 | 0 | 180 | 0 | 94 | 93 | 150 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 51 | 0 | 42 | 0 | 120 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 37 | 19 | 21 | 4 | 0 | 0 | 80 | 305 | 0 | 188 | 50 | 96 | 29 | 53 | 0 | 43 | 0 | 0 | 43 | 18 | 5 | 33 | 21 | 130 | 152 | 0 | 17 | 2 | 59 | 30 | 47 | 44 | 130 | 195 | 63 | 85 | 0 | 0 | 0 | 0 | 9 | 290 | 24 | 0 | 0 | 286 | 0 | 0 | 193 | 0 | 149 | 18 | 100 | 0 | 10 | 0 | 96 | 84 | 0 | 5 | 176 | 54 | 0 | 80 | 113 | 100 | 5 | 104 |  | 928 | 0 | 325 | 0 | 83 | 120 | 0 | 0 | 0 | 0 | 0 | 50 | 14 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 7 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 181 | 0 | 77 | 0 | 169 | 0 | 387 | 90 | 0 | 94 | 0 | 109 | 0 | 7 | 109 | 470 |  | 6745 | 3470 | 10215 | 3176 | 928 | 1991 | 3026 | 620 | 42 | 270 | 130 | 32 | 0 | 98.23
13:00 | 0 | 0 | 200 | 115 | 0 | 43 | 0 | 0 | 346 |  | 0 | 260 | 130 | 100 | 97 | 55 | 0 | 0 | 175 | 0 | 92 | 93 | 150 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 51 | 0 | 42 | 0 | 120 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 50 | 30 | 21 | 9 | 0 | 0 | 80 | 320 | 0 | 180 | 50 | 85 | 29 | 52 | 0 | 51 | 0 | 0 | 43 | 18 | 5 | 33 | 21 | 138 | 149 | 0 | 17 | 1 | 59 | 30 | 50 | 44 | 163 | 192 | 63 | 84 | 0 | 0 | 0 | 0 | 9 | 295 | 24 | 0 | 0 | 286 | 0 | 0 | 192 | 0 | 149 | 19 | 100 | 0 | 10 | 0 | 105 | 84 | 0 | 5 | 180 | 54 | 0 | 80 | 101 | 100 | 100 | 104 |  | 928 | 0 | 305 | 0 | 83 | 120 | 0 | 0 | 0 | 0 | 0 | 50 | 16 | 32 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 7 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 196 | 0 | 77 | 0 | 188 | 0 | 409 | 90 | 0 | 94 | 0 | 113 | 0 | 4 | 109 | 490 |  | 6818 | 3557 | 10375 | 3270 | 928 | 1986 | 3060 | 640 | 42 | 282 | 138 | 29 | 10375 | 98.25
14:00 | 0 | 0 | 200 | 115 | 0 | 43 | 0 | 0 | 344 |  | 0 | 210 | 150 | 100 | 97 | 55 | 0 | 0 | 120 | 0 | 99 | 93 | 150 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 51 | 0 | 40 | 0 | 120 | 0 | 25 | 206 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 50 | 46 | 21 | 4 | 0 | 0 | 80 | 335 | 0 | 193 | 50 | 96 | 29 | 50 | 0 | 51 | 0 | 0 | 43 | 18 | 8 | 33 | 21 | 146 | 150 | 0 | 17 | 1 | 59 | 30 | 53 | 44 | 163 | 203 | 62 | 85 | 0 | 0 | 0 | 0 | 9 | 290 | 24 | 0 | 0 | 286 | 0 | 0 | 192 | 0 | 149 | 20 | 100 | 0 | 10 | 0 | 105 | 84 | 0 | 4 | 180 | 54 | 0 | 80 | 96 | 100 | 95 | 104 |  | 928 | 0 | 305 | 0 | 83 | 120 | 0 | 0 | 0 | 0 | 8 | 50 | 18 | 32 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 7 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 196 | 0 | 77 | 0 | 174 | 0 | 374 | 90 | 0 | 94 | 0 | 111 | 0 | 4 | 109 | 510 |  | 6797 | 3541 | 10338 | 3251 | 928 | 1893 | 3104 | 660 | 40 | 287 | 146 | 29 | 0 | 98.27
15:00 | 0 | 0 | 200 | 115 | 0 | 43 | 0 | 0 | 346 |  | 0 | 210 | 145 | 100 | 97 | 55 | 0 | 0 | 190 | 0 | 100 | 93 | 150 | 13 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 51 | 0 | 40 | 0 | 120 | 0 | 25 | 204 | 0 | 138 | 0 |  | 0 | 0 | 0 | 40 | 66 | 48 | 21 | 5 | 0 | 0 | 80 | 320 | 0 | 187 | 50 | 93 | 29 | 49 | 0 | 51 | 0 | 0 | 43 | 18 | 8 | 33 | 21 | 146 | 149 | 0 | 17 | 1 | 58 | 30 | 50 | 44 | 163 | 190 | 62 | 85 | 0 | 0 | 0 | 0 | 9 | 315 | 24 | 0 | 0 | 300 | 0 | 0 | 192 | 0 | 149 | 15 | 100 | 27 | 10 | 0 | 95 | 84 | 0 | 3 | 162 | 54 | 0 | 82 | 97 | 100 | 110 | 104 |  | 928 | 0 | 295 | 0 | 83 | 120 | 0 | 0 | 0 | 0 | 40 | 50 | 22 | 32 | 0 | 0 | 0 | 25 | 0 | 3 | 0 | 0 | 0 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 179 | 0 | 77 | 0 | 183 | 0 | 408 | 90 | 0 | 94 | 0 | 112 | 0 | 5 | 109 | 520 |  | 6929 | 3619 | 10548 | 3276 | 928 | 1958 | 3208 | 670 | 40 | 298 | 146 | 24 | 0 | 98.29
16:00 | 0 | 0 | 200 | 115 | 0 | 43 | 0 | 0 | 305 |  | 0 | 210 | 140 | 100 | 97 | 40 | 0 | 0 | 193 | 0 | 100 | 93 | 115 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 8 | 0 | 40 | 0 | 120 | 0 | 8 | 204 | 0 | 140 | 0 |  | 0 | 0 | 0 | 10 | 81 | 50 | 21 | 5 | 0 | 0 | 80 | 320 | 0 | 180 | 55 | 88 | 29 | 51 | 0 | 51 | 0 | 0 | 43 | 18 | 8 | 33 | 21 | 124 | 149 | 0 | 17 | 0 | 59 | 30 | 51 | 44 | 163 | 191 | 62 | 83 | 0 | 0 | 0 | 0 | 10 | 275 | 24 | 0 | 0 | 300 | 0 | 0 | 192 | 0 | 149 | 2 | 100 | 100 | 10 | 0 | 95 | 84 | 0 | 1 | 162 | 54 | 0 | 82 | 84 | 100 | 18 | 104 |  | 929 | 0 | 395 | 0 | 83 | 120 | 0 | 0 | 0 | 0 | 8 | 60 | 21 | 32 | 0 | 0 | 0 | 25 | 0 | 48 | 0 | 0 | 0 | 25 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 169 | 0 | 77 | 0 | 185 | 0 | 400 | 105 | 0 | 94 | 0 | 113 | 0 | 3 | 109 | 520 |  | 6651 | 3713 | 10364 | 3281 | 929 | 1875 | 3131 | 670 | 40 | 308 | 124 | 6 | 0 | 98.31
17:00 | 0 | 0 | 150 | 115 | 0 | 43 | 0 | 0 | 304 |  | 0 | 210 | 130 | 100 | 97 | 48 | 0 | 0 | 120 | 0 | 100 | 93 | 100 | 12 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 28 | 33 | 33 | 8 | 0 | 41 | 0 | 120 | 0 | 8 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 10 | 89 | 27 | 21 | 12 | 0 | 0 | 80 | 320 | 0 | 179 | 55 | 86 | 29 | 49 | 0 | 10 | 0 | 0 | 43 | 18 | 8 | 33 | 21 | 116 | 153 | 0 | 17 | 0 | 60 | 30 | 53 | 44 | 163 | 190 | 40 | 20 | 0 | 0 | 0 | 0 | 10 | 300 | 16 | 0 | 0 | 300 | 0 | 0 | 192 | 0 | 149 | 1 | 100 | 50 | 10 | 0 | 95 | 84 | 0 | 0 | 162 | 54 | 0 | 52 | 93 | 100 | 0 | 104 |  | 921 | 0 | 405 | 0 | 83 | 120 | 0 | 0 | 4 | 0 | 8 | 58 | 20 | 32 | 0 | 0 | 0 | 25 | 10 | 40 | 0 | 0 | 5 | 25 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 76 | 0 | 159 | 0 | 317 | 105 | 0 | 94 | 0 | 113 | 0 | 1 | 109 | 490 |  | 6275 | 3564 | 9839 | 3075 | 921 | 1717 | 3023 | 640 | 41 | 304 | 116 | 2 | 0 | 98.33
18:00 | 0 | 0 | 200 | 115 | 0 | 42 | 0 | 0 | 277 |  | 0 | 220 | 145 | 100 | 97 | 55 | 0 | 0 | 77 | 0 | 100 | 93 | 150 | 12 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 21 | 33 | 33 | 31 | 0 | 42 | 0 | 120 | 0 | 17 | 207 | 0 | 139 | 0 |  | 0 | 0 | 102 | 40 | 90 | 32 | 21 | 12 | 0 | 0 | 80 | 330 | 0 | 192 | 55 | 94 | 29 | 49 | 0 | 10 | 0 | 50 | 43 | 18 | 8 | 33 | 21 | 150 | 155 | 0 | 17 | 0 | 58 | 30 | 53 | 44 | 130 | 192 | 63 | 20 | 0 | 0 | 0 | 0 | 10 | 290 | 16 | 2 | 43 | 300 | 111 | 52 | 200 | 0 | 149 | 0 | 100 | 95 | 10 | 0 | 95 | 84 | 0 | 0 | 162 | 54 | 0 | 100 | 93 | 100 | 0 | 104 |  | 916 | 0 | 300 | 0 | 83 | 155 | 0 | 0 | 6 | 0 | 40 | 60 | 38 | 56 | 0 | 0 | 0 | 50 | 38 | 80 | 0 | 0 | 43 | 38 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 138 | 0 | 77 | 10 | 167 | 0 | 403 | 105 | 100 | 94 | 0 | 112 | 0 | 0 | 109 | 460 |  | 6908 | 3870 | 10778 | 3027 | 916 | 1761 | 3598 | 610 | 42 | 674 | 150 | 0 | 0 | 98.35
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 200 | 115 | 0 | 42 | 0 | 0 | 351 |  | 0 | 280 | 130 | 100 | 97 | 55 | 0 | 0 | 150 | 0 | 100 | 93 | 150 | 23 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 26 | 33 | 33 | 51 | 0 | 42 | 35 | 120 | 0 | 25 | 203 | 0 | 139 | 0 |  | 0 | 0 | 102 | 60 | 90 | 50 | 21 | 18 | 0 | 0 | 80 | 320 | 0 | 179 | 55 | 86 | 29 | 51 | 0 | 45 | 0 | 50 | 43 | 18 | 8 | 33 | 21 | 156 | 155 | 0 | 17 | 0 | 60 | 30 | 53 | 44 | 163 | 185 | 63 | 88 | 0 | 0 | 0 | 0 | 10 | 285 | 16 | 5 | 100 | 300 | 303 | 99 | 200 | 0 | 149 | 0 | 100 | 200 | 10 | 0 | 102 | 84 | 0 | 0 | 162 | 54 | 0 | 100 | 94 | 100 | 0 | 104 |  | 916 | 0 | 410 | 0 | 83 | 225 | 0 | 0 | 9 | 0 | 40 | 60 | 38 | 80 | 0 | 0 | 0 | 50 | 41 | 97 | 0 | 0 | 44 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 196 | 0 | 77 | 100 | 200 | 0 | 393 | 105 | 175 | 94 | 0 | 108 | 0 | 0 | 109 | 622 |  | 7734 | 4516 | 12250 | 3269 | 916 | 2024 | 4268 | 772 | 77 | 768 | 156 | 0 | 0 | 98.37
19:30 | 0 | 0 | 200 | 115 | 0 | 42 | 0 | 0 | 352 |  | 0 | 420 | 135 | 100 | 97 | 55 | 0 | 0 | 150 | 0 | 100 | 93 | 150 | 100 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 26 | 33 | 33 | 51 | 0 | 43 | 35 | 120 | 0 | 25 | 204 | 0 | 140 | 0 |  | 0 | 0 | 102 | 40 | 90 | 50 | 21 | 22 | 0 | 0 | 80 | 320 | 0 | 178 | 55 | 96 | 29 | 55 | 0 | 51 | 0 | 50 | 43 | 18 | 8 | 33 | 21 | 154 | 155 | 0 | 17 | 0 | 60 | 30 | 53 | 44 | 163 | 185 | 63 | 88 | 0 | 0 | 0 | 0 | 10 | 290 | 24 | 11 | 100 | 300 | 101 | 99 | 200 | 0 | 149 | 0 | 100 | 200 | 10 | 0 | 115 | 84 | 0 | 0 | 162 | 54 | 0 | 100 | 103 | 100 | 0 | 104 |  | 916 | 0 | 410 | 0 | 83 | 225 | 0 | 0 | 14 | 0 | 40 | 59 | 38 | 80 | 0 | 0 | 0 | 50 | 41 | 97 | 0 | 0 | 45 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 183 | 0 | 77 | 100 | 187 | 0 | 402 | 105 | 50 | 94 | 0 | 112 | 0 | 0 | 109 | 622 |  | 7800 | 4383 | 12183 | 3267 | 916 | 2193 | 4029 | 772 | 78 | 774 | 154 | 0 | 0 | 0
20:00 | 0 | 0 | 200 | 115 | 0 | 43 | 0 | 0 | 350 |  | 0 | 420 | 135 | 100 | 97 | 55 | 0 | 0 | 160 | 0 | 100 | 93 | 150 | 97 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 28 | 33 | 33 | 51 | 0 | 43 | 35 | 120 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 102 | 40 | 96 | 50 | 21 | 18 | 0 | 0 | 80 | 320 | 0 | 179 | 55 | 92 | 29 | 54 | 0 | 51 | 0 | 50 | 45 | 18 | 8 | 33 | 21 | 152 | 153 | 0 | 17 | 0 | 60 | 30 | 53 | 44 | 163 | 190 | 63 | 88 | 0 | 0 | 0 | 0 | 10 | 280 | 24 | 11 | 88 | 300 | 105 | 99 | 200 | 0 | 149 | 0 | 100 | 200 | 10 | 0 | 115 | 84 | 0 | 0 | 162 | 54 | 0 | 100 | 96 | 100 | 0 | 104 |  | 916 | 0 | 410 | 0 | 83 | 225 | 0 | 0 | 18 | 0 | 40 | 60 | 38 | 80 | 0 | 0 | 0 | 50 | 41 | 97 | 0 | 0 | 47 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 184 | 0 | 77 | 100 | 187 | 0 | 406 | 105 | 50 | 94 | 0 | 112 | 0 | 0 | 109 | 622 |  | 7783 | 4395 | 12178 | 3280 | 916 | 2181 | 4019 | 772 | 78 | 780 | 152 | 0 | 0 | 98.39
21:00 | 0 | 0 | 200 | 115 | 0 | 43 | 0 | 0 | 351 |  | 0 | 420 | 145 | 100 | 97 | 55 | 0 | 0 | 155 | 0 | 100 | 93 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 51 | 0 | 43 | 35 | 120 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 102 | 40 | 97 | 50 | 21 | 23 | 0 | 0 | 80 | 325 | 0 | 191 | 55 | 94 | 29 | 54 | 0 | 51 | 0 | 50 | 52 | 18 | 8 | 33 | 21 | 152 | 154 | 0 | 17 | 0 | 60 | 30 | 17 | 44 | 163 | 197 | 63 | 88 | 0 | 0 | 0 | 0 | 10 | 285 | 24 | 11 | 81 | 300 | 55 | 50 | 200 | 0 | 149 | 0 | 100 | 200 | 10 | 0 | 115 | 84 | 0 | 0 | 162 | 54 | 0 | 100 | 94 | 100 | 0 | 104 |  | 915 | 0 | 410 | 0 | 83 | 225 | 0 | 0 | 21 | 0 | 40 | 60 | 38 | 80 | 0 | 0 | 0 | 50 | 41 | 97 | 0 | 0 | 43 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 189 | 0 | 78 | 100 | 192 | 0 | 412 | 105 | 0 | 94 | 0 | 112 | 0 | 0 | 109 | 622 |  | 7713 | 4360 | 12073 | 3312 | 915 | 2163 | 3902 | 772 | 78 | 779 | 152 | 0 | 0 | 98.4
22:00 | 0 | 0 | 200 | 115 | 0 | 43 | 0 | 0 | 351 |  | 0 | 420 | 145 | 100 | 97 | 55 | 0 | 0 | 196 | 0 | 100 | 93 | 150 | 20 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 51 | 0 | 43 | 0 | 120 | 0 | 25 | 204 | 0 | 140 | 0 |  | 0 | 0 | 102 | 20 | 97 | 50 | 21 | 30 | 0 | 0 | 80 | 310 | 0 | 182 | 26 | 94 | 29 | 54 | 0 | 51 | 0 | 50 | 52 | 18 | 8 | 33 | 21 | 152 | 154 | 0 | 17 | 0 | 60 | 30 | 0 | 44 | 163 | 190 | 63 | 88 | 0 | 0 | 0 | 0 | 10 | 300 | 24 | 11 | 78 | 300 | 108 | 50 | 200 | 0 | 149 | 0 | 100 | 200 | 15 | 0 | 115 | 84 | 0 | 0 | 162 | 54 | 0 | 100 | 102 | 100 | 0 | 104 |  | 915 | 0 | 410 | 0 | 85 | 225 | 0 | 0 | 20 | 0 | 40 | 60 | 38 | 80 | 0 | 0 | 0 | 50 | 41 | 97 | 0 | 0 | 43 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 199 | 0 | 79 | 100 | 201 | 0 | 400 | 105 | 0 | 94 | 0 | 112 | 0 | 0 | 109 | 622 |  | 7628 | 4369 | 11997 | 3342 | 915 | 2128 | 3867 | 772 | 43 | 778 | 152 | 0 | 0 | 98.41
23:00 | 0 | 0 | 200 | 115 | 0 | 43 | 0 | 0 | 351 |  | 0 | 420 | 145 | 100 | 97 | 45 | 0 | 0 | 195 | 0 | 100 | 93 | 150 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 51 | 0 | 43 | 0 | 120 | 0 | 25 | 205 | 0 | 139 | 0 |  | 0 | 0 | 102 | 20 | 97 | 50 | 21 | 33 | 0 | 0 | 80 | 325 | 0 | 194 | 26 | 94 | 26 | 54 | 0 | 51 | 0 | 50 | 52 | 18 | 5 | 33 | 21 | 162 | 154 | 0 | 17 | 0 | 60 | 30 | 0 | 44 | 163 | 200 | 65 | 88 | 0 | 0 | 0 | 0 | 10 | 285 | 24 | 11 | 20 | 300 | 23 | 50 | 200 | 0 | 149 | 0 | 100 | 200 | 30 | 0 | 115 | 84 | 0 | 0 | 162 | 54 | 0 | 100 | 103 | 100 | 0 | 104 |  | 916 | 0 | 410 | 0 | 86 | 225 | 0 | 0 | 26 | 0 | 40 | 60 | 38 | 80 | 0 | 0 | 0 | 50 | 41 | 97 | 0 | 0 | 43 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 189 | 0 | 78 | 100 | 176 | 0 | 413 | 105 | 0 | 94 | 0 | 110 | 0 | 0 | 109 | 622 |  | 7513 | 4352 | 11865 | 3339 | 916 | 2128 | 3721 | 772 | 43 | 784 | 162 | 0 | 0 | 98.42
24:00 | 0 | 0 | 200 | 115 | 0 | 43 | 0 | 0 | 351 |  | 0 | 420 | 140 | 100 | 94 | 40 | 0 | 0 | 198 | 0 | 100 | 93 | 150 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 51 | 0 | 43 | 0 | 120 | 0 | 25 | 203 | 0 | 140 | 0 |  | 0 | 0 | 102 | 20 | 97 | 50 | 21 | 39 | 0 | 0 | 80 | 310 | 0 | 182 | 26 | 94 | 26 | 54 | 0 | 51 | 0 | 50 | 52 | 18 | 8 | 33 | 20 | 162 | 155 | 0 | 17 | 0 | 60 | 30 | 0 | 44 | 163 | 191 | 65 | 88 | 0 | 0 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 300 | 0 | 0 | 193 | 0 | 149 | 0 | 100 | 170 | 30 | 0 | 115 | 84 | 0 | 0 | 162 | 54 | 0 | 100 | 105 | 100 | 0 | 104 |  | 916 | 0 | 400 | 0 | 90 | 225 | 0 | 0 | 26 | 0 | 40 | 60 | 38 | 80 | 0 | 0 | 0 | 50 | 25 | 97 | 0 | 0 | 43 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 180 | 0 | 76 | 100 | 170 | 0 | 407 | 105 | 0 | 94 | 0 | 112 | 0 | 0 | 109 | 622 |  | 7362 | 4309 | 11671 | 3283 | 916 | 2141 | 3586 | 772 | 43 | 768 | 162 | 0 | 0 | 98.43
KWH | 0 | 0 | 4776000 | 2772000 | 4770800 | 1021409 | 0 | 0 | 8182000 |  | 0 | 7083800 | 3360844 | 2409600 | 2181720 | 1171718 | 0 | 0 | 4253000 | 0 | 2384640 | 2253744 | 2727840 | 463698 | 0 | 0 | 0 | 1196280 | 1184962 | 1317103 | 446004 | 600000 | 614880 | 792900 | 819000 | 783672 | 0 | 939420 | 124000 | 2800000 | 0 | 378095 | 4880413 | 0 | 3230828 | 0 |  | 0 | 0 | 1007600 | 308760 | 1768320 | 914400 | 480768 | 474240 | 0 | 0 | 1913438 | 7699000 | 0 | 4468000 | 786181 | 2171610 | 658872 | 1286880 | 0 | 1128883 | 0 | 349208 | 1036886 | 407196 | 163980 | 814200 | 49370 | 3415680 | 3632280 | 0 | 377820 | 11600 | 1411000 | 719400 | 1073400 | 1041768 | 3654490 | 4372000 | 1491456 | 1982400 | 0 | 842490 | 171000 | 0 | 223920 | 7143250 | 541088 | 124048 | 407808 | 6674179 | 658224 | 417890 | 4644000 | 4080 | 3393360 | 123930 | 1752000 | 165880 | 1222763 | 0 | 2131200 | 1748508 | 0 | 30480 | 2506582 | 1300732 | 0 | 1657560 | 2505720 | 1916160 | 377600 | 2623680 |  | 22170181 | 0 | 8771040 | 0 | 1887360 | 3708977 | 0 | 0 | 109140 | 0 | 445125 | 1284000 | 614619 | 1074912 | 0 | 0 | 0 | 525392 | 281397 | 1168128 | 0 | 0 | 356818 | 874080 | 0 | 480240 | 221862 | 245178 | 0 | 0 | 3691000 | 0 | 0 | 0 | 0 | 4287455 | 0 | 1858233 | 792000 | 4418009 | 0 | 9341763 | 2319840 | 276774 | 2152896 | 0 | 2538240 | 0 | 38041 | 2465472 | 13714000 |  | 161528788 | 92112172 | 253640960 | 77877323 | 22170181 | 47599338 | 73671467 | 17405000 | 1063420 | 10234500 | 3415680 | 204051 | 0
Fuel Cost | 0 | 0 | 6972960 | 4074840 | 0 | 1348259.88 | 0 | 0 | 8427460 |  | 0 | 7721342 | 3730536.84 | 18288864 | 15032050.8 | 9912734.28 | 0 | 0 | 7357690 | 0 | 17956339.2 | 20554145.28 | 26841945.6 | 4275295.56 | 0 | 0 | 0 | 8732844 | 9159756.26 | 12986635.58 | 334503 | 450000 | 0 | 0 | 0 | 7578108.24 | 0 | 253643.4 | 33480 | 5068000 | 0 | 3512502.55 | 5319650.17 | 0 | 5492407.6 | 0 |  | 0 | 0 | 9773720 | 2948658 | 15384384 | 7242048 | 605767.68 | 1408492.8 | 0 | 0 | 2812753.86 | 5697260 | 0 | 4110560 | 1014173.49 | 2497351.5 | 744525.36 | 1801632 | 0 | 1930389.93 | 0 | 3527000.8 | 9902261.3 | 517138.92 | 122985 | 1424850 | 37027.5 | 25617600 | 3850216.8 | 0 | 479831.4 | 184904 | 2314040 | 1151040 | 1910652 | 1625158.08 | 4166118.6 | 4546880 | 2938168.32 | 3786384 | 0 | 1457507.7 | 374490 | 0 | 456796.8 | 7214682.5 | 405816 | 94276.48 | 6936814.08 | 50456793.24 | 11176643.52 | 6987120.8 | 24148800 | 68217.6 | 33390662.4 | 1448741.7 | 14278800 | 1799798 | 8620479.15 | 0 | 19436544 | 16523400.6 | 0 | 0 | 18949759.92 | 11329375.72 | 0 | 16542448.8 | 21474020.4 | 12761625.6 | 0 | 0 |  | 127700242.56 | 0 | 9209592 | 0 | 14834649.6 | 51406421.22 | 0 | 0 | 1144878.6 | 0 | 4638202.5 | 1450920 | 952659.45 | 10491141.12 | 0 | 0 | 0 | 5169857.28 | 2858993.52 | 10337932.8 | 0 | 0 | 3457566.42 | 8469835.2 | 0 | 922060.8 | 343886.1 | 185599.746 | 0 | 0 | 20005220 | 0 | 0 | 0 | 0 | 5659440.6 | 0 | 2787349.5 | 13471920 | 5169070.53 | 0 | 9248345.37 | 24219129.6 | 4707925.74 | 20430983.04 | 0 | 19696742.4 | 0 | 420353.05 | 18219838.08 | 60204460 |  | 623823582.59 | 457815216.826 | 1081638799.416 | 92927160.166 | 127700242.56 | 57065843.3 | 581258835 | 80209680 | 287123.4 | 114518316.24 | 25617600 | 2053998.75 | 0
Yesterday Day Peak | 0 | 0 | 200 | 115 | 0 | 43 | 0 | 0 | 347 |  | 0 | 340 | 140 | 100 | 95 | 55 | 0 | 0 | 180 | 0 | 94 | 93 | 150 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 51 | 0 | 42 | 0 | 120 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 37 | 19 | 21 | 4 | 0 | 0 | 80 | 305 | 0 | 188 | 50 | 96 | 29 | 53 | 0 | 43 | 0 | 0 | 43 | 18 | 5 | 33 | 21 | 130 | 152 | 0 | 17 | 2 | 59 | 30 | 47 | 44 | 130 | 195 | 63 | 85 | 0 | 0 | 0 | 0 | 9 | 290 | 24 | 0 | 0 | 286 | 0 | 0 | 193 | 0 | 149 | 18 | 100 | 0 | 10 | 0 | 96 | 84 | 0 | 5 | 176 | 54 | 0 | 80 | 113 | 100 | 5 | 104 |  | 928 | 0 | 325 | 0 | 83 | 120 | 0 | 0 | 0 | 0 | 0 | 50 | 14 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 7 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 181 | 0 | 77 | 0 | 169 | 0 | 387 | 90 | 0 | 94 | 0 | 109 | 0 | 7 | 109 | 470 |  | 10215 | DayPeak
Yesterday Evening Peak | 0 | 0 | 200 | 115 | 0 | 42 | 0 | 0 | 351 | 0 | 0 | 280 | 130 | 100 | 97 | 55 | 0 | 0 | 150 | 0 | 100 | 93 | 150 | 23 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 26 | 33 | 33 | 51 | 0 | 42 | 35 | 120 | 0 | 25 | 203 | 0 | 139 | 0 | 0 | 0 | 0 | 102 | 60 | 90 | 50 | 21 | 18 | 0 | 0 | 80 | 320 | 0 | 179 | 55 | 86 | 29 | 51 | 0 | 45 | 0 | 50 | 43 | 18 | 8 | 33 | 21 | 156 | 155 | 0 | 17 | 0 | 60 | 30 | 53 | 44 | 163 | 185 | 63 | 88 | 0 | 0 | 0 | 0 | 10 | 285 | 16 | 5 | 100 | 300 | 303 | 99 | 200 | 0 | 149 | 0 | 100 | 200 | 10 | 0 | 102 | 84 | 0 | 0 | 162 | 54 | 0 | 100 | 94 | 100 | 0 | 104 |  | 916 | 0 | 410 | 0 | 83 | 225 | 0 | 0 | 9 | 0 | 40 | 60 | 38 | 80 | 0 | 0 | 0 | 50 | 41 | 97 | 0 | 0 | 44 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 196 | 0 | 77 | 100 | 200 | 0 | 393 | 105 | 175 | 94 | 0 | 108 | 0 | 0 | 109 | 622 |  | 12250 | EvPeak
Forecast for Evening | 0 | 0 | 220 | 115 | 200 | 42 | 0 | 0 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 40 | 0 | 0 | 200 | 0 | 100 | 93 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 44 | 0 | 120 | 0 | 25 | 221 | 0 | 145 | 0 | 0 | 0 |  | 100 | 100 | 90 | 50 | 21 | 25 | 0 | 0 | 80 | 360 | 360 | 225 | 26 | 100 | 30 | 55 | 0 | 51 | 0 | 50 | 52 | 18 | 8 | 33 | 21 | 173 | 160 | 0 | 17 | 0 | 60 | 30 | 51 | 44 | 163 | 200 | 65 | 86 | 0 | 0 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 86 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 104 |  | 927 | 16 | 410 | 0 | 115 | 225 | 0 | 0 | 30 | 60 | 40 | 65 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 0 | 0 | 43 | 52 | 34 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 200 | 0 | 78 | 100 | 220 | 0 | 414 | 90 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620
Forecast for Day | 0 | 0 | 220 | 115 | 200 | 42 | 0 | 0 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 40 | 0 | 0 | 200 | 0 | 100 | 93 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 44 | 0 | 120 | 0 | 25 | 221 | 0 | 140 | 0 | 0 | 0 |  | 100 | 100 | 90 | 50 | 21 | 10 | 0 | 0 | 80 | 360 | 0 | 225 | 26 | 100 | 30 | 55 | 0 | 51 | 0 | 0 | 52 | 18 | 8 | 33 | 21 | 162 | 160 | 0 | 17 | 1.6 | 60 | 30 | 51 | 44 | 163 | 200 | 65 | 86 | 0 | 0 | 18 | 0 | 10 | 341 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 200 | 150 | 0 | 115 | 85 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 104 |  | 927 | 0 | 410 | 0 | 115 | 225 | 0 | 0 | 0 | 0 | 40 | 65 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 52 | 0 | 22 | 10 | 10 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 200 |  | 78 | 50 | 220 | 0 | 414 | 90 | 100 | 100 | 100 | 100 | 0 | 8 | 113 | 620
Generation at 08:00(Today) | 0 | 0 | 200 | 115 | 200 | 43 | 0 | 0 | 300 | 0 | 0 | 370 | 143 |  | 94 | 39 | 0 | 0 | 195 | 0 | 7 | 50 | 0 | 11 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 25 | 28 | 33 | 33 | 0 | 0 | 43 | 0 | 120 | 0 | 0 | 204 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 19 | 21 | 11 | 0 | 0 | 80 | 275 | 0 | 193 | 26 | 95 | 26 | 55 | 0 | 51 | 0 | 0 | 8 | 18 | 8 | 33 | 20 | 126 | 156 | 0 | 17 | 1 | 60 | 30 | 0 | 47 | 130 | 193 | 65 | 84 | 0 | 0 | 0 | 0 | 10 | 295 | 24 | 8 | 0 | 195 | 0 | 0 | 200 | 0 | 141 | 5 | 100 | 0 | 30 | 0 | 12 | 15 | 0 | 3 | 162 | 54 | 0 | 0 | 103 | 100 | 0 | 104 | 0 | 918 | 0 | 355 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 78 | 0 | 187 | 0 | 400 | 90 | 0 | 35 | 0 | 107 | 0 | 2 | 109 | 313 | 0
199
| Minimum Generation |  | 8783 | 7:00
| Highest Generation |  | 12250 | 19:00
| Day Peak Generation |  | 10215 | 12:00
| Evening Peak Generation |  | 12250 | 19:00
| HVDC Max Flow |  | 929 | 16:00
| HVDC EvPeak Flow |  | 916 | 19:00
| Load factor L.F |  | 86.27%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-09-30
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-09-29 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10215 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 9241 | MW
Evening Peak Generation : |  | 12250 | MW Hour : | 19:00 | Available Max Generation : |  | 14541 | MW
E.P. Demand (at gen end) : |  | 12250 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 12800 | MW
Maximum Generation : |  | 12250 | MW Hour : | 19:00 | Reserve(Generation end) |  | 1741 | MW
Total Gen. (MKWH) : |  | 253.641 | System Load Factor : | 86.27% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 246 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-09-30
Actual : | 98.46 | Ft.(MSL) , | Rule curve : | 105.76 | Ft.( MSL )
Gas Consumed : | Total = | 1119.61 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 149993003.466
: |  | Coal : | 80209680 | Oil : | 695777151.24 | Total : | 925979834.706
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4588.6427 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1565.0376 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1403.0495 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1268.0674 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1145.7721 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 924.6093 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 511.0185 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 237.9038 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 713.1332 |  |  | 0 | 0%
Total | 0 |  | 12357.2341 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 10) Siddirganj-335 MW
2) Bibiyana #3
3) Ghorasal Unit-1,2,3,
4) Ashuganj unit-3,4
5) Kaptai-2,4,5
6) Raozan #1,2
7) Sirajganj #1
8) Baghabari-71 MW,100 MW
9) Ashuganj (S)-360 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) After maintenance Tongi-Kabirpur 132 kV Ckt-1 was switched on at 08:52.
b) After maintenance Kabirpur 132 kV main bus was switched on at 11:19.
c) Mymensing 132 kV bus-A was under shut down from 08:52 to 16:52 for C/M.
d) Barisal (S) 132/33kV T-1 transformer was under shut down from 08:20 to 10:07 for oil leakage maint.
e) Sreemangal 132/33kV T-1 & T2 transformer tripped at 10:35 due to lockout of HV side,T2 also tripped and |  |  |  |  | About 15 MW power interruption occurred under Sreemangal S/S area
were switched on at 11:03. |  |  |  |  | from 10:35 to 11:03.
f) Shahjibazar 132/33kV T-2 transformer was under shut down from 10:24 to 13:45 due to red hot maint
at 33 kV Bus connector.
g) After clearance of SE grid circle CTG TK Chemical 132/20kV T-1 transformer was switched on at 08:52
h) Sylhet-Chattak 132 kV Ckt-1 was under shut down from 09:40 to 10:50 for bus maintenance at Sylhet S/S.
i) Sylhet S/S 132 kV bus section-3 & 4 was under shut from 11:50 to 16:04 due to red hot maintenance
between section-3 & 4 isolator.
j) After maintenance Sikalbaha-TK Chemical 132 kV Ckt was switched on at 14:00.
k) Tongi 230/132kV T-03 transformer was under shut down from 08:58 to 15:28 for oil leakage from 132 kV
R-phase bushing.
l) Barisal (N) 132/33kV T-5 transformer tripped at 13:20 operating PRD.
m) Agrabad 132/33kV T-1 transformer was under shut down from 14:24 to 14:43 for D/W.
n) Agrabad 132/33kV T-2 transformer was under shut down from 14:46 to 15:09 for D/W.
o) After maintenance Chapainawabganj 132/33kV T-2 transformer was switched on at 15:05.
p) Chapainawabganj 132/33kV T-3 transformer was under shut down from 16:02 to 17:40 for project work.
q) Sylhet-Chattak 132 kV Ckt-2 was under shut down from 10:56 to 16:17 for bus maintenance at Sylhet S/S.
r) Kulaura 132/33kV T-2 transformer was under shut down from 06:03 to 09:26(30-09-2020) for D/W.
s) Shahjadpur-Baghabari 132 kV Ckt-2 was under shut down from 07:19 to 08:23(30-09-2020) for C/M
t) Goalpara 132/33kV T-5 transformer was under shut down from 07:06 to 10:05(30-09-2020) for C/M.
u) Sylhet 132 kV bus-2,3 & 4 are under shut down since 07:23(30-09-2020) for red hot maintenance.
v) Bogura 132/33 kV T2 transformer tripped at 05:38 from both side showing differential,PRD,buchaltz
relay at 132 kV side & trip Ckt unhealthy at 33 kV side.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-09-29 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 200 | 4776000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 115 | 2772000 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 4770800 | Machine problem
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 42 | 1021409 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 351 | 8182000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 280 | 7083800 | Dirty Fuel
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 2409600
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 130 | 3360844 | Gas shorage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 97 | 2181720
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1171718
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 23 | 463698 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 446004
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 150 | 4253000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 2384640
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under Maintenance
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 2253744 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel Shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1196280
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 2727840
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 1184962
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1317103
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 51 | 1214880 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 792900
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 819000
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 783672
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 6674179
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 303 | 658224
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 99 | 417890
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 4080 | Fuel Shortage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3393360
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 84 | 1748508 | Engine problem
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2623680
| Dhaka area Total |  |  |  | 5895 | 3259 | 73087535
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2800000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 378095
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 123930
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 914400
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 77 | 1063420 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4880413
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 139 | 3230828
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 1007600
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 60 | 308760 | High voltage
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1752000
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 480768
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 18 | 474240
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 90 | 1768320 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 30480
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 162 | 2506582 | Low demand.
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1300732
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1916160
| Chattogram area Total |  |  |  | 2266 | 1321 | 24936728
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 1913438
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 179 | 4468000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 320 | 7699000 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 658872 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 51 | 1286880
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 55 | 786181 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 45 | 1128883
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 10 | 1222763 | R/H at APSCL
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 349208
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 86 | 2171610
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 165880
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 407196 | Engine problem
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 163980 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 156 | 3415680
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 814200
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 1036886
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 49370 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 100 | 407808 | Engine problem
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 100 | 1657560 | Low demand.
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 94 | 2505720 | Engine problem
| Cumilla Area Total |  |  |  | 2980 | 1678 | 32309115
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 155 | 3632280 | Machine problem & Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 377820 | Engine problem
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 0 | 0 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11600
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 4644000 | Low demand.
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 102 | 2131200 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 474 | 10796900
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1411000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 719400 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3654490
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 185 | 4372000 | Gas shortage.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1073400
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 44 | 1041768
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 124048
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 63 | 1491456
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 88 | 1982400
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 842490 | R/H at Bus section analiser
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 171000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 541088
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 7143250 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 223920
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 377600 | On test
| Sylhet Area Total |  |  |  | 1988 | 1002 | 25169310
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 916 | 22170181
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 83 | 1887360
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 9 | 109140
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 225 | 3708977
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 410 | 8771040
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 445125
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 792000
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 2319840
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1888 | 40203663
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 80 | 1074912
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 38 | 614619
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 60 | 1284000 | GT-2 Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 77 | 1858233 | Engine problem
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 622 | 13714000 | Under maint unit 1
| Barisal Area Total |  |  |  | 1054 | 877 | 18545764
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 525392
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 41 | 281397
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel Shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel Shortage
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 44 | 356818
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | STG U/M & Gas Shortage
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 196 | 4287455 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 200 | 4418009 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 393 | 9341763 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 480240
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 10 | 221862
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 245178
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 874080
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 97 | 1168128
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 175 | 276774 | Low demand.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 94 | 2152896 | Engine problem
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 2465472
| Rajshahi Area Total |  |  |  | 2183 | 1493 | 27095464
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3691000 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 108 | 2538240
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 38041
| Rangpur Area Total |  |  |  | 605 | 258 | 6267281
| Total |  |  |  | 19892 | 12250 | 258411760
| Eastern Grid Total |  |  |  | 13766 | 7734 | 166299588
| Western Grid Total |  |  |  | 6126 | 4516 | 92112172
| National Grid Total |  |  |  | 19892 | 12250 | 258411760
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-09-29
| (a) ENTIRE EASTERN GRID : |  | 8003 | MW | (b) ENTIRE WESTERN GRID : |  | 3816 | MW
| i) Dhaka area |  | 4236 | MW | i) Khulna area |  | 1479 | MW
| ii) Chittagong area |  | 1239 | MW | ii) Rajshahi area |  | 1253 | MW
| iii) Comilla area |  | 1156 | MW | iii) Barisal area |  | 343 | MW
| iv) Mymensingh area |  | 944 | MW | iv) Rangpur area |  | 741 | MW
| v) Sylhet area |  | 428 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11819 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 128 | 15:00 | Sherpur | 106 | 22:00 | Jhenida | 103 | 21:00
| Munsiganj | 122 | 0:00 | Srimongal | 51 | 19:30 | Bottail | 126 | 18:30
| Sonargaon | 93 | 20:00 | Shahjibazar | 124 | 21:00 | G.K Project | 57 | 19:30
| Shyampur | 190 | 2:00 | Fenchuganj | 46 | 21:00 | Faridpur | 193 | 0.8125
| Bhulta | 195 | 19:00 | Kulawara | 49 | 18:00 | Madaripur | 103 | 0.91667
| Madanganj | 65 | 0:00 | Sylhet | 115 | 14:00 | Sariatpur | 64 | 21:00
| Shitalakhya | 113 | 16:00 | Chatak | 29 | 22:00 | Gopalganj | 90 | 18:30
| Rahim steel | 18 | 16:00 | Sunamganj | 38 | 2:00 | Bagerhat | 102 | 21:00
| Matuail | 83 | 9:00 | Biani Bazar | 62 | 18:00 | Mongla | 34 | 10:00
| Ghorasal | 88 | 22:00 | Comilla (S) | 162 | 23:00 | Satkhira | 112 | 0.875
| Narsingdi | 168 | 21:00 | Comilla(N) | 135 | 19:30 | Gallamari | 48 | 1:00
| Haripur (SBU) | 97 | 12:00 | Chandpur | 105 | 23:00 | Magura | 52 | 0.79167
| Ullon | 54 | 18:00 | Feni | 124 | 19:00 | Norail | 40 | 20:00
| Hasnabad | 205 | 18:30 | Chowmuhani | 184 | 19:30 | Chuadanga | 89 | 19:30
| Magbazar | 103 | 15:00 | Ashuganj | 56 | 0:00 | Barisal(N) | 45 | 0.91667
| Maniknagar | 94 | 11:00 | Daudkandi | 147 | 20:00 | Barisal (S) | 102 | 0.83333
| Bangabhaban | 36 | 10:00 | B.Baria | 163 | 19:30 | Patuakhali | 121 | 0.91667
| Narinda | 90 | 18:30 | Ramganj | 116 | 22:00 | Bhandaria | 55 | 0.875
| Dhanmondi | 175 | 13:00 | Chaddagram | 38 | 21:00 | Borhan Uddin | 44 | 18:30
| Lalbag | 86 | 12:00 | PHP | 10 | 21:00 | Ishurdi | 67 | 19:00
| Madartek | 72 | 22:00 | Madunaghat | 57 | 18:00 | Ruppur Paromanobik | 2 | 1:00
| Dhaka University |  |  | Hathazari | 106 | 0.79167 | Natore | 123 | 21:00
| Fatullah | 44 | 0.375 | Khulshi | 206 | 0.58333 | Bogra | 164 | 21:00
| Mirpur | 108 | 18:00 | Halishahar | 136 | 0.83333 | Noagaon | 113 | 21:00
| Kalyanpur | 92 | 18:00 | Baraulia | 138 | 0.95833 | Rajshahi | 148 | 20:00
| Gulshan | 134 | 13:00 | Sikalbaha | 28 | 0.79167 | Rajshahi New | 13 | 19:30
| Uttara | 96 | 18:00 | Dohazari | 86 | 0 | C.Nawabganj | 72 | 21:00
| Uttara New | 32 | 18:00 | Cox'sbazar | 99 | 0.79167 | Amnura | 42 | 19:00
| Kamrangirchar | 90 | 19:00 | Chandraghona | 34 | 0.77083 | Pabna | 126 | 20:00
| Savar | 143 | 9:00 | Kaptai | 4.5 | 0.77083 | Shahjadpur | 109 | 19:30
| Bhasantec | 156 | 13:00 | A. Khaer Stl. | 8 | 0.041667 | Serajganj | 114 | 20:00
| Agargaon | 76 | 13:00 | Bakulia | 106 | 0.75 | Niyamatpur | 56 | 21:00
| Satmosjid | 97 | 19:00 | Julda | 24 | 0.25 | Joypurhat | 61 | 20:00
| Tongi | 101 | 0.79167 | TK chemical | 25 | 0.041667 | Sherpur(Bogura) | 48 | 19:00
| Kabirpur | 231 | 12:00 | Modern Steel | 13 | 0.125 | Mohastangor | 54 | 1:00
| Basundhara | 139 | 13:00 | Shahmirpur | 23 | 0.58333 | Rangpur | 152 | 22:00
| Manikganj | 72 | 0.875 | Khagrachhari | 24 | 0.25 | Lalmonirhat | 59 | 19:30
| Joydevpur | 157 | 11:00 | Matarbari | 37 | 0.875 | Saidpur | 113 | 19:00
| New Tongi | 111 | 15:00 | Baroiar Hat | 48 | 0.75 | Purbasadipur | 104 | 20:00
| Korda | 259 | 18:30 | Rangamati | 12 | 0.75 | Thakurgaon | 83 | 19:30
| Dhamrai | 86 | 19:30 | Abul Khair 230 | 61 | 0.54167 | Palashbari | 125 | 21:00
| Rajendrapur | 100 | 22:00 | BSRM | 156 | 0.41667 | Barapukuria | 51 | 20:00
| Valuka | 138 | 18:30 | GPH Ispat | 82 | 0.95833 | Panchagar | 52 | 19:00
| Tangail | 197 | 21:00 | Goalpara | 18 | 0.54167 | Joldhaka | 29 | 20:00
| Mymensing | 176 | 18:00 | Central s/s | 99 | 19:00 | Kurigram | 58 | 18:30
| Kishorganj | 144 | 23:00 | Noapara | 57 | 18:30
| Netrokona | 115 | 24:00 | Jessore | 114 | 18:30
| Jamalpur | 145 | 21:00 | Benapol | 50 | 18:30
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-09-29 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 397 | 5:00 | 386 | 18:30 | Kaliakoir | 381 | 0.25 | 367 | 0.75
| Bheramara | 393 | 7:00 | 386 | 19:00 | Bhulta | 391 | 0.25 | 378 | 0.5
| Ashuganj(N) | 397 | 5:00 | 384 | 12:00 | Gopalganj | 414 | 0.375 | 390 | 0.875
| Payra | 415 | 4:00 | 401 | 21:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 232 | 8:00 | 230 | 1:00 | Comilla (N) | 235 | 2:00 | 230 | 11:00
| Ishurdi | 234 | 17:00 | 223 | 22:00 | Hathazari | 226 | 18:30 | 222 | 6:00
| Ashuganj | 237 | 5:00 | 230 | 12:00 | Megnaghat | 232 | 5:00 | 223 | 15:00
| Serajganj | 233 | 8:00 | 225 | 23:00 | Fenchuganj | 240 | 5:00 | 229 | 18:00
| Baghabari | 241 | 18:00 | 234 | 22:00 | Siddhirganj | 232 | 21:00 | 223 | 12:00
| Barapukuria | 238 | 6:00 | 227 | 21:00 | Maniknagar | 226 | 6:00 | 221 | 12:00
| Bogra | 228 | 17:00 | 213 | 22:00 | Agargaon | 229 | 9:00 | 216 | 13:00
| Rajshahi | 230 | 18:00 | 216 | 20:00 | Barisal | 249 | 2:00 | 232 | 22:00
| Khulna South | 239 | 18:00 | 227 | 20:00 | AKSML | 222 | 6:00 | 220 | 3:00
| Rampura | 228 | 4:00 | 221 | 12:00 | BSRM | 226 | 19:00 | 221 | 12:00
| Haripur | 230 | 3:00 | 220 | 12:00 | Bibiyana | 240 | 6:00 | 231 | 18:00
| Hasnabad | 230 | 1:00 | 220 | 15:00 | Bhulta | 233 | 19:00 | 224 | 17:00
| Shyampur | 227 | 4:00 | 218 | 12:00 | Ashuganj (S) | 236 | 6:00 | 234 | 12:00
| Aminbazar | 224 | 9:00 | 217 | 16:00 | Kaliakoir | 234 | 5:00 | 224 | 1:00
| Tongi | 227 | 19:30 | 220 | 11:00 | GPH | 222 | 5:00 | 219 | 8:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 133 | 5:00 | 127 | 12:00 | Hathazari | 135 | 0.77083 | 132 | 0.16667
| Munsiganj | 133 | 5:00 | 128 | 15:00 | Khulshi | 133 | 0.79167 | 130 | 0.29167
| Sonargaon | 134 | 3:00 | 129 | 11:00 | Halishahar | 136 | 0.77083 | 131 | 0.375
| Shyampur | 134 | 5:00 | 128 | 12:00 | Baraulia | 135 | 0.79167 | 129 | 0.083333
| Bhulta | 124 | 1:00 | 120 | 11:00 | Sikalbaha | 136 | 19:00 | 131 | 0.33333
| Madanganj | 138 | 5:00 | 126 | 12:00 | Dohazari | 132 | 18:30 | 126 | 0.29167
| Shitalakhya | 142 | 2:00 | 133 | 15:00 | Cox'sbazar | 125 | 0.41667 | 118 | 0.083333
| Rahim steal | 131 | 7:00 | 127 | 12:00 | Chandraghona | 134 | 0.75 | 131 | 0.125
| Matuail | 133 | 5:00 | 127 | 12:00 | Kaptai | 133 | 18:00 | 130 | 0.33333
| Ghorasal | 136 | 1:00 | 136 | 1:00 | A. Khaer Stl. | 133 | 0.83333 | 129 | 8:00
| Narsinghdi | 128 | 7:00 | 121 | 12:00 | Bakulia | 134 | 0.77083 | 130 | 0.375
| Haripur (SBU) | 134 | 6:00 | 127 | 12:00 | Julda | 135 | 0.75 | 132 | 0.125
| Ullon | 136 | 4:00 | 128 | 12:00 | TK Chemical | 135 | 0.75 | 130 | 11:00
| Hasnabad | 138 | 1:00 | 130 | 11:00 | Modern Steel | 134 | 0.75 | 131 | 0.20833
| Magbazar | 136 | 5:00 | 128 | 12:00 | Shahmirpur | 135 | 0.77083 | 131 | 0.20833
| Maniknagar | 135 | 7:00 | 127 | 12:00 | Khagrachhari | 132 | 0.25 | 130 | 0.16667
| Bangabhaban | 135 | 7:00 | 127 | 12:00 | Matarbari | 127 | 0.375 | 121 | 0.083333
| Narinda | 135 | 7:00 | 127 | 12:00 | Baroiar Hat | 135 | 0.375 | 131 | 0.29167
| Dhanmondi | 136 | 4:00 | 128 | 12:00 | Rangamati | 134 | 0.79167 | 130 | 8:00
| Lalbag | 138 | 21:00 | 128 | 12:00 | Goalpara S/S | 137 | 10:00 | 131 | 21:00
| Madartek | 135 | 4:00 | 128 | 11:00 | Khulna Central S/S | 137 | 0.375 | 131 | 21:00
| Dhaka University |  |  |  |  | Noapara | 136 | 18:00 | 128 | 21:00
| Fatuiiah | 134 | 0.16667 | 128 | 12:00 | Jessore | 132 | 18:00 | 121 | 20:00
| Mirpur | 137 | 6:00 | 126 | 11:00 | Benapol | 133 | 18:00 | 120 | 21:00
| Kalyanpur | 135 | 4:00 | 128 | 12:00 | Jhenida | 130 | 0.75 | 115 | 20:00
| Gulshan | 134 | 6:00 | 127 | 12:00 | Bottail | 135 | 18:00 | 125 | 20:00
| Uttara | 135 | 6:00 | 127 | 11:00 | G.K Project | 140 | 0.33333 | 135 | 18:30
| Uttara New | 136 | 4:00 | 125 | 12:00 | Faridpur | 133 | 8:00 | 122 | 22:00
| Kamrangirchar | 135 | 6:00 | 127 | 12:00 | Madaripur | 137 | 0.29167 | 129 | 21:00
| Savar | 135 | 7;00 | 127 | 11:00 | Shariyatpur S/S | 138 | 0.25 | 126 | 21:00
| Bhasantec | 139 | 6:00 | 129 | 12:00 | Gopalganj | 137 | 8:00 | 124 | 20:00
| Agargaon | 140 | 6;00 | 131 | 12:00 | Bagerhat | 135 | 10:00 | 123 | 22:00
| Satmosjid | 139 | 6:00 | 130 | 12;00 | Mongla | 131 | 0.41667 | 123 | 20:00
| Tongi | 136 | 0.875 | 131 | 11:00 | Satkhira | 135 | 0.41667 | 125 | 21:00
| Kabirpur | 134 | 6:00 | 126 | 178:30 | Gallamari | 137 | 17:00 | 130 | 21:00
| Basundhara | 136 | 6:00 | 127 | 13:00 | Magura | 127 | 7:00 | 108 | 21:00
| Manikganj | 139 | 20:00 | 134 | 18:30 | Norail | 126 | 0.29167 | 109 | 23:00
| Joydevpur | 140 | 21:00 | 134 | 7:00 | Chuadanga | 125 | 8:00 | 104 | 21:00
| New Tongi | 135 | 0.91667 | 130 | 18:00 | Barisal(N) | 140 | 4:00 | 131 | 22:00
| Kodda | 137 | 24:00 | 130 | 0.75 | Barisal (S) | 139 | 0.33333 | 129 | 21:00
| Dhamrai | 134 | 6:00 | 126 | 18:30 | Patuakhali(S) | 136 | 0.29167 | 122 | 22:00
| Rajendrapur | 135 | 2:00 | 125 | 7:00 | Bhandaria | 131 | 9:00 | 118 | 21:00
| Valuka | 124 | 10:00 | 108 | 18:30 | Ishurdi | 138 | 18:00 | 132 | 20:00
| Tangail | 133 | 6:00 | 120 | 18:30 | Ruppur Paromanobik | 137 | 17:00 | 131 | 22:00
| Mymensing | 129 | 10:00 | 114 | 18:30 | Natore | 138 | 18:00 | 130 | 20:00
| Kishorganj | 130 | 10:00 | 118 | 18:30 | Bogra | 139 | 17:00 | 127 | 22:00
| Netrokona | 123 | 6:00 | 110 | 18:30 | Noagaon | 134 | 6:00 | 121 | 21:00
| Jamalpur | 138 | 10:00 | 124 | 18:30 | Rajshahi | 139 | 18:00 | 129 | 22:00
| Sherpur | 137 | 10:00 | 123 | 18:30 | Rajshahi New | 140 | 18:00 | 131 | 21:00
| Srimongal | 138 | 6:00 | 129 | 0.91667 | C.Nawabganj | 137 | 17:00 | 128 | 20:00
| Shahjibazar | 137 | 7:00 | 128 | 0.95833 | Amnura | 136 | 17:00 | 129 | 20:00
| Fenchuganj | 135 | 4:00 | 125 | 0.95833 | Pabna | 135 | 18:00 | 128 | 20:00
| Khulawara | 135 | 6:00 | 124 | 0.95833 | Shahjadpur | 140 | 18:00 | 132 | 20:00
| Sylhet | 134 | 7:00 | 115 | 0.95833 | Serajganj | 135 | 8:00 | 127 | 20:00
| Chatak | 131 | 5:00 | 105 | 18:30 | Niyamatpur | 133 | 6:00 | 118 | 20:00
| Sunamganj | 131 | 6:00 | 110 | 0.91667 | Joypurhat | 135 | 17:00 | 119 | 21:00
| Biani Bazar | 132 | 6:00 | 110 | 0.75 | Sherpur(Bogura) | 138 | 18:00 | 127 | 22:00
| Comilla(s) | 127 | 06.:00 | 120 | 13:00 | Mohastangor | 138 | 17:00 | 126 | 20:00
| Comilla(n) | 138 | 19:00 | 135 | 13:00 | Rangpur | 134 | 17:00 | 117 | 21:00
| Chandpur | 138 | 19:00 | 132 | 14:00 | Lalmonirhat | 133 | 6:00 | 116 | 20:00
| Feni | 137 | 19:00 | 132 | 7:00 | Saidpur | 132 | 6:00 | 116 | 21:00
| Chowmuhani | 136 | 14:00 | 132 | 21:00 | Purbasadipur | 130 | 17:00 | 112 | 21:00
| Ashuganj | 136 | 13:00 | 131 | 23:00 | Thakurgaon | 130 | 6:00 | 112 | 21:00
| Daudkandi | 136 | 19:00 | 128 | 16:00 | Palashbari | 135 | 17:00 | 119 | 22:00
| B.Baria | 134 | 10:00 | 126 | 21:00 | Barapukuria | 138 | 17:00 | 127 | 21:00
| Ramganj | 131 | 19:00 | 128 | 22:00 | Panchagar | 127 | 7:00 | 109 | 21:00
| Chaddagram | 137 | 19:00 | 133 | 15:00 | Joldhaka | 132 | 17:00 | 114 | 21:00
| PHP | 135 | 10:00 | 131 | 8:00 | Kurigram | 132 | 6:00 | 113 | 21:00
| Madanhat | 137 | 19:00 | 132 | 3:00

## L-Curve
Date | 2020-09-29
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 380 | 7362 | 4309 | 11671 |  |  |  | QF-LDC-11
0:30 | 369 | 7190 | 4196.5 | 11386.5 | Date: | 2020-09-29
1:00 | 358 | 7018 | 4084 | 11102
1:30 | 325 | 6948 | 3997 | 10945
2:00 | 292 | 6878 | 3910 | 10788
2:30 | 287.5 | 6802.5 | 3853 | 10655.5 | [5 empty] | Gen. at Eve. Peak | 12250 | 12250 MW (19:00 )
3:00 | 283 | 6727 | 3796 | 10523 | [6 empty] | 19:00
3:30 | 290 | 6655 | 3760 | 10415 | [5 empty] | Gen. at Day Peak | 10215 | 10215 MW (12:00 )
4:00 | 297 | 6583 | 3724 | 10307 | [6 empty] | 12:00
4:30 | 306 | 6533 | 3660 | 10193 | [5 empty] | Highest Generation | 12250
5:00 | 315 | 6483 | 3596 | 10079 | [6 empty] | 19:00
5:30 | 363.5 | 6246.5 | 3456 | 9702.5
6:00 | 412 | 6010 | 3316 | 9326
6:30 | 411 | 5808 | 3246.5 | 9054.5
7:00 | 410 | 5606 | 3177 | 8783
7:30 | 475 | 5644 | 3158.5 | 8802.5
8:00 | 540 | 5682 | 3140 | 8822
8:30 | 584 | 5842.5 | 3229 | 9071.5
9:00 | 628 | 6003 | 3318 | 9321
9:30 | 622.5 | 6239 | 3365 | 9604
10:00 | 617 | 6475 | 3412 | 9887
10:30 | 577.5 | 6522.5 | 3399 | 9921.5
11:00 | 538 | 6570 | 3386 | 9956
11:30 | 531.5 | 6657.5 | 3428 | 10085.5
12:00 | 525 | 6745 | 3470 | 10215
12:30 | 496.5 | 6781.5 | 3513.5 | 10295
13:00 | 468 | 6818 | 3557 | 10375
13:30 | 470 | 6807.5 | 3549 | 10356.5
14:00 | 472 | 6797 | 3541 | 10338
14:30 | 482 | 6863 | 3580 | 10443
15:00 | 492 | 6929 | 3619 | 10548
15:30 | 582 | 6790 | 3666 | 10456
16:00 | 672 | 6651 | 3713 | 10364
16:30 | 723.5 | 6463 | 3638.5 | 10101.5
17:00 | 775 | 6275 | 3564 | 9839
17:30 | 714.5 | 6591.5 | 3717 | 10308.5
18:00 | 654 | 6908 | 3870 | 10778
18:30 | 524.5 | 7321 | 4193 | 11514
19:00 | 395 | 7734 | 4516 | 12250
19:30 | 280 | 7800 | 4383 | 12183
20:00 | 246 | 7783 | 4395 | 12178 |  |  |  | Executive Engineer
20:30 | 250.5 | 7748 | 4377.5 | 12125.5 |  |  |  | Network Operation Division
21:00 | 255 | 7713 | 4360 | 12073
21:30 | 260 | 7670.5 | 4364.5 | 12035
22:00 | 265 | 7628 | 4369 | 11997 |  |  |  |  | Page 6 of 7
22:30 | 315.5 | 7570.5 | 4360.5 | 11931
23:00 | 366 | 7513 | 4352 | 11865
23:30 | 373 | 7437.5 | 4330.5 | 11768
24:00 | 380 | 7362 | 4309 | 11671
12250 MW (19:00 )
10215 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-09-29 |  | Energy | 253640960
[10 empty] | 2020-09-29 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3283 | 916 | 2141 | 3721 | 772 | 43 | 768 | 0 | 162
0:30 | 3262.5 | 921.5 | 2124.5 | 3487.5 | 761 | 42.5 | 695.5 | 0 | 159 | Date: | 2020-09-29
1:00 | 3242 | 927 | 2108 | 3254 | 750 | 42 | 623 | 0 | 156
1:30 | 3247.5 | 927 | 2104.5 | 3170.5 | 740 | 42 | 559.5 | 0 | 154 | [7 empty] | Total Energy | 253.641 | Total Energy Gen 253.641 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 253.641 MKWHr
2:00 | 3253 | 927 | 2101 | 3087 | 730 | 42 | 496 | 0 | 152 | [7 empty] | Energy not Served | 0
2:30 | 3250 | 926.5 | 2096 | 3013.5 | 730 | 42 | 447.5 | 0 | 150 | [7 empty] | Energy Requirement | 253.641
3:00 | 3247 | 926 | 2091 | 2940 | 730 | 42 | 399 | 0 | 148
3:30 | 3243.5 | 927 | 2098 | 2878.5 | 730 | 42 | 349 | 0 | 147 | [6 empty] | Shortage
4:00 | 3240 | 928 | 2105 | 2817 | 730 | 42 | 299 | 0 | 146
4:30 | 3239.5 | 927.5 | 2104.5 | 2739.5 | 730 | 42 | 268 | 0 | 142
5:00 | 3239 | 927 | 2104 | 2662 | 730 | 42 | 237 | 0 | 138
5:30 | 3231.5 | 927 | 2055.5 | 2409 | 715 | 42 | 186.5 | 0 | 136
6:00 | 3224 | 927 | 2007 | 2156 | 700 | 42 | 136 | 0 | 134
6:30 | 3206 | 927 | 1942.5 | 1969 | 685 | 42 | 152 | 0 | 128 |  |  |  |  | Coal
7:00 | 3188 | 927 | 1878 | 1782 | 670 | 42 | 168 | 0 | 122
7:30 | 3161 | 927 | 1882 | 1845.5 | 645 | 42.5 | 168 | 0 | 123 |  |  |  | Oil |  |  |  | ,
8:00 | 3134 | 927 | 1886 | 1909 | 620 | 43 | 168 | 0 | 124
8:30 | 3110.5 | 927.5 | 1961 | 2108.5 | 615 | 43.5 | 168 | 0 | 123
9:00 | 3087 | 928 | 2036 | 2308 | 610 | 44 | 168 | 0 | 122
9:30 | 3061.5 | 928 | 2040.5 | 2588 | 615 | 44 | 184 | 0 | 123
10:00 | 3036 | 928 | 2045 | 2868 | 620 | 44 | 200 | 0 | 124
10:30 | 3078 | 928 | 1987.5 | 2886.5 | 617.5 | 44 | 226.5 | 0 | 128
11:00 | 3120 | 928 | 1930 | 2905 | 615 | 44 | 253 | 0 | 132
11:30 | 3148 | 928 | 1960.5 | 2965.5 | 617.5 | 43 | 261.5 | 0 | 131
12:00 | 3176 | 928 | 1991 | 3026 | 620 | 42 | 270 | 0 | 130
12:30 | 3223 | 928 | 1988.5 | 3043 | 630 | 42 | 276 | 0 | 134
13:00 | 3270 | 928 | 1986 | 3060 | 640 | 42 | 282 | 0 | 138
13:30 | 3270 | 928 | 1986 | 3060 | 640 | 42 | 282 | 0 | 138
14:00 | 3270 | 928 | 1986 | 3060 | 640 | 42 | 282 | 0 | 138
14:30 | 3273 | 928 | 1972 | 3134 | 655 | 41 | 290 | 0 | 142
15:00 | 3276 | 928 | 1958 | 3208 | 670 | 40 | 298 | 0 | 146
15:30 | 3278.5 | 928.5 | 1916.5 | 3169.5 | 670 | 40 | 303 | 0 | 135
16:00 | 3281 | 929 | 1875 | 3131 | 670 | 40 | 308 | 0 | 124
16:30 | 3178 | 925 | 1796 | 3077 | 655 | 40.5 | 306 | 0 | 120
17:00 | 3075 | 921 | 1717 | 3023 | 640 | 41 | 304 | 0 | 116
17:30 | 3051 | 918.5 | 1739 | 3310.5 | 625 | 41.5 | 489 | 0 | 133
18:00 | 3027 | 916 | 1761 | 3598 | 610 | 42 | 674 | 0 | 150
18:30 | 3148 | 916 | 1892.5 | 3933 | 691 | 59.5 | 721 | 0 | 153
19:00 | 3269 | 916 | 2024 | 4268 | 772 | 77 | 768 | 0 | 156
19:30 | 3267 | 916 | 2193 | 4029 | 772 | 78 | 774 | 0 | 154
20:00 | 3280 | 916 | 2181 | 4019 | 772 | 78 | 780 | 0 | 152
20:30 | 3296 | 915.5 | 2172 | 3960.5 | 772 | 78 | 779.5 | 0 | 152
21:00 | 3312 | 915 | 2163 | 3902 | 772 | 78 | 779 | 0 | 152
21:30 | 3327 | 915 | 2145.5 | 3884.5 | 772 | 60.5 | 778.5 | 0 | 152
22:00 | 3342 | 915 | 2128 | 3867 | 772 | 43 | 778 | 0 | 152
22:30 | 3340.5 | 915.5 | 2128 | 3794 | 772 | 43 | 781 | 0 | 157
23:00 | 3339 | 916 | 2128 | 3721 | 772 | 43 | 784 | 0 | 162
23:30 | 3311 | 916 | 2134.5 | 3721 | 772 | 43 | 776 | 0 | 162 | Max Temp. in Dhaka |  | 33.4° C
24:00 | 3283 | 916 | 2141 | 3721 | 772 | 43 | 768 | 0 | 162
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 253.641 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 253.641 MKWHr
Note on W13: Author:

## Generation
g | 2020-09-29
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 43 | 44 | 44 | 44 | 42 | 42 | 40 | 40 | 40 | 41 | 42 |  | 42 | 43 | 43 | 43 | 43 | 43 | 43 | 939420
2 | Karnaphuli Hydro PP Unit-4 & 5 | [19 empty] | 35 | 35 | 35 | 35 |  |  |  | 124000
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | [8 empty] | 14 | 25 | 25 | 25 | 25 | 8 | 8 | 17 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 378095
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 4 | 6 | 11 | 13 | 20 | 18 | 19 | 20 | 15 | 2 | 1 | [9 empty] | 123930
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 203 | 203 | 204 | 204 | 204 | 203 | 203 | 204 | 204 | 204 | 204 | 204 | 206 | 204 | 204 | 204 | 207 |  | 203 | 204 | 204 | 204 | 204 | 205 | 203 | 4880413
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 145 | 144 | 139 | 139 | 139 | 139 | 103 | 104 | 103 | 139 | 139 | 139 | 139 | 139 | 138 | 140 | 139 | 139 |  | 139 | 140 | 139 | 139 | 140 | 139 | 140 | 3230828
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 100 | 68 | 68 | 34 | 34 | [12 empty] | 102 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 1007600
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
| Daudkandi 200 MW PP (B.Trac) | [17 empty] | 43 |  | 100 | 100 | 88 | 81 | 78 | 20 |  | 407808
14 | Titas 50 MW Peaking PP | [17 empty] | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 349208
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 195 | 195 | 195 | 195 | 195 | 190 | 160 | 120 | 120 | 120 | 180 | 180 | 175 | 120 | 190 | 193 | 120 | 77 |  | 150 | 150 | 160 | 155 | 196 | 195 | 198 | 4253000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 300 | 300 | 300 | 300 | 300 | 230 | 145 | 145 | 154 | 260 | 275 | 286 | 286 | 286 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 6674179
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 50 | 50 | 50 | 50 | 50 | 50 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 26 | 26 | 26 | 786181
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 150 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4776000
23 | Ghorasal TPP Unit-5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2772000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4770800
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1913438
32 | Ashuganj 50 MW PP | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 26 | 26 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 26 | 26 | 658872
33 | Ashuganj 225 MW CCPP | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 176 | 180 | 180 | 179 | 188 | 180 | 193 | 187 | 180 | 179 | 192 |  | 179 | 178 | 179 | 191 | 182 | 194 | 182 | 4468000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 295 | 295 | 295 | 305 | 320 | 335 | 320 | 320 | 320 | 330 |  | 320 | 320 | 320 | 325 | 310 | 325 | 310 | 7699000
35 | Ashuganj 55 MW PP (Precision) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 53 | 52 | 50 | 49 | 51 | 49 | 49 |  | 51 | 55 | 54 | 54 | 54 | 54 | 54 | 1286880
36 | Chandpur 150 MW CCPP | 88 | 89 | 89 | 88 | 89 | 86 | 85 | 90 | 95 | 85 | 88 | 96 | 85 | 96 | 93 | 88 | 86 | 94 |  | 86 | 96 | 92 | 94 | 94 | 94 | 94 | 2171610
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 380 | 380 | 380 | 380 | 380 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 260 | 210 | 210 | 210 | 210 | 220 |  | 280 | 420 | 420 | 420 | 420 | 420 | 420 | 7083800
41 | Haripur 360MW CCPP(HPL) | 349 | 349 | 349 | 350 | 349 | 348 | 353 | 348 | 348 | 349 | 348 | 347 | 346 | 344 | 346 | 305 | 304 | 277 |  | 351 | 352 | 350 | 351 | 351 | 351 | 351 | 8182000
42 | RPCL 210MW CCPP | 158 | 158 | 158 | 158 | 158 | 160 | 159 | 156 | 157 | 154 | 153 | 152 | 149 | 150 | 149 | 149 | 153 | 155 |  | 155 | 155 | 153 | 154 | 154 | 154 | 155 | 3632280
43
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 59 | 59 | 59 | 58 | 59 | 60 | 58 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1411000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 719400
46 | Shajibazar 330 MW CCPP | 187 | 188 | 186 | 184 | 184 | 184 | 184 | 202 | 191 | 185 | 191 | 195 | 192 | 203 | 190 | 191 | 190 | 192 |  | 185 | 185 | 190 | 197 | 190 | 200 | 191 | 4372000
47 | Shahjibazar GTPP Unit- 8 & 9 | 63 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 63 | 63 | 63 | 62 | 62 | 62 | 40 | 63 |  | 63 | 63 | 63 | 63 | 63 | 65 | 65 | 1491456
48 | Shahjibazar 86MW PP (Shahjibazar) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 84 | 85 | 85 | 83 | 20 | 20 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 1982400
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 30 | [17 empty] | 842490
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | [17 empty] | 171000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 223920
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [9 empty] | 2 |  | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 124048
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 46 | 47 | 47 | 50 | 53 | 50 | 51 | 53 | 53 |  | 53 | 53 | 53 | 17 | 0 |  |  | 1073400
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 |  | 16 | 24 | 24 | 24 | 24 | 24 | 24 | 541088
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 290 | 285 | 290 | 280 | 270 | 260 | 280 | 300 | 285 | 280 | 290 | 295 | 290 | 315 | 275 | 300 | 290 |  | 285 | 290 | 280 | 285 | 300 | 285 | 300 | 7143250
| Bibiyana South 400 MW | [10 empty] | 10 | 5 | 100 | 95 | 110 | 18 | [10 empty] | 377600
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1317103
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 18 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 480768
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 446004
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 377820
63 | Impoprt (Tripura) | 156 | 152 | 148 | 146 | 138 | 134 | 122 | 124 | 122 | 124 | 132 | 130 | 138 | 146 | 146 | 124 | 116 | 150 |  | 156 | 154 | 152 | 152 | 152 | 162 | 162 | 3415680
64 | Malancha, Ctg. EPZ (United) | 42 | 40 | 42 | 42 | 42 | 42 | 31 | 7 | 5 | 5 | 5 | 4 | 9 | 4 | 5 | 5 | 12 | 12 |  | 18 | 22 | 18 | 23 | 30 | 33 | 39 | 474240
65 | Feni 22MW PP (Doreen) | 18 | 18 | 18 | 13 | 13 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 407196
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 5 | 8 | 163980
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 814200
68 | Cumilla 25 MW PP (Summit) | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 49370
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 27 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 25 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 21 |  | 26 | 26 | 28 | 28 | 28 | 28 | 28 | 614880
71 | Maona 33 MW PP(Summit) | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 792900
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 16 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 819000
73 | Ghorashal 108MW PP (Regent) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 42 |  | 42 | 42 | 43 | 43 | 43 | 43 | 43 | 1021409
| Feni Lanka Power | 82 | 82 | 82 | 36 | 17 |  |  |  | 80 | 80 | 80 | 80 | 80 | 80 | 82 | 82 | 52 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1657560
| Chowmuhani 113 MW | 113 | 113 | 113 | 113 | 113 | 109 | 105 | 113 | 108 | 109 | 113 | 113 | 101 | 96 | 97 | 84 | 93 | 93 |  | 94 | 103 | 96 | 94 | 102 | 103 | 105 | 2505720
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 100 | 100 | 100 | 100 | 100 | 92 | 96 | 100 | 100 | 100 | 94 | 92 | 99 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2384640
78 | Gazipur 52 MW PP | 51 | 51 | [7 empty] | 45 | 51 | 51 | 51 | 51 | 51 | 8 | 8 | 31 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 783672
79 | Kodda 150MW PP | 150 | 150 | 114 | 48 | 16 | 16 | 48 | 48 | 48 | 80 | 133 | 150 | 150 | 150 | 150 | 115 | 100 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 2727840
80 | Jamalpur 95 MW PP(Powerpac) | [26 empty] | 0
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 43 | 43 | 25 | 25 | 25 | 31 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 45 | 52 | 52 | 52 | 52 | 1036886
| Gazipur 100 MW PP | 86 | 86 | 86 | 86 | 50 | 16 | 4 | 50 | 70 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 1748508
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 0 | 2 | 5 | 3 | 5 | 5 | 4 | 3 | 1 | 0 | [9 empty] | 30480
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1300732
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | 85 | 80 | 79 | 80 | 80 | 80 | 80 | 80 | 80 | 85 | 95 | 95 | 97 | 97 | 97 | 97 | 97 | 97 |  | 97 | 97 | 97 | 97 | 97 | 97 | 94 | 2181720
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 25 | 24 | [6 empty] | 6 | 12 | 12 | 12 | 12 | 12 | 13 | 12 | 12 | 12 |  | 23 | 100 | 97 | 100 | 20 | 12 | 12 | 463698
86 | Meghnaghat CCPP(Summit) | 140 | 140 | 140 | 140 | 140 | 120 | 125 | 138 | 140 | 135 | 135 | 140 | 130 | 150 | 145 | 140 | 130 | 145 |  | 130 | 135 | 135 | 145 | 145 | 145 | 140 | 3360844
87 | Meghnaghat 100 MW(IEL) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 93 | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2409600
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 2623680
88 | Ghorashal 78.5 MW PP(MAX) | [26 empty] | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [14 empty] | 40 | 10 | 10 | 40 |  | 60 | 40 | 40 | 40 | 20 | 20 | 20 | 308760
92 | Fenchuganj 44MW (Energyprima) | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 |  | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 1041768
93 | Ashuganj 51 MW PP (Midland) | 43 | 34 | 34 | 40 | 51 | 51 | 43 | 45 | 51 | 51 | 43 | 43 | 51 | 51 | 51 | 51 | 10 | 10 |  | 45 | 51 | 51 | 51 | 51 | 51 | 51 | 1128883
94 | Gagnagar 102 MW PP (Digital Power) | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 |  | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 2253744
95 | Patenga 50MW PP (Baraka) | 50 | 50 | 50 | 47 | 35 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 30 | 46 | 48 | 50 | 27 | 32 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 914400
96 | Chattogram 108 MW PP (ECPV) | 97 | 97 | 97 | 97 | 97 | 64 | 32 | 31 | 31 | 32 | 32 | 37 | 50 | 50 | 66 | 81 | 89 | 90 |  | 90 | 90 | 96 | 97 | 97 | 97 | 97 | 1768320
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | 40 | 44 | 44 | 45 | 52 | 15 | 15 | 30 | 32 | 55 | 55 | 55 | 55 | 55 | 55 | 40 | 48 | 55 |  | 55 | 55 | 55 | 55 | 55 | 45 | 40 | 1171718
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 |  | 35 | 35 | 35 | 55 | 55 | 55 | 55 | 1184962
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 163 | 110 | 110 | 163 | 163 | 110 | 130 | 163 | 163 | 163 | 163 | 163 | 130 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3654490
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 2 | 1 | 2 | 2 | 1 | 1 | 1 | 0 | 0 | [9 empty] | 11600
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 17 | 17 | 17 | 40 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1196280
104 | Keranigonj 300 MW PP (APR) | [17 empty] | 111 |  | 303 | 101 | 105 | 55 | 108 | 23 |  | 658224
105 | Bramhangoan 100 MW PP (Aggreko) | [17 empty] | 52 |  | 99 | 99 | 99 | 50 | 50 | 50 |  | 417890
106 | Mymensingh 200 MW PP (United) | 194 | 194 | 194 | 194 | 194 | 200 | 200 | 200 | 193 | 193 | 183 | 193 | 192 | 192 | 192 | 192 | 192 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 193 | 4644000
112 | Aurahati 100MW PP (Aggreko) | [26 empty] | 4080
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 149 | 149 | 149 | 143 | 27 | 79 | 144 | 149 | 136 | 149 | 149 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3393360
115 | Juldah 100 MW PP Unit-3 (Acorn) | 40 | 40 | 40 | 40 | 40 | 40 | 20 | 20 | 20 | 60 | 70 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1752000
116 | Chandpur 200MW (Desh energy) | 100 | [13 empty] | 27 | 100 | 50 | 95 |  | 200 | 200 | 200 | 200 | 200 | 200 | 170 | 165880
117 | Ashuganj 150MW PP (Midland) | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 15 | 30 | 30 | 1222763
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 95 | 95 | 95 | 95 | 95 | 35 | 8 | 8 | 32 | 75 | 75 | 96 | 105 | 105 | 95 | 95 | 95 | 95 |  | 102 | 115 | 115 | 115 | 115 | 115 | 115 | 2131200
| Anwara 300 MW PP (United) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 115 | 167 | 176 | 180 | 180 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 2506582
| Juldah unit-2 (Acorn) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1916160
120 | Eastern Zone Total | 7018 | 6878 | 6727 | 6583 | 6483 | 6010 | 5606 | 5682 | 6003 | 6475 | 6570 | 6745 | 6818 | 6797 | 6929 | 6651 | 6275 | 6908 |  | 7734 | 7800 | 7783 | 7713 | 7628 | 7513 | 7362 | 161528788
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 99 | 99 | 99 | 99 | 83 | 49 | 32 | 32 | 43 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 |  | 83 | 83 | 83 | 83 | 85 | 86 | 90 | 1887360
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 4 | 6 |  | 9 | 14 | 18 | 21 | 20 | 26 | 26 | 109140
| Khulna 225 MW CCPP | 190 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 155 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 3708977
129 | Rupsha 105 MW PP (Orion rupsha) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2319840
130
131
132
133
| Barisal 110 MW PP (Summit ) | 64 | 64 | 64 | 64 | 48 | 16 | 16 | 16 | 16 |  |  | 16 | 32 | 32 | 32 | 32 | 32 | 56 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1074912
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 77 | 78 | 77 | 76 | 77 | 76 | 77 | 77 | 77 | 77 | 78 | 77 | 77 | 77 | 77 | 77 | 76 | 77 |  | 77 | 77 | 77 | 78 | 79 | 78 | 76 | 1858233
| Bhola 225 MW CCPP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 60 | 58 | 60 |  | 60 | 59 | 60 | 60 | 60 | 60 | 60 | 1284000
140 | Bhola 33 MW PP (Venture) | 37 | 33 | 30 | 30 | 30 | 25 | 21 | 16 | 10 | 10 | 10 | 14 | 16 | 18 | 22 | 21 | 20 | 38 |  | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 614619
141 | Noapara 100 MW PP (Bangla Trac) | 100 | 30 | [15 empty] | 10 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 792000
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 24 | [10 empty] | 8 | 40 | 8 | 8 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 445125
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 927 | 927 | 926 | 928 | 927 | 927 | 927 | 927 | 928 | 928 | 928 | 928 | 928 | 928 | 928 | 929 | 921 | 916 |  | 916 | 916 | 916 | 915 | 915 | 916 | 916 | 22170181
147 | Bheramara 410 MW CCPP | 330 | 330 | 330 | 330 | 335 | 340 | 360 | 355 | 350 | 335 | 330 | 325 | 305 | 305 | 295 | 395 | 405 | 300 |  | 410 | 410 | 410 | 410 | 410 | 410 | 400 | 8771040
148 | Payra 1320 MW | 600 | 580 | 580 | 580 | 580 | 550 | 520 | 470 | 460 | 470 | 465 | 470 | 490 | 510 | 520 | 520 | 490 | 460 |  | 622 | 622 | 622 | 622 | 622 | 622 | 622 | 13714000
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3691000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 50 | 25 | [10 empty] | 12 | 17 | 25 | 25 | 25 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 525392
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 157 | 157 | 158 | 158 | 157 | 158 | 157 | 161 | 170 | 155 | 156 | 181 | 196 | 196 | 179 | 169 | 152 | 138 |  | 196 | 183 | 184 | 189 | 199 | 189 | 180 | 4287455
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 167 | 169 | 169 | 169 | 166 | 163 | 160 | 160 | 176 | 161 | 160 | 169 | 188 | 174 | 183 | 185 | 159 | 167 |  | 200 | 187 | 187 | 192 | 201 | 176 | 170 | 4418009
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 399 | 406 | 403 | 406 | 405 | 365 | 316 | 337 | 418 | 403 | 359 | 387 | 409 | 374 | 408 | 400 | 317 | 403 |  | 393 | 402 | 406 | 412 | 400 | 413 | 407 | 9341763
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 10 | 38 |  | 41 | 41 | 41 | 41 | 41 | 41 | 25 | 281397
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 17 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 480240
163 | Bogura 20 MW PP (Energyprima) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 7 | 7 | 7 | 7 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 221862
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 245178
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [26 empty] | 0
167 | Katakhali 50 MW Peaking PP | 36 | 36 | [14 empty] | 5 | 43 |  | 44 | 45 | 47 | 43 | 43 | 43 | 43 | 356818
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | [5 empty] | 18 | 25 | 52 | 52 | 52 | 52 | 52 | 25 | 25 | 38 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 874080
170 | Chapainawabganj 100 MW Peaking PP | 97 | 97 | 97 | 97 | 67 | [9 empty] | 3 | 48 | 40 | 80 |  | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 1168128
171 | Baghabari 200 MW PP (Paramount) | [17 empty] | 100 |  | 175 | 50 | 50 |  |  |  |  | 276774
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 50 | 35 | 35 | 35 | 50 | 90 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 2152896
172 | Confidence Power Bogura Unit-1 113 MW | 109 | 109 | 109 | 109 | 109 | 50 | 50 | 50 | 90 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 |  | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 2465472
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | [23 empty] | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 108 | 113 | 113 | 113 | 113 | 113 | 55 | 52 | 61 | 112 | 113 | 109 | 113 | 111 | 112 | 113 | 113 | 112 |  | 108 | 112 | 112 | 112 | 112 | 110 | 112 | 2538240
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 2 | 4 | 3 | 3 | 4 | 7 | 4 | 4 | 5 | 3 | 1 | 0 | [8 empty] | 38041
178
178