## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-10-02 | Friday
|  |  | Date (day): | 2020-10-02 |  | Friday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12995.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13855 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-10-01 | 2020-10-02 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 150 | 100 | 100 | 100 |  |  | Gas shortage
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 115 | 115 | 115 | 75 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 200 | 200
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 43 | 43 | 42 | 42 | 66 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under S/D for dust in gas.
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 315 | 351 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 |  |  | GT-2 under shut down
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 98 | 100 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 130 | 145 | 150 | 150 | 155 |  | GT-2 S/D for Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 97 | 97 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 32 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 86 | 100 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 100 | 195 | 200 | 200
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 84 | 93 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 115 | 150 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 47 | 47 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 28 | 33 | 33 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 16 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 51 | 52 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 300 | 300 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 212 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 50 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 101 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 131 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 82 | 80 | 85 | 86 |  | 19 | Engine problem
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 53 | 104 | 104 | 104
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 2789 | 3411 | 3305 | 3596 | 638 | 1189
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 115 | 115 | 120 | 120 | 60 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 19 | 25 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 2 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 45 | 44 | 44 | 44 | 186 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 204 | 203 | 221 | 221
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 139 | 140 | 140 | 145
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 9 | 102 | 100 | 100
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 50 | 30 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 100 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 20 | 21 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 30 | 40 | 40
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 83 | 93 | 90 | 90 |  | 18 | Engine problem
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 124 | 162 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 1108 | 1268 | 1740 | 1720 | 426 | 116
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 100 | 80 | 80 |  | 54 | Engine problem
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 182 | 176 | 225 | 225 |  |  | FGMO
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 310 | 360 | 360 |  |  | FGMO
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maintenance
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 29 | 30 | 30 | 15 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 54 | 51 | 55 | 55
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 26 | 26 | 26 | 26 | 169 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 30 | 30 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 49 | 0 | 50
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 85 | 85 | 100 | 100 |  | 63 | ST under shut down
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 30 | 200 | 200 | 200
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 108 | 150 | 162 | 173
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 50 | 52 | 52 | 52
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 20 | 21 | 21
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 50 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 70 | 100 | 114 | 114
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 103 | 104 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1232 | 1642 | 1798 | 2059 | 448 | 484
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 121 | 158 | 160 | 160 | 42 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 14 | 14 | 17 | 17 |  | 5 | Engine problem
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 0 | 0 | 0 |  | 95 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 192 | 200 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 95 | 115 | 115
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 443 | 467 | 493.6 | 492 | 42 | 100
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 60 | 60 | 60
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 35 | Unit-4 under shut down
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 0 | 0 |  | 163 | Under Maintenance
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 190 | 140 | 200 | 200 |  | 110 | ST Under maint.
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 40 | 46 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 65 | 65 | 65
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 88 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 140 | 140 | 100 | 100 |  |  | Machine problem
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 25 | 25
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 270 | 290 | 341 | 341 |  |  | FGMO
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 142 | 208 | 50 | 80 |  | 320 | Testing for combined cycle
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 150 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1412 | 1346 | 1091 | 1121 | 0 | 628
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 925 | 917 | 935 | 935
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 81 | 115 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 17 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 230 | 225 | 225
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 375 | 345 | 410 | 410
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 40 | 40 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 53 | 70 | 90 | 90 |  | 15 | Engine problem
| 108 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1594 | 1834 | 1965 | 2121 | 0 | 15
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 110 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 24 | 38 | 33 | 33
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 60 | 0 | 0 | 0 |  | 194 | Under maintenance
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 77 | 92 | 78 | 78 |  | 17 | Engine problem
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 500 | 550 | 620 | 620
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 677 | 790 | 841 | 841 | 0 | 211
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 15 | 50 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 42 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 47 | 43 | 43
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 146 | 147 | 0 | 0 |  | 210 | Shut down for gas shortage
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 174 | 165 | 220 | 220 |  |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 192 | 198 | 220 | 220 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 0 | 0 | 414 | 414 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 34
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 21 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 10 | 10 | 10 | 10
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 10 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 52 | 52 | 52
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 98 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 100 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 35 | 35 | 100 | 113
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 109 | 70 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 762 | 1046 | 1504 | 1642 | 271 | 210
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 111 | 100 | 113
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 269 | 261 | 258 | 263 | 294 | 40
|  | Total |  |  |  |  | 20383 | 19892 | 10286 | 12065 | 12995.6 | 13855 | 2119 | 2993
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9836.7068 | 11538 | 12427.9513 | 13249.8127
| A. |  | 2020-10-01 | (Yesterday) |  |  |  |  | Thursday
| 1 | Highest Generation : |  |  | 12065 | MW at | 20:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
| 2 | Minimum Generation : |  |  | 9083 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12065 | MW
| 3 | Day peak Generation : |  |  | 10286 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11538 | MW
| 4 | Evening peak Generation : |  |  | 12065 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 254.8245 | MKWHr | By Solar | 0.11247 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 126.5878 | MKWHr |  | By Oil: | 84.6037 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 17.2236 | MKWHr |  | By Hydro: | 0.97542 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2119 | MW | Dhaka | 3992 | 3992 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2993 | MW | Chittagong | 1260 | 1260 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5112 | MW | Khulna | 1435 | 1435 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1131.2 | MMCFD |  |  | Rajshahi | 1163 | 1163 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 152244826.89 | ii) Oil : | Taka | 707220560.95 | Comilla | 1161 | 1161 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 79418896 | Total | Taka | 938884283.84 | Mymensingh | 925 | 925 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.017 | MKWHr. | Sylhet | 521 | 521 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 20 | MW (E to W) at | 20:00 | hrs | Barisal | 345 | 345 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 20 | MW at | 20:00 | hrs | Rangpur | 736 | 736 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 32.9° C |  |  | Total | 11538 | 11538 |  | 0
| B. |  | 2020-10-02 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 32.9° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 11500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13855 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 8800 | MW
| 4 | Reserve(Generation end) |  |  |  | 2355 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 242.8912 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8148 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.1113 | MKWHr. | ii) HVDC Flow at Peak Time |  | 917 | MW at | 20:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.2102 | MKWHr. | iii) Maximum HVDC Flow : |  | 926 | MW at | 3:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 98.6 |  | (b) Today: | 98.73 |  | (c) Rule Curve: |  | 106.09
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-10-01
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 150 | 115 | 200 | 42 | 0 | 0 | 355 |  | 0 | 420 | 130 | 100 | 97 | 55 | 0 | 0 | 120 | 0 | 100 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 16 | 52 | 0 | 43 | 0 | 120 | 0 | 25 | 203 | 0 | 139 | 0 |  | 0 | 0 | 44 | 30 | 91 | 50 | 18 | 42 | 0 | 0 | 80 | 275 | 0 | 216 | 26 | 86 | 29 | 55 | 0 | 51 | 0 | 50 | 52 | 18 | 8 | 33 | 21 | 148 | 156 | 0 | 14 | 0 | 60 | 30 | 53 | 47 | 163 | 185 | 64 | 88 | 0 | 140 | 18 | 0 | 10 | 275 | 24 | 8 | 0 | 300 | 0 | 0 | 192 | 0 | 149 | 0 | 100 | 103 | 30 | 140 | 108 | 80 | 0 | 0 | 162 | 54 | 0 | 100 | 103 | 100 | 0 | 53 |  | 925 | 0 | 310 | 0 | 115 | 228 | 0 | 0 | 0 | 0 | 40 | 60 | 38 | 64 | 0 | 0 | 0 | 50 | 12 | 97 | 0 | 0 | 43 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 115 | 0 | 133 | 0 | 92 | 10 | 130 | 0 | 231 | 72 | 0 | 113 | 0 | 113 | 0 | 0 | 109 | 560 |  | 7529 | 3904 | 11433 | 3553 | 925 | 2019 | 3361 | 710 | 43 | 674 | 148 | 0 | 0 | 98.55
2:00 | 0 | 0 | 150 | 115 | 200 | 42 | 0 | 0 | 320 |  | 0 | 400 | 145 | 100 | 97 | 45 | 0 | 0 | 120 | 0 | 100 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 16 | 0 | 0 | 43 | 0 | 120 | 0 | 0 | 202 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 91 | 50 | 18 | 42 | 0 | 0 | 80 | 280 | 0 | 215 | 26 | 96 | 29 | 55 | 0 | 51 | 0 | 0 | 52 | 18 | 8 | 33 | 21 | 144 | 156 | 0 | 14 | 0 | 60 | 30 | 53 | 47 | 163 | 192 | 62 | 88 | 0 | 140 | 18 | 0 | 10 | 275 | 24 | 8 | 0 | 300 | 0 | 0 | 194 | 0 | 149 | 0 | 100 | 0 | 30 | 140 | 105 | 80 | 0 | 0 | 162 | 54 | 0 | 100 | 105 | 100 | 0 | 45 |  | 925 | 0 | 320 | 0 | 115 | 228 | 0 | 0 | 0 | 0 | 40 | 60 | 36 | 32 | 0 | 0 | 0 | 50 | 0 | 97 | 0 | 0 | 0 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 115 | 0 | 132 | 0 | 93 | 0 | 130 | 0 | 232 | 72 | 0 | 113 | 0 | 113 | 0 | 0 | 109 | 570 |  | 7182 | 3826 | 11008 | 3580 | 925 | 1964 | 3107 | 720 | 43 | 525 | 144 | 0 | 0 | 98.56
3:00 | 0 | 0 | 150 | 115 | 200 | 42 | 0 | 0 | 320 |  | 0 | 400 | 130 | 100 | 97 | 55 | 0 | 0 | 120 | 0 | 100 | 93 | 114 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 16 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 97 | 50 | 18 | 42 | 0 | 0 | 80 | 275 | 0 | 216 | 26 | 86 | 29 | 54 | 0 | 51 | 0 | 0 | 52 | 18 | 8 | 33 | 21 | 142 | 161 | 0 | 14 | 0 | 60 | 30 | 53 | 47 | 163 | 188 | 62 | 88 | 0 | 140 | 18 | 0 | 10 | 285 | 24 | 8 | 0 | 300 | 0 | 0 | 194 | 0 | 148 | 0 | 100 | 0 | 30 | 140 | 105 | 80 | 0 | 0 | 162 | 54 | 0 | 60 | 105 | 100 | 0 | 46 |  | 926 | 0 | 330 | 0 | 115 | 190 | 0 | 0 | 0 | 0 | 0 | 60 | 37 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 115 | 0 | 132 | 0 | 93 | 0 | 130 | 0 | 231 | 55 | 0 | 113 | 0 | 111 | 0 | 0 | 109 | 560 |  | 7101 | 3565 | 10666 | 3578 | 926 | 1973 | 2941 | 710 | 42 | 354 | 142 | 0 | 0 | 98.57
4:00 | 0 | 0 | 150 | 115 | 200 | 42 | 0 | 0 | 320 |  | 0 | 400 | 140 | 100 | 97 | 55 | 0 | 0 | 120 | 0 | 100 | 93 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 16 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 97 | 0 | 18 | 42 | 0 | 0 | 80 | 275 | 0 | 215 | 26 | 95 | 29 | 55 | 0 | 51 | 0 | 0 | 52 | 18 | 8 | 33 | 21 | 138 | 161 | 0 | 14 | 0 | 60 | 30 | 52 | 47 | 163 | 197 | 62 | 88 | 0 | 140 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 300 | 0 | 0 | 193 | 0 | 149 | 0 | 100 | 0 | 30 | 140 | 105 | 80 | 0 | 0 | 162 | 54 | 0 | 0 | 105 | 100 | 0 | 53 |  | 926 | 0 | 350 | 0 | 115 | 160 | 0 | 0 | 0 | 0 | 0 | 60 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 115 | 0 | 130 | 0 | 93 | 0 | 130 | 0 | 230 | 55 | 0 | 113 | 0 | 110 | 0 | 0 | 109 | 560 |  | 6954 | 3504 | 10458 | 3613 | 926 | 1982 | 2831 | 710 | 42 | 216 | 138 | 0 | 0 | 98.57
5:00 | 0 | 0 | 150 | 115 | 200 | 42 | 0 | 0 | 320 |  | 0 | 400 | 150 | 100 | 97 | 55 | 0 | 0 | 120 | 0 | 100 | 93 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 16 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 211 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 97 | 0 | 18 | 42 | 0 | 0 | 80 | 295 | 0 | 214 | 26 | 96 | 29 | 55 | 0 | 51 | 0 | 0 | 25 | 18 | 8 | 33 | 21 | 136 | 157 | 0 | 14 | 0 | 60 | 30 | 50 | 47 | 130 | 200 | 62 | 88 | 0 | 140 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 300 | 0 | 0 | 193 | 0 | 149 | 0 | 100 | 0 | 30 | 140 | 105 | 49 | 0 | 0 | 162 | 54 | 0 | 0 | 98 | 100 | 0 | 53 |  | 925 | 0 | 350 | 0 | 83 | 160 | 0 | 0 | 0 | 0 | 0 | 60 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 115 | 0 | 130 | 0 | 93 | 0 | 130 | 0 | 232 | 55 | 0 | 113 | 0 | 94 | 0 | 0 | 109 | 560 |  | 6857 | 3432 | 10289 | 3640 | 925 | 1948 | 2728 | 710 | 42 | 160 | 136 | 0 | 0 | 98.59
6:00 | 0 | 0 | 150 | 115 | 200 | 42 | 0 | 0 | 320 |  | 0 | 400 | 125 | 100 | 97 | 15 | 0 | 0 | 120 | 0 | 100 | 60 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 22 | 25 | 28 | 33 | 16 | 0 | 0 | 43 | 0 | 120 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 87 | 0 | 18 | 42 | 0 | 0 | 80 | 275 | 0 | 217 | 26 | 85 | 29 | 55 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 21 | 130 | 161 | 0 | 14 | 0 | 60 | 30 | 50 | 47 | 130 | 185 | 62 | 88 | 0 | 140 | 18 | 0 | 10 | 275 | 24 | 8 | 0 | 245 | 0 | 0 | 194 | 0 | 149 | 0 | 100 | 0 | 30 | 140 | 85 | 16 | 0 | 0 | 162 | 54 | 0 | 0 | 99 | 100 | 0 | 53 |  | 925 | 0 | 350 | 0 | 28 | 160 | 0 | 0 | 0 | 0 | 0 | 60 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 135 | 0 | 130 | 0 | 93 | 0 | 146 | 0 | 119 | 55 | 0 | 0 | 0 | 77 | 0 | 0 | 109 | 540 |  | 6504 | 3146 | 9650 | 3629 | 925 | 1806 | 2267 | 690 | 43 | 160 | 130 | 0 | 0 | 98.6
7:00 | 0 | 0 | 150 | 115 | 200 | 42 | 0 | 0 | 280 |  | 0 | 370 | 145 | 100 | 97 | 15 | 0 | 0 | 76 | 0 | 100 | 60 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 55 | 22 | 25 | 28 | 33 | 16 | 0 | 0 | 43 | 0 | 120 | 0 | 0 | 204 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 51 | 0 | 18 | 34 | 0 | 0 | 80 | 285 | 0 | 215 | 26 | 96 | 26 | 55 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 21 | 120 | 156 | 0 | 0 | 0 | 60 | 30 | 50 | 47 | 130 | 195 | 62 | 88 | 0 | 140 | 18 | 0 | 10 | 265 | 24 | 8 | 0 | 195 | 0 | 0 | 193 | 0 | 121 | 5 | 50 | 0 | 30 | 140 | 45 | 16 | 0 | 1 | 124 | 54 | 0 | 0 | 97 | 100 | 0 | 53 |  | 925 | 0 | 355 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 60 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 147 | 0 | 132 | 0 | 93 | 0 | 166 | 0 | 0 | 53 | 0 | 0 | 0 | 81 | 0 | 1 | 109 | 470 |  | 6114 | 2969 | 9083 | 3633 | 925 | 1597 | 1978 | 620 | 43 | 160 | 120 | 7 | 0 | 98.62
8:00 | 0 | 0 | 150 | 115 | 200 | 43 | 0 | 0 | 280 |  | 0 | 370 | 140 | 98 | 97 | 15 | 0 | 0 | 76 | 0 | 100 | 60 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 25 | 23 | 33 | 16 | 0 | 0 | 43 | 0 | 120 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 54 | 1 | 18 | 8 | 0 | 0 | 80 | 280 | 0 | 190 | 26 | 96 | 26 | 55 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 21 | 120 | 156 | 0 | 0 | 0 | 60 | 30 | 50 | 47 | 130 | 200 | 65 | 85 | 0 | 140 | 18 | 0 | 10 | 300 | 16 | 8 | 0 | 205 | 0 | 0 | 193 | 0 | 113 | 0 | 100 | 0 | 30 | 140 | 48 | 16 | 0 | 2 | 124 | 54 | 0 | 0 | 99 | 100 | 0 | 53 |  | 925 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 146 | 0 | 152 | 0 | 92 | 0 | 171 | 0 | 0 | 55 | 0 | 0 | 0 | 108 | 0 | 3 | 109 | 470 |  | 6115 | 2978 | 9093 | 3621 | 925 | 1598 | 2041 | 620 | 43 | 120 | 120 | 5 | 0 | 98.62
9:00 | 0 | 0 | 150 | 115 | 200 | 43 | 0 | 0 | 286 |  | 0 | 370 | 145 | 93 | 97 | 37 | 0 | 0 | 120 | 0 | 100 | 84 | 20 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 16 | 33 | 16 | 0 | 0 | 44 | 0 | 120 | 0 | 0 | 206 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 87 | 18 | 18 | 4 | 0 | 0 | 80 | 350 | 0 | 195 | 26 | 96 | 29 | 52 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 21 | 108 | 140 | 0 | 0 | 0 | 60 | 30 | 50 | 47 | 163 | 192 | 64 | 85 | 0 | 140 | 18 | 0 | 10 | 305 | 16 | 8 | 0 | 259 | 0 | 0 | 193 | 0 | 131 | 0 | 100 | 0 | 30 | 140 | 115 | 21 | 0 | 5 | 124 | 54 | 0 | 0 | 97 | 100 | 0 | 53 |  | 925 | 0 | 370 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 146 | 0 | 160 | 0 | 0 | 0 | 175 | 0 | 0 | 55 | 0 | 0 | 0 | 113 | 0 | 4 | 109 | 470 |  | 6569 | 2922 | 9491 | 3740 | 925 | 1546 | 2359 | 620 | 44 | 140 | 108 | 9 | 0 | 98.63
10:00 | 0 | 0 | 150 | 115 | 200 | 43 | 0 | 0 | 286 |  | 0 | 370 | 140 | 93 | 97 | 40 | 0 | 0 | 120 | 0 | 100 | 84 | 48 | 2 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 16 | 33 | 16 | 2 | 0 | 44 | 0 | 120 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 85 | 20 | 18 | 4 | 0 | 0 | 80 | 310 | 0 | 182 | 26 | 92 | 29 | 53 | 0 | 51 | 0 | 0 | 10 | 18 | 8 | 33 | 21 | 106 | 140 | 0 | 14 | 1 | 60 | 30 | 50 | 47 | 163 | 190 | 65 | 85 | 0 | 140 | 18 | 0 | 10 | 295 | 16 | 8 | 0 | 300 | 0 | 0 | 193 | 0 | 145 | 0 | 90 | 0 | 30 | 140 | 115 | 77 | 0 | 4 | 124 | 54 | 0 | 34 | 102 | 100 | 100 | 53 |  | 924 | 0 | 380 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 147 | 0 | 150 | 0 | 51 | 0 | 176 | 0 | 0 | 53 | 0 | 27 | 0 | 113 | 0 | 5 | 109 | 490 |  | 6811 | 3119 | 9930 | 3795 | 924 | 1589 | 2654 | 640 | 44 | 168 | 106 | 10 | 0 | 98.63
11:00 | 0 | 0 | 150 | 115 | 200 | 43 | 0 | 0 | 338 |  | 0 | 225 | 145 | 93 | 97 | 25 | 0 | 0 | 160 | 0 | 100 | 84 | 48 | 34 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 16 | 38 | 0 | 45 | 0 | 120 | 0 | 0 | 209 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 84 | 50 | 18 | 4 | 0 | 0 | 80 | 325 | 0 | 197 | 26 | 96 | 29 | 54 | 0 | 51 | 0 | 0 | 49 | 18 | 0 | 33 | 15 | 106 | 120 | 0 | 14 | 1 | 58 | 30 | 53 | 44 | 163 | 191 | 63 | 85 | 0 | 140 | 18 | 0 | 10 | 300 | 16 | 8 | 0 | 300 | 0 | 0 | 193 | 0 | 139 | 6 | 90 | 0 | 30 | 140 | 115 | 82 | 0 | 5 | 124 | 54 | 0 | 34 | 104 | 100 | 100 | 53 |  | 926 | 0 | 385 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 147 | 0 | 164 | 0 | 69 | 0 | 193 | 0 | 0 | 53 | 0 | 35 | 0 | 113 | 0 | 5 | 109 | 510 |  | 6908 | 3203 | 10111 | 3880 | 926 | 1520 | 2789 | 660 | 45 | 168 | 106 | 17 | 0 | 98.64
12:00 | 0 | 0 | 150 | 115 | 200 | 43 | 0 | 0 | 315 |  | 0 | 225 | 130 | 98 | 97 | 32 | 0 | 0 | 100 | 0 | 100 | 84 | 115 | 86 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 16 | 51 | 0 | 45 | 0 | 115 | 0 | 19 | 204 | 0 | 139 | 0 |  | 0 | 0 | 9 | 50 | 83 | 50 | 18 | 4 | 0 | 0 | 80 | 260 | 0 | 182 | 26 | 85 | 29 | 54 | 0 | 51 | 0 | 0 | 50 | 18 | 8 | 33 | 15 | 108 | 121 | 0 | 14 | 1 | 60 | 30 | 50 | 40 | 163 | 190 | 40 | 85 | 0 | 140 | 18 | 0 | 10 | 270 | 16 | 8 | 0 | 300 | 0 | 0 | 192 | 0 | 131 | 2 | 90 | 30 | 30 | 142 | 115 | 82 | 0 | 2 | 124 | 54 | 0 | 70 | 103 | 100 | 150 | 53 |  | 925 | 0 | 375 | 0 | 81 | 120 | 0 | 0 | 0 | 0 | 40 | 60 | 24 | 16 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 146 | 0 | 174 | 0 | 77 | 0 | 192 | 0 | 0 | 53 | 0 | 35 | 0 | 113 | 0 | 6 | 109 | 500 |  | 6984 | 3302 | 10286 | 3753 | 925 | 1468 | 3067 | 650 | 45 | 259 | 108 | 11 | 0 | 98.64
13:00 | 0 | 0 | 100 | 115 | 200 | 42 | 0 | 0 | 272 |  | 0 | 225 | 135 | 100 | 97 | 40 | 0 | 0 | 100 | 0 | 100 | 93 | 115 | 90 | 0 | 0 | 0 | 54 | 17 | 55 | 22 | 25 | 20 | 33 | 16 | 16 | 0 | 44 | 0 | 115 | 0 | 8 | 204 | 0 | 104 | 0 |  | 0 | 0 | 51 | 10 | 83 | 50 | 18 | 8 | 0 | 0 | 80 | 260 | 0 | 166 | 26 | 85 | 29 | 54 | 0 | 51 | 0 | 19 | 52 | 18 | 8 | 33 | 15 | 120 | 121 | 0 | 14 | 1 | 60 | 30 | 53 | 40 | 110 | 191 | 40 | 88 | 0 | 140 | 18 | 0 | 10 | 285 | 16 | 8 | 0 | 300 | 0 | 0 | 193 | 0 | 133 | 13 | 100 | 17 | 30 | 142 | 115 | 82 | 0 | 6 | 124 | 54 | 0 | 70 | 96 | 100 | 215 | 97 |  | 925 | 0 | 365 | 0 | 95 | 120 | 0 | 0 | 0 | 0 | 8 | 60 | 27 | 16 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 148 | 0 | 144 | 0 | 83 | 0 | 175 | 0 | 0 | 53 | 0 | 35 | 0 | 113 | 0 | 3 | 109 | 470 |  | 6905 | 3233 | 10138 | 3661 | 925 | 1405 | 2992 | 620 | 44 | 348 | 120 | 23 | 10138 | 98.65
14:00 | 0 | 0 | 100 | 115 | 200 | 41 | 0 | 0 | 303 |  | 0 | 225 | 138 | 100 | 97 | 40 | 0 | 0 | 160 | 0 | 100 | 93 | 82 | 30 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 28 | 16 | 16 | 0 | 42 | 0 | 115 | 0 | 8 | 204 | 0 | 104 | 0 |  | 0 | 0 | 51 | 10 | 84 | 50 | 18 | 8 | 0 | 0 | 80 | 260 | 0 | 170 | 26 | 92 | 29 | 52 | 0 | 51 | 0 | 25 | 16 | 18 | 8 | 33 | 9 | 124 | 121 | 0 | 14 | 0 | 58 | 30 | 25 | 20 | 140 | 190 | 50 | 40 | 0 | 100 | 18 | 0 | 10 | 295 | 24 | 8 | 0 | 300 | 0 | 0 | 193 | 0 | 141 | 4 | 100 | 17 | 30 | 142 | 65 | 82 | 0 | 1 | 124 | 54 | 0 | 34 | 104 | 100 | 267 | 104 |  | 924 | 0 | 320 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 8 | 60 | 27 | 16 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 146 | 0 | 157 | 0 | 54 | 0 | 179 | 0 | 0 | 53 | 0 | 35 | 0 | 113 | 0 | 4 | 109 | 470 |  | 6807 | 3109 | 9916 | 3718 | 924 | 1348 | 2810 | 620 | 42 | 321 | 124 | 9 | 0 | 98.66
15:00 | 0 | 0 | 100 | 115 | 200 | 41 | 0 | 0 | 341 |  | 0 | 225 | 138 | 100 | 97 | 40 | 0 | 0 | 180 | 0 | 100 | 93 | 82 | 20 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 28 | 25 | 16 | 0 | 41 | 0 | 115 | 0 | 8 | 217 | 0 | 140 | 0 |  | 0 | 0 | 51 | 10 | 90 | 50 | 19 | 4 | 0 | 0 | 80 | 345 | 0 | 199 | 26 | 96 | 29 | 49 | 0 | 51 | 0 | 25 | 16 | 18 | 0 | 22 | 9 | 126 | 158 | 0 | 14 | 0 | 58 | 30 | 42 | 30 | 163 | 141 | 63 | 88 | 0 | 140 | 18 | 0 | 10 | 310 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 143 | 11 | 100 | 17 | 30 | 142 | 65 | 80 | 0 | 1 | 124 | 49 | 0 | 40 | 101 | 100 | 261 | 104 |  | 917 | 0 | 0 | 0 | 73 | 120 | 0 | 0 | 0 | 0 | 40 | 0 | 25 | 16 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 10 | 10 | 8 | 0 | 0 | 149 | 0 | 0 | 145 | 0 | 176 | 0 | 85 | 0 | 187 | 0 | 0 | 53 | 0 | 35 | 0 | 57 | 0 | 1 | 70 | 480 |  | 7173 | 2720 | 9893 | 3577 | 917 | 1510 | 2759 | 629 | 41 | 321 | 126 | 13 | 0 | 98.66
16:00 | 0 | 0 | 100 | 115 | 200 | 43 | 0 | 0 | 322 |  | 0 | 225 | 140 | 100 | 97 | 40 | 0 | 0 | 180 | 0 | 100 | 93 | 150 | 20 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 28 | 25 | 37 | 0 | 41 | 0 | 115 | 0 | 8 | 204 | 0 | 140 | 0 |  | 0 | 0 | 51 | 10 | 82 | 50 | 20 | 4 | 0 | 0 | 100 | 265 | 0 | 177 | 26 | 86 | 29 | 47 | 0 | 51 | 0 | 25 | 52 | 18 | 8 | 33 | 20 | 130 | 161 | 0 | 14 | 0 | 59 | 30 | 47 | 42 | 110 | 142 | 66 | 88 | 0 | 140 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 300 | 0 | 0 | 180 | 0 | 139 | 7 | 100 | 36 | 30 | 142 | 30 | 80 | 0 | 0 | 161 | 36 | 0 | 52 | 97 | 100 | 266 | 104 |  | 917 | 0 | 0 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 0 | 24 | 48 | 0 | 0 | 0 | 43 | 0 | 45 | 0 | 0 | 0 | 52 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 156 | 0 | 88 | 29 | 190 | 0 | 0 | 53 | 0 | 35 | 0 | 33 | 0 | 1 | 70 | 530 |  | 7147 | 2908 | 10055 | 3484 | 917 | 1448 | 2913 | 680 | 41 | 434 | 130 | 8 | 0 | 98.66
17:00 | 0 | 0 | 100 | 115 | 200 | 43 | 0 | 0 | 323 |  | 0 | 225 | 122 | 100 | 97 | 40 | 0 | 0 | 140 | 0 | 100 | 93 | 150 | 20 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 28 | 25 | 52 | 0 | 41 | 0 | 115 | 0 | 8 | 204 | 0 | 140 | 0 |  | 0 | 0 | 51 | 10 | 88 | 50 | 20 | 12 | 0 | 0 | 100 | 260 | 0 | 177 | 26 | 85 | 29 | 47 | 0 | 51 | 0 | 24 | 52 | 18 | 8 | 33 | 20 | 140 | 160 | 0 | 14 | 0 | 58 | 30 | 53 | 45 | 110 | 140 | 65 | 40 | 0 | 140 | 18 | 0 | 10 | 270 | 24 | 8 | 0 | 300 | 0 | 0 | 180 | 0 | 149 | 1 | 100 | 68 | 30 | 142 | 30 | 80 | 0 | 0 | 162 | 39 | 0 | 52 | 110 | 100 | 0 | 104 |  | 916 | 0 | 40 | 0 | 115 | 120 | 0 | 0 | 3 | 10 | 40 | 0 | 24 | 48 | 0 | 0 | 0 | 50 | 0 | 49 | 0 | 0 | 0 | 52 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 128 | 0 | 165 | 0 | 88 | 0 | 165 | 0 | 0 | 53 | 0 | 35 | 0 | 36 | 0 | 1 | 70 | 500 |  | 6845 | 2897 | 9742 | 3189 | 916 | 1398 | 2949 | 650 | 41 | 457 | 140 | 2 | 0 | 98.67
18:00 | 0 | 0 | 100 | 115 | 200 | 43 | 0 | 0 | 338 |  | 0 | 225 | 150 | 100 | 97 | 45 | 0 | 0 | 170 | 0 | 100 | 93 | 150 | 40 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 28 | 25 | 52 | 0 | 42 | 0 | 115 | 0 | 10 | 227 | 0 | 144 | 0 |  | 0 | 0 | 102 | 10 | 97 | 50 | 20 | 12 | 0 | 0 | 100 | 350 | 0 | 208 | 26 | 96 | 29 | 50 | 0 | 51 | 0 | 46 | 52 | 18 | 8 | 33 | 20 | 172 | 157 | 0 | 14 | 0 | 58 | 30 | 53 | 45 | 110 | 142 | 61 | 40 | 0 | 120 | 18 | 0 | 10 | 265 | 24 | 11 | 66 | 300 | 256 | 0 | 165 | 58 | 149 | 0 | 100 | 73 | 30 | 140 | 41 | 80 | 0 | 0 | 162 | 54 | 0 | 88 | 100 | 100 | 0 | 104 |  | 917 | 0 | 80 | 0 | 115 | 170 | 0 | 0 | 5 | 0 | 40 | 0 | 34 | 77 | 0 | 0 | 0 | 50 | 25 | 55 | 0 | 0 | 28 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 147 | 0 | 160 | 0 | 87 | 8 | 169 | 0 | 0 | 70 | 75 | 35 | 0 | 74 | 0 | 0 | 70 | 520 |  | 7616 | 3255 | 10871 | 3417 | 917 | 1420 | 3602 | 670 | 42 | 631 | 172 | 0 | 0 | 98.67
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 100 | 115 | 200 | 43 | 0 | 0 | 353 |  | 0 | 225 | 138 | 100 | 97 | 55 | 0 | 0 | 185 | 0 | 100 | 93 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 28 | 8 | 52 | 0 | 43 | 0 | 115 | 0 | 25 | 203 | 0 | 140 | 0 |  | 0 | 0 | 102 | 10 | 97 | 50 | 20 | 22 | 0 | 0 | 100 | 310 | 0 | 176 | 26 | 86 | 29 | 51 | 0 | 51 | 0 | 49 | 52 | 18 | 8 | 33 | 20 | 146 | 160 | 0 | 14 | 0 | 60 | 30 | 50 | 46 | 163 | 140 | 65 | 88 | 0 | 140 | 18 | 0 | 10 | 260 | 24 | 11 | 100 | 300 | 248 | 50 | 200 | 99 | 149 | 0 | 100 | 176 | 30 | 142 | 95 | 80 | 0 | 0 | 162 | 54 | 0 | 100 | 109 | 100 | 0 | 104 |  | 917 | 0 | 340 | 0 | 115 | 230 | 0 | 0 | 15 | 0 | 40 | 0 | 37 | 110 | 0 | 0 | 0 | 50 | 42 | 96 | 0 | 0 | 43 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 147 | 0 | 184 | 0 | 87 | 100 | 193 | 0 | 0 | 70 | 100 | 35 | 0 | 113 | 0 | 0 | 70 | 550 |  | 8034 | 3928 | 11962 | 3642 | 917 | 1543 | 4194 | 700 | 43 | 777 | 146 | 0 | 0 | 98.68
19:30 | 0 | 0 | 100 | 115 | 200 | 43 | 0 | 0 | 351 |  | 0 | 225 | 143 | 100 | 97 | 55 | 0 | 0 | 200 | 0 | 100 | 93 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 28 | 17 | 52 | 0 | 43 | 0 | 115 | 0 | 25 | 203 | 0 | 140 | 0 |  | 0 | 0 | 102 | 30 | 90 | 50 | 20 | 25 | 0 | 0 | 100 | 310 | 0 | 184 | 26 | 95 | 29 | 51 | 0 | 51 | 0 | 49 | 52 | 18 | 8 | 33 | 20 | 144 | 158 | 0 | 14 | 0 | 60 | 30 | 50 | 46 | 163 | 140 | 65 | 88 | 0 | 140 | 18 | 0 | 10 | 300 | 24 | 11 | 50 | 300 | 206 | 50 | 200 | 101 | 149 | 0 | 100 | 200 | 30 | 142 | 108 | 80 | 0 | 0 | 162 | 54 | 0 | 100 | 113 | 100 | 0 | 104 |  | 916 | 0 | 345 | 0 | 115 | 230 | 0 | 0 | 15 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 42 | 98 | 0 | 0 | 44 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 147 | 0 | 167 | 0 | 90 | 100 | 192 | 0 | 0 | 70 | 100 | 35 | 0 | 112 | 0 | 0 | 70 | 550 |  | 8081 | 3920 | 12001 | 3668 | 916 | 1588 | 4162 | 700 | 43 | 780 | 144 | 0 | 0 | 0
20:00 | 0 | 0 | 100 | 115 | 200 | 43 | 0 | 0 | 351 |  | 0 | 225 | 145 | 100 | 97 | 55 | 0 | 0 | 195 | 0 | 100 | 93 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 28 | 33 | 52 | 0 | 44 | 0 | 115 | 0 | 25 | 203 | 0 | 140 | 0 |  | 0 | 0 | 102 | 30 | 93 | 50 | 20 | 30 | 0 | 0 | 100 | 310 | 0 | 176 | 26 | 85 | 29 | 51 | 0 | 51 | 0 | 49 | 52 | 18 | 8 | 33 | 20 | 150 | 158 | 0 | 14 | 0 | 60 | 30 | 53 | 46 | 163 | 140 | 65 | 88 | 0 | 140 | 18 | 0 | 10 | 290 | 24 | 11 | 50 | 300 | 212 | 50 | 200 | 101 | 149 | 0 | 100 | 200 | 30 | 208 | 95 | 80 | 0 | 0 | 162 | 54 | 0 | 100 | 104 | 100 | 0 | 104 |  | 917 | 0 | 345 | 0 | 115 | 230 | 0 | 0 | 17 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 42 | 98 | 0 | 0 | 47 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 147 | 0 | 165 | 0 | 92 | 100 | 198 | 0 | 0 | 70 | 100 | 35 | 0 | 111 | 0 | 0 | 70 | 550 |  | 8134 | 3931 | 12065 | 3731 | 917 | 1588 | 4150 | 700 | 44 | 785 | 150 | 0 | 0 | 98.68
21:00 | 0 | 0 | 100 | 115 | 200 | 43 | 0 | 0 | 350 |  | 0 | 225 | 150 | 100 | 97 | 55 | 0 | 0 | 185 | 0 | 100 | 100 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 52 | 0 | 44 | 0 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 102 | 30 | 98 | 50 | 20 | 35 | 0 | 0 | 100 | 330 | 0 | 186 | 26 | 96 | 29 | 52 | 0 | 51 | 0 | 49 | 52 | 18 | 8 | 33 | 20 | 146 | 158 | 0 | 14 | 0 | 60 | 30 | 53 | 46 | 163 | 140 | 65 | 88 | 0 | 140 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 300 | 88 | 50 | 200 | 52 | 149 | 0 | 100 | 200 | 30 | 177 | 64 | 90 | 0 | 0 | 162 | 54 | 0 | 100 | 105 | 100 | 0 | 104 |  | 917 | 0 | 345 | 0 | 115 | 230 | 0 | 0 | 22 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 43 | 98 | 0 | 0 | 43 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 146 | 0 | 166 | 0 | 94 | 100 | 190 | 0 | 0 | 70 | 50 | 35 | 0 | 113 | 0 | 0 | 109 | 580 |  | 7914 | 3948 | 11862 | 3728 | 917 | 1595 | 3915 | 730 | 44 | 787 | 146 | 0 | 0 | 98.69
22:00 | 0 | 0 | 100 | 115 | 200 | 43 | 0 | 0 | 350 |  | 0 | 225 | 150 | 100 | 97 | 55 | 0 | 0 | 190 | 0 | 100 | 102 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 52 | 0 | 44 | 0 | 115 | 0 | 25 | 206 | 0 | 139 | 0 |  | 0 | 0 | 88 | 30 | 97 | 50 | 20 | 40 | 0 | 0 | 100 | 340 | 0 | 190 | 26 | 96 | 26 | 52 | 0 | 51 | 0 | 49 | 52 | 18 | 8 | 33 | 20 | 148 | 158 | 0 | 14 | 0 | 60 | 30 | 53 | 46 | 163 | 140 | 65 | 88 | 0 | 140 | 18 | 0 | 10 | 310 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 85 | 30 | 295 | 64 | 98 | 0 | 0 | 162 | 54 | 0 | 100 | 108 | 100 | 0 | 104 |  | 917 | 0 | 360 | 0 | 115 | 230 | 0 | 0 | 22 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 12 | 98 | 0 | 0 | 43 | 52 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 145 | 0 | 171 | 0 | 94 | 100 | 196 | 0 | 0 | 70 | 0 | 35 | 0 | 113 | 0 | 0 | 109 | 580 |  | 7770 | 3893 | 11663 | 3889 | 917 | 1621 | 3572 | 730 | 44 | 742 | 148 | 0 | 0 | 98.69
23:00 | 0 | 0 | 100 | 115 | 200 | 42 | 0 | 0 | 352 |  | 0 | 225 | 145 | 100 | 97 | 55 | 0 | 0 | 185 | 0 | 100 | 102 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 52 | 0 | 44 | 0 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 102 | 30 | 97 | 50 | 20 | 41 | 0 | 0 | 100 | 325 | 0 | 176 | 26 | 95 | 29 | 52 | 0 | 51 | 0 | 50 | 52 | 18 | 8 | 33 | 21 | 146 | 158 | 0 | 14 | 0 | 60 | 30 | 53 | 46 | 163 | 142 | 66 | 88 | 0 | 140 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 85 | 30 | 295 | 64 | 98 | 0 | 0 | 162 | 54 | 0 | 100 | 112 | 100 | 0 | 104 |  | 917 | 0 | 340 | 0 | 115 | 230 | 0 | 0 | 22 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 0 | 98 | 0 | 0 | 43 | 52 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 146 | 0 | 176 | 0 | 93 | 100 | 187 | 0 | 0 | 70 | 0 | 35 | 0 | 112 | 0 | 0 | 109 | 570 |  | 7744 | 3846 | 11590 | 3836 | 917 | 1612 | 3570 | 720 | 44 | 745 | 146 | 0 | 0 | 98.7
24:00 | 0 | 0 | 100 | 115 | 200 | 41 | 0 | 0 | 354 |  | 0 | 225 | 140 | 100 | 97 | 55 | 0 | 0 | 185 | 0 | 100 | 102 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 0 | 33 | 33 | 52 | 0 | 44 | 0 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 68 | 30 | 97 | 50 | 20 | 42 | 0 | 0 | 100 | 325 | 0 | 176 | 26 | 86 | 29 | 54 | 0 | 51 | 0 | 0 | 52 | 18 | 8 | 33 | 21 | 142 | 158 | 0 | 14 | 0 | 60 | 30 | 53 | 47 | 163 | 140 | 67 | 88 | 0 | 140 | 18 | 0 | 10 | 270 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 16 | 30 | 296 | 64 | 98 | 0 | 0 | 162 | 54 | 0 | 100 | 106 | 100 | 0 | 104 |  | 917 | 0 | 340 | 0 | 115 | 230 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 0 | 98 | 0 | 0 | 43 | 52 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 147 | 0 | 177 | 0 | 94 | 50 | 176 | 0 | 95 | 70 | 0 | 35 | 0 | 63 | 0 | 0 | 90 | 580 |  | 7520 | 3803 | 11323 | 3796 | 917 | 1683 | 3372 | 730 | 44 | 639 | 142 | 0 | 0 | 98.7
KWH | 0 | 0 | 3029000 | 2740500 | 4769700 | 1020363 | 0 | 0 | 7703000 |  | 0 | 6641300 | 3362851 | 2399040 | 2336640 | 1070294 | 0 | 0 | 3641000 | 0 | 2408640 | 2170800 | 2302560 | 985918 | 0 | 0 | 0 | 1228680 | 1239002 | 1304334 | 475560 | 600000 | 523800 | 801100 | 528100 | 678048 | 0 | 975420 | 0 | 2800000 | 0 | 283307 | 4859143 | 0 | 3240192 | 0 |  | 0 | 0 | 996508 | 335040 | 2107440 | 916800 | 428976 | 561120 | 0 | 0 | 2083744 | 7377700 | 0 | 4692000 | 652363 | 2180760 | 674424 | 1264320 | 0 | 1246131 | 0 | 482240 | 929002 | 421020 | 174420 | 798400 | 474110 | 3210240 | 3497400 | 0 | 279396 | 5500 | 1417000 | 736080 | 1188600 | 1058400 | 3601800 | 3939000 | 1453632 | 1944960 | 0 | 3265280 | 415000 | 0 | 248220 | 7144300 | 509184 | 213048 | 237504 | 6997852 | 717785 | 182835 | 4608000 | 341806 | 3450528 | 51165 | 2318400 | 1370880 | 791200 | 3832000 | 2088000 | 1740852 | 0 | 24360 | 3599291 | 1263668 | 0 | 1388520 | 2478840 | 2432640 | 1361500 | 1940160 |  | 22111272 | 0 | 7328736 | 0 | 2032320 | 4081920 | 0 | 0 | 88320 | 3840 | 495000 | 872000 | 725258 | 1038528 | 0 | 0 | 0 | 672448 | 209237 | 998216 | 0 | 0 | 320831 | 736800 | 0 | 471360 | 237096 | 245610 | 0 | 0 | 3696400 | 0 | 0 | 3440800 | 0 | 3949627 | 0 | 1962595 | 727680 | 4331191 | 0 | 516500 | 1466112 | 369526 | 1222752 | 0 | 2323200 | 0 | 31445 | 2331072 | 13527200 |  | 172259636 | 82564892 | 254824528 | 88400133 | 22111272 | 38187686 | 74447587 | 17223600 | 975420 | 10156120 | 3210240 | 112470 | 0
Fuel Cost | 0 | 0 | 4422340 | 4028535 | 5294367 | 1346879.16 | 0 | 0 | 7934090 |  | 0 | 7239017 | 3732764.61 | 18208713.6 | 16099449.6 | 9054687.24 | 0 | 0 | 6298930 | 0 | 18137059.2 | 19797696 | 22657190.4 | 9090163.96 | 0 | 0 | 0 | 8969364 | 9577485.46 | 12860733.24 | 356670 | 450000 | 0 | 0 | 0 | 6556724.16 | 0 | 263363.4 | 0 | 5068000 | 0 | 2631922.03 | 5296465.87 | 0 | 5508326.4 | 0 |  | 0 | 0 | 9666127.6 | 3199632 | 18334728 | 7261056 | 540509.76 | 1666526.4 | 0 | 0 | 3063103.68 | 5459498 | 0 | 4316640 | 841548.27 | 2507874 | 762099.12 | 1770048 | 0 | 2130884.01 | 0 | 4870624 | 8871969.1 | 534695.4 | 130815 | 1397200 | 355582.5 | 24076800 | 3707244 | 0 | 354832.92 | 87670 | 2323880 | 1177728 | 2115708 | 1651104 | 4106052 | 4096560 | 2863655.04 | 3714873.6 | 0 | 5648934.4 | 908850 | 0 | 506368.8 | 7215743 | 381888 | 161916.48 | 4039943.04 | 52903761.12 | 12187989.3 | 3057001.2 | 23961600 | 5714996.32 | 33953195.52 | 598118.85 | 18894960 | 14874048 | 5577960 | 3563760 | 19042560 | 16451051.4 | 0 | 0 | 27210639.96 | 11006548.28 | 0 | 13857429.6 | 21243658.8 | 16201382.4 | 0 | 0 |  | 127360926.72 | 0 | 7695172.8 | 0 | 15974035.2 | 56575411.2 | 0 | 0 | 926476.8 | 40243.2 | 5157900 | 985360 | 1124149.9 | 10136033.28 | 0 | 0 | 0 | 6616888.32 | 2125847.92 | 8834211.6 | 0 | 0 | 3108852.39 | 7139592 | 0 | 905011.2 | 367498.8 | 185926.77 | 0 | 0 | 20034488 | 0 | 0 | 4025736 | 0 | 5213507.64 | 0 | 2943892.5 | 12377836.8 | 5067493.47 | 0 | 511335 | 15306209.28 | 6285637.26 | 11603916.48 | 0 | 18028032 | 0 | 347467.25 | 17226622.08 | 59384408 |  | 658002510.2 | 433616119.86 | 1091618630.06 | 104154097.25 | 127360926.72 | 48090729.64 | 591798687.52 | 79418896 | 263363.4 | 115421873.43 | 24076800 | 1033256.1 | 0
Yesterday Day Peak | 0 | 0 | 150 | 115 | 200 | 43 | 0 | 0 | 315 |  | 0 | 225 | 130 | 98 | 97 | 32 | 0 | 0 | 100 | 0 | 100 | 84 | 115 | 86 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 16 | 51 | 0 | 45 | 0 | 115 | 0 | 19 | 204 | 0 | 139 | 0 |  | 0 | 0 | 9 | 50 | 83 | 50 | 18 | 4 | 0 | 0 | 80 | 260 | 0 | 182 | 26 | 85 | 29 | 54 | 0 | 51 | 0 | 0 | 50 | 18 | 8 | 33 | 15 | 108 | 121 | 0 | 14 | 1 | 60 | 30 | 50 | 40 | 163 | 190 | 40 | 85 | 0 | 140 | 18 | 0 | 10 | 270 | 16 | 8 | 0 | 300 | 0 | 0 | 192 | 0 | 131 | 2 | 90 | 30 | 30 | 142 | 115 | 82 | 0 | 2 | 124 | 54 | 0 | 70 | 103 | 100 | 150 | 53 |  | 925 | 0 | 375 | 0 | 81 | 120 | 0 | 0 | 0 | 0 | 40 | 60 | 24 | 16 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 146 | 0 | 174 | 0 | 77 | 0 | 192 | 0 | 0 | 53 | 0 | 35 | 0 | 113 | 0 | 6 | 109 | 500 |  | 10286 | DayPeak
Yesterday Evening Peak | 0 | 0 | 100 | 115 | 200 | 43 | 0 | 0 | 351 | 0 | 0 | 225 | 145 | 100 | 97 | 55 | 0 | 0 | 195 | 0 | 100 | 93 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 28 | 33 | 52 | 0 | 44 | 0 | 115 | 0 | 25 | 203 | 0 | 140 | 0 | 0 | 0 | 0 | 102 | 30 | 93 | 50 | 20 | 30 | 0 | 0 | 100 | 310 | 0 | 176 | 26 | 85 | 29 | 51 | 0 | 51 | 0 | 49 | 52 | 18 | 8 | 33 | 20 | 150 | 158 | 0 | 14 | 0 | 60 | 30 | 53 | 46 | 163 | 140 | 65 | 88 | 0 | 140 | 18 | 0 | 10 | 290 | 24 | 11 | 50 | 300 | 212 | 50 | 200 | 101 | 149 | 0 | 100 | 200 | 30 | 208 | 95 | 80 | 0 | 0 | 162 | 54 | 0 | 100 | 104 | 100 | 0 | 104 |  | 917 | 0 | 345 | 0 | 115 | 230 | 0 | 0 | 17 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 42 | 98 | 0 | 0 | 47 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 147 | 0 | 165 | 0 | 92 | 100 | 198 | 0 | 0 | 70 | 100 | 35 | 0 | 111 | 0 | 0 | 70 | 550 |  | 12065 | EvPeak
Forecast for Evening | 0 | 0 | 100 | 115 | 200 | 42 | 0 | 0 | 360 | 0 | 0 | 225 | 150 | 100 | 100 | 55 | 0 | 0 | 200 | 0 | 100 | 102 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 44 | 0 | 120 | 0 | 25 | 221 | 0 | 145 | 0 | 0 | 0 |  | 100 | 100 | 90 | 50 | 21 | 40 | 0 | 0 | 80 | 360 | 0 | 225 | 26 | 100 | 30 | 55 | 0 | 51 | 0 | 50 | 52 | 18 | 8 | 33 | 21 | 173 | 160 | 0 | 17 | 0 | 60 | 30 | 51 | 44 | 0 | 200 | 65 | 86 | 0 | 100 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 80 | 115 | 86 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 104 |  | 935 | 16 | 410 | 0 | 115 | 225 | 0 | 0 | 30 | 60 | 40 | 0 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 0 | 0 | 43 | 52 | 34 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 | 0 | 78 | 100 | 220 | 0 | 414 | 90 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620
Forecast for Day | 0 | 0 | 100 | 115 | 200 | 42 | 0 | 0 | 360 | 0 | 0 | 225 | 150 | 100 | 100 | 55 | 0 | 0 | 200 | 0 | 100 | 102 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 44 | 0 | 120 | 0 | 25 | 221 | 0 | 140 | 0 | 0 | 0 |  | 100 | 100 | 90 | 50 | 21 | 40 | 0 | 0 | 80 | 360 | 0 | 225 | 26 | 100 | 30 | 55 | 0 | 51 | 0 | 0 | 52 | 18 | 8 | 33 | 21 | 162 | 160 | 0 | 17 | 1.6 | 60 | 30 | 51 | 44 | 0 | 200 | 65 | 86 | 0 | 100 | 18 | 0 | 10 | 341 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 200 | 150 | 50 | 115 | 85 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 104 |  | 935 | 0 | 410 | 0 | 115 | 225 | 0 | 0 | 0 | 0 | 40 | 0 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 52 | 0 | 22 | 10 | 10 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 |  | 78 | 50 | 220 | 0 | 414 | 90 | 100 | 100 | 100 | 100 | 0 | 8 | 113 | 620
Generation at 08:00(Today) | 0 | 0 | 100 | 115 | 200 | 42 | 0 | 0 | 303 | 0 | 0 | 225 | 138 |  | 80 | 40 | 0 | 0 | 188 | 0 | 89 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 22 | 25 | 23 | 33 | 33 | 0 | 0 | 43 | 0 | 115 | 0 | 0 | 203 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 20 | 42 | 0 | 0 | 80 | 275 | 0 | 178 | 26 | 85 | 20 | 55 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 21 | 96 | 158 | 0 | 14 | 0 | 60 | 30 | 50 | 47 | 0 | 142 | 65 | 85 | 0 | 80 | 18 | 0 | 10 | 280 | 16 | 8 | 0 | 60 | 0 | 0 | 200 | 0 | 112 | 5 | 10 | 0 | 30 | 299 | 16 | 0 | 0 | 2 | 34 | 18 | 0 | 0 | 113 | 70 | 0 | 104 | 0 | 925 | 0 | 225 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 156 | 0 | 89 | 0 | 146 | 0 | 302 | 70 | 0 | 0 | 0 | 34 | 0 | 2 | 35 | 330 | 0
199
| Minimum Generation |  | 9083 | 7:00
| Highest Generation |  | 12065 | 20:00
| Day Peak Generation |  | 10286 | 12:00
| Evening Peak Generation |  | 12065 | 20:00
| HVDC Max Flow |  | 926 | 3:00
| HVDC EvPeak Flow |  | 917 | 20:00
| Load factor L.F |  | 88%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-10-02
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-10-01 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10286 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 8148 | MW
Evening Peak Generation : |  | 12065 | MW Hour : | 20:00 | Available Max Generation : |  | 13855 | MW
E.P. Demand (at gen end) : |  | 12065 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 11500 | MW
Maximum Generation : |  | 12065 | MW Hour : | 20:00 | Reserve(Generation end) |  | 2355 | MW
Total Gen. (MKWH) : |  | 254.8245 | System Load Factor : | 88% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 20 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-10-02
Actual : | 98.73 | Ft.(MSL) , | Rule curve : | 106.09 | Ft.( MSL )
Gas Consumed : | Total = | 1131.2 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 152244826.89
: |  | Coal : | 79418896 | Oil : | 707220560.95 | Total : | 938884283.84
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4092.7094 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1392.7973 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1248.0872 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1127.8185 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1019.1566 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 822.426 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 458.5095 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 211.7168 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 634.3022 |  |  | 0 | 0%
Total | 0 |  | 11007.5234 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ashuganj (S)-360 MW
3) Ghorasal Unit-1,2,3,
4) Ashuganj unit-3,4
5) Kaptai-2,4,5
6) Raozan #1,2
7) Siddirganj-335 MW
8) Baghabari-71 MW,100 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Bogura 132/33 kV T-3 transformer was under shut down from10:08 to 11:40 for R/H maintenance at
132 kV Ct terminal.
b) Bogura 132/33 kV T-4 transformer was under shut down from11:43 to 12:55 for R/H maintenance at
132 kV Ct terminal and 33 kV breaker pole.
c) Bibiyana S/S 230 kV dia-2 mid breaker was under shut down from 11:31 to 12:25 for SF6 gas leakage
maintenance.
d) Haripur-Meghnaghat 230 kV Ckt-1 was shut down at 08:30 for A/M.
e) Mymensingh S/S-RPCL 132 kV Ckt-1 was under shut down from 08:41 to 13:48 for C/M.
f) Shahjibazar 132/33 kV Tr-6 transformer was under shut down from 10:01 to 09:53(02/10/20200 for C/M.
g) Dhamrai 132/33 kV T-2 transformer was under shut down from 09:14 to 11:33 for C/M.
h) Meghnaghat 450 MW GT-2 was shut down at 10:56 for high pressure steam line leakage.
i) Kallyanpur 132/33 kV GT-2 transformer bay was shut down at 13:11 for C/M.
j) Mymensingh-Netrokona 132 kV Ckt-2 was under shut down from 13:33 to 16:59 for C/M.
k) Bheramara-Bottail 132 kV Ckt-1 tripped at 14:34 due to LA burst, B-phase at Bheramara S/S and was
switched on 16:03.
l) Bheramara-Ishurdi 132 kV Ckt-1 tripped at 14:34 due to LA burst, B-phase at Bheramara S/S
showing CAS,CAR,CSW,CD relay at Ishurdi end and was switched on at 19:22.
m) Ishurdi-Natore 132 kV Ckt-1 tripped at 14:35 showing Dist. S,T,Z2 relay and was switched on at 14:46.
n) Bheramara-Ishurdi 132 kV Ckt-2 tripped at 14:34 showing CAT,CD,CSN relay at Ishurdi end and
was switched on at 16:12.
o) Bheramara 410 MW tripped at 14:34 showing negative phase sequence and GT was synchronized at
16:54 and STG was synchronized at 18:03.
p) Bhola 225 MW GT-1 tripped at 14:35 due to rapid frequency variation.
q) Baghabari 230/132 kV T01 transformer tripped at 15:51 showing Gen. trip, mechanical protection operated
and was switched on at 19:32.
r) Ishurdi 132 kV Bus-2 was under shut down from 16:00 to 19:01 to attend DS loop of 132 kV
Bheramara-Ishurdi 132 kV Ckt-1.
s) Tongi 33 kV Bus under 132/33 kV T-3 transformer was under shut down from 21:30 to 22:45 for R/H |  |  |  |  | About 20 MW power interruption occurred under Tongi S/S area
maintenance at Bus coupler. |  |  |  |  | from 21:30 to 22:45.
t) Chowmuhani 33 kV Bus under 132/33 kV T-2 transformer was under shut down from 21:27 to 23:30 for |  |  |  |  | About 86 MW power interruption occurred under Chowmuhani S/S area
R/H maintenance at CT. |  |  |  |  | from 21:27 to 23:30.
u) Rampura 23/132 kV T01 transformer was shut down at 06:20(02/10/20200 for C/M.
v) Daudkandi 132/33 kV T-1 transformer was shut down at 07:04(02/10/2020) for C/M.
w) Sirajganj unit-4 GT was synchronized at 23:08 and STG was synchronized at 00:59(02/10/2020).
x) Bheramara-Faridpur 132 kV Ckt-2 and Bheramara 132 kV Bus-A were under shut down from 07:05(02/10/2020)
to 10:20 for C/M.
y) Kaliakoir-Tangail 132 kV Ckt-2 tripped at 02:16(02/10/2020) from Tangail end showing Dist. R, AR block,
67N relay and was switched on at 04:04.
z) Kushiara 163 MW was shut down at 00:43(02/10/2020) for maintenance.
aa) Khulshi 132/33 kV T-2 transformer was shut down at 01:20(02/10/2020) for C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-10-01 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 100 | 3029000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 115 | 2740500 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 4769700 | Machin problem.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 43 | 1020363 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 351 | 7703000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 6641300 | GT-2 Under maint.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 2399040
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 145 | 3362851 | GT-2 Under S/D due to gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 97 | 2336640
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1070294
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 100 | 985918
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 475560
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 195 | 3641000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 2408640
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under Maintenance
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 2170800 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel Shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1228680
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 2302560
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1239002
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1304334
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 47 | 1123800 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 28 | 801100
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 528100 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 52 | 678048
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 6997852
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 212 | 717785 | Low demand.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 50 | 182835 | Low demand.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 101 | 341806
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3450528
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 80 | 1740852 | Engine problem
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 1940160
| Dhaka area Total |  |  |  | 5895 | 3411 | 69332048
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 115 | 2800000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 283307
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 51165
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 916800
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 44 | 975420 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4859143
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 140 | 3240192
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 996508
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 30 | 335040 | High voltage
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2318400
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 428976
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 30 | 561120
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 93 | 2107440 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 24360
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 162 | 3599291 | Low demand.
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1263668
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2432640
| Chattogram area Total |  |  |  | 2266 | 1268 | 27193470
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 100 | 2083744 | Machine problem
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 176 | 4692000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7377700 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Machine problem.
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 674424 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 51 | 1264320
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 26 | 652363 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1246131
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 30 | 791200 | R/H at APSCL
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 49 | 482240
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 85 | 2180760
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 1370880
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 421020 | Engine problem
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 174420 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 150 | 3210240
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 798400
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 929002
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 474110 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 50 | 237504 | Low demand.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 100 | 1388520 | Engine problem
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 104 | 2478840
| Cumilla Area Total |  |  |  | 2980 | 1642 | 32927818
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 158 | 3497400 | Machine problem & Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 14 | 279396 | Engine problem
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 0 | 0 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 5500
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 4608000
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 95 | 2088000 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 467 | 10478296
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1417000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 736080 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3601800
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 140 | 3939000 | Gas shortage.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1188600
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 46 | 1058400
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 213048
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 65 | 1453632
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 88 | 1944960
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 140 | 3265280
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 415000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 509184
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7144300 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 208 | 3832000
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 248220
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 1361500 | On test
| Sylhet Area Total |  |  |  | 1988 | 1346 | 32328004
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 917 | 22111272
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 2032320
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 17 | 88320
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 230 | 4081920
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 3840 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 345 | 7328736
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 495000
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 727680
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 70 | 1466112 | Engine problem
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1834 | 38335200
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1038528
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 38 | 725258
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 872000 | tripped at 14:34
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 92 | 1962595 | Engine problem
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 550 | 13527200
| Barisal Area Total |  |  |  | 1054 | 790 | 18125581
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 672448
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 42 | 209237
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel Shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel Shortage
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 47 | 320831
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 147 | 3440800 | Gas Shortage
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 165 | 3949627 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 198 | 4331191 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 0 | 516500 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 471360
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 10 | 237096
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 245610
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 736800
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 98 | 998216
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 100 | 369526 | Low demand.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 35 | 1222752
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 70 | 2331072
| Rajshahi Area Total |  |  |  | 2183 | 1046 | 20053066
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3696400 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 111 | 2323200
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 31445
| Rangpur Area Total |  |  |  | 605 | 261 | 6051045
| Total |  |  |  | 19892 | 12065 | 254824528
| Eastern Grid Total |  |  |  | 13766 | 8134 | 172259636
| Western Grid Total |  |  |  | 6126 | 3931 | 82564892
| National Grid Total |  |  |  | 19892 | 12065 | 254824528
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-10-01
| (a) ENTIRE EASTERN GRID : |  | 7859 | MW | (b) ENTIRE WESTERN GRID : |  | 3679 | MW
| i) Dhaka area |  | 3992 | MW | i) Khulna area |  | 1435 | MW
| ii) Chittagong area |  | 1260 | MW | ii) Rajshahi area |  | 1163 | MW
| iii) Comilla area |  | 1161 | MW | iii) Barisal area |  | 345 | MW
| iv) Mymensingh area |  | 925 | MW | iv) Rangpur area |  | 736 | MW
| v) Sylhet area |  | 521 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11538 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 118 | 0:00 | Sherpur | 102 | 1:00 | Jhenida | 108 | 19:00
| Munsiganj | 126 | 21:00 | Srimongal | 44 | 22:00 | Bottail | 116 | 19:30
| Sonargaon | 82 | 1:00 | Shahjibazar | 119 | 21:00 | G.K Project | 52 | 18:30
| Shyampur | 186 | 17:00 | Fenchuganj | 53 | 18:00 | Faridpur | 190 | 0.041667
| Bhulta | 191 | 22:00 | Kulawara | 44 | 18:30 | Madaripur | 100 | 0.91667
| Madanganj | 53 | 2:00 | Sylhet | 138 | 18:00 | Sariatpur | 64 | 21:00
| Shitalakhya | 118 | 13:00 | Chatak | 32 | 19:30 | Gopalganj | 85 | 20:00
| Rahim steel | 24 | 14:00 | Sunamganj | 46 | 21:00 | Bagerhat | 98 | 19:30
| Matuail | 85 | 9:00 | Biani Bazar | 63 | 21:00 | Mongla | 40 | 12:00
| Ghorasal | 79 | 19:30 | Comilla (S) | 172 | 18:00 | Satkhira | 108 | 0.875
| Narsingdi | 170 | 20:00 | Comilla(N) | 123 | 19:30 | Gallamari | 49 | 13:00
| Haripur (SBU) | 98 | 9:00 | Chandpur | 102 | 22:00 | Magura | 52 | 0.77083
| Ullon | 58 | 14:00 | Feni | 122 | 18:30 | Norail | 39 | 18:30
| Hasnabad | 205 | 21:00 | Chowmuhani | 172 | 20:00 | Chuadanga | 90 | 20:00
| Magbazar | 113 | 11:00 | Ashuganj | 64 | 20:00 | Barisal(N) | 43 | 0.91667
| Maniknagar | 96 | 18:00 | Daudkandi | 141 | 20:00 | Barisal (S) | 100 | 0.77083
| Bangabhaban | 36 | 10:00 | B.Baria | 161 | 20:00 | Patuakhali | 121 | 0.91667
| Narinda | 86 | 14:00 | Ramganj | 112 | 21:00 | Bhandaria | 54 | 0.91667
| Dhanmondi | 178 | 11:00 | Chaddagram | 37 | 21:00 | Borhan Uddin | 44 | 21:00
| Lalbag | 90 | 13:00 | PHP | 8 | 10:00 | Ishurdi | 54 | 20:00
| Madartek | 76 | 20:00 | Madunaghat | 57 | 19:30 | Ruppur Paromanobik | 2 | 2:00
| Dhaka University |  |  | Hathazari | 102 | 0.79167 | Natore | 108 | 20:00
| Fatullah | 41 | 0.375 | Khulshi | 195 | 0.5 | Bogra | 162 | 20:00
| Mirpur | 108 | 18:30 | Halishahar | 139 | 0.54167 | Noagaon | 104 | 20:00
| Kalyanpur | 90 | 19:30 | Baraulia | 161 | 0.041667 | Rajshahi | 131 | 1:00
| Gulshan | 134 | 11:00 | Sikalbaha | 27 | 0.77083 | Rajshahi New | 10 | 18:30
| Uttara | 96 | 18:00 | Dohazari | 80 | 0.77083 | C.Nawabganj | 67 | 2:00
| Uttara New | 33 | 10:00 | Cox'sbazar | 102 | 0.83333 | Amnura | 38 | 19:00
| Kamrangirchar | 92 | 18:00 | Chandraghona | 30 | 0.77083 | Pabna | 114 | 19:30
| Savar | 139 | 10:00 | Kaptai | 4.2 | 0.75 | Shahjadpur | 100 | 20:00
| Bhasantec | 154 | 13:00 | A. Khaer Stl. | 7 | 0.33333 | Serajganj | 95 | 19:30
| Agargaon | 75 | 10:00 | Bakulia | 113 | 0.66667 | Niyamatpur | 48 | 1:00
| Satmosjid | 103 | 13:00 | Julda | 22 | 0.66667 | Joypurhat | 52 | 19:30
| Tongi | 101 | 0.375 | TK chemical | 27.6 | 0.79167 | Sherpur(Bogura) | 46 | 1:00
| Kabirpur | 231 | 12:00 | Modern Steel | 13 | 0.125 | Mohastangor | 46 | 19:30
| Basundhara | 139 | 13:00 | Shahmirpur | 21.5 | 0.625 | Rangpur | 143 | 19:00
| Manikganj | 76 | 0.875 | Khagrachhari | 24 | 0.041667 | Lalmonirhat | 52 | 19:30
| Joydevpur | 141 | 13:00 | Matarbari | 37.5 | 0.875 | Saidpur | 96 | 19:30
| New Tongi | 111 | 16:00 | Baroiar Hat | 44 | 0.77083 | Purbasadipur | 97 | 20:00
| Korda | 242 | 1:00 | Rangamati | 12 | 0.77083 | Thakurgaon | 76 | 1:00
| Dhamrai | 76 | 21:00 | Abul Khair 230 | 63 | 0.375 | Palashbari | 120 | 19:00
| Rajendrapur | 94 | 21:00 | BSRM | 131 | 0.45833 | Barapukuria | 48 | 20:00
| Valuka | 130 | 11:00 | GPH Ispat | 83 | 0.70833 | Panchagar | 50 | 18:30
| Tangail | 194 | 19:30 | Goalpara | 29 | 0.041667 | Joldhaka | 24 | 1:00
| Mymensing | 156 | 1:00 | Central s/s | 78 | 18:30 | Kurigram | 56 | 19:00
| Kishorganj | 140 | 1:00 | Noapara | 56 | 18:30
| Netrokona | 113 | 18:30 | Jessore | 110 | 18:30
| Jamalpur | 144 | 1:00 | Benapol | 48 | 18:30
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-10-01 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 396 | 20:00 | 391 | 10:00 | Kaliakoir | 380 | 0.29167 | 369 | 0.45833
| Bheramara | 394 | 18:30 | 389 | 1:00 | Bhulta | 390 | 0.75 | 375 | 0.45833
| Ashuganj(N) | 394 | 17:00 | 382 | 11:00 | Gopalganj | 414 | 0.29167 | 394 | 0.95833
| Payra | 414 | 19:00 | 404 | 23:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 1:00 | 230 | 15:00 | Comilla (N) | 237 | 18:30 | 229 | 11:00
| Ishurdi | 235 | 17:00 | 227 | 15:00 | Hathazari | 227 | 17:00 | 223 | 11:00
| Ashuganj | 236 | 18:30 | 230 | 11:00 | Megnaghat | 232 | 17:00 | 223 | 10:00
| Serajganj | 232 | 5:00 | 225 | 10:00 | Fenchuganj | 238 | 18:00 | 235 | 1:00
| Baghabari | 239 | 8:00 | 236 | 14:00 | Siddhirganj | 231 | 18:30 | 221 | 11:00
| Barapukuria | 237 | 17:00 | 227 | 19:00 | Maniknagar | 229 | 6:00 | 220 | 10:00
| Bogra | 225 | 16:00 | 213 | 22:00 | Agargaon | 228 | 17:00 | 217 | 11:00
| Rajshahi | 231 | 17:00 | 219 | 19:30 | Barisal | 247 | 4:00 | 232 | 23:00
| Khulna South | 236 | 17:00 | 226 | 4:00 | AKSML | 224 | 3:00 | 220 | 17:00
| Rampura | 229 | 5:00 | 221 | 10:00 | BSRM | 226 | 3:00 | 221 | 11:00
| Haripur | 227 | 19:00 | 219 | 10:00 | Bibiyana | 237 | 3:00 | 233 | 23:00
| Hasnabad | 230 | 19:30 | 220 | 10:00 | Bhulta | 230 | 19:00 | 222 | 17:00
| Shyampur | 227 | 19:00 | 217 | 10:00 | Ashuganj (S) | 234 | 4:00 | 229 | 10:00
| Aminbazar | 224 | 8:00 | 221 | 10:00 | Kaliakoir | 232 | 3:00 | 225 | 11:00
| Tongi | 228 | 23:00 | 221 | 11:00 | GPH | 223 | 3:00 | 222 | 1:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 133 | 18:00 | 126 | 10:00 | Hathazari | 135 | 0.16667 | 132 | 0.45833
| Munsiganj | 134 | 19:00 | 128 | 10:00 | Khulshi | 133 | 0.041667 | 130 | 0.45833
| Sonargaon | 135 | 19:00 | 129 | 9:00 | Halishahar | 135 | 0.70833 | 132 | 0.41667
| Shyampur | 135 | 18:30 | 127 | 11:00 | Baraulia | 135 | 0.083333 | 131 | 0.45833
| Bhulta | 125 | 0:00 | 119 | 11:00 | Sikalbaha | 137 | 19:30 | 133 | 0.45833
| Madanganj | 132 | 17:00 | 128 | 10:00 | Dohazari | 133 | 17:00 | 128 | 0.45833
| Shitalakhya | 142 | 19:00 | 132 | 10:00 | Cox'sbazar | 126 | 0.70833 | 120 | 0.45833
| Rahim steal | 132 | 19:00 | 126 | 11:00 | Chandraghona | 135 | 0.70833 | 132 | 0.45833
| Matuail | 133 | 18:00 | 126 | 10:00 | Kaptai | 135 | 22:00 | 132 | 0.041667
| Ghorasal | 139 | 19:30 | 136 | 9:00 | A. Khaer Stl. | 135 | 0.41667 | 129 | 15:00
| Narsinghdi | 126 | 6:00 | 120 | 11:00 | Bakulia | 135 | 0.77083 | 131 | 0.45833
| Haripur (SBU) | 133 | 6:00 | 126 | 11:00 | Julda | 136 | 0.70833 | 133 | 0.16667
| Ullon | 134 | 4:00 | 128 | 10:00 | TK Chemical | 135 | 0.041667 | 129 | 7:00
| Hasnabad | 139 | 18:30 | 130 | 9:00 | Modern Steel | 135 | 0.875 | 132 | 0.25
| Magbazar | 135 | 4:00 | 125 | 13:00 | Shahmirpur | 136 | 0.91667 | 132 | 0.45833
| Maniknagar | 134 | 6:00 | 127 | 10:00 | Khagrachhari | 133 | 0.041667 | 131 | 0.41667
| Bangabhaban | 134 | 6:00 | 127 | 10:00 | Matarbari | 125 | 0.54167 | 123 | 0.041667
| Narinda | 134 | 6:00 | 127 | 10:00 | Baroiar Hat | 136 | 0.77083 | 131 | 0.041667
| Dhanmondi | 134 | 4:00 | 128 | 10:00 | Rangamati | 134 | 0.25 | 131 | 11:00
| Lalbag | 139 | 18:30 | 127 | 10:00 | Goalpara S/S | 137 | 16:00 | 132 | 2:00
| Madartek | 134 | 6:00 | 126 | 11:00 | Khulna Central S/S | 138 | 0.70833 | 131 | 4:00
| Dhaka University |  |  |  |  | Noapara | 135 | 16:00 | 127 | 3:00
| Fatuiiah | 135 | 0.79167 | 127 | 10:00 | Jessore | 131 | 17:00 | 123 | 1:00
| Mirpur | 136 | 3:00 | 128 | 10:00 | Benapol | 132 | 17:00 | 122 | 2:00
| Kalyanpur | 137 | 2:00 | 130 | 10:00 | Jhenida | 126 | 0.41667 | 117 | 19:30
| Gulshan | 134 | 6:00 | 125 | 11:00 | Bottail | 133 | 3:00 | 126 | 19:30
| Uttara | 136 | 23:00 | 128 | 10:00 | G.K Project | 140 | 0.54167 | 135 | 15:00
| Uttara New | 136 | 6:00 | 128 | 10:00 | Faridpur | 132 | 6:00 | 125 | 19:30
| Kamrangirchar | 139 | 18:00 | 126 | 10:00 | Madaripur | 138 | 0.54167 | 129 | 22:00
| Savar | 136 | 5:00 | 128 | 10:00 | Shariyatpur S/S | 137 | 0.29167 | 126 | 20:00
| Bhasantec | 137 | 4:00 | 129 | 11:00 | Gopalganj | 138 | 7:00 | 125 | 19:30
| Agargaon | 138 | 4:00 | 131 | 11:00 | Bagerhat | 132 | 13:00 | 125 | 1:00
| Satmosjid | 138 | 3:00 | 130 | 11:00 | Mongla | 129 | 0.70833 | 123 | 1:00
| Tongi | 137 | 0.95833 | 131 | 9:00 | Satkhira | 136 | 0.70833 | 128 | 1:00
| Kabirpur | 133 | 17:00 | 130 | 14:00 | Gallamari | 137 | 16:00 | 131 | 3:00
| Basundhara | 134 | 4:00 | 126 | 10:00 | Magura | 128 | 18:00 | 115 | 19:30
| Manikganj | 138 | 21:00 | 131 | 11:00 | Norail | 126 | 0.70833 | 114 | 19:30
| Joydevpur | 141 | 21:00 | 136 | 8:00 | Chuadanga | 120 | 6:00 | 107 | 19:30
| New Tongi | 137 | 0.95833 | 129 | 10:00 | Barisal(N) | 140 | 17:.00 | 131 | 3:00
| Kodda | 137 | 17:00 | 125 | 0.33333 | Barisal (S) | 138 | 0.70833 | 130 | 3:00
| Dhamrai | 133 | 13:00 | 129 | 11:00 | Patuakhali(S) | 134 | 0.29167 | 123 | 22:00
| Rajendrapur | 135 | 23:00 | 122 | 9:00 | Bhandaria | 130 | 17:00 | 120 | 1:00
| Valuka | 129 | 15:00 | 110 | 1:00 | Ishurdi | 138 | 14:00 | 133 | 19:30
| Tangail | 134 | 13:00 | 123 | 1:00 | Ruppur Paromanobik | 136 | 13:00 | 133 | 20:00
| Mymensing | 132 | 15:00 | 116 | 1:00 | Natore | 138 | 16:00 | 131 | 19:00
| Kishorganj | 132 | 17:00 | 117 | 1:00 | Bogra | 136 | 13:00 | 128 | 19:30
| Netrokona | 127 | 9:00 | 110 | 1:00 | Noagaon | 133 | 17:00 | 120 | 20:00
| Jamalpur | 139 | 13:00 | 120 | 21:00 | Rajshahi | 138 | 13:00 | 132 | 19:00
| Sherpur | 139 | 17:00 | 123 | 21:00 | Rajshahi New | 140 | 17:00 | 132 | 4:00
| Srimongal | 136 | 6:00 | 132 | 0.375 | C.Nawabganj | 136 | 13:00 | 128 | 11:00
| Shahjibazar | 136 | 7:00 | 131 | 0.041667 | Amnura | 137 | 16:00 | 131 | 3:00
| Fenchuganj | 135 | 6:00 | 131 | 0.041667 | Pabna | 136 | 17:00 | 129 | 20:00
| Khulawara | 133 | 5:00 | 131 | 0.041667 | Shahjadpur | 138 | 13:00 | 134 | 19:30
| Sylhet | 138 | 18:00 | 129 | 0.041667 | Serajganj | 134 | 17:00 | 128 | 19:30
| Chatak | 129 | 6:00 | 125 | 1:00 | Niyamatpur | 132 | 6:00 | 118 | 19:30
| Sunamganj | 129 | 17:00 | 122 | 0.041667 | Joypurhat | 135 | 16:00 | 119 | 19:30
| Biani Bazar | 131 | 10:00 | 125 | 0.041667 | Sherpur(Bogura) | 135 | 13:00 | 127 | 19:30
| Comilla(s) | 127 | 6:00 | 121 | 21:00 | Mohastangor | 136 | 16:00 | 125 | 20:00
| Comilla(n) | 141 | 18:30 | 134 | 15:00 | Rangpur | 132 | 14:00 | 117 | 20:00
| Chandpur | 140 | 1:00 | 130 | 6:00 | Lalmonirhat | 132 | 16:00 | 116 | 18:30
| Feni | 137 | 18:30 | 131 | 9:00 | Saidpur | 130 | 14:00 | 120 | 19:00
| Chowmuhani | 134 | 18:00 | 130 | 7:00 | Purbasadipur | 129 | 16:00 | 113 | 18:30
| Ashuganj | 136 | 17:00 | 133 | 2:00 | Thakurgaon | 128 | 16:00 | 115 | 19:00
| Daudkandi | 135 | 18:00 | 128 | 15:00 | Palashbari | 132 | 16:00 | 120 | 19:00
| B.Baria | 133 | 7:00 | 128 | 22:00 | Barapukuria | 137 | 17:00 | 127 | 20:00
| Ramganj | 130 | 19:30 | 123 | 24:00 | Panchagar | 126 | 17:00 | 112 | 19:00
| Chaddagram | 138 | 19:00 | 132 | 14:00 | Joldhaka | 131 | 14:00 | 115 | 19:00
| PHP | 135 | 23:00 | 129 | 15:00 | Kurigram | 130 | 14:00 | 114 | 20:00
| Madanhat | 137 | 18:30 | 134 | 10:00

## L-Curve
Date | 2020-10-01
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 128 | 7520 | 3803 | 11323 |  |  |  | QF-LDC-11
0:30 | 112 | 7524.5 | 3853.5 | 11378 | Date: | 2020-10-01
1:00 | 96 | 7529 | 3904 | 11433
1:30 | 106 | 7355.5 | 3865 | 11220.5
2:00 | 116 | 7182 | 3826 | 11008
2:30 | 98 | 7141.5 | 3695.5 | 10837 | [5 empty] | Gen. at Eve. Peak | 12065 | 9500 MW (19:30 )
3:00 | 80 | 7101 | 3565 | 10666 | [6 empty] | 20:00
3:30 | 81.5 | 7027.5 | 3534.5 | 10562 | [5 empty] | Gen. at Day Peak | 10286 | 7952.5 MW (12:00 )
4:00 | 83 | 6954 | 3504 | 10458 | [6 empty] | 12:00
4:30 | 101.5 | 6905.5 | 3468 | 10373.5 | [5 empty] | Highest Generation | 12065
5:00 | 120 | 6857 | 3432 | 10289 | [6 empty] | 20:00
5:30 | 185 | 6680.5 | 3289 | 9969.5
6:00 | 250 | 6504 | 3146 | 9650
6:30 | 228 | 6309 | 3057.5 | 9366.5
7:00 | 206 | 6114 | 2969 | 9083
7:30 | 219 | 6114.5 | 2973.5 | 9088
8:00 | 232 | 6115 | 2978 | 9093
8:30 | 223.5 | 6342 | 2950 | 9292
9:00 | 215 | 6569 | 2922 | 9491
9:30 | 291.5 | 6690 | 3020.5 | 9710.5
10:00 | 368 | 6811 | 3119 | 9930
10:30 | 405 | 6859.5 | 3161 | 10020.5
11:00 | 442 | 6908 | 3203 | 10111
11:30 | 421 | 6946 | 3252.5 | 10198.5
12:00 | 400 | 6984 | 3302 | 10286
12:30 | 423.5 | 6944.5 | 3267.5 | 10212
13:00 | 447 | 6905 | 3233 | 10138
13:30 | 430.5 | 6856 | 3171 | 10027
14:00 | 414 | 6807 | 3109 | 9916
14:30 | 313.5 | 6990 | 2914.5 | 9904.5
15:00 | 213 | 7173 | 2720 | 9893
15:30 | 259.5 | 7160 | 2814 | 9974
16:00 | 306 | 7147 | 2908 | 10055
16:30 | 333 | 6996 | 2902.5 | 9898.5
17:00 | 360 | 6845 | 2897 | 9742
17:30 | 247.5 | 7230.5 | 3076 | 10306.5
18:00 | 135 | 7616 | 3255 | 10871
18:30 | 136 | 7825 | 3591.5 | 11416.5
19:00 | 137 | 8034 | 3928 | 11962
19:30 | 62 | 8081 | 3920 | 12001
20:00 | 20 | 8134 | 3931 | 12065 |  |  |  | Executive Engineer
20:30 | 52.5 | 8024 | 3939.5 | 11963.5 |  |  |  | Network Operation Division
21:00 | 85 | 7914 | 3948 | 11862
21:30 | 86.5 | 7842 | 3920.5 | 11762.5
22:00 | 88 | 7770 | 3893 | 11663 |  |  |  |  | Page 6 of 7
22:30 | 95.5 | 7757 | 3869.5 | 11626.5
23:00 | 103 | 7744 | 3846 | 11590
23:30 | 115.5 | 7632 | 3824.5 | 11456.5
24:00 | 128 | 7520 | 3803 | 11323
9500 MW (19:30 )
7952.5 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-10-01 |  | Energy | 254824528
[10 empty] | 2020-10-01 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3796 | 917 | 1683 | 3570 | 730 | 44 | 639 | 0 | 142
0:30 | 3674.5 | 921 | 1851 | 3465.5 | 720 | 43.5 | 656.5 | 0 | 145 | Date: | 2020-10-01
1:00 | 3553 | 925 | 2019 | 3361 | 710 | 43 | 674 | 0 | 148
1:30 | 3566.5 | 925 | 1991.5 | 3234 | 715 | 43 | 599.5 | 0 | 146 | [7 empty] | Total Energy | 254.8245 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 3580 | 925 | 1964 | 3107 | 720 | 43 | 525 | 0 | 144 | [7 empty] | Energy not Served | 0
2:30 | 3579 | 925.5 | 1968.5 | 3024 | 715 | 42.5 | 439.5 | 0 | 143 | [7 empty] | Energy Requirement | 254.8245
3:00 | 3578 | 926 | 1973 | 2941 | 710 | 42 | 354 | 0 | 142
3:30 | 3595.5 | 926 | 1977.5 | 2886 | 710 | 42 | 285 | 0 | 140 | [6 empty] | Shortage
4:00 | 3613 | 926 | 1982 | 2831 | 710 | 42 | 216 | 0 | 138
4:30 | 3626.5 | 925.5 | 1965 | 2779.5 | 710 | 42 | 188 | 0 | 137
5:00 | 3640 | 925 | 1948 | 2728 | 710 | 42 | 160 | 0 | 136
5:30 | 3634.5 | 925 | 1877 | 2497.5 | 700 | 42.5 | 160 | 0 | 133
6:00 | 3629 | 925 | 1806 | 2267 | 690 | 43 | 160 | 0 | 130
6:30 | 3631 | 925 | 1701.5 | 2122.5 | 655 | 43 | 160 | 0 | 125 |  |  |  |  | Coal
7:00 | 3633 | 925 | 1597 | 1978 | 620 | 43 | 160 | 0 | 120
7:30 | 3627 | 925 | 1597.5 | 2009.5 | 620 | 43 | 140 | 0 | 120 |  |  |  | Oil |  |  |  | ,
8:00 | 3621 | 925 | 1598 | 2041 | 620 | 43 | 120 | 0 | 120
8:30 | 3680.5 | 925 | 1572 | 2200 | 620 | 43.5 | 130 | 0 | 114
9:00 | 3740 | 925 | 1546 | 2359 | 620 | 44 | 140 | 0 | 108
9:30 | 3767.5 | 924.5 | 1567.5 | 2506.5 | 630 | 44 | 154 | 0 | 107
10:00 | 3795 | 924 | 1589 | 2654 | 640 | 44 | 168 | 0 | 106
10:30 | 3837.5 | 925 | 1554.5 | 2721.5 | 650 | 44.5 | 168 | 0 | 106
11:00 | 3880 | 926 | 1520 | 2789 | 660 | 45 | 168 | 0 | 106
11:30 | 3816.5 | 925.5 | 1494 | 2928 | 655 | 45 | 213.5 | 0 | 107
12:00 | 3753 | 925 | 1468 | 3067 | 650 | 45 | 259 | 0 | 108
12:30 | 3707 | 925 | 1436.5 | 3029.5 | 635 | 44.5 | 303.5 | 0 | 114
13:00 | 3661 | 925 | 1405 | 2992 | 620 | 44 | 348 | 0 | 120
13:30 | 3661 | 925 | 1405 | 2992 | 620 | 44 | 348 | 0 | 120
14:00 | 3661 | 925 | 1405 | 2992 | 620 | 44 | 348 | 0 | 120
14:30 | 3619 | 921 | 1457.5 | 2875.5 | 624.5 | 42.5 | 334.5 | 0 | 123
15:00 | 3577 | 917 | 1510 | 2759 | 629 | 41 | 321 | 0 | 126
15:30 | 3530.5 | 917 | 1479 | 2836 | 654.5 | 41 | 377.5 | 0 | 128
16:00 | 3484 | 917 | 1448 | 2913 | 680 | 41 | 434 | 0 | 130
16:30 | 3336.5 | 916.5 | 1423 | 2931 | 665 | 41 | 445.5 | 0 | 135
17:00 | 3189 | 916 | 1398 | 2949 | 650 | 41 | 457 | 0 | 140
17:30 | 3303 | 916.5 | 1409 | 3275.5 | 660 | 41.5 | 544 | 0 | 156
18:00 | 3417 | 917 | 1420 | 3602 | 670 | 42 | 631 | 0 | 172
18:30 | 3529.5 | 917 | 1481.5 | 3898 | 685 | 42.5 | 704 | 0 | 159
19:00 | 3642 | 917 | 1543 | 4194 | 700 | 43 | 777 | 0 | 146
19:30 | 3668 | 916 | 1588 | 4162 | 700 | 43 | 780 | 0 | 144
20:00 | 3731 | 917 | 1588 | 4150 | 700 | 44 | 785 | 0 | 150
20:30 | 3729.5 | 917 | 1591.5 | 4032.5 | 715 | 44 | 786 | 0 | 148
21:00 | 3728 | 917 | 1595 | 3915 | 730 | 44 | 787 | 0 | 146
21:30 | 3808.5 | 917 | 1608 | 3743.5 | 730 | 44 | 764.5 | 0 | 147
22:00 | 3889 | 917 | 1621 | 3572 | 730 | 44 | 742 | 0 | 148
22:30 | 3862.5 | 917 | 1616.5 | 3571 | 725 | 44 | 743.5 | 0 | 147
23:00 | 3836 | 917 | 1612 | 3570 | 720 | 44 | 745 | 0 | 146
23:30 | 3816 | 917 | 1647.5 | 3570 | 725 | 44 | 692 | 0 | 144 | Max Temp. in Dhaka |  | 32.9° C
24:00 | 3796 | 917 | 1683 | 3570 | 730 | 44 | 639 | 0 | 142
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
Note on W13: Author:

## Generation
g | 2020-10-01
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 43 | 43 | 42 | 42 | 42 | 43 | 43 | 43 | 44 | 44 | 45 | 45 | 44 | 42 | 41 | 41 | 41 | 42 |  | 43 | 43 | 44 | 44 | 44 | 44 | 44 | 975420
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 0 | [9 empty] | 19 | 8 | 8 | 8 | 8 | 8 | 10 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 283307
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 5 |  |  |  | 6 | 2 | 13 | 4 | 11 | 7 | 1 | [9 empty] | 51165
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 202 | 203 | 203 | 211 | 203 | 204 | 204 | 206 | 203 | 209 | 204 | 204 | 204 | 217 | 204 | 204 | 227 |  | 203 | 203 | 203 | 204 | 206 | 204 | 204 | 4859143
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 139 | 139 | 139 | 139 | 139 | 139 | 140 | 139 | 139 | 139 | 139 | 139 | 104 | 104 | 140 | 140 | 140 | 144 |  | 140 | 140 | 140 | 139 | 139 | 139 | 139 | 3240192
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 44 | 0 | [9 empty] | 9 | 51 | 51 | 51 | 51 | 51 | 102 |  | 102 | 102 | 102 | 102 | 88 | 102 | 68 | 996508
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [17 empty] | 66 |  | 100 | 50 | 50 |  |  |  |  | 237504
14 | Titas 50 MW Peaking PP | 50 | 0 | [10 empty] | 19 | 25 | 25 | 25 | 24 | 46 |  | 49 | 49 | 49 | 49 | 49 | 50 | 0 | 482240
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 120 | 120 | 120 | 120 | 120 | 120 | 76 | 76 | 120 | 120 | 160 | 100 | 100 | 160 | 180 | 180 | 140 | 170 |  | 185 | 200 | 195 | 185 | 190 | 185 | 185 | 3641000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 300 | 300 | 300 | 300 | 300 | 245 | 195 | 205 | 259 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 6997852
19 | Ashuganj 195MW PP (APSCL-United) | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 652363
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 3029000
23 | Ghorasal TPP Unit-5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2740500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4769700
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2083744
32 | Ashuganj 50 MW PP | 29 | 29 | 29 | 29 | 29 | 29 | 26 | 26 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 |  | 29 | 29 | 29 | 29 | 26 | 29 | 29 | 674424
33 | Ashuganj 225 MW CCPP | 216 | 215 | 216 | 215 | 214 | 217 | 215 | 190 | 195 | 182 | 197 | 182 | 166 | 170 | 199 | 177 | 177 | 208 |  | 176 | 184 | 176 | 186 | 190 | 176 | 176 | 4692000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 275 | 280 | 275 | 275 | 295 | 275 | 285 | 280 | 350 | 310 | 325 | 260 | 260 | 260 | 345 | 265 | 260 | 350 |  | 310 | 310 | 310 | 330 | 340 | 325 | 325 | 7377700
35 | Ashuganj 55 MW PP (Precision) | 55 | 55 | 54 | 55 | 55 | 55 | 55 | 55 | 52 | 53 | 54 | 54 | 54 | 52 | 49 | 47 | 47 | 50 |  | 51 | 51 | 51 | 52 | 52 | 52 | 54 | 1264320
36 | Chandpur 150 MW CCPP | 86 | 96 | 86 | 95 | 96 | 85 | 96 | 96 | 96 | 92 | 96 | 85 | 85 | 92 | 96 | 86 | 85 | 96 |  | 86 | 95 | 85 | 96 | 96 | 95 | 86 | 2180760
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 420 | 400 | 400 | 400 | 400 | 400 | 370 | 370 | 370 | 370 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 6641300
41 | Haripur 360MW CCPP(HPL) | 355 | 320 | 320 | 320 | 320 | 320 | 280 | 280 | 286 | 286 | 338 | 315 | 272 | 303 | 341 | 322 | 323 | 338 |  | 353 | 351 | 351 | 350 | 350 | 352 | 354 | 7703000
42 | RPCL 210MW CCPP | 156 | 156 | 161 | 161 | 157 | 161 | 156 | 156 | 140 | 140 | 120 | 121 | 121 | 121 | 158 | 161 | 160 | 157 |  | 160 | 158 | 158 | 158 | 158 | 158 | 158 | 3497400
43
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 58 | 60 | 60 | 58 | 58 | 59 | 58 | 58 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1417000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 736080
46 | Shajibazar 330 MW CCPP | 185 | 192 | 188 | 197 | 200 | 185 | 195 | 200 | 192 | 190 | 191 | 190 | 191 | 190 | 141 | 142 | 140 | 142 |  | 140 | 140 | 140 | 140 | 140 | 142 | 140 | 3939000
47 | Shahjibazar GTPP Unit- 8 & 9 | 64 | 62 | 62 | 62 | 62 | 62 | 62 | 65 | 64 | 65 | 63 | 40 | 40 | 50 | 63 | 66 | 65 | 61 |  | 65 | 65 | 65 | 65 | 65 | 66 | 67 | 1453632
48 | Shahjibazar 86MW PP (Shahjibazar) | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 85 | 85 | 85 | 85 | 85 | 88 | 40 | 88 | 88 | 40 | 40 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 1944960
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 100 | 140 | 140 | 140 | 120 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3265280
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 415000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 248220
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 213048
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 52 | 50 | 50 | 50 | 50 | 50 | 50 | 53 | 50 | 53 | 25 | 42 | 47 | 53 | 53 |  | 50 | 50 | 53 | 53 | 53 | 53 | 53 | 1188600
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 16 | 16 | 16 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 509184
57 | Bibiana-II 341 MW CCPP (Summit) | 275 | 275 | 285 | 300 | 300 | 275 | 265 | 300 | 305 | 295 | 300 | 270 | 285 | 295 | 310 | 290 | 270 | 265 |  | 260 | 300 | 290 | 290 | 310 | 300 | 270 | 7144300
| Bibiyana South 400 MW | [9 empty] | 100 | 100 | 150 | 215 | 267 | 261 | 266 | [10 empty] | 1361500
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1304334
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 428976
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 475560
62 | Tangail 22 MW PP (Doreen) | 14 | 14 | 14 | 14 | 14 | 14 |  |  |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 279396
63 | Impoprt (Tripura) | 148 | 144 | 142 | 138 | 136 | 130 | 120 | 120 | 108 | 106 | 106 | 108 | 120 | 124 | 126 | 130 | 140 | 172 |  | 146 | 144 | 150 | 146 | 148 | 146 | 142 | 3210240
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 34 | 8 | 4 | 4 | 4 | 4 | 8 | 8 | 4 | 4 | 12 | 12 |  | 22 | 25 | 30 | 35 | 40 | 41 | 42 | 561120
65 | Feni 22MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 421020
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 |  | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 174420
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 22 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 798400
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15 | 15 | 15 | 9 | 9 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 21 | 21 | 474110
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 23 | 16 | 16 | 22 | 22 | 20 | 20 | 20 | 20 | 20 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 523800
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 33 | 33 | 33 | 33 | 801100
72 | Rupganj 33 MW PP(Summit) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 25 | 25 | 25 | 25 |  | 8 | 17 | 33 | 33 | 33 | 33 | 33 | 528100
73 | Ghorashal 108MW PP (Regent) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 43 | 43 | 43 | 43 | 43 | 42 | 41 | 41 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 42 | 41 | 1020363
| Feni Lanka Power | 100 | 100 | 60 | 0 | [5 empty] | 34 | 34 | 70 | 70 | 34 | 40 | 52 | 52 | 88 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1388520
| Chowmuhani 113 MW | 103 | 105 | 105 | 105 | 98 | 99 | 97 | 99 | 97 | 102 | 104 | 103 | 96 | 104 | 101 | 97 | 110 | 100 |  | 109 | 113 | 104 | 105 | 108 | 112 | 106 | 2478840
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2408640
78 | Gazipur 52 MW PP | 52 | 0 | [7 empty] | 2 | 38 | 51 | 16 | 16 | 16 | 37 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 678048
79 | Kodda 150MW PP | 150 | 150 | 114 | 32 | 0 |  |  |  | 20 | 48 | 48 | 115 | 115 | 82 | 82 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 2302560
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | 52 | 25 | 0 |  |  |  | 10 | 49 | 50 | 52 | 16 | 16 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 929002
| Gazipur 100 MW PP | 80 | 80 | 80 | 80 | 49 | 16 | 16 | 16 | 21 | 77 | 82 | 82 | 82 | 82 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 90 | 98 | 98 | 98 | 1740852
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 5 | 4 | 5 | 2 | 6 | 1 | 1 | 0 | [10 empty] | 24360
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 49 | 36 | 39 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1263668
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 |  | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 2336640
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [9 empty] | 2 | 34 | 86 | 90 | 30 | 20 | 20 | 20 | 40 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 985918
86 | Meghnaghat CCPP(Summit) | 130 | 145 | 130 | 140 | 150 | 125 | 145 | 140 | 145 | 140 | 145 | 130 | 135 | 138 | 138 | 140 | 122 | 150 |  | 138 | 143 | 145 | 150 | 150 | 145 | 140 | 3362851
87 | Meghnaghat 100 MW(IEL) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 98 | 93 | 93 | 93 | 98 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2399040
| Meghnaghat 104 MW PP (OPCL) | 53 | 45 | 46 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 97 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 1940160
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 30 | 0 | [9 empty] | 50 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 30 | 30 | 30 | 30 | 30 | 30 | 335040
92 | Fenchuganj 44MW (Energyprima) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 44 | 40 | 40 | 20 | 30 | 42 | 45 | 45 |  | 46 | 46 | 46 | 46 | 46 | 46 | 47 | 1058400
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1246131
94 | Gagnagar 102 MW PP (Digital Power) | 93 | 93 | 93 | 93 | 93 | 60 | 60 | 60 | 84 | 84 | 84 | 84 | 93 | 93 | 93 | 93 | 93 | 93 |  | 93 | 93 | 93 | 100 | 102 | 102 | 102 | 2170800
95 | Patenga 50MW PP (Baraka) | 50 | 50 | 50 | 0 |  |  |  | 1 | 18 | 20 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 916800
96 | Chattogram 108 MW PP (ECPV) | 91 | 91 | 97 | 97 | 97 | 87 | 51 | 54 | 87 | 85 | 84 | 83 | 83 | 84 | 90 | 82 | 88 | 97 |  | 97 | 90 | 93 | 98 | 97 | 97 | 97 | 2107440
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | 55 | 45 | 55 | 55 | 55 | 15 | 15 | 15 | 37 | 40 | 25 | 32 | 40 | 40 | 40 | 40 | 40 | 45 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1070294
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 55 | 55 | 55 | 55 | 17 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1239002
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 130 | 130 | 130 | 130 | 163 | 163 | 163 | 163 | 110 | 140 | 163 | 110 | 110 | 110 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3601800
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | [9 empty] | 5500
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 17 | 17 | 17 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1228680
104 | Keranigonj 300 MW PP (APR) | [17 empty] | 256 |  | 248 | 206 | 212 | 88 |  |  | 0 | 717785
105 | Bramhangoan 100 MW PP (Aggreko) | [19 empty] | 50 | 50 | 50 | 50 |  |  | 0 | 182835
106 | Mymensingh 200 MW PP (United) | 192 | 194 | 194 | 193 | 193 | 194 | 193 | 193 | 193 | 193 | 193 | 192 | 193 | 193 | 200 | 180 | 180 | 165 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4608000
112 | Aurahati 100MW PP (Aggreko) | [17 empty] | 58 |  | 99 | 101 | 101 | 52 |  |  | 0 | 341806
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 148 | 149 | 149 | 149 | 121 | 113 | 131 | 145 | 139 | 131 | 133 | 141 | 143 | 139 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3450528
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 100 | 100 | 90 | 90 | 90 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2318400
116 | Chandpur 200MW (Desh energy) | 103 | 0 | [9 empty] | 30 | 17 | 17 | 17 | 36 | 68 | 73 |  | 176 | 200 | 200 | 200 | 85 | 85 | 16 | 1370880
117 | Ashuganj 150MW PP (Midland) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 791200
118 | Bibiyana-III 400 MW CCPP | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 142 | 142 | 142 | 142 | 142 | 142 | 140 |  | 142 | 142 | 208 | 177 | 295 | 295 | 296 | 3832000
| Jamalpur 115 MW PP (United) | 108 | 105 | 105 | 105 | 105 | 85 | 45 | 48 | 115 | 115 | 115 | 115 | 115 | 65 | 65 | 30 | 30 | 41 |  | 95 | 108 | 95 | 64 | 64 | 64 | 64 | 2088000
| Anwara 300 MW PP (United) | 162 | 162 | 162 | 162 | 162 | 162 | 124 | 124 | 124 | 124 | 124 | 124 | 124 | 124 | 124 | 161 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3599291
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2432640
120 | Eastern Zone Total | 7529 | 7182 | 7101 | 6954 | 6857 | 6504 | 6114 | 6115 | 6569 | 6811 | 6908 | 6984 | 6905 | 6807 | 7173 | 7147 | 6845 | 7616 |  | 8034 | 8081 | 8134 | 7914 | 7770 | 7744 | 7520 | 172259636
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 115 | 115 | 115 | 115 | 83 | 28 |  |  |  | 66 | 66 | 81 | 95 | 66 | 73 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2032320
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 3 | 5 |  | 15 | 15 | 17 | 22 | 22 | 22 |  | 88320
| Khulna 225 MW CCPP | 228 | 228 | 190 | 160 | 160 | 160 | 160 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 170 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 4081920
129 | Rupsha 105 MW PP (Orion rupsha) | 72 | 72 | 55 | 55 | 55 | 55 | 53 | 55 | 55 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1466112
130
131
132
133
| Barisal 110 MW PP (Summit ) | 64 | 32 | 16 | 0 | [5 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 48 | 48 | 77 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 1038528
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 92 | 93 | 93 | 93 | 93 | 93 | 93 | 92 | 0 | 51 | 69 | 77 | 83 | 54 | 85 | 88 | 88 | 87 |  | 87 | 90 | 92 | 94 | 94 | 93 | 94 | 1962595
| Bhola 225 MW CCPP | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | [11 empty] | 0 | 872000
140 | Bhola 33 MW PP (Venture) | 38 | 36 | 37 | 32 | 31 | 27 | 25 | 24 | 23 | 24 | 24 | 24 | 27 | 27 | 25 | 24 | 24 | 34 |  | 37 | 38 | 38 | 38 | 38 | 38 | 38 | 725258
141 | Noapara 100 MW PP (Bangla Trac) | 10 | 0 | [13 empty] | 29 |  | 8 |  | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 727680
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 0 | [8 empty] | 40 | 8 | 8 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 495000
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 10 | [9 empty] | 3840
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 925 | 925 | 926 | 926 | 925 | 925 | 925 | 925 | 925 | 924 | 926 | 925 | 925 | 924 | 917 | 917 | 916 | 917 |  | 917 | 916 | 917 | 917 | 917 | 917 | 917 | 22111272
147 | Bheramara 410 MW CCPP | 310 | 320 | 330 | 350 | 350 | 350 | 355 | 355 | 370 | 380 | 385 | 375 | 365 | 320 |  |  | 40 | 80 |  | 340 | 345 | 345 | 345 | 360 | 340 | 340 | 7328736
148 | Payra 1320 MW | 560 | 570 | 560 | 560 | 560 | 540 | 470 | 470 | 470 | 490 | 510 | 500 | 470 | 470 | 480 | 530 | 500 | 520 |  | 550 | 550 | 550 | 580 | 580 | 570 | 580 | 13527200
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3696400
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 50 | 50 | 0 | [8 empty] | 15 | 43 | 43 | 43 | 43 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 672448
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 115 | 115 | 115 | 115 | 115 | 135 | 147 | 146 | 146 | 147 | 147 | 146 | 148 | 146 | 145 | 130 | 128 | 147 |  | 147 | 147 | 147 | 146 | 145 | 146 | 147 | 3440800
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 133 | 132 | 132 | 130 | 130 | 130 | 132 | 152 | 160 | 150 | 164 | 174 | 144 | 157 | 176 | 156 | 165 | 160 |  | 184 | 167 | 165 | 166 | 171 | 176 | 177 | 3949627
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 130 | 130 | 130 | 130 | 130 | 146 | 166 | 171 | 175 | 176 | 193 | 192 | 175 | 179 | 187 | 190 | 165 | 169 |  | 193 | 192 | 198 | 190 | 196 | 187 | 176 | 4331191
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 231 | 232 | 231 | 230 | 232 | 119 | [19 empty] | 95 | 516500
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 12 | 0 | [15 empty] | 25 |  | 42 | 42 | 42 | 43 | 12 |  |  | 209237
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 17 | 21 | 21 | 21 | 21 | 21 | 21 | 10 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 22 | 22 | 22 | 471360
163 | Bogura 20 MW PP (Energyprima) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 237096
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 245610
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | 43 | 0 | [15 empty] | 28 |  | 43 | 44 | 47 | 43 | 43 | 43 | 43 | 320831
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 0 | [6 empty] | 16 | 16 | 52 | 52 | 16 | 20 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 736800
170 | Chapainawabganj 100 MW Peaking PP | 97 | 97 | 50 | 24 | 0 | [10 empty] | 45 | 49 | 55 |  | 96 | 98 | 98 | 98 | 98 | 98 | 98 | 998216
171 | Baghabari 200 MW PP (Paramount) | [17 empty] | 75 |  | 100 | 100 | 100 | 50 |  |  | 0 | 369526
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 113 | 0 |  |  |  | 27 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 1222752
172 | Confidence Power Bogura Unit-1 113 MW | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 109 | 109 | 109 | 90 | 2331072
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 111 | 110 | 94 | 77 | 81 | 108 | 113 | 113 | 113 | 113 | 113 | 113 | 57 | 33 | 36 | 74 |  | 113 | 112 | 111 | 113 | 113 | 112 | 63 | 2323200
177 | Sympa Solar Power 8MW | [6 empty] | 1 | 3 | 4 | 5 | 5 | 6 | 3 | 4 | 1 | 1 | 1 | [9 empty] | 31445
178
178