## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-10-03 | Saturday
|  |  | Date (day): | 2020-10-03 |  | Saturday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13051.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13893 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-10-02 | 2020-10-03 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 120 | 120 | 120 |  |  | Gas shortage
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 115 | 115 | 115 | 75 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 200 | 200
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 42 | 42 | 42 | 42 | 66 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under S/D for dust in gas.
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 343 | 353 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 |  |  | GT-2 under shut down
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 93 | 92 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 150 | 140 | 150 | 150 | 155 |  | GT-2 S/D for Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 97 | 97 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 100 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 185 | 188 | 120 | 120 |  |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 99 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 84 | 102 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 98 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 37 | 47 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 28 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 52 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 122 | 300 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 25 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 112 | 132 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 105 | 85 | 86 |  | 19 | Engine problem
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 2372 | 3039 | 3245 | 3536 | 638 | 1181
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 115 | 115 | 120 | 120 | 60 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 45 | 45 | 44 | 44 | 186 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 225 | 204 | 221 | 221
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 145 | 139 | 140 | 145
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 100 | 100
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 40 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 100 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 21 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 35 | 42 | 40 | 40
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 18 | 91 | 90 | 90 |  | 18 | Engine problem
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 164 | 162 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 18 | 52 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 999 | 1253 | 1740 | 1720 | 426 | 116
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 70 | 55 | 80 | 80 |  | 54 | Engine problem
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 37 | 142 | 225 | 225 |  |  | FGMO
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 160 | 245 | 360 | 360 |  |  | FGMO
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maintenance
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 3 | 29 | 30 | 30 | 15 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 55 | 55 | 55
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 26 | 26 | 26 | 169 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 30 | 30 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 48 | 0 | 50
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 94 | 90 | 100 | 100 |  | 63 | ST under shut down
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 100 | 200 | 200
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 22 | 22 | 22
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 5 | 8 | 8 |  | 3 | Engine problem
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 106 | 166 | 162 | 173
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 52 | 52 | 52
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 21 | 21 | 21 | 21
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 100 | 114 | 114
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 110 | 113 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 738 | 1383 | 1802 | 2063 | 448 | 480
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 152 | 160 | 160 | 160 | 42 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 14 | 14 | 17 | 17 |  | 5 | Engine problem
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 0 | 0 | 0 |  | 95 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 200 | 200 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 22 | 65 | 115 | 115
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 390 | 439 | 493.6 | 492 | 42 | 100
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 58 | 60 | 60
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 35 | Unit-4 under shut down
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maintenance
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 142 | 140 | 200 | 200 |  | 110 | ST Under maint.
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 44 | 47 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 62 | 66 | 65 | 65
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 88 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 86 | 177 | 177 | 177 |  |  | Machine problem
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 290 | 341 | 341 |  |  | FGMO
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 52 | 82 | 85 | 85 |  | 315 | Testing for combined cycle
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 981 | 1094 | 1203 | 1203 | 0 | 623
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 926 | 925 | 935 | 935
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 115 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 200 | 225 | 225
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 305 | 335 | 410 | 410
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 40 | 40 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 37 | 100 | 50 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 35 | 53 | 90 | 90 |  | 15 | Engine problem
| 108 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1463 | 1768 | 1965 | 2121 | 0 | 15
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 110 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 18 | 38 | 33 | 33
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 90 | 90 | 78 | 90 |  | 5 | Engine problem
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 500 | 565 | 620 | 620
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 624 | 803 | 841 | 853 | 0 | 199
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 42 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 44 | 43 | 43
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | Shut down for gas shortage
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 179 | 170 | 220 | 220 |  |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 181 | 175 | 220 | 220 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 405 | 406 | 414 | 414 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 34
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 21 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 10 | 10 | 10 | 10
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 10 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 1 | 52 | 52 | 52
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 98 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 35 | 100 | 113
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 90 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 840 | 1204 | 1504 | 1642 | 271 | 210
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 35 | 105 | 100 | 113
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 188 | 255 | 258 | 263 | 294 | 40
|  | Total |  |  |  |  | 20383 | 19892 | 8595 | 11238 | 13051.6 | 13893 | 2119 | 2964
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8198.8254 | 10720 | 12450.0046 | 13252.6215
| A. |  | 2020-10-02 | (Yesterday) |  |  |  |  | Friday
| 1 | Highest Generation : |  |  | 11238 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 8097 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11238 | MW
| 3 | Day peak Generation : |  |  | 8595 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10720 | MW
| 4 | Evening peak Generation : |  |  | 11238 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 231.5921 | MKWHr | By Solar | 0.19865 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 120.8408 | MKWHr |  | By Oil: | 67.8644 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 16.3379 | MKWHr |  | By Hydro: | 0.9534 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2119 | MW | Dhaka | 3550 | 3550 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2964 | MW | Chittagong | 1194 | 1194 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5083 | MW | Khulna | 1361 | 1361 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1058.57 | MMCFD |  |  | Rajshahi | 1099 | 1099 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 147511557.078 | ii) Oil : | Taka | 540543761.63 | Comilla | 1127 | 1127 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 75516047 | Total | Taka | 763571365.708 | Mymensingh | 858 | 858 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 484 | 484 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 296 | MW (E to W) at | 21:00 | hrs | Barisal | 336 | 336 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 195 | MW at | 1:00 | hrs | Rangpur | 711 | 711 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 33.8° C |  |  | Total | 10720 | 10720 |  | 0
| B. |  | 2020-10-03 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 33.5° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 11800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13893 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 9200 | MW
| 4 | Reserve(Generation end) |  |  |  | 2093 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 243.1737 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8517 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.1905 | MKWHr. | ii) HVDC Flow at Peak Time |  | 925 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.2064 | MKWHr. | iii) Maximum HVDC Flow : |  | 926 | MW at | 7:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 98.73 |  | (b) Today: | 98.92 |  | (c) Rule Curve: |  | 106.18
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-10-02
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 100 | 115 | 200 | 42 | 0 | 0 | 352 |  | 0 | 225 | 140 | 100 | 97 | 55 | 0 | 0 | 189 | 0 | 100 | 102 | 114 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 0 | 0 | 44 | 0 | 115 | 0 | 25 | 202 | 0 | 139 | 0 |  | 0 | 0 | 51 | 30 | 97 | 50 | 20 | 40 | 0 | 0 | 100 | 325 | 0 | 178 | 26 | 95 | 29 | 55 | 0 | 51 | 0 | 0 | 52 | 18 | 8 | 33 | 21 | 138 | 0 | 0 | 14 | 0 | 60 | 30 | 53 | 47 | 0 | 141 | 65 | 88 | 0 | 140 | 18 | 0 | 10 | 285 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 30 | 296 | 64 | 98 | 0 | 0 | 162 | 54 | 0 | 100 | 106 | 100 | 0 | 100 |  | 925 | 0 | 340 | 0 | 115 | 230 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 110 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 52 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 146 | 0 | 186 | 0 | 94 | 0 | 189 | 0 | 108 | 70 | 0 | 35 | 0 | 36 | 0 | 0 | 50 | 560 |  | 7067 | 3614 | 10681 | 3693 | 925 | 1545 | 3133 | 710 | 44 | 493 | 138 | 0 | 0 | 98.71
2:00 | 0 | 0 | 100 | 115 | 200 | 42 | 0 | 0 | 354 |  | 0 | 225 | 135 | 100 | 97 | 55 | 0 | 0 | 181 | 0 | 100 | 50 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 0 | 0 | 43 | 0 | 115 | 0 | 0 | 202 | 0 | 139 | 0 |  | 0 | 0 | 17 | 0 | 80 | 0 | 20 | 41 | 0 | 0 | 100 | 325 | 0 | 177 | 26 | 94 | 29 | 55 | 0 | 51 | 0 | 0 | 25 | 18 | 8 | 33 | 21 | 136 | 0 | 0 | 14 | 0 | 60 | 30 | 53 | 47 | 0 | 140 | 65 | 88 | 0 | 140 | 18 | 0 | 10 | 270 | 24 | 11 | 0 | 245 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 30 | 297 | 64 | 34 | 0 | 0 | 162 | 54 | 0 | 40 | 107 | 100 | 0 | 104 |  | 924 | 0 | 340 | 0 | 61 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 80 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 148 | 0 | 176 | 0 | 92 | 0 | 181 | 0 | 400 | 70 | 0 | 35 | 0 | 35 | 0 | 0 | 50 | 560 |  | 6512 | 3635 | 10147 | 3667 | 924 | 1822 | 2526 | 710 | 43 | 319 | 136 | 0 | 0 | 98.71
3:00 | 0 | 0 | 100 | 115 | 200 | 42 | 0 | 0 | 353 |  | 0 | 225 | 145 | 100 | 97 | 55 | 0 | 0 | 191 | 0 | 100 | 50 | 20 | 0 | 0 | 0 | 0 | 17 | 17 | 55 | 22 | 25 | 17 | 33 | 33 | 0 | 0 | 41 | 0 | 115 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 51 | 0 | 20 | 41 | 0 | 0 | 100 | 325 | 0 | 181 | 26 | 96 | 29 | 54 | 0 | 51 | 0 | 0 | 25 | 18 | 8 | 33 | 21 | 132 | 0 | 0 | 14 | 0 | 60 | 30 | 53 | 47 | 0 | 141 | 65 | 88 | 0 | 140 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 245 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 30 | 295 | 64 | 17 | 0 | 0 | 162 | 54 | 0 | 0 | 108 | 100 | 0 | 98 |  | 925 | 0 | 365 | 0 | 16 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 146 | 0 | 179 | 0 | 92 | 0 | 183 | 0 | 414 | 70 | 0 | 35 | 0 | 36 | 0 | 0 | 50 | 560 |  | 6331 | 3610 | 9941 | 3703 | 925 | 1854 | 2326 | 710 | 41 | 250 | 132 | 0 | 0 | 98.72
4:00 | 0 | 0 | 100 | 115 | 200 | 42 | 0 | 0 | 355 |  | 0 | 225 | 140 | 100 | 97 | 55 | 0 | 0 | 190 | 0 | 100 | 50 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 55 | 22 | 25 | 22 | 33 | 33 | 0 | 0 | 41 | 0 | 115 | 0 | 0 | 203 | 0 | 141 | 0 |  | 0 | 0 | 0 | 0 | 51 | 0 | 20 | 42 | 0 | 0 | 100 | 325 | 0 | 177 | 26 | 92 | 29 | 55 | 0 | 51 | 0 | 0 | 25 | 18 | 8 | 33 | 21 | 130 | 0 | 0 | 14 | 0 | 60 | 30 | 53 | 47 | 0 | 140 | 65 | 88 | 0 | 140 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 245 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 30 | 295 | 64 | 16 | 0 | 0 | 162 | 54 | 0 | 0 | 110 | 100 | 0 | 104 |  | 925 | 0 | 300 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 146 | 0 | 180 | 0 | 91 | 0 | 170 | 0 | 408 | 70 | 0 | 35 | 0 | 35 | 0 | 0 | 50 | 530 |  | 6328 | 3475 | 9803 | 3623 | 925 | 1847 | 2311 | 680 | 41 | 246 | 130 | 0 | 0 | 98.72
5:00 | 0 | 0 | 100 | 115 | 200 | 42 | 0 | 0 | 353 |  | 0 | 225 | 145 | 100 | 97 | 55 | 0 | 0 | 192 | 0 | 100 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 22 | 25 | 23 | 33 | 33 | 0 | 0 | 41 | 0 | 115 | 0 | 0 | 205 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 51 | 0 | 20 | 42 | 0 | 0 | 100 | 340 | 0 | 193 | 26 | 96 | 26 | 55 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 33 | 21 | 122 | 0 | 0 | 0 | 0 | 60 | 30 | 53 | 47 | 0 | 139 | 65 | 88 | 0 | 140 | 18 | 0 | 10 | 295 | 24 | 8 | 0 | 220 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 30 | 295 | 85 | 0 | 0 | 0 | 162 | 54 | 0 | 0 | 112 | 100 | 0 | 104 |  | 925 | 0 | 270 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 143 | 0 | 168 | 0 | 90 | 0 | 161 | 0 | 413 | 70 | 0 | 0 | 0 | 34 | 0 | 0 | 35 | 530 |  | 6263 | 3318 | 9581 | 3564 | 925 | 1854 | 2189 | 680 | 41 | 206 | 122 | 0 | 0 | 98.73
6:00 | 0 | 0 | 100 | 115 | 200 | 42 | 0 | 0 | 303 |  | 0 | 225 | 140 | 100 | 80 | 40 | 0 | 0 | 190 | 0 | 100 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 22 | 25 | 23 | 33 | 33 | 0 | 0 | 42 | 0 | 115 | 0 | 0 | 203 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 45 | 0 | 20 | 42 | 0 | 0 | 80 | 295 | 0 | 178 | 26 | 92 | 26 | 54 | 0 | 51 | 0 | 0 | 0 | 16 | 0 | 33 | 21 | 116 | 0 | 0 | 0 | 0 | 60 | 30 | 53 | 47 | 0 | 140 | 65 | 88 | 0 | 101 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 215 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 30 | 298 | 75 | 0 | 0 | 0 | 162 | 41 | 0 | 0 | 113 | 100 | 0 | 104 |  | 925 | 0 | 240 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 134 | 0 | 157 | 0 | 88 | 0 | 153 | 0 | 300 | 70 | 0 | 0 | 0 | 34 | 0 | 0 | 35 | 530 |  | 6009 | 3047 | 9056 | 3399 | 925 | 1683 | 2071 | 680 | 42 | 140 | 116 | 0 | 0 | 98.73
7:00 | 0 | 0 | 100 | 115 | 200 | 42 | 0 | 0 | 303 |  | 0 | 225 | 135 | 100 | 80 | 30 | 0 | 0 | 183 | 0 | 91 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 22 | 25 | 23 | 33 | 33 | 0 | 0 | 43 | 0 | 115 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 20 | 42 | 0 | 0 | 80 | 275 | 0 | 178 | 26 | 85 | 23 | 55 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 19 | 104 | 158 | 0 | 0 | 0 | 60 | 30 | 50 | 47 | 0 | 140 | 65 | 85 | 0 | 100 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 60 | 0 | 0 | 200 | 0 | 123 | 5 | 40 | 0 | 30 | 299 | 16 | 0 | 0 | 1 | 107 | 18 | 0 | 0 | 108 | 70 | 0 | 104 |  | 926 | 0 | 240 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 134 | 0 | 155 | 0 | 88 | 0 | 150 | 0 | 290 | 70 | 0 | 0 | 0 | 34 | 0 | 1 | 35 | 380 |  | 5613 | 2855 | 8468 | 3511 | 926 | 1652 | 1575 | 530 | 43 | 120 | 104 | 7 | 0 | 98.74
8:00 | 0 | 0 | 100 | 115 | 200 | 42 | 0 | 0 | 303 |  | 0 | 225 | 138 | 100 | 80 | 40 | 0 | 0 | 188 | 0 | 89 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 22 | 25 | 23 | 33 | 33 | 0 | 0 | 43 | 0 | 115 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 20 | 42 | 0 | 0 | 80 | 275 | 0 | 178 | 26 | 85 | 20 | 55 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 21 | 96 | 158 | 0 | 14 | 0 | 60 | 30 | 50 | 47 | 0 | 142 | 65 | 85 | 0 | 80 | 18 | 0 | 10 | 280 | 16 | 8 | 0 | 60 | 0 | 0 | 200 | 0 | 112 | 5 | 10 | 0 | 30 | 299 | 16 | 0 | 0 | 2 | 34 | 18 | 0 | 0 | 113 | 70 | 0 | 104 |  | 925 | 0 | 225 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 156 | 0 | 89 | 0 | 146 | 0 | 302 | 70 | 0 | 0 | 0 | 34 | 0 | 2 | 35 | 330 |  | 5483 | 2665 | 8148 | 3351 | 925 | 1664 | 1460 | 480 | 43 | 120 | 96 | 9 | 0 | 98.75
9:00 | 0 | 0 | 99 | 115 | 200 | 42 | 0 | 0 | 271 |  | 0 | 225 | 140 | 100 | 80 | 40 | 0 | 0 | 185 | 0 | 100 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 22 | 25 | 22 | 33 | 33 | 0 | 0 | 44 | 0 | 115 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 20 | 42 | 0 | 0 | 80 | 275 | 0 | 178 | 26 | 90 | 20 | 55 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 21 | 110 | 158 | 0 | 14 | 1 | 60 | 30 | 50 | 47 | 0 | 142 | 64 | 83 | 0 | 20 | 18 | 0 | 10 | 280 | 10 | 8 | 0 | 60 | 0 | 0 | 200 | 0 | 104 | 18 | 10 | 0 | 30 | 299 | 16 | 0 | 0 | 4 | 34 | 18 | 0 | 0 | 113 | 70 | 0 | 104 |  | 925 | 0 | 250 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 162 | 0 | 89 | 0 | 159 | 0 | 308 | 70 | 0 | 0 | 0 | 35 | 0 | 2 | 35 | 330 |  | 5384 | 2713 | 8097 | 3294 | 925 | 1633 | 1466 | 480 | 44 | 120 | 110 | 25 | 0 | 98.75
10:00 | 0 | 0 | 100 | 115 | 200 | 42 | 0 | 0 | 271 |  | 0 | 225 | 150 | 100 | 92 | 40 | 0 | 0 | 195 | 0 | 100 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 22 | 25 | 22 | 25 | 33 | 0 | 0 | 44 | 0 | 115 | 0 | 0 | 216 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 20 | 35 | 0 | 0 | 80 | 310 | 0 | 198 | 26 | 94 | 26 | 55 | 0 | 43 | 0 | 0 | 0 | 18 | 0 | 33 | 21 | 108 | 154 | 0 | 14 | 1 | 60 | 30 | 50 | 47 | 0 | 142 | 62 | 83 | 0 | 20 | 18 | 0 | 10 | 290 | 15 | 8 | 0 | 60 | 0 | 0 | 200 | 0 | 104 | 18 | 10 | 0 | 30 | 190 | 16 | 0 | 0 | 3 | 34 | 18 | 0 | 0 | 106 | 70 | 0 | 104 |  | 925 | 0 | 270 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 167 | 0 | 89 | 0 | 168 | 0 | 393 | 53 | 0 | 0 | 0 | 34 | 0 | 3 | 35 | 330 |  | 5361 | 2810 | 8171 | 3298 | 925 | 1708 | 1463 | 480 | 44 | 120 | 108 | 25 | 0 | 98.76
11:00 | 0 | 0 | 100 | 115 | 200 | 42 | 0 | 0 | 347 |  | 0 | 225 | 140 | 96 | 95 | 40 | 0 | 0 | 187 | 0 | 100 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 22 | 25 | 12 | 25 | 33 | 0 | 0 | 44 | 0 | 115 | 0 | 0 | 204 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 20 | 35 | 0 | 0 | 80 | 280 | 0 | 124 | 26 | 96 | 26 | 54 | 0 | 43 | 0 | 0 | 0 | 18 | 0 | 18 | 21 | 104 | 154 | 0 | 14 | 2 | 60 | 30 | 50 | 47 | 0 | 141 | 62 | 88 | 0 | 35 | 18 | 0 | 10 | 310 | 24 | 8 | 0 | 60 | 0 | 0 | 200 | 0 | 102 | 20 | 50 | 0 | 30 | 112 | 16 | 0 | 0 | 3 | 86 | 18 | 0 | 0 | 105 | 100 | 0 | 104 |  | 925 | 0 | 295 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 172 | 0 | 88 | 0 | 176 | 0 | 412 | 35 | 0 | 0 | 0 | 34 | 0 | 2 | 35 | 400 |  | 5462 | 2917 | 8379 | 3170 | 925 | 1826 | 1613 | 550 | 44 | 120 | 104 | 27 | 0 | 98.76
12:00 | 0 | 0 | 100 | 115 | 200 | 42 | 0 | 0 | 343 |  | 0 | 225 | 150 | 93 | 97 | 40 | 0 | 0 | 185 | 0 | 99 | 84 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 12 | 25 | 33 | 0 | 0 | 45 | 0 | 115 | 0 | 0 | 225 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 18 | 0 | 20 | 35 | 0 | 0 | 70 | 160 | 0 | 37 | 8 | 94 | 3 | 5 | 0 | 43 | 0 | 0 | 0 | 18 | 0 | 33 | 21 | 106 | 152 | 0 | 14 | 2 | 60 | 30 | 50 | 44 | 0 | 142 | 62 | 85 | 0 | 86 | 18 | 0 | 10 | 310 | 24 | 8 | 0 | 122 | 0 | 0 | 200 | 0 | 112 | 20 | 90 | 0 | 30 | 52 | 22 | 0 | 0 | 4 | 164 | 18 | 0 | 0 | 110 | 100 | 0 | 104 |  | 926 | 0 | 305 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 40 | 0 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 179 | 0 | 90 | 37 | 181 | 0 | 405 | 35 | 0 | 0 | 0 | 35 | 0 | 3 | 35 | 500 |  | 5480 | 3115 | 8595 | 2979 | 926 | 1744 | 1996 | 650 | 45 | 120 | 106 | 29 | 0 | 98.74
13:00 | 0 | 0 | 100 | 115 | 200 | 42 | 0 | 0 | 343 |  | 0 | 225 | 145 | 92 | 97 | 40 | 0 | 0 | 185 | 0 | 99 | 102 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 16 | 28 | 33 | 0 | 0 | 44 | 0 | 115 | 0 | 0 | 206 | 0 | 143 | 0 |  | 0 | 0 | 0 | 0 | 71 | 0 | 20 | 39 | 0 | 0 | 0 | 168 | 0 | 24 | 8 | 86 | 3 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 21 | 134 | 150 | 0 | 14 | 1 | 60 | 30 | 50 | 44 | 0 | 140 | 63 | 83 | 0 | 111 | 18 | 0 | 10 | 310 | 24 | 8 | 0 | 275 | 0 | 0 | 200 | 0 | 131 | 20 | 90 | 0 | 30 | 30 | 65 | 6 | 0 | 2 | 175 | 18 | 0 | 55 | 107 | 100 | 0 | 104 |  | 925 | 0 | 270 | 0 | 34 | 120 | 0 | 0 | 0 | 0 | 40 | 0 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 172 | 0 | 90 | 0 | 171 | 0 | 399 | 17 | 0 | 18 | 0 | 34 | 0 | 4 | 35 | 510 |  | 5766 | 3117 | 8883 | 2830 | 925 | 1751 | 2392 | 660 | 44 | 120 | 134 | 27 | 8883 | 98.77
14:00 | 0 | 0 | 100 | 115 | 200 | 41 | 0 | 0 | 332 |  | 0 | 225 | 130 | 93 | 97 | 30 | 0 | 0 | 150 | 0 | 99 | 102 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 16 | 28 | 33 | 0 | 0 | 44 | 0 | 115 | 0 | 0 | 205 | 0 | 138 | 0 |  | 0 | 0 | 0 | 0 | 81 | 0 | 20 | 39 | 0 | 0 | 0 | 145 | 0 | 13 | 8 | 88 | 3 | 5 | 0 | 51 | 0 | 0 | 33 | 18 | 0 | 33 | 21 | 134 | 150 | 0 | 14 | 0 | 60 | 30 | 47 | 44 | 0 | 140 | 65 | 84 | 0 | 120 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 270 | 0 | 0 | 200 | 0 | 130 | 18 | 100 | 0 | 30 | 20 | 35 | 73 | 0 | 1 | 175 | 18 | 0 | 100 | 104 | 100 | 0 | 104 |  | 925 | 0 | 215 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 40 | 0 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 141 | 0 | 88 | 0 | 146 | 0 | 287 | 17 | 0 | 35 | 0 | 34 | 0 | 3 | 35 | 520 |  | 5768 | 2951 | 8719 | 2647 | 925 | 1594 | 2563 | 670 | 44 | 120 | 134 | 22 | 0 | 98.78
15:00 | 0 | 0 | 100 | 115 | 200 | 41 | 0 | 0 | 345 |  | 0 | 225 | 125 | 100 | 97 | 30 | 0 | 0 | 183 | 0 | 99 | 102 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 9 | 28 | 33 | 0 | 0 | 41 | 0 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 83 | 0 | 20 | 37 | 0 | 0 | 0 | 50 | 0 | 10 | 8 | 85 | 3 | 6 | 0 | 5 | 0 | 0 | 52 | 18 | 0 | 33 | 21 | 136 | 158 | 0 | 14 | 0 | 57 | 30 | 49 | 44 | 0 | 141 | 63 | 88 | 0 | 161 | 18 | 0 | 10 | 290 | 24 | 5 | 0 | 268 | 53 | 0 | 200 | 26 | 131 | 14 | 100 | 0 | 30 | 20 | 8 | 104 | 0 | 3 | 180 | 18 | 0 | 100 | 112 | 100 | 0 | 104 |  | 924 | 0 | 215 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 40 | 0 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 138 | 0 | 91 | 0 | 138 | 0 | 313 | 17 | 0 | 35 | 0 | 33 | 0 | 3 | 35 | 550 |  | 5848 | 2997 | 8845 | 2603 | 924 | 1605 | 2680 | 700 | 41 | 136 | 136 | 20 | 0 | 98.78
16:00 | 0 | 0 | 100 | 115 | 200 | 42 | 0 | 0 | 345 |  | 0 | 225 | 140 | 100 | 97 | 30 | 0 | 0 | 150 | 0 | 99 | 102 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 22 | 25 | 12 | 28 | 33 | 0 | 0 | 35 | 0 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 24 | 0 | 20 | 36 | 0 | 0 | 0 | 50 | 0 | 8 | 8 | 96 | 3 | 5 | 0 | 5 | 0 | 0 | 8 | 18 | 0 | 33 | 21 | 130 | 155 | 0 | 14 | 0 | 58 | 30 | 50 | 44 | 0 | 144 | 66 | 88 | 0 | 161 | 18 | 0 | 10 | 270 | 24 | 5 | 0 | 200 | 0 | 0 | 200 | 0 | 121 | 8 | 70 | 0 | 30 | 82 | 8 | 34 | 0 | 0 | 106 | 18 | 0 | 100 | 110 | 70 | 0 | 104 |  | 925 | 0 | 240 | 0 | 20 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 90 | 0 | 138 | 0 | 381 | 17 | 0 | 35 | 0 | 34 | 0 | 2 | 35 | 510 |  | 5364 | 2912 | 8276 | 2675 | 925 | 1650 | 2055 | 660 | 35 | 136 | 130 | 10 | 0 | 98.79
17:00 | 0 | 0 | 114 | 115 | 200 | 42 | 0 | 0 | 350 |  | 0 | 225 | 130 | 95 | 97 | 30 | 0 | 0 | 155 | 0 | 99 | 74 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 22 | 25 | 16 | 25 | 17 | 0 | 0 | 35 | 0 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 22 | 0 | 20 | 37 | 0 | 0 | 0 | 170 | 0 | 28 | 8 | 85 | 3 | 5 | 0 | 5 | 0 | 0 | 8 | 18 | 0 | 33 | 21 | 118 | 159 | 0 | 14 | 0 | 58 | 30 | 53 | 46 | 0 | 141 | 40 | 88 | 0 | 168 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 200 | 33 | 0 | 150 | 0 | 90 | 2 | 70 | 0 | 30 | 15 | 8 | 34 | 0 | 0 | 106 | 26 | 0 | 100 | 68 | 100 | 0 | 104 |  | 925 | 0 | 255 | 0 | 16 | 120 | 0 | 0 | 0 | 6 | 0 | 0 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 139 | 0 | 64 | 0 | 146 | 0 | 328 | 17 | 0 | 35 | 0 | 42 | 0 | 1 | 70 | 520 |  | 5311 | 2900 | 8211 | 2740 | 925 | 1602 | 1977 | 669 | 35 | 142 | 118 | 3 | 0 | 98.67
18:00 | 0 | 0 | 119 | 115 | 200 | 42 | 0 | 0 | 347 |  | 0 | 225 | 150 | 92 | 97 | 30 | 0 | 0 | 80 | 0 | 100 | 84 | 70 | 28 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 14 | 25 | 33 | 13 | 0 | 41 | 0 | 115 | 0 | 5 | 217 | 0 | 144 | 0 |  | 0 | 0 | 82 | 50 | 40 | 1 | 20 | 37 | 0 | 0 | 0 | 210 | 0 | 130 | 26 | 85 | 3 | 5 | 0 | 5 | 0 | 0 | 9 | 18 | 5 | 33 | 16 | 152 | 160 | 0 | 14 | 0 | 57 | 30 | 34 | 47 | 0 | 139 | 66 | 88 | 0 | 175 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 200 | 51 | 0 | 166 | 39 | 94 | 0 | 100 | 3 | 30 | 80 | 20 | 45 | 0 | 0 | 161 | 47 | 0 | 100 | 67 | 100 | 0 | 104 |  | 925 | 0 | 285 | 0 | 45 | 160 | 0 | 0 | 0 | 0 | 40 | 0 | 28 | 110 | 0 | 0 | 0 | 25 | 10 | 15 | 0 | 0 | 28 | 24 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 142 | 0 | 82 | 9 | 149 | 0 | 383 | 17 | 0 | 35 | 0 | 77 | 0 | 0 | 90 | 520 |  | 6061 | 3388 | 9449 | 2984 | 925 | 1670 | 2617 | 670 | 41 | 390 | 152 | 0 | 0 | 98.67
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 120 | 115 | 200 | 42 | 0 | 0 | 351 |  | 0 | 225 | 138 | 92 | 97 | 40 | 0 | 0 | 80 | 0 | 100 | 102 | 98 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 25 | 33 | 52 | 0 | 43 | 0 | 115 | 0 | 25 | 204 | 0 | 104 | 0 |  | 0 | 0 | 102 | 60 | 82 | 36 | 20 | 42 | 0 | 0 | 0 | 245 | 0 | 143 | 26 | 92 | 26 | 45 | 0 | 28 | 0 | 23 | 45 | 22 | 5 | 33 | 16 | 156 | 160 | 0 | 14 | 0 | 58 | 30 | 53 | 47 | 0 | 141 | 40 | 88 | 0 | 179 | 18 | 0 | 10 | 270 | 24 | 11 | 0 | 280 | 25 | 0 | 200 | 27 | 131 | 0 | 100 | 85 | 30 | 85 | 65 | 105 | 0 | 0 | 162 | 52 | 0 | 100 | 113 | 100 | 0 | 104 |  | 925 | 0 | 310 | 0 | 99 | 180 | 0 | 0 | 0 | 0 | 40 | 0 | 35 | 110 | 0 | 0 | 0 | 50 | 42 | 96 | 0 | 0 | 45 | 52 | 0 | 21 | 10 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 167 | 0 | 91 | 96 | 165 | 0 | 411 | 53 | 0 | 35 | 0 | 86 | 0 | 0 | 90 | 565 |  | 6888 | 3931 | 10819 | 3077 | 925 | 1795 | 3473 | 714 | 43 | 636 | 156 | 0 | 0 | 98.68
19:30 | 0 | 0 | 120 | 115 | 200 | 42 | 0 | 0 | 350 |  | 0 | 225 | 145 | 92 | 97 | 55 | 0 | 0 | 120 | 0 | 100 | 102 | 98 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 25 | 33 | 52 | 0 | 43 | 0 | 115 | 0 | 25 | 216 | 0 | 104 | 0 |  | 0 | 0 | 102 | 60 | 91 | 47 | 20 | 42 | 0 | 0 | 0 | 240 | 0 | 141 | 26 | 94 | 26 | 45 | 0 | 51 | 0 | 50 | 52 | 22 | 5 | 33 | 20 | 166 | 157 | 0 | 14 | 0 | 58 | 30 | 50 | 47 | 0 | 140 | 40 | 88 | 0 | 178 | 18 | 0 | 10 | 310 | 24 | 11 | 0 | 300 | 25 | 0 | 200 | 27 | 131 | 0 | 100 | 100 | 30 | 84 | 65 | 105 | 0 | 0 | 162 | 52 | 0 | 100 | 113 | 100 | 0 | 104 |  | 925 | 0 | 310 | 0 | 99 | 185 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 110 | 0 | 0 | 0 | 50 | 42 | 96 | 0 | 0 | 45 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 169 | 0 | 89 | 100 | 168 | 0 | 407 | 53 | 0 | 35 | 0 | 96 | 0 | 0 | 90 | 565 |  | 7113 | 3955 | 11068 | 3130 | 925 | 1850 | 3571 | 715 | 43 | 668 | 166 | 0 | 0 | 0
20:00 | 0 | 0 | 120 | 115 | 200 | 42 | 0 | 0 | 351 |  | 0 | 225 | 140 | 92 | 97 | 55 | 0 | 0 | 165 | 0 | 100 | 102 | 98 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 25 | 33 | 52 | 0 | 44 | 0 | 115 | 0 | 25 | 206 | 0 | 139 | 0 |  | 0 | 0 | 68 | 40 | 91 | 50 | 20 | 42 | 0 | 0 | 0 | 245 | 0 | 141 | 26 | 95 | 29 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 5 | 33 | 20 | 164 | 160 | 0 | 14 | 0 | 58 | 30 | 50 | 47 | 0 | 140 | 66 | 88 | 0 | 177 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 300 | 25 | 0 | 200 | 27 | 132 | 0 | 100 | 100 | 30 | 85 | 65 | 105 | 0 | 0 | 162 | 52 | 0 | 100 | 113 | 100 | 0 | 104 |  | 925 | 0 | 315 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 42 | 97 | 0 | 0 | 47 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 170 | 0 | 91 | 100 | 171 | 0 | 406 | 53 | 0 | 35 | 0 | 102 | 0 | 0 | 90 | 565 |  | 7166 | 4005 | 11171 | 3247 | 925 | 1853 | 3572 | 714 | 44 | 652 | 164 | 0 | 0 | 98.68
21:00 | 0 | 0 | 120 | 115 | 200 | 42 | 0 | 0 | 353 |  | 0 | 225 | 140 | 92 | 97 | 55 | 0 | 0 | 188 | 0 | 100 | 102 | 98 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 28 | 33 | 52 | 0 | 45 | 0 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 68 | 40 | 91 | 50 | 20 | 42 | 0 | 0 | 55 | 245 | 0 | 142 | 26 | 90 | 29 | 55 | 0 | 51 | 0 | 48 | 52 | 22 | 5 | 33 | 21 | 166 | 160 | 0 | 14 | 0 | 58 | 30 | 53 | 47 | 0 | 140 | 66 | 88 | 0 | 177 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 300 | 25 | 0 | 200 | 0 | 132 | 0 | 100 | 100 | 30 | 82 | 65 | 105 | 0 | 0 | 162 | 52 | 0 | 100 | 113 | 100 | 0 | 104 |  | 925 | 0 | 335 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 42 | 98 | 0 | 0 | 44 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 170 | 0 | 90 | 100 | 175 | 0 | 406 | 53 | 0 | 35 | 0 | 105 | 0 | 0 | 90 | 565 |  | 7208 | 4030 | 11238 | 3344 | 925 | 1847 | 3548 | 715 | 45 | 648 | 166 | 0 | 0 | 98.69
22:00 | 0 | 0 | 120 | 115 | 200 | 41 | 0 | 0 | 353 |  | 0 | 225 | 130 | 55 | 97 | 55 | 0 | 0 | 170 | 0 | 94 | 102 | 98 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 28 | 33 | 52 | 0 | 46 | 0 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 68 | 40 | 90 | 50 | 20 | 42 | 0 | 0 | 80 | 245 | 0 | 142 | 26 | 85 | 29 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 5 | 33 | 21 | 170 | 160 | 0 | 14 | 0 | 58 | 30 | 53 | 47 | 0 | 140 | 67 | 88 | 0 | 178 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 132 | 0 | 100 | 100 | 30 | 86 | 65 | 105 | 0 | 0 | 162 | 52 | 0 | 100 | 113 | 100 | 0 | 104 |  | 925 | 0 | 325 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 0 | 39 | 110 | 0 | 0 | 0 | 50 | 42 | 98 | 0 | 0 | 44 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 175 | 0 | 91 | 100 | 175 | 0 | 385 | 53 | 0 | 35 | 0 | 105 | 0 | 0 | 90 | 560 |  | 7143 | 4001 | 11144 | 3347 | 925 | 1827 | 3469 | 710 | 46 | 650 | 170 | 0 | 0 | 98.84
23:00 | 0 | 0 | 120 | 115 | 200 | 41 | 0 | 0 | 353 |  | 0 | 225 | 136 | 33 | 97 | 55 | 0 | 0 | 195 | 0 | 94 | 102 | 98 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 28 | 33 | 52 | 0 | 45 | 0 | 115 | 0 | 25 | 204 | 0 | 140 | 0 |  | 0 | 0 | 68 | 40 | 91 | 50 | 20 | 42 | 0 | 0 | 80 | 245 | 0 | 142 | 26 | 92 | 29 | 55 | 0 | 51 | 0 | 50 | 52 | 21 | 5 | 33 | 21 | 168 | 160 | 0 | 14 | 0 | 58 | 30 | 50 | 47 | 0 | 142 | 67 | 88 | 0 | 178 | 18 | 0 | 10 | 285 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 134 | 0 | 100 | 68 | 30 | 85 | 71 | 105 | 0 | 0 | 162 | 52 | 0 | 100 | 113 | 100 | 0 | 104 |  | 925 | 0 | 320 | 0 | 115 | 150 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 42 | 98 | 0 | 0 | 43 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 182 | 0 | 90 | 0 | 175 | 0 | 399 | 53 | 0 | 35 | 0 | 105 | 0 | 0 | 90 | 560 |  | 7126 | 3864 | 10990 | 3382 | 925 | 1831 | 3330 | 710 | 45 | 599 | 168 | 0 | 0 | 98.85
24:00 | 0 | 0 | 120 | 115 | 200 | 41 | 0 | 0 | 353 |  | 0 | 225 | 135 | 24 | 96 | 55 | 0 | 0 | 195 | 0 | 100 | 102 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 28 | 33 | 52 | 0 | 45 | 0 | 115 | 0 | 25 | 203 | 0 | 139 | 0 |  | 0 | 0 | 68 | 20 | 92 | 50 | 20 | 42 | 0 | 0 | 80 | 245 | 0 | 30 | 26 | 87 | 29 | 55 | 0 | 51 | 0 | 50 | 52 | 21 | 5 | 33 | 21 | 162 | 159 | 0 | 14 | 0 | 58 | 30 | 50 | 47 | 0 | 142 | 67 | 88 | 0 | 178 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 133 | 0 | 100 | 50 | 30 | 88 | 85 | 105 | 0 | 0 | 162 | 38 | 0 | 100 | 113 | 100 | 0 | 104 |  | 925 | 0 | 320 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 42 | 98 | 0 | 0 | 43 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 187 | 0 | 91 | 0 | 178 | 0 | 379 | 53 | 0 | 35 | 0 | 92 | 0 | 0 | 50 | 560 |  | 7017 | 3770 | 10787 | 3273 | 925 | 1817 | 3234 | 710 | 45 | 621 | 162 | 0 | 0 | 98.86
KWH | 0 | 0 | 2594000 | 2772000 | 4846945 | 996318 | 0 | 0 | 8027000 |  | 0 | 4842750 | 3318691 | 2175360 | 2281440 | 1080350 | 0 | 0 | 4321000 | 0 | 2377920 | 1748736 | 972000 | 727713 | 0 | 0 | 0 | 786960 | 920510 | 1318918 | 482076 | 600000 | 444240 | 773300 | 799400 | 325932 | 0 | 953400 | 0 | 2800000 | 0 | 196223 | 4905766 | 0 | 3126240 | 0 |  | 0 | 0 | 564931 | 328800 | 1342080 | 365280 | 471456 | 981120 | 0 | 0 | 1322376 | 6049200 | 0 | 3119000 | 535272 | 2158340 | 449208 | 983040 | 0 | 1064626 | 0 | 247248 | 595373 | 419796 | 66780 | 800300 | 513610 | 3206400 | 3687640 | 0 | 272880 | 8000 | 1401000 | 721680 | 1206000 | 1100520 | 0 | 3167000 | 1506912 | 2062080 | 0 | 3111900 | 422000 | 0 | 248040 | 7136700 | 541920 | 204000 | 0 | 5356907 | 172711 | 15622 | 4744800 | 132941 | 3071088 | 141345 | 1959360 | 544320 | 796218 | 3950000 | 1143600 | 1206648 | 0 | 23000 | 3364691 | 868275 | 0 | 1303020 | 2570400 | 2310720 | 0 | 2601600 |  | 22190545 | 0 | 7025760 | 0 | 1114560 | 3922560 | 0 | 0 | 0 | 1792 | 466875 | 0 | 685205 | 1438560 | 0 | 0 | 0 | 307520 | 239598 | 785382 | 0 | 0 | 271069 | 544320 | 0 | 502320 | 236448 | 228114 | 0 | 0 | 3682200 | 0 | 0 | 1129100 | 0 | 4187782 | 0 | 2116260 | 549120 | 4195936 | 0 | 8528400 | 1227840 | 0 | 604416 | 0 | 1278720 | 0 | 26302 | 1274688 | 12655700 |  | 150174962 | 81417092 | 231592054 | 79588657 | 22190545 | 41252099 | 60552306 | 16337900 | 953400 | 7312100 | 3206400 | 198647 | 0
Fuel Cost | 0 | 0 | 3787240 | 4074840 | 5380108.95 | 1315139.76 | 0 | 0 | 8267810 |  | 0 | 5278597.5 | 3683747.01 | 16510982.4 | 15719121.6 | 9139761 | 0 | 0 | 7475330 | 0 | 17905737.6 | 15948472.32 | 9564480 | 6709513.86 | 0 | 0 | 0 | 5744808 | 7115542.3 | 13004531.48 | 361557 | 450000 | 0 | 0 | 0 | 3151762.44 | 0 | 257418 | 0 | 5068000 | 0 | 1822911.67 | 5347284.94 | 0 | 5314608 | 0 |  | 0 | 0 | 5479830.7 | 3140040 | 11676096 | 2893017.6 | 594034.56 | 2913926.4 | 0 | 0 | 1943892.72 | 4476408 | 0 | 2869480 | 690500.88 | 2482091 | 507605.04 | 1376256 | 0 | 1820510.46 | 0 | 2497204.8 | 5685812.15 | 533140.92 | 50085 | 1400525 | 385207.5 | 24048000 | 3908898.4 | 0 | 346557.6 | 127520 | 2297640 | 1154688 | 2146680 | 1716811.2 | 0 | 3293680 | 2968616.64 | 3938572.8 | 0 | 5383587 | 924180 | 0 | 506001.6 | 7208067 | 406440 | 155040 | 0 | 40498216.92 | 2932632.78 | 261199.84 | 24672960 | 2222773.52 | 30219505.92 | 1652323.05 | 15968784 | 5905872 | 5613336.9 | 3673500 | 10429632 | 11402823.6 | 0 | 0 | 25437063.96 | 7562675.25 | 0 | 13004139.6 | 22028328 | 15389395.2 | 0 | 0 |  | 127817539.2 | 0 | 7377048 | 0 | 8760441.6 | 54366681.6 | 0 | 0 | 0 | 18780.16 | 4864837.5 | 0 | 1062067.75 | 14040345.6 | 0 | 0 | 0 | 3025996.8 | 2434315.68 | 6950630.7 | 0 | 0 | 2626658.61 | 5274460.8 | 0 | 964454.4 | 366494.4 | 172682.298 | 0 | 0 | 19957524 | 0 | 0 | 1321047 | 0 | 5527872.24 | 0 | 3174390 | 9340531.2 | 4909245.12 | 0 | 8443116 | 12818649.6 | 0 | 5735907.84 | 0 | 9922867.2 | 0 | 290637.1 | 9419944.32 | 55558523 |  | 531221113.34 | 386543689.718 | 917764803.058 | 96322160.928 | 127817539.2 | 51189396.15 | 453579182.58 | 75516047 | 257418 | 86964579.05 | 24048000 | 2070480.15 | 0
Yesterday Day Peak | 0 | 0 | 100 | 115 | 200 | 42 | 0 | 0 | 343 |  | 0 | 225 | 150 | 93 | 97 | 40 | 0 | 0 | 185 | 0 | 99 | 84 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 12 | 25 | 33 | 0 | 0 | 45 | 0 | 115 | 0 | 0 | 225 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 18 | 0 | 20 | 35 | 0 | 0 | 70 | 160 | 0 | 37 | 8 | 94 | 3 | 5 | 0 | 43 | 0 | 0 | 0 | 18 | 0 | 33 | 21 | 106 | 152 | 0 | 14 | 2 | 60 | 30 | 50 | 44 | 0 | 142 | 62 | 85 | 0 | 86 | 18 | 0 | 10 | 310 | 24 | 8 | 0 | 122 | 0 | 0 | 200 | 0 | 112 | 20 | 90 | 0 | 30 | 52 | 22 | 0 | 0 | 4 | 164 | 18 | 0 | 0 | 110 | 100 | 0 | 104 |  | 926 | 0 | 305 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 40 | 0 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 179 | 0 | 90 | 37 | 181 | 0 | 405 | 35 | 0 | 0 | 0 | 35 | 0 | 3 | 35 | 500 |  | 8595 | DayPeak
Yesterday Evening Peak | 0 | 0 | 120 | 115 | 200 | 42 | 0 | 0 | 353 | 0 | 0 | 225 | 140 | 92 | 97 | 55 | 0 | 0 | 188 | 0 | 100 | 102 | 98 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 28 | 33 | 52 | 0 | 45 | 0 | 115 | 0 | 25 | 204 | 0 | 139 | 0 | 0 | 0 | 0 | 68 | 40 | 91 | 50 | 20 | 42 | 0 | 0 | 55 | 245 | 0 | 142 | 26 | 90 | 29 | 55 | 0 | 51 | 0 | 48 | 52 | 22 | 5 | 33 | 21 | 166 | 160 | 0 | 14 | 0 | 58 | 30 | 53 | 47 | 0 | 140 | 66 | 88 | 0 | 177 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 300 | 25 | 0 | 200 | 0 | 132 | 0 | 100 | 100 | 30 | 82 | 65 | 105 | 0 | 0 | 162 | 52 | 0 | 100 | 113 | 100 | 0 | 104 |  | 925 | 0 | 335 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 42 | 98 | 0 | 0 | 44 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 170 | 0 | 90 | 100 | 175 | 0 | 406 | 53 | 0 | 35 | 0 | 105 | 0 | 0 | 90 | 565 |  | 11238 | EvPeak
Forecast for Evening | 0 | 0 | 120 | 115 | 200 | 42 | 0 | 0 | 360 | 0 | 0 | 225 | 150 | 100 | 100 | 55 | 0 | 0 | 120 | 0 | 100 | 102 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 44 | 0 | 120 | 0 | 25 | 221 | 0 | 145 | 0 | 0 | 0 |  | 100 | 100 | 90 | 50 | 21 | 40 | 0 | 0 | 80 | 360 | 0 | 225 | 26 | 100 | 30 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 8 | 33 | 21 | 173 | 160 | 0 | 17 | 0 | 60 | 30 | 51 | 44 | 0 | 200 | 65 | 86 | 0 | 177 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 85 | 115 | 86 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 104 |  | 935 | 16 | 410 | 0 | 115 | 225 | 0 | 0 | 30 | 60 | 40 | 0 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 0 | 0 | 43 | 52 | 34 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 | 0 | 90 | 100 | 220 | 0 | 414 | 90 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620
Forecast for Day | 0 | 0 | 120 | 115 | 200 | 42 | 0 | 0 | 360 | 0 | 0 | 225 | 150 | 100 | 100 | 55 | 0 | 0 | 120 | 0 | 100 | 102 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 44 | 0 | 120 | 0 | 25 | 221 | 0 | 140 | 0 | 0 | 0 |  | 100 | 100 | 90 | 50 | 21 | 40 | 0 | 0 | 80 | 360 | 0 | 225 | 26 | 100 | 30 | 55 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 33 | 21 | 162 | 160 | 0 | 17 | 1.6 | 60 | 30 | 51 | 44 | 0 | 200 | 65 | 86 | 0 | 177 | 18 | 0 | 10 | 341 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 200 | 150 | 85 | 115 | 85 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 104 |  | 935 | 0 | 410 | 0 | 115 | 225 | 0 | 0 | 0 | 0 | 40 | 0 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 43 | 52 | 0 | 22 | 10 | 10 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 |  | 78 | 50 | 220 | 0 | 414 | 90 | 100 | 100 | 100 | 100 | 0 | 8 | 113 | 620
Generation at 08:00(Today) | 0 | 0 | 121 | 115 | 200 | 41 | 0 | 0 | 303 | 0 | 0 | 225 | 140 |  | 96 | 30 | 0 | 0 | 120 | 0 | 7 | 102 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 22 | 33 | 17 | 0 | 0 | 41 | 0 | 115 | 0 | 0 | 204 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 20 | 13 | 0 | 0 | 80 | 15 | 0 | 179 | 26 | 92 | 27 | 55 | 0 | 51 | 0 | 0 | 0 | 19 | 2 | 33 | 15 | 120 | 157 | 0 | 14 | 1 | 58 | 30 | 47 | 47 | 0 | 140 | 65 | 85 | 0 | 178 | 18 | 0 | 10 | 300 | 24 | 5 | 0 | 230 | 0 | 0 | 200 | 0 | 103 | 10 | 90 | 0 | 30 | 84 | 8 | 17 | 0 | 2 | 122 | 36 | 0 | 0 | 113 | 100 | 0 | 104 | 0 | 918 | 0 | 325 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 190 | 0 | 73 | 0 | 191 | 0 | 337 | 17 | 0 | 35 | 0 | 35 | 0 | 1 | 35 | 500 | 0
199
| Minimum Generation |  | 8097 | 9:00
| Highest Generation |  | 11238 | 21:00
| Day Peak Generation |  | 8595 | 12:00
| Evening Peak Generation |  | 11238 | 21:00
| HVDC Max Flow |  | 926 | 7:00
| HVDC EvPeak Flow |  | 925 | 21:00
| Load factor L.F |  | 85.87%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-10-03
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-10-02 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8595 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 8517 | MW
Evening Peak Generation : |  | 11238 | MW Hour : | 21:00 | Available Max Generation : |  | 13893 | MW
E.P. Demand (at gen end) : |  | 11238 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 11800 | MW
Maximum Generation : |  | 11238 | MW Hour : | 21:00 | Reserve(Generation end) |  | 2093 | MW
Total Gen. (MKWH) : |  | 231.5921 | System Load Factor : | 85.87% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 195 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-10-03
Actual : | 98.92 | Ft.(MSL) , | Rule curve : | 106.18 | Ft.( MSL )
Gas Consumed : | Total = | 1058.57 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 147511557.078
: |  | Coal : | 75516047 | Oil : | 540543761.63 | Total : | 763571365.708
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4187.8731 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1425.8482 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1277.8226 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1154.7306 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1043.4526 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 842.0337 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 468.5854 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 216.7418 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 649.4289 |  |  | 0 | 0%
Total | 0 |  | 11266.517 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ashuganj (S)-360 MW
3) Ghorasal Unit-1,2,3,
4) Ashuganj unit-3,4
5) Kaptai-2,4,5
6) Raozan #1,2
7) Siddirganj-335 MW
8) Baghabari-71 MW,100 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Chowmuhuni 132/33 kV T-2 transformer was under shut down from08:20 to 10:00 due to oil leakage |  |  |  |  | About 10 MW power interruption occurred under Chowmuhuni S/S area
at 33 kV B-phase CT. |  |  |  |  | from 08:20 to 10:00.
b) Shahjibazar 132/33 kV T-4 transformer was under shut down from 09:38 to 17:20 for C/M.
c) Daudkandi 132/33 kV T-2 transformer was under shut down from 11:40 to 16:12 for C/M.
d) Jhenaidah 132/33 kV T-2 transformer was under shut down from 08:15 to 11:52 for C/M.
e) Jhenaidah 132/33 kV T-1 transformer was under shut down from 11:56 to 12:59 for C/M.
f) Gopalganj(N)-Gopalganj(O) 132 kV Ckt tripped at 12:35 showing Dist. Z2 at Gopalganj(N) end and |  |  |  |  | About 50 MW power interruption occurred under Gopalganj S/S area
was switched on at 12:42. |  |  |  |  | from 12:35 to 12:42.
g) Tangail-Kaliakoir 132 kV Ckt-1 was under shut down from 08:24 to 15:01 for C/M.
h) Bhulta-Haripur 132 kV Ckt-1 was under shut down from 10:53 to 12:55 for C/M.
i) Ashuganj 225 MW CCPP ST was shut down at 11:59 due to gas shortage and was synchronized
at 02:29(03-10-2020).
j) Ashuganj unit-5 was shut down at 12:04 due to gas shortage and was synchronized at 20:27.
k) Norail-Magura 132 kV Ckt-1 was under shut down from 12:34 to 21:34 for C/M.
l) Khagrachari 132/33 kV T-1 transformer was under shut down from 10:02 to 12:07 for C/M.
m) Haripur-Meghnaghat 230 kV Ckt-1 was switched on at 21:22.
n) Bagherhat 132/33 kV T1 & T2 transformers tripped at 23:06 due to 33 kv cable fault of T1 transformer |  |  |  |  | About 10 MW power interruption occurred under Bagherhat S/S area
and were switched on at 01:58(03-10-2020), 23:37 respectively. |  |  |  |  | from 23:06 to 23:37.
o) Bakulia 132/33 kV T-3 transformer was shut down at 06:17(03-10-2020) for C/M.
p) Hasnabad-Sitalakha 132 kV Ckt was shut down at 07:32(03-10-2020) for D/W.
q) Hasnabad-Brahmangaon 132 kV Ckt was shut down at 07:45(03-10-2020) for D/W.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-10-02 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 120 | 2594000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 115 | 2772000 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 4846945 | Machin problem.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 42 | 996318 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 353 | 8027000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4842750 | GT-2 Under maint.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 92 | 2175360
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 140 | 3318691 | GT-2 Under S/D due to gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 97 | 2281440
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1080350
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 100 | 727713
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 482076
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 188 | 4321000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 2377920
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under Maintenance
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1748736
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel Shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 786960
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 98 | 972000 | Low demand.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 920510
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1318918
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 47 | 1044240 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 28 | 773300
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 799400
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 52 | 325932
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 5356907
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 25 | 172711 | Low demand.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 15622 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 132941 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 132 | 3071088 | Low demand.
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 1206648
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2601600
| Dhaka area Total |  |  |  | 5895 | 3039 | 62091076
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 115 | 2800000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 196223
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 141345
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 365280
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 45 | 953400 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4905766
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 139 | 3126240
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 564931 | Low demand.
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 40 | 328800 | High voltage
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1959360
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 471456
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 981120
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 91 | 1342080 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 23000
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 162 | 3364691 | Low demand.
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 52 | 868275
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2310720
| Chattogram area Total |  |  |  | 2266 | 1253 | 24702687
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 55 | 1322376 | Under maint.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 142 | 3119000 | ST under maint.
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 245 | 6049200 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Machine problem.
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 449208 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 55 | 983040
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 26 | 535272 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1064626
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 30 | 796218 | R/H at APSCL
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 48 | 247248
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2158340
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 100 | 544320 | Low demand.
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 419796
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 5 | 66780 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 166 | 3206400
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 800300
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 595373
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 513610 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 100 | 1303020 | Engine problem
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 2570400
| Cumilla Area Total |  |  |  | 2980 | 1383 | 26744527
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 160 | 3687640 | Machine problem & Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 14 | 272880 | Engine problem
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 0 | 0 | Man power problem due to corona effected.
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 8000
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 4744800 | Low demand.
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 65 | 1143600 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 439 | 9856920
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 58 | 1401000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 721680 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 140 | 3167000 | Gas shortage & ST under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1206000
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 47 | 1100520
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 204000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 66 | 1506912 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 88 | 2062080
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 177 | 3111900
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 422000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 541920
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7136700 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 82 | 3950000
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 248040
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1094 | 26779752
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 925 | 22190545
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 1114560
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 200 | 3922560 | Low demand.
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 1792 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 335 | 7025760 | Gas shortage.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 466875
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 549120
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 1227840 | Engine problem
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1768 | 36499052
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1438560
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 38 | 685205
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 90 | 2116260 | Engine problem
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 565 | 12655700
| Barisal Area Total |  |  |  | 1054 | 803 | 16895725
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 307520
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 42 | 239598
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel Shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel Shortage
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 44 | 271069
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 1129100 | Gas Shortage
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 170 | 4187782 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 175 | 4195936 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 406 | 8528400 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 502320
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 10 | 236448
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 228114
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 544320
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 98 | 785382
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 35 | 604416 | Engine problem
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 90 | 1274688 | Engine problem
| Rajshahi Area Total |  |  |  | 2183 | 1204 | 23035093
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3682200 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 105 | 1278720 | Engine problem
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 26302
| Rangpur Area Total |  |  |  | 605 | 255 | 4987222
| Total |  |  |  | 19892 | 11238 | 231592054
| Eastern Grid Total |  |  |  | 13766 | 7208 | 150174962
| Western Grid Total |  |  |  | 6126 | 4030 | 81417092
| National Grid Total |  |  |  | 19892 | 11238 | 231592054
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-10-02
| (a) ENTIRE EASTERN GRID : |  | 7213 | MW | (b) ENTIRE WESTERN GRID : |  | 3507 | MW
| i) Dhaka area |  | 3550 | MW | i) Khulna area |  | 1361 | MW
| ii) Chittagong area |  | 1194 | MW | ii) Rajshahi area |  | 1099 | MW
| iii) Comilla area |  | 1127 | MW | iii) Barisal area |  | 336 | MW
| iv) Mymensingh area |  | 858 | MW | iv) Rangpur area |  | 711 | MW
| v) Sylhet area |  | 484 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 10720 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 116 | 24:00 | Sherpur | 98 | 1:00 | Jhenida | 104 | 18:30
| Munsiganj | 120 | 1:00 | Srimongal | 49 | 19:30 | Bottail | 108 | 18:30
| Sonargaon | 82 | 1:00 | Shahjibazar | 114 | 21:00 | G.K Project | 49 | 18:30
| Shyampur | 184 | 3:00 | Fenchuganj | 44 | 1:00 | Faridpur | 168 | 0.91667
| Bhulta | 183 | 24:00 | Kulawara | 44 | 18:00 | Madaripur | 96 | 0.875
| Madanganj | 50 | 5:00 | Sylhet | 121 | 19:00 | Sariatpur | 62 | 21:00
| Shitalakhya | 82 | 2:00 | Chatak | 28 | 1:00 | Gopalganj | 83 | 21:00
| Rahim steel | 4 | 7:00 | Sunamganj | 44 | 19:30 | Bagerhat | 90 | 21:00
| Matuail | 72 | 6:00 | Biani Bazar | 56 | 18:00 | Mongla | 36 | 1:00
| Ghorasal | 71 | 22:00 | Comilla (S) | 170 | 22:00 | Satkhira | 105 | 0.83333
| Narsingdi | 167 | 1:00 | Comilla(N) | 111 | 21:00 | Gallamari | 41 | 1:00
| Haripur (SBU) | 85 | 2:00 | Chandpur | 104 | 18:30 | Magura | 50 | 0.77083
| Ullon | 58 | 19:00 | Feni | 100 | 18:30 | Norail | 36 | 21:00
| Hasnabad | 181 | 1:00 | Chowmuhani | 172 | 21:00 | Chuadanga | 87 | 18:30
| Magbazar | 79 | 18:00 | Ashuganj | 59 | 22:00 | Barisal(N) | 41 | 0.875
| Maniknagar | 76 | 22:00 | Daudkandi | 134 | 20:00 | Barisal (S) | 90 | 0.875
| Bangabhaban | 15 | 18:00 | B.Baria | 151 | 20:00 | Patuakhali | 115 | 0.91667
| Narinda | 76 | 23:00 | Ramganj | 110 | 20:00 | Bhandaria | 50 | 0.83333
| Dhanmondi | 126 | 12:00 | Chaddagram | 37 | 22:00 | Borhan Uddin | 45 | 1:00
| Lalbag | 67 | 1:00 | PHP | 5 | 21:00 | Ishurdi | 54 | 20:00
| Madartek | 71 | 23:00 | Madunaghat | 53 | 20:00 | Ruppur Paromanobik | 2 | 7:00
| Dhaka University |  |  | Hathazari | 94 | 0.79167 | Natore | 107 | 21:00
| Fatullah | 40 | 0.041667 | Khulshi | 184 | 0.8125 | Bogra | 145 | 20:00
| Mirpur | 95 | 19:30 | Halishahar | 128 | 0.75 | Noagaon | 105 | 21:00
| Kalyanpur | 86 | 19:30 | Baraulia | 127 | 0.125 | Rajshahi | 125 | 20:00
| Gulshan | 100 | 18:30 | Sikalbaha | 27 | 0.77083 | Rajshahi New | 9 | 20:00
| Uttara | 85 | 19:00 | Dohazari | 76 | 0.79167 | C.Nawabganj | 63 | 19:00
| Uttara New | 27 | 19:00 | Cox'sbazar | 102 | 0.875 | Amnura | 38 | 19:00
| Kamrangirchar | 71 | 20:00 | Chandraghona | 30 | 0.77083 | Pabna | 107 | 20:00
| Savar | 109 | 20:00 | Kaptai | 4.4 | 0.77083 | Shahjadpur | 93 | 20:00
| Bhasantec | 137 | 18:30 | A. Khaer Stl. | 8 | 0.125 | Serajganj | 78 | 20:00
| Agargaon | 64 | 18:30 | Bakulia | 91 | 0.95833 | Niyamatpur | 49 | 21:00
| Satmosjid | 97 | 18:30 | Julda | 21 | 0.041667 | Joypurhat | 48 | 19:30
| Tongi | 80 | 0.041667 | TK chemical | 28.8 | 0.91667 | Sherpur(Bogura) | 42 | 18:30
| Kabirpur | 149 | 1:00 | Modern Steel | 13 | 0.041667 | Mohastangor | 44 | 19:00
| Basundhara | 124 | 18:00 | Shahmirpur | 20 | 0.041667 | Rangpur | 139 | 19:00
| Manikganj | 74 | 0.77083 | Khagrachhari | 24 | 0.66667 | Lalmonirhat | 55 | 22:00
| Joydevpur | 121 | 1:00 | Matarbari | 39 | 0.875 | Saidpur | 91 | 19:00
| New Tongi | 85 | 1:00 | Baroiar Hat | 60 | 0.77083 | Purbasadipur | 93 | 20:00
| Korda | 190 | 21:00 | Rangamati | 12 | 0.77083 | Thakurgaon | 76 | 19:30
| Dhamrai | 76 | 19:30 | Abul Khair 230 | 60 | 0.5 | Palashbari | 115 | 19:30
| Rajendrapur | 84 | 22:00 | BSRM | 140 | 0.54167 | Barapukuria | 42 | 1:00
| Valuka | 116 | 1:00 | GPH Ispat | 70 | 0.20833 | Panchagar | 51 | 18:00
| Tangail | 180 | 21:00 | Goalpara | 26 | 0.041667 | Joldhaka | 26 | 19:00
| Mymensing | 166 | 21:00 | Central s/s | 75 | 19:00 | Kurigram | 54 | 19:30
| Kishorganj | 134 | 24:00 | Noapara | 47 | 19:00
| Netrokona | 109 | 19:00 | Jessore | 99 | 18:30
| Jamalpur | 125 | 1:00 | Benapol | 44 | 18:30
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-10-02 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 398 | 6:00 | 391 | 11:00 | Kaliakoir | 381 | 0.29167 | 375 | 0.41667
| Bheramara | 395 | 14:00 | 389 | 19:00 | Bhulta | 392 | 0.25 | 382 | 0.5
| Ashuganj(N) | 395 | 13:00 | 385 | 16:00 | Gopalganj | 416 | 0.29167 | 390 | 0.91667
| Payra | 417 | 19:00 | 404 | 19:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 1:00 | 232 | 10:00 | Comilla (N) | 237 | 14:00 | 233 | 4:00
| Ishurdi | 235 | 8:00 | 227 | 3:00 | Hathazari | 229 | 14:00 | 224 | 9:00
| Ashuganj | 238 | 18:30 | 232 | 2:00 | Megnaghat | 234 | 17:00 | 230 | 1:00
| Serajganj | 230 | 7:00 | 225 | 1:00 | Fenchuganj | 238 | 14:00 | 232 | 19:00
| Baghabari | 240 | 6:00 | 236 | 1:00 | Siddhirganj | 233 | 18:30 | 228 | 12:00
| Barapukuria | 238 | 17:00 | 229 | 19:30 | Maniknagar | 232 | 18:30 | 227 | 12:00
| Bogra | 228 | 17:00 | 216 | 21:00 | Agargaon | 230 | 6:00 | 224 | 10:00
| Rajshahi | 228 | 8:00 | 220 | 3:00 | Barisal | 248 | 15:00 | 235 | 20:00
| Khulna South | 236 | 14:00 | 225 | 3:00 | AKSML | 226 | 14:00 | 220 | 4:00
| Rampura | 230 | 15:00 | 227 | 11:00 | BSRM | 229 | 15:00 | 222 | 5:00
| Haripur | 232 | 19:00 | 225 | 11:00 | Bibiyana | 237 | 17:00 | 233 | 3:00
| Hasnabad | 230 | 1:00 | 225 | 3:00 | Bhulta | 234 | 19:00 | 228 | 17:00
| Shyampur | 229 | 19:00 | 224 | 3:00 | Ashuganj (S) | 235 | 14:00 | 231 | 12:00
| Aminbazar | 231 | 18:00 | 226 | 2:00 | Kaliakoir | 233 | 18:00 | 228 | 3:00
| Tongi | 231 | 23:00 | 225 | 9:00 | GPH | 224 | 18:00 | 219 | 8:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 133 | 18:00 | 126 | 10:00 | Hathazari | 135 | 0.16667 | 132 | 0.45833
| Munsiganj | 134 | 19:00 | 128 | 10:00 | Khulshi | 133 | 0.041667 | 130 | 0.45833
| Sonargaon | 135 | 19:00 | 129 | 9:00 | Halishahar | 135 | 0.70833 | 132 | 0.41667
| Shyampur | 135 | 18:30 | 127 | 11:00 | Baraulia | 135 | 0.083333 | 131 | 0.45833
| Bhulta | 125 | 0:00 | 119 | 11:00 | Sikalbaha | 137 | 19:30 | 133 | 0.45833
| Madanganj | 132 | 17:00 | 128 | 10:00 | Dohazari | 133 | 17:00 | 128 | 0.45833
| Shitalakhya | 142 | 19:00 | 132 | 10:00 | Cox'sbazar | 126 | 0.70833 | 120 | 0.45833
| Rahim steal | 132 | 19:00 | 126 | 11:00 | Chandraghona | 135 | 0.70833 | 132 | 0.45833
| Matuail | 133 | 18:00 | 126 | 10:00 | Kaptai | 135 | 22:00 | 132 | 0.041667
| Ghorasal | 139 | 19:30 | 136 | 9:00 | A. Khaer Stl. | 135 | 0.41667 | 129 | 15:00
| Narsinghdi | 126 | 6:00 | 120 | 11:00 | Bakulia | 135 | 0.77083 | 131 | 0.45833
| Haripur (SBU) | 133 | 6:00 | 126 | 11:00 | Julda | 136 | 0.70833 | 133 | 0.16667
| Ullon | 134 | 4:00 | 128 | 10:00 | TK Chemical | 135 | 0.041667 | 129 | 7:00
| Hasnabad | 139 | 18:30 | 130 | 9:00 | Modern Steel | 135 | 0.875 | 132 | 0.25
| Magbazar | 135 | 4:00 | 125 | 13:00 | Shahmirpur | 136 | 0.91667 | 132 | 0.45833
| Maniknagar | 134 | 6:00 | 127 | 10:00 | Khagrachhari | 133 | 0.041667 | 131 | 0.41667
| Bangabhaban | 134 | 6:00 | 127 | 10:00 | Matarbari | 125 | 0.54167 | 123 | 0.041667
| Narinda | 134 | 6:00 | 127 | 10:00 | Baroiar Hat | 136 | 0.77083 | 131 | 0.041667
| Dhanmondi | 134 | 4:00 | 128 | 10:00 | Rangamati | 134 | 0.25 | 131 | 11:00
| Lalbag | 139 | 18:30 | 127 | 10:00 | Goalpara S/S | 137 | 16:00 | 132 | 2:00
| Madartek | 134 | 6:00 | 126 | 11:00 | Khulna Central S/S | 138 | 0.70833 | 131 | 4:00
| Dhaka University |  |  |  |  | Noapara | 135 | 16:00 | 127 | 3:00
| Fatuiiah | 135 | 0.79167 | 127 | 10:00 | Jessore | 131 | 17:00 | 123 | 1:00
| Mirpur | 136 | 3:00 | 128 | 10:00 | Benapol | 132 | 17:00 | 122 | 2:00
| Kalyanpur | 137 | 2:00 | 130 | 10:00 | Jhenida | 126 | 0.41667 | 117 | 19:30
| Gulshan | 134 | 6:00 | 125 | 11:00 | Bottail | 133 | 3:00 | 126 | 19:30
| Uttara | 136 | 23:00 | 128 | 10:00 | G.K Project | 140 | 0.54167 | 135 | 15:00
| Uttara New | 136 | 6:00 | 128 | 10:00 | Faridpur | 132 | 6:00 | 125 | 19:30
| Kamrangirchar | 139 | 18:00 | 126 | 10:00 | Madaripur | 138 | 0.54167 | 129 | 22:00
| Savar | 136 | 5:00 | 128 | 10:00 | Shariyatpur S/S | 137 | 0.29167 | 126 | 20:00
| Bhasantec | 137 | 4:00 | 129 | 11:00 | Gopalganj | 138 | 7:00 | 125 | 19:30
| Agargaon | 138 | 4:00 | 131 | 11:00 | Bagerhat | 132 | 13:00 | 125 | 1:00
| Satmosjid | 138 | 3:00 | 130 | 11:00 | Mongla | 129 | 0.70833 | 123 | 1:00
| Tongi | 137 | 0.95833 | 131 | 9:00 | Satkhira | 136 | 0.70833 | 128 | 1:00
| Kabirpur | 133 | 17:00 | 130 | 14:00 | Gallamari | 137 | 16:00 | 131 | 3:00
| Basundhara | 134 | 4:00 | 126 | 10:00 | Magura | 128 | 18:00 | 115 | 19:30
| Manikganj | 138 | 21:00 | 131 | 11:00 | Norail | 126 | 0.70833 | 114 | 19:30
| Joydevpur | 141 | 21:00 | 136 | 8:00 | Chuadanga | 120 | 6:00 | 107 | 19:30
| New Tongi | 137 | 0.95833 | 129 | 10:00 | Barisal(N) | 140 | 17:.00 | 131 | 3:00
| Kodda | 137 | 17:00 | 125 | 0.33333 | Barisal (S) | 138 | 0.70833 | 130 | 3:00
| Dhamrai | 133 | 13:00 | 129 | 11:00 | Patuakhali(S) | 134 | 0.29167 | 123 | 22:00
| Rajendrapur | 135 | 23:00 | 122 | 9:00 | Bhandaria | 130 | 17:00 | 120 | 1:00
| Valuka | 129 | 15:00 | 110 | 1:00 | Ishurdi | 138 | 14:00 | 133 | 19:30
| Tangail | 134 | 13:00 | 123 | 1:00 | Ruppur Paromanobik | 136 | 13:00 | 133 | 20:00
| Mymensing | 132 | 15:00 | 116 | 1:00 | Natore | 138 | 16:00 | 131 | 19:00
| Kishorganj | 132 | 17:00 | 117 | 1:00 | Bogra | 136 | 13:00 | 128 | 19:30
| Netrokona | 127 | 9:00 | 110 | 1:00 | Noagaon | 133 | 17:00 | 120 | 20:00
| Jamalpur | 139 | 13:00 | 120 | 21:00 | Rajshahi | 138 | 13:00 | 132 | 19:00
| Sherpur | 139 | 17:00 | 123 | 21:00 | Rajshahi New | 140 | 17:00 | 132 | 4:00
| Srimongal | 136 | 6:00 | 132 | 0.375 | C.Nawabganj | 136 | 13:00 | 128 | 11:00
| Shahjibazar | 136 | 7:00 | 131 | 0.041667 | Amnura | 137 | 16:00 | 131 | 3:00
| Fenchuganj | 135 | 6:00 | 131 | 0.041667 | Pabna | 136 | 17:00 | 129 | 20:00
| Khulawara | 133 | 5:00 | 131 | 0.041667 | Shahjadpur | 138 | 13:00 | 134 | 19:30
| Sylhet | 138 | 18:00 | 129 | 0.041667 | Serajganj | 134 | 17:00 | 128 | 19:30
| Chatak | 129 | 6:00 | 125 | 1:00 | Niyamatpur | 132 | 6:00 | 118 | 19:30
| Sunamganj | 129 | 17:00 | 122 | 0.041667 | Joypurhat | 135 | 16:00 | 119 | 19:30
| Biani Bazar | 131 | 10:00 | 125 | 0.041667 | Sherpur(Bogura) | 135 | 13:00 | 127 | 19:30
| Comilla(s) | 127 | 6:00 | 121 | 21:00 | Mohastangor | 136 | 16:00 | 125 | 20:00
| Comilla(n) | 141 | 18:30 | 134 | 15:00 | Rangpur | 132 | 14:00 | 117 | 20:00
| Chandpur | 140 | 1:00 | 130 | 6:00 | Lalmonirhat | 132 | 16:00 | 116 | 18:30
| Feni | 137 | 18:30 | 131 | 9:00 | Saidpur | 130 | 14:00 | 120 | 19:00
| Chowmuhani | 134 | 18:00 | 130 | 7:00 | Purbasadipur | 129 | 16:00 | 113 | 18:30
| Ashuganj | 136 | 17:00 | 133 | 2:00 | Thakurgaon | 128 | 16:00 | 115 | 19:00
| Daudkandi | 135 | 18:00 | 128 | 15:00 | Palashbari | 132 | 16:00 | 120 | 19:00
| B.Baria | 133 | 7:00 | 128 | 22:00 | Barapukuria | 137 | 17:00 | 127 | 20:00
| Ramganj | 130 | 19:30 | 123 | 24:00 | Panchagar | 126 | 17:00 | 112 | 19:00
| Chaddagram | 138 | 19:00 | 132 | 14:00 | Joldhaka | 131 | 14:00 | 115 | 19:00
| PHP | 135 | 23:00 | 129 | 15:00 | Kurigram | 130 | 14:00 | 114 | 20:00
| Madanhat | 137 | 18:30 | 134 | 10:00

## L-Curve
Date | 2020-10-02
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 347 | 7017 | 3770 | 10787 |  |  |  | QF-LDC-11
0:30 | 271 | 7042 | 3692 | 10734 | Date: | 2020-10-02
1:00 | 195 | 7067 | 3614 | 10681
1:30 | 299 | 6789.5 | 3624.5 | 10414
2:00 | 403 | 6512 | 3635 | 10147
2:30 | 408 | 6421.5 | 3622.5 | 10044 | [5 empty] | Gen. at Eve. Peak | 11238 | 11238 MW (21:00 )
3:00 | 413 | 6331 | 3610 | 9941 | [6 empty] | 21:00
3:30 | 372.5 | 6329.5 | 3542.5 | 9872 | [5 empty] | Gen. at Day Peak | 8595 | 8595 MW (12:00 )
4:00 | 332 | 6328 | 3475 | 9803 | [6 empty] | 12:00
4:30 | 289 | 6295.5 | 3396.5 | 9692 | [5 empty] | Highest Generation | 11238
5:00 | 246 | 6263 | 3318 | 9581 | [6 empty] | 21:00
5:30 | 302.5 | 6136 | 3182.5 | 9318.5
6:00 | 359 | 6009 | 3047 | 9056
6:30 | 359.5 | 5811 | 2951 | 8762
7:00 | 360 | 5613 | 2855 | 8468
7:30 | 323.5 | 5548 | 2760 | 8308
8:00 | 287 | 5483 | 2665 | 8148
8:30 | 318.5 | 5433.5 | 2689 | 8122.5
9:00 | 350 | 5384 | 2713 | 8097
9:30 | 390 | 5372.5 | 2761.5 | 8134
10:00 | 430 | 5361 | 2810 | 8171
10:30 | 452 | 5411.5 | 2863.5 | 8275
11:00 | 474 | 5462 | 2917 | 8379
11:30 | 528 | 5471 | 3016 | 8487
12:00 | 582 | 5480 | 3115 | 8595
12:30 | 520 | 5623 | 3116 | 8739
13:00 | 458 | 5766 | 3117 | 8883
13:30 | 424 | 5767 | 3034 | 8801
14:00 | 390 | 5768 | 2951 | 8719
14:30 | 450 | 5808 | 2974 | 8782
15:00 | 510 | 5848 | 2997 | 8845
15:30 | 588 | 5606 | 2954.5 | 8560.5
16:00 | 666 | 5364 | 2912 | 8276
16:30 | 622 | 5337.5 | 2906 | 8243.5
17:00 | 578 | 5311 | 2900 | 8211
17:30 | 465.5 | 5686 | 3144 | 8830
18:00 | 353 | 6061 | 3388 | 9449
18:30 | 316.5 | 6474.5 | 3659.5 | 10134
19:00 | 280 | 6888 | 3931 | 10819
19:30 | 302 | 7113 | 3955 | 11068
20:00 | 299 | 7166 | 4005 | 11171 |  |  |  | Executive Engineer
20:30 | 297.5 | 7187 | 4017.5 | 11204.5 |  |  |  | Network Operation Division
21:00 | 296 | 7208 | 4030 | 11238
21:30 | 321.5 | 7175.5 | 4015.5 | 11191
22:00 | 347 | 7143 | 4001 | 11144 |  |  |  |  | Page 6 of 7
22:30 | 354.5 | 7134.5 | 3932.5 | 11067
23:00 | 362 | 7126 | 3864 | 10990
23:30 | 354.5 | 7071.5 | 3817 | 10888.5
24:00 | 347 | 7017 | 3770 | 10787
11238 MW (21:00 )
8595 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-10-02 |  | Energy | 231592054
[10 empty] | 2020-10-02 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3273 | 925 | 1817 | 3330 | 710 | 45 | 621 | 0 | 162
0:30 | 3483 | 925 | 1681 | 3231.5 | 710 | 44.5 | 557 | 0 | 150 | Date: | 2020-10-02
1:00 | 3693 | 925 | 1545 | 3133 | 710 | 44 | 493 | 0 | 138
1:30 | 3680 | 924.5 | 1683.5 | 2829.5 | 710 | 43.5 | 406 | 0 | 137 | [7 empty] | Total Energy | 231.5921 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 3667 | 924 | 1822 | 2526 | 710 | 43 | 319 | 0 | 136 | [7 empty] | Energy not Served | 0
2:30 | 3685 | 924.5 | 1838 | 2426 | 710 | 42 | 284.5 | 0 | 134 | [7 empty] | Energy Requirement | 231.5921
3:00 | 3703 | 925 | 1854 | 2326 | 710 | 41 | 250 | 0 | 132
3:30 | 3663 | 925 | 1850.5 | 2318.5 | 695 | 41 | 248 | 0 | 131 | [6 empty] | Shortage
4:00 | 3623 | 925 | 1847 | 2311 | 680 | 41 | 246 | 0 | 130
4:30 | 3593.5 | 925 | 1850.5 | 2250 | 680 | 41 | 226 | 0 | 126
5:00 | 3564 | 925 | 1854 | 2189 | 680 | 41 | 206 | 0 | 122
5:30 | 3481.5 | 925 | 1768.5 | 2130 | 680 | 41.5 | 173 | 0 | 119
6:00 | 3399 | 925 | 1683 | 2071 | 680 | 42 | 140 | 0 | 116
6:30 | 3455 | 925.5 | 1667.5 | 1823 | 605 | 42.5 | 130 | 0 | 110 |  |  |  |  | Coal
7:00 | 3511 | 926 | 1652 | 1575 | 530 | 43 | 120 | 0 | 104
7:30 | 3431 | 925.5 | 1658 | 1517.5 | 505 | 43 | 120 | 0 | 100 |  |  |  | Oil |  |  |  | ,
8:00 | 3351 | 925 | 1664 | 1460 | 480 | 43 | 120 | 0 | 96
8:30 | 3322.5 | 925 | 1648.5 | 1463 | 480 | 43.5 | 120 | 0 | 103
9:00 | 3294 | 925 | 1633 | 1466 | 480 | 44 | 120 | 0 | 110
9:30 | 3296 | 925 | 1670.5 | 1464.5 | 480 | 44 | 120 | 0 | 109
10:00 | 3298 | 925 | 1708 | 1463 | 480 | 44 | 120 | 0 | 108
10:30 | 3234 | 925 | 1767 | 1538 | 515 | 44 | 120 | 0 | 106
11:00 | 3170 | 925 | 1826 | 1613 | 550 | 44 | 120 | 0 | 104
11:30 | 3074.5 | 925.5 | 1785 | 1804.5 | 600 | 44.5 | 120 | 0 | 105
12:00 | 2979 | 926 | 1744 | 1996 | 650 | 45 | 120 | 0 | 106
12:30 | 2904.5 | 925.5 | 1747.5 | 2194 | 655 | 44.5 | 120 | 0 | 120
13:00 | 2830 | 925 | 1751 | 2392 | 660 | 44 | 120 | 0 | 134
13:30 | 2830 | 925 | 1751 | 2392 | 660 | 44 | 120 | 0 | 134
14:00 | 2830 | 925 | 1751 | 2392 | 660 | 44 | 120 | 0 | 134
14:30 | 2716.5 | 924.5 | 1678 | 2536 | 680 | 42.5 | 128 | 0 | 135
15:00 | 2603 | 924 | 1605 | 2680 | 700 | 41 | 136 | 0 | 136
15:30 | 2639 | 924.5 | 1627.5 | 2367.5 | 680 | 38 | 136 | 0 | 133
16:00 | 2675 | 925 | 1650 | 2055 | 660 | 35 | 136 | 0 | 130
16:30 | 2707.5 | 925 | 1626 | 2016 | 664.5 | 35 | 139 | 0 | 124
17:00 | 2740 | 925 | 1602 | 1977 | 669 | 35 | 142 | 0 | 118
17:30 | 2862 | 925 | 1636 | 2297 | 669.5 | 38 | 266 | 0 | 135
18:00 | 2984 | 925 | 1670 | 2617 | 670 | 41 | 390 | 0 | 152
18:30 | 3030.5 | 925 | 1732.5 | 3045 | 692 | 42 | 513 | 0 | 154
19:00 | 3077 | 925 | 1795 | 3473 | 714 | 43 | 636 | 0 | 156
19:30 | 3130 | 925 | 1850 | 3571 | 715 | 43 | 668 | 0 | 166
20:00 | 3247 | 925 | 1853 | 3572 | 714 | 44 | 652 | 0 | 164
20:30 | 3295.5 | 925 | 1850 | 3560 | 714.5 | 44.5 | 650 | 0 | 165
21:00 | 3344 | 925 | 1847 | 3548 | 715 | 45 | 648 | 0 | 166
21:30 | 3345.5 | 925 | 1837 | 3508.5 | 712.5 | 45.5 | 649 | 0 | 168
22:00 | 3347 | 925 | 1827 | 3469 | 710 | 46 | 650 | 0 | 170
22:30 | 3364.5 | 925 | 1829 | 3399.5 | 710 | 45.5 | 624.5 | 0 | 169
23:00 | 3382 | 925 | 1831 | 3330 | 710 | 45 | 599 | 0 | 168
23:30 | 3327.5 | 925 | 1824 | 3330 | 710 | 45 | 610 | 0 | 165 | Max Temp. in Dhaka |  | 33.8° C
24:00 | 3273 | 925 | 1817 | 3330 | 710 | 45 | 621 | 0 | 162
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
Note on W13: Author:

## Generation
g | 2020-10-02
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 44 | 43 | 41 | 41 | 41 | 42 | 43 | 43 | 44 | 44 | 44 | 45 | 44 | 44 | 41 | 35 | 35 | 41 |  | 43 | 43 | 44 | 45 | 46 | 45 | 45 | 953400
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | [16 empty] | 5 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 196223
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 5 | 5 | 18 | 18 | 20 | 20 | 20 | 18 | 14 | 8 | 2 | [9 empty] | 141345
6 | Sikalbaha 225MW CCPP (Gas) | 202 | 202 | 203 | 203 | 205 | 203 | 203 | 203 | 204 | 216 | 204 | 225 | 206 | 205 | 204 | 204 | 204 | 217 |  | 204 | 216 | 206 | 204 | 204 | 204 | 203 | 4905766
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 139 | 139 | 139 | 141 | 140 | 140 | 139 | 139 | 104 | 104 | 140 | 145 | 143 | 138 | 139 | 139 | 139 | 144 |  | 104 | 104 | 139 | 139 | 139 | 140 | 139 | 3126240
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 17 | [15 empty] | 82 |  | 102 | 102 | 68 | 68 | 68 | 68 | 68 | 564931
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [19 empty] | 23 | 50 | 50 | 48 | 50 | 50 | 50 | 247248
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 189 | 181 | 191 | 190 | 192 | 190 | 183 | 188 | 185 | 195 | 187 | 185 | 185 | 150 | 183 | 150 | 155 | 80 |  | 80 | 120 | 165 | 188 | 170 | 195 | 195 | 4321000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 300 | 245 | 245 | 245 | 220 | 215 | 60 | 60 | 60 | 60 | 60 | 122 | 275 | 270 | 268 | 200 | 200 | 200 |  | 280 | 300 | 300 | 300 | 300 | 300 | 300 | 5356907
19 | Ashuganj 195MW PP (APSCL-United) | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 8 | 8 | 8 | 8 | 8 | 8 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 535272
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 99 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 114 | 119 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2594000
23 | Ghorasal TPP Unit-5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2772000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4846945
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 100 | 100 | 100 | 100 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 70 | 0 | [9 empty] | 55 | 80 | 80 | 80 | 1322376
32 | Ashuganj 50 MW PP | 29 | 29 | 29 | 29 | 26 | 26 | 23 | 20 | 20 | 26 | 26 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 26 | 26 | 29 | 29 | 29 | 29 | 29 | 449208
33 | Ashuganj 225 MW CCPP | 178 | 177 | 181 | 177 | 193 | 178 | 178 | 178 | 178 | 198 | 124 | 37 | 24 | 13 | 10 | 8 | 28 | 130 |  | 143 | 141 | 141 | 142 | 142 | 142 | 30 | 3119000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 325 | 325 | 325 | 325 | 340 | 295 | 275 | 275 | 275 | 310 | 280 | 160 | 168 | 145 | 50 | 50 | 170 | 210 |  | 245 | 240 | 245 | 245 | 245 | 245 | 245 | 6049200
35 | Ashuganj 55 MW PP (Precision) | 55 | 55 | 54 | 55 | 55 | 54 | 55 | 55 | 55 | 55 | 54 | 5 | 5 | 5 | 6 | 5 | 5 | 5 |  | 45 | 45 | 55 | 55 | 55 | 55 | 55 | 983040
36 | Chandpur 150 MW CCPP | 95 | 94 | 96 | 92 | 96 | 92 | 85 | 85 | 90 | 94 | 96 | 94 | 86 | 88 | 85 | 96 | 85 | 85 |  | 92 | 94 | 95 | 90 | 85 | 92 | 87 | 2158340
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 4842750
41 | Haripur 360MW CCPP(HPL) | 352 | 354 | 353 | 355 | 353 | 303 | 303 | 303 | 271 | 271 | 347 | 343 | 343 | 332 | 345 | 345 | 350 | 347 |  | 351 | 350 | 351 | 353 | 353 | 353 | 353 | 8027000
42 | RPCL 210MW CCPP | [6 empty] | 158 | 158 | 158 | 154 | 154 | 152 | 150 | 150 | 158 | 155 | 159 | 160 |  | 160 | 157 | 160 | 160 | 160 | 160 | 159 | 3687640
43
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 57 | 58 | 58 | 57 |  | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 1401000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 721680
46 | Shajibazar 330 MW CCPP | 141 | 140 | 141 | 140 | 139 | 140 | 140 | 142 | 142 | 142 | 141 | 142 | 140 | 140 | 141 | 144 | 141 | 139 |  | 141 | 140 | 140 | 140 | 140 | 142 | 142 | 3167000
47 | Shahjibazar GTPP Unit- 8 & 9 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 64 | 62 | 62 | 62 | 63 | 65 | 63 | 66 | 40 | 66 |  | 40 | 40 | 66 | 66 | 67 | 67 | 67 | 1506912
48 | Shahjibazar 86MW PP (Shahjibazar) | 88 | 88 | 88 | 88 | 88 | 88 | 85 | 85 | 83 | 83 | 88 | 85 | 83 | 84 | 88 | 88 | 88 | 88 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 2062080
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 140 | 140 | 140 | 140 | 140 | 101 | 100 | 80 | 20 | 20 | 35 | 86 | 111 | 120 | 161 | 161 | 168 | 175 |  | 179 | 178 | 177 | 177 | 178 | 178 | 178 | 3111900
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 422000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 248040
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 204000
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 49 | 50 | 53 | 34 |  | 53 | 50 | 50 | 53 | 53 | 50 | 50 | 1206000
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 10 | 15 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 541920
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 270 | 290 | 290 | 295 | 290 | 280 | 280 | 280 | 290 | 310 | 310 | 310 | 280 | 290 | 270 | 290 | 280 |  | 270 | 310 | 300 | 290 | 290 | 285 | 290 | 7136700
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1318918
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 471456
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 482076
62 | Tangail 22 MW PP (Doreen) | 14 | 14 | 14 | 14 |  |  |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 272880
63 | Impoprt (Tripura) | 138 | 136 | 132 | 130 | 122 | 116 | 104 | 96 | 110 | 108 | 104 | 106 | 134 | 134 | 136 | 130 | 118 | 152 |  | 156 | 166 | 164 | 166 | 170 | 168 | 162 | 3206400
64 | Malancha, Ctg. EPZ (United) | 40 | 41 | 41 | 42 | 42 | 42 | 42 | 42 | 42 | 35 | 35 | 35 | 39 | 39 | 37 | 36 | 37 | 37 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 981120
65 | Feni 22MW PP (Doreen) | 18 | 18 | 18 | 18 |  | 16 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 419796
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | [13 empty] | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 66780
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 18 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 800300
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 |  | 16 | 20 | 20 | 21 | 21 | 21 | 21 | 513610
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 22 | 22 | 17 | 22 | 23 | 23 | 23 | 23 | 22 | 22 | 12 | 12 | 16 | 16 | 9 | 12 | 16 | 14 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 444240
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 28 | 28 | 28 | 28 | 25 | 25 |  | 25 | 25 | 25 | 28 | 28 | 28 | 28 | 773300
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 17 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 799400
73 | Ghorashal 108MW PP (Regent) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 41 | 41 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 41 | 41 | 41 | 996318
| Feni Lanka Power | 100 | 40 | [10 empty] | 55 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1303020
| Chowmuhani 113 MW | 106 | 107 | 108 | 110 | 112 | 113 | 108 | 113 | 113 | 106 | 105 | 110 | 107 | 104 | 112 | 110 | 68 | 67 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2570400
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 100 | 100 | 100 | 100 | 100 | 91 | 89 | 100 | 100 | 100 | 99 | 99 | 99 | 99 | 99 | 99 | 100 |  | 100 | 100 | 100 | 100 | 94 | 94 | 100 | 2377920
78 | Gazipur 52 MW PP | [17 empty] | 13 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 325932
79 | Kodda 150MW PP | 114 | 48 | 20 | 16 | 16 | [9 empty] | 16 | 16 | 16 | 70 |  | 98 | 98 | 98 | 98 | 98 | 98 | 150 | 972000
80 | Jamalpur 95 MW PP(Powerpac) | [25 empty] | 0 | 0
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 25 | 25 | 25 | [9 empty] | 33 | 52 | 8 | 8 | 9 |  | 45 | 52 | 52 | 52 | 52 | 52 | 52 | 595373
| Gazipur 100 MW PP | 98 | 34 | 17 | 16 | [8 empty] | 6 | 73 | 104 | 34 | 34 | 45 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1206648
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 4 | 3 | 3 | 4 | 2 | 1 | 3 | 0 | [10 empty] | 23000
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 41 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 26 | 47 |  | 52 | 52 | 52 | 52 | 52 | 52 | 38 | 868275
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | 97 | 97 | 97 | 97 | 97 | 80 | 80 | 80 | 80 | 92 | 95 | 97 | 97 | 97 | 97 | 97 | 97 | 97 |  | 97 | 97 | 97 | 97 | 97 | 97 | 96 | 2281440
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 50 | [16 empty] | 28 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 727713
86 | Meghnaghat CCPP(Summit) | 140 | 135 | 145 | 140 | 145 | 140 | 135 | 138 | 140 | 150 | 140 | 150 | 145 | 130 | 125 | 140 | 130 | 150 |  | 138 | 145 | 140 | 140 | 130 | 136 | 135 | 3318691
87 | Meghnaghat 100 MW(IEL) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 96 | 93 | 92 | 93 | 100 | 100 | 95 | 92 |  | 92 | 92 | 92 | 92 | 55 | 33 | 24 | 2175360
| Meghnaghat 104 MW PP (OPCL) | 100 | 104 | 98 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 2601600
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 30 | [16 empty] | 50 |  | 60 | 60 | 40 | 40 | 40 | 40 | 20 | 328800
92 | Fenchuganj 44MW (Energyprima) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 44 | 44 | 44 | 44 | 44 | 46 | 47 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 1100520
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 51 | 51 | 5 | 5 | 5 | 5 |  | 28 | 51 | 51 | 51 | 51 | 51 | 51 | 1064626
94 | Gagnagar 102 MW PP (Digital Power) | 102 | 50 | 50 | 50 | 50 | 50 | 24 | 7 | 7 | 7 | 32 | 84 | 102 | 102 | 102 | 102 | 74 | 84 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 1748736
95 | Patenga 50MW PP (Baraka) | 50 | [16 empty] | 1 |  | 36 | 47 | 50 | 50 | 50 | 50 | 50 | 365280
96 | Chattogram 108 MW PP (ECPV) | 97 | 80 | 51 | 51 | 51 | 45 | 12 | 12 | 12 | 12 | 12 | 18 | 71 | 81 | 83 | 24 | 22 | 40 |  | 82 | 91 | 91 | 91 | 90 | 91 | 92 | 1342080
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 40 | 30 | 40 | 40 | 40 | 40 | 40 | 40 | 30 | 30 | 30 | 30 | 30 |  | 40 | 55 | 55 | 55 | 55 | 55 | 55 | 1080350
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 55 | 55 | 55 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 920510
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 1 | 2 | 2 | 1 | 0 | 0 | 0 | [10 empty] | 8000
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 17 | 17 | [6 empty] | 17 | 54 | 54 | 54 | 54 | 17 | 17 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 786960
104 | Keranigonj 300 MW PP (APR) | [14 empty] | 53 |  | 33 | 51 |  | 25 | 25 | 25 | 25 |  |  | 0 | 172711
105 | Bramhangoan 100 MW PP (Aggreko) | [25 empty] | 0 | 15622
106 | Mymensingh 200 MW PP (United) | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 150 | 166 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4744800
112 | Aurahati 100MW PP (Aggreko) | [14 empty] | 26 |  |  | 39 |  | 27 | 27 | 27 |  |  |  | 0 | 132941
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 149 | 149 | 149 | 149 | 123 | 112 | 104 | 104 | 102 | 112 | 131 | 130 | 131 | 121 | 90 | 94 |  | 131 | 131 | 132 | 132 | 132 | 134 | 133 | 3071088
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 40 | 10 | 10 | 10 | 50 | 90 | 90 | 100 | 100 | 70 | 70 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1959360
116 | Chandpur 200MW (Desh energy) | [17 empty] | 3 |  | 85 | 100 | 100 | 100 | 100 | 68 | 50 | 544320
117 | Ashuganj 150MW PP (Midland) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 796218
118 | Bibiyana-III 400 MW CCPP | 296 | 297 | 295 | 295 | 295 | 298 | 299 | 299 | 299 | 190 | 112 | 52 | 30 | 20 | 20 | 82 | 15 | 80 |  | 85 | 84 | 85 | 82 | 86 | 85 | 88 | 3950000
| Jamalpur 115 MW PP (United) | 64 | 64 | 64 | 64 | 85 | 75 | 16 | 16 | 16 | 16 | 16 | 22 | 65 | 35 | 8 | 8 | 8 | 20 |  | 65 | 65 | 65 | 65 | 65 | 71 | 85 | 1143600
| Anwara 300 MW PP (United) | 162 | 162 | 162 | 162 | 162 | 162 | 107 | 34 | 34 | 34 | 86 | 164 | 175 | 175 | 180 | 106 | 106 | 161 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3364691
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 70 | 70 | 70 | 70 | 100 | 100 | 100 | 100 | 100 | 70 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2310720
120 | Eastern Zone Total | 7067 | 6512 | 6331 | 6328 | 6263 | 6009 | 5613 | 5483 | 5384 | 5361 | 5462 | 5480 | 5766 | 5768 | 5848 | 5364 | 5311 | 6061 |  | 6888 | 7113 | 7166 | 7208 | 7143 | 7126 | 7017 | 150174962
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 115 | 61 | 16 | [9 empty] | 34 | 66 | 66 | 20 | 16 | 45 |  | 99 | 99 | 115 | 115 | 115 | 115 | 115 | 1114560
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
| Khulna 225 MW CCPP | 230 | 230 | 230 | 230 | 190 | 140 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 160 |  | 180 | 185 | 200 | 200 | 200 | 150 | 120 | 3922560
129 | Rupsha 105 MW PP (Orion rupsha) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 53 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1227840
130
131
132
133
| Barisal 110 MW PP (Summit ) | 110 | 80 | 80 | 80 | 64 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 1438560
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 94 | 92 | 92 | 91 | 90 | 88 | 88 | 89 | 89 | 89 | 88 | 90 | 90 | 88 | 91 | 90 | 64 | 82 |  | 91 | 89 | 91 | 90 | 91 | 90 | 91 | 2116260
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 37 | 36 | 36 | 32 | 32 | 32 | 26 | 25 | 23 | 18 | 18 | 18 | 21 | 22 | 22 | 20 | 20 | 28 |  | 35 | 37 | 38 | 38 | 39 | 38 | 38 | 685205
141 | Noapara 100 MW PP (Bangla Trac) | [11 empty] | 37 | [5 empty] | 9 |  | 96 | 100 | 100 | 100 | 100 |  | 0 | 549120
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | [10 empty] | 40 | 40 | 40 | 40 |  |  | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 466875
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 6 | [9 empty] | 1792
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 925 | 924 | 925 | 925 | 925 | 925 | 926 | 925 | 925 | 925 | 925 | 926 | 925 | 925 | 924 | 925 | 925 | 925 |  | 925 | 925 | 925 | 925 | 925 | 925 | 925 | 22190545
147 | Bheramara 410 MW CCPP | 340 | 340 | 365 | 300 | 270 | 240 | 240 | 225 | 250 | 270 | 295 | 305 | 270 | 215 | 215 | 240 | 255 | 285 |  | 310 | 310 | 315 | 335 | 325 | 320 | 320 | 7025760
148 | Payra 1320 MW | 560 | 560 | 560 | 530 | 530 | 530 | 380 | 330 | 330 | 330 | 400 | 500 | 510 | 520 | 550 | 510 | 520 | 520 |  | 565 | 565 | 565 | 565 | 560 | 560 | 560 | 12655700
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 150 |  | 149 | 150 | 149 | 150 | 150 | 150 | 150 | 3682200
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 25 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 307520
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 146 | 148 | 146 | 146 | 143 | 134 | 134 | [19 empty] | 1129100
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 186 | 176 | 179 | 180 | 168 | 157 | 155 | 156 | 162 | 167 | 172 | 179 | 172 | 141 | 138 | 140 | 139 | 142 |  | 167 | 169 | 170 | 170 | 175 | 182 | 187 | 4187782
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 189 | 181 | 183 | 170 | 161 | 153 | 150 | 146 | 159 | 168 | 176 | 181 | 171 | 146 | 138 | 138 | 146 | 149 |  | 165 | 168 | 171 | 175 | 175 | 175 | 178 | 4195936
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 108 | 400 | 414 | 408 | 413 | 300 | 290 | 302 | 308 | 393 | 412 | 405 | 399 | 287 | 313 | 381 | 328 | 383 |  | 411 | 407 | 406 | 406 | 385 | 399 | 379 | 8528400
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 10 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 239598
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 502320
163 | Bogura 20 MW PP (Energyprima) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 236448
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 228114
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [17 empty] | 28 |  | 45 | 45 | 47 | 44 | 44 | 43 | 43 | 271069
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | 52 | [10 empty] | 1 | 52 | 52 | 52 |  |  | 24 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 544320
170 | Chapainawabganj 100 MW Peaking PP | 98 | 24 | [15 empty] | 15 |  | 96 | 96 | 97 | 98 | 98 | 98 | 98 | 785382
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 35 | 35 | [8 empty] | 18 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 604416
172 | Confidence Power Bogura Unit-1 113 MW | 50 | 50 | 50 | 50 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 70 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 50 | 1274688
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 36 | 35 | 36 | 35 | 34 | 34 | 34 | 34 | 35 | 34 | 34 | 35 | 34 | 34 | 33 | 34 | 42 | 77 |  | 86 | 96 | 102 | 105 | 105 | 105 | 92 | 1278720
177 | Sympa Solar Power 8MW | [6 empty] | 1 | 2 | 2 | 3 | 2 | 3 | 4 | 3 | 3 | 2 | 1 | [9 empty] | 26302
178
178