## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-10-04 | Sunday
|  |  | Date (day): | 2020-10-04 |  | Sunday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13187.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14068 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-10-03 | 2020-10-04 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 119 | 120 | 120 | 120 | 60 |  | Gas shortage
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 115 | 115 | 115 | 75 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 200 | 200
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 42 | 41 | 42 | 42 | 66 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under S/D for dust in gas.
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 342 | 350 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 |  | 225 | GT-2 under shut down
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 7 | 7 | 7 | 93 |  | Fuel shortage
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 150 | 290 | 280 | 305
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 80 | 97 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 7 | 22 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 189 | 188 | 120 | 150 |  |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 7 | 7 | 7 | 93 |  | Fuel shortage
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 50 | 16 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 64 | 150 | 149 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 33 | 47 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 52 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 285 | 300 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 100 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 85 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 101 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 112 | 132 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 98 | 104 | 100 | 100
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 2502 | 3160 | 3204 | 3550 | 729 | 1387
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 115 | 115 | 120 | 120 | 60 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 22 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 43 | 44 | 44 | 44 | 186 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 207 | 203 | 221 | 221
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 140 | 139 | 140 | 140
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 100 | 100
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 20 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 21 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 26 | 10 | 25
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 82 | 97 | 100 | 100
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 160 | 162 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 48 | 54 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 1080 | 1254 | 1720 | 1710 | 426 | 98
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 80 | 80 | 80 |  | 54 | Engine problem
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 190 | 181 | 225 | 225 |  |  | FGMO
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 160 | 310 | 360 | 360 |  |  | FGMO
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maintenance
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 29 | 30 | 30 | 15 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 50 | 30 | 55 | 55
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 30 | 30 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 50 | 0 | 50
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 96 | 90 | 90 | 90 |  | 73 | ST under shut down
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 200 | 200 | 200
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 8 | 8 |  | 3 | Engine problem
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 130 | 158 | 162 | 173
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 52 | 52 | 52
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 21 | 21 | 21 | 21
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 50 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 100 | 100 | 100 | 100 |  | 14 | Engine problem
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 104 | 113 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1161 | 1616 | 1760 | 2021 | 466 | 504
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 151 | 157 | 160 | 160 | 42 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 14 | 14 | 14 | 14 |  | 8 | Engine problem
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 0 | 0 | 0 |  | 95 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 3 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 200 | 200 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 10 | 95 | 115 | 115
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 378 | 466 | 490.6 | 489 | 42 | 103
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 58 | 60 | 60 | 60
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 35 | Unit-4 under shut down
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maintenance
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 142 | 177 | 200 | 200 |  | 110 | ST Under maint.
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 50 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 44 | 46 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 65 | 65 | 65 | 65
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 88 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 178 | 218 | 220 | 220
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 285 | 341 | 341 |  |  | FGMO
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 86 | 420 | 400 | 400 |  |  | Testing for combined cycle
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 266 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1368 | 1502 | 1561 | 1561 | 0 | 308
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 918 | 917 | 935 | 935
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 73 | 115 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 10 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 225 | 225 | 225
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 290 | 260 | 410 | 410
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 53 | 53 | 53 |  | 52 | Engine problem
| 108 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1418 | 1720 | 1928 | 2084 | 0 | 52
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 25 | 36 | 33 | 33
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 87 | 88 | 80 | 90
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 500 | 600 | 620 | 620
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 612 | 834 | 843 | 853 | 0 | 194
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 42 | 0 | 42
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 47 | 50 | 50
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 174 | 158 | 220 | 220 |  |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 176 | 170 | 220 | 220 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 405 | 412 | 414 | 414 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 34
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 21 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 10 | 10 | 10 | 10
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 10 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 31 | 52 | 52 | 52
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 24 | 98 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 100 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 35 | 35 | 35 | 35 |  | 78 | Engine problem
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 90 | 90 | 90 |  | 23 | Engine problem
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 922 | 1296 | 1423 | 1550 | 481 | 101
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 151 | 150 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 28 | 93 | 100 | 100 |  | 13 | Engine problem
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 183 | 243 | 258 | 250 | 294 | 53
|  | Total |  |  |  |  | 20383 | 19892 | 9624 | 12091 | 13187.6 | 14068 | 2438 | 2800
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9231.5898 | 11598 | 12649.8871 | 13494.3895
| A. |  | 2020-10-03 | (Yesterday) |  |  |  |  | Saturday
| 1 | Highest Generation : |  |  | 12091 | MW at | 20:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
| 2 | Minimum Generation : |  |  | 8517 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12091 | MW
| 3 | Day peak Generation : |  |  | 9624 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11598 | MW
| 4 | Evening peak Generation : |  |  | 12091 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 243.1386 | MKWHr | By Solar | 0.1947 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 123.3017 | MKWHr |  | By Oil: | 75.9241 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 17.222 | MKWHr |  | By Hydro: | 0.94002 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2438 | MW | Dhaka | 4072 | 4072 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2800 | MW | Chittagong | 1178 | 1178 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5238 | MW | Khulna | 1461 | 1461 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1120.12 | MMCFD |  |  | Rajshahi | 1224 | 1224 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 147135871.418 | ii) Oil : | Taka | 618250589.12 | Comilla | 1180 | 1180 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 79401778 | Total | Taka | 844788238.538 | Mymensingh | 931 | 931 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 523 | 523 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 160 | MW (E to W) at | 20:00 | hrs | Barisal | 344 | 344 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 52 | MW at | 21:00 | hrs | Rangpur | 685 | 685 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 33.3° C |  |  | Total | 11598 | 11598 |  | 0
| B. |  | 2020-10-04 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 33.1° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12700 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14068 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10000 | MW
| 4 | Reserve(Generation end) |  |  |  | 1368 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 255.385 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8930 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.0771 | MKWHr. | ii) HVDC Flow at Peak Time |  | 917 | MW at | 20:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.479 | MKWHr. | iii) Maximum HVDC Flow : |  | 926 | MW at | 7:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 98.92 |  | (b) Today: | 99.42 |  | (c) Rule Curve: |  | 106.27
.

## YesterdayGen
2020-10-03
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 120 | 115 | 200 | 41 | 0 | 0 | 353 |  | 0 | 225 | 130 | 24 | 96 | 55 | 0 | 0 | 185 | 0 | 100 | 102 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 28 | 33 | 52 | 0 | 44 | 0 | 115 | 0 | 25 | 202 | 0 | 140 | 0 |  | 0 | 0 | 51 | 20 | 91 | 50 | 20 | 42 | 0 | 0 | 80 | 245 | 0 | 40 | 26 | 86 | 29 | 55 | 0 | 51 | 0 | 0 | 52 | 21 | 5 | 33 | 21 | 158 | 159 | 0 | 14 | 0 | 58 | 30 | 50 | 47 | 0 | 141 | 67 | 88 | 0 | 178 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 133 | 0 | 100 | 0 | 30 | 85 | 85 | 105 | 0 | 0 | 162 | 36 | 0 | 100 | 113 | 100 | 0 | 104 |  | 925 | 0 | 320 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 64 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 43 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 187 | 0 | 92 | 0 | 180 | 0 | 362 | 36 | 0 | 35 | 0 | 40 | 0 | 0 | 50 | 560 |  | 6869 | 3509 | 10378 | 3267 | 925 | 1791 | 3021 | 710 | 44 | 462 | 158 | 0 | 0 | 98.87
2:00 | 0 | 0 | 120 | 115 | 200 | 41 | 0 | 0 | 355 |  | 0 | 225 | 130 | 24 | 96 | 55 | 0 | 0 | 185 | 0 | 94 | 102 | 115 | 65 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 28 | 33 | 0 | 0 | 43 | 0 | 115 | 0 | 0 | 202 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 92 | 50 | 20 | 42 | 0 | 0 | 80 | 245 | 0 | 53 | 26 | 86 | 29 | 55 | 0 | 51 | 0 | 0 | 52 | 21 | 5 | 33 | 21 | 154 | 161 | 0 | 14 | 0 | 58 | 30 | 50 | 47 | 0 | 141 | 65 | 88 | 0 | 178 | 18 | 0 | 10 | 285 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 133 | 0 | 100 | 0 | 30 | 87 | 85 | 105 | 0 | 0 | 162 | 36 | 0 | 100 | 113 | 100 | 0 | 104 |  | 924 | 0 | 320 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 64 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 187 | 0 | 92 | 0 | 180 | 0 | 363 | 36 | 0 | 35 | 0 | 36 | 0 | 0 | 50 | 560 |  | 6663 | 3410 | 10073 | 3282 | 924 | 1799 | 2828 | 710 | 43 | 333 | 154 | 0 | 0 | 98.88
3:00 | 0 | 0 | 120 | 115 | 200 | 41 | 0 | 0 | 355 |  | 0 | 225 | 135 | 24 | 96 | 30 | 0 | 0 | 195 | 0 | 38 | 102 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 28 | 33 | 0 | 0 | 41 | 0 | 115 | 0 | 0 | 202 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 91 | 50 | 20 | 42 | 0 | 0 | 80 | 245 | 0 | 154 | 26 | 88 | 29 | 55 | 0 | 51 | 0 | 0 | 52 | 21 | 5 | 33 | 21 | 150 | 158 | 0 | 14 | 0 | 58 | 30 | 50 | 47 | 0 | 140 | 65 | 88 | 0 | 178 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 132 | 0 | 100 | 0 | 30 | 87 | 85 | 105 | 0 | 0 | 162 | 36 | 0 | 0 | 113 | 100 | 0 | 104 |  | 925 | 0 | 320 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 32 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 187 | 0 | 92 | 0 | 183 | 0 | 402 | 36 | 0 | 35 | 0 | 36 | 0 | 0 | 50 | 560 |  | 6451 | 3367 | 9818 | 3394 | 925 | 1832 | 2553 | 710 | 41 | 213 | 150 | 0 | 0 | 98.89
4:00 | 0 | 0 | 120 | 115 | 200 | 41 | 0 | 0 | 352 |  | 0 | 225 | 140 | 24 | 96 | 30 | 0 | 0 | 195 | 0 | 7 | 102 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 28 | 33 | 0 | 0 | 40 | 0 | 115 | 0 | 0 | 204 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 86 | 0 | 20 | 42 | 0 | 0 | 80 | 245 | 0 | 187 | 26 | 96 | 27 | 55 | 0 | 51 | 0 | 0 | 0 | 19 | 5 | 33 | 21 | 150 | 158 | 0 | 14 | 0 | 58 | 30 | 50 | 47 | 0 | 140 | 65 | 88 | 0 | 178 | 18 | 0 | 10 | 295 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 132 | 0 | 100 | 0 | 30 | 87 | 85 | 50 | 0 | 0 | 162 | 36 | 0 | 0 | 113 | 100 | 0 | 104 |  | 925 | 0 | 320 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 187 | 0 | 92 | 0 | 186 | 0 | 404 | 36 | 0 | 35 | 0 | 36 | 0 | 0 | 35 | 560 |  | 6265 | 3205 | 9470 | 3433 | 925 | 1841 | 2251 | 710 | 40 | 120 | 150 | 0 | 0 | 98.9
5:00 | 0 | 0 | 120 | 115 | 200 | 41 | 0 | 0 | 353 |  | 0 | 225 | 143 | 24 | 96 | 30 | 0 | 0 | 165 | 0 | 7 | 102 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 22 | 25 | 22 | 28 | 33 | 0 | 0 | 40 | 0 | 115 | 0 | 0 | 204 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 91 | 0 | 20 | 42 | 0 | 0 | 80 | 245 | 0 | 189 | 26 | 96 | 27 | 54 | 0 | 51 | 0 | 0 | 0 | 19 | 5 | 33 | 21 | 144 | 158 | 0 | 14 | 0 | 58 | 30 | 50 | 47 | 0 | 142 | 65 | 88 | 0 | 178 | 18 | 0 | 10 | 295 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 132 | 0 | 100 | 0 | 30 | 86 | 65 | 50 | 0 | 0 | 162 | 36 | 0 | 0 | 113 | 100 | 0 | 104 |  | 925 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 189 | 0 | 91 | 0 | 188 | 0 | 405 | 36 | 0 | 35 | 0 | 30 | 0 | 0 | 35 | 550 |  | 6183 | 3177 | 9360 | 3410 | 925 | 1841 | 2180 | 700 | 40 | 120 | 144 | 0 | 0 | 98.91
6:00 | 0 | 0 | 120 | 115 | 200 | 41 | 0 | 0 | 356 |  | 0 | 225 | 128 | 24 | 96 | 30 | 0 | 0 | 115 | 0 | 7 | 102 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 22 | 25 | 22 | 28 | 33 | 0 | 0 | 41 | 0 | 115 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 84 | 0 | 20 | 38 | 0 | 0 | 80 | 140 | 0 | 179 | 26 | 85 | 27 | 54 | 0 | 51 | 0 | 0 | 0 | 19 | 5 | 33 | 21 | 136 | 160 | 0 | 14 | 0 | 58 | 30 | 50 | 47 | 0 | 141 | 67 | 88 | 0 | 178 | 18 | 0 | 10 | 285 | 24 | 8 | 0 | 245 | 0 | 0 | 200 | 0 | 128 | 0 | 60 | 0 | 30 | 86 | 45 | 17 | 0 | 0 | 126 | 36 | 0 | 0 | 113 | 100 | 0 | 104 |  | 925 | 0 | 330 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 192 | 0 | 90 | 0 | 190 | 0 | 355 | 36 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 550 |  | 5780 | 3141 | 8921 | 3250 | 925 | 1775 | 1974 | 700 | 41 | 120 | 136 | 0 | 0 | 98.92
7:00 | 0 | 0 | 120 | 115 | 200 | 41 | 0 | 0 | 303 |  | 0 | 225 | 140 | 24 | 96 | 30 | 0 | 0 | 120 | 0 | 7 | 102 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 55 | 22 | 25 | 22 | 28 | 33 | 0 | 0 | 41 | 0 | 115 | 0 | 0 | 210 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 62 | 0 | 20 | 36 | 0 | 0 | 80 | 15 | 0 | 197 | 26 | 94 | 27 | 55 | 0 | 51 | 0 | 0 | 0 | 19 | 2 | 33 | 17 | 162 | 158 | 0 | 14 | 0 | 58 | 30 | 50 | 47 | 0 | 140 | 66 | 85 | 0 | 178 | 18 | 0 | 10 | 275 | 24 | 8 | 0 | 230 | 0 | 0 | 200 | 0 | 102 | 4 | 60 | 0 | 30 | 87 | 8 | 17 | 0 | 1 | 88 | 36 | 0 | 0 | 113 | 100 | 0 | 104 |  | 926 | 0 | 340 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 193 | 0 | 91 | 0 | 191 | 0 | 338 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 530 |  | 5484 | 3080 | 8564 | 3166 | 926 | 1689 | 1775 | 680 | 41 | 120 | 162 | 5 | 0 | 98.93
8:00 | 0 | 0 | 121 | 115 | 200 | 41 | 0 | 0 | 303 |  | 0 | 225 | 140 | 24 | 96 | 30 | 0 | 0 | 120 | 0 | 7 | 102 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 22 | 33 | 17 | 0 | 0 | 41 | 0 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 67 | 0 | 20 | 13 | 0 | 0 | 80 | 15 | 0 | 179 | 26 | 92 | 27 | 55 | 0 | 51 | 0 | 0 | 0 | 19 | 2 | 33 | 15 | 120 | 157 | 0 | 14 | 1 | 58 | 30 | 47 | 47 | 0 | 140 | 65 | 85 | 0 | 178 | 18 | 0 | 10 | 300 | 24 | 5 | 0 | 230 | 0 | 0 | 200 | 0 | 103 | 10 | 90 | 0 | 30 | 84 | 8 | 17 | 0 | 2 | 122 | 36 | 0 | 0 | 113 | 100 | 0 | 104 |  | 918 | 0 | 325 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 190 | 0 | 73 | 0 | 191 | 0 | 337 | 17 | 0 | 35 | 0 | 35 | 0 | 1 | 35 | 500 |  | 5526 | 2991 | 8517 | 3080 | 918 | 1669 | 1905 | 650 | 41 | 120 | 120 | 14 | 0 | 98.94
9:00 | 0 | 0 | 119 | 115 | 200 | 41 | 0 | 0 | 303 |  | 0 | 225 | 140 | 24 | 96 | 30 | 0 | 0 | 120 | 0 | 7 | 102 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 22 | 33 | 17 | 0 | 0 | 42 | 0 | 115 | 0 | 0 | 204 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 91 | 2 | 20 | 4 | 0 | 0 | 80 | 30 | 0 | 181 | 26 | 95 | 27 | 54 | 0 | 51 | 0 | 0 | 1 | 19 | 5 | 33 | 20 | 118 | 156 | 0 | 14 | 2 | 60 | 30 | 47 | 47 | 0 | 140 | 65 | 85 | 0 | 178 | 18 | 0 | 9 | 290 | 24 | 8 | 0 | 265 | 0 | 0 | 180 | 0 | 109 | 0 | 100 | 0 | 30 | 87 | 0 | 52 | 0 | 4 | 125 | 36 | 0 | 0 | 110 | 100 | 0 | 104 |  | 918 | 0 | 320 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 190 | 0 | 73 | 0 | 189 | 0 | 338 | 17 | 0 | 35 | 0 | 35 | 0 | 2 | 35 | 480 |  | 5635 | 2980 | 8615 | 3126 | 918 | 1647 | 2006 | 630 | 42 | 120 | 118 | 8 | 0 | 98.95
10:00 | 0 | 0 | 121 | 115 | 200 | 43 | 0 | 0 | 347 |  | 0 | 225 | 130 | 8 | 96 | 30 | 0 | 0 | 120 | 0 | 7 | 50 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 9 | 33 | 17 | 0 | 0 | 42 | 0 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 85 | 18 | 20 | 4 | 0 | 0 | 80 | 90 | 0 | 180 | 8 | 85 | 29 | 53 | 0 | 51 | 0 | 0 | 16 | 19 | 5 | 33 | 20 | 122 | 154 | 0 | 14 | 2 | 60 | 30 | 47 | 44 | 0 | 141 | 65 | 80 | 0 | 178 | 18 | 0 | 9 | 290 | 24 | 8 | 0 | 300 | 0 | 0 | 180 | 0 | 109 | 18 | 100 | 0 | 30 | 87 | 0 | 70 | 0 | 5 | 124 | 36 | 0 | 0 | 105 | 100 | 273 | 104 |  | 918 | 0 | 315 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 188 | 0 | 73 | 0 | 186 | 0 | 312 | 17 | 0 | 35 | 0 | 34 | 0 | 2 | 35 | 480 |  | 5982 | 2942 | 8924 | 3427 | 918 | 1640 | 1999 | 629 | 42 | 120 | 122 | 27 | 0 | 98.96
11:00 | 0 | 0 | 120 | 115 | 200 | 43 | 0 | 0 | 347 |  | 0 | 225 | 140 | 7 | 85 | 32 | 0 | 0 | 153 | 0 | 7 | 50 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 8 | 0 | 17 | 0 | 0 | 43 | 0 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 85 | 22 | 20 | 2 | 0 | 0 | 80 | 130 | 0 | 180 | 8 | 96 | 29 | 52 | 0 | 51 | 0 | 0 | 25 | 22 | 5 | 33 | 21 | 120 | 154 | 0 | 14 | 1 | 60 | 30 | 50 | 44 | 0 | 140 | 65 | 83 | 0 | 178 | 18 | 0 | 9 | 300 | 24 | 8 | 0 | 286 | 0 | 0 | 185 | 0 | 125 | 20 | 100 | 0 | 30 | 84 | 0 | 73 | 0 | 6 | 160 | 36 | 0 | 17 | 105 | 100 | 271 | 104 |  | 918 | 0 | 305 | 0 | 49 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 181 | 0 | 88 | 0 | 184 | 0 | 366 | 17 | 0 | 35 | 0 | 29 | 0 | 3 | 35 | 480 |  | 6119 | 3022 | 9141 | 3455 | 918 | 1722 | 2103 | 630 | 43 | 120 | 120 | 30 | 0 | 98.97
12:00 | 0 | 0 | 119 | 115 | 200 | 42 | 0 | 0 | 342 |  | 0 | 225 | 150 | 7 | 80 | 40 | 0 | 0 | 189 | 0 | 7 | 50 | 64 | 7 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 8 | 33 | 17 | 0 | 0 | 43 | 0 | 115 | 0 | 0 | 207 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 82 | 50 | 20 | 3 | 0 | 0 | 80 | 160 | 0 | 190 | 8 | 96 | 29 | 50 | 0 | 51 | 0 | 0 | 52 | 22 | 5 | 33 | 21 | 130 | 151 | 0 | 14 | 3 | 58 | 30 | 47 | 44 | 0 | 142 | 65 | 83 | 0 | 178 | 18 | 0 | 9 | 310 | 24 | 8 | 0 | 285 | 0 | 0 | 200 | 0 | 112 | 20 | 100 | 0 | 30 | 86 | 10 | 98 | 0 | 2 | 160 | 48 | 0 | 100 | 104 | 90 | 266 | 104 |  | 918 | 0 | 290 | 0 | 73 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 31 | 0 | 21 | 10 | 11 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 174 | 0 | 87 | 0 | 176 | 0 | 405 | 17 | 0 | 35 | 0 | 28 | 0 | 4 | 35 | 500 |  | 6489 | 3135 | 9624 | 3534 | 918 | 1762 | 2349 | 651 | 43 | 208 | 130 | 29 | 0 | 98.98
13:00 | 0 | 0 | 120 | 115 | 200 | 42 | 0 | 0 | 302 |  | 0 | 225 | 220 | 7 | 90 | 40 | 0 | 0 | 120 | 0 | 7 | 50 | 150 | 90 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 8 | 33 | 17 | 16 | 0 | 43 | 0 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 86 | 50 | 20 | 8 | 0 | 0 | 80 | 345 | 0 | 179 | 8 | 85 | 29 | 52 | 0 | 51 | 0 | 0 | 52 | 22 | 5 | 33 | 21 | 134 | 153 | 0 | 14 | 1 | 58 | 30 | 47 | 43 | 0 | 142 | 40 | 85 | 0 | 178 | 18 | 0 | 10 | 270 | 24 | 8 | 0 | 290 | 0 | 0 | 192 | 0 | 124 | 19 | 100 | 0 | 30 | 87 | 45 | 105 | 0 | 5 | 161 | 51 | 0 | 100 | 110 | 100 | 278 | 104 |  | 918 | 0 | 270 | 0 | 83 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 164 | 0 | 86 | 0 | 130 | 0 | 303 | 17 | 0 | 35 | 0 | 24 | 0 | 5 | 35 | 500 |  | 6843 | 3010 | 9853 | 3539 | 918 | 1590 | 2630 | 651 | 43 | 318 | 134 | 30 | 9853 | 98.99
14:00 | 0 | 0 | 120 | 115 | 200 | 43 | 0 | 0 | 271 |  | 0 | 225 | 300 | 7 | 96 | 40 | 0 | 0 | 120 | 0 | 7 | 50 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 20 | 33 | 17 | 20 | 0 | 42 | 0 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 10 | 90 | 50 | 20 | 5 | 0 | 0 | 80 | 360 | 0 | 179 | 8 | 85 | 29 | 10 | 0 | 51 | 0 | 0 | 52 | 19 | 5 | 33 | 21 | 136 | 153 | 0 | 14 | 1 | 58 | 30 | 47 | 46 | 0 | 138 | 40 | 40 | 0 | 135 | 18 | 0 | 10 | 270 | 24 | 8 | 0 | 300 | 0 | 0 | 192 | 0 | 132 | 0 | 100 | 0 | 30 | 80 | 24 | 105 | 0 | 4 | 161 | 36 | 0 | 100 | 111 | 100 | 273 | 104 |  | 918 | 0 | 255 | 0 | 83 | 120 | 0 | 0 | 0 | 0 | 8 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 19 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 88 | 0 | 130 | 0 | 183 | 17 | 0 | 35 | 0 | 27 | 0 | 4 | 35 | 500 |  | 6769 | 2871 | 9640 | 3455 | 918 | 1355 | 2738 | 650 | 42 | 337 | 136 | 9 | 0 | 99
15:00 | 0 | 0 | 120 | 115 | 200 | 43 | 0 | 0 | 344 |  | 0 | 225 | 290 | 7 | 92 | 40 | 0 | 0 | 160 | 0 | 7 | 50 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 20 | 33 | 17 | 48 | 0 | 40 | 0 | 115 | 0 | 10 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 10 | 90 | 50 | 20 | 5 | 0 | 0 | 80 | 355 | 0 | 183 | 8 | 90 | 26 | 10 | 0 | 51 | 0 | 0 | 52 | 19 | 5 | 33 | 21 | 140 | 154 | 0 | 14 | 0 | 57 | 30 | 47 | 46 | 0 | 142 | 40 | 84 | 0 | 185 | 18 | 0 | 10 | 285 | 24 | 8 | 0 | 300 | 0 | 0 | 192 | 0 | 132 | 13 | 100 | 0 | 30 | 80 | 24 | 105 | 0 | 4 | 161 | 36 | 0 | 100 | 112 | 100 | 274 | 104 |  | 919 | 0 | 285 | 0 | 83 | 120 | 0 | 0 | 0 | 0 | 8 | 0 | 25 | 0 | 0 | 0 | 0 | 10 | 0 | 48 | 0 | 0 | 36 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 89 | 0 | 159 | 0 | 189 | 17 | 0 | 35 | 0 | 27 | 0 | 2 | 35 | 540 |  | 7036 | 3023 | 10059 | 3632 | 919 | 1492 | 2763 | 690 | 40 | 364 | 140 | 19 | 0 | 99.01
16:00 | 0 | 0 | 120 | 115 | 200 | 41 | 0 | 0 | 344 |  | 0 | 225 | 280 | 7 | 80 | 40 | 0 | 0 | 120 | 0 | 7 | 40 | 98 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 17 | 0 | 0 | 40 | 0 | 115 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 91 | 50 | 20 | 6 | 0 | 0 | 80 | 355 | 0 | 182 | 8 | 95 | 26 | 10 | 0 | 51 | 0 | 0 | 52 | 21 | 5 | 33 | 21 | 144 | 154 | 0 | 14 | 0 | 57 | 30 | 50 | 46 | 0 | 141 | 40 | 87 | 0 | 191 | 18 | 0 | 9 | 290 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 132 | 10 | 100 | 0 | 30 | 85 | 24 | 105 | 0 | 2 | 161 | 42 | 0 | 30 | 113 | 100 | 250 | 104 |  | 917 | 0 | 295 | 0 | 87 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 25 | 0 | 48 | 0 | 0 | 43 | 25 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 87 | 0 | 130 | 0 | 270 | 17 | 0 | 35 | 0 | 27 | 0 | 1 | 35 | 540 |  | 6708 | 3073 | 9781 | 3533 | 917 | 1582 | 2528 | 690 | 40 | 334 | 144 | 13 | 0 | 99.02
17:00 | 0 | 0 | 120 | 115 | 200 | 41 | 0 | 0 | 302 |  | 0 | 225 | 280 | 7 | 91 | 40 | 0 | 0 | 120 | 0 | 7 | 40 | 98 | 38 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 17 | 0 | 0 | 40 | 0 | 115 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 91 | 50 | 20 | 8 | 0 | 0 | 80 | 335 | 0 | 182 | 8 | 85 | 29 | 10 | 0 | 51 | 0 | 0 | 52 | 21 | 5 | 33 | 21 | 136 | 156 | 0 | 14 | 0 | 60 | 30 | 10 | 10 | 0 | 142 | 40 | 86 | 0 | 191 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 131 | 2 | 100 | 0 | 30 | 95 | 24 | 105 | 0 | 0 | 125 | 54 | 0 | 17 | 113 | 100 | 0 | 104 |  | 918 | 0 | 300 | 0 | 99 | 120 | 0 | 0 | 2 | 0 | 0 | 0 | 25 | 6 | 0 | 0 | 0 | 25 | 0 | 48 | 0 | 0 | 43 | 25 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 90 | 0 | 130 | 0 | 351 | 17 | 0 | 35 | 0 | 32 | 0 | 0 | 35 | 490 |  | 6274 | 3135 | 9409 | 3277 | 918 | 1548 | 2512 | 640 | 40 | 336 | 136 | 2 | 0 | 99.04
18:00 | 0 | 0 | 120 | 115 | 200 | 41 | 0 | 0 | 324 |  | 0 | 225 | 300 | 7 | 97 | 40 | 0 | 0 | 120 | 0 | 7 | 16 | 150 | 22 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 21 | 33 | 17 | 16 | 0 | 40 | 0 | 115 | 0 | 9 | 213 | 0 | 139 | 0 |  | 0 | 0 | 99 | 10 | 91 | 50 | 20 | 8 | 0 | 0 | 80 | 330 | 0 | 200 | 8 | 95 | 29 | 10 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 33 | 21 | 170 | 154 | 0 | 14 | 0 | 59 | 30 | 19 | 15 | 0 | 178 | 65 | 87 | 0 | 200 | 18 | 0 | 10 | 285 | 24 | 8 | 108 | 300 | 219 | 50 | 200 | 98 | 132 | 0 | 100 | 15 | 30 | 215 | 29 | 105 | 0 | 0 | 125 | 54 | 0 | 80 | 113 | 100 | 0 | 104 |  | 918 | 0 | 290 | 0 | 99 | 145 | 0 | 0 | 3 | 10 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 25 | 10 | 87 | 0 | 0 | 43 | 25 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 153 | 0 | 90 | 20 | 142 | 0 | 354 | 17 | 100 | 35 | 0 | 71 | 0 | 0 | 90 | 500 |  | 7328 | 3607 | 10935 | 3539 | 918 | 1596 | 3450 | 650 | 40 | 572 | 170 | 0 | 0 | 99.06
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 120 | 115 | 200 | 41 | 0 | 0 | 350 |  | 0 | 225 | 280 | 7 | 80 | 55 | 0 | 0 | 185 | 0 | 7 | 16 | 150 | 23 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 21 | 33 | 33 | 52 | 0 | 42 | 0 | 115 | 0 | 3 | 204 | 0 | 139 | 0 |  | 0 | 0 | 102 | 20 | 93 | 50 | 20 | 21 | 0 | 0 | 80 | 310 | 0 | 181 | 8 | 90 | 29 | 10 | 0 | 51 | 0 | 50 | 52 | 22 | 8 | 33 | 21 | 156 | 157 | 0 | 14 | 0 | 60 | 30 | 50 | 46 | 0 | 181 | 65 | 88 | 0 | 218 | 18 | 0 | 10 | 290 | 24 | 11 | 157 | 300 | 106 | 85 | 200 | 101 | 131 | 0 | 100 | 157 | 30 | 308 | 82 | 105 | 0 | 0 | 161 | 54 | 0 | 100 | 113 | 100 | 0 | 104 |  | 918 | 0 | 285 | 0 | 99 | 225 | 0 | 0 | 6 | 0 | 40 | 0 | 37 | 110 | 0 | 0 | 0 | 50 | 42 | 98 | 0 | 0 | 44 | 50 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 93 | 99 | 170 | 0 | 403 | 53 | 150 | 35 | 0 | 90 | 0 | 0 | 90 | 580 |  | 7870 | 4117 | 11987 | 3716 | 918 | 1754 | 3904 | 730 | 42 | 767 | 156 | 0 | 0 | 99.08
19:30 | 0 | 0 | 120 | 115 | 200 | 41 | 0 | 0 | 350 |  | 0 | 225 | 290 | 7 | 97 | 55 | 0 | 0 | 185 | 0 | 7 | 16 | 150 | 23 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 21 | 33 | 33 | 52 | 0 | 42 | 0 | 115 | 0 | 12 | 203 | 0 | 139 | 0 |  | 0 | 0 | 102 | 20 | 97 | 50 | 20 | 22 | 0 | 0 | 80 | 310 | 0 | 181 | 8 | 88 | 29 | 10 | 0 | 51 | 0 | 50 | 52 | 22 | 8 | 33 | 21 | 154 | 157 | 0 | 14 | 0 | 60 | 30 | 50 | 46 | 0 | 183 | 65 | 88 | 0 | 219 | 18 | 0 | 10 | 295 | 24 | 11 | 50 | 300 | 100 | 85 | 200 | 101 | 131 | 0 | 100 | 200 | 30 | 370 | 95 | 105 | 0 | 0 | 161 | 54 | 0 | 100 | 113 | 100 | 0 | 104 |  | 918 | 0 | 280 | 0 | 99 | 225 | 0 | 0 | 16 | 0 | 40 | 0 | 37 | 110 | 0 | 0 | 0 | 50 | 42 | 98 | 0 | 0 | 45 | 50 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 89 | 100 | 170 | 0 | 409 | 53 | 100 | 35 | 0 | 90 | 0 | 0 | 90 | 600 |  | 7919 | 4096 | 12015 | 3773 | 918 | 1762 | 3838 | 750 | 42 | 778 | 154 | 0 | 0 | 0
20:00 | 0 | 0 | 120 | 115 | 200 | 41 | 0 | 0 | 350 |  | 0 | 225 | 290 | 7 | 97 | 55 | 0 | 0 | 188 | 0 | 7 | 16 | 150 | 22 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 52 | 0 | 44 | 0 | 115 | 0 | 22 | 203 | 0 | 139 | 0 |  | 0 | 0 | 102 | 20 | 97 | 50 | 20 | 26 | 0 | 0 | 80 | 310 | 0 | 181 | 8 | 90 | 29 | 30 | 0 | 51 | 0 | 50 | 52 | 22 | 8 | 33 | 21 | 158 | 157 | 0 | 14 | 0 | 60 | 30 | 50 | 46 | 0 | 177 | 65 | 88 | 0 | 218 | 18 | 0 | 10 | 285 | 24 | 11 | 50 | 300 | 100 | 85 | 200 | 101 | 132 | 0 | 100 | 200 | 30 | 420 | 95 | 104 | 0 | 0 | 162 | 54 | 0 | 100 | 113 | 100 | 0 | 104 |  | 917 | 0 | 260 | 0 | 115 | 225 | 0 | 0 | 10 | 0 | 40 | 0 | 36 | 110 | 0 | 0 | 0 | 50 | 42 | 98 | 0 | 0 | 47 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 88 | 100 | 170 | 0 | 412 | 53 | 100 | 35 | 0 | 93 | 0 | 0 | 90 | 600 |  | 7998 | 4093 | 12091 | 3802 | 917 | 1777 | 3869 | 750 | 44 | 774 | 158 | 0 | 0 | 99.1
21:00 | 0 | 0 | 120 | 115 | 200 | 41 | 0 | 0 | 349 |  | 0 | 225 | 300 | 7 | 97 | 40 | 0 | 0 | 155 | 0 | 7 | 16 | 150 | 23 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 52 | 0 | 44 | 0 | 115 | 0 | 25 | 205 | 0 | 139 | 0 |  | 0 | 0 | 102 | 20 | 97 | 50 | 20 | 33 | 0 | 0 | 80 | 320 | 0 | 194 | 8 | 95 | 29 | 55 | 0 | 51 | 0 | 42 | 52 | 22 | 8 | 33 | 21 | 158 | 158 | 0 | 14 | 0 | 59 | 30 | 50 | 47 | 0 | 179 | 65 | 88 | 0 | 218 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 300 | 100 | 82 | 183 | 101 | 149 | 0 | 100 | 200 | 30 | 418 | 95 | 104 | 0 | 0 | 162 | 54 | 0 | 100 | 113 | 100 | 0 | 104 |  | 918 | 0 | 245 | 0 | 115 | 225 | 0 | 0 | 17 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 42 | 98 | 0 | 0 | 43 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 89 | 100 | 140 | 0 | 414 | 53 | 0 | 35 | 0 | 100 | 0 | 0 | 90 | 600 |  | 7970 | 3964 | 11934 | 3754 | 918 | 1819 | 3722 | 750 | 44 | 769 | 158 | 0 | 0 | 99.12
22:00 | 0 | 0 | 120 | 115 | 200 | 41 | 0 | 0 | 351 |  | 0 | 225 | 290 | 7 | 97 | 40 | 0 | 0 | 155 | 0 | 7 | 16 | 150 | 40 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 52 | 0 | 44 | 0 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 102 | 20 | 97 | 50 | 20 | 40 | 0 | 0 | 80 | 310 | 0 | 183 | 8 | 95 | 29 | 55 | 0 | 51 | 0 | 42 | 52 | 22 | 8 | 33 | 21 | 158 | 157 | 0 | 14 | 0 | 60 | 30 | 50 | 47 | 0 | 180 | 65 | 88 | 0 | 218 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 296 | 103 | 56 | 192 | 97 | 149 | 0 | 100 | 200 | 30 | 418 | 103 | 104 | 0 | 0 | 162 | 54 | 0 | 100 | 113 | 100 | 0 | 104 |  | 918 | 0 | 255 | 0 | 115 | 225 | 0 | 0 | 13 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 42 | 98 | 0 | 0 | 43 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 92 | 100 | 140 | 0 | 414 | 53 | 0 | 35 | 0 | 98 | 0 | 0 | 90 | 600 |  | 7961 | 3971 | 11932 | 3743 | 918 | 1841 | 3713 | 750 | 44 | 765 | 158 | 0 | 0 | 99.14
23:00 | 0 | 0 | 120 | 115 | 200 | 42 | 0 | 0 | 353 |  | 0 | 225 | 295 | 7 | 97 | 40 | 0 | 0 | 155 | 0 | 7 | 16 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 52 | 0 | 44 | 0 | 115 | 0 | 25 | 203 | 0 | 140 | 0 |  | 0 | 0 | 102 | 20 | 97 | 50 | 20 | 42 | 0 | 0 | 80 | 310 | 0 | 181 | 8 | 87 | 29 | 55 | 0 | 51 | 0 | 42 | 52 | 22 | 8 | 33 | 21 | 158 | 157 | 0 | 14 | 0 | 60 | 30 | 50 | 47 | 10 | 180 | 66 | 88 | 0 | 218 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 286 | 100 | 38 | 200 | 61 | 149 | 0 | 90 | 200 | 30 | 422 | 115 | 104 | 0 | 0 | 162 | 54 | 0 | 100 | 110 | 100 | 0 | 104 |  | 918 | 0 | 240 | 0 | 115 | 230 | 0 | 0 | 13 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 42 | 98 | 0 | 0 | 43 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 92 | 100 | 140 | 0 | 407 | 53 | 0 | 35 | 0 | 96 | 0 | 0 | 90 | 600 |  | 7966 | 3952 | 11918 | 3723 | 918 | 1839 | 3716 | 750 | 44 | 770 | 158 | 0 | 0 | 99.16
24:00 | 0 | 0 | 120 | 115 | 200 | 42 | 0 | 0 | 354 |  | 0 | 225 | 265 | 7 | 96 | 40 | 0 | 0 | 145 | 0 | 7 | 16 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 52 | 0 | 44 | 0 | 115 | 0 | 25 | 204 | 0 | 140 | 0 |  | 0 | 0 | 85 | 20 | 98 | 50 | 20 | 42 | 0 | 0 | 80 | 310 | 0 | 180 | 8 | 85 | 29 | 55 | 0 | 51 | 0 | 41 | 52 | 22 | 8 | 33 | 21 | 152 | 157 | 0 | 14 | 0 | 60 | 30 | 50 | 47 | 20 | 180 | 67 | 88 | 0 | 219 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 286 | 25 | 30 | 193 | 54 | 149 | 0 | 90 | 200 | 30 | 425 | 115 | 104 | 0 | 0 | 162 | 40 | 0 | 100 | 113 | 100 | 0 | 104 |  | 918 | 0 | 240 | 0 | 115 | 230 | 0 | 0 | 13 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 42 | 98 | 0 | 0 | 43 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 92 | 100 | 140 | 0 | 386 | 53 | 0 | 35 | 0 | 67 | 0 | 0 | 50 | 600 |  | 7798 | 3862 | 11660 | 3716 | 918 | 1819 | 3509 | 750 | 44 | 752 | 152 | 0 | 0 | 99.18
KWH | 0 | 0 | 2883000 | 2677500 | 4784200 | 992136 | 0 | 0 | 7994000 |  | 0 | 4684300 | 4860276 | 355200 | 2239992 | 965304 | 0 | 0 | 3993000 | 0 | 409920 | 1436544 | 2085600 | 965836 | 0 | 0 | 0 | 1203120 | 1275831 | 1322681 | 428976 | 600000 | 448200 | 770500 | 654500 | 492996 | 0 | 940020 | 0 | 2700000 | 0 | 204228 | 4849873 | 0 | 3316504 | 0 |  | 0 | 0 | 704750 | 168720 | 2143680 | 861600 | 481728 | 595200 | 0 | 0 | 1933474 | 6035300 | 0 | 4160000 | 384727 | 2172700 | 653688 | 1037760 | 0 | 1244730 | 0 | 253640 | 921398 | 473688 | 139500 | 817500 | 508160 | 3479040 | 3674880 | 0 | 323316 | 10850 | 1396000 | 711480 | 1130400 | 1066464 | 16936 | 3484000 | 1449 | 1981440 | 0 | 4502760 | 420000 | 0 | 239400 | 7118800 | 574200 | 204000 | 292608 | 7000361 | 740176 | 420725 | 4711200 | 560523 | 3127540 | 127575 | 2348160 | 1196640 | 791200 | 3881000 | 1336800 | 2080992 | 0 | 31560 | 3633164 | 1033000 | 0 | 1357740 | 2688000 | 2386560 | 1790200 | 2621760 |  | 22077090 | 0 | 7377120 | 0 | 1707840 | 3558720 | 0 | 0 | 72000 | 4352 | 308250 | 0 | 738760 | 1067520 | 0 | 0 | 0 | 427504 | 239242 | 1147832 | 0 | 0 | 457500 | 641280 | 0 | 503760 | 236808 | 240084 | 0 | 0 | 3686600 | 0 | 0 | 0 | 0 | 4345327 | 0 | 2111359 | 619200 | 4308555 | 0 | 8508327 | 756000 | 393593 | 912480 | 0 | 1171200 | 0 | 24711 | 1241088 | 13535400 |  | 160719079 | 82419502 | 243138581 | 82716362 | 22077090 | 40585307 | 66972926 | 17222000 | 940020 | 8951140 | 3479040 | 194696 | 0
Fuel Cost | 0 | 0 | 4209180 | 3935925 | 5310462 | 1309619.52 | 0 | 0 | 8233820 |  | 0 | 5105887 | 5394906.36 | 2695968 | 15433544.88 | 8166471.84 | 0 | 0 | 6907890 | 0 | 3086697.6 | 13101281.28 | 20522304 | 8905007.92 | 0 | 0 | 0 | 8782776 | 9862173.63 | 13041634.66 | 321732 | 450000 | 0 | 0 | 0 | 4767271.32 | 0 | 253805.4 | 0 | 4887000 | 0 | 1897278.12 | 5286361.57 | 0 | 5638056.8 | 0 |  | 0 | 0 | 6836075 | 1611276 | 18650016 | 6823872 | 606977.28 | 1767744 | 0 | 0 | 2842206.78 | 4466122 | 0 | 3827200 | 496297.83 | 2498605 | 738667.44 | 1452864 | 0 | 2128488.3 | 0 | 2561764 | 8799350.9 | 601583.76 | 104625 | 1430625 | 381120 | 26092800 | 3895372.8 | 0 | 410611.32 | 172949 | 2289440 | 1138368 | 2012112 | 1663683.84 | 19307.04 | 3623360 | 2854.53 | 3784550.4 | 0 | 7789774.8 | 919800 | 0 | 488376 | 7189988 | 430650 | 155040 | 4977262.08 | 52922729.16 | 12568188.48 | 7034522 | 24498240 | 9371944.56 | 30774993.6 | 1491351.75 | 19137504 | 12983544 | 5577960 | 3609330 | 12191616 | 19665374.4 | 0 | 0 | 27466719.84 | 8997430 | 0 | 13550245.2 | 23036160 | 15894489.6 | 0 | 0 |  | 127164038.4 | 0 | 7745976 | 0 | 13423622.4 | 49323859.2 | 0 | 0 | 755280 | 45608.96 | 3211965 | 0 | 1145078 | 10418995.2 | 0 | 0 | 0 | 4206639.36 | 2430698.72 | 10158313.2 | 0 | 0 | 4433175 | 6214003.2 | 0 | 967219.2 | 367052.4 | 181743.588 | 0 | 0 | 19981372 | 0 | 0 | 0 | 0 | 5735831.64 | 0 | 3167038.5 | 10532592 | 5041009.35 | 0 | 8423243.73 | 7892640 | 6695016.93 | 8659435.2 | 0 | 9088512 | 0 | 273056.55 | 9171640.32 | 59420406 |  | 603961177.59 | 396275062.048 | 1000236239.638 | 97413501.658 | 127164038.4 | 49722369.76 | 516976871.68 | 79401778 | 253805.4 | 101273717.44 | 26092800 | 1937357.3 | 0
Yesterday Day Peak | 0 | 0 | 119 | 115 | 200 | 42 | 0 | 0 | 342 |  | 0 | 225 | 150 | 7 | 80 | 40 | 0 | 0 | 189 | 0 | 7 | 50 | 64 | 7 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 8 | 33 | 17 | 0 | 0 | 43 | 0 | 115 | 0 | 0 | 207 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 82 | 50 | 20 | 3 | 0 | 0 | 80 | 160 | 0 | 190 | 8 | 96 | 29 | 50 | 0 | 51 | 0 | 0 | 52 | 22 | 5 | 33 | 21 | 130 | 151 | 0 | 14 | 3 | 58 | 30 | 47 | 44 | 0 | 142 | 65 | 83 | 0 | 178 | 18 | 0 | 9 | 310 | 24 | 8 | 0 | 285 | 0 | 0 | 200 | 0 | 112 | 20 | 100 | 0 | 30 | 86 | 10 | 98 | 0 | 2 | 160 | 48 | 0 | 100 | 104 | 90 | 266 | 104 |  | 918 | 0 | 290 | 0 | 73 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 31 | 0 | 21 | 10 | 11 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 174 | 0 | 87 | 0 | 176 | 0 | 405 | 17 | 0 | 35 | 0 | 28 | 0 | 4 | 35 | 500 |  | 9624 | DayPeak
Yesterday Evening Peak | 0 | 0 | 120 | 115 | 200 | 41 | 0 | 0 | 350 | 0 | 0 | 225 | 290 | 7 | 97 | 55 | 0 | 0 | 188 | 0 | 7 | 16 | 150 | 22 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 52 | 0 | 44 | 0 | 115 | 0 | 22 | 203 | 0 | 139 | 0 | 0 | 0 | 0 | 102 | 20 | 97 | 50 | 20 | 26 | 0 | 0 | 80 | 310 | 0 | 181 | 8 | 90 | 29 | 30 | 0 | 51 | 0 | 50 | 52 | 22 | 8 | 33 | 21 | 158 | 157 | 0 | 14 | 0 | 60 | 30 | 50 | 46 | 0 | 177 | 65 | 88 | 0 | 218 | 18 | 0 | 10 | 285 | 24 | 11 | 50 | 300 | 100 | 85 | 200 | 101 | 132 | 0 | 100 | 200 | 30 | 420 | 95 | 104 | 0 | 0 | 162 | 54 | 0 | 100 | 113 | 100 | 0 | 104 |  | 917 | 0 | 260 | 0 | 115 | 225 | 0 | 0 | 10 | 0 | 40 | 0 | 36 | 110 | 0 | 0 | 0 | 50 | 42 | 98 | 0 | 0 | 47 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 88 | 100 | 170 | 0 | 412 | 53 | 100 | 35 | 0 | 93 | 0 | 0 | 90 | 600 |  | 12091 | EvPeak
Forecast for Evening | 0 | 0 | 120 | 115 | 200 | 42 | 0 | 0 | 360 | 0 | 0 | 225 | 305 | 7 | 100 | 55 | 0 | 0 | 150 | 0 | 7 | 102 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 44 | 0 | 120 | 0 | 25 | 221 | 0 | 140 | 0 | 0 | 0 |  | 100 | 100 | 100 | 50 | 21 | 25 | 0 | 0 | 80 | 360 | 0 | 225 | 8 | 90 | 30 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 8 | 33 | 21 | 173 | 160 | 0 | 14 | 0 | 60 | 30 | 51 | 44 | 0 | 200 | 65 | 86 | 0 | 220 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 100 | 100 | 0 | 300 | 54 | 110 | 100 | 113 | 100 | 0 | 104 |  | 935 | 16 | 410 | 0 | 115 | 225 | 0 | 0 | 30 | 60 | 40 | 0 | 33 | 110 | 0 | 0 | 0 | 50 | 42 | 100 | 0 | 0 | 50 | 52 | 34 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 | 0 | 90 | 100 | 220 | 0 | 414 | 53 | 200 | 35 | 100 | 100 | 0 | 0 | 90 | 620
Forecast for Day | 0 | 0 | 120 | 115 | 200 | 42 | 0 | 0 | 360 | 0 | 0 | 225 | 280 | 7 | 100 | 55 | 0 | 0 | 120 | 0 | 7 | 102 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 44 | 0 | 120 | 0 | 25 | 221 | 0 | 140 | 0 | 0 | 0 |  | 100 | 100 | 100 | 50 | 21 | 10 | 0 | 0 | 80 | 360 | 0 | 225 | 8 | 90 | 30 | 55 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 33 | 21 | 162 | 160 | 0 | 14 | 1.6 | 60 | 30 | 51 | 44 | 0 | 200 | 65 | 86 | 0 | 220 | 18 | 0 | 10 | 341 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 200 | 150 | 400 | 115 | 100 | 100 | 5 | 300 | 54 | 110 | 100 | 113 | 100 | 0 | 104 |  | 935 | 0 | 410 | 0 | 115 | 225 | 0 | 0 | 0 | 0 | 40 | 0 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 50 | 52 | 0 | 22 | 10 | 10 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 |  | 80 | 50 | 220 | 0 | 414 | 53 | 100 | 35 | 100 | 100 | 0 | 8 | 90 | 620
Generation at 08:00(Today) | 0 | 0 | 120 | 115 | 200 | 42 | 0 | 0 | 323 | 0 | 0 | 225 | 290 |  | 80 | 30 | 0 | 0 | 155 | 0 | 7 | 16 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 22 | 25 | 22 | 33 | 33 | 0 | 0 | 43 | 0 | 120 | 0 | 0 | 205 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 19 | 20 | 3 | 0 | 0 | 80 | 325 | 0 | 187 | 8 | 94 | 26 | 56 | 0 | 51 | 0 | 0 | 8 | 22 | 8 | 33 | 21 | 106 | 158 | 0 | 14 | 1 | 60 | 30 | 50 | 47 | 0 | 181 | 40 | 85 | 0 | 218 | 18 | 0 | 10 | 300 | 24 | 0 | 0 | 95 | 0 | 0 | 120 | 0 | 117 | 9 | 60 | 0 | 16 | 419 | 29 | 20 | 0 | 3 | 160 | 17 | 0 | 17 | 55 | 100 | 0 | 104 | 0 | 925 | 0 | 200 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 89 | 0 | 140 | 0 | 416 | 18 | 0 | 35 | 0 | 27 | 0 | 2 | 35 | 520 | 0
199
| Minimum Generation |  | 8517 | 8:00
| Highest Generation |  | 12091 | 20:00
| Day Peak Generation |  | 9624 | 12:00
| Evening Peak Generation |  | 12091 | 20:00
| HVDC Max Flow |  | 926 | 7:00
| HVDC EvPeak Flow |  | 917 | 20:00
| Load factor L.F |  | 83.79%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-10-04
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-10-03 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9624 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 8930 | MW
Evening Peak Generation : |  | 12091 | MW Hour : | 20:00 | Available Max Generation : |  | 14068 | MW
E.P. Demand (at gen end) : |  | 12091 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 12700 | MW
Maximum Generation : |  | 12091 | MW Hour : | 20:00 | Reserve(Generation end) |  | 1368 | MW
Total Gen. (MKWH) : |  | 243.1386 | System Load Factor : | 83.79% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 52 | MW at | 21:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-10-04
Actual : | 99.42 | Ft.(MSL) , | Rule curve : | 106.27 | Ft.( MSL )
Gas Consumed : | Total = | 1120.12 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 147135871.418
: |  | Coal : | 79401778 | Oil : | 618250589.12 | Total : | 844788238.538
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4527.6238 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1543.8454 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1383.9832 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1250.8114 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1130.1936 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 912.0368 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 504.5579 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 234.6818 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 703.4339 |  |  | 0 | 0%
Total | 0 |  | 12191.1679 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Baghabari-71 MW,100 MW
3) Ghorasal Unit-1,2,3,
4) Ashuganj unit-3,4
5) Kaptai-2,4,5
6) Raozan #1,2
7) Siddirganj-335 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Aminbazar-Kaliakoir 132 kV Ckt-1 was under shut down from 09:42 to 16:59 for A/M.
b) Mirpur-Uttara 132 kV Ckt was under shut down from 08:20 to 17:50 for A/M.
c) B.Pukuria-Saidpur 132 kV Ckt-1 was under shut down from 10:08 to 23:13 due to problem at CT
at Saidpur end.
d) Mymensing-Netrokona 132 kV Ckt-1 was under shut down from 09:14 to 13:35 for C/M.
e) Mymensing 132 kV Bus-B was under shut down from 09:48 to 17:05 for C/M.
f) HVDC 10CF13 filter was under shut down from 09:14 to 16:05 for A/M.
g) Tangail 132/33 kV T-2 transformer was under shut down from 08:2 to 12:32 for C/M.
h) Rangpur 132/33 kV T-1 transformer was under shut down from 08:10 to 16:20 for A/M.
i) Bogura 230/132 kV T-1 transformer was under shut down from 08:11 to 17:44 for A/M.
j) After maintenance Ashuganj(N)-360 MW CCPP ST was synchronized at 09:18.
k) Summit Megnaghat-305 MW GT-2 was synchronized at 11:17.
l) Chandraghona-Rangamati 132 kV Ckt-1 was under shut down from 10:35 to 17:10 for D/W.
m) Natore 132/33 kV T-1 transformer was under shut down from 13:11 to 16:33 for C/M.
n) Natore 132/33 kV T-2 transformer was under shut down from 14:15 to 14:44 for C/M.
o) Chandraghona-Rangamati 132 kV Ckt-2 was under shut down from 17:17 to 21:06 for D/W.
p) Bibiyana-3 CCPP GT & ST were synchronized at 16:37 & 17:18 respectively.
q) Haripur-Megnaghat 230 kV Ckt-1 was under shut down from 08:15 to 21:10 for A/M.
r) Barapukuria 132/33 kV T-3 transformer tripped at 16:26 showing O/C & E/F relays and was switched
on at 16:41.
s) Chandraghona-Rangamati 132 kV Ckt-1 tripped at 17:31 showing gen.trip at Chandraghona end and |  |  |  |  | About 25 MW power interruption occurred under Rangamati &
was switched on at 17:40. |  |  |  |  | Khagrachari S/S areas from 17:31 to 17:40.
t) Bagerhat-Bhandaria 132 kV Ckt was under shut down from 06:23 to 08:38(4/10/20) for red hot maint.
u) Chowmuhoni 132/33 kV T-1 transformer is under shut down since 06:32(4/10/20) for C/M. |  |  |  |  | About 20 MW power interruption occurred under Chowmuhoni S/S area
since 06:32(4/10/20).
v) Raozan #1 tripped at 03:02(4/10/20) due to boiler trip and was synchronized at 04:46(4/10/20).
w) Kuiara-163 MW CCPP GT was synchronized at 22:58 and shut down at 06:40(4/10/20) for internal problem.
x) Siddirganj-Maniknagar 230 kV Ckt-1 is under shut down since 07:17(4/10/20) for A/M.
y) Ashuganj(S)-360 MW CCPP GT was synchronized at 02:23(4/10/20).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-10-03 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 120 | 2883000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 115 | 2677500 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 4784200 | Machin problem.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 41 | 992136 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 350 | 7994000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4684300 | GT-2 Under maint.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 7 | 355200 | Fuel Shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 290 | 4860276
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 97 | 2239992
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 965304
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 22 | 965836 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 428976
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 188 | 3993000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 7 | 409920 | Fuel Shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under Maintenance
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 16 | 1436544 | Fuel Shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel Shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1203120
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 2085600
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1275831
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1322681
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 47 | 1048200 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 770500
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 654500
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 52 | 492996
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 7000361
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 100 | 740176 | Low demand.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 85 | 420725 | Engine problem
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 101 | 560523
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 132 | 3127540 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 104 | 2080992
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2621760
| Dhaka area Total |  |  |  | 5895 | 3160 | 65075689
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 115 | 2700000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 22 | 204228
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 127575
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 861600
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 44 | 940020 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4849873
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 139 | 3316504
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 704750
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 20 | 168720 | High voltage
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2348160
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 481728
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 26 | 595200
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 97 | 2143680 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 31560
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 162 | 3633164 | transformer O/L.
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1033000
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2386560
| Chattogram area Total |  |  |  | 2266 | 1254 | 26526322
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 1933474 | Under maint.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 181 | 4160000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 6035300 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 653688 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 30 | 1037760 | Gas shortage
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 384727 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1244730
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 30 | 791200 | R/H at APSCL
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 253640
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2172700
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 1196640
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 473688
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 139500 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 158 | 3479040
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 817500
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 921398
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 508160 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 50 | 292608 | Low demand.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 100 | 1357740 | Engine problem
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 2688000
| Cumilla Area Total |  |  |  | 2980 | 1616 | 30541493
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 157 | 3674880 | Machine problem & Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 14 | 323316 | Engine problem
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 0 | 0 | Man power problem due to corona effected.
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10850
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 4711200 | Low demand.
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 95 | 1336800 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 466 | 10057046
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1396000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 711480 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 16936
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 177 | 3484000 | Gas shortage & ST under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1130400
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 46 | 1066464
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 204000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 65 | 1449 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 88 | 1981440
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 218 | 4502760
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 420000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 574200
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 7118800 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 420 | 3881000
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 239400
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 1790200 | On test
| Sylhet Area Total |  |  |  | 1988 | 1502 | 28518529
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 917 | 22077090
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 1707840
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 10 | 72000 | Engine problem
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 225 | 3558720
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 4352 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 260 | 7377120 | Gas shortage.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 308250
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 619200
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 756000 | Engine problem
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Line O/L.
| Khulna Area Total |  |  |  | 2284 | 1720 | 36480572
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1067520
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 36 | 738760
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 88 | 2111359 | Engine problem
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 600 | 13535400
| Barisal Area Total |  |  |  | 1054 | 834 | 17453039
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 427504
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 42 | 239242
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel Shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel Shortage
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 47 | 457500
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas Shortage
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 158 | 4345327 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 170 | 4308555 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 412 | 8508327 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 503760
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 10 | 236808
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 240084
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 641280
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 98 | 1147832
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 100 | 393593 | Low demand.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 35 | 912480 | Engine problem
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 90 | 1241088 | Engine problem
| Rajshahi Area Total |  |  |  | 2183 | 1296 | 23603380
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3686600 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 93 | 1171200 | Engine problem
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 24711
| Rangpur Area Total |  |  |  | 605 | 243 | 4882511
| Total |  |  |  | 19892 | 12091 | 243138581
| Eastern Grid Total |  |  |  | 13766 | 7998 | 160719079
| Western Grid Total |  |  |  | 6126 | 4093 | 82419502
| National Grid Total |  |  |  | 19892 | 12091 | 243138581
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-10-03
| (a) ENTIRE EASTERN GRID : |  | 7884 | MW | (b) ENTIRE WESTERN GRID : |  | 3714 | MW
| i) Dhaka area |  | 4072 | MW | i) Khulna area |  | 1461 | MW
| ii) Chittagong area |  | 1178 | MW | ii) Rajshahi area |  | 1224 | MW
| iii) Comilla area |  | 1180 | MW | iii) Barisal area |  | 344 | MW
| iv) Mymensingh area |  | 931 | MW | iv) Rangpur area |  | 685 | MW
| v) Sylhet area |  | 523 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11598 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 124 | 9:00 | Sherpur | 102 | 18:30 | Jhenida | 104 | 18:30
| Munsiganj | 120 | 21:00 | Srimongal | 51 | 19:00 | Bottail | 126 | 18:30
| Sonargaon | 71 | 1:00 | Shahjibazar | 119 | 19:30 | G.K Project | 52 | 18:30
| Shyampur | 194 | 10:00 | Fenchuganj | 46 | 18:30 | Faridpur | 194 | 0.875
| Bhulta | 202 | 19:00 | Kulawara | 47 | 19:30 | Madaripur | 104 | 0.875
| Madanganj | 60 | 11:00 | Sylhet | 141 | 18:30 | Sariatpur | 64 | 20:00
| Shitalakhya | 101 | 12:00 | Chatak | 29 | 22:00 | Gopalganj | 91 | 19:00
| Rahim steel | 18 | 14:00 | Sunamganj | 48 | 20:00 | Bagerhat | 101 | 20:00
| Matuail | 82 | 12:00 | Biani Bazar | 54 | 22:00 | Mongla | 38 | 9:00
| Ghorasal | 80 | 22:00 | Comilla (S) | 170 | 18:00 | Satkhira | 107 | 0.8125
| Narsingdi | 172 | 19:30 | Comilla(N) | 129 | 19:30 | Gallamari | 45 | 15:00
| Haripur (SBU) | 103 | 21:00 | Chandpur | 104 | 20:00 | Magura | 55 | 0.79167
| Ullon | 61 | 18:00 | Feni | 126 | 20:00 | Norail | 42 | 19:00
| Hasnabad | 211 | 20:00 | Chowmuhani | 180 | 21:00 | Chuadanga | 91 | 20:00
| Magbazar | 95 | 14:00 | Ashuganj | 64 | 20:00 | Barisal(N) | 45 | 0.875
| Maniknagar | 86 | 12:00 | Daudkandi | 139 | 19:30 | Barisal (S) | 100 | 0.91667
| Bangabhaban | 20 | 10:00 | B.Baria | 156 | 19:30 | Patuakhali | 118 | 0.875
| Narinda | 86 | 11:00 | Ramganj | 112 | 21:00 | Bhandaria | 52 | 0.83333
| Dhanmondi | 166 | 13:00 | Chaddagram | 37 | 21:00 | Borhan Uddin | 45 | 22:00
| Lalbag | 82 | 18:00 | PHP | 11 | 19:00 | Ishurdi | 66 | 18:30
| Madartek | 73 | 23:00 | Madunaghat | 57 | 20:00 | Ruppur Paromanobik | 2 | 21:00
| Dhaka University |  |  | Hathazari | 103 | 0.79167 | Natore | 119 | 20:00
| Fatullah | 43 | 0.58333 | Khulshi | 205 | 0.75 | Bogra | 162 | 20:00
| Mirpur | 109 | 18:00 | Halishahar | 132 | 0.77083 | Noagaon | 110 | 21:00
| Kalyanpur | 92 | 18:30 | Baraulia | 117 | 0.95833 | Rajshahi | 138 | 20:00
| Gulshan | 114 | 13:00 | Sikalbaha | 26 | 0.75 | Rajshahi New | 9 | 21:00
| Uttara | 89 | 18:30 | Dohazari | 92 | 0.875 | C.Nawabganj | 67 | 21:00
| Uttara New | 33 | 18:30 | Cox'sbazar | 107 | 0.83333 | Amnura | 42 | 20:00
| Kamrangirchar | 91 | 19:00 | Chandraghona | 32 | 0.77083 | Pabna | 120 | 20:00
| Savar | 144 | 15:00 | Kaptai | 4.8 | 0.75 | Shahjadpur | 102 | 21:00
| Bhasantec | 148 | 18:30 | A. Khaer Stl. | 7 | 0.625 | Serajganj | 103 | 19:30
| Agargaon | 67 | 18:30 | Bakulia | 108 | 0.77083 | Niyamatpur | 51 | 21:00
| Satmosjid | 101 | 18:30 | Julda | 21 | 0.625 | Joypurhat | 55 | 19:30
| Tongi | 98 | 0.54167 | TK chemical | 26 | 0.041667 | Sherpur(Bogura) | 46 | 18:30
| Kabirpur | 218 | 15:00 | Modern Steel | 14 | 0.95833 | Mohastangor | 47 | 20:00
| Basundhara | 138 | 18:00 | Shahmirpur | 30 | 0.875 | Rangpur | 143 | 18:30
| Manikganj | 70 | 0.875 | Khagrachhari | 26 | 0.041667 | Lalmonirhat | 55 | 18:30
| Joydevpur | 144 | 18:30 | Matarbari | 40.5 | 0.8125 | Saidpur | 82 | 10:00
| New Tongi | 106 | 13:00 | Baroiar Hat | 50 | 0.041667 | Purbasadipur | 86 | 21:00
| Korda | 239 | 15:00 | Rangamati | 12 | 0.77083 | Thakurgaon | 70 | 21:00
| Dhamrai | 92 | 19:00 | Abul Khair 230 | 63 | 0.29167 | Palashbari | 116 | 20:00
| Rajendrapur | 98 | 21:00 | BSRM | 153 | 0.66667 | Barapukuria | 53 | 21:00
| Valuka | 126 | 22:00 | GPH Ispat | 76 | 0.375 | Panchagar | 44 | 18:00
| Tangail | 195 | 19:00 | Goalpara | 28 | 0.54167 | Joldhaka | 25 | 18:30
| Mymensing | 162 | 18:00 | Central s/s | 81 | 18:30 | Kurigram | 57 | 19:00
| Kishorganj | 145 | 22:00 | Noapara | 54 | 18:30
| Netrokona | 113 | 22:00 | Jessore | 114 | 18:30
| Jamalpur | 131 | 23:00 | Benapol | 40 | 18:30
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-10-03 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 398 | 1:00 | 387 | 21:00 | Kaliakoir | 382 | 0.29167 | 366 | 0.5
| Bheramara | 395 | 6:00 | 390 | 1:00 | Bhulta | 390 | 0.083333 | 369 | 0.45833
| Ashuganj(N) | 395 | 3:00 | 375 | 11:00 | Gopalganj | 412 | 0.25 | 390 | 0.77083
| Payra | 413 | 1:00 | 402 | 18:30
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 236 | 1:00 | 232 | 22:00 | Comilla (N) | 239 | 18:30 | 224 | 13:00
| Ishurdi | 231 | 6:00 | 225 | 21:00 | Hathazari | 228 | 2:00 | 224 | 11:00
| Ashuganj | 236 | 1:00 | 228 | 11:00 | Megnaghat | 232 | 5:00 | 224 | 13:00
| Serajganj | 229 | 7:00 | 225 | 11:00 | Fenchuganj | 236 | 2:00 | 231 | 18:00
| Baghabari | 238 | 1:00 | 233 | 22:00 | Siddhirganj | 234 | 1:00 | 219 | 11:00
| Barapukuria | 238 | 17:00 | 230 | 24:00 | Maniknagar | 230 | 2:00 | 216 | 12:00
| Bogra | 225 | 17:00 | 214 | 19:30 | Agargaon | 230 | 7:00 | 213 | 12:00
| Rajshahi | 226 | 18:00 | 217 | 20:00 | Barisal | 251 | 1:00 | 230 | 21:00
| Khulna South | 233 | 17:00 | 227 | 4:00 | AKSML | 224 | 1:00 | 221 | 4:00
| Rampura | 230 | 1:00 | 220 | 11:00 | BSRM | 226 | 4:00 | 220 | 11:00
| Haripur | 229 | 1:00 | 217 | 12:00 | Bibiyana | 236 | 2:00 | 228 | 20:00
| Hasnabad | 230 | 1:00 | 218 | 12:00 | Bhulta | 233 | 19:00 | 220 | 17:00
| Shyampur | 228 | 1:00 | 213 | 11:00 | Ashuganj (S) | 234 | 2:00 | 229 | 11:00
| Aminbazar | 224 | 18:00 | 216 | 12:00 | Kaliakoir | 233 | 3:00 | 222 | 11:00
| Tongi | 231 | 1:00 | 219 | 11:00 | GPH | 224 | 3:00 | 219 | 7:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 133 | 1:00 | 123 | 11:00 | Hathazari | 135 | 0.041667 | 133 | 0.45833
| Munsiganj | 135 | 8:00 | 125 | 12:00 | Khulshi | 133 | 0.041667 | 131 | 0.41667
| Sonargaon | 132 | 1:00 | 126 | 12:00 | Halishahar | 136 | 0.083333 | 133 | 0.20833
| Shyampur | 135 | 2:00 | 124 | 12:00 | Baraulia | 134 | 0.041667 | 130 | 0.875
| Bhulta | 129 | 9:00 | 118 | 15:00 | Sikalbaha | 136 | 1:00 | 134 | 0.125
| Madanganj | 132 | 5:00 | 124 | 12:00 | Dohazari | 133 | 8:00 | 129 | 0.625
| Shitalakhya | 143 | 1:00 | 125 | 11:00 | Cox'sbazar | 129 | 0.33333 | 117 | 0.83333
| Rahim steal | 132 | 1:00 | 123 | 12:00 | Chandraghona | 135 | 0.33333 | 132 | 0.66667
| Matuail | 133 | 1:00 | 123 | 11:00 | Kaptai | 134 | 1:00 | 132 | 0.29167
| Ghorasal | 140 | 1:00 | 136 | 21:00 | A. Khaer Stl. | 134 | 0.041667 | 132 | 12:00
| Narsinghdi | 128 | 7:00 | 120 | 12:00 | Bakulia | 134 | 0.083333 | 132 | 0.66667
| Haripur (SBU) | 133 | 1:00 | 124 | 11:00 | Julda | 135 | 0.29167 | 133 | 0.625
| Ullon | 137 | 4:00 | 127 | 11:00 | TK Chemical | 135 | 0.041667 | 134 | 10:00
| Hasnabad | 140 | 2:00 | 127 | 11:00 | Modern Steel | 135 | 0.041667 | 133 | 0.41667
| Magbazar | 137 | 5:00 | 127 | 9:00 | Shahmirpur | 136 | 0.041667 | 133 | 0.70833
| Maniknagar | 135 | 1:00 | 125 | 12:00 | Khagrachhari | 133 | 0.041667 | 130 | 0.79167
| Bangabhaban | 135 | 1:00 | 125 | 12:00 | Matarbari | 131 | 0.45833 | 120 | 0.83333
| Narinda | 135 | 1:00 | 125 | 12:00 | Baroiar Hat | 134 | 0.58333 | 130 | 0.66667
| Dhanmondi | 137 | 4:00 | 127 | 11:00 | Rangamati | 134 | 0.041667 | 131 | 16:00
| Lalbag | 140 | 1:00 | 125 | 11:00 | Goalpara S/S | 135 | 17:00 | 131 | 6:00
| Madartek | 136 | 1:00 | 127 | 11:00 | Khulna Central S/S | 135 | 0.70833 | 131 | 18:30
| Dhaka University |  |  |  |  | Noapara | 132 | 9:00 | 128 | 5:00
| Fatuiiah | 135 | 0.083333 | 125 | 10:00 | Jessore | 130 | 9:00 | 122 | 18:30
| Mirpur | 138 | 6:00 | 127 | 12:00 | Benapol | 130 | 9:00 | 122 | 18:30
| Kalyanpur | 138 | 6:00 | 128 | 12:00 | Jhenida | 128 | 0.375 | 116 | 18:30
| Gulshan | 136 | 2:00 | 126 | 12:00 | Bottail | 134 | 9:00 | 126 | 18:30
| Uttara | 136 | 6:00 | 126 | 12:00 | G.K Project | 139 | 0.45833 | 135 | 19:00
| Uttara New | 137 | 5:00 | 126 | 12:00 | Faridpur | 132 | 9:00 | 124 | 21:00
| Kamrangirchar | 136 | 4:00 | 123 | 12:00 | Madaripur | 137 | 0.29167 | 127 | 18:30
| Savar | 137 | 6:00 | 126 | 12:00 | Shariyatpur S/S | 137 | 0.29167 | 126 | 21:00
| Bhasantec | 139 | 6:00 | 127 | 12:00 | Gopalganj | 136 | 6:00 | 125 | 20:00
| Agargaon | 140 | 6:00 | 129 | 12:00 | Bagerhat | 131 | 17:00 | 124 | 19:30
| Satmosjid | 140 | 6:00 | 128 | 12:00 | Mongla | 127 | 0.16667 | 120 | 18:00
| Tongi | 137 | 0.041667 | 129 | 11:00 | Satkhira | 134 | 0.70833 | 126 | 19:30
| Kabirpur | 135 | 4:00 | 126 | 20:00 | Gallamari | 134 | 17:00 | 131 | 4:00
| Basundhara | 136 | 1:00 | 127 | 11:00 | Magura | 127 | 9:00 | 114 | 18:30
| Manikganj | 140 | 1:00 | 131 | 12:00 | Norail | 126 | 0.375 | 112 | 18:30
| Joydevpur | 142 | 13:00 | 135 | 11:00 | Chuadanga | 124 | 9:00 | 107 | 18:30
| New Tongi | 137 | 0.041667 | 127 | 12:00 | Barisal(N) | 141 | 7:00 | 128 | 18:30
| Kodda | 136 | 3:00 | 123 | 0.5 | Barisal (S) | 139 | 0.29167 | 128 | 15:00
| Dhamrai | 135 | 5:00 | 125 | 21:00 | Patuakhali(S) | 135 | 0.29167 | 122 | 21:00
| Rajendrapur | 137 | 1:00 | 125 | 12:00 | Bhandaria | 126 | 11:00 | 116 | 20:00
| Valuka | 131 | 14:00 | 126 | 2:00 | Ishurdi | 137 | 6:00 | 132 | 21:00
| Tangail | 134 | 6:00 | 122 | 20:00 | Ruppur Paromanobik | 136 | 5:00 | 132 | 21:00
| Mymensing | 133 | 8:00 | 112 | 21:00 | Natore | 137 | 17:00 | 130 | 21:00
| Kishorganj | 132 | 8:00 | 117 | 21:00 | Bogra | 135 | 6:00 | 127 | 21:00
| Netrokona | 131 | 8:00 | 108 | 21:00 | Noagaon | 131 | 7:00 | 119 | 21:00
| Jamalpur | 139 | 8:00 | 123 | 21:00 | Rajshahi | 137 | 17:00 | 131 | 21:00
| Sherpur | 137 | 5:00 | 120 | 21:00 | Rajshahi New | 138 | 17:00 | 131 | 21:00
| Srimongal | 138 | 8:00 | 133 | 0.79167 | C.Nawabganj | 136 | 17:00 | 130 | 21:00
| Shahjibazar | 135 | 9:00 | 130 | 0.79167 | Amnura | 137 | 17:00 | 129 | 5:00
| Fenchuganj | 135 | 4:00 | 131 | 0.77083 | Pabna | 134 | 5:00 | 128 | 21:00
| Khulawara | 134 | 6:00 | 130 | 0.75 | Shahjadpur | 137 | 6:00 | 135 | 21:00
| Sylhet | 133 | 5:00 | 130 | 0.041667 | Serajganj | 133 | 6:00 | 127 | 21:00
| Chatak | 132 | 7:00 | 126 | 22:00 | Niyamatpur | 132 | 6:00 | 116 | 21:00
| Sunamganj | 131 | 8:00 | 124 | 0.91667 | Joypurhat | 132 | 6:00 | 119 | 21:00
| Biani Bazar | 132 | 7:00 | 126 | 0.91667 | Sherpur(Bogura) | 135 | 17:00 | 128 | 21:00
| Comilla(s) | 129 | 6:00 | 117 | 18:00 | Mohastangor | 134 | 17:00 | 126 | 21:00
| Comilla(n) | 138 | 18:30 | 134 | 16:00 | Rangpur | 130 | 17:00 | 117 | 18:30
| Chandpur | 138 | 19:00 | 132 | 10:00 | Lalmonirhat | 126 | 7:00 | 118 | 20:00
| Feni | 135 | 19:00 | 131 | 11:00 | Saidpur | 130 | 6:00 | 120 | 11:00
| Chowmuhani | 135 | 7:00 | 130 | 18:00 | Purbasadipur | 129 | 6:00 | 113 | 19:30
| Ashuganj | 136 | 6:00 | 131 | 23:00 | Thakurgaon | 127 | 17:00 | 113 | 11:00
| Daudkandi | 138 | 18:30 | 126 | 11:00 | Palashbari | 130 | 6:00 | 120 | 21:00
| B.Baria | 134 | 8:00 | 127 | 20:00 | Barapukuria | 138 | 17:00 | 131 | 19:00
| Ramganj | 130 | 20:00 | 127 | 17:00 | Panchagar | 126 | 17:00 | 112 | 19:00
| Chaddagram | 135 | 19:30 | 134 | 12:00 | Joldhaka | 131 | 6:00 | 116 | 21:00
| PHP | 135 | 12:00 | 129 | 4:00 | Kurigram | 127 | 17:00 | 116 | 20:00
| Madanhat | 137 | 1:00 | 135 | 4:00

## L-Curve
Date | 2020-10-03
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 172 | 7798 | 3862 | 11660 |  |  |  | QF-LDC-11
0:30 | 211 | 7333.5 | 3685.5 | 11019 | Date: | 2020-10-03
1:00 | 250 | 6869 | 3509 | 10378
1:30 | 251 | 6766 | 3459.5 | 10225.5
2:00 | 252 | 6663 | 3410 | 10073
2:30 | 256.5 | 6557 | 3388.5 | 9945.5 | [5 empty] | Gen. at Eve. Peak | 12091 | 12091 MW (20:00 )
3:00 | 261 | 6451 | 3367 | 9818 | [6 empty] | 20:00
3:30 | 272.5 | 6358 | 3286 | 9644 | [5 empty] | Gen. at Day Peak | 9624 | 9624 MW (12:00 )
4:00 | 284 | 6265 | 3205 | 9470 | [6 empty] | 12:00
4:30 | 285.5 | 6224 | 3191 | 9415 | [5 empty] | Highest Generation | 12091
5:00 | 287 | 6183 | 3177 | 9360 | [6 empty] | 20:00
5:30 | 379 | 5981.5 | 3159 | 9140.5
6:00 | 471 | 5780 | 3141 | 8921
6:30 | 499 | 5632 | 3110.5 | 8742.5
7:00 | 527 | 5484 | 3080 | 8564
7:30 | 521.5 | 5505 | 3035.5 | 8540.5
8:00 | 516 | 5526 | 2991 | 8517
8:30 | 542 | 5580.5 | 2985.5 | 8566
9:00 | 568 | 5635 | 2980 | 8615
9:30 | 540.5 | 5808.5 | 2961 | 8769.5
10:00 | 513 | 5982 | 2942 | 8924
10:30 | 518.5 | 6050.5 | 2982 | 9032.5
11:00 | 524 | 6119 | 3022 | 9141
11:30 | 474.5 | 6304 | 3078.5 | 9382.5
12:00 | 425 | 6489 | 3135 | 9624
12:30 | 339 | 6666 | 3072.5 | 9738.5
13:00 | 253 | 6843 | 3010 | 9853
13:30 | 199 | 6806 | 2940.5 | 9746.5
14:00 | 145 | 6769 | 2871 | 9640
14:30 | 170 | 6902.5 | 2947 | 9849.5
15:00 | 195 | 7036 | 3023 | 10059
15:30 | 320.5 | 6872 | 3048 | 9920
16:00 | 446 | 6708 | 3073 | 9781
16:30 | 519 | 6491 | 3104 | 9595
17:00 | 592 | 6274 | 3135 | 9409
17:30 | 465 | 6801 | 3371 | 10172
18:00 | 338 | 7328 | 3607 | 10935
18:30 | 275 | 7599 | 3862 | 11461
19:00 | 212 | 7870 | 4117 | 11987
19:30 | 185 | 7919 | 4096 | 12015
20:00 | 160 | 7998 | 4093 | 12091 |  |  |  | Executive Engineer
20:30 | 106 | 7984 | 4028.5 | 12012.5 |  |  |  | Network Operation Division
21:00 | 52 | 7970 | 3964 | 11934
21:30 | 88 | 7965.5 | 3967.5 | 11933
22:00 | 124 | 7961 | 3971 | 11932 |  |  |  |  | Page 6 of 7
22:30 | 151 | 7963.5 | 3961.5 | 11925
23:00 | 178 | 7966 | 3952 | 11918
23:30 | 175 | 7882 | 3907 | 11789
24:00 | 172 | 7798 | 3862 | 11660
12091 MW (20:00 )
9624 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-10-03 |  | Energy | 243138581
[10 empty] | 2020-10-03 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3716 | 918 | 1819 | 3716 | 750 | 44 | 752 | 0 | 152
0:30 | 3491.5 | 921.5 | 1805 | 3368.5 | 730 | 44 | 607 | 0 | 155 | Date: | 2020-10-03
1:00 | 3267 | 925 | 1791 | 3021 | 710 | 44 | 462 | 0 | 158
1:30 | 3274.5 | 924.5 | 1795 | 2924.5 | 710 | 43.5 | 397.5 | 0 | 156 | [7 empty] | Total Energy | 243.1386 | Total Energy Gen 243.139 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 243.139 MKWHr
2:00 | 3282 | 924 | 1799 | 2828 | 710 | 43 | 333 | 0 | 154 | [7 empty] | Energy not Served | 0
2:30 | 3338 | 924.5 | 1815.5 | 2690.5 | 710 | 42 | 273 | 0 | 152 | [7 empty] | Energy Requirement | 243.1386
3:00 | 3394 | 925 | 1832 | 2553 | 710 | 41 | 213 | 0 | 150
3:30 | 3413.5 | 925 | 1836.5 | 2402 | 710 | 40.5 | 166.5 | 0 | 150 | [6 empty] | Shortage
4:00 | 3433 | 925 | 1841 | 2251 | 710 | 40 | 120 | 0 | 150
4:30 | 3421.5 | 925 | 1841 | 2215.5 | 705 | 40 | 120 | 0 | 147
5:00 | 3410 | 925 | 1841 | 2180 | 700 | 40 | 120 | 0 | 144
5:30 | 3330 | 925 | 1808 | 2077 | 700 | 40.5 | 120 | 0 | 140
6:00 | 3250 | 925 | 1775 | 1974 | 700 | 41 | 120 | 0 | 136
6:30 | 3208 | 925.5 | 1732 | 1874.5 | 690 | 41 | 120 | 0 | 149 |  |  |  |  | Coal
7:00 | 3166 | 926 | 1689 | 1775 | 680 | 41 | 120 | 0 | 162
7:30 | 3123 | 922 | 1679 | 1840 | 665 | 41 | 120 | 0 | 141 |  |  |  | Oil |  |  |  | ,
8:00 | 3080 | 918 | 1669 | 1905 | 650 | 41 | 120 | 0 | 120
8:30 | 3103 | 918 | 1658 | 1955.5 | 640 | 41.5 | 120 | 0 | 119
9:00 | 3126 | 918 | 1647 | 2006 | 630 | 42 | 120 | 0 | 118
9:30 | 3276.5 | 918 | 1643.5 | 2002.5 | 629.5 | 42 | 120 | 0 | 120
10:00 | 3427 | 918 | 1640 | 1999 | 629 | 42 | 120 | 0 | 122
10:30 | 3441 | 918 | 1681 | 2051 | 629.5 | 42.5 | 120 | 0 | 121
11:00 | 3455 | 918 | 1722 | 2103 | 630 | 43 | 120 | 0 | 120
11:30 | 3494.5 | 918 | 1742 | 2226 | 640.5 | 43 | 164 | 0 | 125
12:00 | 3534 | 918 | 1762 | 2349 | 651 | 43 | 208 | 0 | 130
12:30 | 3536.5 | 918 | 1676 | 2489.5 | 651 | 43 | 263 | 0 | 132
13:00 | 3539 | 918 | 1590 | 2630 | 651 | 43 | 318 | 0 | 134
13:30 | 3539 | 918 | 1590 | 2630 | 651 | 43 | 318 | 0 | 134
14:00 | 3539 | 918 | 1590 | 2630 | 651 | 43 | 318 | 0 | 134
14:30 | 3585.5 | 918.5 | 1541 | 2696.5 | 670.5 | 41.5 | 341 | 0 | 137
15:00 | 3632 | 919 | 1492 | 2763 | 690 | 40 | 364 | 0 | 140
15:30 | 3582.5 | 918 | 1537 | 2645.5 | 690 | 40 | 349 | 0 | 142
16:00 | 3533 | 917 | 1582 | 2528 | 690 | 40 | 334 | 0 | 144
16:30 | 3405 | 917.5 | 1565 | 2520 | 665 | 40 | 335 | 0 | 140
17:00 | 3277 | 918 | 1548 | 2512 | 640 | 40 | 336 | 0 | 136
17:30 | 3408 | 918 | 1572 | 2981 | 645 | 40 | 454 | 0 | 153
18:00 | 3539 | 918 | 1596 | 3450 | 650 | 40 | 572 | 0 | 170
18:30 | 3627.5 | 918 | 1675 | 3677 | 690 | 41 | 669.5 | 0 | 163
19:00 | 3716 | 918 | 1754 | 3904 | 730 | 42 | 767 | 0 | 156
19:30 | 3773 | 918 | 1762 | 3838 | 750 | 42 | 778 | 0 | 154
20:00 | 3802 | 917 | 1777 | 3869 | 750 | 44 | 774 | 0 | 158
20:30 | 3778 | 917.5 | 1798 | 3795.5 | 750 | 44 | 771.5 | 0 | 158
21:00 | 3754 | 918 | 1819 | 3722 | 750 | 44 | 769 | 0 | 158
21:30 | 3748.5 | 918 | 1830 | 3717.5 | 750 | 44 | 767 | 0 | 158
22:00 | 3743 | 918 | 1841 | 3713 | 750 | 44 | 765 | 0 | 158
22:30 | 3733 | 918 | 1840 | 3714.5 | 750 | 44 | 767.5 | 0 | 158
23:00 | 3723 | 918 | 1839 | 3716 | 750 | 44 | 770 | 0 | 158
23:30 | 3719.5 | 918 | 1829 | 3716 | 750 | 44 | 761 | 0 | 155 | Max Temp. in Dhaka |  | 33.3° C
24:00 | 3716 | 918 | 1819 | 3716 | 750 | 44 | 752 | 0 | 152
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
Total Energy Gen 243.139 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 243.139 MKWHr
Note on W13: Author:

## Generation
g | 2020-10-03
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 44 | 43 | 41 | 40 | 40 | 41 | 41 | 41 | 42 | 42 | 43 | 43 | 43 | 42 | 40 | 40 | 40 | 40 |  | 42 | 42 | 44 | 44 | 44 | 44 | 44 | 940020
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2700000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | [13 empty] | 10 |  |  | 9 |  | 3 | 12 | 22 | 25 | 25 | 25 | 25 | 204228
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 4 | 10 |  | 18 | 20 | 20 | 19 |  | 13 | 10 | 2 | [9 empty] | 127575
6 | Sikalbaha 225MW CCPP (Gas) | 202 | 202 | 202 | 204 | 204 | 203 | 210 | 204 | 204 | 204 | 204 | 207 | 204 | 204 | 204 | 204 | 204 | 213 |  | 204 | 203 | 203 | 205 | 204 | 203 | 204 | 4849873
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 140 | 140 | 140 | 140 | 140 | 139 | 139 | 139 | 140 | 139 | 139 | 140 | 139 | 139 | 139 | 104 | 104 | 139 |  | 139 | 139 | 139 | 139 | 139 | 140 | 140 | 3316504
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | [16 empty] | 99 |  | 102 | 102 | 102 | 102 | 102 | 102 | 85 | 704750
12 | Hathazari 100 MW peaking PP
Sikalbaha 105 MW PP (Baraka Sikalbaha)
| Daudkandi 200 MW PP (B.Trac) | [17 empty] | 108 |  | 157 | 50 | 50 |  |  |  |  | 292608
14 | Titas 50 MW Peaking PP | [19 empty] | 50 | 50 | 50 | 42 | 42 | 42 | 41 | 253640
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 185 | 185 | 195 | 195 | 165 | 115 | 120 | 120 | 120 | 120 | 153 | 189 | 120 | 120 | 160 | 120 | 120 | 120 |  | 185 | 185 | 188 | 155 | 155 | 155 | 145 | 3993000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 300 | 300 | 300 | 300 | 300 | 245 | 230 | 230 | 265 | 300 | 286 | 285 | 290 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 296 | 286 | 286 | 7000361
19 | Ashuganj 195MW PP (APSCL-United) | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 384727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 121 | 119 | 121 | 120 | 119 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2883000
23 | Ghorasal TPP Unit-5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2677500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4784200
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1933474
32 | Ashuganj 50 MW PP | 29 | 29 | 29 | 27 | 27 | 27 | 27 | 27 | 27 | 29 | 29 | 29 | 29 | 29 | 26 | 26 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 653688
33 | Ashuganj 225 MW CCPP | 40 | 53 | 154 | 187 | 189 | 179 | 197 | 179 | 181 | 180 | 180 | 190 | 179 | 179 | 183 | 182 | 182 | 200 |  | 181 | 181 | 181 | 194 | 183 | 181 | 180 | 4160000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 245 | 245 | 245 | 245 | 245 | 140 | 15 | 15 | 30 | 90 | 130 | 160 | 345 | 360 | 355 | 355 | 335 | 330 |  | 310 | 310 | 310 | 320 | 310 | 310 | 310 | 6035300
35 | Ashuganj 55 MW PP (Precision) | 55 | 55 | 55 | 55 | 54 | 54 | 55 | 55 | 54 | 53 | 52 | 50 | 52 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 30 | 55 | 55 | 55 | 55 | 1037760
36 | Chandpur 150 MW CCPP | 86 | 86 | 88 | 96 | 96 | 85 | 94 | 92 | 95 | 85 | 96 | 96 | 85 | 85 | 90 | 95 | 85 | 95 |  | 90 | 88 | 90 | 95 | 95 | 87 | 85 | 2172700
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 4684300
41 | Haripur 360MW CCPP(HPL) | 353 | 355 | 355 | 352 | 353 | 356 | 303 | 303 | 303 | 347 | 347 | 342 | 302 | 271 | 344 | 344 | 302 | 324 |  | 350 | 350 | 350 | 349 | 351 | 353 | 354 | 7994000
42 | RPCL 210MW CCPP | 159 | 161 | 158 | 158 | 158 | 160 | 158 | 157 | 156 | 154 | 154 | 151 | 153 | 153 | 154 | 154 | 156 | 154 |  | 157 | 157 | 157 | 158 | 157 | 157 | 157 | 3674880
43
44 | Fenchugonj CCPP Phase-1 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 60 | 60 | 60 | 58 | 58 | 58 | 57 | 57 | 60 | 59 |  | 60 | 60 | 60 | 59 | 60 | 60 | 60 | 1396000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 711480
46 | Shajibazar 330 MW CCPP | 141 | 141 | 140 | 140 | 142 | 141 | 140 | 140 | 140 | 141 | 140 | 142 | 142 | 138 | 142 | 141 | 142 | 178 |  | 181 | 183 | 177 | 179 | 180 | 180 | 180 | 3484000
47 | Shahjibazar GTPP Unit- 8 & 9 | 67 | 65 | 65 | 65 | 65 | 67 | 66 | 65 | 65 | 65 | 65 | 65 | 40 | 40 | 40 | 40 | 40 | 65 |  | 65 | 65 | 65 | 65 | 65 | 66 | 67 | 1449
48 | Shahjibazar 86MW PP (Shahjibazar) | 88 | 88 | 88 | 88 | 88 | 88 | 85 | 85 | 85 | 80 | 83 | 83 | 85 | 40 | 84 | 87 | 86 | 87 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 1981440
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 135 | 185 | 191 | 191 | 200 |  | 218 | 219 | 218 | 218 | 218 | 218 | 219 | 4502760
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 420000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 9 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 239400
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 204000
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 47 | 47 | 50 | 47 | 47 | 47 | 47 | 50 | 10 | 19 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1130400
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 574200
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 285 | 280 | 295 | 295 | 285 | 275 | 300 | 290 | 290 | 300 | 310 | 270 | 270 | 285 | 290 | 290 | 285 |  | 290 | 295 | 285 | 290 | 300 | 290 | 280 | 7118800
| Bibiyana South 400 MW | [9 empty] | 273 | 271 | 266 | 278 | 273 | 274 | 250 | [10 empty] | 1790200
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1322681
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 481728
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 428976
62 | Tangail 22 MW PP (Doreen) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 323316
63 | Impoprt (Tripura) | 158 | 154 | 150 | 150 | 144 | 136 | 162 | 120 | 118 | 122 | 120 | 130 | 134 | 136 | 140 | 144 | 136 | 170 |  | 156 | 154 | 158 | 158 | 158 | 158 | 152 | 3479040
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 38 | 36 | 13 | 4 | 4 | 2 | 3 | 8 | 5 | 5 | 6 | 8 | 8 |  | 21 | 22 | 26 | 33 | 40 | 42 | 42 | 595200
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 22 | 22 | 22 | 19 | 19 | 21 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 473688
66 | Feni 11 MW PP (Doreen) | 5 | 5 | 5 | 5 | 5 | 5 | 2 | 2 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 139500
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 817500
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 17 | 15 | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 508160
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 9 | 8 | 8 | 8 | 20 | 20 | 20 | 20 | 21 |  | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 448200
71 | Maona 33 MW PP(Summit) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 33 | 33 | 33 | 0 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 770500
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 654500
73 | Ghorashal 108MW PP (Regent) | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 43 | 43 | 42 | 42 | 43 | 43 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 42 | 42 | 992136
| Feni Lanka Power | 100 | 100 | [8 empty] | 17 | 100 | 100 | 100 | 100 | 30 | 17 | 80 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1357740
| Chowmuhani 113 MW | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 110 | 105 | 105 | 104 | 110 | 111 | 112 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 110 | 113 | 2688000
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 94 | 38 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 409920
78 | Gazipur 52 MW PP | 52 | [11 empty] | 16 | 20 | 48 |  |  | 16 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 492996
79 | Kodda 150MW PP | 150 | 115 | 48 | [8 empty] | 64 | 150 | 150 | 150 | 98 | 98 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 2085600
80 | Jamalpur 95 MW PP(Powerpac) | [25 empty] | 0 | 0
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | [5 empty] | 1 | 16 | 25 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 921398
| Gazipur 100 MW PP | 105 | 105 | 105 | 50 | 50 | 17 | 17 | 17 | 52 | 70 | 73 | 98 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 104 | 104 | 104 | 104 | 104 | 2080992
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 4 | 5 | 6 | 2 | 5 | 4 | 4 | 2 | [10 empty] | 31560
| Jodiac Power | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 48 | 51 | 36 | 36 | 42 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 40 | 1033000
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 85 | 80 | 90 | 96 | 92 | 80 | 91 | 97 |  | 80 | 97 | 97 | 97 | 97 | 97 | 96 | 2239992
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 100 | 65 | [9 empty] | 7 | 90 | 100 | 100 | 50 | 38 | 22 |  | 23 | 23 | 22 | 23 | 40 | 100 | 100 | 965836
86 | Meghnaghat CCPP(Summit) | 130 | 130 | 135 | 140 | 143 | 128 | 140 | 140 | 140 | 130 | 140 | 150 | 220 | 300 | 290 | 280 | 280 | 300 |  | 280 | 290 | 290 | 300 | 290 | 295 | 265 | 4860276
87 | Meghnaghat 100 MW(IEL) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 8 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 355200
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 2621760
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 20 | [12 empty] | 10 | 10 |  |  | 10 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 168720
92 | Fenchuganj 44MW (Energyprima) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 44 | 44 | 44 | 43 | 46 | 46 | 46 | 10 | 15 |  | 46 | 46 | 46 | 47 | 47 | 47 | 47 | 1066464
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1244730
94 | Gagnagar 102 MW PP (Digital Power) | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 50 | 50 | 50 | 50 | 50 | 50 | 40 | 40 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 1436544
95 | Patenga 50MW PP (Baraka) | 50 | 50 | 50 | [5 empty] | 2 | 18 | 22 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 861600
96 | Chattogram 108 MW PP (ECPV) | 91 | 92 | 91 | 86 | 91 | 84 | 62 | 67 | 91 | 85 | 85 | 82 | 86 | 90 | 90 | 91 | 91 | 91 |  | 93 | 97 | 97 | 97 | 97 | 97 | 98 | 2143680
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 32 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 55 | 55 | 55 | 40 | 40 | 40 | 40 | 965304
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1275831
101 | Kushiara 163 MW CCPP (KP) | [24 empty] | 10 | 20 | 16936
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 2 | 2 | 1 | 3 | 1 | 1 | 0 | 0 | [10 empty] | 10850
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 17 | 17 | 17 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1203120
104 | Keranigonj 300 MW PP (APR) | [17 empty] | 219 |  | 106 | 100 | 100 | 100 | 103 | 100 | 25 | 740176
105 | Bramhangoan 100 MW PP (Aggreko) | [17 empty] | 50 |  | 85 | 85 | 85 | 82 | 56 | 38 | 30 | 420725
106 | Mymensingh 200 MW PP (United) | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 180 | 180 | 185 | 200 | 192 | 192 | 192 | 200 | 200 | 200 |  | 200 | 200 | 200 | 183 | 192 | 200 | 193 | 4711200
112 | Aurahati 100MW PP (Aggreko) | [17 empty] | 98 |  | 101 | 101 | 101 | 101 | 97 | 61 | 54 | 560523
114 | Kodda 149 MW PP Unit-1 (Summit) | 133 | 133 | 132 | 132 | 132 | 128 | 102 | 103 | 109 | 109 | 125 | 112 | 124 | 132 | 132 | 132 | 131 | 132 |  | 131 | 131 | 132 | 149 | 149 | 149 | 149 | 3127540
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 60 | 60 | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 2348160
116 | Chandpur 200MW (Desh energy) | [17 empty] | 15 |  | 157 | 200 | 200 | 200 | 200 | 200 | 200 | 1196640
117 | Ashuganj 150MW PP (Midland) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 791200
118 | Bibiyana-III 400 MW CCPP | 85 | 87 | 87 | 87 | 86 | 86 | 87 | 84 | 87 | 87 | 84 | 86 | 87 | 80 | 80 | 85 | 95 | 215 |  | 308 | 370 | 420 | 418 | 418 | 422 | 425 | 3881000
| Jamalpur 115 MW PP (United) | 85 | 85 | 85 | 85 | 65 | 45 | 8 | 8 |  |  |  | 10 | 45 | 24 | 24 | 24 | 24 | 29 |  | 82 | 95 | 95 | 95 | 103 | 115 | 115 | 1336800
| Anwara 300 MW PP (United) | 162 | 162 | 162 | 162 | 162 | 126 | 88 | 122 | 125 | 124 | 160 | 160 | 161 | 161 | 161 | 161 | 125 | 125 |  | 161 | 161 | 162 | 162 | 162 | 162 | 162 | 3633164
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2386560
120 | Eastern Zone Total | 6869 | 6663 | 6451 | 6265 | 6183 | 5780 | 5484 | 5526 | 5635 | 5982 | 6119 | 6489 | 6843 | 6769 | 7036 | 6708 | 6274 | 7328 |  | 7870 | 7919 | 7998 | 7970 | 7961 | 7966 | 7798 | 160719079
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 115 | 115 | 115 | 16 |  |  |  |  | 16 | 16 | 49 | 73 | 83 | 83 | 83 | 87 | 99 | 99 |  | 99 | 99 | 115 | 115 | 115 | 115 | 115 | 1707840
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 2 | 3 |  | 6 | 16 | 10 | 17 | 13 | 13 | 13 | 72000
| Khulna 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 145 |  | 225 | 225 | 225 | 225 | 225 | 230 | 230 | 3558720
129 | Rupsha 105 MW PP (Orion rupsha) | 36 | 36 | 36 | 36 | 36 | 36 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 756000
130
131
132
133
| Barisal 110 MW PP (Summit ) | 64 | 64 | 32 | 32 | 32 | 32 | 16 | [9 empty] | 6 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 1067520
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 92 | 92 | 92 | 92 | 91 | 90 | 91 | 73 | 73 | 73 | 88 | 87 | 86 | 88 | 89 | 87 | 90 | 90 |  | 93 | 89 | 88 | 89 | 92 | 92 | 92 | 2111359
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 38 | 38 | 37 | 32 | 32 | 28 | 25 | 25 | 23 | 23 | 23 | 25 | 27 | 27 | 25 | 27 | 25 | 38 |  | 37 | 37 | 36 | 38 | 38 | 38 | 38 | 738760
141 | Noapara 100 MW PP (Bangla Trac) | [17 empty] | 20 |  | 99 | 100 | 100 | 100 | 100 | 100 | 100 | 619200
142 | Noapara 40 MW PP (Khanjahan Ali) | [13 empty] | 8 | 8 |  |  | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 308250
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 10 | [8 empty] | 4352
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 925 | 924 | 925 | 925 | 925 | 925 | 926 | 918 | 918 | 918 | 918 | 918 | 918 | 918 | 919 | 917 | 918 | 918 |  | 918 | 918 | 917 | 918 | 918 | 918 | 918 | 22077090
147 | Bheramara 410 MW CCPP | 320 | 320 | 320 | 320 | 320 | 330 | 340 | 325 | 320 | 315 | 305 | 290 | 270 | 255 | 285 | 295 | 300 | 290 |  | 285 | 280 | 260 | 245 | 255 | 240 | 240 | 7377120
148 | Payra 1320 MW | 560 | 560 | 560 | 560 | 550 | 550 | 530 | 500 | 480 | 480 | 480 | 500 | 500 | 500 | 540 | 540 | 490 | 500 |  | 580 | 600 | 600 | 600 | 600 | 600 | 600 | 13535400
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 150 | 151 | 151 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3686600
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [14 empty] | 10 | 25 | 25 | 25 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 427504
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 187 | 187 | 187 | 187 | 189 | 192 | 193 | 190 | 190 | 188 | 181 | 174 | 164 | 130 | 152 | 152 | 152 | 153 |  | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 4345327
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 180 | 180 | 183 | 186 | 188 | 190 | 191 | 191 | 189 | 186 | 184 | 176 | 130 | 130 | 159 | 130 | 130 | 142 |  | 170 | 170 | 170 | 140 | 140 | 140 | 140 | 4308555
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 362 | 363 | 402 | 404 | 405 | 355 | 338 | 337 | 338 | 312 | 366 | 405 | 303 | 183 | 189 | 270 | 351 | 354 |  | 403 | 409 | 412 | 414 | 414 | 407 | 386 | 8508327
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 10 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 239242
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 503760
163 | Bogura 20 MW PP (Energyprima) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 236808
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 240084
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | 43 | [12 empty] | 19 | 36 | 43 | 43 | 43 |  | 44 | 45 | 47 | 43 | 43 | 43 | 43 | 457500
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | 52 | [10 empty] | 31 | 52 | 52 | 52 | 25 | 25 | 25 |  | 50 | 50 | 52 | 52 | 52 | 52 | 52 | 641280
170 | Chapainawabganj 100 MW Peaking PP | 98 | 98 | 45 | [8 empty] | 24 | 48 | 48 | 48 | 48 | 48 | 87 |  | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 1147832
171 | Baghabari 200 MW PP (Paramount) | [17 empty] | 100 |  | 150 | 100 | 100 |  |  |  | 0 | 393593
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 912480
172 | Confidence Power Bogura Unit-1 113 MW | 50 | 50 | 50 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 50 | 1241088
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 40 | 36 | 36 | 36 | 30 | 34 | 34 | 35 | 35 | 34 | 29 | 28 | 24 | 27 | 27 | 27 | 32 | 71 |  | 90 | 90 | 93 | 100 | 98 | 96 | 67 | 1171200
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 2 | 3 | 4 | 5 | 4 | 2 | 1 | 0 | [9 empty] | 24711
178
178