## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-10-05 | Monday
|  |  | Date (day): | 2020-10-05 |  | Monday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13427.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14573 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-10-04 | 2020-10-05 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 150 | 150 | 150 | 150 | 30 |  | Gas shortage
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 115 | 115 | 115 | 75 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 200 | 200
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 42 | 42 | 42 | 42 | 66 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under S/D for dust in gas.
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 344 | 350 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 92 | 7 | 7 | 93 |  | Fuel shortage
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 300 | 290 | 305 | 305
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 80 | 80 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 34 | 40 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 12 | 66 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 0 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 180 | 153 | 200 | 200 |  |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 7 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 16 | 7 | 7 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 64 | 150 | 149 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 45 | 45 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 33 | 51 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 230 | 300 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 153 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 25 | 74 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 98 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 149 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 68 | 103 | 100 | 100
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 2682 | 3274 | 3337 | 3948 | 606 | 1162
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 115 | 115 | 120 | 120 | 60 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 13 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 44 | 42 | 44 | 44 | 186 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 209 | 204 | 221 | 221
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 107 | 139 | 140 | 140
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 100 | 100
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 37 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 21 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 16 | 10 | 25
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 62 | 97 | 100 | 100
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 141 | 143 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 18 | 54 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 954 | 1244 | 1720 | 1710 | 426 | 98
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 100 | 100 | 100 |  | 34 | Engine problem
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 199 | 176 | 225 | 225 |  |  | FGMO
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 345 | 315 | 360 | 360 |  |  | FGMO
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 195 | 170 | 250 | 250 |  | 110 | ST under maintenance
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 29 | 30 | 30 | 15 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 50 | 55 | 55 | 55
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 30 | 30 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 42 | 0 | 50
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 96 | 90 | 90 | 90 |  | 73 | ST under shut down
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 200 | 200 | 200
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 21 | 22 | 22
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 124 | 156 | 162 | 173
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 52 | 52 | 52
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 21 | 21 | 21 | 21
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 130 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 34 | 100 | 100 | 100 |  | 14 | Engine problem
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 113 | 113 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1479 | 1900 | 2030 | 2291 | 466 | 234
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 153 | 156 | 160 | 160 | 42 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 14 | 17 | 14 | 14 |  | 8 | Engine problem
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 0 | 0 | 0 |  | 95 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 160 | 200 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 45 | 96 | 115 | 115
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 373 | 469 | 490.6 | 489 | 42 | 103
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 57 | 60 | 60 | 60
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 35 | Unit-4 under shut down
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maintenance
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 181 | 180 | 200 | 200 |  | 110 | ST Under maint.
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 50 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 47 | 47 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 0 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 65 | 66 | 65 | 65
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 88 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 198 | 216 | 220 | 220
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 290 | 341 | 341 |  |  | FGMO
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 415 | 421 | 400 | 400
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 199 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1675 | 1500 | 1561 | 1561 | 0 | 308
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 900 | 901 | 912 | 912
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 49 | 115 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 9 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 160 | 225 | 225
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 315 | 245 | 270 | 270
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 53 | 53 | 53 |  | 52 | Engine problem
| 108 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1401 | 1623 | 1765 | 1921 | 0 | 52
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 110 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 26 | 38 | 33 | 33
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 90 | 89 | 80 | 90
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 490 | 570 | 620 | 620
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 622 | 807 | 843 | 853 | 0 | 194
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 42 | 0 | 42
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 43 | 50 | 50
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 164 | 140 | 220 | 220 |  |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 140 | 131 | 220 | 220 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 388 | 400 | 414 | 414 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 34
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 10 | 10 | 10 | 10
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 10 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 8 | 52 | 52 | 52
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 96 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 120 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 35 | 35 | 35 | 35 |  | 78 | Engine problem
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 109 | 90 | 90 |  | 23 | Engine problem
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 812 | 1261 | 1423 | 1550 | 481 | 101
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 27 | 89 | 100 | 100 |  | 13 | Engine problem
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 182 | 239 | 258 | 250 | 294 | 53
|  | Total |  |  |  |  | 20383 | 19892 | 10180 | 12317 | 13427.6 | 14573 | 2315 | 2305
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9777.4945 | 11830 | 12896.6882 | 13996.8004
| A. |  | 2020-10-04 | (Yesterday) |  |  |  |  | Sunday
| 1 | Highest Generation : |  |  | 12317 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 8930 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12317 | MW
| 3 | Day peak Generation : |  |  | 10180 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11830 | MW
| 4 | Evening peak Generation : |  |  | 12317 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 258.5077 | MKWHr | By Solar | 0.17375 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 134.5672 | MKWHr |  | By Oil: | 80.1432 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 17.6036 | MKWHr |  | By Hydro: | 0.96408 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2315 | MW | Dhaka | 4241 | 4241 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2305 | MW | Chittagong | 1200 | 1200 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4620 | MW | Khulna | 1498 | 1498 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1171.58 | MMCFD |  |  | Rajshahi | 1239 | 1239 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 158762687.078 | ii) Oil : | Taka | 644095388.85 | Comilla | 1150 | 1150 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 81079886 | Total | Taka | 883937961.928 | Mymensingh | 934 | 934 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.434 | MKWHr. | Sylhet | 496 | 496 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -75 | MW (E to W) at | 19:00 | hrs | Barisal | 332 | 332 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -230 | MW at | 21:00 | hrs | Rangpur | 740 | 740 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.0° C |  |  | Total | 11830 | 11830 |  | 0
| B. |  | 2020-10-05 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 33.3° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12700 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14573 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10500 | MW
| 4 | Reserve(Generation end) |  |  |  | 1873 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 266.5461 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8982 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.8015 | MKWHr. | ii) HVDC Flow at Peak Time |  | 901 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.2544 | MKWHr. | iii) Maximum HVDC Flow : |  | 926 | MW at | 7:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 99.42 |  | (b) Today: | 99.99 |  | (c) Rule Curve: |  | 106.36
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-10-04
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 120 | 115 | 200 | 42 | 0 | 0 | 323 |  | 0 | 225 | 285 | 7 | 82 | 40 | 0 | 0 | 155 | 0 | 7 | 16 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 52 | 0 | 44 | 0 | 115 | 0 | 25 | 203 | 0 | 140 | 0 |  | 0 | 0 | 102 | 0 | 97 | 50 | 20 | 42 | 0 | 0 | 80 | 310 | 10 | 183 | 8 | 95 | 26 | 55 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 33 | 21 | 148 | 157 | 0 | 14 | 0 | 60 | 30 | 50 | 47 | 15 | 182 | 40 | 88 | 0 | 218 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 300 | 0 | 0 | 194 | 0 | 149 | 0 | 90 | 132 | 30 | 420 | 85 | 104 | 0 | 0 | 162 | 37 | 0 | 100 | 113 | 100 | 0 | 104 |  | 925 | 0 | 240 | 0 | 115 | 170 | 0 | 0 | 13 | 0 | 40 | 0 | 38 | 96 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 92 | 100 | 140 | 0 | 419 | 18 | 0 | 35 | 0 | 28 | 0 | 0 | 50 | 600 |  | 7519 | 3619 | 11138 | 3711 | 925 | 1816 | 3211 | 750 | 44 | 533 | 148 | 0 | 0 | 99.22
2:00 | 0 | 0 | 120 | 115 | 200 | 41 | 0 | 0 | 323 |  | 0 | 225 | 280 | 7 | 95 | 40 | 0 | 0 | 155 | 0 | 7 | 16 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 52 | 0 | 43 | 0 | 115 | 0 | 25 | 203 | 0 | 140 | 0 |  | 0 | 0 | 102 | 0 | 97 | 50 | 20 | 42 | 0 | 0 | 80 | 310 | 20 | 181 | 8 | 96 | 26 | 55 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 33 | 21 | 142 | 157 | 0 | 14 | 0 | 60 | 30 | 50 | 47 | 20 | 180 | 40 | 88 | 0 | 218 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 300 | 0 | 0 | 193 | 0 | 149 | 0 | 100 | 0 | 30 | 424 | 85 | 104 | 0 | 0 | 162 | 34 | 0 | 100 | 113 | 100 | 0 | 104 |  | 924 | 0 | 240 | 0 | 115 | 120 | 0 | 0 | 13 | 0 | 40 | 0 | 37 | 96 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 92 | 20 | 140 | 0 | 402 | 17 | 0 | 35 | 0 | 26 | 0 | 0 | 50 | 580 |  | 7419 | 3447 | 10866 | 3722 | 924 | 1812 | 3010 | 730 | 43 | 483 | 142 | 0 | 0 | 99.26
3:00 | 0 | 0 | 120 | 115 | 200 | 41 | 0 | 0 | 324 |  | 0 | 225 | 290 | 7 | 96 | 40 | 0 | 0 | 155 | 0 | 7 | 16 | 115 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 203 | 0 | 140 | 0 |  | 0 | 0 | 68 | 0 | 97 | 50 | 20 | 42 | 0 | 0 | 80 | 310 | 20 | 182 | 8 | 96 | 26 | 55 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 33 | 21 | 138 | 157 | 0 | 14 | 0 | 60 | 30 | 50 | 47 | 30 | 181 | 40 | 88 | 0 | 218 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 300 | 0 | 0 | 193 | 0 | 149 | 0 | 100 | 0 | 30 | 421 | 85 | 104 | 0 | 0 | 162 | 27 | 0 | 100 | 113 | 100 | 0 | 104 |  | 925 | 0 | 240 | 0 | 115 | 120 | 0 | 0 | 12 | 0 | 40 | 0 | 37 | 64 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 92 | 0 | 140 | 0 | 423 | 17 | 0 | 35 | 0 | 25 | 0 | 0 | 50 | 580 |  | 7127 | 3415 | 10542 | 3606 | 925 | 1854 | 2834 | 730 | 42 | 413 | 138 | 0 | 0 | 99.3
4:00 | 0 | 0 | 120 | 115 | 200 | 41 | 0 | 0 | 323 |  | 0 | 225 | 265 | 7 | 95 | 40 | 0 | 0 | 155 | 0 | 7 | 16 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 34 | 0 | 93 | 50 | 20 | 42 | 0 | 0 | 80 | 310 | 30 | 181 | 8 | 86 | 26 | 55 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 33 | 21 | 134 | 159 | 0 | 14 | 0 | 60 | 30 | 50 | 47 | 35 | 180 | 40 | 88 | 0 | 218 | 18 | 0 | 9 | 285 | 24 | 8 | 0 | 300 | 0 | 0 | 194 | 0 | 149 | 0 | 100 | 0 | 30 | 418 | 85 | 103 | 0 | 0 | 162 | 36 | 0 | 100 | 113 | 100 | 0 | 104 |  | 925 | 0 | 240 | 0 | 115 | 120 | 0 | 0 | 12 | 0 | 40 | 0 | 36 | 64 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 52 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 92 | 0 | 140 | 0 | 394 | 17 | 0 | 35 | 0 | 27 | 0 | 0 | 35 | 580 |  | 7002 | 3369 | 10371 | 3600 | 925 | 1812 | 2750 | 730 | 41 | 379 | 134 | 0 | 0 | 99.34
5:00 | 0 | 0 | 120 | 115 | 200 | 41 | 0 | 0 | 323 |  | 0 | 225 | 285 | 7 | 80 | 40 | 0 | 0 | 155 | 0 | 7 | 16 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 0 | 0 | 40 | 0 | 90 | 0 | 0 | 203 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 97 | 50 | 20 | 42 | 0 | 0 | 80 | 310 | 30 | 182 | 8 | 95 | 26 | 55 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 33 | 21 | 130 | 159 | 0 | 14 | 0 | 60 | 30 | 50 | 44 | 35 | 180 | 40 | 88 | 0 | 218 | 18 | 0 | 10 | 285 | 24 | 0 | 0 | 300 | 0 | 0 | 194 | 0 | 149 | 0 | 100 | 0 | 30 | 419 | 85 | 50 | 0 | 0 | 162 | 36 | 0 | 70 | 108 | 100 | 0 | 104 |  | 925 | 0 | 245 | 0 | 104 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 92 | 0 | 140 | 0 | 403 | 18 | 0 | 35 | 0 | 27 | 0 | 0 | 35 | 580 |  | 6942 | 3186 | 10128 | 3698 | 925 | 1818 | 2585 | 730 | 40 | 202 | 130 | 0 | 0 | 99.38
6:00 | 0 | 0 | 120 | 115 | 200 | 41 | 0 | 0 | 323 |  | 0 | 225 | 260 | 7 | 80 | 40 | 0 | 0 | 150 | 0 | 7 | 7 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 22 | 25 | 22 | 33 | 33 | 0 | 0 | 42 | 0 | 115 | 0 | 0 | 204 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 81 | 23 | 20 | 38 | 0 | 0 | 80 | 310 | 30 | 181 | 8 | 86 | 26 | 55 | 0 | 51 | 0 | 0 | 50 | 22 | 8 | 33 | 21 | 126 | 159 | 0 | 14 | 0 | 60 | 30 | 50 | 47 | 35 | 183 | 40 | 88 | 0 | 218 | 18 | 0 | 9 | 280 | 24 | 0 | 0 | 195 | 0 | 0 | 193 | 0 | 149 | 0 | 100 | 0 | 30 | 417 | 35 | 16 | 0 | 0 | 162 | 36 | 0 | 24 | 107 | 100 | 0 | 104 |  | 925 | 0 | 255 | 0 | 51 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 90 | 0 | 140 | 0 | 378 | 18 | 0 | 35 | 0 | 27 | 0 | 0 | 35 | 540 |  | 6506 | 3048 | 9554 | 3720 | 925 | 1780 | 2135 | 690 | 42 | 136 | 126 | 0 | 0 | 99.42
7:00 | 0 | 0 | 120 | 115 | 200 | 42 | 0 | 0 | 323 |  | 0 | 225 | 290 | 7 | 80 | 25 | 0 | 0 | 155 | 0 | 7 | 16 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 22 | 25 | 22 | 33 | 33 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 203 | 0 | 138 | 0 |  | 0 | 0 | 0 | 0 | 23 | 19 | 20 | 33 | 0 | 0 | 80 | 310 | 35 | 184 | 8 | 96 | 26 | 55 | 0 | 51 | 0 | 0 | 8 | 22 | 8 | 33 | 21 | 112 | 158 | 0 | 14 | 0 | 60 | 30 | 50 | 47 | 0 | 182 | 40 | 88 | 0 | 216 | 18 | 0 | 9 | 265 | 24 | 0 | 0 | 95 | 0 | 0 | 120 | 0 | 144 | 5 | 50 | 0 | 30 | 419 | 16 | 16 | 0 | 1 | 125 | 36 | 0 | 17 | 55 | 100 | 0 | 104 |  | 926 | 0 | 185 | 0 | 18 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 90 | 0 | 140 | 0 | 415 | 18 | 0 | 35 | 0 | 27 | 0 | 1 | 35 | 540 |  | 5988 | 2947 | 8935 | 3673 | 926 | 1758 | 1591 | 690 | 42 | 136 | 112 | 7 | 0 | 99.45
8:00 | 0 | 0 | 120 | 115 | 200 | 42 | 0 | 0 | 323 |  | 0 | 225 | 290 | 7 | 80 | 30 | 0 | 0 | 155 | 0 | 7 | 16 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 22 | 25 | 22 | 33 | 33 | 0 | 0 | 43 | 0 | 120 | 0 | 0 | 205 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 16 | 19 | 20 | 3 | 0 | 0 | 80 | 325 | 0 | 187 | 8 | 94 | 26 | 56 | 0 | 51 | 0 | 0 | 8 | 22 | 8 | 33 | 21 | 106 | 158 | 0 | 14 | 1 | 60 | 30 | 50 | 47 | 0 | 181 | 40 | 85 | 0 | 218 | 18 | 0 | 10 | 300 | 24 | 0 | 0 | 95 | 0 | 0 | 120 | 0 | 117 | 9 | 60 | 0 | 16 | 419 | 29 | 20 | 0 | 3 | 160 | 17 | 0 | 17 | 55 | 100 | 0 | 104 |  | 925 | 0 | 200 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 89 | 0 | 140 | 0 | 416 | 18 | 0 | 35 | 0 | 27 | 0 | 2 | 35 | 520 |  | 5997 | 2933 | 8930 | 3673 | 925 | 1755 | 1607 | 670 | 43 | 136 | 106 | 15 | 0 | 99.48
9:00 | 0 | 0 | 120 | 115 | 200 | 41 | 0 | 0 | 292 |  | 0 | 225 | 288 | 7 | 80 | 40 | 0 | 0 | 120 | 0 | 7 | 16 | 82 | 7 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 0 | 0 | 43 | 0 | 120 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 60 | 19 | 20 | 3 | 0 | 0 | 80 | 325 | 35 | 181 | 8 | 94 | 26 | 56 | 0 | 51 | 0 | 0 | 37 | 22 | 8 | 33 | 21 | 110 | 156 | 0 | 14 | 1 | 60 | 30 | 50 | 47 | 0 | 180 | 40 | 85 | 0 | 218 | 18 | 0 | 10 | 280 | 16 | 0 | 0 | 180 | 0 | 0 | 160 | 0 | 134 | 16 | 100 | 0 | 30 | 419 | 45 | 68 | 0 | 4 | 161 | 17 | 0 | 52 | 105 | 100 | 0 | 104 |  | 901 | 0 | 190 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 89 | 0 | 140 | 0 | 386 | 17 | 0 | 35 | 0 | 27 | 0 | 2 | 35 | 500 |  | 6499 | 2920 | 9419 | 3610 | 901 | 1678 | 2202 | 650 | 43 | 202 | 110 | 23 | 0 | 99.51
10:00 | 0 | 0 | 120 | 115 | 200 | 41 | 0 | 0 | 328 |  | 0 | 225 | 285 | 7 | 80 | 40 | 0 | 0 | 120 | 0 | 7 | 16 | 64 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 21 | 33 | 33 | 0 | 0 | 43 | 0 | 115 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 60 | 19 | 20 | 3 | 0 | 0 | 80 | 325 | 235 | 182 | 8 | 87 | 26 | 54 | 0 | 43 | 0 | 0 | 52 | 22 | 8 | 33 | 21 | 112 | 154 | 0 | 14 | 2 | 60 | 30 | 47 | 44 | 0 | 181 | 40 | 83 | 0 | 218 | 18 | 0 | 10 | 290 | 24 | 5 | 0 | 230 | 0 | 0 | 160 | 0 | 149 | 11 | 100 | 0 | 30 | 423 | 45 | 68 | 0 | 5 | 124 | 17 | 0 | 34 | 113 | 100 | 100 | 104 |  | 901 | 0 | 190 | 0 | 49 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 10 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 158 | 0 | 89 | 0 | 140 | 0 | 385 | 17 | 0 | 35 | 0 | 26 | 0 | 3 | 35 | 470 |  | 6847 | 2857 | 9704 | 3917 | 901 | 1705 | 2202 | 619 | 43 | 184 | 112 | 21 | 0 | 99.54
11:00 | 0 | 0 | 120 | 115 | 200 | 42 | 0 | 0 | 346 |  | 0 | 225 | 290 | 7 | 80 | 28 | 0 | 0 | 180 | 0 | 7 | 16 | 64 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 33 | 26 | 0 | 44 | 0 | 115 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 62 | 19 | 18 | 2 | 0 | 0 | 80 | 295 | 245 | 183 | 8 | 87 | 26 | 51 | 0 | 43 | 0 | 0 | 52 | 22 | 8 | 33 | 21 | 116 | 154 | 0 | 14 | 2 | 59 | 30 | 50 | 44 | 0 | 183 | 40 | 40 | 0 | 198 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 230 | 0 | 25 | 160 | 0 | 149 | 0 | 100 | 0 | 30 | 421 | 45 | 68 | 0 | 3 | 124 | 18 | 0 | 34 | 113 | 100 | 220 | 104 |  | 900 | 0 | 210 | 0 | 49 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 159 | 0 | 89 | 0 | 140 | 0 | 380 | 17 | 0 | 35 | 0 | 27 | 0 | 5 | 35 | 470 |  | 6991 | 2877 | 9868 | 4078 | 900 | 1666 | 2250 | 620 | 44 | 184 | 116 | 10 | 0 | 99.56
12:00 | 0 | 0 | 150 | 115 | 200 | 42 | 0 | 0 | 344 |  | 0 | 225 | 300 | 7 | 80 | 34 | 0 | 0 | 180 | 0 | 7 | 16 | 64 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 33 | 33 | 0 | 44 | 0 | 115 | 0 | 0 | 209 | 0 | 107 | 0 |  | 0 | 0 | 0 | 0 | 62 | 19 | 20 | 2 | 0 | 0 | 80 | 345 | 195 | 199 | 8 | 96 | 26 | 50 | 0 | 43 | 0 | 0 | 52 | 22 | 8 | 33 | 21 | 124 | 153 | 0 | 14 | 1 | 57 | 30 | 50 | 47 | 0 | 181 | 65 | 83 | 0 | 198 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 230 | 0 | 25 | 160 | 0 | 149 | 13 | 100 | 0 | 30 | 415 | 45 | 68 | 0 | 4 | 141 | 18 | 0 | 34 | 113 | 100 | 199 | 104 |  | 900 | 0 | 315 | 0 | 49 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 164 | 0 | 90 | 0 | 140 | 0 | 388 | 17 | 0 | 35 | 0 | 27 | 0 | 5 | 35 | 490 |  | 7163 | 3017 | 10180 | 4246 | 900 | 1729 | 2290 | 640 | 44 | 184 | 124 | 23 | 0 | 99.58
13:00 | 0 | 0 | 150 | 115 | 200 | 42 | 0 | 0 | 344 |  | 0 | 225 | 290 | 7 | 80 | 40 | 0 | 0 | 178 | 0 | 7 | 16 | 64 | 13 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 33 | 33 | 0 | 40 | 0 | 115 | 0 | 0 | 207 | 0 | 144 | 0 |  | 0 | 0 | 0 | 0 | 75 | 32 | 20 | 8 | 0 | 0 | 100 | 325 | 190 | 189 | 8 | 95 | 29 | 50 | 0 | 43 | 0 | 0 | 52 | 22 | 8 | 33 | 21 | 120 | 151 | 0 | 11 | 0 | 58 | 30 | 50 | 47 | 0 | 182 | 65 | 83 | 0 | 219 | 18 | 0 | 9 | 310 | 24 | 8 | 0 | 280 | 0 | 25 | 185 | 0 | 149 | 9 | 100 | 0 | 30 | 418 | 65 | 68 | 0 | 4 | 177 | 33 | 0 | 100 | 103 | 100 | 150 | 104 |  | 900 | 0 | 285 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 140 | 0 | 404 | 17 | 0 | 35 | 0 | 26 | 0 | 4 | 35 | 500 |  | 7392 | 3013 | 10405 | 4204 | 900 | 1679 | 2611 | 650 | 40 | 184 | 120 | 17 | 10405 | 99.6
14:00 | 0 | 0 | 150 | 115 | 200 | 42 | 0 | 0 | 344 |  | 0 | 225 | 280 | 7 | 80 | 40 | 0 | 0 | 135 | 0 | 7 | 16 | 64 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 33 | 33 | 0 | 39 | 0 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 17 | 18 | 85 | 50 | 20 | 8 | 0 | 0 | 100 | 315 | 175 | 177 | 8 | 96 | 26 | 53 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 33 | 21 | 132 | 152 | 0 | 14 | 0 | 58 | 30 | 50 | 47 | 0 | 180 | 60 | 83 | 0 | 219 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 285 | 37 | 25 | 191 | 7 | 149 | 5 | 100 | 0 | 30 | 420 | 85 | 68 | 0 | 5 | 180 | 35 | 0 | 100 | 104 | 100 | 150 | 104 |  | 901 | 0 | 260 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 21 | 10 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 138 | 0 | 398 | 17 | 0 | 35 | 0 | 27 | 0 | 3 | 35 | 520 |  | 7433 | 3024 | 10457 | 4065 | 901 | 1665 | 2772 | 669 | 39 | 201 | 132 | 13 | 0 | 99.61
15:00 | 0 | 0 | 150 | 115 | 200 | 42 | 0 | 0 | 344 |  | 0 | 225 | 290 | 7 | 80 | 40 | 0 | 0 | 97 | 0 | 7 | 16 | 150 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 33 | 48 | 0 | 39 | 0 | 115 | 0 | 15 | 204 | 0 | 139 | 0 |  | 0 | 0 | 17 | 40 | 90 | 50 | 20 | 6 | 0 | 0 | 100 | 315 | 185 | 184 | 8 | 86 | 29 | 51 | 0 | 51 | 0 | 25 | 52 | 21 | 8 | 33 | 21 | 128 | 153 | 0 | 14 | 1 | 57 | 30 | 50 | 43 | 0 | 182 | 65 | 83 | 0 | 219 | 18 | 0 | 10 | 300 | 24 | 8 | 30 | 300 | 35 | 50 | 190 | 25 | 145 | 16 | 100 | 36 | 30 | 417 | 85 | 84 | 0 | 3 | 180 | 37 | 0 | 100 | 110 | 100 | 0 | 104 |  | 900 | 0 | 240 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 40 | 0 | 26 | 80 | 0 | 0 | 0 | 17 | 0 | 42 | 0 | 0 | 43 | 51 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 137 | 0 | 4 | 0 | 134 | 0 | 405 | 17 | 20 | 35 | 0 | 27 | 0 | 2 | 35 | 520 |  | 7586 | 3187 | 10773 | 3864 | 900 | 1680 | 3056 | 670 | 39 | 414 | 128 | 22 | 0 | 99.62
16:00 | 0 | 0 | 150 | 115 | 200 | 42 | 0 | 0 | 347 |  | 0 | 225 | 285 | 7 | 80 | 40 | 0 | 0 | 97 | 0 | 7 | 16 | 150 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 33 | 25 | 0 | 42 | 0 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 17 | 10 | 90 | 50 | 20 | 4 | 0 | 0 | 100 | 315 | 170 | 177 | 8 | 96 | 29 | 52 | 0 | 51 | 0 | 25 | 52 | 21 | 0 | 33 | 21 | 128 | 154 | 0 | 14 | 1 | 60 | 30 | 50 | 45 | 0 | 182 | 65 | 83 | 0 | 219 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 300 | 0 | 25 | 191 | 0 | 132 | 9 | 100 | 61 | 30 | 419 | 85 | 84 | 0 | 2 | 162 | 44 | 0 | 45 | 110 | 100 | 0 | 104 |  | 901 | 0 | 250 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 8 | 0 | 27 | 64 | 0 | 0 | 0 | 50 | 10 | 90 | 0 | 0 | 43 | 8 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 136 | 0 | 81 | 0 | 132 | 0 | 306 | 17 | 0 | 35 | 0 | 27 | 0 | 1 | 35 | 520 |  | 7335 | 3153 | 10488 | 3857 | 901 | 1643 | 2729 | 670 | 42 | 505 | 128 | 13 | 0 | 99.63
17:00 | 0 | 0 | 150 | 115 | 200 | 42 | 0 | 0 | 297 |  | 0 | 225 | 280 | 26 | 80 | 40 | 0 | 0 | 54 | 0 | 7 | 7 | 98 | 15 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 33 | 25 | 0 | 41 | 0 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 17 | 10 | 91 | 19 | 20 | 11 | 0 | 0 | 100 | 275 | 170 | 177 | 8 | 86 | 29 | 50 | 0 | 51 | 0 | 25 | 52 | 21 | 0 | 33 | 21 | 124 | 154 | 0 | 14 | 0 | 60 | 30 | 11 | 10 | 0 | 182 | 45 | 20 | 0 | 213 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 300 | 0 | 0 | 182 | 0 | 141 | 4 | 100 | 34 | 30 | 421 | 45 | 32 | 0 | 0 | 162 | 48 | 0 | 34 | 110 | 100 | 0 | 104 |  | 901 | 0 | 265 | 0 | 32 | 120 | 0 | 0 | 2 | 1 | 8 | 0 | 27 | 48 | 0 | 0 | 0 | 50 | 42 | 96 | 0 | 0 | 43 | 8 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 136 | 0 | 85 | 0 | 131 | 0 | 291 | 17 | 0 | 35 | 0 | 36 | 0 | 0 | 35 | 480 |  | 6808 | 3082 | 9890 | 3754 | 901 | 1460 | 2482 | 630 | 41 | 494 | 124 | 4 | 0 | 99.64
18:00 | 0 | 0 | 150 | 115 | 200 | 42 | 0 | 0 | 243 |  | 0 | 225 | 300 | 63 | 80 | 40 | 0 | 0 | 115 | 0 | 7 | 7 | 150 | 15 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 33 | 43 | 0 | 41 | 0 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 98 | 10 | 97 | 37 | 20 | 8 | 0 | 0 | 100 | 270 | 195 | 186 | 8 | 95 | 29 | 53 | 0 | 51 | 0 | 40 | 52 | 21 | 8 | 33 | 21 | 156 | 154 | 0 | 17 | 0 | 60 | 30 | 22 | 20 | 0 | 180 | 65 | 88 | 0 | 176 | 18 | 0 | 10 | 250 | 24 | 8 | 100 | 300 | 140 | 78 | 191 | 83 | 149 | 0 | 100 | 91 | 30 | 417 | 50 | 103 | 0 | 0 | 88 | 54 | 0 | 100 | 110 | 100 | 0 | 104 |  | 901 | 0 | 270 | 0 | 93 | 160 | 0 | 0 | 9 | 10 | 40 | 0 | 37 | 80 | 0 | 0 | 0 | 50 | 42 | 96 | 0 | 0 | 43 | 31 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 142 | 0 | 89 | 15 | 130 | 0 | 385 | 17 | 100 | 35 | 0 | 72 | 0 | 0 | 108 | 450 |  | 7714 | 3598 | 11312 | 3851 | 901 | 1563 | 3502 | 600 | 41 | 698 | 156 | 0 | 0 | 99.65
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 150 | 115 | 200 | 42 | 0 | 0 | 350 |  | 0 | 225 | 290 | 92 | 80 | 40 | 0 | 0 | 153 | 0 | 7 | 7 | 150 | 66 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 20 | 33 | 33 | 51 | 0 | 42 | 0 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 102 | 37 | 97 | 50 | 20 | 16 | 0 | 0 | 100 | 315 | 170 | 176 | 8 | 90 | 29 | 55 | 0 | 51 | 0 | 42 | 52 | 21 | 8 | 33 | 21 | 156 | 156 | 0 | 17 | 0 | 60 | 30 | 50 | 47 | 0 | 180 | 66 | 88 | 0 | 216 | 18 | 0 | 10 | 290 | 24 | 0 | 130 | 300 | 153 | 74 | 200 | 98 | 149 | 0 | 100 | 200 | 30 | 421 | 96 | 103 | 0 | 0 | 143 | 54 | 0 | 100 | 113 | 100 | 0 | 104 |  | 901 | 0 | 245 | 0 | 115 | 160 | 0 | 0 | 9 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 42 | 96 | 0 | 0 | 43 | 52 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 89 | 100 | 131 | 0 | 400 | 53 | 120 | 35 | 0 | 89 | 0 | 0 | 109 | 570 |  | 8387 | 3930 | 12317 | 3885 | 901 | 1791 | 4128 | 720 | 42 | 694 | 156 | 0 | 0 | 99.66
19:30 | 0 | 0 | 150 | 115 | 200 | 42 | 0 | 0 | 350 |  | 0 | 225 | 300 | 92 | 96 | 40 | 0 | 0 | 194 | 0 | 7 | 7 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 20 | 33 | 33 | 51 | 0 | 42 | 0 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 85 | 60 | 97 | 50 | 20 | 22 | 0 | 0 | 100 | 315 | 180 | 181 | 8 | 95 | 29 | 55 | 0 | 51 | 0 | 42 | 52 | 21 | 8 | 33 | 21 | 156 | 156 | 0 | 17 | 0 | 60 | 30 | 50 | 47 | 0 | 180 | 65 | 88 | 0 | 219 | 18 | 0 | 10 | 300 | 24 | 0 | 50 | 300 | 106 | 64 | 200 | 99 | 149 | 0 | 100 | 200 | 30 | 420 | 105 | 103 | 0 | 0 | 143 | 54 | 0 | 100 | 113 | 100 | 0 | 104 |  | 901 | 0 | 233 | 0 | 115 | 160 | 0 | 0 | 9 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 42 | 96 | 0 | 0 | 43 | 52 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 133 | 0 | 89 | 100 | 129 | 0 | 413 | 53 | 50 | 35 | 0 | 89 | 0 | 0 | 109 | 590 |  | 8404 | 3872 | 12276 | 3926 | 901 | 1820 | 4014 | 740 | 42 | 677 | 156 | 0 | 0 | 0
20:00 | 0 | 0 | 150 | 115 | 200 | 42 | 0 | 0 | 348 |  | 0 | 225 | 300 | 95 | 96 | 40 | 0 | 0 | 195 | 0 | 7 | 7 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 33 | 51 | 0 | 44 | 0 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 85 | 60 | 97 | 50 | 20 | 25 | 0 | 0 | 100 | 315 | 185 | 183 | 8 | 96 | 29 | 55 | 0 | 51 | 0 | 42 | 52 | 21 | 8 | 33 | 21 | 156 | 156 | 0 | 17 | 0 | 60 | 30 | 50 | 47 | 0 | 180 | 65 | 88 | 0 | 219 | 18 | 0 | 10 | 280 | 24 | 0 | 50 | 300 | 104 | 62 | 200 | 99 | 149 | 0 | 100 | 200 | 30 | 420 | 105 | 103 | 0 | 0 | 143 | 54 | 0 | 100 | 112 | 100 | 0 | 104 |  | 901 | 0 | 220 | 0 | 115 | 150 | 0 | 0 | 13 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 42 | 96 | 0 | 0 | 47 | 52 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 131 | 0 | 89 | 100 | 128 | 0 | 358 | 53 | 50 | 35 | 0 | 90 | 0 | 0 | 109 | 590 |  | 8416 | 3800 | 12216 | 3941 | 901 | 1746 | 4013 | 740 | 44 | 675 | 156 | 0 | 0 | 99.67
21:00 | 0 | 0 | 150 | 115 | 200 | 42 | 0 | 0 | 352 |  | 0 | 225 | 300 | 100 | 96 | 40 | 0 | 0 | 195 | 0 | 7 | 7 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 33 | 51 | 0 | 45 | 0 | 115 | 0 | 25 | 203 | 0 | 139 | 0 |  | 0 | 0 | 99 | 60 | 97 | 50 | 20 | 32 | 0 | 0 | 100 | 315 | 170 | 177 | 8 | 96 | 29 | 57 | 0 | 51 | 0 | 42 | 52 | 21 | 8 | 33 | 21 | 156 | 157 | 0 | 17 | 0 | 60 | 30 | 50 | 47 | 0 | 181 | 65 | 88 | 0 | 219 | 18 | 0 | 10 | 290 | 24 | 0 | 0 | 300 | 105 | 30 | 200 | 101 | 149 | 0 | 100 | 200 | 30 | 425 | 105 | 103 | 0 | 0 | 143 | 54 | 0 | 100 | 113 | 100 | 0 | 104 |  | 901 | 0 | 220 | 0 | 115 | 150 | 0 | 0 | 16 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 42 | 96 | 0 | 0 | 43 | 52 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 89 | 100 | 128 | 0 | 300 | 53 | 50 | 35 | 0 | 91 | 0 | 0 | 109 | 590 |  | 8366 | 3741 | 12107 | 3925 | 901 | 1711 | 3941 | 740 | 45 | 688 | 156 | 0 | 0 | 99.68
22:00 | 0 | 0 | 150 | 115 | 200 | 42 | 0 | 0 | 351 |  | 0 | 225 | 300 | 100 | 96 | 40 | 0 | 0 | 195 | 0 | 7 | 7 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 33 | 51 | 0 | 45 | 0 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 87 | 40 | 97 | 50 | 20 | 40 | 0 | 0 | 100 | 315 | 180 | 181 | 8 | 95 | 29 | 57 | 0 | 51 | 0 | 42 | 52 | 21 | 8 | 33 | 21 | 156 | 156 | 0 | 17 | 0 | 60 | 30 | 50 | 47 | 0 | 183 | 65 | 88 | 0 | 219 | 18 | 0 | 10 | 295 | 24 | 2 | 0 | 300 | 108 | 21 | 200 | 57 | 149 | 0 | 100 | 200 | 30 | 422 | 55 | 103 | 0 | 0 | 143 | 54 | 0 | 100 | 113 | 100 | 0 | 104 |  | 901 | 0 | 220 | 0 | 115 | 150 | 0 | 0 | 19 | 0 | 40 | 0 | 39 | 110 | 0 | 0 | 0 | 50 | 42 | 96 | 0 | 0 | 43 | 52 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 90 | 100 | 128 | 0 | 332 | 53 | 0 | 35 | 0 | 90 | 0 | 0 | 109 | 590 |  | 8260 | 3727 | 11987 | 3939 | 901 | 1757 | 3770 | 740 | 45 | 679 | 156 | 0 | 0 | 0
23:00 | 0 | 0 | 150 | 115 | 200 | 42 | 0 | 0 | 350 |  | 0 | 225 | 310 | 100 | 92 | 48 | 0 | 0 | 160 | 0 | 20 | 7 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 33 | 51 | 0 | 45 | 0 | 115 | 0 | 0 | 217 | 0 | 145 | 0 |  | 0 | 0 | 90 | 40 | 97 | 50 | 20 | 41 | 0 | 0 | 100 | 350 | 210 | 197 | 8 | 94 | 29 | 56 | 0 | 51 | 0 | 42 | 52 | 21 | 8 | 33 | 21 | 156 | 156 | 0 | 17 | 0 | 60 | 30 | 50 | 47 | 0 | 182 | 65 | 88 | 0 | 219 | 18 | 0 | 10 | 295 | 24 | 8 | 0 | 300 | 24 | 16 | 200 | 0 | 149 | 0 | 100 | 200 | 30 | 421 | 55 | 103 | 0 | 0 | 143 | 54 | 0 | 100 | 113 | 100 | 0 | 104 |  | 900 | 0 | 220 | 0 | 115 | 150 | 0 | 0 | 23 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 42 | 96 | 0 | 0 | 43 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 90 | 100 | 125 | 0 | 331 | 53 | 0 | 35 | 0 | 92 | 0 | 0 | 109 | 590 |  | 8186 | 3726 | 11912 | 4004 | 900 | 1753 | 3628 | 740 | 45 | 686 | 156 | 0 | 0 | 0
24:00 | 0 | 0 | 150 | 115 | 200 | 42 | 0 | 0 | 353 |  | 0 | 225 | 300 | 100 | 80 | 40 | 0 | 0 | 160 | 0 | 32 | 7 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 51 | 0 | 45 | 0 | 115 | 0 | 3 | 204 | 0 | 139 | 0 |  | 0 | 0 | 102 | 40 | 98 | 50 | 20 | 42 | 0 | 0 | 100 | 315 | 170 | 176 | 8 | 84 | 29 | 53 | 0 | 51 | 0 | 42 | 52 | 21 | 8 | 33 | 21 | 154 | 156 | 0 | 17 | 0 | 58 | 30 | 50 | 47 | 0 | 182 | 67 | 88 | 0 | 218 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 300 | 23 | 31 | 193 | 0 | 149 | 0 | 100 | 200 | 30 | 424 | 55 | 103 | 0 | 0 | 143 | 37 | 0 | 100 | 113 | 100 | 0 | 104 |  | 900 | 0 | 220 | 0 | 115 | 150 | 0 | 0 | 23 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 42 | 96 | 0 | 0 | 43 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 90 | 100 | 125 | 0 | 303 | 36 | 0 | 35 | 0 | 74 | 0 | 0 | 54 | 590 |  | 8057 | 3608 | 11665 | 3883 | 900 | 1731 | 3514 | 740 | 45 | 698 | 154 | 0 | 0 | 0
KWH | 0 | 0 | 3260000 | 2772000 | 4793936 | 989000 | 0 | 0 | 7922000 |  | 0 | 4664800 | 6936465 | 816960 | 2038464 | 949606 | 0 | 0 | 3866000 | 0 | 238080 | 312624 | 2557440 | 977766 | 0 | 0 | 0 | 1233360 | 1257427 | 1257888 | 443556 | 600000 | 476280 | 816800 | 834800 | 700356 | 0 | 964080 | 0 | 2500000 | 0 | 283219 | 4892462 | 0 | 3142127 | 0 |  | 0 | 0 | 1020172 | 376200 | 1980480 | 946560 | 469344 | 537600 | 0 | 0 | 2143852 | 7819500 | 3201200 | 4443000 | 200727 | 2170550 | 635328 | 1300800 | 0 | 1223513 | 0 | 364360 | 1156968 | 504360 | 173880 | 817100 | 511910 | 3254400 | 3649880 | 0 | 333072 | 11750 | 1415000 | 719520 | 1133400 | 1070928 | 0 | 4156000 | 1233792 | 1918080 | 0 | 5163290 | 425000 | 0 | 240660 | 7070700 | 564792 | 96000 | 289152 | 6548725 | 731911 | 450974 | 4384800 | 463081 | 3537220 | 100575 | 2283840 | 1663680 | 767781 | 10104000 | 1738800 | 1883832 | 0 | 32521 | 3628145 | 899936 | 0 | 1843380 | 2572080 | 2413440 | 1315500 | 2582400 |  | 21801454 | 0 | 5837184 | 0 | 2063040 | 3292800 | 0 | 0 | 144960 | 7808 | 491250 | 0 | 741946 | 1627200 | 0 | 0 | 0 | 493280 | 353507 | 1255376 | 0 | 0 | 400200 | 822720 | 0 | 503280 | 234720 | 237834 | 0 | 0 | 3689400 | 0 | 0 | 0 | 0 | 3771609 | 0 | 1919355 | 789120 | 3544164 | 0 | 9041090 | 616320 | 327093 | 934464 | 0 | 1078080 | 0 | 28905 | 1358400 | 13914200 |  | 177186937 | 81320759 | 258507696 | 93854622 | 21801454 | 40712599 | 70253287 | 17603600 | 964080 | 9889903 | 3254400 | 173751 | 0
Fuel Cost | 0 | 0 | 4759600 | 4074840 | 5321268.96 | 1305480 | 0 | 0 | 8159660 |  | 0 | 5084632 | 7699476.15 | 6200726.4 | 14045016.96 | 8033666.76 | 0 | 0 | 6688180 | 0 | 1792742.4 | 2851130.88 | 25165209.6 | 9015002.52 | 0 | 0 | 0 | 9003528 | 9719910.71 | 12402775.68 | 332667 | 450000 | 0 | 0 | 0 | 6772442.52 | 0 | 260301.6 | 0 | 4525000 | 0 | 2631104.51 | 5332783.58 | 0 | 5341615.9 | 0 |  | 0 | 0 | 9895668.4 | 3592710 | 17230176 | 7496755.2 | 591373.44 | 1596672 | 0 | 0 | 3151462.44 | 5786430 | 3201200 | 4087560 | 258937.83 | 2496132.5 | 717920.64 | 1821120 | 0 | 2092207.23 | 0 | 3680036 | 11049044.4 | 640537.2 | 130410 | 1429925 | 383932.5 | 24408000 | 3868872.8 | 0 | 423001.44 | 187295 | 2320600 | 1151232 | 2017452 | 1670647.68 | 0 | 4322240 | 2430570.24 | 3663532.8 | 0 | 8932491.7 | 930750 | 0 | 490946.4 | 7141407 | 423594 | 72960 | 4918475.52 | 49508361 | 12427848.78 | 7540285.28 | 22800960 | 7742714.32 | 34806244.8 | 1175721.75 | 18613296 | 18050928 | 5412856.05 | 9396720 | 15857856 | 17802212.4 | 0 | 0 | 27428776.2 | 7838442.56 | 0 | 18396932.4 | 22042725.6 | 16073510.4 | 0 | 0 |  | 125576375.04 | 0 | 6129043.2 | 0 | 16215494.4 | 45638208 | 0 | 0 | 1520630.4 | 81827.84 | 5118825 | 0 | 1150016.3 | 15881472 | 0 | 0 | 0 | 4853875.2 | 3591631.12 | 11110077.6 | 0 | 0 | 3877938 | 7972156.8 | 0 | 966297.6 | 363816 | 180040.338 | 0 | 0 | 19996548 | 0 | 0 | 0 | 0 | 4978523.88 | 0 | 2879032.5 | 13422931.2 | 4146671.88 | 0 | 8950679.1 | 6434380.8 | 5563851.93 | 8868063.36 | 0 | 8365900.8 | 0 | 319400.25 | 10038576 | 61083338 |  | 630589433.03 | 405275622.538 | 1035865055.568 | 109150150.638 | 125576375.04 | 49612536.44 | 534680286.69 | 81079886 | 260301.6 | 109415102.16 | 24408000 | 1682417 | 0
Yesterday Day Peak | 0 | 0 | 150 | 115 | 200 | 42 | 0 | 0 | 344 |  | 0 | 225 | 300 | 7 | 80 | 34 | 0 | 0 | 180 | 0 | 7 | 16 | 64 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 33 | 33 | 0 | 44 | 0 | 115 | 0 | 0 | 209 | 0 | 107 | 0 |  | 0 | 0 | 0 | 0 | 62 | 19 | 20 | 2 | 0 | 0 | 80 | 345 | 195 | 199 | 8 | 96 | 26 | 50 | 0 | 43 | 0 | 0 | 52 | 22 | 8 | 33 | 21 | 124 | 153 | 0 | 14 | 1 | 57 | 30 | 50 | 47 | 0 | 181 | 65 | 83 | 0 | 198 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 230 | 0 | 25 | 160 | 0 | 149 | 13 | 100 | 0 | 30 | 415 | 45 | 68 | 0 | 4 | 141 | 18 | 0 | 34 | 113 | 100 | 199 | 104 |  | 900 | 0 | 315 | 0 | 49 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 164 | 0 | 90 | 0 | 140 | 0 | 388 | 17 | 0 | 35 | 0 | 27 | 0 | 5 | 35 | 490 |  | 10180 | DayPeak
Yesterday Evening Peak | 0 | 0 | 150 | 115 | 200 | 42 | 0 | 0 | 350 | 0 | 0 | 225 | 290 | 92 | 80 | 40 | 0 | 0 | 153 | 0 | 7 | 7 | 150 | 66 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 20 | 33 | 33 | 51 | 0 | 42 | 0 | 115 | 0 | 25 | 204 | 0 | 139 | 0 | 0 | 0 | 0 | 102 | 37 | 97 | 50 | 20 | 16 | 0 | 0 | 100 | 315 | 170 | 176 | 8 | 90 | 29 | 55 | 0 | 51 | 0 | 42 | 52 | 21 | 8 | 33 | 21 | 156 | 156 | 0 | 17 | 0 | 60 | 30 | 50 | 47 | 0 | 180 | 66 | 88 | 0 | 216 | 18 | 0 | 10 | 290 | 24 | 0 | 130 | 300 | 153 | 74 | 200 | 98 | 149 | 0 | 100 | 200 | 30 | 421 | 96 | 103 | 0 | 0 | 143 | 54 | 0 | 100 | 113 | 100 | 0 | 104 |  | 901 | 0 | 245 | 0 | 115 | 160 | 0 | 0 | 9 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 42 | 96 | 0 | 0 | 43 | 52 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 89 | 100 | 131 | 0 | 400 | 53 | 120 | 35 | 0 | 89 | 0 | 0 | 109 | 570 |  | 12317 | EvPeak
Forecast for Evening | 0 | 0 | 150 | 115 | 200 | 42 | 0 | 0 | 360 | 0 | 0 | 450 | 305 | 7 | 100 | 55 | 0 | 0 | 200 | 0 | 100 | 102 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 44 | 0 | 120 | 0 | 25 | 221 | 0 | 140 | 0 | 0 | 0 |  | 100 | 100 | 100 | 50 | 21 | 25 | 0 | 0 | 100 | 360 | 250 | 225 | 8 | 90 | 30 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 8 | 33 | 21 | 173 | 160 | 0 | 14 | 0 | 60 | 30 | 51 | 44 | 0 | 200 | 65 | 86 | 0 | 220 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 100 | 100 | 0 | 300 | 54 | 110 | 100 | 113 | 100 | 0 | 104 |  | 912 | 16 | 270 | 0 | 115 | 225 | 0 | 0 | 30 | 60 | 40 | 0 | 33 | 110 | 0 | 0 | 0 | 50 | 42 | 100 | 0 | 0 | 50 | 52 | 34 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 | 0 | 90 | 100 | 220 | 0 | 414 | 53 | 200 | 35 | 100 | 100 | 0 | 0 | 90 | 620
Forecast for Day | 0 | 0 | 150 | 115 | 200 | 42 | 0 | 0 | 360 | 0 | 0 | 225 | 305 | 7 | 100 | 55 | 0 | 0 | 200 | 0 | 100 | 7 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 44 | 0 | 120 | 0 | 25 | 221 | 0 | 140 | 0 | 0 | 0 |  | 100 | 100 | 100 | 50 | 21 | 10 | 0 | 0 | 100 | 360 | 250 | 225 | 8 | 90 | 30 | 55 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 33 | 21 | 162 | 160 | 0 | 14 | 1.6 | 60 | 30 | 51 | 44 | 0 | 200 | 65 | 86 | 0 | 220 | 18 | 0 | 10 | 341 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 200 | 150 | 400 | 115 | 100 | 100 | 5 | 300 | 54 | 110 | 100 | 113 | 100 | 0 | 104 |  | 912 | 0 | 270 | 0 | 115 | 225 | 0 | 0 | 0 | 0 | 40 | 0 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 50 | 52 | 0 | 22 | 10 | 10 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 |  | 80 | 50 | 220 | 0 | 414 | 53 | 100 | 35 | 100 | 100 | 0 | 8 | 90 | 620
Generation at 08:00(Today) | 0 | 0 | 150 | 115 | 200 | 41 | 0 | 0 | 302 | 0 | 0 | 225 | 305 |  | 96 | 40 | 0 | 0 | 130 | 0 | 60 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 19 | 25 | 21 | 33 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 205 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 20 | 9 | 0 | 0 | 100 | 330 | 195 | 192 | 8 | 96 | 29 | 56 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 112 | 157 | 0 | 17 | 0 | 58 | 30 | 50 | 47 | 0 | 180 | 65 | 85 | 0 | 218 | 0 | 0 | 10 | 300 | 24 | 8 | 0 | 145 | 0 | 0 | 127 | 0 | 131 | 13 | 40 | 0 | 7 | 425 | 8 | 0 | 0 | 1 | 143 | 36 | 0 | 0 | 57 | 100 | 0 | 83 | 0 | 901 | 0 | 270 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 130 | 0 | 86 | 0 | 151 | 0 | 331 | 18 | 0 | 35 | 0 | 29 | 0 | 2 | 36 | 500 | 0
199
| Minimum Generation |  | 8930 | 8:00
| Highest Generation |  | 12317 | 19:00
| Day Peak Generation |  | 10180 | 12:00
| Evening Peak Generation |  | 12317 | 19:00
| HVDC Max Flow |  | 926 | 7:00
| HVDC EvPeak Flow |  | 901 | 19:00
| Load factor L.F |  | 87.45%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-10-05
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-10-04 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10180 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 8982 | MW
Evening Peak Generation : |  | 12317 | MW Hour : | 19:00 | Available Max Generation : |  | 14573 | MW
E.P. Demand (at gen end) : |  | 12317 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 12700 | MW
Maximum Generation : |  | 12317 | MW Hour : | 19:00 | Reserve(Generation end) |  | 1873 | MW
Total Gen. (MKWH) : |  | 258.5077 | System Load Factor : | 87.45% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -230 | MW at | 21:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-10-05
Actual : | 99.99 | Ft.(MSL) , | Rule curve : | 106.36 | Ft.( MSL )
Gas Consumed : | Total = | 1171.58 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 158762687.078
: |  | Coal : | 81079886 | Oil : | 644095388.85 | Total : | 883937961.928
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4533.2742 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1545.8078 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1385.7487 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1252.4093 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1131.6361 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 913.201 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 505.1561 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 234.9802 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 704.3321 |  |  | 0 | 0%
Total | 0 |  | 12206.5456 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Baghabari-71 MW,100 MW
3) Ghorasal Unit-1,2,3,
4) Ashuganj unit-3,4
5) Kaptai-2,4,5
6) Raozan #1,2
7) Siddirganj-335 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Baghabari 230/132 kV T-2 transformer was under shut down from 08:05 to 13:32 for C/m.
b) Rangpur 132/33 kV T-1 transformer was under shut down from 08:04 to 17:10 for A/M.
c) Ashuganj 450 MW south GT was synchronized at 08:33 after maintenance work.
d) Bakulia 132/33 kV T-3 transformer tripped at 09:52 due to 33 kV feeder fault showing Diff. relay at 132 kV |  |  |  |  | About 07 MW power interruption occurred under Bakulia S/S area
side and O/C relay at 33 kV side and was switched on at 11:50. |  |  |  |  | from 09:52 to 11:50.
e) Mirpur-Uttara(3rd) 132 kV Ckt was shut down at 07:48 for A/M and still under maintenance.
f) Kallyanpur 132/33 kV GT-2 transformer was shut down at 09:32 for C/M.
g) Polashbari 132/33 kv T-1 transformer was under shut down from 09:10 to 10:30 for R/H maintenance |  |  |  |  | About 22 MW power interruption occurred under Polashbari S/S area
work at 33 kV PBS feeder. |  |  |  |  | from 09:10 to 10:30.
h) Madaripur 132/33 kV T-3 transformer tripped at 09:45 due to 33 kV feeder fault and was switched on |  |  |  |  | About 10 MW power interruption occurred under Madaripur S/S area
at 12:00. |  |  |  |  | from 09:45 to 12:00.
i) Barishal(N)-Bhola 230 kV Ckt-1 tripped at 12:43 showing Dist. L3,Z1,15.07 Km at Barishal(N) end and Dist.
65.5 Km at Bhola end and was switched on at 13:29. At the same time Bhola Agreeko 95 MW also tripped
and was synchronized at 14:59.
j) Siddhirganj-Haripur 230 kV Ckt-2 was under shut down from 14:52 to 16:47 for R/H maintenance at
Siddhirganj end.
k) Siddhirganj GT-1 was shut down at 14:10 for checking of vibration sensor and was synchronized at 17:43.
l) HVDC Bheramara Aux. transformer tripped at 17:16 showing PRD and was switched on at 19:07.
m) GK. Project S/S 132/33 kV T-1 and T-2 transformers tripped at 16:27 due to 33 kV feeder fault and T-1 |  |  |  |  | About 36 MW power interruption occurred under GK. Project S/S area
& T-2 were switched on at 17:54 and 17:53 respectively. |  |  |  |  | from 16:27 to 17:54.
n) Raozan unit-1 was shut down at 00:28(05/10/20200 due to problem with feed water pump.
o) Barapukuria 132/33 kV T-3 transformer tripped at 01:32(05/10/20200 from both sides showing O/C,E/F
relay at 3 kV side and L/O at 132 kV side and was switched on at 01:42.
p) Fenchuganj S/S-Sylhet 132 kV Ckt tripped at 03:05(05/10/2020) from Fenchuganj S/S end showing Dist.
3-phase,Gen. trip and was switched on at 03:34. At the same time Sylhet 20 MW,10 MW and Fenchuganj
Energy Prima also tripped.
q) Bhola Agreeko 95 MW tripped at 03:35(05/10/2020) due to gas shortage and was synchronized at 04:28.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-10-04 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 150 | 3260000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 115 | 2772000 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 4793936 | Machin problem.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 42 | 989000 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 350 | 7922000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4664800 | GT-2 Under maint.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 92 | 816960 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 290 | 6936465
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 80 | 2038464 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 40 | 949606 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 66 | 977766 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 443556 | machine tripped at 18:47.
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 153 | 3866000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 7 | 238080 | Fuel Shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under Maintenance
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 7 | 312624 | Fuel Shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel Shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1233360
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 2557440
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1257427
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1257888
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 45 | 1076280 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 816800
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 834800
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 700356
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 6548725
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 153 | 731911 | Low demand.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 74 | 450974 | Engine problem
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 98 | 463081
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3537220
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 103 | 1883832
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2582400
| Dhaka area Total |  |  |  | 5895 | 3274 | 66913751
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 115 | 2500000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 283219
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 100575
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 946560
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 42 | 964080 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4892462
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 139 | 3142127
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 1020172
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 37 | 376200 | High voltage
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2283840
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 469344
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 16 | 537600
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 97 | 1980480 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 32521
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 143 | 3628145 | transformer O/L.
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 899936
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2413440
| Chattogram area Total |  |  |  | 2266 | 1244 | 26470701
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 100 | 2143852 | Gas shortage
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 176 | 4443000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 315 | 7819500 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 170 | 3201200 | ST under maint.
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 635328 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 55 | 1300800
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1223513
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 30 | 767781 | R/H at APSCL
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 42 | 364360
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2170550
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 1663680
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 504360
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 173880 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 156 | 3254400
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 817100
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 1156968
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 511910 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 130 | 289152 | Low demand.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 100 | 1843380 | Engine problem
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 2572080
| Cumilla Area Total |  |  |  | 2980 | 1900 | 37057521
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 156 | 3649880 | Machine problem & Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 333072 | Engine problem
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 0 | 0 | Man power problem due to corona effected.
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11750
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 4384800 | Engine problem
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 96 | 1738800 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 469 | 10118302
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1415000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 719520 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 180 | 4156000 | Gas shortage & ST under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1133400
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 47 | 1070928
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 96000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 66 | 1233792 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 88 | 1918080
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 216 | 5163290
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 425000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 564792
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7070700 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 421 | 10104000
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 240660
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 1315500 | On test
| Sylhet Area Total |  |  |  | 1988 | 1500 | 36626662
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 901 | 21801454
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 2063040
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 9 | 144960 | Engine problem
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 160 | 3292800
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 7808 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 245 | 5837184 | Gas shortage.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 491250
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 789120
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 616320 | Engine problem
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Line O/L.
| Khulna Area Total |  |  |  | 2284 | 1623 | 35043936
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1627200
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 38 | 741946
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 89 | 1919355 | Engine problem
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 570 | 13914200
| Barisal Area Total |  |  |  | 1054 | 807 | 18202701
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 493280
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 42 | 353507
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel Shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel Shortage
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 43 | 400200
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas Shortage
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 140 | 3771609 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 131 | 3544164 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 400 | 9041090 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 503280
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 10 | 234720
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 237834
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 822720
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 96 | 1255376 | Engine problem
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 120 | 327093 | Low demand.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 35 | 934464 | Engine problem
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 1358400 | Engine problem
| Rajshahi Area Total |  |  |  | 2183 | 1261 | 23277737
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3689400 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 89 | 1078080 | Engine problem
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 28905
| Rangpur Area Total |  |  |  | 605 | 239 | 4796385
| Total |  |  |  | 19892 | 12317 | 258507696
| Eastern Grid Total |  |  |  | 13766 | 8387 | 177186937
| Western Grid Total |  |  |  | 6126 | 3930 | 81320759
| National Grid Total |  |  |  | 19892 | 12317 | 258507696
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-10-04
| (a) ENTIRE EASTERN GRID : |  | 8021 | MW | (b) ENTIRE WESTERN GRID : |  | 3809 | MW
| i) Dhaka area |  | 4241 | MW | i) Khulna area |  | 1498 | MW
| ii) Chittagong area |  | 1200 | MW | ii) Rajshahi area |  | 1239 | MW
| iii) Comilla area |  | 1150 | MW | iii) Barisal area |  | 332 | MW
| iv) Mymensingh area |  | 934 | MW | iv) Rangpur area |  | 740 | MW
| v) Sylhet area |  | 496 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11830 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 124 | 9:00 | Sherpur | 106 | 21:00 | Jhenida | 110 | 19:00
| Munsiganj | 126 | 0:00 | Srimongal | 59 | 18:30 | Bottail | 122 | 18:30
| Sonargaon | 76 | 19:30 | Shahjibazar | 114 | 24:00 | G.K Project | 55 | 21:00
| Shyampur | 198 | 1:00 | Fenchuganj | 46 | 18:30 | Faridpur | 198 | 0.875
| Bhulta | 207 | 22:00 | Kulawara | 43 | 18:00 | Madaripur | 103 | 0.875
| Madanganj | 57 | 1:00 | Sylhet | 140 | 19:30 | Sariatpur | 66 | 22:00
| Shitalakhya | 115 | 15:00 | Chatak | 29 | 19:00 | Gopalganj | 90 | 21:00
| Rahim steel | 16 | 18:30 | Sunamganj | 46 | 20:00 | Bagerhat | 100 | 18:30
| Matuail | 84 | 9:00 | Biani Bazar | 52 | 20:00 | Mongla | 36 | 9:00
| Ghorasal | 82 | 21:00 | Comilla (S) | 156 | 18:00 | Satkhira | 107 | 0.875
| Narsingdi | 171 | 20:00 | Comilla(N) | 123 | 18:00 | Gallamari | 44 | 23:00
| Haripur (SBU) | 113 | 11:00 | Chandpur | 107 | 20:00 | Magura | 52 | 0.77083
| Ullon | 61 | 18:00 | Feni | 125 | 18:30 | Norail | 40 | 19:30
| Hasnabad | 205 | 18:00 | Chowmuhani | 182 | 18:30 | Chuadanga | 89 | 19:30
| Magbazar | 105 | 11:00 | Ashuganj | 61 | 23:00 | Barisal(N) | 44 | 0.83333
| Maniknagar | 100 | 16:00 | Daudkandi | 146 | 19:30 | Barisal (S) | 92 | 0.75
| Bangabhaban | 36 | 11:00 | B.Baria | 156 | 22:00 | Patuakhali | 125 | 0.91667
| Narinda | 90 | 18:00 | Ramganj | 114 | 22:00 | Bhandaria | 52 | 0.83333
| Dhanmondi | 203 | 13:00 | Chaddagram | 36 | 18:30 | Borhan Uddin | 45 | 20:00
| Lalbag | 136 | 19:30 | PHP | 11 | 24:00 | Ishurdi | 66 | 19:00
| Madartek | 72 | 22:00 | Madunaghat | 55 | 18:00 | Ruppur Paromanobik | 3 | 16:00
| Dhaka University |  |  | Hathazari | 102 | 0.77083 | Natore | 122 | 21:00
| Fatullah | 40 | 0.625 | Khulshi | 180 | 0.041667 | Bogra | 166 | 21:00
| Mirpur | 107 | 18:00 | Halishahar | 149 | 0.625 | Noagaon | 113 | 21:00
| Kalyanpur | 92 | 18:00 | Baraulia | 155 | 0.95833 | Rajshahi | 147 | 20:00
| Gulshan | 140 | 13:00 | Sikalbaha | 26 | 0.75 | Rajshahi New | 10 | 21:00
| Uttara | 95 | 13:00 | Dohazari | 80 | 0.041667 | C.Nawabganj | 68 | 19:00
| Uttara New | 34 | 18:30 | Cox'sbazar | 106 | 0.77083 | Amnura | 40 | 21:00
| Kamrangirchar | 99 | 19:00 | Chandraghona | 30 | 0.75 | Pabna | 124 | 20:00
| Savar | 144 | 18:30 | Kaptai | 4.6 | 0.75 | Shahjadpur | 109 | 21:00
| Bhasantec | 154 | 13:00 | A. Khaer Stl. | 10 | 0.625 | Serajganj | 106 | 19:00
| Agargaon | 78 | 13:00 | Bakulia | 111 | 0.58333 | Niyamatpur | 52 | 21:00
| Satmosjid | 103 | 13:00 | Julda | 26 | 0.45833 | Joypurhat | 54 | 19:00
| Tongi | 110 | 0.66667 | TK chemical | 29.3 | 0.83333 | Sherpur(Bogura) | 47 | 21:00
| Kabirpur | 214 | 14:00 | Modern Steel | 16 | 0.083333 | Mohastangor | 46 | 20:00
| Basundhara | 142 | 13:00 | Shahmirpur | 28 | 0.041667 | Rangpur | 147 | 18:30
| Manikganj | 72 | 0.875 | Khagrachhari | 26 | 0.083333 | Lalmonirhat | 54 | 18:00
| Joydevpur | 150 | 18:00 | Matarbari | 39.5 | 0.8125 | Saidpur | 95 | 20:00
| New Tongi | 110 | 15:00 | Baroiar Hat | 48 | 0.75 | Purbasadipur | 98 | 19:00
| Korda | 242 | 19:00 | Rangamati | 12 | 0.75 | Thakurgaon | 75 | 19:30
| Dhamrai | 94 | 19:00 | Abul Khair 230 | 62 | 0.54167 | Palashbari | 120 | 19:00
| Rajendrapur | 110 | 19:00 | BSRM | 153 | 0.54167 | Barapukuria | 45 | 19:00
| Valuka | 138 | 18:30 | GPH Ispat | 74 | 0.875 | Panchagar | 49 | 20:00
| Tangail | 179 | 19:30 | Goalpara | 28 | 0.54167 | Joldhaka | 24 | 20:00
| Mymensing | 164 | 18:00 | Central s/s | 87 | 19:00 | Kurigram | 53 | 18:30
| Kishorganj | 146 | 21:00 | Noapara | 54 | 18:30
| Netrokona | 111 | 23:00 | Jessore | 118 | 18:30
| Jamalpur | 138 | 22:00 | Benapol | 40 | 19:00
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-10-04 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 397 | 6:00 | 385 | 12:00 | Kaliakoir | 377 | 0.20833 | 360 | 0.45833
| Bheramara | 397 | 6:00 | 390 | 19:30 | Bhulta | 390 | 0.20833 | 372 | 0.5
| Ashuganj(N) | 394 | 4:00 | 379 | 12:00 | Gopalganj | 412 | 0.45833 | 391 | 0.8125
| Payra | 414 | 2:00 | 403 | 19:30
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 238 | 1:00 | 235 | 8:00 | Comilla (N) | 235 | 21:00 | 226 | 12:00
| Ishurdi | 232 | 6:00 | 224 | 21:00 | Hathazari | 227 | 21:00 | 221 | 12:00
| Ashuganj | 235 | 1:00 | 228 | 12:00 | Megnaghat | 232 | 6:00 | 220 | 11:00
| Serajganj | 230 | 18:00 | 225 | 1:00 | Fenchuganj | 236 | 4:00 | 230 | 13:00
| Baghabari | 240 | 16:00 | 233 | 19:30 | Siddhirganj | 230 | 3:00 | 218 | 12:00
| Barapukuria | 237 | 17:00 | 228 | 19:00 | Maniknagar | 228 | 5:00 | 215 | 12:00
| Bogra | 225 | 18:00 | 212 | 20:00 | Agargaon | 228 | 5:00 | 213 | 12:00
| Rajshahi | 226 | 17:00 | 215 | 12:00 | Barisal | 249 | 4:00 | 214 | 13:00
| Khulna South | 233 | 6:00 | 223 | 20:00 | AKSML | 224 | 2:00 | 217 | 12:00
| Rampura | 229 | 5:00 | 219 | 12:00 | BSRM | 226 | 1:00 | 217 | 12:00
| Haripur | 227 | 20:00 | 216 | 12:00 | Bibiyana | 236 | 4:00 | 229 | 12:00
| Hasnabad | 230 | 21:00 | 215 | 12:00 | Bhulta | 231 | 19:00 | 218 | 17:00
| Shyampur | 226 | 2:00 | 214 | 12:00 | Ashuganj (S) | 234 | 23:00 | 228 | 12:00
| Aminbazar | 228 | 4:00 | 215 | 12:00 | Kaliakoir | 231 | 4:00 | 218 | 12:00
| Tongi | 228 | 21:00 | 218 | 9:00 | GPH | 224 | 4:00 | 217 | 8:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 130 | 19:00 | 122 | 12:00 | Hathazari | 136 | 0.875 | 131 | 0.5
| Munsiganj | 133 | 19:00 | 123 | 16:00 | Khulshi | 134 | 0.875 | 128 | 0.5
| Sonargaon | 132 | 18:30 | 123 | 12:00 | Halishahar | 135 | 0.041667 | 129 | 0.5
| Shyampur | 133 | 3:00 | 125 | 11:00 | Baraulia | 135 | 0.83333 | 130 | 0.5
| Bhulta | 122 | 18:00 | 116 | 12:00 | Sikalbaha | 137 | 21:00 | 131 | 0.5
| Madanganj | 132 | 18:30 | 123 | 12:00 | Dohazari | 132 | 17:00 | 123 | 0.41667
| Shitalakhya | 133 | 19:00 | 123 | 16:00 | Cox'sbazar | 125 | 0.70833 | 117 | 0.83333
| Rahim steal | 131 | 20:00 | 122 | 12:00 | Chandraghona | 135 | 0.041667 | 130 | 0.5
| Matuail | 130 | 19:00 | 122 | 12:00 | Kaptai | 134 | 1:00 | 131 | 0.375
| Ghorasal | 139 | 19:30 | 135 | 12:00 | A. Khaer Stl. | 134 | 0.875 | 129 | 12:00
| Narsinghdi | 124 | 5:00 | 117 | 11:00 | Bakulia | 135 | 0.083333 | 130 | 0.5
| Haripur (SBU) | 131 | 6:00 | 122 | 12:00 | Julda | 136 | 0.041667 | 131 | 0.5
| Ullon | 135 | 5:00 | 125 | 13:00 | TK Chemical | 136 | 0 | 130 | 11:00
| Hasnabad | 137 | 1:00 | 127 | 11:00 | Modern Steel | 135 | 0.041667 | 130 | 0.5
| Magbazar | 135 | 4:00 | 126 | 12:00 | Shahmirpur | 135 | 0.20833 | 131 | 0.45833
| Maniknagar | 133 | 4:00 | 118 | 12:00 | Khagrachhari | 134 | 0.083333 | 129 | 0.54167
| Bangabhaban | 133 | 4:00 | 118 | 12:00 | Matarbari | 128 | 0.70833 | 120 | 0.75
| Narinda | 133 | 4:00 | 118 | 12:00 | Baroiar Hat | 134 | 0.375 | 129 | 0.41667
| Dhanmondi | 135 | 5:00 | 125 | 13:00 | Rangamati | 134 | 0.041667 | 130 | 12:00
| Lalbag | 138 | 2:00 | 123 | 19:30 | Goalpara S/S | 135 | 6:00 | 129 | 18:30
| Madartek | 135 | 2:00 | 126 | 12:00 | Khulna Central S/S | 134 | 0.375 | 129 | 18:30
| Dhaka University |  |  |  |  | Noapara | 134 | 18:00 | 127 | 19:30
| Fatuiiah | 133 | 0.16667 | 125 | 12:00 | Jessore | 129 | 6:00 | 120 | 18:30
| Mirpur | 136 | 3:00 | 126 | 12:00 | Benapol | 130 | 8:00 | 120 | 18:30
| Kalyanpur | 137 | 2:00 | 128 | 12:00 | Jhenida | 127 | 0.375 | 112 | 20:00
| Gulshan | 134 | 1:00 | 125 | 12:00 | Bottail | 132 | 8:00 | 124 | 19:30
| Uttara | 134 | 4:00 | 123 | 17:00 | G.K Project | 139 | 0.33333 | 133 | 20:00
| Uttara New | 135 | 4:00 | 125 | 10:00 | Faridpur | 131 | 5:00 | 123 | 19:30
| Kamrangirchar | 137 | 20:00 | 122 | 12:00 | Madaripur | 137 | 0.375 | 129 | 20:00
| Savar | 137 | 4:00 | 126 | 12:00 | Shariyatpur S/S | 136 | 0.20833 | 126 | 19:30
| Bhasantec | 137 | 1:00 | 127 | 12:00 | Gopalganj | 137 | 5:00 | 125 | 19:30
| Agargaon | 138 | 3:00 | 127 | 12:00 | Bagerhat | 132 | 6:00 | 120 | 18:30
| Satmosjid | 138 | 4:00 | 127 | 12:00 | Mongla | 129 | 0.25 | 119 | 20:00
| Tongi | 136 | 0.16667 | 127 | 11:00 | Satkhira | 133 | 0.375 | 124 | 20:00
| Kabirpur | 133 | 6:00 | 126 | 10:00 | Gallamari | 134 | 6:00 | 129 | 18:30
| Basundhara | 135 | 1:00 | 126 | 13:00 | Magura | 126 | 8:00 | 110 | 18:30
| Manikganj | 139 | 24:00 | 131 | 17:00 | Norail | 127 | 0.375 | 109 | 19:30
| Joydevpur | 141 | 21:00 | 135 | 11:00 | Chuadanga | 124 | 8:00 | 102 | 19:30
| New Tongi | 135 | 1904-01-02 | 125 | 12:00 | Barisal(N) | 141 | 5:00 | 122 | 13:00
| Kodda | 137 | 24:00 | 124 | 0.41667 | Barisal (S) | 140 | 0.125 | 121 | 13:00
| Dhamrai | 133 | 5:00 | 124 | 12:00 | Patuakhali(S) | 135 | 0.375 | 118 | 13:00
| Rajendrapur | 135 | 2:00 | 122 | 17:00 | Bhandaria | 134 | 6:00 | 115 | 18:30
| Valuka | 124 | 6:00 | 109 | 18:30 | Ishurdi | 137 | 17:00 | 132 | 21:00
| Tangail | 133 | 6:00 | 123 | 19:30 | Ruppur Paromanobik | 137 | 6:00 | 131 | 20:00
| Mymensing | 127 | 6:00 | 115 | 18:30 | Natore | 136 | 17:00 | 129 | 21:00
| Kishorganj | 129 | 6:00 | 118 | 22:00 | Bogra | 135 | 17:00 | 126 | 20:00
| Netrokona | 126 | 7:00 | 110 | 19:30 | Noagaon | 131 | 18:00 | 118 | 20:00
| Jamalpur | 136 | 16:00 | 123 | 22:00 | Rajshahi | 137 | 17:00 | 130 | 21:00
| Sherpur | 136 | 14:00 | 122 | 0:00 | Rajshahi New | 139 | 17:00 | 130 | 12:00
| Srimongal | 136 | 7:00 | 134 | 0.041667 | C.Nawabganj | 137 | 17:00 | 127 | 12:00
| Shahjibazar | 136 | 7:00 | 131 | 0.041667 | Amnura | 138 | 17:00 | 126 | 13:00
| Fenchuganj | 135 | 9:00 | 132 | 0.041667 | Pabna | 134 | 17:00 | 128 | 21:00
| Khulawara | 134 | 5:00 | 132 | 0.041667 | Shahjadpur | 139 | 17:00 | 132 | 13:00
| Sylhet | 133 | 7:00 | 130 | 0.75 | Serajganj | 132 | 18:00 | 127 | 21:00
| Chatak | 132 | 7:00 | 126 | 18:30 | Niyamatpur | 129 | 7:00 | 115 | 20:00
| Sunamganj | 132 | 9:00 | 125 | 0.041667 | Joypurhat | 131 | 17:00 | 117 | 20:00
| Biani Bazar | 133 | 8:00 | 127 | 0.041667 | Sherpur(Bogura) | 135 | 17:00 | 127 | 21:00
| Comilla(s) | 127 | 7:00 | 118 | 18:00 | Mohastangor | 134 | 18:00 | 124 | 21:00
| Comilla(n) | 138 | 19:30 | 134 | 11:00 | Rangpur | 131 | 17:00 | 117 | 20:00
| Chandpur | 138 | 8:00 | 132 | 15:00 | Lalmonirhat | 128 | 6:00 | 117 | 21:00
| Feni | 137 | 21:00 | 132 | 11:00 | Saidpur | 130 | 17:00 | 118 | 20:00
| Chowmuhani | 133 | 21:00 | 130 | 7:00 | Purbasadipur | 129 | 17:00 | 115 | 19:00
| Ashuganj | 136 | 8:00 | 132 | 1:00 | Thakurgaon | 128 | 6:00 | 116 | 21:00
| Daudkandi | 137 | 18:30 | 124 | 12:00 | Palashbari | 130 | 17:00 | 119 | 20:00
| B.Baria | 133 | 7:00 | 127 | 22:00 | Barapukuria | 137 | 17:00 | 128 | 21:00
| Ramganj | 130 | 19:00 | 128 | 22:00 | Panchagar | 129 | 6:00 | 113 | 12:00
| Chaddagram | 136 | 20:0 | 133 | 7:00 | Joldhaka | 129 | 17:00 | 115 | 20:00
| PHP | 134 | 19:00 | 129 | 12:00 | Kurigram | 127 | 17:00 | 113 | 18:30
| Madanhat | 136 | 1:00 | 133 | 10:00

## L-Curve
Date | 2020-10-04
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 118 | 8057 | 3608 | 11665 |  |  |  | QF-LDC-11
0:30 | 117.5 | 7788 | 3613.5 | 11401.5 | Date: | 2020-10-04
1:00 | 117 | 7519 | 3619 | 11138
1:30 | 86 | 7469 | 3533 | 11002
2:00 | 55 | 7419 | 3447 | 10866
2:30 | 88.5 | 7273 | 3431 | 10704 | [5 empty] | Gen. at Eve. Peak | 12317 | 9500 MW (19:30 )
3:00 | 122 | 7127 | 3415 | 10542 | [6 empty] | 19:00
3:30 | 113 | 7064.5 | 3392 | 10456.5 | [5 empty] | Gen. at Day Peak | 10180 | 7952.5 MW (12:00 )
4:00 | 104 | 7002 | 3369 | 10371 | [6 empty] | 12:00
4:30 | 113 | 6972 | 3277.5 | 10249.5 | [5 empty] | Highest Generation | 12317
5:00 | 122 | 6942 | 3186 | 10128 | [6 empty] | 19:00
5:30 | 212 | 6724 | 3117 | 9841
6:00 | 302 | 6506 | 3048 | 9554
6:30 | 299 | 6247 | 2997.5 | 9244.5
7:00 | 296 | 5988 | 2947 | 8935
7:30 | 309.5 | 5992.5 | 2940 | 8932.5
8:00 | 323 | 5997 | 2933 | 8930
8:30 | 339 | 6248 | 2926.5 | 9174.5
9:00 | 355 | 6499 | 2920 | 9419
9:30 | 330 | 6673 | 2888.5 | 9561.5
10:00 | 305 | 6847 | 2857 | 9704
10:30 | 255 | 6919 | 2867 | 9786
11:00 | 205 | 6991 | 2877 | 9868
11:30 | 202.5 | 7077 | 2947 | 10024
12:00 | 200 | 7163 | 3017 | 10180
12:30 | 172 | 7277.5 | 3015 | 10292.5
13:00 | 144 | 7392 | 3013 | 10405
13:30 | 119 | 7412.5 | 3018.5 | 10431
14:00 | 94 | 7433 | 3024 | 10457
14:30 | 142 | 7509.5 | 3105.5 | 10615
15:00 | 190 | 7586 | 3187 | 10773
15:30 | 262.5 | 7460.5 | 3170 | 10630.5
16:00 | 335 | 7335 | 3153 | 10488
16:30 | 403.5 | 7071.5 | 3117.5 | 10189
17:00 | 472 | 6808 | 3082 | 9890
17:30 | 407 | 7261 | 3340 | 10601
18:00 | 342 | 7714 | 3598 | 11312
18:30 | 208.5 | 8050.5 | 3764 | 11814.5
19:00 | 75 | 8387 | 3930 | 12317
19:30 | 136 | 8404 | 3872 | 12276
20:00 | 204 | 8416 | 3800 | 12216 |  |  |  | Executive Engineer
20:30 | 217 | 8391 | 3770.5 | 12161.5 |  |  |  | Network Operation Division
21:00 | 230 | 8366 | 3741 | 12107
21:30 | 216 | 8313 | 3734 | 12047
22:00 | 202 | 8260 | 3727 | 11987 |  |  |  |  | Page 6 of 7
22:30 | 162.5 | 8223 | 3726.5 | 11949.5
23:00 | 123 | 8186 | 3726 | 11912
23:30 | 120.5 | 8121.5 | 3667 | 11788.5
24:00 | 118 | 8057 | 3608 | 11665
9500 MW (19:30 )
7952.5 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-10-04 |  | Energy | 258507696
[10 empty] | 2020-10-04 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3883 | 900 | 1731 | 3628 | 740 | 45 | 698 | 0 | 154
0:30 | 3797 | 912.5 | 1773.5 | 3419.5 | 745 | 44.5 | 615.5 | 0 | 151 | Date: | 2020-10-04
1:00 | 3711 | 925 | 1816 | 3211 | 750 | 44 | 533 | 0 | 148
1:30 | 3716.5 | 924.5 | 1814 | 3110.5 | 740 | 43.5 | 508 | 0 | 145 | [7 empty] | Total Energy | 258.5077 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 3722 | 924 | 1812 | 3010 | 730 | 43 | 483 | 0 | 142 | [7 empty] | Energy not Served | 0
2:30 | 3664 | 924.5 | 1833 | 2922 | 730 | 42.5 | 448 | 0 | 140 | [7 empty] | Energy Requirement | 258.5077
3:00 | 3606 | 925 | 1854 | 2834 | 730 | 42 | 413 | 0 | 138
3:30 | 3603 | 925 | 1833 | 2792 | 730 | 41.5 | 396 | 0 | 136 | [6 empty] | Shortage
4:00 | 3600 | 925 | 1812 | 2750 | 730 | 41 | 379 | 0 | 134
4:30 | 3649 | 925 | 1815 | 2667.5 | 730 | 40.5 | 290.5 | 0 | 132
5:00 | 3698 | 925 | 1818 | 2585 | 730 | 40 | 202 | 0 | 130
5:30 | 3709 | 925 | 1799 | 2360 | 710 | 41 | 169 | 0 | 128
6:00 | 3720 | 925 | 1780 | 2135 | 690 | 42 | 136 | 0 | 126
6:30 | 3696.5 | 925.5 | 1769 | 1863 | 690 | 42 | 136 | 0 | 119 |  |  |  |  | Coal
7:00 | 3673 | 926 | 1758 | 1591 | 690 | 42 | 136 | 0 | 112
7:30 | 3673 | 925.5 | 1756.5 | 1599 | 680 | 42.5 | 136 | 0 | 109 |  |  |  | Oil |  |  |  | ,
8:00 | 3673 | 925 | 1755 | 1607 | 670 | 43 | 136 | 0 | 106
8:30 | 3641.5 | 913 | 1716.5 | 1904.5 | 660 | 43 | 169 | 0 | 108
9:00 | 3610 | 901 | 1678 | 2202 | 650 | 43 | 202 | 0 | 110
9:30 | 3763.5 | 901 | 1691.5 | 2202 | 634.5 | 43 | 193 | 0 | 111
10:00 | 3917 | 901 | 1705 | 2202 | 619 | 43 | 184 | 0 | 112
10:30 | 3997.5 | 900.5 | 1685.5 | 2226 | 619.5 | 43.5 | 184 | 0 | 114
11:00 | 4078 | 900 | 1666 | 2250 | 620 | 44 | 184 | 0 | 116
11:30 | 4162 | 900 | 1697.5 | 2270 | 630 | 44 | 184 | 0 | 120
12:00 | 4246 | 900 | 1729 | 2290 | 640 | 44 | 184 | 0 | 124
12:30 | 4225 | 900 | 1704 | 2450.5 | 645 | 42 | 184 | 0 | 122
13:00 | 4204 | 900 | 1679 | 2611 | 650 | 40 | 184 | 0 | 120
13:30 | 4204 | 900 | 1679 | 2611 | 650 | 40 | 184 | 0 | 120
14:00 | 4204 | 900 | 1679 | 2611 | 650 | 40 | 184 | 0 | 120
14:30 | 4034 | 900 | 1679.5 | 2833.5 | 660 | 39.5 | 299 | 0 | 124
15:00 | 3864 | 900 | 1680 | 3056 | 670 | 39 | 414 | 0 | 128
15:30 | 3860.5 | 900.5 | 1661.5 | 2892.5 | 670 | 40.5 | 459.5 | 0 | 128
16:00 | 3857 | 901 | 1643 | 2729 | 670 | 42 | 505 | 0 | 128
16:30 | 3805.5 | 901 | 1551.5 | 2605.5 | 650 | 41.5 | 499.5 | 0 | 126
17:00 | 3754 | 901 | 1460 | 2482 | 630 | 41 | 494 | 0 | 124
17:30 | 3802.5 | 901 | 1511.5 | 2992 | 615 | 41 | 596 | 0 | 140
18:00 | 3851 | 901 | 1563 | 3502 | 600 | 41 | 698 | 0 | 156
18:30 | 3868 | 901 | 1677 | 3815 | 660 | 41.5 | 696 | 0 | 156
19:00 | 3885 | 901 | 1791 | 4128 | 720 | 42 | 694 | 0 | 156
19:30 | 3926 | 901 | 1820 | 4014 | 740 | 42 | 677 | 0 | 156
20:00 | 3941 | 901 | 1746 | 4013 | 740 | 44 | 675 | 0 | 156
20:30 | 3933 | 901 | 1728.5 | 3977 | 740 | 44.5 | 681.5 | 0 | 156
21:00 | 3925 | 901 | 1711 | 3941 | 740 | 45 | 688 | 0 | 156
21:30 | 3932 | 901 | 1734 | 3855.5 | 740 | 45 | 683.5 | 0 | 156
22:00 | 3939 | 901 | 1757 | 3770 | 740 | 45 | 679 | 0 | 156
22:30 | 3971.5 | 900.5 | 1755 | 3699 | 740 | 45 | 682.5 | 0 | 156
23:00 | 4004 | 900 | 1753 | 3628 | 740 | 45 | 686 | 0 | 156
23:30 | 3943.5 | 900 | 1742 | 3628 | 740 | 45 | 692 | 0 | 155 | Max Temp. in Dhaka |  | 34.0° C
24:00 | 3883 | 900 | 1731 | 3628 | 740 | 45 | 698 | 0 | 154
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
Note on W13: Author:

## Generation
g | 2020-10-04
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 44 | 43 | 42 | 41 | 40 | 42 | 42 | 43 | 43 | 43 | 44 | 44 | 40 | 39 | 39 | 42 | 41 | 41 |  | 42 | 42 | 44 | 45 | 45 | 45 | 45 | 964080
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 115 | 115 | 0 | 0 | 90 | 115 | 120 | 120 | 120 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2500000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | [12 empty] | 15 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 |  | 3 | 283219
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 5 | 9 | 16 | 11 |  | 13 | 9 | 5 | 16 | 9 | 4 | [9 empty] | 100575
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 203 | 203 | 204 | 203 | 204 | 203 | 205 | 204 | 204 | 204 | 209 | 207 | 204 | 204 | 204 | 204 | 204 |  | 204 | 204 | 204 | 203 | 204 | 217 | 204 | 4892462
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 140 | 140 | 140 | 139 | 140 | 140 | 138 | 139 | 104 | 104 | 104 | 107 | 144 | 139 | 139 | 139 | 139 | 139 |  | 139 | 139 | 139 | 139 | 139 | 145 | 139 | 3142127
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 102 | 102 | 68 | 34 | [9 empty] | 17 | 17 | 17 | 17 | 98 |  | 102 | 85 | 85 | 99 | 87 | 90 | 102 | 1020172
12 | Hathazari 100 MW peaking PP
Sikalbaha 105 MW PP (Baraka Sikalbaha)
| Daudkandi 200 MW PP (B.Trac) | [14 empty] | 30 |  |  | 100 |  | 130 | 50 | 50 |  |  |  |  | 289152
14 | Titas 50 MW Peaking PP | [14 empty] | 25 | 25 | 25 | 40 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 364360
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 155 | 155 | 155 | 155 | 155 | 150 | 155 | 155 | 120 | 120 | 180 | 180 | 178 | 135 | 97 | 97 | 54 | 115 |  | 153 | 194 | 195 | 195 | 195 | 160 | 160 | 3866000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 300 | 300 | 300 | 300 | 300 | 195 | 95 | 95 | 180 | 230 | 230 | 230 | 280 | 285 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 6548725
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3260000
23 | Ghorasal TPP Unit-5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2772000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4793936
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2143852
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 29 | 26 | 29 | 29 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 635328
33 | Ashuganj 225 MW CCPP | 183 | 181 | 182 | 181 | 182 | 181 | 184 | 187 | 181 | 182 | 183 | 199 | 189 | 177 | 184 | 177 | 177 | 186 |  | 176 | 181 | 183 | 177 | 181 | 197 | 176 | 4443000
34 | Ashuganj 450 MW CCPP(South) | 10 | 20 | 20 | 30 | 30 | 30 | 35 | 0 | 35 | 235 | 245 | 195 | 190 | 175 | 185 | 170 | 170 | 195 |  | 170 | 180 | 185 | 170 | 180 | 210 | 170 | 3201200
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 325 | 325 | 325 | 295 | 345 | 325 | 315 | 315 | 315 | 275 | 270 |  | 315 | 315 | 315 | 315 | 315 | 350 | 315 | 7819500
35 | Ashuganj 55 MW PP (Precision) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 56 | 56 | 54 | 51 | 50 | 50 | 53 | 51 | 52 | 50 | 53 |  | 55 | 55 | 55 | 57 | 57 | 56 | 53 | 1300800
36 | Chandpur 150 MW CCPP | 95 | 96 | 96 | 86 | 95 | 86 | 96 | 94 | 94 | 87 | 87 | 96 | 95 | 96 | 86 | 96 | 86 | 95 |  | 90 | 95 | 96 | 96 | 95 | 94 | 84 | 2170550
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 4664800
41 | Haripur 360MW CCPP(HPL) | 323 | 323 | 324 | 323 | 323 | 323 | 323 | 323 | 292 | 328 | 346 | 344 | 344 | 344 | 344 | 347 | 297 | 243 |  | 350 | 350 | 348 | 352 | 351 | 350 | 353 | 7922000
42 | RPCL 210MW CCPP | 157 | 157 | 157 | 159 | 159 | 159 | 158 | 158 | 156 | 154 | 154 | 153 | 151 | 152 | 153 | 154 | 154 | 154 |  | 156 | 156 | 156 | 157 | 156 | 156 | 156 | 3649880
43
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 59 | 57 | 58 | 58 | 57 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 58 | 1415000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 719520
46 | Shajibazar 330 MW CCPP | 182 | 180 | 181 | 180 | 180 | 183 | 182 | 181 | 180 | 181 | 183 | 181 | 182 | 180 | 182 | 182 | 182 | 180 |  | 180 | 180 | 180 | 181 | 183 | 182 | 182 | 4156000
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 65 | 65 | 60 | 65 | 65 | 45 | 65 |  | 66 | 65 | 65 | 65 | 65 | 65 | 67 | 1233792
48 | Shahjibazar 86MW PP (Shahjibazar) | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 85 | 85 | 83 | 40 | 83 | 83 | 83 | 83 | 83 | 20 | 88 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 1918080
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 218 | 218 | 218 | 218 | 218 | 218 | 216 | 218 | 218 | 218 | 198 | 198 | 219 | 219 | 219 | 219 | 213 | 176 |  | 216 | 219 | 219 | 219 | 219 | 219 | 218 | 5163290
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 425000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 9 | 10 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 9 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 240660
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | [5 empty] | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [5 empty] | 2 | 8 | 8 | 96000
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 50 | 50 | 50 | 50 | 50 | 50 | 11 | 22 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1133400
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 564792
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 290 | 300 | 285 | 285 | 280 | 265 | 300 | 280 | 290 | 280 | 290 | 310 | 290 | 300 | 280 | 290 | 250 |  | 290 | 300 | 280 | 290 | 295 | 295 | 300 | 7070700
| Bibiyana South 400 MW | [9 empty] | 100 | 220 | 199 | 150 | 150 | [12 empty] | 1315500
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1257888
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 18 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 469344
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  |  |  | 22 | 22 | 22 | 22 | 22 | 443556
62 | Tangail 22 MW PP (Doreen) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 11 | 14 | 14 | 14 | 14 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 333072
63 | Impoprt (Tripura) | 148 | 142 | 138 | 134 | 130 | 126 | 112 | 106 | 110 | 112 | 116 | 124 | 120 | 132 | 128 | 128 | 124 | 156 |  | 156 | 156 | 156 | 156 | 156 | 156 | 154 | 3254400
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 38 | 33 | 3 | 3 | 3 | 2 | 2 | 8 | 8 | 6 | 4 | 11 | 8 |  | 16 | 22 | 25 | 32 | 40 | 41 | 42 | 537600
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504360
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  |  | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 173880
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 817100
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 511910
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 22 | 476280
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 816800
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 834800
73 | Ghorashal 108MW PP (Regent) | 42 | 41 | 41 | 41 | 41 | 41 | 42 | 42 | 41 | 41 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 989000
| Feni Lanka Power | 100 | 100 | 100 | 100 | 70 | 24 | 17 | 17 | 52 | 34 | 34 | 34 | 100 | 100 | 100 | 45 | 34 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1843380
| Chowmuhani 113 MW | 113 | 113 | 113 | 113 | 108 | 107 | 55 | 55 | 105 | 113 | 113 | 113 | 103 | 104 | 110 | 110 | 110 | 110 |  | 113 | 113 | 112 | 113 | 113 | 113 | 113 | 2572080
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 20 | 32 | 238080
78 | Gazipur 52 MW PP | 52 | 52 | [8 empty] | 26 | 33 | 33 | 33 | 48 | 25 | 25 | 43 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 700356
79 | Kodda 150MW PP | 150 | 150 | 115 | 115 | 82 | 16 | 16 | 16 | 82 | 64 | 64 | 64 | 64 | 64 | 150 | 150 | 98 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 2557440
80 | Jamalpur 95 MW PP(Powerpac) | [26 empty] | 0
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | 52 | 52 | 50 | 8 | 8 | 37 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1156968
| Gazipur 100 MW PP | 104 | 104 | 104 | 103 | 50 | 16 | 16 | 20 | 68 | 68 | 68 | 68 | 68 | 68 | 84 | 84 | 32 | 103 |  | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 1883832
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 3 | 4 | 5 | 3 | 4 | 4 | 5 | 3 | 2 | 0 | [9 empty] | 32521
| Jodiac Power | 37 | 34 | 27 | 36 | 36 | 36 | 36 | 17 | 17 | 17 | 18 | 18 | 33 | 35 | 37 | 44 | 48 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 37 | 899936
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | 82 | 95 | 96 | 95 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 96 | 96 | 96 | 96 | 92 | 80 | 2038464
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 100 | 100 | 50 | [5 empty] | 7 | 12 | 12 | 12 | 13 | 12 | 12 | 12 | 15 | 15 |  | 66 | 100 | 100 | 100 | 100 | 100 | 100 | 977766
86 | Meghnaghat CCPP(Summit) | 285 | 280 | 290 | 265 | 285 | 260 | 290 | 290 | 288 | 285 | 290 | 300 | 290 | 280 | 290 | 285 | 280 | 300 |  | 290 | 300 | 300 | 300 | 300 | 310 | 300 | 6936465
87 | Meghnaghat 100 MW(IEL) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 26 | 63 |  | 92 | 92 | 95 | 100 | 100 | 100 | 100 | 816960
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 2582400
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [13 empty] | 18 | 40 | 10 | 10 | 10 |  | 37 | 60 | 60 | 60 | 40 | 40 | 40 | 376200
92 | Fenchuganj 44MW (Energyprima) | 47 | 47 | 47 | 47 | 44 | 47 | 47 | 47 | 47 | 44 | 44 | 47 | 47 | 47 | 43 | 45 | 10 | 20 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 1070928
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1223513
94 | Gagnagar 102 MW PP (Digital Power) | 16 | 16 | 16 | 16 | 16 | 7 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 312624
95 | Patenga 50MW PP (Baraka) | 50 | 50 | 50 | 50 | 50 | 23 | 19 | 19 | 19 | 19 | 19 | 19 | 32 | 50 | 50 | 50 | 19 | 37 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 946560
96 | Chattogram 108 MW PP (ECPV) | 97 | 97 | 97 | 93 | 97 | 81 | 23 | 16 | 60 | 60 | 62 | 62 | 75 | 85 | 90 | 90 | 91 | 97 |  | 97 | 97 | 97 | 97 | 97 | 97 | 98 | 1980480
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | 40 | 40 | 40 | 40 | 40 | 40 | 25 | 30 | 40 | 40 | 28 | 34 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 48 | 40 | 949606
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 35 | 17 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1257427
101 | Kushiara 163 MW CCPP (KP) | 15 | 20 | 30 | 35 | 35 | 35
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 1 | 0 | 0 | 1 | 1 | 0 | [9 empty] | 11750
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 17 | 17 | 17 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1233360
104 | Keranigonj 300 MW PP (APR) | [13 empty] | 37 | 35 |  |  | 140 |  | 153 | 106 | 104 | 105 | 108 | 24 | 23 | 731911
105 | Bramhangoan 100 MW PP (Aggreko) | [10 empty] | 25 | 25 | 25 | 25 | 50 | 25 |  | 78 |  | 74 | 64 | 62 | 30 | 21 | 16 | 31 | 450974
106 | Mymensingh 200 MW PP (United) | 194 | 193 | 193 | 194 | 194 | 193 | 120 | 120 | 160 | 160 | 160 | 160 | 185 | 191 | 190 | 191 | 182 | 191 |  | 200 | 200 | 200 | 200 | 200 | 200 | 193 | 4384800
112 | Aurahati 100MW PP (Aggreko) | [13 empty] | 7 | 25 |  |  | 83 |  | 98 | 99 | 99 | 101 | 57 |  |  | 463081
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 149 | 149 | 149 | 149 | 144 | 117 | 134 | 149 | 149 | 149 | 149 | 149 | 145 | 132 | 141 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3537220
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 100 | 100 | 100 | 100 | 100 | 50 | 60 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2283840
116 | Chandpur 200MW (Desh energy) | 132 | [13 empty] | 36 | 61 | 34 | 91 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 1663680
117 | Ashuganj 150MW PP (Midland) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 16 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 767781
118 | Bibiyana-III 400 MW CCPP | 420 | 424 | 421 | 418 | 419 | 417 | 419 | 419 | 419 | 423 | 421 | 415 | 418 | 420 | 417 | 419 | 421 | 417 |  | 421 | 420 | 420 | 425 | 422 | 421 | 424 | 10104000
| Jamalpur 115 MW PP (United) | 85 | 85 | 85 | 85 | 85 | 35 | 16 | 29 | 45 | 45 | 45 | 45 | 65 | 85 | 85 | 85 | 45 | 50 |  | 96 | 105 | 105 | 105 | 55 | 55 | 55 | 1738800
| Anwara 300 MW PP (United) | 162 | 162 | 162 | 162 | 162 | 162 | 125 | 160 | 161 | 124 | 124 | 141 | 177 | 180 | 180 | 162 | 162 | 88 |  | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 3628145
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2413440
120 | Eastern Zone Total | 7519 | 7419 | 7127 | 7002 | 6942 | 6506 | 5988 | 5997 | 6499 | 6847 | 6991 | 7163 | 7392 | 7433 | 7586 | 7335 | 6808 | 7714 |  | 8387 | 8404 | 8416 | 8366 | 8260 | 8186 | 8057 | 177186937
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 115 | 115 | 115 | 115 | 104 | 51 | 18 | 16 | 66 | 49 | 49 | 49 | 99 | 99 | 99 | 99 | 32 | 93 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2063040
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 13 | 13 | 12 | 12 | [12 empty] | 2 | 9 |  | 9 | 9 | 13 | 16 | 19 | 23 | 23 | 144960
| Khulna 225 MW CCPP | 170 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 160 |  | 160 | 160 | 150 | 150 | 150 | 150 | 150 | 3292800
129 | Rupsha 105 MW PP (Orion rupsha) | 18 | 17 | 17 | 17 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 53 | 53 | 53 | 53 | 53 | 53 | 36 | 616320
130
131
132
133
| Barisal 110 MW PP (Summit ) | 96 | 96 | 64 | 64 | 64 | 48 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 64 | 80 | 64 | 48 | 80 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 1627200
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 92 | 92 | 92 | 92 | 92 | 90 | 90 | 89 | 89 | 89 | 89 | 90 |  | 0 | 4 | 81 | 85 | 89 |  | 89 | 89 | 89 | 89 | 90 | 90 | 90 | 1919355
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 38 | 37 | 37 | 36 | 35 | 31 | 26 | 19 | 24 | 24 | 25 | 26 | 25 | 25 | 26 | 27 | 27 | 37 |  | 38 | 38 | 38 | 38 | 39 | 38 | 38 | 741946
141 | Noapara 100 MW PP (Bangla Trac) | 100 | 20 | [15 empty] | 15 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 789120
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 40 | 40 | [10 empty] | 40 | 8 | 8 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 491250
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 1 | 10 | [8 empty] | 7808
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 925 | 924 | 925 | 925 | 925 | 925 | 926 | 925 | 901 | 901 | 900 | 900 | 900 | 901 | 900 | 901 | 901 | 901 |  | 901 | 901 | 901 | 901 | 901 | 900 | 900 | 21801454
147 | Bheramara 410 MW CCPP | 240 | 240 | 240 | 240 | 245 | 255 | 185 | 200 | 190 | 190 | 210 | 315 | 285 | 260 | 240 | 250 | 265 | 270 |  | 245 | 233 | 220 | 220 | 220 | 220 | 220 | 5837184
148 | Payra 1320 MW | 600 | 580 | 580 | 580 | 580 | 540 | 540 | 520 | 500 | 470 | 470 | 490 | 500 | 520 | 520 | 520 | 480 | 450 |  | 570 | 590 | 590 | 590 | 590 | 590 | 590 | 13914200
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 150 | 150 | 150 | 149 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3689400
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [14 empty] | 17 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 493280
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 159 | 164 | 160 | 140 | 137 | 136 | 136 | 142 |  | 140 | 133 | 131 | 130 | 130 | 130 | 130 | 3771609
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 138 | 134 | 132 | 131 | 130 |  | 131 | 129 | 128 | 128 | 128 | 125 | 125 | 3544164
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 419 | 402 | 423 | 394 | 403 | 378 | 415 | 416 | 386 | 385 | 380 | 388 | 404 | 398 | 405 | 306 | 291 | 385 |  | 400 | 413 | 358 | 300 | 332 | 331 | 303 | 9041090
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [15 empty] | 10 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 353507
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 503280
163 | Bogura 20 MW PP (Energyprima) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 234720
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 237834
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [14 empty] | 43 | 43 | 43 | 43 |  | 43 | 43 | 47 | 43 | 43 | 43 | 43 | 400200
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 52 | 16 | 8 | 8 | 8 | 25 | 8 | 8 | 8 | 39 | 51 | 51 | 8 | 8 | 31 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 822720
170 | Chapainawabganj 100 MW Peaking PP | 98 | 98 | 98 | 98 | [10 empty] | 42 | 90 | 96 | 96 |  | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 1255376
171 | Baghabari 200 MW PP (Paramount) | [14 empty] | 20 |  |  | 100 |  | 120 | 50 | 50 | 50 |  |  |  | 327093
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 934464
172 | Confidence Power Bogura Unit-1 113 MW | 50 | 50 | 50 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 108 |  | 109 | 109 | 109 | 109 | 109 | 109 | 54 | 1358400
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 28 | 26 | 25 | 27 | 27 | 27 | 27 | 27 | 27 | 26 | 27 | 27 | 26 | 27 | 27 | 27 | 36 | 72 |  | 89 | 89 | 90 | 91 | 90 | 92 | 74 | 1078080
177 | Sympa Solar Power 8MW | [6 empty] | 1 | 2 | 2 | 3 | 5 | 5 | 4 | 3 | 2 | 1 | 0 | [9 empty] | 28905
178
178