## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-10-08 | Thursday
|  |  | Date (day): | 2020-10-08 |  | Thursday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13378.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14513 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-10-07 | 2020-10-08 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 115 | 115 | 115 | 75 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 200 | 200
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 69 | 71 | 78 | 78
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 84 | 84 | 100 | 100
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under S/D for dust in gas.
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 345 | 353 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 |  |  | GT-1 under maint.
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 7 | 7 | 7 | 93 |  | Fuel Shortage
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 312 | 280 | 305 | 305
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 80 | 97 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 51 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 12 | 12 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 73 | 185 | 200 | 200
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 94 | 94 | 40 | 40 |  |  | Fuel shortage
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 150 | 149 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 47 | 55 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 52 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 195 | 300 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 131 | 131 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 67 | 85 | 100 | 100
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 17 | 17 | 17 |  |  | Fuel Shortage
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 2453 | 2916 | 3181 | 3560 | 612 | 1162
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 8 | 25 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 79 | 120 | 120 | 120 | 110 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 218 | 204 | 221 | 221
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 146 | 139 | 140 | 140
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 100 | 100
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 40 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 95 | 100 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 21 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 7 | 14 | 10 | 15
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 78 | 84 | 84 | 84
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 160 | 143 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 54 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 1100 | 1315 | 1780 | 1760 | 350 | 98
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 80 | 80 | 80 |  | 54 | Engine problem
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 210 | 215 | 225 | 225 |  |  | FGMO
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 350 | 310 | 360 | 360 |  |  | FGMO
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 235 | 240 | 235 | 360
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 29 | 30 | 30 | 15 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 55 | 55
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 43 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 30 | 30 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 50 | 0 | 50
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 96 | 91 | 92 | 92 |  | 71 | ST under shut down
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 153 | 200 | 200
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 21 | 22 | 22
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 9 | 9 | 8 | 8 |  | 3 | Engine problem
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 112 | 156 | 162 | 173
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 24 | 52 | 52 | 52
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 21 | 21 | 21
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 100 | 100 | 100 |  | 14 | Engine problem
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 110 | 113 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1421 | 1759 | 1997 | 2383 | 466 | 142
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 158 | 145 | 160 | 160 | 42 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 14 | 14 |  | 8 | Engine problem
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 0 | 0 | 0 |  | 95 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 194 | 200 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 55 | 105 | 115 | 115
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 425 | 467 | 490.6 | 489 | 42 | 103
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 60 | 60 | 60
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 35 | Unit-4 under shut down
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 115 | 115 |  | 48 | STG under maint.
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 74 | 195 | 140 | 200 |  | 110 | ST Under maint.
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 53 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 47 | 40 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 66 | 65 | 65
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 86 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 170 | 218 | 220 | 220
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 25 | 25
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 295 | 341 | 341 |  |  | FGMO
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 330 | 365 | 430 | 430
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 275 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1502 | 1453 | 1646 | 1706 | 0 | 193
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 915 | 906 | 915 | 915
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 32 | 101 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 12 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 215 | 225 | 225
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 330 | 395 | 410 | 410
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 53 | 70 | 70 | 70 |  | 35 | Engine problem.
| 108 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1450 | 1839 | 1925 | 2081 | 0 | 35
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 100 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 19 | 36 | 33 | 33
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 85 | 94 | 80 | 90
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 510 | 560 | 620 | 620
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 614 | 790 | 843 | 853 | 0 | 194
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 35 | 0 | 42
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 39 | 50 | 50
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 130 | 154 | 220 | 220 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 383 | 410 | 414 | 414 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 0 | 34
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 8 | 8 | 10 | 10
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 10 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 52 | 52 | 52
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 97 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 35 | 90 | 113 | 113 |  | 0 | Engine problem
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 36 | 109 | 113 | 113 |  | 0 | Engine problem
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 625 | 1107 | 1304 | 1431 | 701 | 0
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 42 | 103 | 54 | 100 |  | 13 | Engine problem
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 197 | 253 | 212 | 250 | 294 | 53
|  | Total |  |  |  |  | 20383 | 19892 | 9787 | 11899 | 13378.6 | 14513 | 2465 | 1980
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9300.0764 | 11307 | 12712.9868 | 13790.9481
| A. |  | 2020-10-07 | (Yesterday) |  |  |  |  | Wednesday
| 1 | Highest Generation : |  |  | 11899 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
| 2 | Minimum Generation : |  |  | 8442 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11899 | MW
| 3 | Day peak Generation : |  |  | 9787 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11307 | MW
| 4 | Evening peak Generation : |  |  | 11899 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 244.4528 | MKWHr | By Solar | 0.20948 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 130.9815 | MKWHr |  | By Oil: | 69.47 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 16.3975 | MKWHr |  | By Hydro: | 2.4677 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2465 | MW | Dhaka | 4043 | 4043 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 1980 | MW | Chittagong | 1183 | 1183 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4445 | MW | Khulna | 1442 | 1442 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1130.76 | MMCFD |  |  | Rajshahi | 1117 | 1117 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 152378221.64 | ii) Oil : | Taka | 545928744.23 | Comilla | 1124 | 1124 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 75782223 | Total | Taka | 774089188.87 | Mymensingh | 876 | 876 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.2425 | MKWHr. | Sylhet | 472 | 472 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 125 | MW (E to W) at | 19:30 | hrs | Barisal | 331 | 331 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -81 | MW at | 2:00 | hrs | Rangpur | 719 | 719 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.4° C |  |  | Total | 11307 | 11307 |  | 0
| B. |  | 2020-10-08 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 31.9° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12400 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14513 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10200 | MW
| 4 | Reserve(Generation end) |  |  |  | 2113 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 254.7453 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8686 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.8633 | MKWHr. | ii) HVDC Flow at Peak Time |  | 906 | MW at | 19:30 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.0634 | MKWHr. | iii) Maximum HVDC Flow : |  | 915 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 101.42 |  | (b) Today: | 101.82 |  | (c) Rule Curve: |  | 106.63
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-10-07
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 115 | 200 | 51 | 0 | 0 | 357 |  | 0 | 450 | 275 | 7 | 96 | 50 | 0 | 0 | 145 | 0 | 100 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 42 | 70 | 120 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 6 | 20 | 84 | 50 | 20 | 35 | 0 | 0 | 80 | 260 | 235 | 32 | 8 | 87 | 29 | 10 | 0 | 51 | 0 | 0 | 52 | 21 | 10 | 33 | 21 | 138 | 160 | 0 | 17 | 0 | 60 | 30 | 53 | 47 | 0 | 140 | 62 | 86 | 0 | 218 | 0 | 0 | 10 | 260 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 124 | 0 | 100 | 0 | 30 | 430 | 85 | 83 | 0 | 0 | 180 | 36 | 0 | 78 | 113 | 100 | 0 | 17 |  | 915 | 0 | 290 | 0 | 115 | 185 | 0 | 0 | 0 | 0 | 40 | 0 | 30 | 80 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 25 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 30 | 140 | 0 | 310 | 54 | 0 | 35 | 0 | 41 | 0 | 0 | 54 | 570 |  | 7305 | 3295 | 10600 | 3484 | 915 | 1880 | 2912 | 720 | 112 | 439 | 138 | 0 | 0 | 101.32
2:00 | 0 | 0 | 0 | 115 | 200 | 70 | 60 | 0 | 356 |  | 0 | 450 | 290 | 7 | 96 | 52 | 0 | 0 | 145 | 0 | 100 | 94 | 85 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 42 | 70 | 120 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 45 | 27 | 20 | 36 | 0 | 0 | 80 | 260 | 235 | 36 | 8 | 90 | 26 | 10 | 0 | 51 | 0 | 0 | 24 | 21 | 10 | 33 | 21 | 136 | 158 | 0 | 17 | 0 | 60 | 30 | 53 | 47 | 0 | 142 | 62 | 86 | 0 | 218 | 0 | 0 | 10 | 270 | 24 | 8 | 0 | 245 | 0 | 0 | 200 | 0 | 120 | 0 | 100 | 0 | 30 | 428 | 85 | 70 | 0 | 0 | 180 | 36 | 0 | 17 | 113 | 100 | 0 | 17 |  | 915 | 0 | 315 | 0 | 90 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 80 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 140 | 0 | 327 | 54 | 0 | 35 | 0 | 42 | 0 | 0 | 54 | 570 |  | 7060 | 3102 | 10162 | 3511 | 915 | 1985 | 2530 | 720 | 112 | 253 | 136 | 0 | 0 | 101.34
3:00 | 0 | 0 | 0 | 115 | 200 | 80 | 73 | 0 | 356 |  | 0 | 450 | 280 | 7 | 96 | 52 | 0 | 0 | 145 | 0 | 100 | 94 | 85 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 40 | 70 | 120 | 0 | 0 | 203 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 12 | 19 | 20 | 36 | 0 | 0 | 80 | 260 | 235 | 44 | 8 | 88 | 26 | 10 | 0 | 51 | 0 | 0 | 24 | 21 | 10 | 33 | 21 | 136 | 158 | 0 | 17 | 0 | 60 | 30 | 53 | 47 | 0 | 142 | 62 | 86 | 0 | 218 | 0 | 0 | 10 | 280 | 24 | 8 | 0 | 195 | 0 | 0 | 200 | 0 | 132 | 0 | 70 | 0 | 30 | 428 | 55 | 34 | 0 | 0 | 180 | 17 | 0 | 17 | 113 | 100 | 0 | 17 |  | 915 | 0 | 330 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 64 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 160 | 0 | 316 | 54 | 0 | 35 | 0 | 42 | 0 | 0 | 36 | 530 |  | 6894 | 3028 | 9922 | 3553 | 915 | 2007 | 2268 | 680 | 110 | 253 | 136 | 0 | 0 | 101.36
4:00 | 0 | 0 | 0 | 115 | 200 | 79 | 73 | 0 | 356 |  | 0 | 450 | 300 | 7 | 96 | 52 | 0 | 0 | 145 | 0 | 100 | 68 | 82 | 0 | 0 | 0 | 0 | 17 | 17 | 55 | 22 | 25 | 31 | 28 | 33 | 0 | 0 | 40 | 70 | 120 | 0 | 0 | 203 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 12 | 19 | 20 | 38 | 0 | 0 | 80 | 260 | 235 | 44 | 8 | 90 | 26 | 10 | 0 | 51 | 0 | 0 | 24 | 21 | 10 | 33 | 21 | 132 | 158 | 0 | 17 | 0 | 60 | 30 | 53 | 47 | 0 | 140 | 62 | 86 | 0 | 218 | 0 | 0 | 10 | 280 | 24 | 8 | 0 | 145 | 0 | 0 | 200 | 0 | 130 | 0 | 30 | 0 | 30 | 426 | 55 | 34 | 0 | 0 | 125 | 17 | 0 | 17 | 113 | 70 | 0 | 17 |  | 915 | 0 | 340 | 0 | 32 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 32 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 160 | 0 | 324 | 54 | 0 | 35 | 0 | 42 | 0 | 0 | 36 | 530 |  | 6660 | 2977 | 9637 | 3556 | 915 | 2013 | 1981 | 680 | 110 | 250 | 132 | 0 | 0 | 101.38
5:00 | 0 | 0 | 0 | 115 | 200 | 79 | 73 | 0 | 354 |  | 0 | 450 | 310 | 7 | 96 | 52 | 0 | 0 | 145 | 0 | 100 | 68 | 48 | 0 | 0 | 0 | 0 | 17 | 17 | 55 | 22 | 25 | 31 | 28 | 33 | 0 | 0 | 40 | 70 | 120 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 20 | 41 | 0 | 0 | 80 | 260 | 235 | 43 | 8 | 95 | 26 | 10 | 0 | 51 | 0 | 0 | 24 | 21 | 10 | 33 | 21 | 132 | 158 | 0 | 17 | 0 | 60 | 30 | 53 | 47 | 0 | 142 | 62 | 86 | 0 | 218 | 0 | 0 | 10 | 290 | 24 | 8 | 0 | 65 | 0 | 0 | 200 | 0 | 130 | 0 | 30 | 0 | 30 | 426 | 35 | 16 | 0 | 0 | 106 | 17 | 0 | 0 | 113 | 70 | 0 | 17 |  | 915 | 0 | 350 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 160 | 0 | 359 | 54 | 0 | 35 | 0 | 42 | 0 | 0 | 36 | 530 |  | 6479 | 2957 | 9436 | 3571 | 915 | 2058 | 1802 | 680 | 110 | 168 | 132 | 0 | 0 | 101.4
6:00 | 0 | 0 | 0 | 115 | 200 | 79 | 73 | 0 | 302 |  | 0 | 300 | 285 | 7 | 86 | 52 | 0 | 0 | 76 | 0 | 95 | 40 | 48 | 0 | 0 | 0 | 0 | 17 | 17 | 55 | 22 | 25 | 10 | 28 | 16 | 0 | 0 | 40 | 70 | 120 | 0 | 0 | 203 | 0 | 138 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 20 | 39 | 0 | 0 | 80 | 260 | 235 | 43 | 8 | 86 | 26 | 10 | 0 | 51 | 0 | 0 | 16 | 21 | 10 | 33 | 21 | 112 | 158 | 0 | 17 | 0 | 60 | 30 | 53 | 47 | 0 | 142 | 52 | 86 | 0 | 185 | 0 | 0 | 10 | 280 | 24 | 8 | 0 | 65 | 0 | 0 | 200 | 0 | 131 | 0 | 30 | 0 | 30 | 429 | 35 | 56 | 0 | 0 | 51 | 17 | 0 | 0 | 113 | 40 | 0 | 17 |  | 915 | 0 | 375 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 130 | 0 | 305 | 54 | 0 | 35 | 0 | 42 | 0 | 0 | 36 | 530 |  | 5968 | 2874 | 8842 | 3406 | 915 | 1785 | 1666 | 680 | 110 | 168 | 112 | 0 | 0 | 101.42
7:00 | 0 | 0 | 0 | 115 | 200 | 80 | 73 | 0 | 303 |  | 0 | 225 | 305 | 7 | 87 | 30 | 0 | 0 | 75 | 0 | 100 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 25 | 20 | 28 | 16 | 0 | 0 | 40 | 35 | 120 | 0 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 20 | 36 | 0 | 0 | 80 | 260 | 235 | 51 | 8 | 96 | 26 | 10 | 0 | 51 | 0 | 0 | 0 | 21 | 10 | 33 | 21 | 104 | 158 | 0 | 17 | 0 | 60 | 30 | 53 | 47 | 0 | 141 | 40 | 86 | 0 | 184 | 0 | 0 | 10 | 290 | 24 | 8 | 0 | 30 | 0 | 0 | 200 | 0 | 114 | 5 | 10 | 0 | 30 | 427 | 8 | 85 | 0 | 1 | 34 | 17 | 0 | 0 | 113 | 30 | 0 | 17 |  | 915 | 0 | 400 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 130 | 0 | 335 | 17 | 0 | 0 | 0 | 42 | 0 | 0 | 36 | 530 |  | 5617 | 2825 | 8442 | 3386 | 915 | 1749 | 1407 | 680 | 75 | 120 | 104 | 6 | 0 | 101.43
8:00 | 0 | 0 | 0 | 115 | 200 | 81 | 72 | 0 | 303 |  | 0 | 225 | 295 | 7 | 97 | 30 | 0 | 0 | 74 | 0 | 100 | 40 | 0 | 0 | 0 | 0 | 0 | 25 | 17 | 23 | 0 | 25 | 30 | 28 | 33 | 0 | 0 | 41 | 35 | 120 | 0 | 0 | 204 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 20 | 4 | 0 | 0 | 80 | 275 | 235 | 67 | 8 | 92 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 9 | 33 | 21 | 104 | 161 | 0 | 17 | 0 | 60 | 30 | 53 | 47 | 0 | 140 | 40 | 84 | 0 | 184 | 0 | 0 | 10 | 300 | 24 | 2 | 0 | 32 | 0 | 0 | 170 | 0 | 119 | 11 | 60 | 0 | 30 | 430 | 8 | 85 | 0 | 2 | 87 | 21 | 0 | 11 | 109 | 90 | 0 | 17 |  | 915 | 0 | 410 | 0 | 2 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 130 | 0 | 318 | 27 | 0 | 0 | 0 | 41 | 0 | 1 | 36 | 530 |  | 5855 | 2826 | 8681 | 3485 | 915 | 1696 | 1591 | 680 | 76 | 120 | 104 | 14 | 0 | 101.44
9:00 | 0 | 0 | 0 | 115 | 200 | 81 | 71 | 0 | 250 |  | 0 | 225 | 290 | 7 | 97 | 46 | 0 | 0 | 70 | 0 | 100 | 50 | 16 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 25 | 30 | 28 | 33 | 0 | 0 | 41 | 35 | 120 | 0 | 1 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 78 | 13 | 20 | 7 | 0 | 0 | 80 | 275 | 235 | 133 | 8 | 90 | 23 | 5 | 0 | 51 | 0 | 0 | 6 | 19 | 9 | 33 | 19 | 100 | 162 | 0 | 17 | 0 | 60 | 30 | 53 | 47 | 0 | 140 | 40 | 84 | 0 | 151 | 0 | 0 | 10 | 280 | 24 | 2 | 0 | 100 | 0 | 0 | 178 | 0 | 131 | 15 | 60 | 0 | 30 | 426 | 8 | 85 | 0 | 4 | 88 | 35 | 0 | 17 | 109 | 100 | 0 | 17 |  | 914 | 0 | 410 | 0 | 28 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 130 | 0 | 304 | 53 | 0 | 28 | 0 | 42 | 0 | 2 | 36 | 510 |  | 6090 | 2870 | 8960 | 3468 | 914 | 1608 | 1977 | 660 | 76 | 136 | 100 | 21 | 0 | 101.45
10:00 | 0 | 0 | 0 | 115 | 200 | 77 | 70 | 0 | 280 |  | 0 | 225 | 310 | 7 | 94 | 40 | 0 | 0 | 70 | 0 | 100 | 94 | 16 | 0 | 0 | 0 | 0 | 54 | 25 | 55 | 19 | 25 | 30 | 28 | 33 | 27 | 0 | 43 | 35 | 120 | 0 | 7 | 207 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 84 | 19 | 20 | 6 | 0 | 0 | 80 | 290 | 235 | 128 | 8 | 97 | 5 | 5 | 0 | 51 | 0 | 0 | 23 | 19 | 9 | 33 | 19 | 108 | 159 | 0 | 17 | 1 | 60 | 30 | 47 | 43 | 0 | 70 | 40 | 40 | 0 | 151 | 0 | 0 | 10 | 290 | 16 | 5 | 0 | 195 | 0 | 0 | 200 | 0 | 130 | 18 | 60 | 0 | 30 | 325 | 8 | 85 | 0 | 4 | 88 | 31 | 0 | 17 | 111 | 100 | 270 | 17 |  | 915 | 0 | 370 | 0 | 32 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 9 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 130 | 0 | 336 | 53 | 0 | 35 | 0 | 42 | 0 | 3 | 36 | 510 |  | 6417 | 2872 | 9289 | 3538 | 915 | 1619 | 2209 | 660 | 78 | 136 | 108 | 26 | 0 | 101.46
11:00 | 0 | 0 | 0 | 115 | 200 | 80 | 69 | 0 | 330 |  | 0 | 225 | 310 | 7 | 80 | 40 | 0 | 0 | 73 | 0 | 100 | 94 | 10 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 22 | 33 | 33 | 0 | 0 | 44 | 35 | 120 | 0 | 8 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 84 | 19 | 20 | 5 | 0 | 0 | 80 | 280 | 235 | 214 | 8 | 96 | 29 | 5 | 0 | 51 | 0 | 0 | 24 | 19 | 9 | 33 | 19 | 108 | 159 | 0 | 17 | 1 | 60 | 30 | 47 | 43 | 0 | 71 | 40 | 84 | 0 | 165 | 0 | 0 | 9 | 280 | 8 | 8 | 0 | 195 | 0 | 0 | 200 | 0 | 131 | 19 | 94 | 0 | 30 | 320 | 43 | 85 | 0 | 5 | 105 | 36 | 0 | 0 | 107 | 90 | 280 | 17 |  | 914 | 0 | 325 | 0 | 32 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 130 | 0 | 337 | 53 | 0 | 35 | 0 | 42 | 0 | 4 | 36 | 510 |  | 6679 | 2825 | 9504 | 3644 | 914 | 1699 | 2241 | 660 | 79 | 130 | 108 | 29 | 0 | 101.47
12:00 | 0 | 0 | 0 | 115 | 200 | 84 | 69 | 0 | 345 |  | 0 | 225 | 312 | 7 | 80 | 40 | 0 | 0 | 73 | 0 | 100 | 94 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 0 | 0 | 44 | 35 | 120 | 0 | 8 | 218 | 0 | 146 | 0 |  | 0 | 0 | 0 | 0 | 78 | 19 | 20 | 7 | 0 | 0 | 80 | 350 | 235 | 210 | 8 | 96 | 29 | 5 | 0 | 51 | 0 | 0 | 24 | 19 | 9 | 33 | 20 | 112 | 158 | 0 | 17 | 1 | 60 | 30 | 47 | 47 | 0 | 74 | 40 | 85 | 0 | 170 | 0 | 0 | 10 | 310 | 16 | 8 | 0 | 195 | 0 | 0 | 194 | 0 | 131 | 20 | 95 | 0 | 30 | 330 | 55 | 67 | 0 | 4 | 160 | 36 | 0 | 0 | 110 | 90 | 275 | 17 |  | 915 | 0 | 330 | 0 | 32 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 130 | 0 | 383 | 53 | 0 | 35 | 0 | 42 | 0 | 5 | 36 | 510 |  | 6901 | 2886 | 9787 | 3757 | 915 | 1810 | 2304 | 660 | 79 | 120 | 112 | 30 | 0 | 101.48
13:00 | 0 | 0 | 0 | 115 | 200 | 84 | 69 | 0 | 300 |  | 0 | 225 | 275 | 7 | 80 | 40 | 0 | 0 | 115 | 0 | 92 | 94 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 23 | 33 | 0 | 0 | 45 | 35 | 120 | 0 | 8 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 65 | 19 | 20 | 5 | 0 | 0 | 80 | 325 | 235 | 212 | 8 | 87 | 26 | 5 | 0 | 51 | 0 | 0 | 42 | 19 | 9 | 33 | 20 | 120 | 141 | 0 | 17 | 1 | 60 | 30 | 47 | 47 | 0 | 76 | 40 | 85 | 0 | 211 | 0 | 0 | 10 | 300 | 16 | 8 | 0 | 242 | 0 | 0 | 200 | 0 | 130 | 17 | 100 | 0 | 30 | 330 | 55 | 85 | 0 | 5 | 160 | 36 | 0 | 17 | 110 | 100 | 282 | 17 |  | 915 | 0 | 290 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 130 | 0 | 341 | 53 | 0 | 42 | 0 | 42 | 0 | 7 | 36 | 510 |  | 6922 | 2878 | 9800 | 3726 | 915 | 1709 | 2440 | 660 | 80 | 120 | 120 | 30 | 9800 | 101.49
14:00 | 0 | 0 | 0 | 115 | 200 | 84 | 71 | 0 | 250 |  | 0 | 225 | 300 | 7 | 80 | 40 | 0 | 0 | 73 | 0 | 95 | 94 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 21 | 25 | 33 | 0 | 0 | 45 | 35 | 120 | 0 | 8 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 82 | 19 | 20 | 3 | 0 | 0 | 80 | 285 | 235 | 215 | 8 | 96 | 26 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 9 | 33 | 21 | 126 | 123 | 0 | 17 | 1 | 60 | 30 | 53 | 47 | 0 | 77 | 65 | 85 | 0 | 218 | 0 | 0 | 10 | 290 | 16 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 130 | 17 | 100 | 0 | 30 | 233 | 55 | 83 | 0 | 4 | 124 | 23 | 0 | 17 | 111 | 100 | 278 | 17 |  | 907 | 0 | 290 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 22 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 130 | 0 | 414 | 53 | 0 | 64 | 0 | 42 | 0 | 4 | 70 | 480 |  | 6784 | 2978 | 9762 | 3574 | 907 | 1734 | 2559 | 630 | 80 | 126 | 126 | 26 | 0 | 101.5
15:00 | 0 | 0 | 0 | 115 | 200 | 84 | 70 | 0 | 345 |  | 0 | 225 | 275 | 7 | 80 | 40 | 0 | 0 | 155 | 0 | 100 | 94 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 15 | 33 | 33 | 0 | 0 | 85 | 35 | 120 | 0 | 0 | 204 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 83 | 25 | 20 | 2 | 0 | 0 | 80 | 310 | 200 | 215 | 8 | 87 | 29 | 5 | 0 | 43 | 0 | 0 | 52 | 21 | 9 | 33 | 21 | 126 | 126 | 0 | 17 | 1 | 60 | 30 | 50 | 47 | 0 | 83 | 65 | 85 | 0 | 216 | 0 | 0 | 10 | 295 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 131 | 13 | 100 | 0 | 30 | 233 | 55 | 85 | 0 | 3 | 124 | 17 | 0 | 52 | 107 | 100 | 281 | 17 |  | 907 | 0 | 420 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 9 | 22 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 155 | 0 | 316 | 53 | 0 | 74 | 0 | 42 | 0 | 3 | 72 | 480 |  | 7000 | 3065 | 10065 | 3816 | 907 | 1723 | 2594 | 630 | 120 | 129 | 126 | 20 | 0 | 101.52
16:00 | 0 | 0 | 0 | 115 | 200 | 84 | 71 | 0 | 346 |  | 0 | 225 | 285 | 7 | 80 | 40 | 0 | 0 | 122 | 0 | 100 | 94 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 85 | 35 | 120 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 83 | 50 | 20 | 2 | 0 | 0 | 80 | 315 | 220 | 214 | 8 | 94 | 29 | 5 | 0 | 43 | 0 | 0 | 25 | 21 | 9 | 33 | 21 | 122 | 143 | 0 | 17 | 0 | 60 | 30 | 50 | 47 | 0 | 125 | 65 | 20 | 0 | 218 | 0 | 0 | 10 | 280 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 131 | 8 | 50 | 0 | 30 | 233 | 25 | 50 | 0 | 2 | 88 | 17 | 0 | 17 | 104 | 100 | 112 | 17 |  | 907 | 0 | 415 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 12 | 22 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 158 | 0 | 339 | 70 | 0 | 74 | 0 | 42 | 0 | 2 | 72 | 480 |  | 6576 | 3031 | 9607 | 3717 | 907 | 1676 | 2291 | 630 | 120 | 132 | 122 | 12 | 0 | 101.54
17:00 | 0 | 0 | 0 | 115 | 200 | 52 | 40 | 0 | 300 |  | 0 | 225 | 270 | 7 | 97 | 40 | 0 | 0 | 70 | 0 | 100 | 94 | 40 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 85 | 35 | 120 | 0 | 0 | 204 | 0 | 138 | 0 |  | 0 | 0 | 0 | 0 | 83 | 50 | 20 | 10 | 0 | 0 | 80 | 310 | 200 | 215 | 8 | 85 | 29 | 5 | 0 | 43 | 0 | 0 | 25 | 21 | 9 | 33 | 20 | 114 | 143 | 0 | 17 | 0 | 60 | 30 | 14 | 10 | 0 | 140 | 64 | 20 | 0 | 204 | 0 | 0 | 10 | 300 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 132 | 2 | 50 | 12 | 30 | 234 | 8 | 50 | 0 | 0 | 88 | 27 | 0 | 17 | 110 | 100 | 0 | 17 |  | 907 | 0 | 350 | 0 | 16 | 120 | 0 | 0 | 0 | 10 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 9 | 10 | 14 | 0 | 0 | 12 | 17 | 16 | 22 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 130 | 0 | 392 | 70 | 0 | 76 | 0 | 48 | 0 | 2 | 109 | 480 |  | 6262 | 3089 | 9351 | 3426 | 907 | 1569 | 2350 | 630 | 120 | 231 | 114 | 4 | 0 | 101.56
18:00 | 0 | 0 | 0 | 115 | 200 | 84 | 50 | 0 | 350 |  | 0 | 225 | 270 | 7 | 97 | 40 | 0 | 0 | 185 | 0 | 100 | 94 | 150 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 21 | 33 | 33 | 42 | 0 | 85 | 35 | 120 | 0 | 20 | 205 | 0 | 139 | 0 |  | 0 | 0 | 102 | 10 | 83 | 50 | 20 | 7 | 0 | 0 | 80 | 290 | 230 | 215 | 8 | 89 | 29 | 5 | 0 | 43 | 0 | 50 | 47 | 21 | 9 | 33 | 21 | 158 | 143 | 0 | 17 | 0 | 60 | 30 | 52 | 28 | 0 | 185 | 65 | 86 | 0 | 197 | 0 | 0 | 10 | 285 | 24 | 8 | 0 | 300 | 107 | 25 | 200 | 60 | 131 | 0 | 100 | 150 | 30 | 317 | 20 | 85 | 0 | 0 | 123 | 36 | 0 | 100 | 111 | 100 | 0 | 17 |  | 907 | 0 | 380 | 0 | 59 | 170 | 0 | 0 | 5 | 0 | 40 | 0 | 29 | 70 | 0 | 0 | 0 | 50 | 42 | 97 | 0 | 0 | 0 | 45 | 19 | 22 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 17 | 140 | 0 | 383 | 70 | 0 | 90 | 0 | 80 | 0 | 0 | 109 | 480 |  | 7723 | 3564 | 11287 | 3712 | 907 | 1766 | 3309 | 630 | 120 | 685 | 158 | 0 | 0 | 101.58
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 115 | 200 | 84 | 71 | 0 | 352 |  | 0 | 225 | 255 | 7 | 97 | 44 | 0 | 0 | 185 | 0 | 100 | 94 | 150 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 85 | 35 | 120 | 0 | 25 | 204 | 0 | 140 | 0 |  | 0 | 0 | 102 | 40 | 83 | 50 | 20 | 11 | 0 | 0 | 80 | 310 | 240 | 217 | 8 | 85 | 29 | 5 | 0 | 43 | 0 | 50 | 52 | 21 | 9 | 33 | 21 | 154 | 146 | 0 | 17 | 0 | 60 | 30 | 53 | 40 | 0 | 185 | 67 | 86 | 0 | 218 | 0 | 0 | 10 | 280 | 24 | 11 | 0 | 300 | 32 | 0 | 200 | 52 | 131 | 0 | 100 | 195 | 30 | 365 | 105 | 85 | 0 | 0 | 143 | 42 | 0 | 100 | 113 | 100 | 0 | 17 |  | 907 | 0 | 410 | 0 | 99 | 200 | 0 | 0 | 5 | 0 | 40 | 0 | 36 | 100 | 0 | 0 | 0 | 50 | 35 | 97 | 0 | 0 | 4 | 52 | 30 | 22 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 99 | 154 | 0 | 380 | 70 | 0 | 90 | 0 | 101 | 0 | 0 | 109 | 560 |  | 7959 | 3913 | 11872 | 3870 | 907 | 1808 | 3580 | 710 | 120 | 723 | 154 | 0 | 0 | 101.6
19:30 | 0 | 0 | 0 | 115 | 200 | 84 | 71 | 0 | 353 |  | 0 | 225 | 280 | 7 | 97 | 51 | 0 | 0 | 185 | 0 | 100 | 94 | 150 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 85 | 35 | 120 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 102 | 40 | 84 | 50 | 20 | 14 | 0 | 0 | 80 | 310 | 240 | 215 | 8 | 91 | 29 | 5 | 0 | 43 | 0 | 50 | 52 | 21 | 9 | 33 | 21 | 156 | 145 | 0 | 17 | 0 | 60 | 30 | 53 | 40 | 0 | 195 | 66 | 86 | 0 | 218 | 0 | 0 | 10 | 295 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 131 | 0 | 100 | 153 | 30 | 365 | 105 | 85 | 0 | 0 | 143 | 54 | 0 | 100 | 113 | 100 | 0 | 17 |  | 906 | 0 | 395 | 0 | 101 | 215 | 0 | 0 | 12 | 0 | 40 | 0 | 36 | 100 | 0 | 0 | 0 | 50 | 35 | 97 | 0 | 0 | 39 | 52 | 30 | 22 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 100 | 154 | 0 | 410 | 70 | 0 | 90 | 0 | 103 | 0 | 0 | 109 | 560 |  | 7910 | 3989 | 11899 | 3866 | 906 | 1857 | 3504 | 710 | 120 | 780 | 156 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 115 | 200 | 84 | 71 | 0 | 355 |  | 0 | 225 | 265 | 7 | 97 | 51 | 0 | 0 | 190 | 0 | 100 | 94 | 150 | 17 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 87 | 35 | 120 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 102 | 40 | 84 | 50 | 20 | 17 | 0 | 0 | 80 | 310 | 240 | 216 | 8 | 85 | 29 | 5 | 0 | 43 | 0 | 50 | 52 | 21 | 9 | 33 | 21 | 156 | 145 | 0 | 17 | 0 | 60 | 30 | 53 | 44 | 0 | 195 | 67 | 86 | 0 | 218 | 0 | 0 | 10 | 285 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 131 | 0 | 100 | 120 | 30 | 365 | 105 | 85 | 0 | 0 | 144 | 54 | 0 | 100 | 113 | 100 | 0 | 17 |  | 906 | 0 | 385 | 0 | 101 | 215 | 0 | 0 | 18 | 0 | 40 | 0 | 36 | 99 | 0 | 0 | 0 | 50 | 35 | 97 | 0 | 0 | 16 | 52 | 30 | 22 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 100 | 154 | 0 | 389 | 70 | 0 | 94 | 0 | 103 | 0 | 0 | 109 | 560 |  | 7870 | 3941 | 11811 | 3857 | 906 | 1832 | 3465 | 710 | 122 | 763 | 156 | 0 | 0 | 101.62
21:00 | 0 | 0 | 0 | 115 | 200 | 84 | 71 | 0 | 356 |  | 0 | 225 | 280 | 7 | 97 | 51 | 0 | 0 | 190 | 0 | 100 | 94 | 150 | 62 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 31 | 33 | 33 | 52 | 0 | 87 | 35 | 120 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 102 | 20 | 84 | 50 | 20 | 22 | 0 | 0 | 80 | 310 | 240 | 215 | 8 | 91 | 29 | 5 | 0 | 43 | 0 | 50 | 52 | 21 | 9 | 33 | 21 | 152 | 146 | 0 | 17 | 0 | 60 | 30 | 53 | 44 | 0 | 140 | 67 | 86 | 0 | 180 | 0 | 0 | 10 | 285 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 132 | 0 | 100 | 0 | 30 | 364 | 105 | 85 | 0 | 0 | 144 | 54 | 0 | 100 | 113 | 100 | 0 | 17 |  | 906 | 0 | 360 | 0 | 103 | 215 | 0 | 0 | 18 | 0 | 40 | 0 | 36 | 110 | 0 | 0 | 0 | 50 | 39 | 97 | 0 | 0 | 16 | 52 | 30 | 22 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 100 | 157 | 0 | 411 | 70 | 0 | 94 | 0 | 105 | 0 | 0 | 109 | 580 |  | 7706 | 3980 | 11686 | 3748 | 906 | 1860 | 3401 | 730 | 122 | 767 | 152 | 0 | 0 | 101.64
22:00 | 0 | 0 | 0 | 115 | 200 | 84 | 71 | 0 | 354 |  | 0 | 225 | 290 | 7 | 97 | 51 | 0 | 0 | 160 | 0 | 100 | 70 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 31 | 33 | 33 | 52 | 0 | 88 | 35 | 120 | 0 | 25 | 204 | 0 | 138 | 0 |  | 0 | 0 | 102 | 0 | 84 | 50 | 20 | 30 | 0 | 0 | 80 | 270 | 240 | 215 | 8 | 96 | 29 | 5 | 0 | 43 | 0 | 0 | 52 | 21 | 10 | 33 | 21 | 154 | 144 | 0 | 17 | 0 | 60 | 30 | 53 | 47 | 15 | 140 | 66 | 85 | 0 | 178 | 0 | 0 | 10 | 290 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 131 | 0 | 100 | 0 | 30 | 364 | 105 | 85 | 0 | 0 | 144 | 54 | 0 | 100 | 113 | 100 | 0 | 17 |  | 907 | 0 | 350 | 0 | 109 | 218 | 0 | 0 | 12 | 0 | 40 | 0 | 37 | 110 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 16 | 52 | 29 | 22 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 100 | 160 | 0 | 368 | 70 | 0 | 94 | 0 | 105 | 0 | 0 | 109 | 580 |  | 7620 | 3844 | 11464 | 3671 | 907 | 1845 | 3410 | 730 | 123 | 624 | 154 | 0 | 0 | 101.66
23:00 | 0 | 0 | 0 | 115 | 200 | 81 | 71 | 0 | 354 |  | 0 | 225 | 288 | 7 | 97 | 51 | 0 | 0 | 160 | 0 | 94 | 40 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 89 | 35 | 120 | 0 | 25 | 204 | 0 | 140 | 0 |  | 0 | 0 | 34 | 0 | 84 | 50 | 20 | 33 | 0 | 0 | 80 | 280 | 245 | 215 | 8 | 96 | 29 | 5 | 0 | 43 | 0 | 0 | 52 | 21 | 10 | 33 | 21 | 150 | 145 | 0 | 17 | 0 | 60 | 30 | 53 | 47 | 115 | 142 | 66 | 85 | 0 | 178 | 0 | 0 | 10 | 295 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 130 | 0 | 100 | 0 | 30 | 364 | 105 | 85 | 0 | 0 | 144 | 54 | 0 | 100 | 112 | 100 | 0 | 17 |  | 907 | 0 | 355 | 0 | 107 | 180 | 0 | 0 | 11 | 0 | 33 | 0 | 37 | 110 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 16 | 52 | 0 | 22 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 156 | 0 | 397 | 70 | 0 | 94 | 0 | 104 | 0 | 0 | 109 | 580 |  | 7582 | 3696 | 11278 | 3692 | 907 | 1979 | 3208 | 730 | 124 | 488 | 150 | 0 | 0 | 101.68
24:00 | 0 | 0 | 0 | 115 | 200 | 84 | 71 | 0 | 355 |  | 0 | 225 | 280 | 7 | 97 | 51 | 0 | 0 | 155 | 0 | 100 | 40 | 64 | 30 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 89 | 35 | 120 | 0 | 0 | 204 | 0 | 138 | 0 |  | 0 | 0 | 17 | 0 | 84 | 50 | 20 | 34 | 0 | 0 | 80 | 290 | 245 | 216 | 8 | 94 | 29 | 5 | 0 | 43 | 0 | 0 | 52 | 21 | 10 | 33 | 21 | 144 | 158 | 0 | 17 | 0 | 60 | 30 | 53 | 47 | 116 | 142 | 67 | 85 | 0 | 178 | 0 | 0 | 10 | 295 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 131 | 0 | 100 | 0 | 30 | 364 | 105 | 69 | 0 | 0 | 144 | 38 | 0 | 70 | 113 | 100 | 0 | 17 |  | 907 | 0 | 355 | 0 | 103 | 140 | 0 | 0 | 11 | 0 | 16 | 0 | 38 | 110 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 25 | 0 | 22 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 165 | 0 | 396 | 72 | 0 | 94 | 0 | 104 | 0 | 0 | 109 | 580 |  | 7338 | 3603 | 10941 | 3717 | 907 | 1985 | 3005 | 730 | 124 | 329 | 144 | 0 | 0 | 101.7
KWH | 0 | 0 | 46000 | 2709000 | 4835709 | 1835818 | 1557024 | 0 | 7877000 |  | 0 | 6069000 | 6881600 | 198720 | 2214288 | 1108301 | 0 | 0 | 3273000 | 0 | 2387520 | 1910016 | 1589280 | 362093 | 0 | 0 | 0 | 1013760 | 1032280 | 1261857 | 431388 | 600000 | 642060 | 775900 | 813500 | 317064 | 0 | 1395720 | 1072000 | 2900000 | 0 | 210099 | 4863880 | 0 | 3236230 | 0 |  | 0 | 0 | 623697 | 152760 | 1541760 | 717120 | 465696 | 472320 | 0 | 0 | 1933474 | 7227000 | 5684000 | 3578000 | 200727 | 2140010 | 600264 | 201600 | 0 | 1145727 | 0 | 201480 | 846283 | 487764 | 240480 | 813900 | 504930 | 3063360 | 3540280 | 0 | 383940 | 5050 | 1426000 | 723240 | 1183800 | 1069200 | 244636 | 2841000 | 1353216 | 1916160 | 0 | 4792470 | 0 | 0 | 240840 | 7046250 | 517412 | 193048 | 0 | 5482361 | 95943 | 31956 | 4766400 | 83943 | 3119470 | 137295 | 1894080 | 576000 | 799563 | 8640000 | 1429200 | 1737468 | 0 | 33360 | 2965745 | 801918 | 0 | 1003200 | 2679600 | 2214720 | 1900200 | 432000 |  | 21863273 | 0 | 8730144 | 0 | 1466880 | 3571200 | 0 | 0 | 76380 | 6400 | 321000 | 0 | 619402 | 1046496 | 0 | 0 | 0 | 228961 | 150623 | 916920 | 0 | 0 | 77696 | 419520 | 190222 | 491280 | 196812 | 254340 | 0 | 0 | 3686600 | 0 | 0 | 0 | 0 | 0 | 0 | 2140916 | 563520 | 3923609 | 0 | 8451870 | 1399680 | 0 | 1391520 | 0 | 1419840 | 0 | 33773 | 1539552 | 12710900 |  | 166563423 | 77889329 | 244452752 | 88021084 | 21863273 | 42960382 | 61837096 | 16397500 | 2467720 | 7632859 | 3063360 | 209478 | 0
Fuel Cost | 0 | 0 | 67160 | 3982230 | 5367636.99 | 2423279.76 | 2646940.8 | 0 | 8113310 |  | 0 | 6615210 | 7638576 | 1508284.8 | 15256444.32 | 9376226.46 | 0 | 0 | 5662290 | 0 | 17978025.6 | 17419345.92 | 15638515.2 | 3338497.46 | 0 | 0 | 0 | 7400448 | 7979524.4 | 12441910.02 | 323541 | 450000 | 0 | 0 | 0 | 3066008.88 | 0 | 376844.4 | 289440 | 5249000 | 0 | 1951819.71 | 5301629.2 | 0 | 5501591 | 0 |  | 0 | 0 | 6049860.9 | 1458858 | 13413312 | 5679590.4 | 586776.96 | 1402790.4 | 0 | 0 | 2842206.78 | 5347980 | 5684000 | 3291760 | 258937.83 | 2461011.5 | 678298.32 | 282240 | 0 | 1959193.17 | 0 | 2034948 | 8082002.65 | 619460.28 | 180360 | 1424325 | 378697.5 | 22975200 | 3752696.8 | 0 | 487603.8 | 80497 | 2338640 | 1157184 | 2107164 | 1667952 | 278885.04 | 2954640 | 2665835.52 | 3659865.6 | 0 | 8290973.1 | 0 | 0 | 491313.6 | 7116712.5 | 388059 | 146716.48 | 0 | 41446649.16 | 1629112.14 | 534304.32 | 24785280 | 1403526.96 | 30695584.8 | 1604978.55 | 15436752 | 6249600 | 5636919.15 | 8035200 | 13034304 | 16419072.6 | 0 | 0 | 22421032.2 | 6984705.78 | 0 | 10011936 | 22964172 | 14750035.2 | 0 | 0 |  | 125932452.48 | 0 | 9166651.2 | 0 | 11529676.8 | 49496832 | 0 | 0 | 801226.2 | 67072 | 3344820 | 0 | 960073.1 | 10213800.96 | 0 | 0 | 0 | 2252976.24 | 1530329.68 | 8114742 | 0 | 0 | 752874.24 | 4065148.8 | 1845153.4 | 943257.6 | 305058.6 | 192535.38 | 0 | 0 | 19981372 | 0 | 0 | 0 | 0 | 0 | 0 | 3211374 | 9585475.2 | 4590622.53 | 0 | 8367351.3 | 14612659.2 | 0 | 13205524.8 | 0 | 11017958.4 | 0 | 373191.65 | 11377289.28 | 55800851 |  | 542083442.91 | 383638350.04 | 925721792.95 | 99567312.34 | 125932452.48 | 52810909.3 | 457344214.37 | 75782223 | 666284.4 | 88584529.86 | 22975200 | 2058667.2 | 0
Yesterday Day Peak | 0 | 0 | 0 | 115 | 200 | 84 | 69 | 0 | 345 |  | 0 | 225 | 312 | 7 | 80 | 40 | 0 | 0 | 73 | 0 | 100 | 94 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 0 | 0 | 44 | 35 | 120 | 0 | 8 | 218 | 0 | 146 | 0 |  | 0 | 0 | 0 | 0 | 78 | 19 | 20 | 7 | 0 | 0 | 80 | 350 | 235 | 210 | 8 | 96 | 29 | 5 | 0 | 51 | 0 | 0 | 24 | 19 | 9 | 33 | 20 | 112 | 158 | 0 | 17 | 1 | 60 | 30 | 47 | 47 | 0 | 74 | 40 | 85 | 0 | 170 | 0 | 0 | 10 | 310 | 16 | 8 | 0 | 195 | 0 | 0 | 194 | 0 | 131 | 20 | 95 | 0 | 30 | 330 | 55 | 67 | 0 | 4 | 160 | 36 | 0 | 0 | 110 | 90 | 275 | 17 |  | 915 | 0 | 330 | 0 | 32 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 130 | 0 | 383 | 53 | 0 | 35 | 0 | 42 | 0 | 5 | 36 | 510 |  | 9787 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 115 | 200 | 84 | 71 | 0 | 353 | 0 | 0 | 225 | 280 | 7 | 97 | 51 | 0 | 0 | 185 | 0 | 100 | 94 | 150 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 85 | 35 | 120 | 0 | 25 | 204 | 0 | 139 | 0 | 0 | 0 | 0 | 102 | 40 | 84 | 50 | 20 | 14 | 0 | 0 | 80 | 310 | 240 | 215 | 8 | 91 | 29 | 5 | 0 | 43 | 0 | 50 | 52 | 21 | 9 | 33 | 21 | 156 | 145 | 0 | 17 | 0 | 60 | 30 | 53 | 40 | 0 | 195 | 66 | 86 | 0 | 218 | 0 | 0 | 10 | 295 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 131 | 0 | 100 | 153 | 30 | 365 | 105 | 85 | 0 | 0 | 143 | 54 | 0 | 100 | 113 | 100 | 0 | 17 |  | 906 | 0 | 395 | 0 | 101 | 215 | 0 | 0 | 12 | 0 | 40 | 0 | 36 | 100 | 0 | 0 | 0 | 50 | 35 | 97 | 0 | 0 | 39 | 52 | 30 | 22 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 100 | 154 | 0 | 410 | 70 | 0 | 90 | 0 | 103 | 0 | 0 | 109 | 560 |  | 11899 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 115 | 200 | 100 | 78 | 0 | 360 | 0 | 0 | 225 | 305 | 7 | 100 | 55 | 0 | 0 | 200 | 0 | 100 | 40 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 85 | 35 | 120 | 0 | 25 | 221 | 0 | 140 | 0 | 0 | 0 |  | 100 | 100 | 84 | 50 | 21 | 15 | 0 | 0 | 80 | 360 | 360 | 225 | 8 | 92 | 30 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 8 | 33 | 21 | 173 | 160 | 0 | 14 | 0 | 60 | 30 | 51 | 44 | 115 | 200 | 65 | 86 | 0 | 220 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 430 | 115 | 100 | 100 | 0 | 300 | 54 | 110 | 100 | 113 | 100 | 0 | 17 |  | 915 | 16 | 410 | 0 | 115 | 225 | 0 | 0 | 30 | 60 | 40 | 0 | 33 | 110 | 0 | 0 | 0 | 50 | 42 | 100 | 0 | 0 | 50 | 52 | 34 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 100 | 220 | 0 | 414 | 70 | 200 | 113 | 100 | 100 | 0 | 0 | 113 | 620
Forecast for Day | 0 | 0 | 0 | 115 | 200 | 100 | 78 | 0 | 360 | 0 | 0 | 225 | 305 | 7 | 100 | 55 | 0 | 0 | 200 | 0 | 100 | 40 | 149 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 85 | 35 | 120 | 0 | 25 | 221 | 0 | 140 | 0 | 0 | 0 |  | 100 | 100 | 84 | 50 | 21 | 10 | 0 | 0 | 80 | 360 | 235 | 225 | 8 | 92 | 30 | 55 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 33 | 21 | 162 | 160 | 0 | 14 | 1.6 | 60 | 30 | 51 | 44 | 115 | 140 | 65 | 86 | 0 | 220 | 18 | 0 | 10 | 341 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 200 | 150 | 430 | 115 | 100 | 100 | 5 | 300 | 54 | 110 | 100 | 113 | 100 | 0 | 17 |  | 915 | 0 | 410 | 0 | 115 | 225 | 0 | 0 | 0 | 0 | 40 | 0 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 50 | 52 | 0 | 22 | 10 | 10 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 |  | 80 | 50 | 220 | 0 | 414 | 70 | 100 | 113 | 100 | 54 | 0 | 8 | 113 | 620
Generation at 08:00(Today) | 0 | 0 | 0 | 115 | 200 | 84 | 40 | 0 | 307 | 0 | 0 | 225 | 300 |  | 82 | 15 | 0 | 0 | 160 | 0 | 7 | 40 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 85 | 35 | 120 | 0 | 0 | 218 | 0 | 100 | 0 | 0 | 0 | 0 | 17 | 0 | 4 | 0 | 20 | 7 | 0 | 0 | 75 | 300 | 120 | 131 | 8 | 96 | 10 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 10 | 33 | 20 | 106 | 154 | 0 | 17 | 1 | 60 | 30 | 50 | 47 | 114 | 141 | 65 | 86 | 0 | 177 | 0 | 0 | 10 | 315 | 24 | 8 | 0 | 34 | 0 | 0 | 180 | 0 | 107 | 0 | 37 | 0 | 13 | 364 | 3 | 0 | 0 | 3 | 82 | 17 | 0 | 0 | 113 | 100 | 0 | 17 | 0 | 905 | 0 | 380 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 177 | 0 | 371 | 35 | 0 | 0 | 0 | 38 | 0 | 1 | 109 | 500 | 0
199
| Minimum Generation |  | 8442 | 7:00
| Highest Generation |  | 11899 | 19:30
| Day Peak Generation |  | 9787 | 12:00
| Evening Peak Generation |  | 11899 | 19:30
| HVDC Max Flow |  | 915 | 1:00
| HVDC EvPeak Flow |  | 906 | 19:30
| Load factor L.F |  | 85.6%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-10-08
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-10-07 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9787 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 8686 | MW
Evening Peak Generation : |  | 11899 | MW Hour : | 19:30 | Available Max Generation : |  | 14513 | MW
E.P. Demand (at gen end) : |  | 11899 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 12400 | MW
Maximum Generation : |  | 11899 | MW Hour : | 19:30 | Reserve(Generation end) |  | 2113 | MW
Total Gen. (MKWH) : |  | 244.4528 | System Load Factor : | 85.6% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -81 | MW at | 2:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-10-08
Actual : | 101.82 | Ft.(MSL) , | Rule curve : | 106.63 | Ft.( MSL )
Gas Consumed : | Total = | 1130.76 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 152378221.64
: |  | Coal : | 75782223 | Oil : | 545928744.23 | Total : | 774089188.87
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4381.8212 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1493.2074 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1338.4248 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1209.5787 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1092.969 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 881.9953 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 489.1204 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 226.9829 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 680.2579 |  |  | 0 | 0%
Total | 0 |  | 11794.3577 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Baghabari-71 MW,100 MW
3) Ghorasal Unit-1,2,3,4
4) Ashuganj unit-3,4
5) Kaptai-2,4
6) Raozan #2
7) Siddirganj-335 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Mirpur-Uttara(3rd-phase) 132 kV Ckt was under shut down from 08:41 to 17:02 for A/M.
b) Haripur-Meghnaghat 230 kV Ckt-2 was under shut down from 08:35 to 17:17 for A/M.
c) Mymensingh S/S-Mymensingh RPCL 132 kV Ckt-2 was under shut down from 09:37 to 11:21 for C/M.
d) Mymensingh-Kishoreganj 132 kV Ckt-2 was under shut down from 11:28 to 13:22 for C/M.
e) Mymensingh-Kishoreganj 132 kV Ckt-1 was under shut down from 13:26 to 14:35 for C/M.
f) Savar 132/33 kV T-3 transformer was under shut down from 12:25 17:21 for R/H maintenance at R-phase,
pole of 33 kV CB.
g) Sylhet 33 kV CB under 132/33 kV T-2 transformer was opened for preventing R/H maint. at Bus-sectionalizer.
h) Sikalbaha 132 kV Bus-A was under shut down from 09:28 to 11:40 for installing of LA.
i) Savar 132/33 kV T-1 & T-2 transformers tripped at 09:07 showing E/F relay due to flashing at isolator of 33 kV |  |  |  |  | About 25 MW power interruption occurred under Savar S/S area
capacitor bank and were switched on at 09:13. At the same time Northern P.P. got tripped. |  |  |  |  | from 09:07 to 09:13.
j) Bheramara HVDC filter 10CF!% at 400 kV was under shut down from 08:40 to 16:08.
k) Rangpur 132/33 kV T-3 transformer was under shut down from 09:20 to 18:40 for A/M.
l) Bogura 230/132 kV TO-3 transformer was under shut down from 11:34 to 20:09.
m) Rampura-Bashundhara 132 kV Ckt-1 tripped at 14:29 from Rampura end showing Dist. C,Z1 at Rampura
end and Dist. Z1, AR at Bashundhara end and was switched on at 14:48.
n) Siddhirganj S/S-Siddhirganj EGCB 335 MW ST 230 kV Ckt was shut down at 17:08 for internal maint.
o) Shahjibazar CCPP ST was force shut down at 20:23 for internal problem.
p) Kushiara CCPP 163 MW GT was synchronized at 21:44.
q) Lalbagh-Kallyanpur 132 kV Ckts 1 & 2 tripped at 05:59(08/10/2020) showing Dir. E/F, master trip at Lalbagh
end.
r) Kabirpur 132/33 kV T-1 transformer was under shut down from 06:37(08/10/20200 to 09:21 for C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-10-07 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 46000 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 115 | 2709000 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 4835709 | Machin problem.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 71 | 1557024
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 84 | 1835818
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 353 | 7877000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 6069000 | GT-1 under maintenance
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 7 | 198720 | Fuel Shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 280 | 6881600 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 97 | 2214288
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 51 | 1108301 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 12 | 362093 | Fuel Shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 431388
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 185 | 3273000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 2387520
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under Maintenance
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 94 | 1910016 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel Shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1013760
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1589280
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1032280
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1261857
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1242060 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 775900
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 813500
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 52 | 317064
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 5482361
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 95943 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 31956 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 83943 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 131 | 3119470 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 85 | 1737468 | Engine problem
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 432000 | Fuel Shortage
| Dhaka area Total |  |  |  | 5895 | 2916 | 62725319
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2900000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 210099
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 137295
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 717120
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 120 | 2467720 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4863880
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 139 | 3236230
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 623697
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 40 | 152760 | Low demand.
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1894080
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 465696
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 14 | 472320
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 84 | 1541760 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 33360
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 143 | 2965745 | Transformer O/L.
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 801918
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2214720
| Chattogram area Total |  |  |  | 2266 | 1315 | 25698400
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 1933474 | Engine problem
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 215 | 3578000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7227000 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 240 | 5684000 | STG under maintenance
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 600264 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 201600 | Gas shortage
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 1145727
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 30 | 799563 | R/H at APSCL
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 201480
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 91 | 2140010
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 153 | 576000 | Low demand.
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 487764
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 9 | 240480
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 156 | 3063360
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 813900
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 846283
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 504930 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 100 | 1003200 | Engine problem
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 2679600
| Cumilla Area Total |  |  |  | 2980 | 1759 | 33927362
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 145 | 3540280 | Machine problem & Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 383940 | Engine problem
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 0 | 0 | Man power problem due to corona effected.
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 5050
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 4766400 | Engine problem
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 105 | 1429200 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 467 | 10124870
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1426000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 723240 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 244636 | Under maint.
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 195 | 2841000 | Gas shortage & ST under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1183800
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 40 | 1069200
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 193048
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 66 | 1353216 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1916160
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 218 | 4792470
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 517412
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7046250 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 365 | 8640000
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 240840
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 1900200 | On test
| Sylhet Area Total |  |  |  | 1988 | 1453 | 34087472
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 906 | 21863273
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 101 | 1466880 | Engine problem
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 12 | 76380 | Engine problem
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 215 | 3571200
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 6400 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 395 | 8730144 | Gas shortage.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 321000
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 563520
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 70 | 1399680 | Engine problem
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Line O/L.
| Khulna Area Total |  |  |  | 2284 | 1839 | 37998477
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 100 | 1046496
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 36 | 619402
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 94 | 2140916
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 560 | 12710900
| Barisal Area Total |  |  |  | 1054 | 790 | 16517714
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 228961
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 35 | 150623
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel Shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel Shortage
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 39 | 77696
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas Shortage
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas Shortage
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 154 | 3923609 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 410 | 8451870 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 190222
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 491280
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 8 | 196812
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 254340
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 419520
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 97 | 916920
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 90 | 1391520 | Engine problem
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 1539552
| Rajshahi Area Total |  |  |  | 2183 | 1107 | 18232925
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3686600 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 103 | 1419840 | Engine problem
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 33773
| Rangpur Area Total |  |  |  | 605 | 253 | 5140213
| Total |  |  |  | 19892 | 11899 | 244452752
| Eastern Grid Total |  |  |  | 13766 | 7910 | 166563423
| Western Grid Total |  |  |  | 6126 | 3989 | 77889329
| National Grid Total |  |  |  | 19892 | 11899 | 244452752
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-10-07
| (a) ENTIRE EASTERN GRID : |  | 7698 | MW | (b) ENTIRE WESTERN GRID : |  | 3609 | MW
| i) Dhaka area |  | 4043 | MW | i) Khulna area |  | 1442 | MW
| ii) Chittagong area |  | 1183 | MW | ii) Rajshahi area |  | 1117 | MW
| iii) Comilla area |  | 1124 | MW | iii) Barisal area |  | 331 | MW
| iv) Mymensingh area |  | 876 | MW | iv) Rangpur area |  | 719 | MW
| v) Sylhet area |  | 472 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11307 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 128 | 15:00 | Sherpur | 92 | 18:30 | Jhenida | 102 | 18:30
| Munsiganj | 118 | 1:00 | Srimongal | 43 | 18:30 | Bottail | 122 | 19:30
| Sonargaon | 73 | 1:00 | Shahjibazar | 111 | 21:00 | G.K Project | 50 | 18:30
| Shyampur | 194 | 10:00 | Fenchuganj | 43 | 18:00 | Faridpur | 187 | 0.875
| Bhulta | 187 | 20:00 | Kulawara | 47 | 19:30 | Madaripur | 97 | 0.875
| Madanganj | 56 | 11:00 | Sylhet | 127 | 18:00 | Sariatpur | 64 | 22:00
| Shitalakhya | 112 | 16:00 | Chatak | 26 | 18:30 | Gopalganj | 89 | 21:00
| Rahim steel | 18 | 17:00 | Sunamganj | 38 | 18:30 | Bagerhat | 98 | 18:30
| Matuail | 83 | 12:00 | Biani Bazar | 49 | 19:30 | Mongla | 34 | 1:00
| Ghorasal | 74 | 20:00 | Comilla (S) | 158 | 18:00 | Satkhira | 110 | 0.875
| Narsingdi | 162 | 21:00 | Comilla(N) | 123 | 22:00 | Gallamari | 48 | 20:00
| Haripur (SBU) | 98 | 10:00 | Chandpur | 103 | 22:00 | Magura | 50 | 0.77083
| Ullon | 60 | 18:00 | Feni | 114 | 18:00 | Norail | 41 | 19:00
| Hasnabad | 208 | 21:00 | Chowmuhani | 178 | 18:00 | Chuadanga | 88 | 19:00
| Magbazar | 106 | 13:00 | Ashuganj | 61 | 23:00 | Barisal(N) | 41 | 0.83333
| Maniknagar | 94 | 15:00 | Daudkandi | 141 | 19:30 | Barisal (S) | 98 | 0.91667
| Bangabhaban | 36 | 10:00 | B.Baria | 153 | 22:00 | Patuakhali | 114 | 0.8125
| Narinda | 86 | 18:00 | Ramganj | 112 | 22:00 | Bhandaria | 52 | 0.8125
| Dhanmondi | 198 | 17:00 | Chaddagram | 36 | 18:00 | Borhan Uddin | 43 | 21:00
| Lalbag | 90 | 13:00 | PHP | 9 | 9:00 | Ishurdi | 57 | 18:30
| Madartek | 69 | 22:00 | Madunaghat | 59 | 13:00 | Ruppur Paromanobik | 2 | 21:00
| Dhaka University |  |  | Hathazari | 101 | 0.79167 | Natore | 105 | 21:00
| Fatullah | 41 | 0.375 | Khulshi | 208 | 0.625 | Bogra | 155 | 20:00
| Mirpur | 108 | 18:00 | Halishahar | 142 | 0.625 | Noagaon | 106 | 21:00
| Kalyanpur | 88 | 15:00 | Baraulia | 149 | 0.95833 | Rajshahi | 134 | 21:00
| Gulshan | 132 | 13:00 | Sikalbaha | 27 | 0.83333 | Rajshahi New | 10 | 21:00
| Uttara | 88 | 13:00 | Dohazari | 78 | 0.91667 | C.Nawabganj | 58 | 19:00
| Uttara New | 32 | 14:00 | Cox'sbazar | 104 | 0.77083 | Amnura | 38 | 20:00
| Kamrangirchar | 88 | 13:00 | Chandraghona | 32 | 0.77083 | Pabna | 107 | 20:00
| Savar | 139 | 12:00 | Kaptai | 4.5 | 0.75 | Shahjadpur | 98 | 20:00
| Bhasantec | 152 | 13:00 | A. Khaer Stl. | 0 | 0.041667 | Serajganj | 95 | 19:30
| Agargaon | 79 | 13:00 | Bakulia | 108 | 0.77083 | Niyamatpur | 50 | 20:00
| Satmosjid | 99 | 13:00 | Julda | 22 | 0.041667 | Joypurhat | 51 | 19:30
| Tongi | 100 | 0.5 | TK chemical | 30 | 0.77083 | Sherpur(Bogura) | 43 | 18:30
| Kabirpur | 222 | 18:00 | Modern Steel | 14 | 0.083333 | Mohastangor | 42 | 21:00
| Basundhara | 129 | 13:00 | Shahmirpur | 22.5 | 0.625 | Rangpur | 144 | 19:00
| Manikganj | 72 | 0.875 | Khagrachhari | 26 | 0.83333 | Lalmonirhat | 53 | 19:00
| Joydevpur | 129 | 18:30 | Matarbari | 37 | 0.83333 | Saidpur | 98 | 19:30
| New Tongi | 108 | 12:00 | Baroiar Hat | 48 | 0.79167 | Purbasadipur | 92 | 19:00
| Kodda | 228 | 18:00 | Rangamati | 12 | 0.75 | Thakurgaon | 74 | 20:00
| Dhamrai | 82 | 18:30 | Abul Khair 230 | 62 | 0.041667 | Palashbari | 112 | 20:00
| Rajendrapur | 98 | 19:00 | BSRM | 105 | 0.5 | Barapukuria | 46 | 19:30
| Valuka | 120 | 18:30 | GPH Ispat | 17 | 0.041667 | Panchagar | 48 | 21:00
| Tangail | 166 | 19:30 | Goalpara | 28 | 0.83333 | Joldhaka | 24 | 20:00
| Mymensing | 162 | 18:00 | Central s/s | 87 | 19:00 | Kurigram | 51 | 18:30
| Kishorganj | 131 | 20:00 | Noapara | 58 | 21:00
| Netrokona | 100 | 20:00 | Jessore | 120 | 18:30
| Jamalpur | 129 | 20:00 | Benapol | 40 | 19:30
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-10-07 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 395 | 6:00 | 388 | 11:00 | Kaliakoir | 378 | 0.70833 | 365 | 0.45833
| Bheramara | 394 | 1:00 | 390 | 11:00 | Bhulta | 388 | 0.125 | 374 | 0.45833
| Ashuganj(N) | 393 | 1:00 | 381 | 11:00 | Gopalganj | 412 | 0.70833 | 390 | 0.875
| Payra | 413 | 3:00 | 404 | 20:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 7:00 | 230 | 13:00 | Comilla (N) | 233 | 1:00 | 227 | 12:00
| Ishurdi | 235 | 17:00 | 227 | 18:30 | Hathazari | 226 | 1:00 | 222 | 7:00
| Ashuganj | 238 | 4:00 | 230 | 12:00 | Megnaghat | 230 | 24:00 | 225 | 11:00
| Serajganj | 230 | 5:00 | 226 | 1:00 | Fenchuganj | 237 | 6:00 | 231 | 18:00
| Baghabari | 239 | 9:00 | 236 | 1:00 | Siddhirganj | 231 | 6:00 | 219 | 12:00
| Barapukuria | 238 | 6:00 | 228 | 18:30 | Maniknagar | 228 | 2:00 | 218 | 11:00
| Bogra | 228 | 17:00 | 219 | 18:30 | Agargaon | 225 | 8:00 | 214 | 12:00
| Rajshahi | 229 | 17:00 | 219 | 18:30 | Barisal | 248 | 1:00 | 236 | 20:00
| Khulna South | 238 | 17:00 | 227 | 5:00 | AKSML | 223 | 1:00 | 219 | 12:00
| Rampura | 229 | 2:00 | 220 | 11:00 | BSRM | 223 | 2:00 | 219 | 12:00
| Haripur | 228 | 4:00 | 218 | 12:00 | Bibiyana | 234 | 1:00 | 231 | 11:00
| Hasnabad | 225 | 1:00 | 215 | 12:00 | Bhulta | 230 | 19:00 | 220 | 17:00
| Shyampur | 225 | 3:00 | 214 | 12:00 | Ashuganj (S) | 235 | 6:00 | 229 | 11:00
| Aminbazar | 226 | 1:00 | 216 | 12:00 | Kaliakoir | 229 | 1:00 | 220 | 11:00
| Tongi | 226 | 1:00 | 218 | 11:00 | GPH | 222 | 1:00 | 218 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 130 | 1:00 | 124 | 11:00 | Hathazari | 134 | 0.125 | 132 | 0.20833
| Munsiganj | 134 | 3:00 | 126 | 11:00 | Khulshi | 133 | 0.041667 | 129 | 0.5
| Sonargaon | 129 | 1:00 | 126 | 11:00 | Halishahar | 135 | 0.79167 | 130 | 0.25
| Shyampur | 132 | 2:00 | 125 | 12:00 | Baraulia | 134 | 0.041667 | 131 | 0.41667
| Bhulta | 125 | 5:00 | 117 | 12:00 | Sikalbaha | 136 | 20:00 | 131 | 0.29167
| Madanganj | 131 | 4:00 | 124 | 11:00 | Dohazari | 132 | 20:00 | 127 | 0.25
| Shitalakhya | 134 | 1:00 | 126 | 11:00 | Cox'sbazar | 125 | 0.375 | 116 | 0.95833
| Rahim steal | 131 | 4:00 | 124 | 12:00 | Chandraghona | 134 | 0.041667 | 132 | 0.16667
| Matuail | 130 | 1:00 | 124 | 11:00 | Kaptai | 135 | 1:00 | 132 | 0.20833
| Ghorasal | 138 | 18:00 | 136 | 1:00 | A. Khaer Stl. | 132 | 0.041667 | 130 | 5:00
| Narsinghdi | 126 | 7:00 | 120 | 12:00 | Bakulia | 134 | 0.041667 | 130 | 0.29167
| Haripur (SBU) | 132 | 6:00 | 128 | 22:00 | Julda | 135 | 0.041667 | 131 | 0.29167
| Ullon | 134 | 1:00 | 126 | 12:00 | TK Chemical | 134 | 0.041667 | 132 | 6:00
| Hasnabad | 135 | 1:00 | 127 | 12:00 | Modern Steel | 135 | 0.77083 | 131 | 0.16667
| Magbazar | 135 | 5:00 | 126 | 12:00 | Shahmirpur | 135 | 0.83333 | 131 | 0.25
| Maniknagar | 134 | 5:00 | 125 | 11:00 | Khagrachhari | 133 | 0.83333 | 130 | 0.29167
| Bangabhaban | 134 | 5:00 | 125 | 11:00 | Matarbari | 128 | 0.29167 | 120 | 0.041667
| Narinda | 134 | 5:00 | 125 | 11:00 | Baroiar Hat | 134 | 0.79167 | 129 | 0.58333
| Dhanmondi | 134 | 1:00 | 126 | 12:00 | Rangamati | 133 | 0.041667 | 131 | 8:00
| Lalbag | 135 | 5:00 | 123 | 12:00 | Goalpara S/S | 137 | 14:00 | 132 | 5:00
| Madartek | 134 | 3:00 | 126 | 11:00 | Khulna Central S/S | 137 | 0.58333 | 132 | 2:00
| Dhaka University |  |  |  |  | Noapara | 134 | 9:00 | 128 | 2:00
| Fatuiiah | 133 | 0.25 | 125 | 12:00 | Jessore | 131 | 15:00 | 124 | 18:30
| Mirpur | 135 | 3:00 | 125 | 12:00 | Benapol | 132 | 17:00 | 125 | 2:00
| Kalyanpur | 135 | 1:00 | 126 | 12:00 | Jhenida | 129 | 0.70833 | 118 | 18:30
| Gulshan | 133 | 1:00 | 125 | 12:00 | Bottail | 134 | 14:00 | 127 | 18:30
| Uttara | 134 | 1:00 | 126 | 12:00 | G.K Project | 140 | 0.58333 | 136 | 20:00
| Uttara New | 134 | 1:00 | 126 | 11:00 | Faridpur | 133 | 17:00 | 124 | 20:00
| Kamrangirchar | 133 | 3:00 | 123 | 12:00 | Madaripur | 137 | 0.70833 | 130 | 19:30
| Savar | 135 | 2:00 | 125 | 12:00 | Shariyatpur S/S | 136 | 0.33333 | 127 | 19:30
| Bhasantec | 137 | 3:00 | 127 | 12:00 | Gopalganj | 136 | 17:00 | 125 | 21:00
| Agargaon | 138 | 2:00 | 128 | 12:00 | Bagerhat | 134 | 14:00 | 125 | 19:30
| Satmosjid | 137 | 2:00 | 128 | 12:00 | Mongla | 130 | 0.41667 | 125 | 19:30
| Tongi | 135 | 0.91667 | 129 | 11:00 | Satkhira | 136 | 0.58333 | 129 | 18:30
| Kabirpur | 133 | 23:00 | 124 | 7:00 | Gallamari | 138 | 15:00 | 132 | 2:00
| Basundhara | 134 | 1:00 | 126 | 16:00 | Magura | 128 | 16:00 | 115 | 19:30
| Manikganj | 137 | 22:00 | 130 | 16:00 | Norail | 125 | 0.70833 | 111 | 19:00
| Joydevpur | 141 | 6:00 | 135 | 13:00 | Chuadanga | 123 | 16:00 | 107 | 18:30
| New Tongi | 134 | 0.875 | 127 | 11:00 | Barisal(N) | 140 | 9:00 | 132 | 20:00
| Kodda | 134 | 21:00 | 123 | 0.66667 | Barisal (S) | 139 | 0.375 | 132 | 13:00
| Dhamrai | 134 | 6:00 | 128 | 18:30 | Patuakhali(S) | 136 | 0.375 | 127 | 20:00
| Rajendrapur | 131 | 22:00 | 120 | 12:00 | Bhandaria | 130 | 9:00 | 120 | 18:30
| Valuka | 132 | 7:00 | 117 | 1:00 | Ishurdi | 138 | 14:00 | 133 | 19:00
| Tangail | 136 | 13:00 | 126 | 18:30 | Ruppur Paromanobik | 138 | 17:00 | 133 | 19:30
| Mymensing | 132 | 7:00 | 121 | 1:00 | Natore | 138 | 17:00 | 132 | 21:00
| Kishorganj | 130 | 12:00 | 123 | 1:00 | Bogra | 140 | 17:00 | 130 | 18:30
| Netrokona | 132 | 7:00 | 118 | 18:30 | Noagaon | 134 | 6:00 | 125 | 19:00
| Jamalpur | 139 | 6:00 | 131 | 18:00 | Rajshahi | 138 | 17:00 | 131 | 20:00
| Sherpur | 138 | 6:00 | 129 | 18:00 | Rajshahi New | 139 | 17:00 | 131 | 20:00
| Srimongal | 137 | 5:00 | 134 | 0.75 | C.Nawabganj | 135 | 17:00 | 129 | 12:00
| Shahjibazar | 135 | 6:00 | 131 | 0.041667 | Amnura | 136 | 17:00 | 129 | 12:00
| Fenchuganj | 135 | 6:00 | 131 | 0.70833 | Pabna | 136 | 18:00 | 131 | 20:00
| Khulawara | 134 | 6:00 | 131 | 0.66667 | Shahjadpur | 139 | 5:00 | 135 | 10:00
| Sylhet | 134 | 6:00 | 130 | 0.70833 | Serajganj | 134 | 18:00 | 130 | 21:00
| Chatak | 132 | 5:00 | 128 | 18:00 | Niyamatpur | 134 | 17:00 | 122 | 18:30
| Sunamganj | 131 | 5:00 | 127 | 0.77083 | Joypurhat | 135 | 6:00 | 124 | 20:00
| Biani Bazar | 132 | 6:00 | 128 | 0.66667 | Sherpur(Bogura) | 138 | 17:00 | 130 | 20:00
| Comilla(s) | 130 | 6:00 | 120 | 18:00 | Mohastangor | 137 | 17:00 | 126 | 21:00
| Comilla(n) | 136 | 10:00 | 132 | 13:00 | Rangpur | 133 | 6:00 | 119 | 18:30
| Chandpur | 140 | 19:00 | 130 | 16:00 | Lalmonirhat | 132 | 6:00 | 117 | 18:30
| Feni | 135 | 18:00 | 129 | 16:00 | Saidpur | 133 | 17:00 | 120 | 18:30
| Chowmuhani | 133 | 18:30 | 130 | 8:00 | Purbasadipur | 131 | 6:00 | 117 | 18:30
| Ashuganj | 135 | 12:00 | 132 | 2:00 | Thakurgaon | 129 | 6:00 | 118 | 18:00
| Daudkandi | 129 | 18:00 | 124 | 12:00 | Palashbari | 134 | 17:00 | 124 | 1:00
| B.Baria | 133 | 7:00 | 128 | 22:00 | Barapukuria | 138 | 17:00 | 128 | 18:30
| Ramganj | 130 | 18:30 | 121 | 23:00 | Panchagar | 127 | 7:00 | 108 | 18:30
| Chaddagram | 136 | 17:00 | 131 | 4:00 | Joldhaka | 132 | 6:00 | 115 | 18:30
| PHP | 133 | 9:00 | 129 | 12:00 | Kurigram | 130 | 17:00 | 115 | 18:30
| Madanhat | 136 | 19:00 | 132 | 5:00

## L-Curve
Date | 2020-10-07
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 158 | 7338 | 3603 | 10941 |  |  |  | QF-LDC-11
0:30 | 111.5 | 7321.5 | 3449 | 10770.5 | Date: | 2020-10-07
1:00 | 65 | 7305 | 3295 | 10600
1:30 | 73 | 7182.5 | 3198.5 | 10381
2:00 | 81 | 7060 | 3102 | 10162
2:30 | 40.5 | 6977 | 3065 | 10042 | [5 empty] | Gen. at Eve. Peak | 11899 | 9500 MW (19:30 )
3:00 | 0 | 6894 | 3028 | 9922 | [6 empty] | 19:30
3:30 | 21 | 6777 | 3002.5 | 9779.5 | [5 empty] | Gen. at Day Peak | 9787 | 7952.5 MW (12:00 )
4:00 | 42 | 6660 | 2977 | 9637 | [6 empty] | 12:00
4:30 | 64.5 | 6569.5 | 2967 | 9536.5 | [5 empty] | Highest Generation | 11899
5:00 | 87 | 6479 | 2957 | 9436 | [6 empty] | 19:30
5:30 | 175 | 6223.5 | 2915.5 | 9139
6:00 | 263 | 5968 | 2874 | 8842
6:30 | 276.5 | 5792.5 | 2849.5 | 8642
7:00 | 290 | 5617 | 2825 | 8442
7:30 | 273.5 | 5736 | 2825.5 | 8561.5
8:00 | 257 | 5855 | 2826 | 8681
8:30 | 311.5 | 5972.5 | 2848 | 8820.5
9:00 | 366 | 6090 | 2870 | 8960
9:30 | 368 | 6253.5 | 2871 | 9124.5
10:00 | 370 | 6417 | 2872 | 9289
10:30 | 336.5 | 6548 | 2848.5 | 9396.5
11:00 | 303 | 6679 | 2825 | 9504
11:30 | 258 | 6790 | 2855.5 | 9645.5
12:00 | 213 | 6901 | 2886 | 9787
12:30 | 165.5 | 6911.5 | 2882 | 9793.5
13:00 | 118 | 6922 | 2878 | 9800
13:30 | 219 | 6853 | 2928 | 9781
14:00 | 320 | 6784 | 2978 | 9762
14:30 | 364 | 6892 | 3021.5 | 9913.5
15:00 | 408 | 7000 | 3065 | 10065
15:30 | 456.5 | 6788 | 3048 | 9836
16:00 | 505 | 6576 | 3031 | 9607
16:30 | 552.5 | 6419 | 3060 | 9479
17:00 | 600 | 6262 | 3089 | 9351
17:30 | 390.5 | 6992.5 | 3326.5 | 10319
18:00 | 181 | 7723 | 3564 | 11287
18:30 | 152.5 | 7841 | 3738.5 | 11579.5
19:00 | 124 | 7959 | 3913 | 11872
19:30 | 125 | 7910 | 3989 | 11899
20:00 | 98 | 7870 | 3941 | 11811 |  |  |  | Executive Engineer
20:30 | 123 | 7788 | 3960.5 | 11748.5 |  |  |  | Network Operation Division
21:00 | 148 | 7706 | 3980 | 11686
21:30 | 140 | 7663 | 3912 | 11575
22:00 | 132 | 7620 | 3844 | 11464 |  |  |  |  | Page 6 of 7
22:30 | 144 | 7601 | 3770 | 11371
23:00 | 156 | 7582 | 3696 | 11278
23:30 | 157 | 7460 | 3649.5 | 11109.5
24:00 | 158 | 7338 | 3603 | 10941
9500 MW (19:30 )
7952.5 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-10-07 |  | Energy | 244452752
[10 empty] | 2020-10-07 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3717 | 907 | 1985 | 3208 | 730 | 124 | 329 | 0 | 144
0:30 | 3600.5 | 911 | 1932.5 | 3060 | 725 | 118 | 384 | 0 | 141 | Date: | 2020-10-07
1:00 | 3484 | 915 | 1880 | 2912 | 720 | 112 | 439 | 0 | 138
1:30 | 3497.5 | 915 | 1932.5 | 2721 | 720 | 112 | 346 | 0 | 137 | [7 empty] | Total Energy | 244.4528 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 3511 | 915 | 1985 | 2530 | 720 | 112 | 253 | 0 | 136 | [7 empty] | Energy not Served | 0
2:30 | 3532 | 915 | 1996 | 2399 | 700 | 111 | 253 | 0 | 136 | [7 empty] | Energy Requirement | 244.4528
3:00 | 3553 | 915 | 2007 | 2268 | 680 | 110 | 253 | 0 | 136
3:30 | 3554.5 | 915 | 2010 | 2124.5 | 680 | 110 | 251.5 | 0 | 134 | [6 empty] | Shortage
4:00 | 3556 | 915 | 2013 | 1981 | 680 | 110 | 250 | 0 | 132
4:30 | 3563.5 | 915 | 2035.5 | 1891.5 | 680 | 110 | 209 | 0 | 132
5:00 | 3571 | 915 | 2058 | 1802 | 680 | 110 | 168 | 0 | 132
5:30 | 3488.5 | 915 | 1921.5 | 1734 | 680 | 110 | 168 | 0 | 122
6:00 | 3406 | 915 | 1785 | 1666 | 680 | 110 | 168 | 0 | 112
6:30 | 3396 | 915 | 1767 | 1536.5 | 680 | 92.5 | 144 | 0 | 108 |  |  |  |  | Coal
7:00 | 3386 | 915 | 1749 | 1407 | 680 | 75 | 120 | 0 | 104
7:30 | 3435.5 | 915 | 1722.5 | 1499 | 680 | 75.5 | 120 | 0 | 104 |  |  |  | Oil |  |  |  | ,
8:00 | 3485 | 915 | 1696 | 1591 | 680 | 76 | 120 | 0 | 104
8:30 | 3476.5 | 914.5 | 1652 | 1784 | 670 | 76 | 128 | 0 | 102
9:00 | 3468 | 914 | 1608 | 1977 | 660 | 76 | 136 | 0 | 100
9:30 | 3503 | 914.5 | 1613.5 | 2093 | 660 | 77 | 136 | 0 | 104
10:00 | 3538 | 915 | 1619 | 2209 | 660 | 78 | 136 | 0 | 108
10:30 | 3591 | 914.5 | 1659 | 2225 | 660 | 78.5 | 133 | 0 | 108
11:00 | 3644 | 914 | 1699 | 2241 | 660 | 79 | 130 | 0 | 108
11:30 | 3700.5 | 914.5 | 1754.5 | 2272.5 | 660 | 79 | 125 | 0 | 110
12:00 | 3757 | 915 | 1810 | 2304 | 660 | 79 | 120 | 0 | 112
12:30 | 3741.5 | 915 | 1759.5 | 2372 | 660 | 79.5 | 120 | 0 | 116
13:00 | 3726 | 915 | 1709 | 2440 | 660 | 80 | 120 | 0 | 120
13:30 | 3726 | 915 | 1709 | 2440 | 660 | 80 | 120 | 0 | 120
14:00 | 3726 | 915 | 1709 | 2440 | 660 | 80 | 120 | 0 | 120
14:30 | 3771 | 911 | 1716 | 2517 | 645 | 100 | 124.5 | 0 | 123
15:00 | 3816 | 907 | 1723 | 2594 | 630 | 120 | 129 | 0 | 126
15:30 | 3766.5 | 907 | 1699.5 | 2442.5 | 630 | 120 | 130.5 | 0 | 124
16:00 | 3717 | 907 | 1676 | 2291 | 630 | 120 | 132 | 0 | 122
16:30 | 3571.5 | 907 | 1622.5 | 2320.5 | 630 | 120 | 181.5 | 0 | 118
17:00 | 3426 | 907 | 1569 | 2350 | 630 | 120 | 231 | 0 | 114
17:30 | 3569 | 907 | 1667.5 | 2829.5 | 630 | 120 | 458 | 0 | 136
18:00 | 3712 | 907 | 1766 | 3309 | 630 | 120 | 685 | 0 | 158
18:30 | 3791 | 907 | 1787 | 3444.5 | 670 | 120 | 704 | 0 | 156
19:00 | 3870 | 907 | 1808 | 3580 | 710 | 120 | 723 | 0 | 154
19:30 | 3866 | 906 | 1857 | 3504 | 710 | 120 | 780 | 0 | 156
20:00 | 3857 | 906 | 1832 | 3465 | 710 | 122 | 763 | 0 | 156
20:30 | 3802.5 | 906 | 1846 | 3433 | 720 | 122 | 765 | 0 | 154
21:00 | 3748 | 906 | 1860 | 3401 | 730 | 122 | 767 | 0 | 152
21:30 | 3709.5 | 906.5 | 1852.5 | 3405.5 | 730 | 122.5 | 695.5 | 0 | 153
22:00 | 3671 | 907 | 1845 | 3410 | 730 | 123 | 624 | 0 | 154
22:30 | 3681.5 | 907 | 1912 | 3309 | 730 | 123.5 | 556 | 0 | 152
23:00 | 3692 | 907 | 1979 | 3208 | 730 | 124 | 488 | 0 | 150
23:30 | 3704.5 | 907 | 1982 | 3208 | 730 | 124 | 408.5 | 0 | 147 | Max Temp. in Dhaka |  | 34.4° C
24:00 | 3717 | 907 | 1985 | 3208 | 730 | 124 | 329 | 0 | 144
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
Note on W13: Author:

## Generation
g | 2020-10-07
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 42 | 42 | 40 | 40 | 40 | 40 | 40 | 41 | 41 | 43 | 44 | 44 | 45 | 45 | 85 | 85 | 85 | 85 |  | 85 | 85 | 87 | 87 | 88 | 89 | 89 | 1395720
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 1072000
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2900000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [8 empty] | 1 | 7 | 8 | 8 | 8 | 8 |  |  |  | 20 |  | 25 | 25 | 25 | 25 | 25 | 25 |  | 210099
| Teknaf 20MW PP (Solartech) | [6 empty] | 5 | 11 | 15 | 18 | 19 | 20 | 17 | 17 | 13 | 8 | 2 | [9 empty] | 137295
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 204 | 204 | 207 | 204 | 218 | 204 | 204 | 204 | 204 | 204 | 205 |  | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 4863880
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 139 | 139 | 140 | 140 | 139 | 138 | 104 | 140 | 104 | 104 | 139 | 146 | 139 | 139 | 140 | 139 | 138 | 139 |  | 140 | 139 | 139 | 139 | 138 | 140 | 138 | 3236230
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 6 | [16 empty] | 102 |  | 102 | 102 | 102 | 102 | 102 | 34 | 17 | 623697
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [17 empty] | 50 |  | 50 | 50 | 50 | 50 |  |  | 0 | 201480
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 145 | 145 | 145 | 145 | 145 | 76 | 75 | 74 | 70 | 70 | 73 | 73 | 115 | 73 | 155 | 122 | 70 | 185 |  | 185 | 185 | 190 | 190 | 160 | 160 | 155 | 3273000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 300 | 245 | 195 | 145 | 65 | 65 | 30 | 32 | 100 | 195 | 195 | 195 | 242 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 5482361
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | [25 empty] | 0 | 46000
23 | Ghorasal TPP Unit-5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2709000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4835709
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1933474
32 | Ashuganj 50 MW PP | 29 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 23 | 5 | 29 | 29 | 26 | 26 | 29 | 29 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 600264
33 | Ashuganj 225 MW CCPP | 32 | 36 | 44 | 44 | 43 | 43 | 51 | 67 | 133 | 128 | 214 | 210 | 212 | 215 | 215 | 214 | 215 | 215 |  | 217 | 215 | 216 | 215 | 215 | 215 | 216 | 3578000
34 | Ashuganj 450 MW CCPP(South) | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 200 | 220 | 200 | 230 |  | 240 | 240 | 240 | 240 | 240 | 245 | 245 | 5684000
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 275 | 275 | 290 | 280 | 350 | 325 | 285 | 310 | 315 | 310 | 290 |  | 310 | 310 | 310 | 310 | 270 | 280 | 290 | 7227000
35 | Ashuganj 55 MW PP (Precision) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 201600
36 | Chandpur 150 MW CCPP | 87 | 90 | 88 | 90 | 95 | 86 | 96 | 92 | 90 | 97 | 96 | 96 | 87 | 96 | 87 | 94 | 85 | 89 |  | 85 | 91 | 85 | 91 | 96 | 96 | 94 | 2140010
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 300 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 6069000
41 | Haripur 360MW CCPP(HPL) | 357 | 356 | 356 | 356 | 354 | 302 | 303 | 303 | 250 | 280 | 330 | 345 | 300 | 250 | 345 | 346 | 300 | 350 |  | 352 | 353 | 355 | 356 | 354 | 354 | 355 | 7877000
42 | RPCL 210MW CCPP | 160 | 158 | 158 | 158 | 158 | 158 | 158 | 161 | 162 | 159 | 159 | 158 | 141 | 123 | 126 | 143 | 143 | 143 |  | 146 | 145 | 145 | 146 | 144 | 145 | 158 | 3540280
43
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1426000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 723240
46 | Shajibazar 330 MW CCPP | 140 | 142 | 142 | 140 | 142 | 142 | 141 | 140 | 140 | 70 | 71 | 74 | 76 | 77 | 83 | 125 | 140 | 185 |  | 185 | 195 | 195 | 140 | 140 | 142 | 142 | 2841000
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 62 | 62 | 62 | 62 | 52 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 65 | 65 | 65 | 64 | 65 |  | 67 | 66 | 67 | 67 | 66 | 66 | 67 | 1353216
48 | Shahjibazar 86MW PP (Shahjibazar) | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 84 | 84 | 40 | 84 | 85 | 85 | 85 | 85 | 20 | 20 | 86 |  | 86 | 86 | 86 | 86 | 85 | 85 | 85 | 1916160
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 218 | 218 | 218 | 218 | 218 | 185 | 184 | 184 | 151 | 151 | 165 | 170 | 211 | 218 | 216 | 218 | 204 | 197 |  | 218 | 218 | 218 | 180 | 178 | 178 | 178 | 4792470
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 240840
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 2 | 2 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 193048
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 47 | 47 | 47 | 47 | 53 | 50 | 50 | 14 | 52 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1183800
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 8 | 16 | 16 | 16 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 517412
57 | Bibiana-II 341 MW CCPP (Summit) | 260 | 270 | 280 | 280 | 290 | 280 | 290 | 300 | 280 | 290 | 280 | 310 | 300 | 290 | 295 | 280 | 300 | 285 |  | 280 | 295 | 285 | 285 | 290 | 295 | 295 | 7046250
| Bibiyana South 400 MW | [9 empty] | 270 | 280 | 275 | 282 | 278 | 281 | 112 | [10 empty] | 1900200
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 55 | 17 | 23 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1261857
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 465696
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 |  |  |  | 19 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 431388
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 383940
63 | Impoprt (Tripura) | 138 | 136 | 136 | 132 | 132 | 112 | 104 | 104 | 100 | 108 | 108 | 112 | 120 | 126 | 126 | 122 | 114 | 158 |  | 154 | 156 | 156 | 152 | 154 | 150 | 144 | 3063360
64 | Malancha, Ctg. EPZ (United) | 35 | 36 | 36 | 38 | 41 | 39 | 36 | 4 | 7 | 6 | 5 | 7 | 5 | 3 | 2 | 2 | 10 | 7 |  | 11 | 14 | 17 | 22 | 30 | 33 | 34 | 472320
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 19 | 19 | 19 | 19 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 487764
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 240480
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 813900
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 19 | 20 | 20 | 21 | 21 | 21 | 20 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504930
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 31 | 31 | 31 | 10 | 20 | 30 | 30 | 30 | 22 | 22 | 22 | 21 | 15 | 29 | 29 | 21 |  | 30 | 30 | 30 | 31 | 31 | 31 | 31 | 642060
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 33 | 33 | 23 | 25 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 775900
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 16 | 16 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 813500
73 | Ghorashal 108MW PP (Regent) | 51 | 70 | 80 | 79 | 79 | 79 | 80 | 81 | 81 | 77 | 80 | 84 | 84 | 84 | 84 | 84 | 52 | 84 |  | 84 | 84 | 84 | 84 | 84 | 81 | 84 | 1835818
| Feni Lanka Power | 78 | 17 | 17 | 17 |  |  |  | 11 | 17 | 17 |  |  | 17 | 17 | 52 | 17 | 17 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 70 | 1003200
| Chowmuhani 113 MW | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 109 | 109 | 111 | 107 | 110 | 110 | 111 | 107 | 104 | 110 | 111 |  | 113 | 113 | 113 | 113 | 113 | 112 | 113 | 2679600
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 100 | 100 | 100 | 100 | 95 | 100 | 100 | 100 | 100 | 100 | 100 | 92 | 95 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 94 | 100 | 2387520
78 | Gazipur 52 MW PP | [9 empty] | 27 | [7 empty] | 42 |  | 52 | 52 | 52 | 52 | 52 |  | 0 | 317064
79 | Kodda 150MW PP | 150 | 85 | 85 | 82 | 48 | 48 |  |  | 16 | 16 | 10 | [5 empty] | 40 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 64 | 1589280
80 | Jamalpur 95 MW PP(Powerpac) | [25 empty] | 0 | 0
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 24 | 24 | 24 | 24 | 16 |  |  | 6 | 23 | 24 | 24 | 42 | 52 | 52 | 25 | 25 | 47 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 846283
| Gazipur 100 MW PP | 83 | 70 | 34 | 34 | 16 | 56 | 85 | 85 | 85 | 85 | 85 | 67 | 85 | 83 | 85 | 50 | 50 | 85 |  | 85 | 85 | 85 | 85 | 85 | 85 | 69 | 1737468
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 4 | 4 | 5 | 4 | 5 | 4 | 3 | 2 | 0 | [9 empty] | 33360
| Jodiac Power | 36 | 36 | 17 | 17 | 17 | 17 | 17 | 21 | 35 | 31 | 36 | 36 | 36 | 23 | 17 | 17 | 27 | 36 |  | 42 | 54 | 54 | 54 | 54 | 54 | 38 | 801918
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | 96 | 96 | 96 | 96 | 96 | 86 | 87 | 97 | 97 | 94 | 80 | 80 | 80 | 80 | 80 | 80 | 97 | 97 |  | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 2214288
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [17 empty] | 10 |  | 12 | 12 | 17 | 62 | 100 | 100 | 30 | 362093
86 | Meghnaghat CCPP(Summit) | 275 | 290 | 280 | 300 | 310 | 285 | 305 | 295 | 290 | 310 | 310 | 312 | 275 | 300 | 275 | 285 | 270 | 270 |  | 255 | 280 | 265 | 280 | 290 | 288 | 280 | 6881600
87 | Meghnaghat 100 MW(IEL) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 198720
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 432000
88 | Ghorashal 78.5 MW PP(MAX) |  | 60 | 73 | 73 | 73 | 73 | 73 | 72 | 71 | 70 | 69 | 69 | 69 | 71 | 70 | 71 | 40 | 50 |  | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 1557024
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 20 | [16 empty] | 10 |  | 40 | 40 | 40 | 20 |  |  | 0 | 152760
92 | Fenchuganj 44MW (Energyprima) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 43 | 43 | 47 | 47 | 47 | 47 | 47 | 10 | 28 |  | 40 | 40 | 44 | 44 | 47 | 47 | 47 | 1069200
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1145727
94 | Gagnagar 102 MW PP (Digital Power) | 94 | 94 | 94 | 68 | 68 | 40 | 32 | 40 | 50 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 |  | 94 | 94 | 94 | 94 | 70 | 40 | 40 | 1910016
95 | Patenga 50MW PP (Baraka) | 50 | 27 | 19 | 19 |  |  |  |  | 13 | 19 | 19 | 19 | 19 | 19 | 25 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 717120
96 | Chattogram 108 MW PP (ECPV) | 84 | 45 | 12 | 12 | 12 | 12 | 12 | 12 | 78 | 84 | 84 | 78 | 65 | 82 | 83 | 83 | 83 | 83 |  | 83 | 84 | 84 | 84 | 84 | 84 | 84 | 1541760
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | 50 | 52 | 52 | 52 | 52 | 52 | 30 | 30 | 46 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 44 | 51 | 51 | 51 | 51 | 51 | 51 | 1108301
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 17 | 17 | 17 | 17 | 17 | 35 | 25 | 35 | 55 | 55 | 55 | 55 | 35 | 35 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1032280
101 | Kushiara 163 MW CCPP (KP) | [23 empty] | 15 | 115 | 116 | 244636
102 | Sarishabari 3 MW Solar Plant | [7 empty] | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | [9 empty] | 5050
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 17 | 17 | 17 | 17 | 17 | 17 | 25 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 17 | 17 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1013760
104 | Keranigonj 300 MW PP (APR) | [17 empty] | 107 |  | 32 | [5 empty] | 0 | 95943
105 | Bramhangoan 100 MW PP (Aggreko) | [17 empty] | 25 | [7 empty] | 0 | 31956
106 | Mymensingh 200 MW PP (United) | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 170 | 178 | 200 | 200 | 194 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4766400
112 | Aurahati 100MW PP (Aggreko) | [17 empty] | 60 |  | 52 | [5 empty] | 0 | 83943
114 | Kodda 149 MW PP Unit-1 (Summit) | 124 | 120 | 132 | 130 | 130 | 131 | 114 | 119 | 131 | 130 | 131 | 131 | 130 | 130 | 131 | 131 | 132 | 131 |  | 131 | 131 | 131 | 132 | 131 | 130 | 131 | 3119470
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 70 | 30 | 30 | 30 | 10 | 60 | 60 | 60 | 94 | 95 | 100 | 100 | 100 | 50 | 50 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1894080
116 | Chandpur 200MW (Desh energy) | [16 empty] | 12 | 150 |  | 195 | 153 | 120 |  |  |  | 0 | 576000
117 | Ashuganj 150MW PP (Midland) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 799563
118 | Bibiyana-III 400 MW CCPP | 430 | 428 | 428 | 426 | 426 | 429 | 427 | 430 | 426 | 325 | 320 | 330 | 330 | 233 | 233 | 233 | 234 | 317 |  | 365 | 365 | 365 | 364 | 364 | 364 | 364 | 8640000
| Jamalpur 115 MW PP (United) | 85 | 85 | 55 | 55 | 35 | 35 | 8 | 8 | 8 | 8 | 43 | 55 | 55 | 55 | 55 | 25 | 8 | 20 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1429200
| Anwara 300 MW PP (United) | 180 | 180 | 180 | 125 | 106 | 51 | 34 | 87 | 88 | 88 | 105 | 160 | 160 | 124 | 124 | 88 | 88 | 123 |  | 143 | 143 | 144 | 144 | 144 | 144 | 144 | 2965745
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 70 | 70 | 40 | 30 | 90 | 100 | 100 | 90 | 90 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2214720
120 | Eastern Zone Total | 7305 | 7060 | 6894 | 6660 | 6479 | 5968 | 5617 | 5855 | 6090 | 6417 | 6679 | 6901 | 6922 | 6784 | 7000 | 6576 | 6262 | 7723 |  | 7959 | 7910 | 7870 | 7706 | 7620 | 7582 | 7338 | 166563423
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 115 | 90 | 66 | 32 | 16 | 16 |  | 2 | 28 | 32 | 32 | 32 | 99 | 99 | 99 | 16 | 16 | 59 |  | 99 | 101 | 101 | 103 | 109 | 107 | 103 | 1466880
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [17 empty] | 5 |  | 5 | 12 | 18 | 18 | 12 | 11 | 11 | 76380
| Khulna 225 MW CCPP | 185 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 170 |  | 200 | 215 | 215 | 215 | 218 | 180 | 140 | 3571200
129 | Rupsha 105 MW PP (Orion rupsha) | 54 | 54 | 54 | 54 | 54 | 54 | 17 | 27 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 72 | 1399680
130
131
132
133
| Barisal 110 MW PP (Summit ) | 80 | 80 | 64 | 32 | 32 | 16 | [11 empty] | 70 |  | 100 | 100 | 99 | 110 | 110 | 110 | 110 | 1046496
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 90 | 90 | 91 | 90 | 89 | 89 | 90 | 89 | 88 | 86 | 85 | 85 | 83 | 87 | 86 | 88 | 89 | 91 |  | 94 | 94 | 91 | 91 | 90 | 90 | 90 | 2140916
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 30 | 29 | 28 | 26 | 26 | 23 | 20 | 14 | 14 | 15 | 15 | 19 | 19 | 21 | 22 | 28 | 21 | 29 |  | 36 | 36 | 36 | 36 | 37 | 37 | 38 | 619402
141 | Noapara 100 MW PP (Bangla Trac) | 30 | [16 empty] | 17 |  | 99 | 100 | 100 | 100 | 100 |  | 0 | 563520
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | [16 empty] | 40 |  | 40 | 40 | 40 | 40 | 40 | 33 | 16 | 321000
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 10 | [9 empty] | 6400
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 915 | 915 | 915 | 915 | 915 | 915 | 915 | 915 | 914 | 915 | 914 | 915 | 915 | 907 | 907 | 907 | 907 | 907 |  | 907 | 906 | 906 | 906 | 907 | 907 | 907 | 21863273
147 | Bheramara 410 MW CCPP | 290 | 315 | 330 | 340 | 350 | 375 | 400 | 410 | 410 | 370 | 325 | 330 | 290 | 290 | 420 | 415 | 350 | 380 |  | 410 | 395 | 385 | 360 | 350 | 355 | 355 | 8730144
148 | Payra 1320 MW | 570 | 570 | 530 | 530 | 530 | 530 | 530 | 530 | 510 | 510 | 510 | 510 | 510 | 480 | 480 | 480 | 480 | 480 |  | 560 | 560 | 560 | 580 | 580 | 580 | 580 | 12710900
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3686600
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [16 empty] | 9 | 50 |  | 50 | 50 | 50 | 50 |  |  | 0 | 228961
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 140 | 140 | 160 | 160 | 160 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 155 | 158 | 130 | 140 |  | 154 | 154 | 154 | 157 | 160 | 156 | 165 | 3923609
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 310 | 327 | 316 | 324 | 359 | 305 | 335 | 318 | 304 | 336 | 337 | 383 | 341 | 414 | 316 | 339 | 392 | 383 |  | 380 | 410 | 389 | 411 | 368 | 397 | 396 | 8451870
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 10 | 42 |  | 35 | 35 | 35 | 39 |  |  |  | 150623
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 491280
163 | Bogura 20 MW PP (Energyprima) | 10 | 10 | 10 | 10 | 10 | 8 | 10 | 10 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 196812
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 11 | 11 | 9 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 254340
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [26 empty] | 0
167 | Katakhali 50 MW Peaking PP | [16 empty] | 12 |  |  | 4 | 39 | 16 | 16 | 16 | 16 |  | 77696
168 | Santahar 50 MW Peaking PP | [13 empty] | 6 | 9 | 12 | 16 | 19 |  | 30 | 30 | 30 | 30 | 29 |  | 0 | 190222
169 | Natore 52 MW PP (Rajlanka) | 25 | [13 empty] | 16 | 17 | 17 | 45 |  | 52 | 52 | 52 | 52 | 52 | 52 | 25 | 419520
170 | Chapainawabganj 100 MW Peaking PP | 98 | 48 | 48 | 48 | [12 empty] | 14 | 97 |  | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 916920
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 35 | 35 | 35 | 35 |  |  | 28 | 35 | 35 | 35 | 42 | 64 | 74 | 74 | 76 | 90 |  | 90 | 90 | 94 | 94 | 94 | 94 | 94 | 1391520
172 | Confidence Power Bogura Unit-1 113 MW | 54 | 54 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 70 | 72 | 72 | 109 | 109 |  | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 1539552
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 41 | 42 | 42 | 42 | 42 | 42 | 42 | 41 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 48 | 80 |  | 101 | 103 | 103 | 105 | 105 | 104 | 104 | 1419840
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 7 | 4 | 3 | 2 | 2 | [9 empty] | 33773
178
178