## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-10-13 | Tuesday
|  |  | Date (day): | 2020-10-13 |  | Tuesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14144.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15017 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-10-12 | 2020-10-13 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 170 | 170 | 170 | 170 | 10 |  | Gas shortage
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 115 | 115 | 115 | 75 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 200 | 200 |  |  | Gas shortage
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 |  | 78 | Engine problem
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 42 | 42 | 41 | 41 |  | 67 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under S/D for dust in gas.
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 350 | 352 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 450 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 16 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 260 | 250 | 305 | 305
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 80 | 80 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 17 | 26 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 94 | 175 | 150 | 190
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 7 | 7 | 7 | 93 |  | Fuel shortage
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 7 | 16 | 16 | 86 |  | Fuel shortage
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 53 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 145 | 150 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 35 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 54 | 54 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 40 | 51 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 285 | 300 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 180 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 25 | 93 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 93 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 132 | 132 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 102 | 102 | 100 | 100
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 17 | 104 | 104 | 0
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 2946 | 3349 | 3541 | 3871 | 528 | 1307
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 115 | 115 | 120 | 120 | 60 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 16 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 45 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 121 | 123 | 123 | 123 | 107 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 205 | 204 | 221 | 221
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 139 | 138 | 145 | 145
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 7 | 9 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 47 | 0 | 102 | 102
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 40 | 100 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 21 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 0 | 10 | 5
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 82 | 84 | 84 |  | 24 | Engine problem
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 179 | 180 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 18 | 54 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 1184 | 1300 | 1790 | 1760 | 347 | 122
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 80 | 80 | 80 | 49 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 0 | 0 | 0 |  | 134 | Engine problem
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 213 | 214 | 225 | 225 |  |  | FGMO
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 275 | 360 | 360 |  |  | FGMO
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 345 | 360 | 360
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 16 | 16 | 30 | 30 | 15 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 30 | 46 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 50 | 0 | 50
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 86 | 95 | 95 |  | 68 | ST under shut down
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 1 | 190 | 200 | 200
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 10 | 10
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 100 | 158 | 162 | 173
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 52 | 52 | 52
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 21 | 21 | 21
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 150 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 100 | 100 | 100 |  | 14 | Engine problem
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 102 | 111 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1394 | 2018 | 2077 | 2338 | 436 | 216
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 151 | 156 | 160 | 160 | 42 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 17 | 17 |  | 5 | Engine problem
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 48 | 48 | 49 | 49 |  | 46 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 130 | 190 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 16 | 105 | 115 | 115
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 364 | 516 | 542.6 | 541 | 42 | 51
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 83 | 87 | 90 | 90
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 43 | 43 | 43 | 43 |  | 35 | Unit-4 under shut down
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 115 | 110 | 115 | 115 |  | 48 | STG under maint.
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 100 | 100 | 100 | 110 |  | 110 | GT-2 S/D & ST Under maint.
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 49 | 46 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 46 | 41 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 63 | 65 | 65 | 65 |  |  | FGMO
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 87 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 132 | 132 | 132 | 132
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 25 | 25
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 280 | 341 | 341 |  |  | FGMO
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 412 | 419 | 430 | 430
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1459 | 1455 | 1561 | 1571 | 0 | 193
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 892 | 892 | 905 | 905
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 99 | 96 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 9 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 210 | 200 | 220 |  | 230 | ST Under maint.
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 175 | 235 | 410 | 410
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 40 | 40 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 98 | 50 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 35 | 90 | 105
| 108 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1343 | 1615 | 1910 | 2101 | 0 | 230
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 32 | 110 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 25 | 38 | 33 | 33
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 88 | 92 | 92
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 440 | 600 | 560 | 560
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 497 | 836 | 795 | 795 | 0 | 194
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 65 | 65 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 70 | 70 | 30 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 35 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 36 | 50 | 50
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 179 | 183 | 225 | 225 | 220 |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 189 | 187 | 220 | 220 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 403 | 314 | 414 | 414 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 24 | 0 | 30
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 22 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 7 | 10 | 10 | 10
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 52 | 52 | 52
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 96 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 150 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 79 | 108 | 113 | 113
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 109 | 109 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 1049 | 1387 | 1665 | 1785 | 631 | 0
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 104 | 96 | 105 | 105 |  | 8 | Engine problem
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 259 | 246 | 263 | 255 | 294 | 48
|  | Total |  |  |  |  | 20383 | 19892 | 10495 | 12722 | 14144.6 | 15017 | 2278 | 2361
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9923.3104 | 12029 | 13374.1073 | 14198.9855
| A. |  | 2020-10-12 | (Yesterday) |  |  |  |  | Monday
| 1 | Highest Generation : |  |  | 12722 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 9260 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12722 | MW
| 3 | Day peak Generation : |  |  | 10495 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12029 | MW
| 4 | Evening peak Generation : |  |  | 12722 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 264.8155 | MKWHr | By Solar | 0.21199 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 137.1022 | MKWHr |  | By Oil: | 82.6964 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 17.2973 | MKWHr |  | By Hydro: | 2.8564 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2278 | MW | Dhaka | 4291 | 4291 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2361 | MW | Chittagong | 1240 | 1240 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4639 | MW | Khulna | 1461 | 1461 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1205.43 | MMCFD |  |  | Rajshahi | 1282 | 1282 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 160782643.848 | ii) Oil : | Taka | 689956199.32 | Comilla | 1150 | 1150 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 79751400 | Total | Taka | 930490243.168 | Mymensingh | 969 | 969 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.2925 | MKWHr. | Sylhet | 542 | 542 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 20 | MW (E to W) at | 19:00 | hrs | Barisal | 361 | 361 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -32 | MW at | 19:30 | hrs | Rangpur | 733 | 733 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 33.0° C |  |  | Total | 12029 | 12029 |  | 0
| B. |  | 2020-10-13 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 34.8° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13100 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15017 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10800 | MW
| 4 | Reserve(Generation end) |  |  |  | 1917 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 272.6838 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9317 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.4247 | MKWHr. | ii) HVDC Flow at Peak Time |  | 892 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.2266 | MKWHr. | iii) Maximum HVDC Flow : |  | 897 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 101.99 |  | (b) Today: | 102.1 |  | (c) Rule Curve: |  | 107.1
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-10-12
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 150 | 115 | 200 | 43 | 0 | 0 | 351 |  | 0 | 450 | 265 | 100 | 80 | 55 | 0 | 0 | 118 | 0 | 7 | 7 | 133 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 83 | 35 | 115 | 0 | 25 | 204 | 0 | 105 | 0 |  | 0 | 0 | 85 | 40 | 83 | 50 | 20 | 34 | 0 | 0 | 80 | 260 | 355 | 213 | 8 | 96 | 16 | 5 | 0 | 51 | 0 | 49 | 43 | 21 | 10 | 33 | 21 | 152 | 154 | 48 | 17 | 0 | 87 | 43 | 47 | 46 | 110 | 100 | 65 | 87 | 0 | 132 | 0 | 0 | 10 | 290 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 147 | 0 | 100 | 100 | 10 | 423 | 115 | 102 | 0 | 0 | 162 | 36 | 0 | 100 | 110 | 100 | 0 | 20 |  | 896 | 0 | 270 | 0 | 115 | 230 | 0 | 0 | 35 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 10 | 43 | 0 | 94 | 0 | 0 | 28 | 52 | 32 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 148 | 0 | 91 | 99 | 162 | 0 | 354 | 17 | 0 | 113 | 0 | 111 | 0 | 0 | 0 | 600 |  | 8042 | 3880 | 11922 | 3929 | 896 | 2046 | 3302 | 750 | 118 | 729 | 152 | 0 | 0 | 101.99
2:00 | 0 | 0 | 150 | 115 | 200 | 43 | 0 | 0 | 351 |  | 0 | 400 | 260 | 100 | 92 | 55 | 0 | 0 | 110 | 0 | 7 | 7 | 133 | 88 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 85 | 35 | 115 | 0 | 25 | 204 | 0 | 104 | 0 |  | 0 | 0 | 19 | 40 | 83 | 50 | 20 | 34 | 0 | 0 | 80 | 260 | 355 | 213 | 8 | 90 | 16 | 5 | 0 | 51 | 0 | 0 | 43 | 21 | 10 | 33 | 21 | 148 | 155 | 48 | 17 | 0 | 87 | 43 | 47 | 46 | 110 | 102 | 65 | 87 | 0 | 132 | 0 | 0 | 10 | 280 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 17 | 10 | 422 | 105 | 102 | 0 | 0 | 162 | 36 | 0 | 100 | 113 | 100 | 0 | 17 |  | 897 | 0 | 270 | 0 | 115 | 230 | 0 | 0 | 29 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 25 | 0 | 94 | 0 | 0 | 28 | 52 | 32 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 148 | 0 | 93 | 50 | 154 | 0 | 350 | 17 | 0 | 113 | 0 | 111 | 0 | 0 | 10 | 580 |  | 7831 | 3778 | 11609 | 3898 | 897 | 1984 | 3242 | 730 | 120 | 590 | 148 | 0 | 0 | 101.99
3:00 | 0 | 0 | 150 | 115 | 200 | 43 | 0 | 0 | 351 |  | 0 | 400 | 255 | 100 | 95 | 55 | 0 | 0 | 110 | 0 | 7 | 7 | 133 | 88 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 85 | 35 | 115 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 34 | 0 | 83 | 50 | 20 | 34 | 0 | 0 | 80 | 260 | 355 | 213 | 8 | 96 | 16 | 5 | 0 | 51 | 0 | 0 | 43 | 21 | 10 | 33 | 21 | 146 | 157 | 48 | 17 | 0 | 87 | 43 | 47 | 46 | 110 | 100 | 65 | 84 | 0 | 132 | 0 | 0 | 10 | 280 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 17 | 10 | 424 | 105 | 102 | 0 | 0 | 161 | 36 | 0 | 100 | 104 | 100 | 0 | 17 |  | 895 | 0 | 270 | 0 | 115 | 230 | 0 | 0 | 17 | 0 | 24 | 0 | 38 | 110 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 148 | 0 | 93 | 20 | 154 | 0 | 340 | 17 | 0 | 113 | 0 | 96 | 0 | 0 | 90 | 550 |  | 7721 | 3658 | 11379 | 3906 | 895 | 1971 | 3133 | 700 | 120 | 508 | 146 | 0 | 0 | 101.99
4:00 | 0 | 0 | 150 | 115 | 200 | 43 | 0 | 0 | 325 |  | 0 | 370 | 265 | 96 | 95 | 55 | 0 | 0 | 110 | 0 | 7 | 7 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 86 | 35 | 115 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 17 | 0 | 83 | 50 | 20 | 35 | 0 | 0 | 80 | 260 | 355 | 210 | 8 | 97 | 16 | 5 | 0 | 51 | 0 | 0 | 43 | 21 | 10 | 33 | 21 | 146 | 155 | 48 | 17 | 0 | 86 | 43 | 47 | 46 | 110 | 100 | 65 | 84 | 0 | 130 | 0 | 0 | 10 | 280 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 10 | 424 | 105 | 102 | 0 | 0 | 162 | 23 | 0 | 17 | 106 | 100 | 0 | 17 |  | 895 | 0 | 270 | 0 | 115 | 210 | 0 | 0 | 0 | 0 | 24 | 0 | 36 | 96 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 148 | 0 | 93 | 0 | 154 | 0 | 360 | 17 | 0 | 113 | 0 | 100 | 0 | 0 | 109 | 550 |  | 7382 | 3576 | 10958 | 3899 | 895 | 1934 | 2878 | 700 | 121 | 385 | 146 | 0 | 0 | 101.99
5:00 | 0 | 0 | 150 | 115 | 200 | 43 | 0 | 0 | 325 |  | 0 | 370 | 285 | 100 | 95 | 55 | 0 | 0 | 115 | 0 | 7 | 7 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 86 | 35 | 115 | 0 | 0 | 204 | 0 | 106 | 0 |  | 0 | 0 | 17 | 0 | 83 | 19 | 20 | 37 | 0 | 0 | 80 | 260 | 355 | 213 | 8 | 97 | 16 | 5 | 0 | 51 | 0 | 0 | 43 | 21 | 10 | 33 | 21 | 142 | 155 | 48 | 17 | 0 | 86 | 43 | 47 | 46 | 110 | 101 | 65 | 84 | 0 | 132 | 0 | 0 | 10 | 290 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 10 | 422 | 105 | 50 | 0 | 0 | 161 | 18 | 0 | 0 | 103 | 100 | 0 | 17 |  | 892 | 0 | 270 | 0 | 115 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 150 | 0 | 93 | 0 | 156 | 0 | 390 | 17 | 0 | 113 | 0 | 102 | 0 | 0 | 109 | 550 |  | 7316 | 3394 | 10710 | 3914 | 892 | 1975 | 2755 | 700 | 121 | 211 | 142 | 0 | 0 | 101.99
6:00 | 0 | 0 | 150 | 115 | 200 | 43 | 0 | 0 | 303 |  | 0 | 340 | 275 | 100 | 95 | 55 | 0 | 0 | 115 | 0 | 7 | 7 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 88 | 35 | 115 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 17 | 0 | 60 | 18 | 20 | 35 | 0 | 0 | 80 | 260 | 355 | 213 | 8 | 93 | 16 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 0 | 33 | 21 | 132 | 68 | 48 | 17 | 0 | 86 | 43 | 47 | 46 | 110 | 101 | 65 | 84 | 0 | 132 | 0 | 0 | 10 | 290 | 24 | 8 | 0 | 145 | 0 | 0 | 200 | 0 | 149 | 0 | 50 | 0 | 10 | 423 | 95 | 0 | 0 | 0 | 161 | 18 | 0 | 0 | 108 | 100 | 0 | 17 |  | 892 | 0 | 270 | 0 | 34 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 149 | 0 | 93 | 0 | 156 | 0 | 310 | 17 | 0 | 0 | 0 | 104 | 0 | 0 | 109 | 550 |  | 6748 | 3071 | 9819 | 3808 | 892 | 1836 | 2175 | 700 | 123 | 153 | 132 | 0 | 0 | 101.99
7:00 | 0 | 0 | 150 | 115 | 200 | 43 | 0 | 0 | 262 |  | 0 | 320 | 285 | 100 | 95 | 55 | 0 | 0 | 75 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 88 | 35 | 115 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 17 | 0 | 11 | 18 | 20 | 22 | 0 | 0 | 80 | 275 | 300 | 213 | 8 | 96 | 16 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 0 | 33 | 21 | 116 | 52 | 48 | 17 | 0 | 86 | 43 | 47 | 46 | 110 | 102 | 40 | 82 | 0 | 132 | 0 | 0 | 10 | 300 | 24 | 8 | 0 | 145 | 0 | 0 | 192 | 0 | 117 | 4 | 20 | 0 | 10 | 420 | 75 | 0 | 0 | 1 | 106 | 18 | 0 | 0 | 102 | 100 | 0 | 17 |  | 893 | 0 | 270 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 150 | 0 | 92 | 0 | 157 | 0 | 339 | 17 | 0 | 0 | 0 | 104 | 0 | 1 | 109 | 520 |  | 6272 | 2988 | 9260 | 3690 | 893 | 1795 | 1830 | 670 | 123 | 137 | 116 | 6 | 0 | 102
8:00 | 0 | 0 | 150 | 115 | 200 | 41 | 0 | 0 | 262 |  | 0 | 320 | 290 | 100 | 95 | 55 | 0 | 0 | 76 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 88 | 35 | 115 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 17 | 0 | 11 | 18 | 20 | 3 | 0 | 0 | 80 | 260 | 300 | 206 | 8 | 96 | 16 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 33 | 21 | 110 | 100 | 48 | 17 | 1 | 85 | 43 | 47 | 46 | 110 | 100 | 51 | 82 | 0 | 132 | 0 | 0 | 10 | 300 | 24 | 8 | 0 | 145 | 0 | 0 | 192 | 0 | 112 | 12 | 25 | 0 | 10 | 419 | 75 | 1 | 0 | 2 | 106 | 18 | 0 | 0 | 102 | 100 | 0 | 17 |  | 893 | 0 | 310 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 145 | 0 | 92 | 0 | 164 | 0 | 340 | 17 | 0 | 0 | 0 | 105 | 0 | 3 | 109 | 500 |  | 6293 | 3016 | 9309 | 3767 | 893 | 1774 | 1837 | 650 | 123 | 137 | 110 | 18 | 0 | 102
9:00 | 0 | 0 | 150 | 115 | 200 | 41 | 0 | 0 | 332 |  | 0 | 390 | 280 | 100 | 80 | 55 | 0 | 0 | 35 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 87 | 35 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 17 | 0 | 0 | 19 | 20 | 2 | 0 | 0 | 80 | 360 | 300 | 205 | 8 | 96 | 16 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 90 | 85 | 48 | 17 | 2 | 87 | 43 | 46 | 46 | 110 | 100 | 50 | 82 | 0 | 132 | 0 | 0 | 10 | 290 | 24 | 8 | 0 | 180 | 0 | 0 | 160 | 0 | 130 | 16 | 100 | 0 | 10 | 418 | 45 | 45 | 0 | 3 | 157 | 18 | 0 | 0 | 105 | 100 | 0 | 17 |  | 892 | 0 | 280 | 0 | 9 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 170 | 0 | 91 | 0 | 173 | 0 | 403 | 17 | 0 | 13 | 0 | 106 | 0 | 3 | 109 | 410 |  | 6676 | 3012 | 9688 | 3857 | 892 | 1962 | 2044 | 560 | 122 | 137 | 90 | 24 | 0 | 102
10:00 | 0 | 0 | 150 | 115 | 200 | 41 | 0 | 0 | 345 |  | 0 | 420 | 285 | 100 | 80 | 55 | 0 | 0 | 60 | 0 | 7 | 7 | 25 | 4 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 8 | 0 | 87 | 35 | 115 | 0 | 2 | 232 | 0 | 138 | 0 |  | 0 | 0 | 17 | 0 | 0 | 44 | 17 | 2 | 0 | 0 | 80 | 260 | 300 | 211 | 8 | 96 | 16 | 5 | 0 | 51 | 0 | 0 | 26 | 19 | 8 | 33 | 18 | 92 | 85 | 48 | 17 | 2 | 85 | 43 | 46 | 46 | 110 | 99 | 63 | 82 | 0 | 132 | 0 | 0 | 10 | 300 | 16 | 8 | 0 | 280 | 0 | 0 | 130 | 0 | 132 | 18 | 100 | 0 | 15 | 416 | 16 | 102 | 0 | 2 | 161 | 18 | 0 | 17 | 104 | 100 | 0 | 17 |  | 893 | 0 | 300 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 21 | 8 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 190 | 0 | 91 | 0 | 185 | 0 | 408 | 17 | 0 | 50 | 0 | 105 | 0 | 3 | 109 | 400 |  | 6919 | 3200 | 10119 | 3858 | 893 | 2018 | 2400 | 549 | 122 | 162 | 92 | 25 | 0 | 102.01
11:00 | 0 | 0 | 150 | 115 | 200 | 42 | 0 | 0 | 344 |  | 0 | 420 | 285 | 100 | 80 | 55 | 0 | 0 | 86 | 0 | 7 | 7 | 135 | 12 | 0 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 29 | 33 | 33 | 25 | 0 | 86 | 35 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 17 | 0 | 0 | 46 | 17 | 2 | 0 | 0 | 80 | 270 | 300 | 213 | 8 | 96 | 16 | 5 | 0 | 51 | 0 | 0 | 43 | 19 | 8 | 33 | 18 | 94 | 89 | 48 | 17 | 1 | 83 | 43 | 46 | 46 | 115 | 100 | 40 | 84 | 0 | 132 | 0 | 0 | 10 | 300 | 16 | 8 | 0 | 300 | 0 | 25 | 130 | 0 | 132 | 19 | 100 | 0 | 30 | 412 | 16 | 102 | 0 | 4 | 178 | 18 | 0 | 17 | 105 | 100 | 0 | 17 |  | 892 | 0 | 300 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 21 | 7 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 171 | 0 | 88 | 0 | 180 | 0 | 407 | 17 | 0 | 57 | 0 | 104 | 0 | 6 | 109 | 400 |  | 7188 | 3195 | 10383 | 3820 | 892 | 2021 | 2583 | 550 | 121 | 272 | 94 | 30 | 0 | 102.02
12:00 | 0 | 0 | 170 | 115 | 200 | 42 | 0 | 0 | 350 |  | 0 | 420 | 260 | 100 | 80 | 55 | 0 | 0 | 94 | 0 | 7 | 7 | 145 | 17 | 0 | 0 | 0 | 53 | 55 | 55 | 0 | 25 | 29 | 33 | 33 | 40 | 0 | 86 | 35 | 115 | 0 | 25 | 205 | 0 | 139 | 0 |  | 0 | 7 | 47 | 40 | 0 | 45 | 20 | 2 | 0 | 0 | 80 | 260 | 300 | 213 | 8 | 90 | 16 | 5 | 0 | 51 | 0 | 0 | 43 | 19 | 8 | 33 | 18 | 100 | 151 | 48 | 17 | 2 | 83 | 43 | 49 | 46 | 115 | 100 | 63 | 82 | 0 | 132 | 0 | 0 | 10 | 300 | 16 | 8 | 0 | 285 | 0 | 25 | 130 | 0 | 132 | 16 | 100 | 1 | 30 | 412 | 16 | 102 | 0 | 5 | 179 | 18 | 0 | 17 | 102 | 100 | 0 | 17 |  | 892 | 0 | 175 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 40 | 0 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 20 | 7 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 189 | 0 | 403 | 17 | 0 | 79 | 0 | 104 | 0 | 5 | 109 | 440 |  | 7347 | 3148 | 10495 | 3794 | 892 | 1935 | 2716 | 590 | 121 | 319 | 100 | 28 | 0 | 102.04
13:00 | 0 | 0 | 170 | 115 | 200 | 42 | 0 | 0 | 345 |  | 0 | 420 | 260 | 98 | 63 | 55 | 0 | 0 | 60 | 0 | 7 | 7 | 150 | 47 | 0 | 0 | 0 | 53 | 55 | 55 | 0 | 25 | 28 | 33 | 33 | 51 | 0 | 86 | 35 | 115 | 0 | 25 | 205 | 0 | 140 | 0 |  | 0 | 8 | 51 | 40 | 3 | 42 | 20 | 2 | 0 | 0 | 80 | 260 | 300 | 212 | 8 | 95 | 16 | 5 | 0 | 51 | 0 | 0 | 43 | 19 | 8 | 33 | 18 | 108 | 149 | 48 | 17 | 2 | 85 | 43 | 46 | 46 | 114 | 101 | 63 | 82 | 0 | 132 | 0 | 0 | 10 | 290 | 16 | 8 | 0 | 280 | 0 | 25 | 130 | 0 | 132 | 19 | 100 | 46 | 30 | 412 | 16 | 102 | 0 | 5 | 180 | 18 | 0 | 17 | 105 | 100 | 0 | 17 |  | 893 | 0 | 200 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 40 | 0 | 25 | 64 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 20 | 8 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 178 | 0 | 60 | 0 | 180 | 0 | 400 | 17 | 0 | 70 | 0 | 73 | 0 | 7 | 109 | 460 |  | 7386 | 3278 | 10664 | 3780 | 893 | 1974 | 2774 | 609 | 121 | 372 | 108 | 33 | 10664 | 102.04
14:00 | 0 | 0 | 170 | 115 | 200 | 42 | 0 | 0 | 323 |  | 0 | 350 | 250 | 98 | 70 | 55 | 0 | 0 | 90 | 0 | 7 | 7 | 150 | 48 | 0 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 28 | 33 | 33 | 51 | 0 | 86 | 35 | 115 | 0 | 25 | 204 | 0 | 110 | 0 |  | 0 | 8 | 51 | 20 | 64 | 47 | 20 | 2 | 0 | 0 | 80 | 260 | 355 | 211 | 8 | 95 | 16 | 5 | 0 | 51 | 0 | 25 | 43 | 19 | 8 | 33 | 18 | 116 | 155 | 48 | 17 | 2 | 85 | 43 | 49 | 46 | 114 | 102 | 64 | 84 | 0 | 132 | 0 | 0 | 10 | 280 | 16 | 8 | 0 | 300 | 0 | 25 | 130 | 51 | 131 | 16 | 100 | 70 | 30 | 326 | 16 | 86 | 0 | 4 | 179 | 18 | 0 | 17 | 103 | 100 | 0 | 17 |  | 893 | 0 | 200 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 40 | 0 | 25 | 32 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 20 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 160 | 0 | 75 | 0 | 182 | 0 | 382 | 17 | 0 | 72 | 0 | 64 | 0 | 0 | 109 | 480 |  | 7431 | 3219 | 10650 | 3758 | 893 | 1876 | 2837 | 630 | 121 | 397 | 116 | 22 | 0 | 102.05
15:00 | 0 | 0 | 170 | 115 | 200 | 42 | 0 | 0 | 345 |  | 0 | 350 | 285 | 100 | 80 | 55 | 0 | 0 | 92 | 0 | 7 | 7 | 150 | 28 | 0 | 0 | 0 | 53 | 55 | 35 | 19 | 25 | 28 | 33 | 33 | 51 | 0 | 86 | 35 | 115 | 0 | 25 | 205 | 0 | 140 | 0 |  | 0 | 8 | 50 | 40 | 80 | 45 | 20 | 2 | 0 | 0 | 70 | 280 | 345 | 201 | 8 | 96 | 16 | 5 | 0 | 51 | 0 | 50 | 43 | 19 | 8 | 33 | 18 | 136 | 152 | 48 | 17 | 1 | 83 | 43 | 49 | 46 | 110 | 101 | 62 | 84 | 0 | 132 | 0 | 0 | 10 | 300 | 24 | 8 | 0 | 300 | 33 | 50 | 130 | 51 | 132 | 12 | 100 | 100 | 30 | 226 | 16 | 102 | 0 | 3 | 179 | 19 | 0 | 17 | 102 | 100 | 0 | 17 |  | 892 | 0 | 200 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 40 | 0 | 25 | 32 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 20 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 174 | 0 | 78 | 0 | 174 | 0 | 403 | 17 | 0 | 72 | 0 | 96 | 0 | 1 | 109 | 490 |  | 7577 | 3308 | 10885 | 3688 | 892 | 1938 | 3032 | 640 | 121 | 421 | 136 | 17 | 0 | 102.06
16:00 | 0 | 0 | 170 | 115 | 200 | 42 | 0 | 0 | 349 |  | 0 | 400 | 250 | 100 | 80 | 40 | 0 | 0 | 85 | 0 | 7 | 7 | 150 | 26 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 28 | 33 | 33 | 51 | 0 | 84 | 35 | 115 | 0 | 25 | 205 | 0 | 139 | 0 |  | 0 | 9 | 50 | 40 | 71 | 50 | 20 | 0 | 0 | 25 | 70 | 275 | 345 | 173 | 8 | 86 | 16 | 5 | 0 | 51 | 0 | 50 | 43 | 19 | 8 | 33 | 18 | 132 | 154 | 48 | 17 | 1 | 85 | 43 | 46 | 46 | 110 | 100 | 64 | 84 | 0 | 132 | 0 | 0 | 10 | 280 | 24 | 8 | 0 | 296 | 0 | 0 | 130 | 26 | 132 | 6 | 100 | 100 | 30 | 238 | 16 | 102 | 0 | 1 | 179 | 41 | 0 | 17 | 107 | 100 | 0 | 17 |  | 892 | 0 | 200 | 0 | 85 | 120 | 0 | 0 | 0 | 0 | 40 | 0 | 26 | 32 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 20 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 189 | 0 | 383 | 17 | 0 | 72 | 0 | 100 | 0 | 5 | 109 | 490 |  | 7447 | 3314 | 10761 | 3703 | 892 | 1951 | 2882 | 640 | 119 | 429 | 132 | 13 | 0 | 102.07
17:00 | 0 | 0 | 170 | 115 | 200 | 42 | 0 | 0 | 347 |  | 0 | 400 | 260 | 100 | 66 | 40 | 0 | 0 | 54 | 0 | 7 | 16 | 100 | 26 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 29 | 33 | 33 | 51 | 0 | 84 | 35 | 115 | 0 | 25 | 204 | 0 | 140 | 0 |  | 0 | 9 | 42 | 10 | 82 | 50 | 0 | 4 | 0 | 60 | 55 | 275 | 345 | 154 | 8 | 87 | 16 | 5 | 0 | 51 | 0 | 50 | 8 | 19 | 10 | 33 | 18 | 138 | 154 | 48 | 17 | 0 | 86 | 43 | 18 | 15 | 110 | 101 | 40 | 84 | 0 | 132 | 0 | 0 | 10 | 260 | 24 | 8 | 0 | 283 | 0 | 0 | 130 | 0 | 132 | 0 | 100 | 50 | 30 | 215 | 16 | 102 | 0 | 0 | 124 | 54 | 0 | 17 | 105 | 100 | 0 | 17 |  | 892 | 0 | 235 | 0 | 49 | 120 | 0 | 0 | 3 | 0 | 0 | 0 | 26 | 32 | 0 | 0 | 0 | 50 | 9 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 161 | 0 | 88 | 0 | 181 | 0 | 315 | 17 | 0 | 35 | 0 | 104 | 0 | 2 | 109 | 490 |  | 7037 | 3118 | 10155 | 3620 | 892 | 1814 | 2547 | 640 | 119 | 383 | 138 | 2 | 0 | 102.08
18:00 | 0 | 0 | 170 | 115 | 200 | 42 | 0 | 0 | 339 |  | 0 | 420 | 300 | 36 | 76 | 55 | 0 | 0 | 140 | 0 | 7 | 16 | 150 | 26 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 22 | 33 | 33 | 51 | 0 | 88 | 35 | 115 | 0 | 25 | 217 | 0 | 100 | 0 |  | 0 | 9 | 0 | 100 | 82 | 50 | 20 | 8 | 0 | 80 | 0 | 300 | 345 | 185 | 8 | 95 | 16 | 5 | 0 | 51 | 0 | 50 | 16 | 19 | 10 | 33 | 21 | 158 | 153 | 48 | 17 | 0 | 83 | 43 | 45 | 25 | 110 | 100 | 65 | 87 | 0 | 132 | 0 | 0 | 10 | 285 | 24 | 8 | 85 | 298 | 180 | 78 | 150 | 91 | 132 | 0 | 100 | 72 | 33 | 334 | 37 | 102 | 0 | 0 | 175 | 54 | 0 | 100 | 111 | 100 | 0 | 17 |  | 892 | 0 | 235 | 0 | 92 | 135 | 0 | 0 | 3 | 0 | 40 | 0 | 37 | 80 | 0 | 0 | 0 | 43 | 23 | 84 | 0 | 0 | 38 | 52 | 18 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 153 | 0 | 88 | 5 | 169 | 0 | 363 | 17 | 100 | 62 | 0 | 97 | 0 | 0 | 109 | 500 |  | 8144 | 3628 | 11772 | 3840 | 892 | 1955 | 3601 | 650 | 123 | 553 | 158 | 0 | 0 | 102.08
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 170 | 115 | 200 | 42 | 0 | 0 | 352 |  | 0 | 450 | 250 | 16 | 80 | 55 | 0 | 0 | 175 | 0 | 7 | 7 | 150 | 26 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 29 | 33 | 33 | 51 | 0 | 88 | 35 | 115 | 0 | 25 | 204 | 0 | 138 | 0 |  | 0 | 9 | 0 | 100 | 82 | 50 | 20 | 0 | 0 | 80 | 0 | 275 | 345 | 214 | 8 | 86 | 16 | 5 | 0 | 51 | 0 | 50 | 52 | 19 | 8 | 33 | 21 | 158 | 156 | 48 | 17 | 0 | 87 | 43 | 46 | 41 | 110 | 100 | 65 | 87 | 0 | 132 | 0 | 0 | 10 | 280 | 24 | 11 | 150 | 300 | 180 | 93 | 190 | 93 | 132 | 0 | 100 | 190 | 46 | 419 | 105 | 102 | 0 | 0 | 180 | 54 | 0 | 100 | 111 | 100 | 0 | 17 |  | 892 | 0 | 235 | 0 | 96 | 210 | 0 | 0 | 9 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 35 | 96 | 0 | 0 | 36 | 52 | 24 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 183 | 0 | 88 | 98 | 187 | 0 | 314 | 35 | 150 | 108 | 0 | 96 | 0 | 0 | 109 | 600 |  | 8638 | 4084 | 12722 | 4046 | 892 | 1954 | 4130 | 750 | 123 | 669 | 158 | 0 | 0 | 102.08
19:30 | 0 | 0 | 170 | 115 | 200 | 42 | 0 | 0 | 350 |  | 0 | 450 | 265 | 16 | 80 | 55 | 0 | 0 | 180 | 0 | 7 | 7 | 150 | 40 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 88 | 35 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 9 | 0 | 100 | 83 | 50 | 20 | 3 | 0 | 80 | 0 | 275 | 345 | 213 | 8 | 95 | 16 | 5 | 0 | 51 | 0 | 50 | 52 | 19 | 8 | 33 | 21 | 158 | 142 | 48 | 17 | 0 | 85 | 43 | 46 | 41 | 110 | 101 | 63 | 87 | 0 | 132 | 0 | 0 | 10 | 300 | 24 | 11 | 100 | 300 | 125 | 92 | 192 | 93 | 132 | 0 | 100 | 200 | 50 | 416 | 95 | 102 | 0 | 0 | 180 | 54 | 0 | 100 | 113 | 100 | 0 | 17 |  | 893 | 0 | 235 | 0 | 99 | 230 | 0 | 0 | 18 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 35 | 96 | 0 | 0 | 36 | 52 | 24 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 183 | 0 | 86 | 98 | 185 | 0 | 335 | 35 | 50 | 111 | 0 | 103 | 0 | 0 | 109 | 600 |  | 8586 | 4044 | 12630 | 4039 | 893 | 1994 | 3975 | 750 | 123 | 698 | 158 | 0 | 0 | 0
20:00 | 0 | 0 | 170 | 115 | 200 | 42 | 0 | 0 | 348 |  | 0 | 450 | 270 | 16 | 80 | 55 | 0 | 0 | 185 | 0 | 7 | 7 | 150 | 30 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 29 | 33 | 33 | 51 | 0 | 88 | 35 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 9 | 0 | 100 | 82 | 50 | 20 | 8 | 0 | 80 | 0 | 275 | 345 | 213 | 8 | 93 | 16 | 5 | 0 | 51 | 0 | 50 | 52 | 19 | 8 | 33 | 21 | 160 | 140 | 48 | 17 | 0 | 85 | 43 | 46 | 41 | 110 | 100 | 65 | 87 | 0 | 132 | 0 | 0 | 10 | 265 | 24 | 11 | 100 | 300 | 129 | 86 | 192 | 96 | 132 | 0 | 100 | 200 | 50 | 416 | 105 | 102 | 0 | 0 | 180 | 54 | 0 | 100 | 112 | 100 | 0 | 17 |  | 892 | 0 | 235 | 0 | 99 | 230 | 0 | 0 | 18 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 35 | 96 | 0 | 0 | 39 | 52 | 27 | 22 | 10 | 11 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 183 | 0 | 87 | 98 | 186 | 0 | 362 | 35 | 50 | 111 | 0 | 99 | 0 | 0 | 109 | 600 |  | 8561 | 4075 | 12636 | 4041 | 892 | 1990 | 3975 | 751 | 123 | 704 | 160 | 0 | 0 | 102.09
21:00 | 0 | 0 | 170 | 115 | 200 | 42 | 0 | 0 | 350 |  | 0 | 450 | 270 | 16 | 80 | 55 | 0 | 0 | 185 | 0 | 7 | 7 | 150 | 26 | 0 | 0 | 0 | 54 | 55 | 45 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 89 | 35 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 9 | 0 | 100 | 84 | 50 | 20 | 10 | 0 | 80 | 0 | 275 | 345 | 213 | 8 | 96 | 16 | 5 | 0 | 51 | 0 | 50 | 52 | 19 | 8 | 33 | 21 | 158 | 140 | 48 | 17 | 0 | 85 | 43 | 47 | 41 | 110 | 100 | 66 | 87 | 0 | 132 | 0 | 0 | 10 | 300 | 24 | 11 | 30 | 300 | 124 | 30 | 192 | 86 | 132 | 0 | 100 | 200 | 43 | 416 | 115 | 102 | 0 | 0 | 179 | 54 | 0 | 100 | 113 | 100 | 0 | 17 |  | 892 | 0 | 260 | 0 | 99 | 230 | 0 | 0 | 20 | 0 | 40 | 0 | 39 | 110 | 0 | 0 | 0 | 50 | 34 | 96 | 0 | 0 | 36 | 52 | 30 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 192 | 0 | 88 | 100 | 194 | 0 | 361 | 35 | 50 | 111 | 0 | 100 | 0 | 0 | 109 | 600 |  | 8475 | 4121 | 12596 | 4088 | 892 | 2031 | 3848 | 750 | 124 | 705 | 158 | 0 | 0 | 102.09
22:00 | 0 | 0 | 170 | 115 | 200 | 42 | 0 | 0 | 350 |  | 0 | 450 | 265 | 16 | 92 | 55 | 0 | 0 | 185 | 0 | 7 | 7 | 150 | 26 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 89 | 35 | 115 | 0 | 25 | 204 | 0 | 140 | 0 |  | 0 | 9 | 0 | 100 | 84 | 50 | 20 | 14 | 0 | 80 | 0 | 275 | 345 | 213 | 8 | 94 | 16 | 5 | 0 | 51 | 0 | 50 | 52 | 19 | 8 | 33 | 21 | 156 | 140 | 48 | 17 | 0 | 85 | 43 | 47 | 41 | 110 | 100 | 66 | 87 | 0 | 132 | 0 | 0 | 10 | 290 | 24 | 11 | 0 | 300 | 75 | 13 | 200 | 79 | 132 | 0 | 100 | 200 | 48 | 417 | 115 | 102 | 0 | 0 | 180 | 54 | 0 | 100 | 110 | 100 | 0 | 17 |  | 892 | 0 | 315 | 0 | 99 | 230 | 0 | 0 | 29 | 0 | 40 | 0 | 39 | 110 | 0 | 0 | 0 | 50 | 34 | 96 | 0 | 0 | 36 | 52 | 30 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 183 | 0 | 90 | 99 | 186 | 0 | 354 | 35 | 0 | 111 | 0 | 96 | 0 | 0 | 109 | 600 |  | 8392 | 4108 | 12500 | 4126 | 892 | 2020 | 3718 | 750 | 124 | 714 | 156 | 0 | 0 | 102.09
23:00 | 0 | 0 | 170 | 115 | 200 | 42 | 0 | 0 | 350 |  | 0 | 450 | 280 | 16 | 96 | 55 | 0 | 0 | 185 | 0 | 7 | 7 | 150 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 85 | 35 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 8 | 0 | 90 | 84 | 50 | 20 | 26 | 0 | 80 | 0 | 265 | 345 | 213 | 8 | 95 | 16 | 5 | 0 | 51 | 0 | 50 | 25 | 19 | 8 | 33 | 21 | 158 | 153 | 48 | 17 | 0 | 85 | 43 | 47 | 42 | 110 | 100 | 65 | 87 | 0 | 133 | 0 | 0 | 10 | 290 | 24 | 11 | 0 | 300 | 0 | 0 | 192 | 0 | 131 | 0 | 100 | 200 | 50 | 417 | 115 | 102 | 0 | 0 | 180 | 54 | 0 | 100 | 113 | 100 | 0 | 17 |  | 892 | 0 | 310 | 0 | 99 | 230 | 0 | 0 | 29 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 34 | 96 | 0 | 0 | 36 | 52 | 30 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 185 | 0 | 90 | 99 | 187 | 0 | 360 | 35 | 0 | 111 | 0 | 99 | 0 | 0 | 109 | 600 |  | 8215 | 4114 | 12329 | 4127 | 892 | 2038 | 3531 | 750 | 120 | 713 | 158 | 0 | 0 | 102.1
24:00 | 0 | 0 | 170 | 115 | 200 | 44 | 0 | 0 | 351 |  | 0 | 450 | 285 | 16 | 97 | 55 | 0 | 0 | 185 | 0 | 7 | 7 | 150 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 84 | 35 | 115 | 0 | 25 | 204 | 0 | 140 | 0 |  | 0 | 8 | 0 | 70 | 83 | 50 | 20 | 33 | 0 | 80 | 0 | 280 | 345 | 214 | 8 | 96 | 16 | 5 | 0 | 51 | 0 | 0 | 25 | 19 | 8 | 33 | 21 | 154 | 154 | 48 | 17 | 0 | 85 | 43 | 44 | 42 | 110 | 102 | 65 | 87 | 0 | 132 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 131 | 0 | 100 | 50 | 50 | 416 | 115 | 102 | 0 | 0 | 180 | 38 | 0 | 100 | 113 | 100 | 0 | 17 |  | 892 | 0 | 295 | 0 | 115 | 230 | 0 | 0 | 29 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 0 | 96 | 0 | 0 | 36 | 52 | 30 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 187 | 0 | 90 | 70 | 199 | 0 | 360 | 35 | 0 | 111 | 0 | 103 | 0 | 0 | 109 | 600 |  | 8023 | 4069 | 12092 | 4145 | 892 | 2054 | 3349 | 750 | 119 | 629 | 154 | 0 | 0 | 102.1
KWH | 0 | 0 | 3861000 | 2709000 | 4736709 | 1015136 | 0 | 0 | 7989000 |  | 0 | 8813000 | 6587200 | 1854720 | 2057736 | 1321614 | 0 | 0 | 2971000 | 0 | 197760 | 216000 | 2581920 | 643331 | 0 | 0 | 0 | 1139400 | 1249523 | 1209260 | 438120 | 600000 | 678780 | 815700 | 831900 | 794832 | 0 | 2020369 | 836000 | 2800000 | 0 | 433609 | 4917778 | 0 | 2967682 | 0 |  | 0 | 0 | 592441 | 876360 | 1388160 | 1035840 | 457872 | 341280 | 0 | 633280 | 1352430 | 6872700 | 8147000 | 5003000 | 200727 | 2215280 | 364824 | 142560 | 0 | 1242522 | 0 | 550896 | 813682 | 463644 | 178920 | 818300 | 477540 | 3226560 | 3135 | 1135680 | 367416 | 13350 | 2011000 | 1044240 | 1090800 | 1032264 | 2621372 | 2256000 | 1099872 | 2035200 | 0 | 3170310 | 0 | 0 | 244440 | 7135500 | 535752 | 210000 | 344256 | 6726870 | 662013 | 464268 | 4161600 | 564368 | 3251810 | 130545 | 2269440 | 1787520 | 695854 | 9357000 | 1738800 | 2049756 | 0 | 30840 | 3899127 | 791635 | 0 | 1128600 | 2579640 | 2421120 | 63300 | 434880 |  | 21424727 | 0 | 6450624 | 0 | 2000640 | 4062720 | 0 | 0 | 220800 | 0 | 583125 | 0 | 753471 | 1555200 | 0 | 0 | 60000 | 622864 | 213625 | 1036128 | 0 | 0 | 294195 | 812640 | 263895 | 489600 | 225936 | 259524 | 0 | 0 | 3705100 | 0 | 0 | 0 | 0 | 4238682 | 0 | 1985678 | 797760 | 4459818 | 0 | 8844545 | 548160 | 359866 | 1951200 | 0 | 2396160 | 0 | 37255 | 2325888 | 13592200 |  | 178243470 | 86572026 | 264815496 | 90899132 | 21424727 | 46203031 | 72256903 | 17297300 | 2856369 | 10439484 | 3226560 | 211990 | 0
Fuel Cost | 0 | 0 | 5637060 | 3982230 | 5257746.99 | 1339979.52 | 0 | 0 | 8228670 |  | 0 | 9606170 | 7311792 | 14077324.8 | 14177801.04 | 11180854.44 | 0 | 0 | 5139830 | 0 | 1489132.8 | 1969920 | 25406092.8 | 5931511.82 | 0 | 0 | 0 | 8317620 | 9658812.79 | 11923303.6 | 328590 | 450000 | 0 | 0 | 0 | 7686025.44 | 0 | 545499.63 | 225720 | 5068000 | 0 | 4028227.61 | 5360378.02 | 0 | 5045059.4 | 0 |  | 0 | 0 | 5746677.7 | 8369238 | 12076992 | 8203852.8 | 576918.72 | 1013601.6 | 0 | 937254.4 | 1988072.1 | 5085798 | 8147000 | 4602760 | 258937.83 | 2547572 | 412251.12 | 199584 | 0 | 2124712.62 | 0 | 5564049.6 | 7770663.1 | 588827.88 | 134190 | 1432025 | 358155 | 24199200 | 3323.1 | 10311974.4 | 466618.32 | 212799 | 3298040 | 1670784 | 1941624 | 1610331.84 | 2988364.08 | 2346240 | 2166747.84 | 3887232 | 0 | 5484636.3 | 0 | 0 | 498657.6 | 7206855 | 401814 | 159600 | 5855794.56 | 50855137.2 | 11240980.74 | 7762560.96 | 21640320 | 9436232.96 | 31997810.4 | 1526071.05 | 18495936 | 19394592 | 4905770.7 | 8702010 | 15857856 | 19370194.2 | 0 | 0 | 29477400.12 | 6895140.85 | 0 | 11263428 | 22107514.8 | 16124659.2 | 0 | 0 |  | 123406427.52 | 0 | 6773155.2 | 0 | 15725030.4 | 56309299.2 | 0 | 0 | 2316192 | 0 | 6076162.5 | 0 | 1167880.05 | 15178752 | 0 | 0 | 123000 | 6128981.76 | 2170430 | 9169732.8 | 0 | 0 | 2850749.55 | 7874481.6 | 2559781.5 | 940032 | 350200.8 | 196459.668 | 0 | 0 | 20081642 | 0 | 0 | 0 | 0 | 5595060.24 | 0 | 2978517 | 13569897.6 | 5217987.06 | 0 | 8756099.55 | 5722790.4 | 6121320.66 | 18516888 | 0 | 18594201.6 | 0 | 411667.75 | 17188312.32 | 59669758 |  | 639276737.39 | 441740890.728 | 1081017628.118 | 105685194.358 | 123406427.52 | 55097449.49 | 571734212.41 | 79751400 | 771219.63 | 118221986.91 | 24199200 | 2150537.8 | 0
Yesterday Day Peak | 0 | 0 | 170 | 115 | 200 | 42 | 0 | 0 | 350 |  | 0 | 420 | 260 | 100 | 80 | 55 | 0 | 0 | 94 | 0 | 7 | 7 | 145 | 17 | 0 | 0 | 0 | 53 | 55 | 55 | 0 | 25 | 29 | 33 | 33 | 40 | 0 | 86 | 35 | 115 | 0 | 25 | 205 | 0 | 139 | 0 |  | 0 | 7 | 47 | 40 | 0 | 45 | 20 | 2 | 0 | 0 | 80 | 260 | 300 | 213 | 8 | 90 | 16 | 5 | 0 | 51 | 0 | 0 | 43 | 19 | 8 | 33 | 18 | 100 | 151 | 48 | 17 | 2 | 83 | 43 | 49 | 46 | 115 | 100 | 63 | 82 | 0 | 132 | 0 | 0 | 10 | 300 | 16 | 8 | 0 | 285 | 0 | 25 | 130 | 0 | 132 | 16 | 100 | 1 | 30 | 412 | 16 | 102 | 0 | 5 | 179 | 18 | 0 | 17 | 102 | 100 | 0 | 17 |  | 892 | 0 | 175 | 0 | 99 | 120 | 0 | 0 | 0 | 0 | 40 | 0 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 20 | 7 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 189 | 0 | 403 | 17 | 0 | 79 | 0 | 104 | 0 | 5 | 109 | 440 |  | 10495 | DayPeak
Yesterday Evening Peak | 0 | 0 | 170 | 115 | 200 | 42 | 0 | 0 | 352 | 0 | 0 | 450 | 250 | 16 | 80 | 55 | 0 | 0 | 175 | 0 | 7 | 7 | 150 | 26 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 29 | 33 | 33 | 51 | 0 | 88 | 35 | 115 | 0 | 25 | 204 | 0 | 138 | 0 | 0 | 0 | 9 | 0 | 100 | 82 | 50 | 20 | 0 | 0 | 80 | 0 | 275 | 345 | 214 | 8 | 86 | 16 | 5 | 0 | 51 | 0 | 50 | 52 | 19 | 8 | 33 | 21 | 158 | 156 | 48 | 17 | 0 | 87 | 43 | 46 | 41 | 110 | 100 | 65 | 87 | 0 | 132 | 0 | 0 | 10 | 280 | 24 | 11 | 150 | 300 | 180 | 93 | 190 | 93 | 132 | 0 | 100 | 190 | 46 | 419 | 105 | 102 | 0 | 0 | 180 | 54 | 0 | 100 | 111 | 100 | 0 | 17 |  | 892 | 0 | 235 | 0 | 96 | 210 | 0 | 0 | 9 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 35 | 96 | 0 | 0 | 36 | 52 | 24 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 183 | 0 | 88 | 98 | 187 | 0 | 314 | 35 | 150 | 108 | 0 | 96 | 0 | 0 | 109 | 600 |  | 12722 | EvPeak
Forecast for Evening | 0 | 0 | 170 | 115 | 200 | 41 | 0 | 0 | 360 | 0 | 0 | 450 | 305 | 100 | 100 | 55 | 0 | 0 | 190 | 0 | 7 | 16 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 88 | 35 | 120 | 0 | 25 | 221 | 0 | 145 | 0 | 0 | 0 |  | 102 | 100 | 84 | 50 | 21 | 5 | 0 | 80 | 0 | 360 | 360 | 225 | 8 | 95 | 30 | 5 | 0 | 51 | 0 | 50 | 52 | 22 | 10 | 33 | 21 | 173 | 160 | 49 | 17 | 0 | 90 | 43 | 51 | 44 | 115 | 110 | 65 | 86 | 0 | 132 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 430 | 115 | 100 | 100 | 0 | 300 | 54 | 110 | 100 | 113 | 100 | 0 | 104 |  | 905 | 16 | 410 | 0 | 115 | 220 | 0 | 0 | 30 | 60 | 40 | 0 | 33 | 110 | 0 | 70 | 65 | 50 | 40 | 100 | 0 | 0 | 50 | 52 | 30 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 225 | 0 | 92 | 100 | 220 | 0 | 414 | 105 | 200 | 113 | 100 | 105 | 0 | 0 | 113 | 560
Forecast for Day | 0 | 0 | 170 | 115 | 200 | 41 | 0 | 0 | 360 | 0 | 0 | 450 | 305 | 100 | 100 | 55 | 0 | 0 | 150 | 0 | 7 | 16 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 88 | 35 | 120 | 0 | 25 | 221 | 0 | 145 | 0 | 0 | 0 |  | 102 | 100 | 84 | 50 | 21 | 10 | 0 | 80 | 0 | 360 | 360 | 225 | 8 | 95 | 30 | 5 | 0 | 51 | 0 | 0 | 52 | 22 | 10 | 33 | 21 | 162 | 160 | 49 | 17 | 1.6 | 90 | 43 | 51 | 44 | 115 | 100 | 65 | 86 | 0 | 132 | 18 | 0 | 10 | 341 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 200 | 150 | 430 | 115 | 100 | 100 | 5 | 300 | 54 | 110 | 100 | 113 | 100 | 0 | 104 |  | 905 | 0 | 410 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 0 | 33 | 110 | 0 | 70 | 65 | 0 | 0 | 100 | 0 | 0 | 50 | 52 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 225 |  | 92 | 50 | 220 | 0 | 414 | 90 | 100 | 113 | 100 | 105 | 0 | 8 | 113 | 560
Generation at 08:00(Today) | 0 | 0 | 170 | 115 | 200 | 42 | 0 | 0 | 273 | 0 | 0 | 340 | 285 |  | 97 | 40 | 0 | 0 | 120 | 0 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 89 | 35 | 115 | 0 | 0 | 204 | 0 | 104 | 0 | 0 | 0 | 8 | 0 | 0 | 11 | 0 | 18 | 3 | 0 | 80 | 0 | 260 | 368 | 104 | 8 | 95 | 16 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 5 | 33 | 18 | 114 | 155 | 40 | 17 | 0 | 85 | 43 | 43 | 42 | 110 | 8 | 51 | 87 | 0 | 132 | 0 | 0 | 10 | 270 | 24 | 8 | 0 | 195 | 0 | 0 | 150 | 0 | 131 | 11 | 60 | 0 | 50 | 421 | 8 | 0 | 0 | 2 | 179 | 18 | 0 | 0 | 105 | 100 | 0 | 7 | 0 | 900 | 0 | 270 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 170 | 0 | 362 | 17 | 0 | 35 | 0 | 98 | 0 | 3 | 109 | 550 | 0
199
| Minimum Generation |  | 9260 | 7:00
| Highest Generation |  | 12722 | 19:00
| Day Peak Generation |  | 10495 | 12:00
| Evening Peak Generation |  | 12722 | 19:00
| HVDC Max Flow |  | 897 | 2:00
| HVDC EvPeak Flow |  | 892 | 19:00
| Load factor L.F |  | 86.73%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-10-13
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-10-12 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10495 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 9317 | MW
Evening Peak Generation : |  | 12722 | MW Hour : | 19:00 | Available Max Generation : |  | 15017 | MW
E.P. Demand (at gen end) : |  | 12722 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 13100 | MW
Maximum Generation : |  | 12722 | MW Hour : | 19:00 | Reserve(Generation end) |  | 1917 | MW
Total Gen. (MKWH) : |  | 264.8155 | System Load Factor : | 86.73% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -32 | MW at | 19:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-10-13
Actual : | 102.1 | Ft.(MSL) , | Rule curve : | 107.1 | Ft.( MSL )
Gas Consumed : | Total = | 1205.43 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 160782643.848
: |  | Coal : | 79751400 | Oil : | 689956199.32 | Total : | 930490243.168
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4603.9201 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1570.3435 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1407.8232 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1272.3879 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1149.6726 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 927.7571 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 512.6361 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 238.7105 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 715.5616 |  |  | 0 | 0%
Total | 0 |  | 12398.8125 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Baghabari-71 MW,100 MW
3) Ghorasal Unit-1,2,3,4
4) Ashuganj unit-3,4
5) Kaptai-2,4
6) Raozan #2
7) Siddirganj-335 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Saidpur 132/33 kV T3 transformer was under shut down from 08:45 to 15:56 for A/M.
b) Sirajganj 132/33 kV T1 transformer was under shut down from 08:39 to 16:42 for A/M.
c) Patuakhali 132/33 kV T2 transformer was under shut down from 07:07 to 17:13 for A/M.
d) Niamatpur 132/33 kV T3 transformer was under shut down from 10:08 to 13:12 for C/M.
e) Uttara 132/33 kV T3 transformer was under shut down from 09:42 to for C/M.
f) Barisal-Bhola 230 kV Ckt tripped at 11:13 from both end showing Dist. A,B-phase relays and was |  |  |  |  | About 30 MW power interruption occurred under Barisal Zone
switched on at 11:58. |  |  |  |  | from 11:13 to 11:58.
g) Faridpur-Gopalganj 132 kV Ckt-1 tripped at 12:20 showing Dist. C-phase relay at Faridpur end and
was switched on at 12:30.
h) Mymensing-Netrokona 132 kV Ckt-2 tripped at 11:24 from both end showing Dist. Z1,3-phase relay
at Mymensing end & Dist. Z2,3-phase relay at Netrokona end and was switched on at 13:25.
i) Rangamati-Khagrachari 132 kV Ckt-2 was under shut down from 08:36 to 13:24 for A/M.
j)Mymensing-Jamalpur 132 kV Ckt-1 was under shut down from 09:35 to 14:10 for C/M.
k) Ishwardi-Bheramara 132 kV Ckt-2 was under shut down from 05:54 to 15:54 due to relay replacement
work at Ishwardi end.
l) Sikalbaha 132 kV Bus-B was under shut down from 08:49 to 12:05 due to installing L/A by PDB.
m) Jessore 132/33 kV T2 transformer was under shut down from 09:01 to 11:40 due to replacement
Y-phase PT of 33 kV Bus by WZPDCL.
n) Siddirganj 210 MW GT-1 was shut down at 08:33 for replacement air filter.
o) Mymensing-Jamalpur 132 kV Ckt-2 was under shut down from 14:25 to 17:42 for C/M.
p) Ashuganj unit-4 was synchronized at 15:11.
q) Mymensing 33 kV Bus along with 132/33 kV T2 transformer was shut down at 06:04(13/10/2020) for C/M. |  |  |  |  | About 50 MW power interruption occurred under Mymensing S/S area
from 06:04(13/10/2020) to till.
r) Rampura-Gulshan 132 kV Ckt-1 was shut down from 05:27(13/10/2020) to 07:59(13/10/2020) for C/M.
s) Madunaghat-TK. Chemical 132 kV Ckt was shut down at 05:51(13/10/20200 for C/M.
t) Dohazari-Cox'sbazar 132 kV Ckt-2 was shut down at 06:08(13/10/20200 for D/W.
u) Munshiganj 33 kV Bus along with 132/33 kV T1 transformer was shut down at 07:10(13/10/2020) |  |  |  |  | About 30 MW power interruption occurred under Munshiganj S/S area
for C/M. |  |  |  |  | from 07:10(13/10/2020) to till.
v) Ishwardi-Bheramara 132 kV Ckt-2 tripped at 07:35(13/10/2020) showing backup relay at Ishwardi
end and was switched on at 07:50(13/10/2020).
x) Ashuganj 225 MW CCPP STG tripped at 07:45(13/10/2020) due to main solenoid valve problem.
y) Patuakhali 132/33 kV T2 transformer was shut down at 07:03(13/10/2020) for A/M.
z) Bheramara 132/33 kV T1 transformer and its 33 kV Bus was shut down at 07:30(13/10/2020) due to |  |  |  |  | About 12 MW power interruption occurred under Bheramara S/S area
red hot maintenance at 33 kV end. |  |  |  |  | from 07:30(13/10/2020) to till.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-10-12 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 170 | 3861000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 115 | 2709000 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 4736709 | Machin problem.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 42 | 1015136 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 352 | 7989000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 8813000
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 16 | 1854720 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 250 | 6587200 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 80 | 2057736 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1321614
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 26 | 643331 | Fuel Shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 438120
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 175 | 2971000
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 7 | 197760 | Fuel Shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under Maintenance
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 7 | 216000 | Fuel Shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel Shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1139400
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 2581920
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1249523
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 1209260
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 54 | 1278780 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 815700
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 831900
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 794832
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 6726870
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 180 | 662013 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 93 | 464268
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 93 | 564368 | Fuel Shortage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 132 | 3251810 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 102 | 2049756
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 434880 | Fuel Shortage
| Dhaka area Total |  |  |  | 5895 | 3349 | 69466606
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 115 | 2800000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 433609
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 130545
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1035840
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 123 | 2856369 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4917778
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 138 | 2967682
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Transformer overload
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 9 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 592441 | Reserve.
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 876360
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2269440
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 457872
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 0 | 341280
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 82 | 1388160 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 30840
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 180 | 3899127 | Transformer O/L.
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 791635
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Transformer overload
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2421120
| Chattogram area Total |  |  |  | 2266 | 1300 | 28210098
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 80 | 633280 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 1352430 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 214 | 5003000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 275 | 6872700 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 345 | 8147000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 16 | 364824 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 142560 | Auxilary CB problem.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1242522
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 46 | 695854 | R/H at APSCL
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 550896
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 86 | 2215280
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 190 | 1787520
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 463644
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 178920
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 158 | 3226560
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 818300
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 813682
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 477540
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 150 | 344256 | Low demand
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 100 | 1128600
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 111 | 2579640
| Cumilla Area Total |  |  |  | 2980 | 2018 | 39239735
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 156 | 3135 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 367416 | Engine problem
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 48 | 1135680 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13350
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 190 | 4161600
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 105 | 1738800 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 516 | 7419981
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 87 | 2011000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 1044240 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2621372
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 100 | 2256000 | FGMO & ST under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 46 | 1090800
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 41 | 1032264
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 210000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 65 | 1099872 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 87 | 2035200
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 132 | 3170310
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 535752
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7135500 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 419 | 9357000
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 244440
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 63300 | On test
| Sylhet Area Total |  |  |  | 1988 | 1455 | 33907050
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 892 | 21424727
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 96 | 2000640
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 9 | 220800 | Low demand
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 210 | 4062720 | Engine problem
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 235 | 6450624 | Gas shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 583125
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 98 | 797760
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 35 | 548160 | Engine problem
107 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Line O/L.
| Khulna Area Total |  |  |  | 2284 | 1615 | 36088556
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1555200
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 38 | 753471
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 88 | 1985678
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 600 | 13592200
| Barisal Area Total |  |  |  | 1054 | 836 | 17886549
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 60000 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 622864
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 35 | 213625
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel Shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel Shortage
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 36 | 294195
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas Shortage
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 183 | 4238682 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 187 | 4459818 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 314 | 8844545 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 24 | 263895
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 489600
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 10 | 225936
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 259524
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 812640
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 96 | 1036128
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 150 | 359866 | Line O/L.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 108 | 1951200
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 2325888
| Rajshahi Area Total |  |  |  | 2183 | 1387 | 26458406
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3705100 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 96 | 2396160 | Engine problem
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 37255
| Rangpur Area Total |  |  |  | 605 | 246 | 6138515
| Total |  |  |  | 19892 | 12722 | 264815496
| Eastern Grid Total |  |  |  | 13766 | 8638 | 178243470
| Western Grid Total |  |  |  | 6126 | 4084 | 86572026
| National Grid Total |  |  |  | 19892 | 12722 | 264815496
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-10-12
| (a) ENTIRE EASTERN GRID : |  | 8192 | MW | (b) ENTIRE WESTERN GRID : |  | 3837 | MW
| i) Dhaka area |  | 4291 | MW | i) Khulna area |  | 1461 | MW
| ii) Chittagong area |  | 1240 | MW | ii) Rajshahi area |  | 1282 | MW
| iii) Comilla area |  | 1150 | MW | iii) Barisal area |  | 361 | MW
| iv) Mymensingh area |  | 969 | MW | iv) Rangpur area |  | 733 | MW
| v) Sylhet area |  | 542 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 12029 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 134 | 15:00 | Sherpur | 114 | 1:00 | Jhenida | 108 | 21:00
| Munsiganj | 120 | 19:30 | Srimongal | 50 | 18:00 | Bottail | 130 | 18:30
| Sonargaon | 86 | 22:00 | Shahjibazar | 123 | 21:00 | G.K Project | 56 | 19:00
| Shyampur | 198 | 9:00 | Fenchuganj | 45 | 1:00 | Faridpur | 198 | 0.041667
| Bhulta | 202 | 19:00 | Kulawara | 50 | 18:30 | Madaripur | 99 | 0.875
| Madanganj | 55 | 3:00 | Sylhet | 150 | 18:00 | Sariatpur | 64 | 1:00
| Shitalakhya | 128 | 12:00 | Chatak | 32 | 19:00 | Gopalganj | 88 | 19:00
| Rahim steel | 18 | 5:00 | Sunamganj | 51 | 19:30 | Bagerhat | 102 | 21:00
| Matuail | 81 | 9:00 | Biani Bazar | 62 | 18:30 | Mongla | 38 | 9:00
| Ghorasal | 81 | 19:00 | Comilla (S) | 160 | 18:30 | Satkhira | 114 | 0.91667
| Narsingdi | 168 | 20:00 | Comilla(N) | 139 | 19:30 | Gallamari | 52 | 13:00
| Haripur (SBU) | 111 | 21:00 | Chandpur | 108 | 23:00 | Magura | 48 | 0.041667
| Ullon | 65 | 13:00 | Feni | 129 | 18:30 | Norail | 37 | 22:00
| Hasnabad | 191 | 20:00 | Chowmuhani | 190 | 18:00 | Chuadanga | 93 | 23:00
| Magbazar | 105 | 11:00 | Ashuganj | 60 | 23:00 | Barisal(N) | 45 | 0.83333
| Maniknagar | 102 | 10:00 | Daudkandi | 148 | 19:30 | Barisal (S) | 108 | 0.79167
| Bangabhaban | 36 | 10:00 | B.Baria | 162 | 21:00 | Patuakhali | 129 | 0.91667
| Narinda | 88 | 18:30 | Ramganj | 120 | 18:30 | Bhandaria | 58 | 0.91667
| Dhanmondi | 185 | 13:00 | Chaddagram | 40 | 18:00 | Borhan Uddin | 46 | 1:00
| Lalbag | 92 | 13:00 | PHP | 10 | 17:00 | Ishurdi | 61 | 18:30
| Madartek | 73 | 23:00 | Madunaghat | 55 | 21:00 | Ruppur Paromanobik | 3 | 9:00
| Dhaka University |  |  | Hathazari | 107 | 0.79167 | Natore | 123 | 18:30
| Fatullah | 43 | 0.66667 | Khulshi | 216 | 0.5 | Bogra | 176 | 18:30
| Mirpur | 120 | 18:00 | Halishahar | 162 | 0.58333 | Noagaon | 116 | 21:00
| Kalyanpur | 93 | 19:30 | Baraulia | 163 | 0.041667 | Rajshahi | 154 | 20:00
| Gulshan | 138 | 4:00 | Sikalbaha | 26 | 0.75 | Rajshahi New | 13 | 19:00
| Uttara | 103 | 18:00 | Dohazari | 94 | 0.83333 | C.Nawabganj | 69 | 21:00
| Uttara New | 34 | 18:00 | Cox'sbazar | 99 | 0.875 | Amnura | 44 | 20:00
| Kamrangirchar | 94 | 19:00 | Chandraghona | 32 | 0.75 | Pabna | 128 | 19:00
| Savar | 137 | 10:00 | Kaptai | 4.5 | 0.75 | Shahjadpur | 112 | 18:30
| Bhasantec | 159 | 18:00 | A. Khaer Stl. | 0 | 0.041667 | Serajganj | 108 | 19:30
| Agargaon | 78 | 4:00 | Bakulia | 121 | 0.77083 | Niyamatpur | 56 | 1:00
| Satmosjid | 103 | 18:00 | Julda | 21 | 0.5 | Joypurhat | 58 | 21:00
| Tongi | 106 | 0.375 | TK chemical | 28 | 0.041667 | Sherpur(Bogura) | 48 | 18:30
| Kabirpur | 240 | 15:00 | Modern Steel | 14 | 0.20833 | Mohastangor | 50 | 18:30
| Basundhara | 143 | 18:00 | Shahmirpur | 25.6 | 0.75 | Rangpur | 150 | 18:30
| Manikganj | 70 | 21:00 | Khagrachhari | 26 | 0.20833 | Lalmonirhat | 52 | 22:00
| Joydevpur | 157 | 18:00 | Matarbari | 36.5 | 0.875 | Saidpur | 102 | 18:30
| New Tongi | 110 | 10:00 | Baroiar Hat | 50 | 0.83333 | Purbasadipur | 101 | 20:00
| Kodda | 224 | 18:30 | Rangamati | 12 | 0.75 | Thakurgaon | 78 | 20:00
| Dhamrai | 98 | 18:30 | Abul Khair 230 | 28 | 0.70833 | Palashbari | 121 | 19:30
| Rajendrapur | 110 | 19:00 | BSRM | 103 | 0.16667 | Barapukuria | 50 | 19:30
| Valuka | 136 | 19:30 | GPH Ispat | 79 | 0.375 | Panchagar | 50 | 19:30
| Tangail | 202 | 19:00 | Goalpara | 30 | 0.54167 | Joldhaka | 36 | 19:00
| Mymensing | 160 | 21:00 | Central s/s | 87 | 18:30 | Kurigram | 55 | 18:30
| Kishorganj | 140 | 1:00 | Noapara | 51 | 22:00
| Netrokona | 117 | 19:00 | Jessore | 107 | 20:00
| Jamalpur | 144 | 19:30 | Benapol | 48 | 18:30
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-10-12 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 401 | 3:00 | 392 | 10:00 | Kaliakoir | 392 | 0.375 | 380 | 0.45833
| Bheramara | 401 | 3:00 | 387 | 18:30 | Bhulta | 372 | 0.125 | 358 | 0.41667
| Ashuganj(N) | 380 | 4:00 | 366 | 10:00 | Gopalganj | 412 | 0.375 | 380 | 0.77083
| Payra | 417 | 10:00 | 401 | 18:30
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 225 | 22:00 | Comilla (N) | 233 | 11:00 | 223 | 10:00
| Ishurdi | 235 | 6:00 | 224 | 19:30 | Hathazari | 223 | 1:00 | 219 | 11:00
| Ashuganj | 232 | 3:00 | 225 | 10:00 | Megnaghat | 223 | 6:00 | 218 | 9:00
| Serajganj | 230 | 1:00 | 225 | 10:00 | Fenchuganj | 238 | 5:00 | 234 | 18:00
| Baghabari | 239 | 17:00 | 234 | 22:00 | Siddhirganj | 222 | 3:00 | 210 | 7:00
| Barapukuria | 238 | 17:00 | 228 | 18:00 | Maniknagar | 221 | 3:00 | 210 | 10:00
| Bogra | 227 | 7:00 | 216 | 20:00 | Agargaon | 218 | 3:00 | 205 | 11:00
| Rajshahi | 225 | 7:00 | 215 | 20:00 | Barisal | 250 | 1:00 | 226 | 12:00
| Khulna South | 228 | 10:00 | 219 | 20:00 | AKSML | 221 | 3:00 | 216 | 11:00
| Rampura | 222 | 4:00 | 215 | 10:00 | BSRM | 221 | 9:00 | 216 | 9:00
| Haripur | 220 | 5:00 | 211 | 10:00 | Bibiyana | 238 | 4:00 | 231 | 24:00
| Hasnabad | 220 | 1:00 | 210 | 10:00 | Bhulta | 224 | 19:00 | 215 | 17:00
| Shyampur | 220 | 10:00 | 208 | 11:00 | Ashuganj (S) | 230 | 3:00 | 224 | 11:00
| Aminbazar | 217 | 3:00 | 207 | 11:00 | Kaliakoir | 221 | 4:00 | 210 | 16:00
| Tongi | 215 | 4:00 | 208 | 9:00 | GPH | 221 | 4:00 | 217 | 13:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 130 | 4:00 | 123 | 9:00 | Hathazari | 133 | 0.625 | 131 | 0.33333
| Munsiganj | 133 | 18:30 | 123 | 10:00 | Khulshi | 132 | 0.083333 | 128 | 0.33333
| Sonargaon | 130 | 3:00 | 126 | 10:00 | Halishahar | 135 | 0.041667 | 129 | 0.45833
| Shyampur | 132 | 18:30 | 122 | 10:00 | Baraulia | 134 | 0.125 | 129 | 0.29167
| Bhulta | 123 | 18:00 | 117 | 10:00 | Sikalbaha | 135 | 1:00 | 132 | 0.33333
| Madanganj | 132 | 18:30 | 124 | 8:00 | Dohazari | 134 | 1:00 | 125 | 0.83333
| Shitalakhya | 133 | 18:00 | 123 | 9:00 | Cox'sbazar | 121 | 0.25 | 110 | 0.54167
| Rahim steal | 130 | 5:00 | 123 | 10:00 | Chandraghona | 134 | 0.041667 | 131 | 0.375
| Matuail | 130 | 4:00 | 123 | 9:00 | Kaptai | 132 | 1:00 | 130 | 0.45833
| Ghorasal | 135 | 1:00 | 133 | 10:00 | A. Khaer Stl. | 131 | 0.083333 | 129 | 8:00
| Narsinghdi | 127 | 19:00 | 116 | 10:00 | Bakulia | 134 | 0.041667 | 130 | 0.33333
| Haripur (SBU) | 131 | 18:30 | 126 | 18:00 | Julda | 136 | 0.041667 | 132 | 0.33333
| Ullon | 131 | 5:00 | 122 | 10:00 | TK Chemical | 134 | 0.125 | 131 | 9:00
| Hasnabad | 131 | 6:00 | 123 | 10:00 | Modern Steel | 133 | 0.041667 | 130 | 0.33333
| Magbazar | 130 | 2:00 | 121 | 10:00 | Shahmirpur | 134 | 0.041667 | 130 | 0.33333
| Maniknagar | 132 | 5:00 | 124 | 10:00 | Khagrachhari | 134 | 0.20833 | 129 | 0.45833
| Bangabhaban | 132 | 5:00 | 124 | 10:00 | Matarbari | 123 | 0.041667 | 116 | 0.8125
| Narinda | 132 | 5:00 | 124 | 10:00 | Baroiar Hat | 130 | 0.41667 | 127 | 0.20833
| Dhanmondi | 131 | 5:00 | 122 | 10:00 | Rangamati | 134 | 0.16667 | 130 | 11:00
| Lalbag | 133 | 3:00 | 118 | 11:00 | Goalpara S/S | 138 | 10:00 | 133 | 21:00
| Madartek | 130 | 7:00 | 122 | 10:00 | Khulna Central S/S | 138 | 0.125 | 133 | 21:00
| Dhaka University |  |  |  |  | Noapara | 135 | 10:00 | 131 | 21:00
| Fatuiiah | 133 | 0.77083 | 124 | 10:00 | Jessore | 133 | 17:00 | 124 | 21:00
| Mirpur | 133 | 4:00 | 121 | 11:00 | Benapol | 131 | 8:00 | 123 | 21:00
| Kalyanpur | 130 | 4:00 | 123 | 11:00 | Jhenida | 129 | 0.33333 | 117 | 21:00
| Gulshan | 130 | 4:00 | 121 | 11:00 | Bottail | 135 | 17:00 | 126 | 21:00
| Uttara | 129 | 4:00 | 124 | 11:00 | G.K Project | 141 | 0.70833 | 136 | 1:00
| Uttara New | 131 | 4:00 | 118 | 11:00 | Faridpur | 135 | 9:00 | 127 | 1:00
| Kamrangirchar | 128 | 19:00 | 121 | 11:00 | Madaripur | 136 | 0.70833 | 130 | 13:00
| Savar | 130 | 4:00 | 125 | 11:00 | Shariyatpur S/S | 137 | 0.70833 | 129 | 11:00
| Bhasantec | 134 | 4:00 | 121 | 11:00 | Gopalganj | 138 | 9:00 | 125 | 18:00
| Agargaon | 136 | 4:00 | 125 | 10:00 | Bagerhat | 134 | 14:00 | 125 | 22:00
| Satmosjid | 136 | 4:00 | 126 | 11:00 | Mongla | 131 | 0.70833 | 122 | 20:00
| Tongi | 132 | 0.16667 | 126 | 9:00 | Satkhira | 137 | 0.41667 | 129 | 20:00
| Kabirpur | 136 | 17:00 | 131 | 10:00 | Gallamari | 138 | 10:00 | 135 | 18:30
| Basundhara | 130 | 14:00 | 128 | 10:00 | Magura | 130 | 17:00 | 115 | 20:00
| Manikganj | 136 | 13:00 | 122 | 8:00 | Norail | 129 | 0.70833 | 113 | 20:00
| Joydevpur | 139 | 13:00 | 128 | 9:00 | Chuadanga | 123 | 8:00 | 105 | 21:00
| New Tongi | 131 | 0.125 | 132 | 8:00 | Barisal(N) | 141 | 5:00 | 128 | 12:00
| Kodda | 133 | 4:00 | 125 | 0.29167 | Barisal (S) | 139 | 0.375 | 129 | 18:00
| Dhamrai | 136 | 5:00 | 123 | 21:00 | Patuakhali(S) | 135 | 0.375 | 123 | 18:00
| Rajendrapur | 132 | 14:00 | 130 | 9:00 | Bhandaria | 129 | 14:00 | 118 | 21:00
| Valuka | 121 | 17:00 | 107 | 21:00 | Ishurdi | 138 | 7:00 | 132 | 20:00
| Tangail | 135 | 5:00 | 125 | 19:30 | Ruppur Paromanobik | 138 | 7:00 | 132 | 20:00
| Mymensing | 122 | 5:00 | 112 | 21:00 | Natore | 137 | 8:00 | 131 | 20:00
| Kishorganj | 126 | 17:00 | 115 | 19:30 | Bogra | 138 | 17:00 | 129 | 18:30
| Netrokona | 121 | 17:00 | 107 | 21:00 | Noagaon | 133 | 7:00 | 122 | 20:00
| Jamalpur | 137 | 17:00 | 125 | 21:00 | Rajshahi | 135 | 6:00 | 130 | 19:30
| Sherpur | 136 | 17:00 | 124 | 21:00 | Rajshahi New | 137 | 4:00 | 130 | 20:00
| Srimongal | 135 | 17:00 | 129 | 0.95833 | C.Nawabganj | 135 | 3:00 | 128 | 20:00
| Shahjibazar | 131 | 6:00 | 127 | 0.8125 | Amnura | 134 | 2:00 | 129 | 13:00
| Fenchuganj | 134 | 5:00 | 131 | 0.91667 | Pabna | 135 | 8:00 | 130 | 18:30
| Khulawara | 133 | 7:00 | 130 | 0.041667 | Shahjadpur | 139 | 7:00 | 134 | 19:00
| Sylhet | 131 | 5:00 | 128 | 0.041667 | Serajganj | 134 | 7:00 | 127 | 20:00
| Chatak | 130 | 7:00 | 124 | 18:30 | Niyamatpur | 132 | 6:00 | 119 | 20:00
| Sunamganj | 128 | 5:00 | 122 | 0.77083 | Joypurhat | 134 | 7:00 | 120 | 19:00
| Biani Bazar | 130 | 7:00 | 124 | 0.77083 | Sherpur(Bogura) | 137 | 17:00 | 128 | 20:00
| Comilla(s) | 128 | 7:00 | 119 | 18:00 | Mohastangor | 136 | 7:00 | 125 | 18:30
| Comilla(n) | 136 | 18:00 | 131 | 12:00 | Rangpur | 133 | 17:00 | 117 | 18:30
| Chandpur | 136 | 18:00 | 128 | 6:00 | Lalmonirhat | 135 | 6:00 | 116 | 22:00
| Feni | 135 | 19:00 | 128 | 15:00 | Saidpur | 132 | 7:00 | 119 | 21:00
| Chowmuhani | 134 | 19:00 | 126 | 0:00 | Purbasadipur | 129 | 7:00 | 112 | 18:30
| Ashuganj | 130 | 5:00 | 126 | 21:00 | Thakurgaon | 130 | 6:00 | 113 | 20:00
| Daudkandi | 135 | 18:30 | 123 | 0:00 | Palashbari | 134 | 17:00 | 120 | 20:00
| B.Baria | 128 | 7:00 | 122 | 22:00 | Barapukuria | 138 | 17:00 | 128 | 21:00
| Ramganj | 128 | 21:00 | 120 | 0:00 | Panchagar | 126 | 6:00 | 110 | 20:00
| Chaddagram | 134 | 18:00 | 128 | 16:00 | Joldhaka | 133 | 6:00 | 115 | 20:00
| PHP | 133 | 18:30 | 128 | 7:00 | Kurigram | 131 | 17:00 | 112 | 21:00
| Madanhat | 135 | 1:00 | 130 | 9:00

## L-Curve
Date | 2020-10-12
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 152 | 8023 | 4069 | 12092 |  |  |  | QF-LDC-11
0:30 | 108.5 | 8032.5 | 3974.5 | 12007 | Date: | 2020-10-12
1:00 | 65 | 8042 | 3880 | 11922
1:30 | 55.5 | 7936.5 | 3829 | 11765.5
2:00 | 46 | 7831 | 3778 | 11609
2:30 | 58 | 7776 | 3718 | 11494 | [5 empty] | Gen. at Eve. Peak | 12722 | 12722 MW (19:00 )
3:00 | 70 | 7721 | 3658 | 11379 | [6 empty] | 19:00
3:30 | 67.5 | 7551.5 | 3617 | 11168.5 | [5 empty] | Gen. at Day Peak | 10495 | 10495 MW (12:00 )
4:00 | 65 | 7382 | 3576 | 10958 | [6 empty] | 12:00
4:30 | 61.5 | 7349 | 3485 | 10834 | [5 empty] | Highest Generation | 12722
5:00 | 58 | 7316 | 3394 | 10710 | [6 empty] | 19:00
5:30 | 90.5 | 7032 | 3232.5 | 10264.5
6:00 | 123 | 6748 | 3071 | 9819
6:30 | 168.5 | 6510 | 3029.5 | 9539.5
7:00 | 214 | 6272 | 2988 | 9260
7:30 | 292 | 6282.5 | 3002 | 9284.5
8:00 | 370 | 6293 | 3016 | 9309
8:30 | 381 | 6484.5 | 3014 | 9498.5
9:00 | 392 | 6676 | 3012 | 9688
9:30 | 461 | 6797.5 | 3106 | 9903.5
10:00 | 530 | 6919 | 3200 | 10119
10:30 | 468.5 | 7053.5 | 3197.5 | 10251
11:00 | 407 | 7188 | 3195 | 10383
11:30 | 352.5 | 7267.5 | 3171.5 | 10439
12:00 | 298 | 7347 | 3148 | 10495
12:30 | 244 | 7366.5 | 3213 | 10579.5
13:00 | 190 | 7386 | 3278 | 10664
13:30 | 184 | 7408.5 | 3248.5 | 10657
14:00 | 178 | 7431 | 3219 | 10650
14:30 | 239 | 7504 | 3263.5 | 10767.5
15:00 | 300 | 7577 | 3308 | 10885
15:30 | 372.5 | 7512 | 3311 | 10823
16:00 | 445 | 7447 | 3314 | 10761
16:30 | 436 | 7242 | 3216 | 10458
17:00 | 427 | 7037 | 3118 | 10155
17:30 | 346 | 7590.5 | 3373 | 10963.5
18:00 | 265 | 8144 | 3628 | 11772
18:30 | 142.5 | 8391 | 3856 | 12247
19:00 | 20 | 8638 | 4084 | 12722
19:30 | 32 | 8586 | 4044 | 12630
20:00 | 29 | 8561 | 4075 | 12636 |  |  |  | Executive Engineer
20:30 | 20 | 8518 | 4098 | 12616 |  |  |  | Network Operation Division
21:00 | 11 | 8475 | 4121 | 12596
21:30 | 22.5 | 8433.5 | 4114.5 | 12548
22:00 | 34 | 8392 | 4108 | 12500 |  |  |  |  | Page 6 of 7
22:30 | 90 | 8303.5 | 4111 | 12414.5
23:00 | 146 | 8215 | 4114 | 12329
23:30 | 149 | 8119 | 4091.5 | 12210.5
24:00 | 152 | 8023 | 4069 | 12092
12722 MW (19:00 )
10495 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-10-12 |  | Energy | 264815496
[10 empty] | 2020-10-12 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4145 | 892 | 2054 | 3531 | 750 | 119 | 629 | 0 | 154
0:30 | 4037 | 894 | 2050 | 3416.5 | 750 | 118.5 | 679 | 0 | 153 | Date: | 2020-10-12
1:00 | 3929 | 896 | 2046 | 3302 | 750 | 118 | 729 | 0 | 152
1:30 | 3913.5 | 896.5 | 2015 | 3272 | 740 | 119 | 659.5 | 0 | 150 | [7 empty] | Total Energy | 264.8155 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 3898 | 897 | 1984 | 3242 | 730 | 120 | 590 | 0 | 148 | [7 empty] | Energy not Served | 0
2:30 | 3902 | 896 | 1977.5 | 3187.5 | 715 | 120 | 549 | 0 | 147 | [7 empty] | Energy Requirement | 264.8155
3:00 | 3906 | 895 | 1971 | 3133 | 700 | 120 | 508 | 0 | 146
3:30 | 3902.5 | 895 | 1952.5 | 3005.5 | 700 | 120.5 | 446.5 | 0 | 146 | [6 empty] | Shortage
4:00 | 3899 | 895 | 1934 | 2878 | 700 | 121 | 385 | 0 | 146
4:30 | 3906.5 | 893.5 | 1954.5 | 2816.5 | 700 | 121 | 298 | 0 | 144
5:00 | 3914 | 892 | 1975 | 2755 | 700 | 121 | 211 | 0 | 142
5:30 | 3861 | 892 | 1905.5 | 2465 | 700 | 122 | 182 | 0 | 137
6:00 | 3808 | 892 | 1836 | 2175 | 700 | 123 | 153 | 0 | 132
6:30 | 3749 | 892.5 | 1815.5 | 2002.5 | 685 | 123 | 145 | 0 | 124 |  |  |  |  | Coal
7:00 | 3690 | 893 | 1795 | 1830 | 670 | 123 | 137 | 0 | 116
7:30 | 3728.5 | 893 | 1784.5 | 1833.5 | 660 | 123 | 137 | 0 | 113 |  |  |  | Oil |  |  |  | ,
8:00 | 3767 | 893 | 1774 | 1837 | 650 | 123 | 137 | 0 | 110
8:30 | 3812 | 892.5 | 1868 | 1940.5 | 605 | 122.5 | 137 | 0 | 100
9:00 | 3857 | 892 | 1962 | 2044 | 560 | 122 | 137 | 0 | 90
9:30 | 3857.5 | 892.5 | 1990 | 2222 | 554.5 | 122 | 149.5 | 0 | 91
10:00 | 3858 | 893 | 2018 | 2400 | 549 | 122 | 162 | 0 | 92
10:30 | 3839 | 892.5 | 2019.5 | 2491.5 | 549.5 | 121.5 | 217 | 0 | 93
11:00 | 3820 | 892 | 2021 | 2583 | 550 | 121 | 272 | 0 | 94
11:30 | 3807 | 892 | 1978 | 2649.5 | 570 | 121 | 295.5 | 0 | 97
12:00 | 3794 | 892 | 1935 | 2716 | 590 | 121 | 319 | 0 | 100
12:30 | 3787 | 892.5 | 1954.5 | 2745 | 599.5 | 121 | 345.5 | 0 | 104
13:00 | 3780 | 893 | 1974 | 2774 | 609 | 121 | 372 | 0 | 108
13:30 | 3780 | 893 | 1974 | 2774 | 609 | 121 | 372 | 0 | 108
14:00 | 3780 | 893 | 1974 | 2774 | 609 | 121 | 372 | 0 | 108
14:30 | 3734 | 892.5 | 1956 | 2903 | 624.5 | 121 | 396.5 | 0 | 122
15:00 | 3688 | 892 | 1938 | 3032 | 640 | 121 | 421 | 0 | 136
15:30 | 3695.5 | 892 | 1944.5 | 2957 | 640 | 120 | 425 | 0 | 134
16:00 | 3703 | 892 | 1951 | 2882 | 640 | 119 | 429 | 0 | 132
16:30 | 3661.5 | 892 | 1882.5 | 2714.5 | 640 | 119 | 406 | 0 | 135
17:00 | 3620 | 892 | 1814 | 2547 | 640 | 119 | 383 | 0 | 138
17:30 | 3730 | 892 | 1884.5 | 3074 | 645 | 121 | 468 | 0 | 148
18:00 | 3840 | 892 | 1955 | 3601 | 650 | 123 | 553 | 0 | 158
18:30 | 3943 | 892 | 1954.5 | 3865.5 | 700 | 123 | 611 | 0 | 158
19:00 | 4046 | 892 | 1954 | 4130 | 750 | 123 | 669 | 0 | 158
19:30 | 4039 | 893 | 1994 | 3975 | 750 | 123 | 698 | 0 | 158
20:00 | 4041 | 892 | 1990 | 3975 | 751 | 123 | 704 | 0 | 160
20:30 | 4064.5 | 892 | 2010.5 | 3911.5 | 750.5 | 123.5 | 704.5 | 0 | 159
21:00 | 4088 | 892 | 2031 | 3848 | 750 | 124 | 705 | 0 | 158
21:30 | 4107 | 892 | 2025.5 | 3783 | 750 | 124 | 709.5 | 0 | 157
22:00 | 4126 | 892 | 2020 | 3718 | 750 | 124 | 714 | 0 | 156
22:30 | 4126.5 | 892 | 2029 | 3624.5 | 750 | 122 | 713.5 | 0 | 157
23:00 | 4127 | 892 | 2038 | 3531 | 750 | 120 | 713 | 0 | 158
23:30 | 4136 | 892 | 2046 | 3531 | 750 | 119.5 | 671 | 0 | 156 | Max Temp. in Dhaka |  | 33.0° C
24:00 | 4145 | 892 | 2054 | 3531 | 750 | 119 | 629 | 0 | 154
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
Note on W13: Author:

## Generation
g | 2020-10-12
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 83 | 85 | 85 | 86 | 86 | 88 | 88 | 88 | 87 | 87 | 86 | 86 | 86 | 86 | 86 | 84 | 84 | 88 |  | 88 | 88 | 88 | 89 | 89 | 85 | 84 | 2020369
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 836000
3 | Chattogram TPP-1 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | [7 empty] | 2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 433609
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 4 | 12 | 16 | 18 | 19 | 16 | 19 | 16 | 12 | 6 | [10 empty] | 130545
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 232 | 204 | 205 | 205 | 204 | 205 | 205 | 204 | 217 |  | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 4917778
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 105 | 104 | 104 | 104 | 106 | 104 | 104 | 104 | 139 | 138 | 139 | 139 | 140 | 110 | 140 | 139 | 140 | 100 |  | 138 | 139 | 139 | 139 | 140 | 139 | 140 | 2967682
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 85 | 19 | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 47 | 51 | 51 | 50 | 50 | 42 | [8 empty] | 0 | 592441
12 | Hathazari 100 MW peaking PP | [11 empty] | 7 | 8 | 8 | 8 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 8 | 8
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [17 empty] | 85 |  | 150 | 100 | 100 | 30 |  |  |  | 344256
14 | Titas 50 MW Peaking PP | 49 | [12 empty] | 25 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 0 | 550896
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 118 | 110 | 110 | 110 | 115 | 115 | 75 | 76 | 35 | 60 | 86 | 94 | 60 | 90 | 92 | 85 | 54 | 140 |  | 175 | 180 | 185 | 185 | 185 | 185 | 185 | 2971000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 300 | 300 | 300 | 300 | 300 | 145 | 145 | 145 | 180 | 280 | 300 | 285 | 280 | 300 | 300 | 296 | 283 | 298 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 6726870
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 3861000
23 | Ghorasal TPP Unit-5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2709000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4736709
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | [15 empty] | 25 | 60 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 633280
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 70 | 70 | 55 | [8 empty] | 0 | 1352430
32 | Ashuganj 50 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 364824
33 | Ashuganj 225 MW CCPP | 213 | 213 | 213 | 210 | 213 | 213 | 213 | 206 | 205 | 211 | 213 | 213 | 212 | 211 | 201 | 173 | 154 | 185 |  | 214 | 213 | 213 | 213 | 213 | 213 | 214 | 5003000
34 | Ashuganj 450 MW CCPP(South) | 355 | 355 | 355 | 355 | 355 | 355 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 355 | 345 | 345 | 345 | 345 |  | 345 | 345 | 345 | 345 | 345 | 345 | 345 | 8147000
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 260 | 260 | 260 | 260 | 275 | 260 | 360 | 260 | 270 | 260 | 260 | 260 | 280 | 275 | 275 | 300 |  | 275 | 275 | 275 | 275 | 275 | 265 | 280 | 6872700
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 142560
36 | Chandpur 150 MW CCPP | 96 | 90 | 96 | 97 | 97 | 93 | 96 | 96 | 96 | 96 | 96 | 90 | 95 | 95 | 96 | 86 | 87 | 95 |  | 86 | 95 | 93 | 96 | 94 | 95 | 96 | 2215280
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 400 | 400 | 370 | 370 | 340 | 320 | 320 | 390 | 420 | 420 | 420 | 420 | 350 | 350 | 400 | 400 | 420 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 8813000
41 | Haripur 360MW CCPP(HPL) | 351 | 351 | 351 | 325 | 325 | 303 | 262 | 262 | 332 | 345 | 344 | 350 | 345 | 323 | 345 | 349 | 347 | 339 |  | 352 | 350 | 348 | 350 | 350 | 350 | 351 | 7989000
42 | RPCL 210MW CCPP | 154 | 155 | 157 | 155 | 155 | 68 | 52 | 100 | 85 | 85 | 89 | 151 | 149 | 155 | 152 | 154 | 154 | 153 |  | 156 | 142 | 140 | 140 | 140 | 153 | 154 | 3135
43
44 | Fenchugonj CCPP Phase-1 | 87 | 87 | 87 | 86 | 86 | 86 | 86 | 85 | 87 | 85 | 83 | 83 | 85 | 85 | 83 | 85 | 86 | 83 |  | 87 | 85 | 85 | 85 | 85 | 85 | 85 | 2011000
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1044240
46 | Shajibazar 330 MW CCPP | 100 | 102 | 100 | 100 | 101 | 101 | 102 | 100 | 100 | 99 | 100 | 100 | 101 | 102 | 101 | 100 | 101 | 100 |  | 100 | 101 | 100 | 100 | 100 | 100 | 102 | 2256000
47 | Shahjibazar GTPP Unit- 8 & 9 | 65 | 65 | 65 | 65 | 65 | 65 | 40 | 51 | 50 | 63 | 40 | 63 | 63 | 64 | 62 | 64 | 40 | 65 |  | 65 | 63 | 65 | 66 | 66 | 65 | 65 | 1099872
48 | Shahjibazar 86MW PP (Shahjibazar) | 87 | 87 | 84 | 84 | 84 | 84 | 82 | 82 | 82 | 82 | 84 | 82 | 82 | 84 | 84 | 84 | 84 | 87 |  | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 2029440
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 132 | 132 | 132 | 130 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 |  | 132 | 132 | 132 | 132 | 132 | 133 | 132 | 3170310
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 244440
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 210000
55 | Fenchugonj 51 MW PP (Barakatullah) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 46 | 46 | 46 | 49 | 46 | 49 | 49 | 46 | 18 | 45 |  | 46 | 46 | 46 | 47 | 47 | 47 | 44 | 1090800
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 16 | 16 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 535752
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 280 | 280 | 280 | 290 | 290 | 300 | 300 | 290 | 300 | 300 | 300 | 290 | 280 | 300 | 280 | 260 | 285 |  | 280 | 300 | 265 | 300 | 290 | 290 | 300 | 7135500
| Bibiyana South 400 MW | [26 empty] | 63300
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 45 | 55 | 55 | 55 | 1209260
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 20 | 20 | 20 | 20 | 20 |  | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 457872
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 |  |  | 19 | 19 | 22 | 22 | 19 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 438120
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 367416
63 | Impoprt (Tripura) | 152 | 148 | 146 | 146 | 142 | 132 | 116 | 110 | 90 | 92 | 94 | 100 | 108 | 116 | 136 | 132 | 138 | 158 |  | 158 | 158 | 160 | 158 | 156 | 158 | 154 | 3226560
64 | Malancha, Ctg. EPZ (United) | 34 | 34 | 34 | 35 | 37 | 35 | 22 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 4 | 8 |  | 0 | 3 | 8 | 10 | 14 | 26 | 33 | 341280
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 463644
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 10 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 178920
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 818300
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 477540
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 29 | 28 | 28 | 28 | 28 | 29 | 22 |  | 29 | 30 | 29 | 30 | 30 | 30 | 30 | 678780
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 815700
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 831900
73 | Ghorashal 108MW PP (Regent) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 41 | 41 | 41 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 44 | 1015136
| Feni Lanka Power | 100 | 100 | 100 | 17 | [5 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1128600
| Chowmuhani 113 MW | 110 | 113 | 104 | 106 | 103 | 108 | 102 | 102 | 105 | 104 | 105 | 102 | 105 | 103 | 102 | 107 | 105 | 111 |  | 111 | 113 | 112 | 113 | 110 | 113 | 113 | 2579640
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 197760
78 | Gazipur 52 MW PP | 51 | 51 | [7 empty] | 8 | 25 | 40 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 794832
79 | Kodda 150MW PP | 133 | 133 | 133 | 64 | 64 | 16 |  |  |  | 25 | 135 | 145 | 150 | 150 | 150 | 150 | 100 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 2581920
80 | Jamalpur 95 MW PP(Powerpac) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 |  | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 1135680
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 43 | 43 |  |  |  |  | 26 | 43 | 43 | 43 | 43 | 43 | 43 | 8 | 16 |  | 52 | 52 | 52 | 52 | 52 | 25 | 25 | 813682
| Gazipur 100 MW PP | 102 | 102 | 102 | 102 | 50 |  |  | 1 | 45 | 102 | 102 | 102 | 102 | 86 | 102 | 102 | 102 | 102 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 2049756
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 3 | 2 | 4 | 5 | 5 | 4 | 3 | 1 | 0 | [9 empty] | 30840
| Jodiac Power | 36 | 36 | 36 | 23 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 41 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 38 | 791635
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | 80 | 92 | 95 | 95 | 95 | 95 | 95 | 95 | 80 | 80 | 80 | 80 | 63 | 70 | 80 | 80 | 66 | 76 |  | 80 | 80 | 80 | 80 | 92 | 96 | 97 | 2057736
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 25 | 88 | 88 | [6 empty] | 4 | 12 | 17 | 47 | 48 | 28 | 26 | 26 | 26 |  | 26 | 40 | 30 | 26 | 26 | 25 | 25 | 643331
86 | Meghnaghat CCPP(Summit) | 265 | 260 | 255 | 265 | 285 | 275 | 285 | 290 | 280 | 285 | 285 | 260 | 260 | 250 | 285 | 250 | 260 | 300 |  | 250 | 265 | 270 | 270 | 265 | 280 | 285 | 6587200
87 | Meghnaghat 100 MW(IEL) | 100 | 100 | 100 | 96 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 98 | 98 | 100 | 100 | 100 | 36 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 1854720
| Meghnaghat 104 MW PP (OPCL) | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 434880
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 40 | 40 | [9 empty] | 40 | 40 | 20 | 40 | 40 | 10 | 100 |  | 100 | 100 | 100 | 100 | 100 | 90 | 70 | 876360
92 | Fenchuganj 44MW (Energyprima) | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 15 | 25 |  | 41 | 41 | 41 | 41 | 41 | 42 | 42 | 1032264
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1242522
94 | Gagnagar 102 MW PP (Digital Power) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 16 | 16 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 216000
95 | Patenga 50MW PP (Baraka) | 50 | 50 | 50 | 50 | 19 | 18 | 18 | 18 | 19 | 44 | 46 | 45 | 42 | 47 | 45 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1035840
96 | Chattogram 108 MW PP (ECPV) | 83 | 83 | 83 | 83 | 83 | 60 | 11 | 11 |  |  |  |  | 3 | 64 | 80 | 71 | 82 | 82 |  | 82 | 83 | 82 | 84 | 84 | 84 | 83 | 1388160
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 40 | 40 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1321614
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1249523
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 115 | 115 | 114 | 114 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2621372
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 2 | 2 | 1 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 13350
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 35 |  |  | 17 | 35 | 53 | 53 | 53 | 53 | 53 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1139400
104 | Keranigonj 300 MW PP (APR) | [14 empty] | 33 |  |  | 180 |  | 180 | 125 | 129 | 124 | 75 |  | 0 | 662013
105 | Bramhangoan 100 MW PP (Aggreko) | [10 empty] | 25 | 25 | 25 | 25 | 50 |  |  | 78 |  | 93 | 92 | 86 | 30 | 13 |  | 0 | 464268
106 | Mymensingh 200 MW PP (United) | 200 | 200 | 200 | 200 | 200 | 200 | 192 | 192 | 160 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 150 |  | 190 | 192 | 192 | 192 | 200 | 192 | 200 | 4161600
112 | Aurahati 100MW PP (Aggreko) | [13 empty] | 51 | 51 | 26 |  | 91 |  | 93 | 93 | 96 | 86 | 79 |  | 0 | 564368
114 | Kodda 149 MW PP Unit-1 (Summit) | 147 | 149 | 149 | 149 | 149 | 149 | 117 | 112 | 130 | 132 | 132 | 132 | 132 | 131 | 132 | 132 | 132 | 132 |  | 132 | 132 | 132 | 132 | 132 | 131 | 131 | 3251810
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 50 | 20 | 25 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2269440
116 | Chandpur 200MW (Desh energy) | 100 | 17 | 17 | [8 empty] | 1 | 46 | 70 | 100 | 100 | 50 | 72 |  | 190 | 200 | 200 | 200 | 200 | 200 | 50 | 1787520
117 | Ashuganj 150MW PP (Midland) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 15 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 33 |  | 46 | 50 | 50 | 43 | 48 | 50 | 50 | 695854
118 | Bibiyana-III 400 MW CCPP | 423 | 422 | 424 | 424 | 422 | 423 | 420 | 419 | 418 | 416 | 412 | 412 | 412 | 326 | 226 | 238 | 215 | 334 |  | 419 | 416 | 416 | 416 | 417 | 417 | 416 | 9357000
| Jamalpur 115 MW PP (United) | 115 | 105 | 105 | 105 | 105 | 95 | 75 | 75 | 45 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 37 |  | 105 | 95 | 105 | 115 | 115 | 115 | 115 | 1738800
| Anwara 300 MW PP (United) | 162 | 162 | 161 | 162 | 161 | 161 | 106 | 106 | 157 | 161 | 178 | 179 | 180 | 179 | 179 | 179 | 124 | 175 |  | 180 | 180 | 180 | 179 | 180 | 180 | 180 | 3899127
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2421120
120 | Eastern Zone Total | 8042 | 7831 | 7721 | 7382 | 7316 | 6748 | 6272 | 6293 | 6676 | 6919 | 7188 | 7347 | 7386 | 7431 | 7577 | 7447 | 7037 | 8144 |  | 8638 | 8586 | 8561 | 8475 | 8392 | 8215 | 8023 | 178237710
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 115 | 115 | 115 | 115 | 115 | 34 |  |  | 9 | 99 | 99 | 99 | 99 | 99 | 99 | 85 | 49 | 92 |  | 96 | 99 | 99 | 99 | 99 | 99 | 115 | 2000640
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 35 | 29 | 17 | [13 empty] | 3 | 3 |  | 9 | 18 | 18 | 20 | 29 | 29 | 29 | 220800
| Khulna 225 MW CCPP | 230 | 230 | 230 | 210 | 130 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 135 |  | 210 | 230 | 230 | 230 | 230 | 230 | 230 | 4062720
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 548160
130
131
132
133
| Barisal 110 MW PP (Summit ) | 110 | 110 | 110 | 96 | 80 | 48 | [5 empty] | 32 | 64 | 32 | 32 | 32 | 32 | 80 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 1555200
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 91 | 93 | 93 | 93 | 93 | 93 | 92 | 92 | 91 | 91 | 88 |  | 60 | 75 | 78 | 81 | 88 | 88 |  | 88 | 86 | 87 | 88 | 90 | 90 | 90 | 1985678
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 38 | 38 | 38 | 36 | 35 | 30 | 27 | 26 | 24 | 24 | 25 | 25 | 25 | 25 | 25 | 26 | 26 | 37 |  | 38 | 38 | 38 | 39 | 39 | 38 | 38 | 753471
141 | Noapara 100 MW PP (Bangla Trac) | 99 | 50 | 20 | [14 empty] | 5 |  | 98 | 98 | 98 | 100 | 99 | 99 | 70 | 797760
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 24 | 24 | [7 empty] | 40 | 40 | 40 | 40 | 40 |  | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 583125
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 896 | 897 | 895 | 895 | 892 | 892 | 893 | 893 | 892 | 893 | 892 | 892 | 893 | 893 | 892 | 892 | 892 | 892 |  | 892 | 893 | 892 | 892 | 892 | 892 | 892 | 21424727
147 | Bheramara 410 MW CCPP | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 310 | 280 | 300 | 300 | 175 | 200 | 200 | 200 | 200 | 235 | 235 |  | 235 | 235 | 235 | 260 | 315 | 310 | 295 | 6450624
148 | Payra 1320 MW | 600 | 580 | 550 | 550 | 550 | 550 | 520 | 500 | 410 | 400 | 400 | 440 | 460 | 480 | 490 | 490 | 490 | 500 |  | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 13592200
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 150 | 150 | 149 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 151 | 150 | 150 | 150 | 150 | 3705100
153 | Baghabari 71 MW GTPP | 10 | [24 empty] | 0 | 60000
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 43 | 25 | [10 empty] | 43 | 43 | 43 | 50 | 50 | 43 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 622864
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 148 | 148 | 148 | 148 | 150 | 149 | 150 | 145 | 170 | 190 | 171 | 179 | 178 | 160 | 174 | 180 | 161 | 153 |  | 183 | 183 | 183 | 192 | 183 | 185 | 187 | 4238682
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 162 | 154 | 154 | 154 | 156 | 156 | 157 | 164 | 173 | 185 | 180 | 189 | 180 | 182 | 174 | 189 | 181 | 169 |  | 187 | 185 | 186 | 194 | 186 | 187 | 199 | 4459818
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 354 | 350 | 340 | 360 | 390 | 310 | 339 | 340 | 403 | 408 | 407 | 403 | 400 | 382 | 403 | 383 | 315 | 363 |  | 314 | 335 | 362 | 361 | 354 | 360 | 360 | 8844545
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 9 | 23 |  | 35 | 35 | 35 | 34 | 34 | 34 | 0 | 213625
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 489600
163 | Bogura 20 MW PP (Energyprima) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 8 | 7 | 7 | 8 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 225936
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 259524
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | 28 | 28 | [15 empty] | 38 |  | 36 | 36 | 39 | 36 | 36 | 36 | 36 | 294195
168 | Santahar 50 MW Peaking PP | 32 | 32 | [15 empty] | 18 |  | 24 | 24 | 27 | 30 | 30 | 30 | 30 | 263895
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | [6 empty] | 17 | 31 | 52 | 52 | 35 | 52 | 52 | 8 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 812640
170 | Chapainawabganj 100 MW Peaking PP | 94 | 94 | 94 | 94 | [13 empty] | 84 |  | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 1036128
171 | Baghabari 200 MW PP (Paramount) | [17 empty] | 100 |  | 150 | 50 | 50 | 50 |  |  | 0 | 359866
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 113 |  |  |  | 13 | 50 | 57 | 79 | 70 | 72 | 72 | 72 | 35 | 62 |  | 108 | 111 | 111 | 111 | 111 | 111 | 111 | 1951200
172 | Confidence Power Bogura Unit-1 113 MW |  | 10 | 90 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 |  | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 2325888
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | [15 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 111 | 111 | 96 | 100 | 102 | 104 | 104 | 105 | 106 | 105 | 104 | 104 | 73 | 64 | 96 | 100 | 104 | 97 |  | 96 | 103 | 99 | 100 | 96 | 99 | 103 | 2396160
177 | Sympa Solar Power 8MW | [6 empty] | 1 | 3 | 3 | 3 | 6 | 5 | 7 |  | 1 | 5 | 2 | [9 empty] | 37255
178
178