## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-08-18 | Sunday
|  | Date (day): | 2019-08-18 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13556 | MW |  |  | (b) At Evening Peak Hour : |  | 15000 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-08-17 | 2019-08-18 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 70 | 70 | 70 | 70 |  | 15
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 124 | 189 | 190 | 190
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 350 | 350 | 350 | 350
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 20 | 40 | 50 | 75
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 83 | 87 | 90 | 90
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 20 | 20 | 20 | 20 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 350 | 347 | 350 | 350 |  |  | FGMO
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 345 | 356 | 300 | 300
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 350 | 350 | 350 | 350 |  |  | Machine problem
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 274 | 270 | 280 | 280 |  |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 127 | 120 | 100 | 150 | 60 |  | Gas shortage
| Siddhirganj Desh |  | HSD | QRPP | 96*1.2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217 | 217 | 217 | 150 | 208 | 335 | 0 |  | 217 | Under maint.
| Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 6 | 46 | 46 | 46 |  | 5 | Engine problem
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 65 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 72 | 72 | 72 |  | 36 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 34 | 33 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 14 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 42 | 42 | 42 |  | 10 | Engine problem
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 17 | 105 | 100 | 100
| Dhaka area Total |  |  |  |  | 5929 | 5693 | 2369 | 2983 | 4107 | 4447 | 185 | 791
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Under maint.
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 6 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 210 | 214 | 215 | 215
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 204 | 203 | 215 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 130 | 130 | 130 | 150
44 | Sikalbaha 51 MW PP(Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | Contract expired
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 50 | 100
46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D
47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 50 | 80
48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 10 | 100 | 100
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 100 | 100 | 100
50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 14 | 42 | 15 | 25
51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 30 | 95 | 96 |  | 12 | Engine problem
52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 0.8 | 0 | 4.4 | 0
53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 87 | 230 | 260
| Jodiac Power |  | HFO | IPP | 54.36 | 0 | 0 | 18 | 0 | 0 | 0
| Karnaphuli Power Lid. |  | HFO | IPP | 110 | 0 | 0 | 113 | 113 | 113 | 113 |  |  | RRT
| Chattogram area Total |  |  |  |  | 2113 | 2053 | 795.8 | 1177 | 1534.4 | 1651 | 260 | 110
54 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 135 | 135 | 120 | 120 |  |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
55 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 191 | 181 | 220 | 220 |  |  | FGMO
56 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 200 | 360
57 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 260 | 360 | 360 |  |  | FGMO
58 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 30 | 30 | 33 | 33 |  | 12 | Engine problem
59 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 51 | 54 | 52 | 52
60 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract expired
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 55 | 55 | 68 | 68 | 127 |  | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 5 | 43 | 43 | 43 |  | 8 | Engine problem
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 150 | 150
64 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract expired
65 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
66 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 40 | 140 | 140 | 140
67 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 10 | 200 | 200 | 200
68 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
69 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 132 | 166 | 131 | 185
70 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 25 | 33 | 33
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 52 | 52 | 52
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 17 | 20 | 20 | 20 |  | 5 | Engine problem
73 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1038 | 1393 | 1855 | 2319 | 390 | 25
74 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 136 | 154 | 204 | 204
75 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
76 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 91 | 95 | 95
77 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.2 | 0 | 1.6 | 0
78 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 132 | 200 | 200
79 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 59 | 109 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 225.2 | 506 | 635.6 | 634 | 0 | 0
80 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 59 | 60 | 60
81 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 58 | 58 | 58 | 58
82 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
83 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 150 | 152 | 160 | 160 |  |  | FGMO
84 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 50 | 51 | 51
85 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 36 | 50 | 44 | 44
86 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
87 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 58 | 63 | 63 |  |  | FGMO
88 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 73 | 73 | 75
89 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 44 | 44 | 44 | 44 |  | 6 | Engine problem
90 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 47 | 48 | 120 | 120
91 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17 |  | 3 | Engine problem
92 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 30 | 31 | 42 | 43 |  | 7 | Engine problem
93 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 24 | 24 | 24
94 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 300 | 300 | 320 |  |  | FGMO
95 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285 MW | 285 | 285 | 0 | 0 | 0 | 0 |  |  | Under maint.
96 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1879 | 1834 | 966 | 1128 | 1223 | 1263 | 0 | 16
97 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 32
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 732 | 826 | 943 | 943
| Khulna 115 MW PP (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
98 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 115 | 115 | 115
99 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 42 | 0 | 42
100 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 200 | 200
101 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 67 | 0 | 75
102 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 320 | 320 | 320 | 410
103 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
104 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 50 | 80 | 100
105 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 105 | 105 | 105
106 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 18 | 88 | 50 | 100 |  | 5 | Engine problem
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 1070 | 1653 | 1853 | 2162 | 0 | 5
107 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 48 | 70 | 110
108 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
109 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 23 | 34 | 25 | 35
110 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 133 | 132 | 135 | 135
111 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 97 | 96 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 253 | 310 | 325 | 405 | 0 | 0
112 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 55 | 55 | 60 | 60
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
113 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
114 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 30
115 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 12 | 50 | 40 | 50
116 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 8 | 50 | 50
117 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 47 | 47
118 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 190 | 195 | 215 | 215 |  |  | FGMO
119 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas Shortage
120 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 160 | 160 | 205 | 215 |  |  | FGMO
121 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 357 | 341 | 400 | 400
122 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 0 | 35
123 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
124 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 16 | 16 | 16 | 15
125 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 0 | 11 | 11
126 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 52 | 52 | 52
127 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 95 | 80 | 100
128 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
129 | Bagura 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 817 | 1187 | 1561 | 1665 | 220 | 100
130 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 93 | 92 | 90 | 90
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
131 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 250 | 250 | 250 | 250
132 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
133 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  |  | Under maint.
| Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 0 | 0 | 0 | 113 | 114 | 114
| Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 8.4 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 572 | 492 | 351.4 | 455 | 462 | 454 | 0 | 105
| Total |  |  |  |  | 18969 | 18446 | 7885.4 | 10792 | 13556 | 15000 | 1055 | 1152
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7452.1122 | 10199 | 12811.1234 | 14175.7784
A. |  | 2019-08-17 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 10792 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 6767.02 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10792 | MW
3 | Day peak Generation : |  |  | 7885.4 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10199 | MW
4 | Evening peak Generation : |  |  | 10792 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 210.163 | MKWHr | By Solar | 0.20328 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 148.5127 | MKWHr |  | By Oil: | 27.7273 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 7.6137 | MKWHr |  | By Hydro: | 4.9503 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1055 | MW | Dhaka | 3061 | 3061 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1152 | MW | Chittagong | 1060 | 1060 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2207 | MW | Khulna | 1373 | 1373 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1290.94 | MMCFD |  |  | Rajshahi | 1175 | 1175 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 142984506.58 | ii) Oil : | Taka | 184608032.48 | Comilla | 1094 | 1094 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 35899531.68 | Total | Taka | 363492070.74 | Mymensingh | 915 | 915 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 1.428 | MKWHr. | Sylhet | 488 | 488 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -216 | MW (E to W) at | 21:00 | hrs | Barisal | 323 | 323 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -264 | MW at | 1:00 | hrs | Rangpur | 710 | 710 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.4° C |  |  | Total | 10199 | 10199 |  | 0
B. |  | 2019-08-18 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 32.7° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11700 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15000 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9200 | MW
4 | Reserve(Generation end) |  |  |  | 3300 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 227.8453 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7667.61 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.7948 | MKWHr. | ii) HVDC Flow at Peak Time |  | 826 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.361 | MKWHr. | iii) Maximum HVDC Flow : |  | 827 | MW at | 19:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 105.49 |  | (b) Today: | 105.71 |  | (c) Rule Curve: |  | 94.44
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-08-17
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Lid. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence) | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 70 | 104 | 0 | 0 | 350 | 90 | 75 | 345 | 355 |  | 0 | 350 | 248 | 0 | 0 | 0 | 206 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 22 | 25 | 12 | 33 | 14 | 0 | 0 | 123 | 90 | 100 | 0 | 0 | 204 | 0 | 100 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 22 | 42 | 135 | 0 | 0 | 0 | 305 | 181 | 55 | 90 | 33 | 55 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 20 | 148 | 176 | 63 | 20 | 0 | 60 | 58 | 50 | 50 | 130 | 151 | 63 | 76 | 46 | 48 | 0 | 30 | 10 | 290 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 30 | 90 | 0 | 0 | 109 | 0 | 0 | 0 | 33 | 0 | 113 |  | 744 | 0 | 410 | 0 | 49 | 0 | 0 | 0 | 35 | 0 | 40 | 134 | 34 | 48 | 0 | 0 | 60 | 0 | 0 | 48 | 50 | 8 | 0 | 8 | 0 | 22 | 16 | 11 | 82 | 0 | 150 | 0 | 0 | 193 | 0 | 0 | 0 | 97 | 0 | 202 | 0 | 316 | 70 | 0 | 55 | 88 | 80 | 0 | 0 |  | 6047 | 3050 | 9097 | 4193 | 744 | 2232 | 1235 | 232 | 213 | 100 | 148 | 0 | 0 | 105.42
2:00 | 70 | 104 | 0 | 0 | 350 | 87 | 75 | 345 | 354 |  | 0 | 350 | 245 | 0 | 0 | 0 | 205 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 25 | 12 | 33 | 14 | 0 | 0 | 122 | 90 | 100 | 0 | 0 | 204 | 0 | 95 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 20 | 135 | 0 | 0 | 0 | 310 | 181 | 55 | 90 | 33 | 56 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 0 | 20 | 144 | 178 | 8 | 20 | 0 | 60 | 58 | 50 | 50 | 130 | 152 | 40 | 10 | 46 | 48 | 0 | 30 | 0 | 290 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 20 | 70 | 0 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 113 |  | 744 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 8 | 134 | 32 | 0 | 0 | 0 | 60 | 0 | 0 | 48 | 50 | 8 | 0 | 8 | 0 | 22 | 16 | 11 | 84 | 0 | 176 | 0 | 0 | 186 | 0 | 0 | 0 | 97 | 0 | 201 | 0 | 368 | 17 | 0 | 35 | 88 | 70 | 0 | 0 |  | 5693 | 2876 | 8569 | 4091 | 744 | 2181 | 886 | 260 | 212 | 51 | 144 | 0 | 0 | 105.44
3:00 | 70 | 104 | 0 | 0 | 350 | 87 | 50 | 352 | 354 |  | 0 | 350 | 243 | 0 | 0 | 0 | 205 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 25 | 12 | 33 | 14 | 0 | 0 | 117 | 90 | 100 | 0 | 0 | 214 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 80 | 0 | 0 | 0 | 320 | 180 | 55 | 90 | 33 | 56 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 0 | 20 | 140 | 179 | 0 | 20 | 0 | 60 | 58 | 50 | 47 | 130 | 152 | 40 | 10 | 46 | 48 | 0 | 30 | 0 | 310 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 113 |  | 743 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 32 | 0 | 0 | 0 | 60 | 0 | 0 | 8 | 50 | 8 | 0 | 0 | 0 | 5 | 16 | 11 | 83 | 0 | 200 | 0 | 0 | 186 | 0 | 0 | 0 | 96 | 0 | 204 | 0 | 367 | 0 | 0 | 0 | 53 | 35 | 0 | 0 |  | 5516 | 2702 | 8218 | 4072 | 743 | 2144 | 621 | 283 | 207 | 8 | 140 | 0 | 0 | 105.46
4:00 | 70 | 104 | 0 | 0 | 350 | 87 | 50 | 345 | 354 |  | 0 | 350 | 260 | 0 | 0 | 0 | 207 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 25 | 12 | 33 | 14 | 0 | 0 | 116 | 90 | 100 | 0 | 0 | 204 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 80 | 0 | 0 | 0 | 305 | 190 | 8 | 90 | 33 | 5 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 0 | 20 | 134 | 190 | 0 | 20 | 0 | 60 | 58 | 50 | 50 | 130 | 151 | 40 | 10 | 46 | 48 | 0 | 30 | 0 | 315 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 113 |  | 744 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 34 | 0 | 0 | 0 | 60 | 0 | 0 | 8 | 50 | 8 | 0 | 0 | 0 | 5 | 16 | 8 | 83 | 0 | 205 | 0 | 0 | 187 | 0 | 0 | 0 | 97 | 0 | 207 | 0 | 368 | 0 | 0 | 0 | 35 | 0 | 0 | 0 |  | 5423 | 2660 | 8083 | 4063 | 744 | 2058 | 582 | 288 | 206 | 8 | 134 | 0 | 0 | 105.47
5:00 | 70 | 104 | 0 | 0 | 350 | 87 | 50 | 345 | 354 |  | 0 | 350 | 244 | 0 | 0 | 0 | 208 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 25 | 12 | 33 | 14 | 0 | 0 | 116 | 90 | 100 | 0 | 0 | 205 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 80 | 0 | 0 | 0 | 310 | 190 | 8 | 90 | 33 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 11 | 0 | 20 | 132 | 190 | 0 | 20 | 0 | 60 | 58 | 5 | 5 | 130 | 151 | 40 | 10 | 46 | 48 | 0 | 30 | 0 | 300 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 113 |  | 744 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 30 | 0 | 0 | 0 | 60 | 0 | 0 | 8 | 50 | 8 | 0 | 0 | 0 | 5 | 16 | 8 | 83 | 0 | 204 | 0 | 0 | 196 | 0 | 0 | 0 | 73 | 0 | 207 | 0 | 368 | 0 | 0 | 0 | 36 | 0 | 0 | 0 |  | 5236 | 2641 | 7877 | 4054 | 744 | 1887 | 559 | 287 | 206 | 8 | 132 | 0 | 0 | 105.48
6:00 | 70 | 104 | 0 | 0 | 350 | 87 | 20 | 345 | 358 |  | 0 | 350 | 245 | 0 | 0 | 0 | 120 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 25 | 12 | 33 | 14 | 0 | 0 | 117 | 90 | 100 | 0 | 0 | 179 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 23 | 80 | 0 | 0 | 0 | 255 | 161 | 8 | 90 | 33 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 11 | 0 | 20 | 128 | 191 | 0 | 0 | 0 | 60 | 58 | 5 | 5 | 130 | 150 | 40 | 10 | 5 | 48 | 0 | 30 | 0 | 300 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 113 |  | 638 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 25 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 5 | 4 | 8 | 84 | 0 | 204 | 0 | 0 | 192 | 0 | 0 | 0 | 27 | 0 | 200 | 0 | 313 | 0 | 0 | 0 | 18 | 0 | 0 | 0 |  | 4926 | 2372 | 7298 | 3803 | 638 | 1715 | 519 | 288 | 207 | 0 | 128 | 0 | 0 | 105.49
7:00 | 70 | 104 | 0 | 0 | 350 | 64 | 20 | 345 | 333 |  | 0 | 300 | 247 | 0 | 0 | 0 | 120 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 12 | 33 | 14 | 0 | 0 | 124 | 90 | 100 | 0 | 0 | 181 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 80 | 0 | 0 | 0 | 270 | 175 | 8 | 40 | 33 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 11 | 0 | 20 | 112 | 178 | 0 | 0 | 0.1 | 60 | 58 | 5 | 5 | 100 | 150 | 40 | 10 | 5 | 48 | 0 | 10 | 0 | 310 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 1.44 | 0 | 0 | 113 |  | 637 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 21 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 5 | 4 | 8 | 84 | 0 | 204 | 0 | 0 | 168 | 0 | 0 | 0 | 22 | 0 | 178 | 0 | 316 | 0 | 0 | 0 | 18 | 0 | 0 | 0.24 |  | 4603.54 | 2229.24 | 6832.78 | 3609 | 637 | 1562 | 404 | 288 | 214 | 0 | 112 | 6.78 | 0 | 105.5
8:00 | 70 | 104 | 0 | 0 | 350 | 12 | 20 | 358 | 303 |  | 0 | 300 | 270 | 0 | 0 | 0 | 120 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 12 | 33 | 14 | 0 | 0 | 125 | 90 | 100 | 0 | 0 | 181 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 80 | 0 | 0 | 0 | 270 | 176 | 8 | 40 | 33 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 11 | 0 | 17 | 108 | 172 | 0 | 0 | 0.4 | 58 | 58 | 5 | 5 | 100 | 158 | 40 | 10 | 5 | 48 | 0 | 12 | 0 | 315 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 1.66 | 0 | 0 | 113 |  | 638 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 22 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 5 | 4 | 5 | 83 | 0 | 204 | 0 | 0 | 171 | 0 | 0 | 0 | 22 | 0 | 177 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96 |  | 4587.06 | 2179.96 | 6767.02 | 3605 | 638 | 1492 | 409 | 287 | 215 | 0 | 108 | 13.02 | 0 | 105.51
9:00 | 70 | 124 | 0 | 0 | 350 | 12 | 20 | 367 | 353 |  | 0 | 350 | 285 | 0 | 0 | 0 | 120 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 9 | 33 | 14 | 0 | 0 | 125 | 90 | 100 | 0 | 0 | 229 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 80 | 0 | 0 | 0 | 280 | 189 | 8 | 40 | 33 | 5 | 0 | 5 | 0 | 0 | 0 | 8 | 8 | 0 | 17 | 106 | 156 | 3 | 0 | 0.5 | 60 | 58 | 5 | 5 | 163 | 152 | 63 | 10 | 5 | 48 | 0 | 12 | 0 | 315 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 50 | 10 | 0 | 2.636 | 0 | 0 | 113 |  | 638 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 21 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 13 | 5 | 86 | 0 | 204 | 0 | 0 | 175 | 0 | 0 | 0 | 21 | 0 | 172 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 |  | 4952.136 | 2216.4 | 7168.536 | 3733 | 638 | 1693 | 479 | 290 | 215 | 0 | 106 | 14.536 | 0 | 105.52
10:00 | 70 | 124 | 0 | 0 | 350 | 12 | 20 | 348 | 351 |  | 0 | 350 | 287 | 0 | 0 | 0 | 154 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 9 | 33 | 14 | 0 | 0 | 125 | 90 | 100 | 0 | 0 | 204 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 80 | 0 | 0 | 0 | 285 | 191 | 8 | 40 | 33 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 8 | 0 | 17 | 118 | 155 | 8 | 20 | 2.5 | 60 | 58 | 5 | 5 | 163 | 151 | 61 | 10 | 5 | 48 | 0 | 12 | 0 | 300 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 50 | 17 | 0 | 3.128 | 0 | 5 | 113 |  | 735 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 22 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 16 | 5 | 87 | 0 | 250 | 0 | 0 | 176 | 0 | 0 | 0 | 23 | 0 | 162 | 0 | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1 |  | 5012.628 | 2353.1 | 7365.728 | 3768 | 735 | 1677 | 498 | 337 | 215 | 0 | 118 | 17.728 | 0 | 105.53
11:00 | 70 | 124 | 0 | 0 | 350 | 82 | 20 | 355 | 351 |  | 0 | 350 | 275 | 0 | 0 | 0 | 150 | 0 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 22 | 25 | 9 | 33 | 14 | 0 | 0 | 120 | 90 | 100 | 0 | 0 | 204 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 135 | 0 | 0 | 0 | 275 | 186 | 8 | 42 | 33 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 8 | 33 | 17 | 122 | 137 | 8 | 20 | 1.6 | 60 | 58 | 5 | 5 | 163 | 152 | 61 | 10 | 5 | 48 | 0 | 12 | 0 | 295 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 55 | 17 | 0 | 6.19 | 0 | 16 | 113 |  | 713 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 21 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 16 | 5 | 97 | 0 | 250 | 0 | 0 | 202 | 0 | 0 | 0 | 52 | 0 | 165 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6 |  | 5174.79 | 2437.6 | 7612.39 | 3885 | 713 | 1801 | 502 | 347 | 210 | 0 | 122 | 32.39 | 0 | 105.54
12:00 | 70 | 124 | 0 | 0 | 350 | 83 | 20 | 350 | 345 |  | 0 | 350 | 274 | 0 | 0 | 0 | 150 | 0 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 22 | 25 | 9 | 33 | 14 | 0 | 0 | 120 | 90 | 100 | 0 | 0 | 204 | 0 | 130 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 135 | 0 | 0 | 0 | 310 | 191 | 55 | 40 | 30 | 51 | 0 | 5 | 0 | 0 | 0 | 21 | 8 | 33 | 17 | 132 | 136 | 8 | 20 | 2.2 | 60 | 58 | 5 | 36 | 163 | 150 | 60 | 10 | 44 | 47 | 0 | 30 | 0 | 295 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 10 | 0 | 0 | 59 | 17 | 0 | 0.8 | 0 | 18 | 113 |  | 732 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 23 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 16 | 5 | 93 | 0 | 250 | 0 | 0 | 190 | 0 | 0 | 0 | 97 | 0 | 160 | 0 | 357 | 0 | 0 | 0 | 18 | 0 | 0 | 8.4 |  | 5394 | 2491.4 | 7885.4 | 3895 | 732 | 2021 | 535 | 343 | 210 | 0 | 132 | 17.4 | 0 | 105.55
13:00 | 70 | 124 | 0 | 0 | 350 | 81 | 50 | 346 | 300 |  | 10 | 350 | 273 | 0 | 0 | 0 | 150 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 14 | 0 | 0 | 0 | 22 | 25 | 9 | 33 | 7 | 0 | 0 | 120 | 90 | 100 | 0 | 0 | 204 | 0 | 130 | 0 |  | 0 | 0 | 0 | 0 | 0 | 2 | 22 | 26 | 100 | 0 | 0 | 0 | 305 | 195 | 63 | 40 | 33 | 51 | 0 | 20 | 0 | 0 | 0 | 21 | 8 | 33 | 17 | 134 | 126 | 8 | 20 | 1.3 | 60 | 58 | 50 | 50 | 163 | 151 | 61 | 72 | 44 | 48 | 0 | 30 | 10 | 280 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 10 | 17 | 0 | 0 | 109 | 45 | 0 | 3.36 | 0 | 5 | 113 |  | 728 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 22 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 22 | 16 | 5 | 94 | 0 | 249 | 0 | 0 | 189 | 0 | 0 | 0 | 97 | 0 | 167 | 0 | 327 | 0 | 0 | 35 | 17 | 0 | 0 | 8.3 |  | 5634.66 | 2536.3 | 8170.96 | 3926 | 728 | 2124 | 681 | 343 | 210 | 0 | 134 | 24.96 | 0 | 105.56
14:00 | 70 | 124 | 0 | 0 | 320 | 84 | 50 | 350 | 300 |  | 20 | 350 | 270 | 0 | 0 | 0 | 150 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 0 | 0 | 0 | 25 | 9 | 33 | 7 | 0 | 0 | 120 | 90 | 100 | 0 | 0 | 204 | 0 | 131 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 22 | 16 | 100 | 0 | 0 | 0 | 305 | 183 | 45 | 88 | 33 | 51 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 33 | 17 | 138 | 127 | 13 | 20 | 0.2 | 60 | 58 | 53 | 50 | 130 | 150 | 61 | 72 | 44 | 47 | 0 | 31 | 10 | 285 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 38 | 0 | 0 | 109 | 105 | 0 | 0.5 | 5 | 8 | 113 |  | 729 | 0 | 350 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 130 | 23 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 25 | 0 | 0 | 8 | 0 | 22 | 16 | 5 | 93 | 0 | 250 | 0 | 0 | 191 | 0 | 0 | 0 | 96 | 0 | 196 | 0 | 320 | 17 | 0 | 70 | 54 | 27 | 0 | 3.5 |  | 5712.7 | 2704.5 | 8417.2 | 3955 | 729 | 2091 | 928 | 343 | 210 | 0 | 138 | 23.2 | 0 | 105.57
15:00 | 70 | 124 | 0 | 0 | 320 | 82 | 50 | 344 | 300 |  | 20 | 350 | 271 | 0 | 0 | 0 | 150 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 0 | 0 | 0 | 25 | 9 | 33 | 7 | 0 | 0 | 122 | 90 | 100 | 0 | 0 | 205 | 0 | 130 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 22 | 16 | 100 | 0 | 0 | 0 | 305 | 182 | 45 | 86 | 33 | 50 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 33 | 17 | 144 | 127 | 32 | 20 | 1.5 | 59 | 58 | 53 | 50 | 130 | 151 | 51 | 73 | 45 | 50 | 0 | 31 | 10 | 290 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.7 | 10 | 52 | 0 | 0 | 109 | 105 | 0 | 0.5 | 16 | 14 | 113 |  | 729 | 0 | 350 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 131 | 25 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 25 | 0 | 0 | 8 | 0 | 22 | 16 | 5 | 91 | 0 | 250 | 0 | 0 | 193 | 0 | 0 | 0 | 96 | 0 | 187 | 0 | 327 | 17 | 0 | 72 | 53 | 35 | 0 | 6.1 |  | 5753.7 | 2717.1 | 8470.8 | 3933 | 729 | 2104 | 988 | 341 | 212 | 0 | 144 | 19.8 | 0 | 105.58
16:00 | 70 | 123 | 0 | 0 | 320 | 80 | 50 | 344 | 300 |  | 20 | 350 | 265 | 0 | 0 | 0 | 150 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 0 | 0 | 0 | 25 | 9 | 33 | 24 | 0 | 0 | 121 | 90 | 100 | 0 | 0 | 204 | 0 | 130 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 22 | 8 | 100 | 0 | 0 | 0 | 305 | 183 | 45 | 86 | 33 | 51 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 33 | 20 | 138 | 138 | 32 | 20 | 0.2 | 57 | 58 | 53 | 50 | 130 | 152 | 58 | 72 | 44 | 48 | 0 | 31 | 10 | 290 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1 | 10 | 52 | 0 | 0 | 109 | 105 | 0 | 1 | 16 | 10 | 113 |  | 729 | 0 | 350 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 132 | 20 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 25 | 0 | 0 | 8 | 0 | 22 | 16 | 5 | 92 | 0 | 250 | 0 | 0 | 197 | 0 | 0 | 0 | 95 | 0 | 187 | 0 | 334 | 17 | 0 | 36 | 53 | 35 | 0 | 4.8 |  | 5757.3 | 2686.8 | 8444.1 | 3972 | 729 | 2094 | 942 | 342 | 211 | 0 | 138 | 16.1 | 0 | 105.59
17:00 | 70 | 123 | 0 | 0 | 320 | 76 | 40 | 344 | 300 |  | 20 | 350 | 268 | 0 | 0 | 0 | 150 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 0 | 0 | 22 | 25 | 9 | 33 | 29 | 0 | 0 | 121 | 90 | 100 | 0 | 0 | 204 | 0 | 130 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 22 | 34 | 100 | 0 | 0 | 0 | 305 | 181 | 45 | 88 | 33 | 53 | 0 | 12 | 0 | 0 | 0 | 21 | 11 | 33 | 20 | 132 | 152 | 22 | 20 | 0.3 | 57 | 58 | 11 | 10 | 100 | 151 | 64 | 50 | 44 | 50 | 0 | 12 | 10 | 270 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1 | 10 | 30 | 0 | 0 | 109 | 52 | 0 | 0.8 | 16 | 11 | 113 |  | 729 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 110 | 22 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 22 | 16 | 5 | 91 | 0 | 250 | 0 | 0 | 196 | 0 | 0 | 0 | 97 | 0 | 187 | 0 | 310 | 17 | 0 | 36 | 53 | 37 | 0 | 1.4 |  | 5474.2 | 2614.4 | 8088.6 | 3950 | 729 | 1884 | 831 | 341 | 211 | 5 | 132 | 5.6 | 0 | 105.6
18:00 | 70 | 124 | 0 | 0 | 270 | 22 | 40 | 344 | 250 |  | 20 | 350 | 270 | 0 | 0 | 0 | 150 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 6 | 0 | 0 | 0 | 22 | 25 | 9 | 33 | 29 | 0 | 0 | 122 | 90 | 100 | 0 | 0 | 204 | 0 | 130 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 22 | 34 | 100 | 0 | 0 | 0 | 260 | 182 | 8 | 85 | 33 | 10 | 0 | 12 | 0 | 0 | 0 | 21 | 11 | 33 | 20 | 122 | 153 | 8 | 20 | 0.1 | 56 | 58 | 11 | 10 | 100 | 150 | 63 | 10 | 10 | 50 | 0 | 12 | 10 | 270 | 24 | 8 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0.3 | 10 | 17 | 0 | 0 | 109 | 52 | 0 | 0.1 | 16 | 0 | 113 |  | 729 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 123 | 23 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 25 | 0 | 0 | 2 | 0 | 22 | 16 | 5 | 92 | 0 | 250 | 0 | 0 | 192 | 0 | 0 | 0 | 22 | 0 | 179 | 0 | 322 | 17 | 0 | 36 | 54 | 43 | 0 | 0.2 |  | 5069.5 | 2530.2 | 7599.7 | 3803 | 729 | 1564 | 804 | 342 | 212 | 23 | 122 | 0.7 | 0 | 105.61
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 70 | 140 | 0 | 0 | 320 | 61 | 40 | 362 | 320 |  | 20 | 350 | 280 | 3 | 0 | 0 | 202 | 0 | 100 | 0 | 2 | 7 | 50 | 10 | 72 | 0 | 25 | 20 | 55 | 17 | 22 | 25 | 9 | 33 | 29 | 14 | 0 | 123 | 90 | 100 | 0 | 8 | 219 | 0 | 132 | 0 |  | 0 | 0 | 70 | 10 | 28 | 22 | 22 | 34 | 100 | 0 | 0 | 0 | 285 | 203 | 55 | 115 | 33 | 10 | 0 | 12 | 0 | 0 | 9 | 21 | 11 | 25 | 19 | 164 | 150 | 49 | 20 | 0 | 58 | 58 | 18 | 19 | 130 | 150 | 62 | 40 | 10 | 50 | 0 | 32 | 10 | 280 | 24 | 8 | 0 | 1 | 0 | 0 | 100 | 0 | 8 | 0 | 70 | 70 | 11 | 0 | 109 | 105 | 0 | 0 | 60 | 0 | 113 |  | 827 | 0 | 300 | 0 | 33 | 0 | 0 | 0 | 28 | 51 | 40 | 135 | 28 | 48 | 0 | 0 | 55 | 50 | 8 | 92 | 50 | 24 | 44 | 25 | 20 | 22 | 16 | 5 | 92 | 0 | 250 | 0 | 0 | 189 | 0 | 0 | 0 | 95 | 0 | 166 | 0 | 386 | 81 | 0 | 110 | 88 | 108 | 0 | 0 |  | 6393 | 3466 | 9859 | 4047 | 827 | 1968 | 1885 | 342 | 213 | 413 | 164 | 0 | 0 | 105.61
19:30 | 70 | 133 | 0 | 0 | 350 | 80 | 40 | 345 | 320 |  | 20 | 350 | 260 | 7 | 0 | 0 | 202 | 0 | 100 | 0 | 0 | 0 | 55 | 4 | 72 | 0 | 23 | 40 | 55 | 17 | 22 | 25 | 9 | 33 | 29 | 35 | 0 | 123 | 90 | 100 | 0 | 25 | 204 | 0 | 130 | 0 |  | 0 | 0 | 82 | 10 | 30 | 50 | 22 | 42 | 100 | 0 | 0 | 0 | 260 | 181 | 55 | 140 | 33 | 10 | 0 | 20 | 0 | 0 | 43 | 21 | 11 | 25 | 20 | 166 | 152 | 91 | 20 | 0 | 58 | 58 | 50 | 50 | 130 | 151 | 63 | 73 | 40 | 47 | 0 | 31 | 10 | 306 | 24 | 8 | 0 | 7 | 0 | 0 | 120 | 0 | 15 | 0 | 90 | 160 | 0 | 0 | 109 | 105 | 0 | 0 | 83 | 0 | 113 |  | 826 | 0 | 300 | 0 | 95 | 0 | 0 | 0 | 34 | 58 | 40 | 134 | 34 | 48 | 0 | 0 | 55 | 50 | 27 | 95 | 50 | 24 | 44 | 52 | 29 | 22 | 16 | 11 | 93 | 0 | 250 | 0 | 0 | 193 | 0 | 0 | 0 | 97 | 30 | 156 | 0 | 351 | 90 | 0 | 110 | 88 | 111 | 0 | 0 |  | 6853 | 3613 | 10466 | 4015 | 826 | 2127 | 2302 | 343 | 213 | 474 | 166 | 0 | 0 | 105.61
20:00 | 70 | 138 | 0 | 0 | 350 | 87 | 40 | 349 | 320 |  | 20 | 350 | 270 | 0 | 0 | 0 | 206 | 0 | 100 | 0 | 0 | 0 | 65 | 0 | 72 | 0 | 46 | 53 | 55 | 17 | 22 | 25 | 9 | 33 | 29 | 40 | 0 | 123 | 90 | 100 | 0 | 25 | 204 | 0 | 130 | 0 |  | 0 | 0 | 51 | 10 | 30 | 50 | 22 | 42 | 100 | 0 | 0 | 0 | 260 | 181 | 55 | 140 | 33 | 50 | 0 | 36 | 0 | 0 | 52 | 21 | 11 | 25 | 20 | 162 | 153 | 91 | 20 | 0 | 59 | 58 | 50 | 50 | 130 | 150 | 63 | 73 | 45 | 48 | 0 | 31 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 100 | 180 | 0 | 0 | 109 | 105 | 0 | 0 | 84 | 0 | 113 |  | 826 | 0 | 300 | 0 | 115 | 0 | 0 | 0 | 40 | 70 | 40 | 133 | 35 | 48 | 0 | 0 | 55 | 50 | 39 | 95 | 50 | 8 | 47 | 52 | 30 | 22 | 16 | 11 | 93 | 0 | 250 | 0 | 0 | 194 | 0 | 0 | 0 | 97 | 36 | 158 | 0 | 355 | 90 | 0 | 113 | 88 | 111 | 0 | 0 |  | 6963 | 3667 | 10630 | 4032 | 826 | 2194 | 2373 | 343 | 213 | 487 | 162 | 0 | 0 | 105.61
21:00 | 70 | 189 | 0 | 0 | 350 | 87 | 40 | 347 | 356 |  | 20 | 350 | 270 | 0 | 0 | 0 | 208 | 0 | 120 | 0 | 0 | 0 | 65 | 0 | 72 | 0 | 46 | 53 | 55 | 17 | 22 | 25 | 8 | 33 | 33 | 42 | 0 | 124 | 90 | 100 | 0 | 25 | 203 | 0 | 130 | 0 |  | 0 | 0 | 51 | 10 | 30 | 50 | 22 | 42 | 135 | 0 | 0 | 0 | 260 | 181 | 55 | 140 | 30 | 54 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 25 | 20 | 166 | 154 | 91 | 20 | 0 | 59 | 58 | 50 | 50 | 163 | 152 | 58 | 73 | 44 | 48 | 0 | 31 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 132 | 0 | 0 | 0 | 100 | 200 | 0 | 0 | 109 | 105 | 0 | 0 | 87 | 0 | 113 |  | 826 | 0 | 320 | 0 | 115 | 0 | 0 | 0 | 42 | 67 | 40 | 132 | 34 | 48 | 0 | 0 | 55 | 50 | 0 | 95 | 50 | 8 | 0 | 52 | 30 | 22 | 16 | 0 | 92 | 0 | 250 | 0 | 0 | 195 | 0 | 0 | 0 | 96 | 50 | 160 | 0 | 341 | 105 | 0 | 113 | 88 | 113 | 0 | 0 |  | 7187 | 3605 | 10792 | 4146 | 826 | 2257 | 2441 | 342 | 214 | 400 | 166 | 0 | 0 | 105.61
22:00 | 70 | 190 | 0 | 0 | 350 | 87 | 40 | 345 | 356 |  | 20 | 350 | 245 | 0 | 0 | 0 | 209 | 0 | 120 | 0 | 0 | 0 | 65 | 0 | 72 | 0 | 47 | 53 | 55 | 17 | 22 | 25 | 18 | 33 | 29 | 51 | 0 | 125 | 90 | 100 | 0 | 8 | 204 | 0 | 130 | 0 |  | 0 | 0 | 34 | 10 | 30 | 50 | 22 | 42 | 135 | 0 | 0 | 0 | 260 | 181 | 55 | 140 | 30 | 53 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 25 | 20 | 172 | 157 | 91 | 20 | 0 | 60 | 58 | 50 | 50 | 163 | 150 | 59 | 73 | 45 | 47 | 0 | 30 | 10 | 295 | 24 | 8 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 100 | 200 | 0 | 0 | 109 | 105 | 0 | 0 | 87 | 0 | 113 |  | 827 | 0 | 320 | 0 | 115 | 0 | 0 | 0 | 41 | 67 | 40 | 130 | 35 | 48 | 0 | 0 | 60 | 50 | 0 | 95 | 50 | 8 | 0 | 52 | 21 | 22 | 16 | 11 | 93 | 0 | 250 | 0 | 0 | 192 | 0 | 0 | 0 | 97 | 50 | 156 | 0 | 340 | 105 | 0 | 113 | 88 | 113 | 0 | 0 |  | 7166 | 3605 | 10771 | 4162 | 827 | 2252 | 2427 | 343 | 215 | 373 | 172 | 0 | 0 | 105.61
23:00 | 70 | 190 | 0 | 0 | 350 | 87 | 40 | 345 | 357 |  | 20 | 350 | 286 | 0 | 0 | 0 | 207 | 0 | 120 | 0 | 0 | 0 | 65 | 0 | 24 | 0 | 47 | 35 | 0 | 0 | 22 | 25 | 18 | 33 | 29 | 24 | 0 | 125 | 90 | 100 | 0 | 0 | 204 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 50 | 22 | 42 | 135 | 0 | 0 | 0 | 260 | 188 | 55 | 140 | 27 | 53 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 25 | 20 | 170 | 154 | 91 | 20 | 0 | 60 | 58 | 48 | 50 | 163 | 152 | 63 | 70 | 45 | 48 | 0 | 30 | 10 | 285 | 24 | 8 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 100 | 200 | 0 | 0 | 109 | 105 | 0 | 0 | 15 | 0 | 113 |  | 826 | 0 | 320 | 0 | 115 | 0 | 0 | 0 | 41 | 56 | 40 | 135 | 34 | 48 | 0 | 0 | 60 | 50 | 0 | 95 | 50 | 8 | 0 | 25 | 20 | 22 | 16 | 11 | 92 | 0 | 249 | 0 | 0 | 185 | 0 | 0 | 0 | 97 | 48 | 156 | 0 | 378 | 105 | 0 | 113 | 88 | 113 | 0 | 0 |  | 6888 | 3596 | 10484 | 4166 | 826 | 2275 | 2164 | 341 | 215 | 327 | 170 | 0 | 0 | 105.62
24:00 | 70 | 190 | 0 | 0 | 350 | 87 | 40 | 347 | 354 |  | 20 | 350 | 295 | 0 | 0 | 0 | 206 | 0 | 120 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 46 | 35 | 0 | 0 | 22 | 25 | 18 | 33 | 33 | 0 | 0 | 125 | 90 | 100 | 0 | 0 | 205 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 50 | 22 | 42 | 135 | 0 | 0 | 0 | 260 | 188 | 55 | 140 | 27 | 53 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 25 | 20 | 162 | 155 | 91 | 20 | 0 | 60 | 58 | 48 | 50 | 163 | 151 | 63 | 70 | 45 | 48 | 0 | 30 | 10 | 310 | 24 | 8 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 100 | 200 | 0 | 0 | 109 | 53 | 0 | 0 | 0 | 0 | 113 |  | 826 | 0 | 320 | 0 | 68 | 0 | 0 | 0 | 41 | 23 | 40 | 134 | 35 | 48 | 0 | 0 | 60 | 50 | 0 | 95 | 50 | 8 | 0 | 25 | 0 | 22 | 16 | 11 | 91 | 0 | 251 | 0 | 0 | 194 | 0 | 0 | 0 | 98 | 0 | 162 | 0 | 380 | 105 | 0 | 113 | 88 | 113 | 0 | 0 |  | 6742 | 3467 | 10209 | 4186 | 826 | 2301 | 1932 | 342 | 215 | 245 | 162 | 0 | 0 | 105.62
KWH | 1563000 | 3225400 | 0 | 0 | 8226663 | 1665409 | 1059968 | 8503300 | 7949000 |  | 279000 | 8264750 | 6395171 | 8640 | 0 | 0 | 4196456 | 0 | 3048000 | 0 | 6720 | 9360 | 312000 | 14074 | 357120 | 0 | 600912 | 235800 | 214586 | 75721 | 248580 | 600000 | 286020 | 810600 | 499900 | 171852 | 0 | 2794309 | 2156000 | 2400000 | 0 | 84862 | 4787815 | 0 | 2798844 | 0 |  | 0 | 0 | 229888 | 57360 | 136320 | 310080 | 4553280 | 721920 | 2540702 | 0 | 0 | 0 | 7040000 | 4443000 | 836363 | 1977560 | 671544 | 871200 | 0 | 697702 | 0 | 0 | 279940 | 428184 | 236700 | 457700 | 460370 | 3360960 | 3696800 | 775680 | 387000 | 10900 | 1408000 | 1393200 | 768000 | 875736 | 3394612 | 3381000 | 1321920 | 1002240 | 803520 | 1207300 | 0 | 620200 | 139860 | 7379000 | 290784 | 190416 | 0 | 7527 | 0 | 0 | 868800 | 0 | 21600 | 126630 | 667200 | 1601760 | 31781 | 0 | 2000400 | 1133064 | 0 | 22980 | 479 | 86140 | 2705624 |  | 17794819 | 0 | 8794080 | 0 | 677760 | 0 | 0 | 0 | 257760 | 372608 | 302625 | 3172000 | 644283 | 343776 | 0 | 0 | 1375000 | 270344 | 38338 | 645369 | 616300 | 112484 | 99585 | 280320 | 106422 | 424080 | 328428 | 175660 | 2087564 | 0 | 5526100 | 0 | 0 | 4822518 | 0 | 0 | 0 | 1802816 | 201600 | 4536818 | 0 | 8288363 | 746880 | 0 | 1049376 | 1169424 | 1035840 | 0 | 42773 |  | 142020848 | 68142113 | 210162961 | 99975204 | 17794819 | 48537450 | 25394958 | 7613664 | 4950309 | 2332314 | 3360960 | 203283 | 0
Fuel Cost | 1750560 | 3483432 | 0 | 0 | 6087730.62 | 1615446.73 | 1547553.28 | 6122376 | 6041240 |  | 493830 | 6611800 | 5755653.9 | 88128 | 0 | 0 | 5203605.44 | 0 | 3810000 | 0 | 74592 | 95097.6 | 3091920 | 147495.52 | 3249792 | 0 | 5624536.32 | 2261322 | 2047150.44 | 754181.16 | 186435 | 450000 | 0 | 0 | 0 | 1646342.16 | 0 | 726520.34 | 560560 | 3672000 | 0 | 815523.82 | 5027205.75 | 0 | 3554531.88 | 0 |  | 0 | 0 | 2411525.12 | 590234.4 | 1296403.2 | 2902348.8 | 4189017.6 | 2006937.6 | 2667737.1 | 0 | 0 | 0 | 5913600 | 4087560 | 819635.74 | 2630154.8 | 550666.08 | 897336 | 0 | 997713.86 | 0 | 0 | 2631436 | 436747.68 | 177525 | 865053 | 345277 | 23190624 | 3031376 | 7376716.8 | 394740 | 178760 | 1914880 | 1894752 | 1044480 | 1094670 | 4209318.88 | 3110520 | 1969660.8 | 1763942.4 | 891907.2 | 1835096 | 0 | 725634 | 328671 | 5239090 | 218088 | 144716.16 | 0 | 78807.69 | 0 | 0 | 8357856 | 0 | 217944 | 1461310.2 | 6218304 | 15024508.8 | 297787.97 | 0 | 17543508 | 10095600.24 | 0 | 0 | 4416.38 | 0 | 0 |  | 48046011.3 | 0 | 6859382.4 | 0 | 6533606.4 | 0 | 0 | 0 | 2990016 | 4881164.8 | 2992961.25 | 2537600 | 998638.65 | 3692154.24 | 0 | 0 | 2585000 | 3011632.16 | 469640.5 | 6389153.1 | 6391031 | 1317187.64 | 1199999.25 | 2791987.2 | 1048256.7 | 466488 | 541906.2 | 132974.62 | 13297782.68 | 0 | 22601749 | 0 | 0 | 4243815.84 | 0 | 0 | 0 | 2866477.44 | 3407040 | 3992399.84 | 0 | 6050504.99 | 7065484.8 | 0 | 9633271.68 | 10419567.84 | 9674745.6 | 0 | 0 |  | 238526225.46 | 199129631.12 | 437655856.58 | 96225114.61 | 48046011.3 | 46759391.97 | 159114724.85 | 35899531.68 | 1287080.34 | 25493307.63 | 23190624 | 1640070.2 | 0
Yesterday Day Peak | 70 | 124 | 0 | 0 | 350 | 83 | 20 | 350 | 345 |  | 0 | 350 | 274 | 0 | 0 | 0 | 150 | 0 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 22 | 25 | 9 | 33 | 14 | 0 | 0 | 120 | 90 | 100 | 0 | 0 | 204 | 0 | 130 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 135 | 0 | 0 | 0 | 310 | 191 | 55 | 40 | 30 | 51 | 0 | 5 | 0 | 0 | 0 | 21 | 8 | 33 | 17 | 132 | 136 | 8 | 20 | 2.2 | 60 | 58 | 5 | 36 | 163 | 150 | 60 | 10 | 44 | 47 | 0 | 30 | 0 | 295 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 10 | 0 | 0 | 59 | 17 | 0 | 0.8 | 0 | 18 | 113 |  | 732 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 23 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 16 | 5 | 93 | 0 | 250 | 0 | 0 | 190 | 0 | 0 | 0 | 97 | 0 | 160 | 0 | 357 | 0 | 0 | 0 | 18 | 0 | 0 | 8.4 |  | 7885.4 | DayPeak
Yesterday Evening Peak | 70 | 189 | 0 | 0 | 350 | 87 | 40 | 347 | 356 | 0 | 20 | 350 | 270 | 0 | 0 | 0 | 208 | 0 | 120 | 0 | 0 | 0 | 65 | 0 | 72 | 0 | 46 | 53 | 55 | 17 | 22 | 25 | 8 | 33 | 33 | 42 | 0 | 124 | 90 | 100 | 0 | 25 | 203 | 0 | 130 | 0 | 0 | 0 | 0 | 51 | 10 | 30 | 50 | 22 | 42 | 135 | 0 | 0 | 0 | 260 | 181 | 55 | 140 | 30 | 54 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 25 | 20 | 166 | 154 | 91 | 20 | 0 | 59 | 58 | 50 | 50 | 163 | 152 | 58 | 73 | 44 | 48 | 0 | 31 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 132 | 0 | 0 | 0 | 100 | 200 | 0 | 0 | 109 | 105 | 0 | 0 | 87 | 0 | 113 |  | 826 | 0 | 320 | 0 | 115 | 0 | 0 | 0 | 42 | 67 | 40 | 132 | 34 | 48 | 0 | 0 | 55 | 50 | 0 | 95 | 50 | 8 | 0 | 52 | 30 | 22 | 16 | 0 | 92 | 0 | 250 | 0 | 0 | 195 | 0 | 0 | 0 | 96 | 50 | 160 | 0 | 341 | 105 | 0 | 113 | 88 | 113 | 0 | 0 |  | 10792 | EvPeak
Forecast for Evening | 70 | 190 | 0 | 0 | 350 | 90 | 75 | 350 | 300 | 0 | 20 | 350 | 280 | 100 | 100 | 55 | 0 | 0 | 150 | 0 | 100 | 100 | 149 | 100 | 72 | 0 | 46 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 42 | 0 | 125 | 90 | 100 | 0 | 25 | 215 | 0 | 150 | 0 | 0 | 0 | 0 | 80 | 100 | 96 | 50 | 22 | 25 | 120 | 0 | 0 | 360 | 360 | 220 | 68 | 140 | 33 | 52 | 0 | 43 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 185 | 204 | 95 | 20 | 0 | 60 | 58 | 51 | 44 | 163 | 160 | 63 | 75 | 44 | 120 | 17 | 43 | 10 | 320 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 0 | 260 |  | 113 |  | 943 | 32 | 410 | 0 | 115 | 200 | 0 | 0 | 42 | 75 | 40 | 135 | 35 | 110 | 30 | 0 | 60 | 50 | 30 | 100 | 50 | 50 | 47 | 52 | 35 | 22 | 15 | 11 | 90 | 0 | 250 | 0 | 0 | 215 | 0 | 0 | 0 | 95 | 100 | 215 | 0 | 400 | 105 | 200 | 113 | 100 | 114 | 0
Forecast for Day | 70 | 190 | 0 | 0 | 350 | 90 | 50 | 350 | 300 | 0 | 20 | 350 | 280 | 100 | 100 | 55 | 335 | 0 | 100 | 0 | 100 | 100 | 149 | 100 | 72 | 0 | 46 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 42 | 0 | 125 | 90 | 100 | 0 | 25 | 215 | 0 | 130 | 0 | 0 | 0 | 0 | 50 | 100 | 95 | 50 | 22 | 15 | 120 | 0 | 0 | 200 | 360 | 220 | 68 | 140 | 33 | 52 | 0 | 43 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 131 | 204 | 95 | 20 | 1.6 | 60 | 58 | 51 | 44 | 163 | 160 | 63 | 73 | 44 | 120 | 0 | 42 | 10 | 300 | 24 | 11 | 0 | 200 | 0 | 0 | 200 | 0 | 149 | 20 | 100 | 200 | 150 | 0 | 115 | 100 | 50 | 4.4 | 230 |  | 113 |  | 943 | 0 | 320 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 135 | 25 | 70 | 0 | 0 | 60 | 50 | 0 | 80 | 40 | 50 | 47 | 52 | 0 | 22 | 16 | 11 | 90 | 0 | 250 | 0 | 0 | 215 | 0 | 0 | 0 | 95 | 80 | 205 | 0 | 400 | 105 | 100 | 113 | 50 | 114 | 0 | 8
Generation at 08:00(Today) | 70 | 189 | 0 | 0 | 300 | 12 | 40 | 344 | 273 | 0 | 20 | 350 | 265 | 0 | 0 | 0 | 50 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 22 | 25 | 13 | 33 | 33 | 11 | 0 | 119 | 90 | 100 | 0 | 0 | 178 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 32 | 100 | 0 | 0 | 0 | 260 | 181 | 8 | 140 | 24 | 10 | 0 | 10 | 0 | 0 | 0 | 21 | 11 | 25 | 15 | 118 | 189 | 8 | 20 | 0.4 | 60 | 58 | 11 | 10 | 100 | 150 | 62 | 10 | 10 | 48 | 0 | 18 | 10 | 290 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 65 | 52 | 0 | 2.61 | 15 | 0 | 113 | 0 | 834 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 128 | 19 | 16 | 0 | 0 | 60 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 16 | 5 | 91 | 0 | 250 | 0 | 0 | 160 | 0 | 0 | 0 | 22 | 0 | 158 | 0 | 364 | 0 | 0 | 36 | 54 | 35 | 0 | 3.6 | 0
199
| Minimum Generation |  | 6767.02 | 8:00
| Highest Generation |  | 10792 | 21:00
| Day Peak Generation |  | 7885.4 | 12:00
| Evening Peak Generation |  | 10792 | 21:00
| HVDC Max Flow |  | 827 | 19:00
| HVDC EvPeak Flow |  | 826 | 21:00
| Load factor L.F |  | 81.14%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-08-18
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-08-17 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7885.4 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 7667.61 | MW
Evening Peak Generation : |  | 10792 | MW Hour : | 21:00 | Available Max Generation : |  | 15000 | MW
E.P. Demand (at gen end) : |  | 10792 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 11700 | MW
Maximum Generation : |  | 10792 | MW Hour : | 21:00 | Reserve(Generation end) |  | 3300 | MW
Total Gen. (MKWH) : |  | 210.163 | System Load Factor : | 81.14% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -264 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-08-18
Actual : | 105.71 | Ft.(MSL) , | Rule curve : | 94.44 | Ft.( MSL )
Gas Consumed : | Total = | 1290.94 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 142984506.58
|  | Coal : | 35899531.68 | Oil : | 184608032.48 | Total : | 363492070.74
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4115.5781 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1400.7397 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1255.2329 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1134.2857 |  |  | 0 | 0%
) | 0 | 0:00 | 1024.9952 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 827.1379 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 460.9308 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 212.9244 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 637.9373 |  |  | 0 | 0%
Total | 0 |  | 11069.7621 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit- 2. | 7) Ghorasal Unit-5
|  |  |  | 2) Khulna ST 110 MW | 8) Ghorashal Unit-4
|  |  |  | 3) Sikalbaha ST 60 MW | 9) Sirajganj Unit-2
4) Siddhirganj ST
5) Ashuganj #4,5
6) Baghabari 100 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Patuakhali 132/3 kV T1&T2 transformers (33 kV side) along with 33 kV bus was under shut down |  |  |  |  | About 20 MW power interruption occurred under Patuakhali S/S
from 9:36 to 10:24 for R/H maintenance. |  |  |  |  | area from 09:36 to 10:24.
b) Chapainawabganj 132/33 kV T4 transformer was switched on at 11:39.
c) Maniknagar-Narinda 132 kV Ckt-2 along with T2 transformer at Narinda S/S was under shut down from
9:39 to 16:30 for DPDC's work.
d) Aminbazar-Savar 132 kV Ckt-1 along with 132 kV main bus at Savar end was under shut down
from 12:45 to 15:43 for DS replacement.
e) Siddhirganj 132/33 kV GT-2 transformer was shut down at 21:13 to attend R/H at 33 kV cable termination.
f) Narshingdi 132/33 kV T2 transformer tripped at 14:30 showing inter trip relay and was switched |  |  |  |  | About 22 MW power interruption occurred under Narshingdi S/S
on at 15:03. |  |  |  |  | area from 14:30 to 15:03.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-08-17 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 70 | 1563000
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 189 | 3225400
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 350 | 8226663
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 40 | 1059968 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 87 | 1665409 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 20 | 279000 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 347 | 8503300 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 356 | 7949000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 350 | 8264750 | Machine problem
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 8640 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 270 | 6395171 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 0 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 0 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 14074 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 248580
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 120 | 3048000 | Frequency control
| Siddhirganj Desh |  | QRPP | 96*1.2 | 0 | 0 | 0 | Contract Expired
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 6720 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217 | 217 | 208 | 4196456 | Testing
| Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 9360 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 46 | 600912
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 235800
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 65 | 312000 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 214586
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 75721 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 72 | 357120 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 33 | 886020 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 810600
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 499900
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 42 | 171852 | Engine problem
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 7527 | Reserve
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 21600 | Reserve
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 1133064
| Dhaka area Total |  |  |  | 5693 | 2983 | 59990193
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 84862
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 126630
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 310080
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 214 | 4950309
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4787815 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 130 | 2798844 | FGMO
44 | Sikalbaha 51 MW PP(Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 0 | 0 | Contract Expired
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
46 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
47 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 229888 | Low demand
48 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 57360 | Low demand
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 667200
50 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 4553280
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 721920
51 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 30 | 136320 | Transformer overload.
52 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 22980
53 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 87 | 479 | Transformer overload.
| Jodiac Power |  | IPP | 54.36 | 0 | 0 | 86140 | on test
| Karnaphuli Power Lid. |  | IPP | 110 | 0 | 113 | 2705624 | RRT
| Chattogram area Total |  |  |  | 2053 | 1177 | 24639731
54 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 135 | 2540702
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
55 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 181 | 4443000 | FGMO
56 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
57 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 260 | 7040000 | FGMO
58 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 30 | 671544 | Engine problem
59 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 54 | 871200
60 | Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
61 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 55 | 836363 | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 697702 | Engine problem
63 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 31781 | Transformer overload.
64 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
65 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
66 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 140 | 1977560
67 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 1601760
68 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 428184
69 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 236700
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 166 | 3360960
70 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 457700 | Engine problem
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 279940
72 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 460370 | Engine problem
73 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1393 | 25935466
74 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 154 | 3696800 | Gas shortage
75 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 387000
76 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 91 | 775680
77 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10900
78 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 132 | 868800 | Low demand
79 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 109 | 2000400
| Mymensingh Area Total |  |  |  | 637 | 506 | 7739580
80 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 59 | 1408000
81 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 58 | 1393200
82 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3394612
83 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 152 | 3381000 | GT-2 under maint.
84 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 768000
85 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 875736
86 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 190416 | Engine problem
87 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 58 | 1321920 | FGMO
88 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 73 | 1002240 | Engine problem
89 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 44 | 803520 | Engine problem
90 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 48 | 1207300 | Gas shortage
91 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
92 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 31 | 620200 | Gas shortage
93 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 290784
94 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7379000 | FGMO
95 | Bibiyana-III 400 MW CCPP |  | PDB | 285 MW | 285 | 0 | 0 | Under shut down
96 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 139860
| Sylhet Area Total |  |  |  | 1834 | 1128 | 24175788
97 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 826 | 17794819
| Khulna 115 MW PP (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
98 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 677760
99 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 42 | 257760
100 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
101 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 67 | 372608
102 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 320 | 8794080 | Line O/L
103 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 302625
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
104 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 50 | 201600 | Low demand
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 746880
106 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 88 | 1169424 | Engine problem
| Khulna Area Total |  |  |  | 2314 | 1653 | 30317556
107 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 343776 | Low demand
108 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
109 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 34 | 644283
110 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 132 | 3172000 | ST under maint.
111 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 96 | 1802816
| Barisal Area Total |  |  |  | 462 | 310 | 5962875
112 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 55 | 1375000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
113 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 270344
114 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 38338
115 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 616300
116 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 8 | 112484 | Low demand
117 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 99585
118 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 195 | 4822518 | FGMO
119 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
120 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 160 | 4536818 | FGMO
121 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 341 | 8288363 | FGMO
122 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 106422
123 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 424080
124 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 16 | 328428
125 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 0 | 175660
126 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 280320
127 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 95 | 645369
128 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
129 | Bagura 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1049376
| Rajshahi Area Total |  |  |  | 2070 | 1187 | 23169405
130 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 92 | 2087564
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
131 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 250 | 5526100
132 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
133 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
| Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 0 | 113 | 1035840 | On test
| Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 42773
| Rangpur Area Total |  |  |  | 492 | 455 | 8692277
| Total |  |  |  | 18446 | 10792 | 210622871
| Eastern Grid Total |  |  |  | 13108 | 7187 | 142480758
| Western Grid Total |  |  |  | 5338 | 3605 | 68142113
| National Grid Total |  |  |  | 18446 | 10792 | 210622871
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2019-08-17
(a) ENTIRE EASTERN GRID : |  | 6618 | MW | (b) ENTIRE WESTERN GRID : |  | 3581 | MW
i) Dhaka area |  | 3061 | MW | i) Khulna area |  | 1373 | MW
ii) Chittagong area |  | 1060 | MW | ii) Rajshahi area |  | 1175 | MW
iii) Comilla area |  | 1094 | MW | iii) Barisal area |  | 323 | MW
iv) Mymensingh area |  | 915 | MW | iv) Rangpur area |  | 710 | MW
v) Sylhet area |  | 488 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 10199 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 72 | 1400 | Sherpur | 110 | 2300 | Jhenida | 106 | 2100
Munsiganj | 118 | 1930 | Srimongal | 38 | 2100 | Bottail | 114 | 2000
Sonargaon | 63 | 2100 | Shahjibazar | 115 | 2300 | G.K Project | 57 | 2000
Shyampur | 120 | 1000 | Fenchuganj | 46 | 1930 | Faridpur | 174 | 2000
Bhulta | 108 | 2100 | Kulawara | 49 | 1930 | Madaripur | 110 | 100
Madanganj | 42 | 1600 | Sylhet | 131 | 1900 | Sariatpur | 45 | 2200
Shitalakhya | 74 | 2000 | Chatak | 31 | 1930 | Gopalganj | 87 | 2000
Rahim steel | 3 | 900 | Sunamganj | 37 | 2000 | Bagerhat | 84 | 1930
Matuail | 58 | 1200 | Biani Bazar | 55 | 2100 | Mongla | 26 | 1100
Ghorasal | 64 | 1900 | Comilla (S) | 172 | 2200 | Satkhira | 91 | 2000
Narsingdi | 113 | 2100 | Comilla(N) | 121 | 2100 | Gallamari | 40 | 2400
Haripur (SBU) | 63 | 1900 | Chandpur | 104 | 2300 | Magura | 52 | 1930
Ullon | 71 | 1900 | Feni | 124 | 2300 | Norail | 24 | 2000
Hasnabad | 167 | 2000 | Chowmuhani | 178 | 2200 | Chuadanga | 87 | 2000
Magbazar | 97 | 1300 | Ashuganj | 55 | 2300 | Barisal(N) | 40 | 2000
Maniknagar | 80 | 1200 | Daudkandi | 124 | 2100 | Barisal (S) | 94 | 2100
Bangabhaban | 16 | 1200 | B.Baria | 140 | 2200 | Patuakhali | 103 | 2100
Narinda | 50 | 2000 | Ramganj | 98 | 2000 | Bhandaria | 52 | 1900
Dhanmondi | 103 | 1300 | Madunaghat | 51 | 2200 | Borhan Uddin | 37 | 2300
Lalbag | 36 | 1300 | Hathazari | 90 | 2200 | Ishurdi | 62 | 2100
Madartek | 47 | 2000 | Khulshi | 162 | 2300 | Ruppur Paromanobik | 1 | 100
Mirpur | 84 | 1900 | Halishahar | 109 | 1900 | Natore | 128 | 1930
Kalyanpur | 93 | 1930 | Baraulia | 124 | 2400 | Bogra | 129 | 2100
Gulshan | 108 | 1300 | Sikalbaha | 21 | 1830 | Noagaon | 111 | 2100
Uttara | 66 | 1900 | Dohazari | 90 | 1900 | Rajshahi | 149 | 2400
Uttara New | 10 | 1300 | Cox'sbazar | 94 | 2100 | C.Nawabganj | 74 | 2000
Kamrangirchar | 46 | 1930 | Chandraghona | 30 | 1900 | Amnura | 36 | 2000
Savar | 102 | 1830 | Kaptai | 4.2 | 1900 | Pabna | 107 | 2100
Bhasantec | 131 | 1300 | A. Khaer Stl. | 0 | 0 | Shahjadpur | 93 | 2200
Agargaon | 44 | 1300 | Bakulia | 85 | 1900 | Serajganj | 91 | 1930
Satmosjid | 87 | 1900 | Julda | 14 | 1830 | Niyamatpur | 61 | 2100
Tongi | 92 | 1400 | TK chemical | 15 | 2000 | Joypurhat | 52 | 2000
Kabirpur | 133 | 2100 | Modern Steel | 0.6 | 1000 | Mohastangor | 16 | 1930
Basundhara | 112 | 2100 | Shahmirpur | 27 | 1900 | Rangpur | 142 | 1930
Manikganj | 90 | 2100 | Khagrachhari | 18 | 1930 | Lalmonirhat | 68 | 2200
Joydevpur | 170 | 2100 | Matarbari | 26.5 | 2200 | Saidpur | 100 | 2300
New Tongi | 71 | 1900 | Baroiar Hat | 34 | 1930 | Purbasadipur | 96 | 2100
Korda | 162 | 2100 | Rangamati | 30 | 2100 | Thakurgaon | 71 | 1930
Dhamrai | 54 | 2100 | Abul Khair 230 | 128 | 2400 | Palashbari | 118 | 2200
Valuka | 70 | 2100 | BSRM | 114 | 1900 | Barapukuria | 50 | 2100
Tangail | 188 | 2100 | Goalpara | 25 | 2000 | Panchagar | 44 | 2000
Mymensing | 232 | 2200 | Central s/s | 87 | 2000 | Joldhaka | 30 | 2200
Kishorganj | 126 | 1930 | Noapara | 73 | 1930 | Kurigram | 38 | 2100
Netrokona | 106 | 2200 | Jessore | 100 | 2000
Jamalpur | 128 | 2200 | Benapol | 36 | 1930
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-08-17
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | 126
Bibiyana | 390 | 8:00 | 383 | 13:00 | Kaliakoir | 374 | 6:00 | 364
Bheramara | 407 | 5:00 | 392 | 21:00 | Bhulta | 382 | 6:00 | 376
Ashuganj(N) | 381 | 6:00 | 376 | 9:00
230 KV | KV |  | KV |  | 230 KV | KV |  | 13:00
Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 220 | 1:00 | 216
Ishurdi | 235 | 6:00 | 224 | 21:00 | Megnaghat | 227 | 4:00 | 222
Ashuganj | 235 | 2:00 | 231 | 11:00 | Fenchuganj | 236 | 1:00 | 233
Serajganj | 230 | 6:00 | 225 | 19:30 | Siddhirganj | 226 | 6:00 | 222
Baghabari | 232 | 6:00 | 230 | 1:00 | Maniknagar | 225 | 6:00 | 220
Barapukuria | 234 | 18:00 | 224 | 19:30 | Old Airport | 224 | 6:00 | 218
Bogra | 226 | 18:30 | 212 | 22:00 | Barisal | 233 | 17:00 | 222
Khulna South | 228 | 6:00 | 210 | 2:00 | AKSML | 217 | 18:00 | 212
Rampura | 222 | 8:00 | 219 | 13:00 | BSRM | 220 | 1:00 | 216
Haripur | 224 | 1:00 | 220 | 12:00 | Bibiyana | 233 | 7:00 | 229
Hasnabad | 225 | 7:00 | 220 | 13:00 | Bhulta | 225 | 1:00 | 221
Aminbazar | 224 | 2:00 | 220 | 12:00 | Ashuganj (S) | 233 | 1:00 | 230
Tongi | 222 | 1:00 | 216 | 11:00 | Kaliakoir | 227 | 6:00 | 218
Comilla (N) | 230 | 6:00 | 227 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 135 | 500 | 132 | 1100 | Khulshi | 130 | 2100 | 126
Munsiganj | 134 | 2000 | 130 | 1500 | Halishahar | 132 | 1930 | 128
Megnaghat | 132 | 100 | 130 | 1600 | Baraulia | 130 | 1830 | 127
Shyampur | 134 | 2000 | 130 | 1200 | Sikalbaha | 132 | 1900 | 129
Bhulta | 130 | 100 | 126 | 1200 | Dohazari | 130 | 1900 | 126
Madanganj | 134 | 700 | 129 | 1200 | Cox'sbazar | 122 | 800 | 115
Shitalakhya | 135 | 600 | 130 | 1200 | Chandraghona | 131 | 700 | 130
Rahim steal | 135 | 100 | 133 | 1200 | Kaptai | 132 | 100 | 130
Matuail | 134 | 500 | 132 | 1000 | A. Khaer Stl. | 130 | 1900 | 126
Ghorasal | 135 | 100 | 135 | 1200 | Bakulia | 130 | 1900 | 127
Narsinghdi | 131 | 500 | 124 | 2100 | Julda | 132 | 1930 | 128
Haripur (SBU) | 135 | 500 | 133 | 1100 | TK Chemical | 132 | 300 | 128
Ullon | 134 | 600 | 131 | 1200 | Modern Steel | 130 | 400 | 128
Hasnabad | 134 | 700 | 130 | 1300 | Shahmirpur | 132 | 1930 | 127
Magbazar | 135 | 600 | 130 | 1200 | Khagrachhari | 131 | 600 | 129
Maniknagar | 139 | 700 | 136 | 1200 | Matarbari | 124 | 1800 | 119
Bangabhaban | 139 | 700 | 136 | 1200 | Baroiar Hat | 126 | 1930 | 123
Narinda | 139 | 700 | 136 | 1200 | Rangamati | 131 | 1800 | 129
Dhanmondi | 134 | 600 | 131 | 1200 | Goalpara | 138 | 700 | 127
Lalbag | 135 | 600 | 131 | 1200 | Central s/s | 137 | 600 | 125
Madartek | 135 | 600 | 130 | 1200 | Noapara | 132 | 900 | 122
Mirpur | 137 | 800 | 132 | 1700 | Jessore | 132 | 700 | 116
Kalyanpur | 138 | 300 | 134 | 1200 | Benapol | 132 | 700 | 118
Gulshan | 134 | 600 | 130 | 1200 | Jhenida | 130 | 700 | 114
Uttara | 135 | 600 | 130 | 1200 | Bottail | 135 | 800 | 125
Uttara New | 133 | 1900 | 128 | 1200 | G.K Project | 140 | 600 | 134
Kamrangirchar | 133 | 600 | 130 | 1200 | Faridpur | 131 | 700 | 122
Savar | 134 | 600 | 130 | 1200 | Madaripur | 136 | 1700 | 127
Bhasantec | 132 | 500 | 128 | 1200 | Sariatpur | 133 | 1800 | 123
Agargaon | 134 | 600 | 129 | 1200 | Gopalganj | 140 | 1800 | 129
Satmosjid | 135 | 600 | 129 | 1200 | Bagerhat | 135 | 800 | 124
Tongi | 135 | 1800 | 130 | 1100 | Mongla | 132 | 700 | 123
Kabirpur | 135 | 1800 | 130 | 2100 | Satkhira | 138 | 600 | 124
Basundhara | 131 | 1830 | 127 | 1100 | Gallamari | 138 | 600 | 128
Manikganj | 136 | 1900 | 131 | 1000 | Magura | 130 | 700 | 112
Joydevpur | 137 | 2000 | 134 | 1300 | Norail | 128 | 800 | 107
New Tongi | 134 | 1830 | 129 | 1200 | Chuadanga | 128 | 800 | 105
Kodda | 134 | 1900 | 125 | 1200 | Barisal(N) | 138 | 1700 | 131
Dhamrai | 135 | 400 | 127 | 2100 | Barisal (S) | 136 | 1700 | 131
Valuka | 130 | 1800 | 118 | 2200 | Patuakhali | 136 | 700 | 128
Tangail | 134 | 600 | 123 | 2100 | Bhandaria | 137 | 700 | 127
Mymensing | 131 | 1800 | 118 | 2000 | Ishurdi | 138 | 600 | 132
Kishorganj | 130 | 500 | 121 | 2000 | Ruppur Paromanobik | 138 | 500 | 132
Netrokona | 128 | 800 | 116 | 1930 | Natore | 135 | 1830 | 127
Jamalpur | 138 | 1800 | 119 | 500 | Bogra | 137 | 1830 | 127
Sherpur | 137 | 1800 | 118 | 800 | Noagaon | 130 | 1800 | 120
Srimongal | 135 | 100 | 133 | 2000 | Rajshahi | 132 | 1830 | 123
Shahjibazar | 135 | 1400 | 131 | 1900 | C.Nawabganj | 130 | 1830 | 120
Fenchuganj | 135 | 600 | 131 | 1900 | Amnura | 134 | 1830 | 120
Khulawara | 134 | 500 | 131 | 1930 | Pabna | 136 | 1830 | 130
Sylhet | 134 | 900 | 131 | 1930 | Shahjadpur | 140 | 600 | 135
Chatak | 132 | 500 | 128 | 1900 | Serajganj | 136 | 500 | 128
Sunamganj | 132 | 700 | 127 | 1900 | Niyamatpur | 130 | 1830 | 115
Biani Bazar | 132 | 700 | 127 | 1930 | Joypurhat | 132 | 1830 | 116
Comilla(s) | 125 | 300 | 120 | 1000 | Mohastangor | 135 | 18302 | 124
Comilla(n) | 133 | 700 | 131 | 2300 | Rangpur | 129 | 1830 | 116
Chandpur | 127 | 1830 | 125 | 100 | Lalmonirhat | 123 | 1800 | 112
Feni | 125 | 1800 | 121 | 1600 | Saidpur | 128 | 1800 | 114
Chowmuhani | 123 | 1830 | 119 | 1930 | Purbasadipur | 128 | 1830 | 113
Ashuganj | 135 | 100 | 132 | 2100 | Thakurgaon | 123 | 1830 | 106
Daudkandi | 130 | 700 | 127 | 2100 | Palashbari | 130 | 1830 | 118
B.Baria | 132 | 700 | 126 | 2200 | Barapukuria | 134 | 1800 | 124

## L-Curve
Date | 2019-08-17
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 72 | 6742 | 3467 | 10209 |  |  |  | QF-LDC-12
0:30 | 168 | 6394.5 | 3258.5 | 9653 | Date: | 2019-08-17
1:00 | 264 | 6047 | 3050 | 9097
1:30 | 252 | 5870 | 2963 | 8833
2:00 | 240 | 5693 | 2876 | 8569
2:30 | 225 | 5604.5 | 2789 | 8393.5 | [5 empty] | Gen. at Eve. Peak | 10792 | 10792 MW (21:00 )
3:00 | 210 | 5516 | 2702 | 8218 | [6 empty] | 21:00
3:30 | 185 | 5469.5 | 2681 | 8150.5 | [5 empty] | Gen. at Day Peak | 7885.4 | 7885.4 MW (12:00 )
4:00 | 160 | 5423 | 2660 | 8083 | [6 empty] | 12:00
4:30 | 125 | 5329.5 | 2650.5 | 7980 | [5 empty] | Highest Generation | 10792
5:00 | 90 | 5236 | 2641 | 7877 | [6 empty] | 21:00
5:30 | 75 | 5081 | 2506.5 | 7587.5
6:00 | 60 | 4926 | 2372 | 7298
6:30 | 42 | 4764.77 | 2300.62 | 7065.39
7:00 | 24 | 4603.54 | 2229.24 | 6832.78
7:30 | 29 | 4595.3 | 2204.6 | 6799.9
8:00 | 34 | 4587.06 | 2179.96 | 6767.02
8:30 | 24 | 4769.598 | 2198.18 | 6967.778
9:00 | 14 | 4952.136 | 2216.4 | 7168.536
9:30 | 79 | 4982.382 | 2284.75 | 7267.132
10:00 | 144 | 5012.628 | 2353.1 | 7365.728
10:30 | 137 | 5093.709 | 2395.35 | 7489.059
11:00 | 130 | 5174.79 | 2437.6 | 7612.39
11:30 | 110 | 5284.395 | 2464.5 | 7748.895
12:00 | 90 | 5394 | 2491.4 | 7885.4
12:30 | 47 | 5514.33 | 2513.85 | 8028.18
13:00 | 4 | 5634.66 | 2536.3 | 8170.96
13:30 | 9 | 5673.68 | 2620.4 | 8294.08
14:00 | 14 | 5712.7 | 2704.5 | 8417.2
14:30 | 24 | 5733.2 | 2710.8 | 8444
15:00 | 34 | 5753.7 | 2717.1 | 8470.8
15:30 | 44 | 5755.5 | 2701.95 | 8457.45
16:00 | 54 | 5757.3 | 2686.8 | 8444.1
16:30 | 91 | 5615.75 | 2650.6 | 8266.35
17:00 | 128 | 5474.2 | 2614.4 | 8088.6
17:30 | 128 | 5271.85 | 2572.3 | 7844.15
18:00 | 128 | 5069.5 | 2530.2 | 7599.7
18:30 | 108 | 5731.25 | 2998.1 | 8729.35
19:00 | 88 | 6393 | 3466 | 9859
19:30 | 160 | 6853 | 3613 | 10466
20:00 | 176 | 6963 | 3667 | 10630 |  |  |  | Executive Engineer
20:30 | 196 | 7075 | 3636 | 10711 |  |  |  | Network Operation Division
21:00 | 216 | 7187 | 3605 | 10792
21:30 | 213 | 7176.5 | 3605 | 10781.5
22:00 | 210 | 7166 | 3605 | 10771 |  |  |  |  | Page 6 of 7
22:30 | 141 | 7027 | 3600.5 | 10627.5
23:00 | 72 | 6888 | 3596 | 10484
23:30 | 72 | 6815 | 3531.5 | 10346.5
24:00 | 72 | 6742 | 3467 | 10209
10792 MW (21:00 )
7885.4 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-08-17 |  | Energy | 210162961
[10 empty] | 2019-08-17 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4186 | 826 | 2301 | 1932 | 342 | 215 | 245 | 0 | 162
0:30 | 4189.5 | 785 | 2266.5 | 1583.5 | 287 | 214 | 172.5 | 0 | 155 | Date: | 2019-08-17
1:00 | 4193 | 744 | 2232 | 1235 | 232 | 213 | 100 | 0 | 148
1:30 | 4142 | 744 | 2206.5 | 1060.5 | 246 | 212.5 | 75.5 | 0 | 146 | [7 empty] | Total Energy | 210.163 | Total Energy Gen 210.163 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 210.163 MKWHr
2:00 | 4091 | 744 | 2181 | 886 | 260 | 212 | 51 | 0 | 144 | [7 empty] | Energy not Served | 0
2:30 | 4081.5 | 743.5 | 2162.5 | 753.5 | 271.5 | 209.5 | 29.5 | 0 | 142 | [7 empty] | Energy Requirement | 210.163
3:00 | 4072 | 743 | 2144 | 621 | 283 | 207 | 8 | 0 | 140
3:30 | 4067.5 | 743.5 | 2101 | 601.5 | 285.5 | 206.5 | 8 | 0 | 137 | [6 empty] | Shortage
4:00 | 4063 | 744 | 2058 | 582 | 288 | 206 | 8 | 0 | 134
4:30 | 4058.5 | 744 | 1972.5 | 570.5 | 287.5 | 206 | 8 | 0 | 133
5:00 | 4054 | 744 | 1887 | 559 | 287 | 206 | 8 | 0 | 132
5:30 | 3928.5 | 691 | 1801 | 539 | 287.5 | 206.5 | 4 | 0 | 130
6:00 | 3803 | 638 | 1715 | 519 | 288 | 207 | 0 | 0 | 128
6:30 | 3706 | 637.5 | 1638.5 | 461.5 | 288 | 210.5 | 0 | 0 | 120 |  |  |  |  | Coal
7:00 | 3609 | 637 | 1562 | 404 | 288 | 214 | 0 | 0 | 112
7:30 | 3607 | 637.5 | 1527 | 406.5 | 287.5 | 214.5 | 0 | 0 | 110 |  |  |  | Oil |  |  |  | ,
8:00 | 3605 | 638 | 1492 | 409 | 287 | 215 | 0 | 0 | 108
8:30 | 3669 | 638 | 1592.5 | 444 | 288.5 | 215 | 0 | 0 | 107
9:00 | 3733 | 638 | 1693 | 479 | 290 | 215 | 0 | 0 | 106
9:30 | 3750.5 | 686.5 | 1685 | 488.5 | 313.5 | 215 | 0 | 0 | 112
10:00 | 3768 | 735 | 1677 | 498 | 337 | 215 | 0 | 0 | 118
10:30 | 3826.5 | 724 | 1739 | 500 | 342 | 212.5 | 0 | 0 | 120
11:00 | 3885 | 713 | 1801 | 502 | 347 | 210 | 0 | 0 | 122
11:30 | 3890 | 722.5 | 1911 | 518.5 | 345 | 210 | 0 | 0 | 127
12:00 | 3895 | 732 | 2021 | 535 | 343 | 210 | 0 | 0 | 132
12:30 | 3910.5 | 730 | 2072.5 | 608 | 343 | 210 | 0 | 0 | 133
13:00 | 3926 | 728 | 2124 | 681 | 343 | 210 | 0 | 0 | 134
13:30 | 3926 | 728 | 2124 | 681 | 343 | 210 | 0 | 0 | 134
14:00 | 3926 | 728 | 2124 | 681 | 343 | 210 | 0 | 0 | 134
14:30 | 3929.5 | 728.5 | 2114 | 834.5 | 342 | 211 | 0 | 0 | 139
15:00 | 3933 | 729 | 2104 | 988 | 341 | 212 | 0 | 0 | 144
15:30 | 3952.5 | 729 | 2099 | 965 | 341.5 | 211.5 | 0 | 0 | 141
16:00 | 3972 | 729 | 2094 | 942 | 342 | 211 | 0 | 0 | 138
16:30 | 3961 | 729 | 1989 | 886.5 | 341.5 | 211 | 2.5 | 0 | 135
17:00 | 3950 | 729 | 1884 | 831 | 341 | 211 | 5 | 0 | 132
17:30 | 3876.5 | 729 | 1724 | 817.5 | 341.5 | 211.5 | 14 | 0 | 127
18:00 | 3803 | 729 | 1564 | 804 | 342 | 212 | 23 | 0 | 122
18:30 | 3925 | 778 | 1766 | 1344.5 | 342 | 212.5 | 218 | 0 | 143
19:00 | 4047 | 827 | 1968 | 1885 | 342 | 213 | 413 | 0 | 164
19:30 | 4015 | 826 | 2127 | 2302 | 343 | 213 | 474 | 0 | 166
20:00 | 4032 | 826 | 2194 | 2373 | 343 | 213 | 487 | 0 | 162
20:30 | 4089 | 826 | 2225.5 | 2407 | 342.5 | 213.5 | 443.5 | 0 | 164
21:00 | 4146 | 826 | 2257 | 2441 | 342 | 214 | 400 | 0 | 166
21:30 | 4154 | 826.5 | 2254.5 | 2434 | 342.5 | 214.5 | 386.5 | 0 | 169
22:00 | 4162 | 827 | 2252 | 2427 | 343 | 215 | 373 | 0 | 172
22:30 | 4164 | 826.5 | 2263.5 | 2295.5 | 342 | 215 | 350 | 0 | 171
23:00 | 4166 | 826 | 2275 | 2164 | 341 | 215 | 327 | 0 | 170
23:30 | 4176 | 826 | 2288 | 2048 | 341.5 | 215 | 286 | 0 | 166 | Max Temp. in Dhaka |  | 33.4° C
24:00 | 4186 | 826 | 2301 | 1932 | 342 | 215 | 245 | 0 | 162
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 210.163 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 210.163 MKWHr
Note on W13: Author:

## Generation
2019-08-17
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 123 | 122 | 117 | 116 | 116 | 117 | 124 | 125 | 125 | 125 | 120 | 120 | 120 | 120 | 122 | 121 | 121 | 122 |  | 123 | 123 | 123 | 124 | 125 | 125 | 125 | 2794309
2 | Karnaphuli Hydro PP Unit-4 & 5 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2156000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [19 empty] | 8 | 25 | 25 | 25 | 8 |  | 0 | 84862
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 5 | 10 | 10 | 9 | 16 | 6 | 12 | 19 | 11.7 | 10.1 | 3.1 | 0.3 | [8 empty] | 126630
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 204 | 214 | 204 | 205 | 179 | 181 | 181 | 229 | 204 | 204 | 204 | 204 | 204 | 205 | 204 | 204 | 204 |  | 219 | 204 | 204 | 203 | 204 | 204 | 205 | 4787815
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 100 | 95 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 130 | 131 | 130 | 130 | 130 | 130 |  | 132 | 130 | 130 | 130 | 130 | 130 | 130 | 2798844
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 17 | 0 | [17 empty] | 70 | 82 | 51 | 51 | 34 | 0 |  | 229888
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 139 | 145 | 145 | 145 | 120 | 120 | 78 | 100 | 125 | 125 | 127 | 127 | 120 | 120 | 120 | 120 | 70 | 70 |  | 100 | 100 | 100 | 120 | 120 | 120 | 120 | 3048000
17 | Siddhirganj 335 MW CCPP | 206 | 205 | 205 | 207 | 208 | 120 | 120 | 120 | 120 | 154 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 202 | 202 | 206 | 208 | 209 | 207 | 206 | 4196456
18 | Kodda 300 MW PP Unit-2 (Summit) | [19 empty] | 1 | 7 | 0 | 0 |  |  |  | 7527
19 | Ashuganj 195MW PP (APSCL-United) | 55 | 55 | 55 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 55 | 63 | 45 | 45 | 45 | 45 | 8 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 836363
20 | Ghorasal TPP (Unit-1&2) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1563000
21 | Ghorasal Repowered CCPP Unit-3 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 124 | 124 | 124 | 124 | 124 | 124 | 124 | 123 | 123 | 124 |  | 140 | 133 | 138 | 189 | 190 | 190 | 190 | 3225400
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 320 | 320 | 320 | 320 | 270 |  | 320 | 350 | 350 | 350 | 350 | 350 | 350 | 8226663
26
28 | Ashuganj TPP Unit- 3 | 135 | 135 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 135 | 135 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 135 | 135 | 135 | 135 | 2540702
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 30 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 30 | 30 | 27 | 27 | 671544
33 | Ashuganj 225 MW CCPP | 181 | 181 | 180 | 190 | 190 | 161 | 175 | 176 | 189 | 191 | 186 | 191 | 195 | 183 | 182 | 183 | 181 | 182 |  | 203 | 181 | 181 | 181 | 181 | 188 | 188 | 4443000
34 | Ashuganj 450 MW CCPP(South) | 305 | 310 | 320 | 305 | 310 | 255 | 270 | 270 | 280 | 285 | 275 | 310 | 305 | 305 | 305 | 305 | 305 | 260 |  | 285 | 260 | 260 | 260 | 260 | 260 | 260 | 7040000
Ashuganj 450 MW CCPP(North)
35 | Ashuganj 55 MW PP (Precision) | 55 | 56 | 56 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 51 | 51 | 51 | 50 | 51 | 53 | 10 |  | 10 | 10 | 50 | 54 | 53 | 53 | 53 | 871200
36 | Chandpur 150 MW CCPP | 90 | 90 | 90 | 90 | 90 | 90 | 40 | 40 | 40 | 40 | 42 | 40 | 40 | 88 | 86 | 86 | 88 | 85 |  | 115 | 140 | 140 | 140 | 140 | 140 | 140 | 1977560
37 | Tongi 80 MW GTPP
38 | Haripur GTPP | [11 empty] | 0 | 10 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 279000
39 | Haripur 412 MW CCPP | 345 | 345 | 352 | 345 | 345 | 345 | 345 | 358 | 367 | 348 | 355 | 350 | 346 | 350 | 344 | 344 | 344 | 344 |  | 362 | 345 | 349 | 347 | 345 | 345 | 347 | 8503300
40 | Meghnaghat 450 MW CCPP(MPL) | 350 | 350 | 350 | 350 | 350 | 350 | 300 | 300 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 |  | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 8264750
41 | Haripur 360MW CCPP(HPL) | 355 | 354 | 354 | 354 | 354 | 358 | 333 | 303 | 353 | 351 | 351 | 345 | 300 | 300 | 300 | 300 | 300 | 250 |  | 320 | 320 | 320 | 356 | 356 | 357 | 354 | 7949000
42 | RPCL 210MW CCPP | 176 | 178 | 179 | 190 | 190 | 191 | 178 | 172 | 156 | 155 | 137 | 136 | 126 | 127 | 127 | 138 | 152 | 153 |  | 150 | 152 | 153 | 154 | 157 | 154 | 155 | 3696800
43
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 58 | 60 | 60 | 60 | 60 | 60 | 60 | 59 | 57 | 57 | 56 |  | 58 | 58 | 59 | 59 | 60 | 60 | 60 | 1408000
45 | Fenchugonj CCPP Phase-2 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 |  | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 1393200
46 | Shajibazar 330 MW CCPP | 151 | 152 | 152 | 151 | 151 | 150 | 150 | 158 | 152 | 151 | 152 | 150 | 151 | 150 | 151 | 152 | 151 | 150 |  | 150 | 151 | 150 | 152 | 150 | 152 | 151 | 3381000
47 | Shahjibazar GTPP Unit- 8 & 9 | 63 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 63 | 61 | 61 | 60 | 61 | 61 | 51 | 58 | 64 | 63 |  | 62 | 63 | 63 | 58 | 59 | 63 | 63 | 1321920
48 | Shahjibazar 86MW PP (Shahjibazar) | 76 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 72 | 72 | 73 | 72 | 50 | 10 |  | 40 | 73 | 73 | 73 | 73 | 70 | 70 | 1002240
49 | Shahjibazar 50MW PP (EPL) | 46 | 46 | 46 | 46 | 46 | 5 | 5 | 5 | 5 | 5 | 5 | 44 | 44 | 44 | 45 | 44 | 44 | 10 |  | 10 | 40 | 45 | 44 | 45 | 45 | 45 | 803520
50 | Sylhet 150 MW CCPP | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 47 | 48 | 47 | 50 | 48 | 50 | 50 |  | 50 | 47 | 48 | 48 | 47 | 48 | 48 | 1207300
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | 30 | 30 | 30 | 30 | 30 | 30 | 10 | 12 | 12 | 12 | 12 | 30 | 30 | 31 | 31 | 31 | 12 | 12 |  | 32 | 31 | 31 | 31 | 30 | 30 | 30 | 620200
53 | Sylhet 10MW PP (Desh) | 10 | 0 | [10 empty] | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 139860
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 190416
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 50 | 53 | 53 | 53 | 11 | 11 |  | 18 | 50 | 50 | 50 | 50 | 48 | 48 | 768000
56 | Shahjahanulla 25 MW PP | 24 | 0 | [10 empty] | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 290784
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 290 | 310 | 315 | 300 | 300 | 310 | 315 | 315 | 300 | 295 | 295 | 280 | 285 | 290 | 290 | 270 | 270 |  | 280 | 306 | 300 | 300 | 295 | 285 | 310 | 7379000
58 | Nababganj 55 MW PP (Southern power ) | [19 empty] | 17 | 17 | 17 | 17 | 17 |  | 0 | 75721
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 0 |  |  | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 4553280
61 | Narshingdi 22 MW PP (Doreen) | 22 | 0 | [8 empty] | 22 | 22 | 22 |  |  |  | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 248580
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 0 |  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 387000
63 | Impoprt (Tripura) | 148 | 144 | 140 | 134 | 132 | 128 | 112 | 108 | 106 | 118 | 122 | 132 | 134 | 138 | 144 | 138 | 132 | 122 |  | 164 | 166 | 162 | 166 | 172 | 170 | 162 | 3360960
64 | Malancha, Ctg. EPZ (United) | 42 | 20 | 10 | 10 | 10 | 23 | 14 | 14 | 17 | 14 | 14 | 14 | 26 | 16 | 16 | 8 | 34 | 34 |  | 34 | 42 | 42 | 42 | 42 | 42 | 42 | 721920
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 0 |  |  | 8 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 428184
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 236700
67 | Jangalia 33MW PP (Summit) | 33 | 0 | [8 empty] | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 457700
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 20 | 20 |  | 19 | 20 | 20 | 20 | 20 | 20 | 20 | 460
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 8 | 18 | 18 | 18 | 286020
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 810600
72 | Rupganj 33 MW PP(Summit) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 7 | 7 | 7 | 24 | 29 | 29 |  | 29 | 29 | 29 | 33 | 29 | 29 | 33 | 499900
73 | Ghorashal 108MW PP (Regent) | 90 | 87 | 87 | 87 | 87 | 87 | 64 | 12 | 12 | 12 | 82 | 83 | 81 | 84 | 82 | 80 | 76 | 22 |  | 61 | 80 | 87 | 87 | 87 | 87 | 87 | 1665409
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [19 empty] | 2 | [5 empty] | 0 | 6720
78 | Gazipur 52 MW PP | [19 empty] | 14 | 35 | 40 | 42 | 51 | 24 | 0 | 171852
79 | Kodda 150MW PP | [19 empty] | 50 | 55 | 65 | 65 | 65 | 65 | 36 | 312000
80 | Jamalpur 95 MW PP(Powerpac) | 63 | 8 | 0 | [5 empty] | 3 | 8 | 8 | 8 | 8 | 13 | 32 | 32 | 22 | 8 |  | 49 | 91 | 91 | 91 | 91 | 91 | 91 | 775680
81 | Jangalia 52 MW PP (Lakdanavi) | 0 | [18 empty] | 9 | 43 | 52 | 52 | 52 | 52 | 52 | 279940
| Gazipur 100 MW PP | [8 empty] | 10 | 17 | 17 | 17 | 45 | 105 | 105 | 105 | 52 | 52 |  | 105 | 105 | 105 | 105 | 105 | 105 | 53 | 1133064
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1.44 | 1.66 | 2.636 | 3.128 | 6.19 | 0.8 | 3.36 | 0.5 | 0.5 | 1 | 0.8 | 0.1 |  | 0 | [6 empty] | 22980
| Jodiac Power | [9 empty] | 5 | 16 | 18 | 5 | 8 | 14 | 10 | 11 | [8 empty] | 0 | 86140
| Karnaphuli Power Lid. | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2705624
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [19 empty] | 10 | 4 |  |  |  |  | 0 | 14074
86 | Meghnaghat CCPP(Summit) | 248 | 245 | 243 | 260 | 244 | 245 | 247 | 270 | 285 | 287 | 275 | 274 | 273 | 270 | 271 | 265 | 268 | 270 |  | 280 | 260 | 270 | 270 | 245 | 286 | 295 | 6395171
87 | Meghnaghat 100 MW(IEL) | [19 empty] | 3 | 7 |  |  |  |  | 0 | 8640
88 | Ghorashal 78.5 MW PP(MAX) | 75 | 75 | 50 | 50 | 50 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 50 | 50 | 50 | 50 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 1059968
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [19 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 57360
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 47 | 50 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 36 | 50 | 50 | 50 | 50 | 10 | 10 |  | 19 | 50 | 50 | 50 | 50 | 50 | 50 | 875736
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 20 | 43 | 43 | 43 | 12 | 12 |  | 12 | 20 | 36 | 43 | 43 | 43 | 43 | 697702
94 | Gagnagar 102 MW PP (Digital Power) | [19 empty] | 7 | 0 | [5 empty] | 9360
95 | Patenga 50MW PP (Baraka) | [12 empty] | 2 | 6 | 6 | 6 | 6 | 6 |  | 22 | 50 | 50 | 50 | 50 | 50 | 50 | 310080
96 | Chattogram 108 MW PP (ECPV) | [19 empty] | 28 | 30 | 30 | 30 | 30 |  | 0 | 136320
97 | Katpotti 52 MW PP (Sinha) | 46 | 30 | 26 | 26 | 18 | 18 | 6 | 6 | 6 | 6 | 6 | 6 | 14 | 18 | 18 | 18 | 18 | 6 |  | 25 | 23 | 46 | 46 | 47 | 47 | 46 | 600912
98 | Bosila 108MW PP(CLC) | [12 empty] | 8 | 8 | 8 | 8 | 8 | 8 |  | 72 | 72 | 72 | 72 | 72 | 24 | 0 | 357120
99 | Madanganj-55 MW PP(Summit)
100 | Manikganj 55 MW PP (Northern) | [19 empty] | 55 | 55 | 55 | 55 | 55 |  | 0 | 214586
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 130 | 100 | 100 | 163 | 163 | 163 | 163 | 163 | 130 | 130 | 130 | 100 | 100 |  | 130 | 130 | 130 | 163 | 163 | 163 | 163 | 3394612
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0.1 | 0.4 | 0.5 | 2.5 | 1.6 | 2.2 | 1.3 | 0.2 | 1.5 | 0.2 | 0.3 | 0.1 |  | 0 | [6 empty] | 10900
103 | Kamalaghat 54 MW PP(Banco Energy) | [19 empty] | 20 | 40 | 53 | 53 | 53 | 35 | 35 | 235800
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 7 | 7 | 0 | [14 empty] | 12 |  | 100 | 120 | 120 | 132 | 150 | 150 | 120 | 868800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [19 empty] | 8 | 15 | 0 | 0 |  |  |  | 21600
115 | Juldah 100 MW PP Unit-3 (Acorn) | 30 | 20 | 0 | [9 empty] | 10 | 10 | 10 | 10 | 10 | 10 |  | 70 | 90 | 100 | 100 | 100 | 100 | 100 | 667200
116 | Chandpur 200MW (Desh energy) | 90 | 70 | 38 | 35 | 35 | 20 | [5 empty] | 10 | 17 | 38 | 52 | 52 | 30 | 17 |  | 70 | 160 | 180 | 200 | 200 | 200 | 200 | 1601760
117 | Ashuganj 150MW PP (Midland) | [19 empty] | 11 | [5 empty] | 0 | 31781
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 109 | 109 | 55 | 55 | 55 | 55 | 8 | 8 | 50 | 50 | 55 | 59 | 109 | 109 | 109 | 109 | 109 | 109 |  | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 2000400
| Anwara 300 MW PP (United) | 33 | 0 | [7 empty] | 0 |  |  |  | 5 | 16 | 16 | 16 | 16 |  | 60 | 83 | 84 | 87 | 87 | 15 | 0 | 479
120 | Eastern Zone Total | 6047 | 5693 | 5516 | 5423 | 5236 | 4926 | 4603.54 | 4587.06 | 4952.136 | 5012.628 | 5174.79 | 5394 | 5634.66 | 5712.7 | 5753.7 | 5757.3 | 5474.2 | 5069.5 |  | 6393 | 6853 | 6963 | 7187 | 7166 | 6888 | 6742 | 142020848
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 49 | 0 | [11 empty] | 16 | 16 | 16 | 0 |  |  | 33 | 95 | 115 | 115 | 115 | 115 | 68 | 677760
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 35 | 3 | 0 | [16 empty] | 28 | 34 | 40 | 42 | 41 | 41 | 41 | 257760
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 70 | 17 | 0 | [10 empty] | 17 | 17 | 17 | 17 | 17 |  | 81 | 90 | 90 | 105 | 105 | 105 | 105 | 746880
130
131
132
133
| Barisal 110 MW PP (Summit ) | 48 | 0 | [17 empty] | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 343776
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 97 | 97 | 96 | 97 | 73 | 27 | 22 | 22 | 21 | 23 | 52 | 97 | 97 | 96 | 96 | 95 | 97 | 22 |  | 95 | 97 | 97 | 96 | 97 | 97 | 98 | 1802816
| Bhola 225 MW CCPP | 134 | 134 | 135 | 135 | 135 | 134 | 132 | 136 | 135 | 131 | 134 | 133 | 130 | 130 | 131 | 132 | 110 | 123 |  | 135 | 134 | 133 | 132 | 130 | 135 | 134 | 3172000
140 | Bhola 33 MW PP (Venture) | 34 | 32 | 32 | 34 | 30 | 25 | 21 | 22 | 21 | 22 | 21 | 23 | 22 | 23 | 25 | 20 | 22 | 23 |  | 28 | 34 | 35 | 34 | 35 | 34 | 35 | 644283
141 | Noapara 100 MW PP (Bangla Trac) | [19 empty] | 0 | 30 | 36 | 50 | 50 | 48 | 0 | 201600
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 8 | 0 | [10 empty] | 8 | 8 | 8 | 0 |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 302625
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 5 | 23 |  | 51 | 58 | 70 | 67 | 67 | 56 | 23 | 372608
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | 88 | 88 | 53 | 35 | 36 | 18 | 18 | 0 |  |  |  | 18 | 17 | 54 | 53 | 53 | 53 | 54 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 1169424
146 | Bheramara HVDC | 744 | 744 | 743 | 744 | 744 | 638 | 637 | 638 | 638 | 735 | 713 | 732 | 728 | 729 | 729 | 729 | 729 | 729 |  | 827 | 826 | 826 | 826 | 827 | 826 | 826 | 17794819
147 | Bheramara 360 MW CCPP | 410 | 410 | 410 | 410 | 410 | 410 | 360 | 320 | 320 | 320 | 320 | 320 | 350 | 350 | 350 | 350 | 350 | 300 |  | 300 | 300 | 300 | 320 | 320 | 320 | 320 | 8794080
148
149
150 | Barapukuria TPP Unit-1 | 82 | 84 | 83 | 83 | 83 | 84 | 84 | 83 | 86 | 87 | 97 | 93 | 94 | 93 | 91 | 92 | 91 | 92 |  | 92 | 93 | 93 | 92 | 93 | 92 | 91 | 2087564
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 176 | 200 | 205 | 204 | 204 | 204 | 204 | 204 | 250 | 250 | 250 | 249 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 249 | 251 | 5526100
153 | Baghabari 71 MW GTPP | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 60 | 60 | 60 | 1375000
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 270344
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 193 | 186 | 186 | 187 | 196 | 192 | 168 | 171 | 175 | 176 | 202 | 190 | 189 | 191 | 193 | 197 | 196 | 192 |  | 189 | 193 | 194 | 195 | 192 | 185 | 194 | 4822518
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 202 | 201 | 204 | 207 | 207 | 200 | 178 | 177 | 172 | 162 | 165 | 160 | 167 | 196 | 187 | 187 | 187 | 179 |  | 166 | 156 | 158 | 160 | 156 | 156 | 162 | 4536818
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 316 | 368 | 367 | 368 | 368 | 313 | 316 | 320 | 331 | 329 | 360 | 357 | 327 | 320 | 327 | 334 | 310 | 322 |  | 386 | 351 | 355 | 341 | 340 | 378 | 380 | 8288363
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [19 empty] | 8 | 27 | 39 | 0 | 0 |  |  | 38338
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 5 | 5 | 5 | 5 | 5 | 5 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 424080
163 | Bogura 20 MW PP (Energyprima) | 16 | 16 | 16 | 16 | 16 | 4 | 4 | 4 | 13 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 328428
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 11 | 11 | 0 | 11 | 11 | 11 | 175660
165 | Amnura 50 MW PP(Sinha) | 50 | 50 | 50 | 50 | 50 | 50 | 12 | 12 | 12 | 12 | 12 | 12 | 25 | 25 | 25 | 25 | 25 | 25 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 616300
166 | Katakhali 50 MW PP (Northern) | 8 | 8 | 8 | 8 | 8 | 0 | [13 empty] | 24 | 24 | 8 | 8 | 8 | 8 | 8 | 112484
167 | Katakhali 50 MW Peaking PP | [19 empty] | 44 | 44 | 47 | 0 | 0 |  |  | 99585
168 | Santahar 50 MW Peaking PP | [19 empty] | 20 | 29 | 30 | 30 | 21 | 20 | 0 | 106422
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 0 | [10 empty] | 8 | 8 | 8 | 0 | 2 |  | 25 | 52 | 52 | 52 | 52 | 25 | 25 | 280320
170 | Chapainawabganj 100 MW Peaking PP | 48 | 48 | 8 | 8 | 8 | 0 | [13 empty] | 92 | 95 | 95 | 95 | 95 | 95 | 95 | 645369
171 | Baghabari 200 MW PP (Paramount)
172 | Bagura 113 MW PP (Confidence) | 55 | 35 | 0 | [9 empty] | 35 | 70 | 72 | 36 | 36 | 36 |  | 110 | 110 | 113 | 113 | 113 | 113 | 113 | 1049376
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 80 | 70 | 35 | 0 | [9 empty] | 27 | 35 | 35 | 37 | 43 |  | 108 | 111 | 111 | 113 | 113 | 113 | 113 | 1035840
177 | Sympa Solar Power 8MW | [6 empty] | 0.24 | 0.96 | 1.4 | 3.1 | 8.6 | 8.4 | 8.3 | 3.5 | 6.1 | 4.8 | 1.4 | 0.2 | [8 empty] | 42773
178
178