## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-10-18 | Sunday
|  |  | Date (day): | 2020-10-18 |  | Sunday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13861.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14804 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-10-17 | 2020-10-18 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  |  | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 115 | 115 | 115 | 75 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 200 | 200 | 165 |  | Gas shortage
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 67 | 67 | 65 | 65 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 72 | 72 | 72 | 72 | 36 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under S/D for dust in gas.
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 343 | 274 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 420 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 11 | 16 | 16 | 16 | 84 |  | Fuel shortage
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 255 | 285 | 305 | 305
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 79 | 80 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 48 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 74 | 10 | 74 | 26 |  | Fuel shortage
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 185 | 150 | 100 | 150
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 7 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 94 | 94 | 94 | 94 | 8 |  | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 64 | 150 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Engine problem
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 45 | 55 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 51 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 190 | 300 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 120 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 95 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 140 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 80 | 86 | 85 | 85 |  | 20 | Engine problem
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 72 | 34 | 104 | 104
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 2736 | 3201 | 3399 | 3803 | 736 | 1182
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 115 | 120 | 120 | 60 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 14 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 47 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 122 | 123 | 123 | 123 | 107 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 205 | 204 | 221 | 221
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 140 | 145 | 145
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 51 | 102 | 102 | 102
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 100 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 22 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 21 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 6 | 10 | 10
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 90 | 96 | 97 | 97 |  | 11 | Engine problem
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 142 | 178 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 54 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 100 | 100 | 100
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 824 | 1335 | 1803 | 1778 | 347 | 109
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 80 | 80 | 80 | 80 | 49 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 |  | 134 | Under maint
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 182 | 189 | 225 | 225 |  |  | FGMO
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 260 | 360 | 360 |  |  | FGMO
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 355 | 300 | 350 | 350 |  |  | FGMO
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 29 | 30 | 30 | 15 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 47 | 50 | 55 | 55
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 8 | 8 | 8 | 187 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 9 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 127 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 42 | 25 | 50
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 88 | 95 | 95 | 95 |  | 68 | ST under shut down
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 155 | 200 | 200
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 22 | 22
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 10 | 10
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 122 | 166 | 165 | 173
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 42 | 52 | 25 | 52
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 20 | 21 | 21
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 50 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 17 | 0 | 17 | 97 |  | Engine problem & Fuel shortage
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 101 | 101 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1423 | 1812 | 2018 | 2295 | 483 | 202
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 148 | 151 | 160 | 160 | 42 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 20 | 20 |  | 2 | Engine problem
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 40 | 32 | 49 | 49 |  | 46 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 190 | 192 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 65 | 115 | 115 | 115
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 462 | 507 | 545.6 | 544 | 42 | 48
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 82 | 82 | 85 | 85
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 43 | 43 | 43 | 43 |  | 47 | Unit-4 under shut down
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 |  | 53 | STG under maint.
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 160 | 144 | 160 | 160 |  | 170 | GT-2 S/D & ST Under maint.
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 50 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 43 | 42 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 63 | 63 | 65 | 65 |  |  | FGMO
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 86 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 80 | 150 | 150
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 300 | 341 | 341 |  |  | FGMO
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 414 | 416 | 400 | 400
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1388 | 1461 | 1581 | 1581 | 0 | 270
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 918 | 919 | 928 | 928
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 32 | 115 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 24 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 210 | 220 | 220
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 320 | 365 | 410 | 410 | 0
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 53 | 35 | 35 |  | 70 | Fuel shortage
| 108 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1407 | 1826 | 1898 | 2054 | 0 | 70
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 110 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 25 | 37 | 33 | 33
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 88 | 91 | 92 | 92 |  | 3 | Engine problem
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 460 | 600 | 580 | 600
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 589 | 838 | 815 | 835 | 0 | 197
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 42 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 20 | 20 | 20 | 20 | 30 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 50 | 50
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 156 | 173 | 225 | 225 |  |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 157 | 215 | 220 | 220 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 329 | 413 | 414 | 414 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 31 | 0 | 30
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 19 | 21 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 10 | 10 | 10 | 10
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 52 | 52 | 52
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 95 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 25 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 109 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 734 | 1418 | 1550 | 1670 | 461 | 0
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 52 | 89 | 94 | 94 |  | 19 | Engine problem
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 208 | 239 | 252 | 244 | 294 | 59
|  | Total |  |  |  |  | 20383 | 19892 | 9771 | 12637 | 13861.6 | 14804 | 2363 | 2137
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9302.4374 | 12031 | 13196.875 | 14094.0828
| A. |  | 2020-10-17 | (Yesterday) |  |  |  |  | Saturday
| 1 | Highest Generation : |  |  | 12637 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
| 2 | Minimum Generation : |  |  | 8773 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12637 | MW
| 3 | Day peak Generation : |  |  | 9771 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12031 | MW
| 4 | Evening peak Generation : |  |  | 12637 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 257.0104 | MKWHr | By Solar | 0.1556 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 141.0737 | MKWHr |  | By Oil: | 71.1117 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 16.5552 | MKWHr |  | By Hydro: | 2.8351 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2363 | MW | Dhaka | 4203 | 4203 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2137 | MW | Chittagong | 1127 | 1127 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4500 | MW | Khulna | 1536 | 1536 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1177.35 | MMCFD |  |  | Rajshahi | 1290 | 1290 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 163258100.038 | ii) Oil : | Taka | 575018190.51 | Comilla | 1243 | 1243 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 76453720 | Total | Taka | 814730010.548 | Mymensingh | 945 | 945 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 549 | 549 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 140 | MW (E to W) at | 19:30 | hrs | Barisal | 371 | 371 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 76 | MW at | 3:00 | hrs | Rangpur | 767 | 767 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 35.7° C |  |  | Total | 12031 | 12031 |  | 0
| B. |  | 2020-10-18 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 34.7° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14804 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10600 | MW
| 4 | Reserve(Generation end) |  |  |  | 1804 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 264.3931 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8928 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.0364 | MKWHr. | ii) HVDC Flow at Peak Time |  | 919 | MW at | 19:30 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.2429 | MKWHr. | iii) Maximum HVDC Flow : |  | 919 | MW at | 5:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 102.19 |  | (b) Today: | 102.16 |  | (c) Rule Curve: |  | 107.6
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-10-17
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 115 | 200 | 42 | 0 | 0 | 352 |  | 0 | 420 | 265 | 16 | 80 | 55 | 0 | 0 | 182 | 0 | 7 | 7 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 86 | 35 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 17 | 0 | 97 | 44 | 20 | 40 | 0 | 80 | 0 | 310 | 300 | 212 | 45 | 87 | 29 | 40 | 0 | 51 | 0 | 0 | 52 | 19 | 11 | 33 | 21 | 138 | 157 | 48 | 20 | 0 | 85 | 43 | 50 | 47 | 110 | 166 | 65 | 87 | 0 | 0 | 0 | 0 | 10 | 290 | 24 | 8 | 0 | 285 | 0 | 0 | 192 | 0 | 149 | 0 | 78 | 120 | 10 | 420 | 110 | 87 | 0 | 0 | 162 | 36 | 0 | 17 | 110 | 100 | 0 | 81 |  | 918 | 0 | 380 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 0 | 0 | 70 | 20 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 219 | 0 | 90 | 100 | 185 | 0 | 390 | 17 | 0 | 113 | 0 | 101 | 0 | 0 | 109 | 580 |  | 7519 | 3873 | 11392 | 4000 | 918 | 2134 | 2982 | 730 | 121 | 369 | 138 | 0 | 0 | 102.19
2:00 | 0 | 0 | 0 | 115 | 200 | 42 | 0 | 0 | 352 |  | 0 | 370 | 275 | 16 | 80 | 55 | 0 | 0 | 183 | 0 | 7 | 7 | 64 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 86 | 35 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 89 | 19 | 20 | 42 | 0 | 80 | 0 | 300 | 300 | 212 | 45 | 86 | 29 | 40 | 0 | 51 | 0 | 0 | 52 | 19 | 11 | 33 | 21 | 134 | 157 | 48 | 20 | 0 | 85 | 43 | 50 | 47 | 110 | 166 | 65 | 87 | 0 | 0 | 0 | 0 | 10 | 270 | 24 | 8 | 0 | 285 | 0 | 0 | 200 | 0 | 149 | 0 | 78 | 70 | 10 | 421 | 105 | 52 | 0 | 0 | 162 | 36 | 0 | 17 | 110 | 100 | 0 | 72 |  | 918 | 0 | 380 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 110 | 0 | 0 | 0 | 0 | 0 | 70 | 20 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 | 0 | 92 | 50 | 185 | 0 | 389 | 17 | 0 | 70 | 0 | 98 | 0 | 0 | 109 | 580 |  | 7270 | 3768 | 11038 | 3992 | 918 | 2066 | 2753 | 730 | 121 | 324 | 134 | 0 | 0 | 102.19
3:00 | 0 | 0 | 0 | 115 | 200 | 42 | 0 | 0 | 352 |  | 0 | 370 | 265 | 16 | 80 | 55 | 0 | 0 | 175 | 0 | 7 | 7 | 48 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 84 | 35 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 64 | 19 | 20 | 42 | 0 | 80 | 0 | 300 | 300 | 212 | 45 | 86 | 29 | 40 | 0 | 51 | 0 | 0 | 52 | 19 | 11 | 33 | 21 | 134 | 157 | 48 | 20 | 0 | 85 | 43 | 50 | 47 | 110 | 166 | 65 | 87 | 0 | 0 | 0 | 0 | 10 | 270 | 24 | 8 | 0 | 245 | 0 | 0 | 200 | 0 | 149 | 0 | 78 | 50 | 10 | 424 | 85 | 52 | 0 | 0 | 162 | 36 | 0 | 17 | 104 | 100 | 0 | 72 |  | 918 | 0 | 380 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 96 | 0 | 0 | 0 | 0 | 0 | 47 | 20 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 | 0 | 91 | 20 | 185 | 0 | 385 | 17 | 0 | 0 | 0 | 97 | 0 | 0 | 109 | 580 |  | 7108 | 3615 | 10723 | 3987 | 918 | 2061 | 2499 | 730 | 119 | 275 | 134 | 0 | 0 | 102.19
4:00 | 0 | 0 | 0 | 115 | 200 | 42 | 0 | 0 | 352 |  | 0 | 370 | 280 | 16 | 80 | 55 | 0 | 0 | 188 | 0 | 7 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 83 | 35 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 12 | 19 | 20 | 41 | 0 | 80 | 0 | 300 | 300 | 206 | 45 | 95 | 29 | 40 | 0 | 51 | 0 | 0 | 52 | 19 | 11 | 33 | 21 | 130 | 157 | 48 | 20 | 0 | 85 | 43 | 50 | 47 | 110 | 165 | 65 | 87 | 0 | 0 | 0 | 0 | 10 | 270 | 24 | 8 | 0 | 95 | 0 | 0 | 200 | 0 | 149 | 0 | 70 | 34 | 10 | 420 | 65 | 52 | 0 | 0 | 162 | 36 | 0 | 17 | 103 | 100 | 0 | 72 |  | 918 | 0 | 380 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 24 | 0 | 37 | 80 | 0 | 0 | 0 | 0 | 0 | 47 | 20 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 | 0 | 90 | 0 | 186 | 0 | 398 | 17 | 0 | 0 | 0 | 90 | 0 | 0 | 109 | 550 |  | 6849 | 3529 | 10378 | 3999 | 918 | 2072 | 2208 | 700 | 118 | 233 | 130 | 0 | 0 | 102.19
5:00 | 0 | 0 | 0 | 115 | 200 | 72 | 0 | 0 | 352 |  | 0 | 370 | 290 | 16 | 80 | 55 | 0 | 0 | 189 | 0 | 7 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 55 | 55 | 16 | 25 | 30 | 33 | 33 | 0 | 0 | 82 | 35 | 115 | 0 | 0 | 204 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 42 | 0 | 80 | 0 | 300 | 300 | 206 | 45 | 96 | 29 | 40 | 0 | 51 | 0 | 0 | 52 | 19 | 0 | 33 | 21 | 128 | 157 | 48 | 20 | 0 | 85 | 43 | 47 | 44 | 110 | 164 | 65 | 87 | 0 | 0 | 0 | 0 | 10 | 290 | 24 | 8 | 0 | 60 | 0 | 0 | 200 | 0 | 149 | 0 | 70 | 0 | 10 | 420 | 65 | 52 | 0 | 0 | 162 | 17 | 0 | 0 | 103 | 100 | 0 | 72 |  | 919 | 0 | 380 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 219 | 0 | 91 | 0 | 186 | 0 | 424 | 17 | 0 | 0 | 0 | 86 | 0 | 0 | 109 | 550 |  | 6757 | 3431 | 10188 | 3966 | 919 | 2144 | 2078 | 700 | 117 | 136 | 128 | 0 | 0 | 102.19
6:00 | 0 | 0 | 0 | 115 | 200 | 73 | 30 | 0 | 300 |  | 0 | 370 | 275 | 16 | 80 | 55 | 0 | 0 | 145 | 0 | 7 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 55 | 55 | 16 | 25 | 30 | 33 | 33 | 0 | 0 | 83 | 35 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 12 | 12 | 20 | 40 | 0 | 80 | 0 | 300 | 300 | 209 | 0 | 88 | 29 | 40 | 0 | 0 | 0 | 0 | 25 | 19 | 11 | 33 | 21 | 120 | 158 | 48 | 20 | 0 | 85 | 43 | 47 | 44 | 110 | 166 | 65 | 87 | 0 | 0 | 0 | 0 | 10 | 280 | 24 | 8 | 0 | 60 | 0 | 0 | 170 | 0 | 149 | 0 | 10 | 0 | 0 | 421 | 35 | 52 | 0 | 0 | 109 | 17 | 0 | 0 | 103 | 30 | 0 | 72 |  | 918 | 0 | 370 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 214 | 0 | 91 | 0 | 177 | 0 | 309 | 17 | 0 | 0 | 0 | 84 | 0 | 0 | 70 | 540 |  | 6337 | 3171 | 9508 | 3927 | 918 | 1895 | 1704 | 690 | 118 | 136 | 120 | 0 | 0 | 102.19
7:00 | 0 | 0 | 0 | 115 | 200 | 73 | 30 | 0 | 300 |  | 0 | 350 | 270 | 16 | 80 | 30 | 0 | 0 | 95 | 0 | 7 | 64 | 16 | 0 | 0 | 0 | 0 | 0 | 55 | 35 | 16 | 25 | 30 | 33 | 33 | 0 | 0 | 85 | 35 | 115 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 37 | 0 | 80 | 0 | 300 | 300 | 181 | 0 | 87 | 29 | 54 | 0 | 0 | 0 | 0 | 25 | 19 | 11 | 33 | 21 | 106 | 158 | 48 | 20 | 0 | 85 | 43 | 47 | 44 | 110 | 158 | 40 | 40 | 0 | 0 | 0 | 0 | 10 | 270 | 24 | 8 | 0 | 60 | 0 | 0 | 140 | 0 | 149 | 0 | 0 | 0 | 0 | 424 | 35 | 52 | 0 | 1 | 106 | 17 | 0 | 0 | 102 | 0 | 0 | 72 |  | 918 | 0 | 340 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 92 | 0 | 157 | 0 | 298 | 17 | 0 | 0 | 0 | 62 | 0 | 1 | 35 | 480 |  | 5986 | 2929 | 8915 | 3654 | 918 | 1812 | 1537 | 630 | 120 | 136 | 106 | 2 | 0 | 102.19
8:00 | 0 | 0 | 0 | 115 | 200 | 74 | 72 | 0 | 300 |  | 0 | 330 | 275 | 16 | 80 | 30 | 0 | 0 | 95 | 0 | 7 | 64 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 16 | 25 | 20 | 33 | 33 | 0 | 0 | 86 | 35 | 115 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 12 | 17 | 20 | 10 | 0 | 80 | 0 | 280 | 300 | 181 | 0 | 85 | 29 | 55 | 0 | 0 | 0 | 0 | 25 | 19 | 11 | 33 | 21 | 108 | 157 | 48 | 20 | 1 | 85 | 43 | 47 | 44 | 110 | 159 | 40 | 40 | 0 | 0 | 0 | 0 | 10 | 260 | 24 | 8 | 0 | 60 | 0 | 0 | 140 | 0 | 149 | 0 | 0 | 0 | 0 | 422 | 35 | 52 | 0 | 2 | 106 | 17 | 0 | 0 | 96 | 0 | 0 | 72 |  | 918 | 0 | 340 | 0 | 23 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 144 | 0 | 92 | 0 | 157 | 0 | 300 | 17 | 0 | 0 | 0 | 54 | 0 | 2 | 35 | 460 |  | 5948 | 2911 | 8859 | 3626 | 918 | 1799 | 1536 | 610 | 121 | 136 | 108 | 5 | 0 | 102.19
9:00 | 0 | 0 | 0 | 115 | 200 | 75 | 71 | 0 | 277 |  | 0 | 330 | 290 | 16 | 80 | 30 | 0 | 0 | 97 | 0 | 7 | 64 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 19 | 25 | 20 | 33 | 33 | 0 | 0 | 86 | 35 | 115 | 0 | 0 | 204 | 0 | 60 | 0 |  | 0 | 0 | 0 | 0 | 10 | 25 | 20 | 2 | 0 | 80 | 0 | 280 | 300 | 182 | 0 | 95 | 29 | 54 | 0 | 0 | 0 | 0 | 25 | 19 | 5 | 33 | 20 | 104 | 154 | 48 | 20 | 2 | 84 | 43 | 47 | 44 | 110 | 160 | 53 | 40 | 0 | 0 | 0 | 0 | 10 | 280 | 24 | 8 | 0 | 60 | 0 | 0 | 140 | 0 | 149 | 3 | 0 | 0 | 0 | 417 | 35 | 52 | 0 | 2 | 106 | 17 | 0 | 0 | 98 | 0 | 0 | 72 |  | 918 | 0 | 260 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 144 | 0 | 89 | 0 | 157 | 0 | 334 | 17 | 0 | 0 | 0 | 54 | 0 | 4 | 35 | 460 |  | 5929 | 2844 | 8773 | 3519 | 918 | 1818 | 1536 | 610 | 121 | 136 | 104 | 11 | 0 | 102.19
10:00 | 0 | 0 | 0 | 115 | 200 | 73 | 70 | 0 | 339 |  | 0 | 420 | 295 | 18 | 80 | 30 | 0 | 0 | 100 | 0 | 7 | 64 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 19 | 25 | 20 | 33 | 33 | 0 | 0 | 87 | 35 | 115 | 0 | 0 | 218 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 11 | 25 | 20 | 2 | 0 | 80 | 0 | 355 | 300 | 202 | 0 | 95 | 26 | 50 | 0 | 0 | 0 | 0 | 25 | 19 | 5 | 33 | 20 | 106 | 149 | 41 | 17 | 2 | 82 | 43 | 42 | 44 | 110 | 159 | 52 | 40 | 0 | 0 | 0 | 0 | 10 | 310 | 24 | 8 | 0 | 60 | 0 | 0 | 140 | 0 | 138 | 5 | 0 | 0 | 0 | 411 | 35 | 52 | 0 | 3 | 106 | 17 | 0 | 0 | 96 | 0 | 0 | 72 |  | 918 | 0 | 260 | 0 | 32 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 157 | 0 | 89 | 0 | 170 | 0 | 345 | 17 | 0 | 0 | 0 | 52 | 0 | 5 | 35 | 460 |  | 6124 | 2910 | 9034 | 3573 | 918 | 2000 | 1554 | 610 | 122 | 136 | 106 | 15 | 0 | 102.19
11:00 | 0 | 0 | 0 | 115 | 200 | 72 | 68 | 0 | 338 |  | 0 | 420 | 285 | 16 | 79 | 30 | 0 | 0 | 185 | 0 | 7 | 80 | 16 | 0 | 0 | 0 | 0 | 45 | 55 | 55 | 19 | 25 | 20 | 33 | 33 | 0 | 0 | 87 | 35 | 115 | 0 | 0 | 211 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 64 | 27 | 20 | 2 | 0 | 80 | 0 | 320 | 355 | 190 | 0 | 95 | 26 | 46 | 0 | 0 | 0 | 0 | 25 | 18 | 11 | 0 | 20 | 108 | 149 | 40 | 17 | 2 | 82 | 43 | 44 | 43 | 110 | 160 | 62 | 82 | 0 | 0 | 0 | 0 | 10 | 305 | 24 | 8 | 0 | 80 | 0 | 0 | 163 | 0 | 138 | 12 | 0 | 0 | 0 | 411 | 55 | 52 | 0 | 3 | 142 | 17 | 0 | 0 | 94 | 0 | 0 | 72 |  | 918 | 0 | 260 | 0 | 32 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 155 | 0 | 89 | 0 | 150 | 0 | 274 | 17 | 0 | 0 | 0 | 52 | 0 | 6 | 35 | 420 |  | 6471 | 2778 | 9249 | 3620 | 918 | 1959 | 1793 | 570 | 122 | 136 | 108 | 23 | 0 | 102.19
12:00 | 0 | 0 | 0 | 115 | 200 | 72 | 67 | 0 | 343 |  | 0 | 420 | 255 | 11 | 79 | 48 | 0 | 0 | 185 | 0 | 7 | 94 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 20 | 33 | 33 | 0 | 0 | 87 | 35 | 110 | 0 | 0 | 205 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 90 | 47 | 20 | 4 | 0 | 80 | 0 | 300 | 355 | 182 | 0 | 88 | 26 | 47 | 0 | 0 | 0 | 0 | 42 | 18 | 11 | 33 | 18 | 122 | 148 | 40 | 17 | 2 | 82 | 43 | 47 | 43 | 110 | 160 | 63 | 84 | 0 | 0 | 0 | 0 | 10 | 300 | 24 | 8 | 0 | 190 | 0 | 0 | 190 | 0 | 140 | 14 | 0 | 0 | 0 | 414 | 65 | 80 | 0 | 2 | 142 | 17 | 0 | 0 | 101 | 0 | 0 | 72 |  | 918 | 0 | 320 | 0 | 32 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 19 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 156 | 0 | 88 | 0 | 157 | 0 | 329 | 17 | 0 | 0 | 0 | 52 | 0 | 6 | 35 | 460 |  | 6833 | 2938 | 9771 | 3676 | 918 | 2018 | 2046 | 610 | 122 | 235 | 122 | 24 | 0 | 102.19
13:00 | 0 | 0 | 0 | 115 | 200 | 71 | 67 | 0 | 297 |  | 0 | 420 | 290 | 16 | 79 | 55 | 0 | 0 | 185 | 0 | 7 | 94 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 52 | 19 | 25 | 20 | 33 | 33 | 0 | 0 | 87 | 35 | 110 | 0 | 0 | 205 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 90 | 50 | 20 | 8 | 0 | 80 | 0 | 310 | 350 | 193 | 0 | 94 | 29 | 46 | 0 | 0 | 0 | 0 | 52 | 18 | 11 | 33 | 18 | 142 | 147 | 40 | 17 | 2 | 82 | 43 | 47 | 42 | 110 | 158 | 59 | 82 | 0 | 0 | 0 | 0 | 10 | 290 | 24 | 8 | 0 | 200 | 0 | 0 | 190 | 0 | 123 | 0 | 0 | 0 | 0 | 407 | 65 | 87 | 0 | 5 | 142 | 17 | 0 | 0 | 101 | 0 | 0 | 72 |  | 919 | 0 | 395 | 0 | 32 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 19 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 205 | 0 | 86 | 0 | 201 | 0 | 402 | 17 | 0 | 0 | 0 | 53 | 0 | 6 | 50 | 460 |  | 6853 | 3196 | 10049 | 3855 | 919 | 2034 | 2119 | 610 | 122 | 235 | 142 | 13 | 10049 | 102.19
14:00 | 0 | 0 | 0 | 115 | 200 | 72 | 66 | 0 | 286 |  | 0 | 420 | 280 | 16 | 79 | 55 | 0 | 0 | 175 | 0 | 7 | 94 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 52 | 19 | 25 | 19 | 33 | 33 | 0 | 0 | 87 | 35 | 110 | 0 | 0 | 204 | 0 | 0 | 145 |  | 0 | 0 | 51 | 0 | 90 | 50 | 20 | 2 | 0 | 80 | 0 | 300 | 355 | 180 | 8 | 89 | 29 | 47 | 0 | 0 | 0 | 0 | 52 | 18 | 11 | 0 | 20 | 142 | 147 | 40 | 17 | 2 | 81 | 43 | 47 | 39 | 110 | 158 | 62 | 82 | 0 | 0 | 0 | 0 | 10 | 300 | 8 | 8 | 0 | 200 | 0 | 0 | 190 | 0 | 129 | 17 | 22 | 0 | 0 | 411 | 65 | 86 | 0 | 3 | 142 | 17 | 0 | 0 | 100 | 60 | 0 | 70 |  | 919 | 0 | 400 | 0 | 32 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 19 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 186 | 0 | 86 | 0 | 197 | 0 | 381 | 17 | 0 | 0 | 0 | 53 | 0 | 5 | 90 | 460 |  | 7010 | 3196 | 10206 | 3761 | 919 | 2012 | 2233 | 610 | 122 | 380 | 142 | 27 | 0 | 102.19
15:00 | 0 | 0 | 0 | 115 | 200 | 70 | 65 | 0 | 284 |  | 0 | 420 | 265 | 9 | 79 | 55 | 0 | 0 | 173 | 0 | 7 | 94 | 64 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 25 | 20 | 33 | 33 | 0 | 0 | 82 | 35 | 110 | 0 | 0 | 204 | 0 | 0 | 144 |  | 0 | 0 | 68 | 0 | 90 | 50 | 20 | 2 | 0 | 80 | 0 | 300 | 350 | 180 | 8 | 90 | 29 | 43 | 0 | 0 | 0 | 0 | 52 | 18 | 11 | 26 | 20 | 148 | 148 | 40 | 17 | 1 | 82 | 43 | 47 | 39 | 110 | 159 | 50 | 83 | 0 | 20 | 0 | 0 | 10 | 300 | 24 | 8 | 0 | 200 | 75 | 50 | 189 | 26 | 140 | 11 | 22 | 0 | 2 | 407 | 86 | 86 | 0 | 0 | 160 | 20 | 0 | 0 | 101 | 77 | 0 | 38 |  | 919 | 0 | 395 | 0 | 42 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 19 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 189 | 0 | 86 | 0 | 194 | 0 | 399 | 17 | 0 | 0 | 0 | 67 | 0 | 4 | 109 | 500 |  | 7205 | 3306 | 10511 | 3800 | 919 | 2021 | 2444 | 650 | 117 | 396 | 148 | 16 | 0 | 102.19
16:00 | 0 | 0 | 0 | 115 | 200 | 70 | 66 | 0 | 289 |  | 0 | 420 | 245 | 13 | 86 | 55 | 0 | 0 | 173 | 0 | 7 | 94 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 20 | 8 | 33 | 0 | 0 | 82 | 35 | 110 | 0 | 0 | 204 | 0 | 10 | 0 |  | 0 | 0 | 68 | 0 | 90 | 50 | 20 | 2 | 0 | 80 | 0 | 300 | 355 | 180 | 8 | 85 | 29 | 45 | 0 | 1 | 0 | 0 | 16 | 18 | 11 | 33 | 20 | 140 | 150 | 40 | 17 | 1 | 82 | 43 | 47 | 42 | 110 | 140 | 50 | 83 | 0 | 80 | 0 | 0 | 10 | 265 | 24 | 8 | 0 | 215 | 0 | 0 | 200 | 0 | 133 | 4 | 22 | 0 | 60 | 413 | 45 | 86 | 0 | 0 | 160 | 39 | 0 | 0 | 101 | 76 | 0 | 34 |  | 919 | 0 | 400 | 0 | 42 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 19 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 177 | 0 | 86 | 0 | 186 | 0 | 378 | 17 | 0 | 0 | 0 | 95 | 0 | 3 | 109 | 500 |  | 6938 | 3299 | 10237 | 3826 | 919 | 1979 | 2346 | 650 | 117 | 252 | 140 | 8 | 0 | 102.19
17:00 | 0 | 0 | 0 | 115 | 200 | 71 | 40 | 0 | 290 |  | 0 | 420 | 235 | 16 | 67 | 40 | 0 | 0 | 105 | 0 | 7 | 58 | 84 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 19 | 25 | 20 | 17 | 33 | 0 | 0 | 82 | 35 | 110 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 68 | 0 | 96 | 50 | 20 | 4 | 0 | 80 | 0 | 300 | 360 | 180 | 8 | 86 | 29 | 47 | 0 | 14 | 0 | 0 | 16 | 18 | 11 | 33 | 20 | 140 | 150 | 24 | 17 | 0 | 83 | 43 | 16 | 10 | 110 | 139 | 65 | 85 | 0 | 81 | 0 | 0 | 10 | 260 | 24 | 8 | 0 | 230 | 0 | 0 | 170 | 0 | 120 | 1 | 22 | 0 | 103 | 413 | 45 | 68 | 0 | 0 | 125 | 53 | 0 | 0 | 101 | 76 | 0 | 34 |  | 918 | 0 | 350 | 0 | 16 | 120 | 0 | 0 | 7 | 0 | 0 | 0 | 27 | 32 | 0 | 0 | 0 | 0 | 7 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 10 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 177 | 0 | 90 | 0 | 187 | 0 | 371 | 17 | 0 | 0 | 0 | 81 | 0 | 1 | 109 | 470 |  | 6749 | 3187 | 9936 | 3869 | 918 | 1903 | 2082 | 619 | 117 | 286 | 140 | 2 | 0 | 102.19
18:00 | 0 | 0 | 0 | 115 | 200 | 72 | 50 | 0 | 297 |  | 0 | 420 | 270 | 16 | 64 | 40 | 0 | 0 | 185 | 0 | 7 | 80 | 100 | 17 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 18 | 33 | 33 | 16 | 0 | 87 | 35 | 110 | 0 | 6 | 205 | 0 | 140 | 0 |  | 0 | 0 | 102 | 60 | 96 | 50 | 20 | 4 | 0 | 80 | 0 | 300 | 355 | 204 | 45 | 85 | 29 | 48 | 0 | 12 | 0 | 0 | 25 | 18 | 11 | 33 | 20 | 168 | 149 | 32 | 17 | 0 | 82 | 43 | 35 | 20 | 110 | 141 | 64 | 86 | 0 | 100 | 0 | 0 | 10 | 270 | 24 | 11 | 50 | 235 | 300 | 72 | 178 | 0 | 138 | 0 | 22 | 13 | 115 | 376 | 64 | 86 | 0 | 0 | 161 | 54 | 0 | 0 | 100 | 100 | 0 | 34 |  | 919 | 0 | 370 | 0 | 98 | 140 | 0 | 0 | 18 | 10 | 40 | 0 | 37 | 110 | 0 | 0 | 0 | 27 | 10 | 27 | 20 | 0 | 32 | 35 | 32 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 170 | 0 | 91 | 19 | 177 | 0 | 361 | 53 | 165 | 21 | 0 | 81 | 0 | 0 | 109 | 580 |  | 7864 | 3944 | 11808 | 3976 | 919 | 1999 | 3396 | 730 | 122 | 498 | 168 | 0 | 0 | 102.19
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 115 | 200 | 72 | 67 | 0 | 273 |  | 0 | 420 | 275 | 16 | 80 | 55 | 0 | 0 | 150 | 0 | 7 | 94 | 133 | 74 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 87 | 35 | 115 | 0 | 25 | 205 | 0 | 140 | 0 |  | 0 | 0 | 102 | 100 | 96 | 50 | 20 | 12 | 0 | 80 | 0 | 270 | 300 | 180 | 8 | 87 | 29 | 49 | 0 | 9 | 0 | 42 | 52 | 18 | 11 | 33 | 20 | 170 | 152 | 32 | 17 | 0 | 84 | 43 | 44 | 40 | 110 | 139 | 63 | 86 | 0 | 80 | 0 | 0 | 10 | 260 | 24 | 11 | 50 | 300 | 170 | 95 | 200 | 0 | 149 | 0 | 22 | 102 | 127 | 413 | 115 | 86 | 0 | 0 | 161 | 54 | 0 | 7 | 101 | 100 | 0 | 34 |  | 919 | 0 | 385 | 0 | 115 | 200 | 0 | 0 | 21 | 0 | 40 | 0 | 37 | 110 | 0 | 0 | 0 | 50 | 42 | 95 | 20 | 0 | 36 | 52 | 31 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 173 | 0 | 91 | 100 | 220 | 0 | 408 | 53 | 50 | 105 | 0 | 98 | 0 | 0 | 109 | 600 |  | 8195 | 4352 | 12547 | 3931 | 919 | 2027 | 3876 | 750 | 122 | 752 | 170 | 0 | 0 | 102.19
19:30 | 0 | 0 | 0 | 115 | 200 | 72 | 67 | 0 | 274 |  | 0 | 420 | 285 | 16 | 80 | 55 | 0 | 0 | 150 | 0 | 7 | 94 | 150 | 74 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 88 | 35 | 115 | 0 | 25 | 204 | 0 | 140 | 0 |  | 0 | 0 | 102 | 100 | 96 | 50 | 20 | 6 | 0 | 80 | 0 | 260 | 300 | 189 | 8 | 95 | 29 | 50 | 0 | 9 | 0 | 42 | 52 | 18 | 11 | 33 | 20 | 166 | 151 | 32 | 17 | 0 | 82 | 43 | 50 | 42 | 110 | 144 | 63 | 86 | 0 | 80 | 0 | 0 | 10 | 300 | 24 | 11 | 50 | 300 | 120 | 95 | 192 | 0 | 149 | 0 | 22 | 155 | 127 | 416 | 115 | 86 | 0 | 0 | 178 | 54 | 0 | 17 | 101 | 100 | 0 | 34 |  | 919 | 0 | 365 | 0 | 115 | 210 | 0 | 0 | 24 | 0 | 40 | 0 | 37 | 110 | 0 | 0 | 0 | 50 | 42 | 95 | 20 | 0 | 38 | 52 | 31 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 173 | 0 | 91 | 100 | 215 | 0 | 413 | 53 | 25 | 113 | 0 | 89 | 0 | 0 | 109 | 600 |  | 8316 | 4321 | 12637 | 3917 | 919 | 2076 | 3902 | 750 | 123 | 784 | 166 | 0 | 0 | 102.19
20:00 | 0 | 0 | 0 | 115 | 200 | 72 | 67 | 0 | 263 |  | 0 | 420 | 270 | 16 | 85 | 55 | 0 | 0 | 150 | 0 | 7 | 94 | 150 | 75 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 88 | 35 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 102 | 100 | 96 | 50 | 20 | 8 | 0 | 80 | 0 | 260 | 300 | 197 | 8 | 86 | 29 | 51 | 0 | 12 | 0 | 40 | 52 | 19 | 11 | 33 | 20 | 152 | 152 | 32 | 17 | 0 | 83 | 43 | 50 | 44 | 110 | 139 | 63 | 86 | 0 | 80 | 0 | 0 | 10 | 290 | 24 | 11 | 50 | 300 | 120 | 95 | 200 | 0 | 149 | 0 | 22 | 162 | 127 | 417 | 115 | 86 | 0 | 0 | 178 | 54 | 0 | 17 | 100 | 100 | 0 | 34 |  | 919 | 0 | 360 | 0 | 115 | 215 | 0 | 0 | 23 | 0 | 40 | 0 | 36 | 110 | 0 | 0 | 0 | 50 | 42 | 95 | 20 | 0 | 44 | 52 | 31 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 173 | 0 | 91 | 100 | 213 | 0 | 394 | 53 | 25 | 113 | 0 | 90 | 0 | 0 | 109 | 600 |  | 8289 | 4305 | 12594 | 3907 | 919 | 2043 | 3908 | 750 | 123 | 792 | 152 | 0 | 0 | 102.19
21:00 | 0 | 0 | 0 | 115 | 200 | 72 | 67 | 0 | 258 |  | 0 | 420 | 290 | 37 | 97 | 55 | 0 | 0 | 150 | 0 | 7 | 94 | 150 | 75 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 89 | 35 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 102 | 100 | 96 | 50 | 20 | 20 | 0 | 80 | 0 | 270 | 300 | 197 | 8 | 95 | 29 | 50 | 0 | 35 | 0 | 41 | 52 | 19 | 11 | 33 | 20 | 152 | 152 | 40 | 17 | 0 | 82 | 43 | 50 | 44 | 110 | 147 | 63 | 86 | 0 | 80 | 0 | 0 | 10 | 290 | 24 | 11 | 25 | 300 | 30 | 31 | 200 | 0 | 149 | 0 | 22 | 164 | 128 | 414 | 115 | 86 | 0 | 0 | 179 | 54 | 0 | 17 | 101 | 100 | 0 | 35 |  | 918 | 0 | 355 | 0 | 115 | 215 | 0 | 0 | 19 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 42 | 95 | 20 | 0 | 36 | 52 | 31 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 173 | 0 | 90 | 100 | 208 | 0 | 409 | 53 | 0 | 113 | 0 | 88 | 0 | 0 | 109 | 600 |  | 8231 | 4271 | 12502 | 3920 | 918 | 2088 | 3769 | 750 | 124 | 781 | 152 | 0 | 0 | 102.19
22:00 | 0 | 0 | 0 | 115 | 200 | 72 | 68 | 0 | 246 |  | 0 | 420 | 270 | 50 | 97 | 40 | 0 | 0 | 150 | 0 | 7 | 94 | 150 | 74 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 89 | 35 | 115 | 0 | 25 | 204 | 0 | 138 | 0 |  | 0 | 0 | 102 | 100 | 97 | 50 | 20 | 31 | 0 | 80 | 0 | 260 | 300 | 194 | 8 | 90 | 29 | 51 | 0 | 35 | 0 | 41 | 52 | 19 | 11 | 33 | 20 | 150 | 153 | 41 | 17 | 0 | 83 | 43 | 50 | 41 | 110 | 139 | 61 | 87 | 0 | 80 | 0 | 0 | 10 | 300 | 24 | 11 | 25 | 300 | 0 | 17 | 200 | 0 | 149 | 0 | 22 | 164 | 128 | 418 | 115 | 86 | 0 | 0 | 180 | 54 | 0 | 17 | 100 | 100 | 0 | 35 |  | 919 | 0 | 345 | 0 | 115 | 215 | 0 | 0 | 23 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 42 | 95 | 20 | 0 | 36 | 52 | 31 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 177 | 0 | 93 | 100 | 203 | 0 | 404 | 53 | 0 | 113 | 0 | 88 | 0 | 0 | 109 | 600 |  | 8150 | 4263 | 12413 | 3886 | 919 | 2095 | 3704 | 750 | 124 | 785 | 150 | 0 | 0 | 102.17
23:00 | 0 | 0 | 0 | 115 | 200 | 72 | 68 | 0 | 243 |  | 0 | 420 | 275 | 50 | 97 | 40 | 0 | 0 | 155 | 0 | 7 | 94 | 150 | 75 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 88 | 35 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 102 | 60 | 97 | 50 | 20 | 34 | 0 | 80 | 0 | 275 | 300 | 196 | 8 | 95 | 29 | 51 | 0 | 35 | 0 | 41 | 52 | 19 | 11 | 33 | 20 | 154 | 154 | 41 | 17 | 0 | 84 | 43 | 50 | 41 | 110 | 142 | 63 | 87 | 0 | 80 | 0 | 0 | 10 | 285 | 24 | 11 | 0 | 300 | 0 | 21 | 200 | 0 | 149 | 0 | 22 | 164 | 135 | 419 | 115 | 86 | 0 | 0 | 180 | 54 | 0 | 17 | 100 | 100 | 0 | 35 |  | 919 | 0 | 345 | 0 | 115 | 215 | 0 | 0 | 23 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 42 | 95 | 20 | 0 | 36 | 52 | 29 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 176 | 0 | 93 | 100 | 201 | 0 | 409 | 53 | 0 | 113 | 0 | 93 | 0 | 0 | 109 | 600 |  | 8126 | 4269 | 12395 | 3919 | 919 | 2086 | 3661 | 750 | 123 | 783 | 154 | 0 | 0 | 102.16
24:00 | 0 | 0 | 0 | 115 | 200 | 72 | 68 | 0 | 260 |  | 0 | 420 | 270 | 50 | 97 | 40 | 0 | 0 | 150 | 0 | 7 | 94 | 150 | 75 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 88 | 35 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 102 | 30 | 97 | 50 | 20 | 33 | 0 | 80 | 0 | 275 | 300 | 192 | 8 | 88 | 29 | 51 | 0 | 35 | 0 | 41 | 52 | 19 | 11 | 33 | 21 | 146 | 155 | 40 | 17 | 0 | 85 | 43 | 50 | 44 | 110 | 140 | 63 | 87 | 0 | 140 | 0 | 0 | 10 | 295 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 22 | 164 | 135 | 420 | 115 | 86 | 0 | 0 | 180 | 25 | 0 | 17 | 100 | 100 | 0 | 35 |  | 919 | 0 | 335 | 0 | 115 | 215 | 0 | 0 | 17 | 0 | 40 | 0 | 39 | 110 | 0 | 0 | 0 | 50 | 0 | 95 | 20 | 0 | 36 | 52 | 30 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 183 | 0 | 91 | 100 | 199 | 0 | 400 | 53 | 0 | 113 | 0 | 90 | 0 | 0 | 109 | 600 |  | 8107 | 4204 | 12311 | 3960 | 919 | 2105 | 3572 | 750 | 123 | 736 | 146 | 0 | 0 | 102.16
KWH | 0 | 0 | 43000 | 2677500 | 4784864 | 1567136 | 1165024 | 0 | 7239000 |  | 0 | 8983500 | 6693585 | 516480 | 1994424 | 1131984 | 0 | 0 | 4025000 | 0 | 193920 | 1631952 | 1764480 | 481208 | 0 | 0 | 0 | 828360 | 1170807 | 1201182 | 436464 | 600000 | 586980 | 763600 | 787300 | 321648 | 0 | 1995071 | 840000 | 2700000 | 0 | 162284 | 4889647 | 0 | 2246999 | 186801 |  | 0 | 0 | 1069560 | 503040 | 1632000 | 895200 | 443568 | 457920 | 0 | 1929525 | 0 | 7445600 | 7723000 | 4747000 | 368000 | 2171640 | 669888 | 1132320 | 0 | 475651 | 0 | 231112 | 1033860 | 435888 | 237060 | 732100 | 496890 | 3242880 | 3588080 | 964800 | 402660 | 14600 | 1987000 | 1020480 | 1096800 | 1004688 | 2636427 | 3442000 | 1427904 | 1892160 | 0 | 752890 | 0 | 0 | 242100 | 7035352 | 529248 | 213000 | 192192 | 4779816 | 648344 | 358894 | 4399200 | 31590 | 3462910 | 76680 | 630720 | 1270080 | 1137455 | 9999000 | 1897200 | 1723080 | 0 | 22920 | 3577964 | 792111 | 0 | 166440 | 2441880 | 1529280 | 0 | 1391040 |  | 22036363 | 0 | 8612352 | 0 | 992640 | 3789120 | 0 | 0 | 147410 | 12544 | 424500 | 0 | 752925 | 1522560 | 0 | 0 | 0 | 296512 | 211427 | 808000 | 491950 | 0 | 218092 | 365280 | 209338 | 488640 | 234828 | 232974 | 0 | 0 | 3666400 | 0 | 0 | 0 | 0 | 4649409 | 0 | 2159985 | 840960 | 4715618 | 0 | 8995091 | 681600 | 187972 | 943968 | 0 | 1870080 | 0 | 41395 | 2058816 | 12888800 |  | 171462887 | 85547549 | 257010436 | 93146128 | 22036363 | 47927547 | 62167256 | 16555200 | 2835071 | 8944396 | 3242880 | 155595 | 0
Fuel Cost | 0 | 0 | 62780 | 3935925 | 5311199.04 | 2068619.52 | 1980540.8 | 0 | 7456170 |  | 0 | 9792015 | 7429879.35 | 3920083.2 | 13741581.36 | 9576584.64 | 0 | 0 | 6963250 | 0 | 1460217.6 | 14883402.24 | 17362483.2 | 4436737.76 | 0 | 0 | 0 | 6047028 | 9050338.11 | 11843654.52 | 327348 | 450000 | 0 | 0 | 0 | 3110336.16 | 0 | 538669.17 | 226800 | 4887000 | 0 | 1507618.36 | 5329715.23 | 0 | 3819898.3 | 3801400.35 |  | 0 | 0 | 10374732 | 4804032 | 14198400 | 7089984 | 558895.68 | 1360022.4 | 0 | 2855697 | 0 | 5509744 | 7723000 | 4367240 | 474720 | 2497386 | 756973.44 | 1585248 | 0 | 813363.21 | 0 | 2334231.2 | 9873363 | 553577.76 | 177795 | 1281175 | 372667.5 | 24321600 | 3803364.8 | 8760384 | 511378.2 | 232724 | 3258680 | 1632768 | 1952304 | 1567313.28 | 3005526.78 | 3579680 | 2812970.88 | 3614025.6 | 0 | 1302499.7 | 0 | 0 | 493884 | 7105705.52 | 396936 | 161880 | 3269185.92 | 36135408.96 | 11008881.12 | 6000707.68 | 22875840 | 528184.8 | 34075034.4 | 896389.2 | 5140368 | 13780368 | 8019057.75 | 9299070 | 17302464 | 16283106 | 0 | 0 | 27049407.84 | 6899286.81 | 0 | 1661071.2 | 20926911.6 | 10185004.8 | 0 | 0 |  | 126929450.88 | 0 | 9042969.6 | 0 | 7802150.4 | 52517203.2 | 0 | 0 | 1546330.9 | 131461.12 | 4423290 | 0 | 1167033.75 | 14860185.6 | 0 | 0 | 0 | 2917678.08 | 2148098.32 | 7150800 | 3788015 | 0 | 2113311.48 | 3539563.2 | 2030578.6 | 938188.8 | 363983.4 | 176361.318 | 0 | 0 | 19871888 | 0 | 0 | 0 | 0 | 6137219.88 | 0 | 3239977.5 | 14304729.6 | 5517273.06 | 0 | 8905140.09 | 7115904 | 3197403.72 | 8958256.32 | 0 | 14511820.8 | 0 | 457414.75 | 15214650.24 | 56581832 |  | 560732894.94 | 407600163.608 | 968333058.548 | 105374318.388 | 126929450.88 | 57883781.65 | 470589882.06 | 76453720 | 765469.17 | 104428308.45 | 24321600 | 1586527.95 | 0
Yesterday Day Peak | 0 | 0 | 0 | 115 | 200 | 72 | 67 | 0 | 343 |  | 0 | 420 | 255 | 11 | 79 | 48 | 0 | 0 | 185 | 0 | 7 | 94 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 20 | 33 | 33 | 0 | 0 | 87 | 35 | 110 | 0 | 0 | 205 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 90 | 47 | 20 | 4 | 0 | 80 | 0 | 300 | 355 | 182 | 0 | 88 | 26 | 47 | 0 | 0 | 0 | 0 | 42 | 18 | 11 | 33 | 18 | 122 | 148 | 40 | 17 | 2 | 82 | 43 | 47 | 43 | 110 | 160 | 63 | 84 | 0 | 0 | 0 | 0 | 10 | 300 | 24 | 8 | 0 | 190 | 0 | 0 | 190 | 0 | 140 | 14 | 0 | 0 | 0 | 414 | 65 | 80 | 0 | 2 | 142 | 17 | 0 | 0 | 101 | 0 | 0 | 72 |  | 918 | 0 | 320 | 0 | 32 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 19 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 156 | 0 | 88 | 0 | 157 | 0 | 329 | 17 | 0 | 0 | 0 | 52 | 0 | 6 | 35 | 460 |  | 9771 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 115 | 200 | 72 | 67 | 0 | 274 | 0 | 0 | 420 | 285 | 16 | 80 | 55 | 0 | 0 | 150 | 0 | 7 | 94 | 150 | 74 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 88 | 35 | 115 | 0 | 25 | 204 | 0 | 140 | 0 | 0 | 0 | 0 | 102 | 100 | 96 | 50 | 20 | 6 | 0 | 80 | 0 | 260 | 300 | 189 | 8 | 95 | 29 | 50 | 0 | 9 | 0 | 42 | 52 | 18 | 11 | 33 | 20 | 166 | 151 | 32 | 17 | 0 | 82 | 43 | 50 | 42 | 110 | 144 | 63 | 86 | 0 | 80 | 0 | 0 | 10 | 300 | 24 | 11 | 50 | 300 | 120 | 95 | 192 | 0 | 149 | 0 | 22 | 155 | 127 | 416 | 115 | 86 | 0 | 0 | 178 | 54 | 0 | 17 | 101 | 100 | 0 | 34 |  | 919 | 0 | 365 | 0 | 115 | 210 | 0 | 0 | 24 | 0 | 40 | 0 | 37 | 110 | 0 | 0 | 0 | 50 | 42 | 95 | 20 | 0 | 38 | 52 | 31 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 173 | 0 | 91 | 100 | 215 | 0 | 413 | 53 | 25 | 113 | 0 | 89 | 0 | 0 | 109 | 600 |  | 12637 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 115 | 200 | 72 | 65 | 0 | 360 | 0 | 0 | 450 | 305 | 16 | 100 | 55 | 0 | 0 | 150 | 0 | 100 | 94 | 150 | 74 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 88 | 35 | 120 | 0 | 25 | 221 | 0 | 145 | 0 | 0 | 0 |  | 102 | 100 | 97 | 50 | 21 | 10 | 0 | 80 | 0 | 360 | 350 | 225 | 8 | 95 | 30 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 10 | 33 | 21 | 173 | 160 | 49 | 20 | 0 | 85 | 43 | 51 | 44 | 110 | 160 | 65 | 86 | 0 | 150 | 0 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 85 | 100 | 0 | 300 | 54 | 110 | 17 | 113 | 100 | 0 | 104 |  | 928 | 16 | 410 | 0 | 115 | 220 | 0 | 0 | 30 | 60 | 40 | 0 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 20 | 0 | 50 | 52 | 30 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 225 | 0 | 92 | 100 | 220 | 0 | 414 | 35 | 200 | 113 | 100 | 94 | 0 | 0 | 113 | 600
Forecast for Day | 0 | 0 | 0 | 115 | 200 | 72 | 65 | 0 | 360 | 0 | 0 | 450 | 305 | 16 | 100 | 55 | 0 | 0 | 100 | 0 | 100 | 94 | 150 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 88 | 35 | 120 | 0 | 25 | 221 | 0 | 145 | 0 | 0 | 0 |  | 102 | 100 | 97 | 50 | 21 | 10 | 0 | 80 | 0 | 360 | 350 | 225 | 8 | 95 | 30 | 55 | 0 | 51 | 0 | 25 | 25 | 22 | 10 | 33 | 21 | 165 | 160 | 49 | 20 | 1.6 | 85 | 43 | 51 | 44 | 110 | 160 | 65 | 86 | 0 | 150 | 0 | 0 | 10 | 341 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 200 | 150 | 400 | 115 | 85 | 100 | 5 | 300 | 54 | 110 | 0 | 113 | 100 | 0 | 104 |  | 928 | 0 | 410 | 0 | 115 | 220 | 0 | 0 | 0 | 0 | 40 | 0 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 20 | 0 | 50 | 52 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 225 |  | 92 | 50 | 220 | 0 | 414 | 35 | 100 | 113 | 100 | 94 | 0 | 8 | 113 | 580
Generation at 08:00(Today) | 0 | 0 | 0 | 115 | 200 | 72 | 40 | 0 | 282 | 0 | 0 | 330 | 275 |  | 65 | 40 | 0 | 0 | 85 | 0 | 100 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 84 | 35 | 115 | 0 | 0 | 204 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 12 | 20 | 2 | 0 | 80 | 0 | 275 | 300 | 183 | 8 | 94 | 29 | 52 | 0 | 43 | 0 | 0 | 0 | 15 | 11 | 33 | 21 | 92 | 154 | 32 | 20 | 1 | 84 | 43 | 14 | 10 | 110 | 142 | 40 | 40 | 0 | 140 | 0 | 0 | 0 | 290 | 8 | 8 | 0 | 17 | 0 | 0 | 150 | 0 | 149 | 9 | 22 | 0 | 75 | 424 | 8 | 34 | 0 | 0 | 52 | 17 | 0 | 0 | 75 | 70 | 0 | 35 | 0 | 919 | 0 | 290 | 0 | 5 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 24 | 0 | 150 | 0 | 390 | 17 | 0 | 0 | 0 | 33 | 0 | 2 | 35 | 520 | 0
199
| Minimum Generation |  | 8773 | 9:00
| Highest Generation |  | 12637 | 19:30
| Day Peak Generation |  | 9771 | 12:00
| Evening Peak Generation |  | 12637 | 19:30
| HVDC Max Flow |  | 919 | 5:00
| HVDC EvPeak Flow |  | 919 | 19:30
| Load factor L.F |  | 84.74%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-10-18
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-10-17 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9771 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 8928 | MW
Evening Peak Generation : |  | 12637 | MW Hour : | 19:30 | Available Max Generation : |  | 14804 | MW
E.P. Demand (at gen end) : |  | 12637 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 13000 | MW
Maximum Generation : |  | 12637 | MW Hour : | 19:30 | Reserve(Generation end) |  | 1804 | MW
Total Gen. (MKWH) : |  | 257.0104 | System Load Factor : | 84.74% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 76 | MW at | 3:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-10-18
Actual : | 102.16 | Ft.(MSL) , | Rule curve : | 107.6 | Ft.( MSL )
Gas Consumed : | Total = | 1177.35 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 163258100.038
: |  | Coal : | 76453720 | Oil : | 575018190.51 | Total : | 814730010.548
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4599.7147 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1568.883 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1406.5091 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1271.1986 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1148.5989 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 926.8906 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 512.1908 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 238.4885 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 714.8931 |  |  | 0 | 0%
Total | 0 |  | 12387.3673 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Baghabari-71 MW,100 MW
3) Ghorasal Unit-1,2,3
4) Ashuganj unit-3,4
5) Kaptai-2,4
6) Raozan #2
7) Siddirganj-335 MW
8) Haripur 412 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Kaptai-Chandraghona 132 kV Ckt-2 was under shut down from 09:52 to 16:03 for A/M.
b) Rangamati-Khagrachari 132 kV Ckt-2 was under shut down from 08:30 to 14:23 for C/M.
c) Mymensing-Mymensing Solar 50 MW 132 kV Ckt was shut down at 10:50 for test.
d) Saidpur 132/33 kV T5 transformer was under shut down from 08:30 to 16:01 for A/M.
e) Lalmonirhat 132/33 kV T3 transformer was under shut down from 08:20 to 17:05 for A/M.
f) Polashbari 132/33 kV T1 transformer was under shut down from 08:05 to 15:21 for A/M.
g) Jaldhaka 132/33 kV T1 transformer was under shut down from 08:45 to 16:18 for A/M.
h) Sirajganj 132/33 kV T3 transformer was under shut down from 09:24 to 17:35 for A/M.
i) B.Baria 132/33 kV T2 transformer was under shut down from 09:52 to 11:30 for C/M.
j) Agargaon 230/132 kV T2 transformer was under shut down from 08:09 to 11:30 for C/M.
k) Ghorasal-Ishwardi 230 kV Cjkt-1 tripped at 09:58 from both end showing Dist. T-phase relays at
Ishwardi end & DST,PD-3 at Ghorasal end and was switched on at 11:42.
l) Mirpur-Uttara 132 kV Ckt tripped at 10:36 showing Dist. R-phase relays at Mirpur end and was |  |  |  |  | About 80 MW power interruption occurred under Mirpur S/S area
switched on at 10:40. |  |  |  |  | from 10:36 to 10:40.
m) Natore 132/33 kV T3 transformer was switched on at 13:34.
n) Goalpara 132/33 kV T5 transformer was under shut down from 14:06 to 16:47 for A/M.
o) Tangail 132/33 kV T4 transformer was under shut down from 14:34 to 16:48 due to 33 kV Bus-4 PT
maintenance.
p) Baraulia-Hathazari 132 kV Ckt-1 & 2 were shut down at 06:12(18/10/2020) for C/M.
q) Tongi 132/33 kV T1 transformer was shut down from 06:12(18/10/2020) to 07:14(18/10/2020)
for C/M.
r) Comilla(N)-Chuddagram132 kV Ckt-1 & 2 tripped at 05:41(18/10/2020) showing Dist. AB ,Z1 relays
at Comilla(N) end & 21 trip, 3-phase,67N relay at Chauddagram end and were switched on at 06:22,
06:35(18/10/2020) respectively.
s) Barisal-Bhola P/S 230 kV Ckt-1 tripped at 05:55(18/10/2020) showing Dist. Z1 relay at Barisal end
& general trip relay at Bhola P/P end and was switched on at 06:32(18/10/2020).
t) Feni-Chauddagram 132 kV Ckt-2 tripped at 02:55(18/10/2020) showing SOTF,AR fail relay at Feni end
& protection, Lockout,61,67N relay at Chauddagram end and was switched on at 03:35(18/10/2020).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-10-17 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 43000 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 115 | 2677500 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 4784864 | Machin problem.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 67 | 1165024
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 72 | 1567136 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 274 | 7239000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 8983500 | Frequency control.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 16 | 516480 | Fuel Shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 285 | 6693585 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 80 | 1994424 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1131984
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 74 | 481208 | Low demand
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 436464
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 150 | 4025000
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 7 | 193920 | Fuel Shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under Maintenance
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 94 | 1631952 | Fuel Shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel Shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 828360
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1764480
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1170807
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1201182
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1186980 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 763600
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 787300
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 321648
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 4779816
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 120 | 648344 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 95 | 358894
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 31590 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3462910
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 86 | 1723080 | Engine problem
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 34 | 1391040 | Low demand
| Dhaka area Total |  |  |  | 5895 | 3201 | 63985072
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 115 | 2700000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | S/D due to gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 162284
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 76680
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 895200
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 123 | 2835071 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4889647
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 140 | 2433800
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Transformer overload
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 1069560
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 503040
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 22 | 630720 | Machin problem.
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 443568
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 6 | 457920
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 96 | 1632000 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 22920
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 178 | 3577964 | Transformer O/L.
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 792111
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1529280
| Chattogram area Total |  |  |  | 2266 | 1335 | 24651765
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 80 | 1929525 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 189 | 4747000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 260 | 7445600 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 300 | 7723000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 669888 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 50 | 1132320
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 368000 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 9 | 475651
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 127 | 1137455
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 42 | 231112
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 95 | 2171640
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 155 | 1270080 | Low demand
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 435888
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 237060
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 166 | 3242880
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 732100
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 1033860
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 496890
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 50 | 192192 | Low demand
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 166440 | Fuel Shortage
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 101 | 2441880
| Cumilla Area Total |  |  |  | 2980 | 1812 | 38280461
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 151 | 3588080 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 402660 | Engine problem
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 32 | 964800 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14600
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 192 | 4399200
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1897200 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 507 | 11266540
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 82 | 1987000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 1020480 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2636427 | Engine problem
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 144 | 3442000 | FGMO & GT-2 under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1096800
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 42 | 1004688
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 213000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 63 | 1427904 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1892160
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 80 | 752890 | Machin problem.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 529248
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7035352 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 416 | 9999000
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 242100
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1461 | 33279049
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 919 | 22036363
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 992640
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 24 | 147410
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 210 | 3789120
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 12544 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 365 | 8612352
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 424500
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 840960
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 681600 | Fuel Shortage
107 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Line O/L.
| Khulna Area Total |  |  |  | 2284 | 1826 | 37537489
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1522560
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 37 | 752925
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 91 | 2159985
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 600 | 12888800
| Barisal Area Total |  |  |  | 1054 | 838 | 17324270
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 296512
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 42 | 211427
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 20 | 491950 | Engine problem
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel Shortage
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 218092
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas Shortage
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 173 | 4649409 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 215 | 4715618 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 413 | 8995091 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 31 | 209338
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 488640
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 10 | 234828
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 232974
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 365280
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 95 | 808000
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 25 | 187972 | Line O/L.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 943968
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 2058816
| Rajshahi Area Total |  |  |  | 2183 | 1418 | 25107915
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3666400 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 89 | 1870080 | Engine problem
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 41395
| Rangpur Area Total |  |  |  | 605 | 239 | 5577875
| Total |  |  |  | 19892 | 12637 | 257010436
| Eastern Grid Total |  |  |  | 13766 | 8316 | 171462887
| Western Grid Total |  |  |  | 6126 | 4321 | 85547549
| National Grid Total |  |  |  | 19892 | 12637 | 257010436
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-10-17
| (a) ENTIRE EASTERN GRID : |  | 8067 | MW | (b) ENTIRE WESTERN GRID : |  | 3964 | MW
| i) Dhaka area |  | 4203 | MW | i) Khulna area |  | 1536 | MW
| ii) Chittagong area |  | 1127 | MW | ii) Rajshahi area |  | 1290 | MW
| iii) Comilla area |  | 1243 | MW | iii) Barisal area |  | 371 | MW
| iv) Mymensingh area |  | 945 | MW | iv) Rangpur area |  | 767 | MW
| v) Sylhet area |  | 549 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 12031 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 120 | 18:30 | Sherpur | 112 | 21:00 | Jhenida | 109 | 21:00
| Munsiganj | 126 | 21:00 | Srimongal | 57 | 18:00 | Bottail | 130 | 18:30
| Sonargaon | 72 | 18:00 | Shahjibazar | 123 | 20:00 | G.K Project | 57 | 19:30
| Shyampur | 194 | 24:00 | Fenchuganj | 46 | 18:00 | Faridpur | 194 | 0.83333
| Bhulta | 193 | 23:00 | Kulawara | 50 | 19:00 | Madaripur | 100 | 0.83333
| Madanganj | 56 | 22:00 | Sylhet | 151 | 18:00 | Sariatpur | 70 | 22:00
| Shitalakhya | 121 | 15:00 | Chatak | 32 | 21:00 | Gopalganj | 99 | 19:30
| Rahim steel | 20 | 15:00 | Sunamganj | 51 | 21:00 | Bagerhat | 106 | 22:00
| Matuail | 75 | 11:00 | Biani Bazar | 64 | 18:00 | Mongla | 32 | 15:00
| Ghorasal | 89 | 19:00 | Comilla (S) | 170 | 19:00 | Satkhira | 114 | 0.91667
| Narsingdi | 174 | 21:00 | Comilla(N) | 139 | 21:00 | Gallamari | 51 | 23:00
| Haripur (SBU) | 99 | 17:00 | Chandpur | 109 | 22:00 | Magura | 54 | 0.77083
| Ullon | 64 | 18:00 | Feni | 128 | 21:00 | Norail | 42 | 19:30
| Hasnabad | 217 | 19:30 | Chowmuhani | 188 | 19:00 | Chuadanga | 92 | 19:00
| Magbazar | 95 | 15:00 | Ashuganj | 61 | 23:00 | Barisal(N) | 54 | 0.91667
| Maniknagar | 90 | 18:00 | Daudkandi | 150 | 22:00 | Barisal (S) | 106 | 0.83333
| Bangabhaban | 20 | 11:00 | B.Baria | 168 | 20:00 | Patuakhali | 128 | 0.875
| Narinda | 88 | 18:00 | Ramganj | 122 | 22:00 | Bhandaria | 60 | 0.83333
| Dhanmondi | 161 | 13:00 | Chaddagram | 41 | 18:30 | Borhan Uddin | 44 | 22:00
| Lalbag | 86 | 13:00 | PHP | 9 | 17:00 | Ishurdi | 64 | 18:30
| Madartek | 76 | 23:00 | Madunaghat | 59 | 19:30 | Ruppur Paromanobik | 2 | 1:00
| Dhaka University |  |  | Hathazari | 97 | 0.91667 | Natore | 123 | 21:00
| Fatullah | 40 | 0.75 | Khulshi | 209 | 0.75 | Bogra | 169 | 19:30
| Mirpur | 116 | 18:00 | Halishahar | 145 | 0.625 | Noagaon | 117 | 19:30
| Kalyanpur | 111 | 18:00 | Baraulia | 142 | 0 | Rajshahi | 152 | 20:00
| Gulshan | 116 | 18:00 | Sikalbaha | 29 | 0.75 | Rajshahi New | 12 | 19:30
| Uttara | 103 | 18:00 | Dohazari | 92 | 0.79167 | C.Nawabganj | 75 | 20:00
| Uttara New | 41 | 18:00 | Cox'sbazar | 105 | 0.83333 | Amnura | 46 | 20:00
| Kamrangirchar | 101 | 18:00 | Chandraghona | 30 | 0.875 | Pabna | 136 | 19:00
| Savar | 143 | 18:00 | Kaptai | 4.5 | 0.75 | Shahjadpur | 100 | 19:30
| Bhasantec | 149 | 18:00 | A. Khaer Stl. | 12 | 0.125 | Serajganj | 107 | 19:00
| Agargaon | 68 | 18:00 | Bakulia | 125 | 0.625 | Niyamatpur | 56 | 20:00
| Satmosjid | 90 | 18:00 | Julda | 18 | 0.041667 | Joypurhat | 59 | 20:00
| Tongi | 100 | 0.77083 | TK chemical | 26.8 | 0.041667 | Sherpur(Bogura) | 50 | 18:30
| Kabirpur | 226 | 21:00 | Modern Steel | 15 | 0.5 | Mohastangor | 50 | 20:00
| Basundhara | 149 | 15:00 | Shahmirpur | 23 | 0.625 | Rangpur | 140 | 19:00
| Manikganj | 72 | 21:00 | Khagrachhari | 24 | 0.66667 | Lalmonirhat | 56 | 18:30
| Joydevpur | 170 | 18:30 | Matarbari | 37.5 | 0.83333 | Saidpur | 106 | 18:30
| New Tongi | 108 | 15:00 | Baroiar Hat | 48 | 0.75 | Purbasadipur | 101 | 19:00
| Kodda | 228 | 21:00 | Rangamati | 12 | 0.75 | Thakurgaon | 81 | 20:00
| Dhamrai | 96 | 20:00 | Abul Khair 230 | 19 | 0.5 | Palashbari | 121 | 21:00
| Rajendrapur | 96 | 18:00 | BSRM | 110 | 0.083333 | Barapukuria | 52 | 21:00
| Valuka | 130 | 19:00 | GPH Ispat | 78 | 0.75 | Panchagar | 50 | 19:00
| Tangail | 203 | 19:00 | Goalpara | 30 | 0.95833 | Joldhaka | 33 | 18:30
| Mymensing | 184 | 1:00 | Central s/s | 93 | 20:00 | Kurigram | 57 | 18:30
| Kishorganj | 153 | 18:30 | Noapara | 64 | 18:30
| Netrokona | 109 | 21:00 | Jessore | 111 | 18:30
| Jamalpur | 141 | 22:00 | Benapol | 52 | 19:00
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-10-17 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 406 | 6:00 | 397 | 21:00 | Kaliakoir | 401 | 0.25 | 388 | 0.77083
| Bheramara | 392 | 8:00 | 385 | 19:00 | Bhulta | 374 | 0.29167 | 358 | 0.70833
| Ashuganj(N) | 381 | 2:00 | 367 | 10:00 | Gopalganj | 411 | 0.33333 | 381 | 0.75
| Payra | 415 | 7:00 | 402 | 18:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 225 | 14:00 | Comilla (N) | 230 | 5:00 | 224 | 11:00
| Ishurdi | 237 | 12:00 | 223 | 20:00 | Hathazari | 223 | 14:00 | 219 | 9:00
| Ashuganj | 232 | 1:00 | 224 | 10:00 | Megnaghat | 223 | 8:00 | 216 | 17:00
| Serajganj | 231 | 5:00 | 225 | 10:00 | Fenchuganj | 240 | 6:00 | 234 | 20:00
| Baghabari | 238 | 7:00 | 233 | 22:00 | Siddhirganj | 224 | 6:00 | 214 | 17:00
| Barapukuria | 238 | 6:00 | 227 | 19:00 | Maniknagar | 222 | 7:00 | 212 | 16:00
| Bogra | 225 | 8:00 | 215 | 19:30 | Agargaon | 219 | 8:00 | 208 | 10:00
| Rajshahi | 225 | 7:00 | 216 | 19:30 | Barisal | 250 | 12:00 | 229 | 21:00
| Khulna South | 228 | 8:00 | 217 | 5:00 | AKSML | 219 | 3:00 | 214 | 10:00
| Rampura | 223 | 5:00 | 215 | 10:00 | BSRM | 221 | 18:30 | 215 | 10:00
| Haripur | 220 | 3:00 | 213 | 10:00 | Bibiyana | 240 | 2:00 | 234 | 17:00
| Hasnabad | 221 | 18:00 | 214 | 10:00 | Bhulta | 224 | 19:00 | 214 | 17:00
| Shyampur | 219 | 7:00 | 209 | 17:00 | Ashuganj (S) | 229 | 3:00 | 221 | 17:00
| Aminbazar | 217 | 1:00 | 209 | 17:00 | Kaliakoir | 221 | 3:00 | 211 | 10:00
| Tongi | 215 | 1:00 | 205 | 10:00 | GPH | 219 | 3:00 | 212 | 10:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 133 | 3:00 | 128 | 12:00 | Hathazari | 133 | 0.5 | 131 | 0.16667
| Munsiganj | 133 | 1:00 | 126 | 17:00 | Khulshi | 132 | 0.83333 | 125 | 0.375
| Sonargaon | 132 | 3:00 | 127 | 16:00 | Halishahar | 134 | 0.91667 | 124 | 0.41667
| Shyampur | 135 | 7:00 | 128 | 10:00 | Baraulia | 132 | 0.083333 | 128 | 0.41667
| Bhulta | 127 | 5:00 | 120 | 17:00 | Sikalbaha | 135 | 19:00 | 127 | 0.41667
| Madanganj | 136 | 5:00 | 127 | 17:00 | Dohazari | 132 | 12:00 | 126 | 0.41667
| Shitalakhya | 142 | 18:30 | 129 | 17:00 | Cox'sbazar | 127 | 0.5 | 118 | 0.041667
| Rahim steal | 133 | 4:00 | 127 | 17:00 | Chandraghona | 133 | 0.041667 | 129 | 0.41667
| Matuail | 133 | 3:00 | 128 | 12:00 | Kaptai | 132 | 1:00 | 132 | 0.041667
| Ghorasal | 138 | 7:00 | 132 | 11:00 | A. Khaer Stl. | 131 | 0.041667 | 128 | 10:00
| Narsinghdi | 125 | 16:00 | 120 | 21:00 | Bakulia | 134 | 0.91667 | 126 | 0.41667
| Haripur (SBU) | 134 | 3:00 | 128 | 13:00 | Julda | 135 | 0.79167 | 130 | 0.041667
| Ullon | 136 | 5:00 | 129 | 10:00 | TK Chemical | 134 | 0.83333 | 131 | 3:00
| Hasnabad | 137 | 7:00 | 128 | 17:00 | Modern Steel | 133 | 0.91667 | 127 | 0.41667
| Magbazar | 136 | 4:00 | 129 | 17:00 | Shahmirpur | 135 | 0.91667 | 127 | 0.41667
| Maniknagar | 133 | 4:00 | 129 | 2:00 | Khagrachhari | 132 | 0.66667 | 128 | 0.41667
| Bangabhaban | 133 | 4:00 | 129 | 2:00 | Matarbari | 128 | 0.45833 | 120 | 0.041667
| Narinda | 133 | 4:00 | 129 | 2:00 | Baroiar Hat | 130 | 0.29167 | 126 | 0.75
| Dhanmondi | 136 | 5:00 | 129 | 10:00 | Rangamati | 132 | 0.083333 | 128 | 10:00
| Lalbag | 137 | 7:00 | 125 | 17:00 | Goalpara S/S | 137 | 8:00 | 131 | 1:00
| Madartek | 136 | 6:00 | 129 | 10:00 | Khulna Central S/S | 137 | 0.29167 | 132 | 3:00
| Dhaka University |  |  |  |  | Noapara | 135 | 8:00 | 129 | 5:00
| Fatuiiah | 135 | 0.25 | 128 | 10:00 | Jessore | 131 | 8:00 | 122 | 20:00
| Mirpur | 134 | 6:00 | 126 | 12:00 | Benapol | 132 | 8:00 | 121 | 20:00
| Kalyanpur | 135 | 6:00 | 127 | 12:00 | Jhenida | 129 | 0.33333 | 115 | 19:30
| Gulshan | 136 | 6:00 | 129 | 12:00 | Bottail | 134 | 5:00 | 126 | 19:00
| Uttara | 134 | 6:00 | 124 | 12:00 | G.K Project | 141 | 0.33333 | 135 | 21:00
| Uttara New | 133 | 6:00 | 125 | 12:00 | Faridpur | 133 | 11:00 | 125 | 21:00
| Kamrangirchar | 133 | 6:00 | 127 | 12:00 | Madaripur | 138 | 0.33333 | 129 | 21:00
| Savar | 134 | 6:00 | 126 | 12:00 | Shariyatpur S/S | 136 | 0.20833 | 124 | 18:00
| Bhasantec | 135 | 6:00 | 128 | 12:00 | Gopalganj | 137 | 5:00 | 123 | 18:00
| Agargaon | 137 | 6:00 | 126 | 11:00 | Bagerhat | 135 | 8:00 | 125 | 20:00
| Satmosjid | 136 | 6:00 | 125 | 10:00 | Mongla | 132 | 0.70833 | 123 | 1:00
| Tongi | 131 | 0.041667 | 126 | 10:00 | Satkhira | 137 | 0.45833 | 129 | 20:00
| Kabirpur | 129 | 5:00 | 118 | 12:00 | Gallamari | 138 | 11:00 | 132 | 5:00
| Basundhara | 136 | 6:00 | 129 | 13:00 | Magura | 129 | 8:00 | 112 | 19:30
| Manikganj | 132 | 14:00 | 127 | 10:00 | Norail | 128 | 0.41667 | 112 | 19:30
| Joydevpur | 139 | 18:30 | 128 | 10:00 | Chuadanga | 123 | 7:00 | 103 | 21:00
| New Tongi | 132 | 0.16667 | 125 | 10:00 | Barisal(N) | 140 | 5:00 | 129 | 21:00
| Kodda | 137 | 22:00 | 127 | 0.41667 | Barisal (S) | 139 | 0.20833 | 128 | 15:00
| Dhamrai | 128 | 24:00 | 119 | 18:30 | Patuakhali(S) | 135 | 0.33333 | 121 | 21:00
| Rajendrapur | 137 | 18:30 | 124 | 11:00 | Bhandaria | 132 | 17:00 | 117 | 20:00
| Valuka | 124 | 8:00 | 107 | 19:00 | Ishurdi | 137 | 6:00 | 132 | 19:00
| Tangail | 127 | 8:00 | 115 | 18:00 | Ruppur Paromanobik | 137 | 17:00 | 132 | 19:30
| Mymensing | 129 | 8:00 | 113 | 19:00 | Natore | 136 | 7:00 | 130 | 19:00
| Kishorganj | 127 | 8:00 | 116 | 18:30 | Bogra | 135 | 8:00 | 128 | 19:30
| Netrokona | 126 | 5:00 | 109 | 21:00 | Noagaon | 131 | 7:00 | 121 | 19:30
| Jamalpur | 138 | 9:00 | 125 | 22:00 | Rajshahi | 136 | 7:00 | 130 | 19:30
| Sherpur | 137 | 9:00 | 125 | 22:00 | Rajshahi New | 137 | 8:00 | 131 | 14:00
| Srimongal | 135 | 7:00 | 131 | 0.75 | C.Nawabganj | 134 | 7:00 | 129 | 19:30
| Shahjibazar | 133 | 6:00 | 128 | 0.041667 | Amnura | 136 | 8:00 | 128 | 20:00
| Fenchuganj | 135 | 8:00 | 128 | 0.041667 | Pabna | 135 | 6:00 | 128 | 20:00
| Khulawara | 134 | 9:00 | 128 | 0.041667 | Shahjadpur | 139 | 5:00 | 135 | 11:00
| Sylhet | 131 | 8:00 | 124 | 0.041667 | Serajganj | 133 | 6:00 | 127 | 19:00
| Chatak | 128 | 7:00 | 119 | 1:00 | Niyamatpur | 131 | 7:00 | 118 | 20:00
| Sunamganj | 127 | 7:00 | 115 | 0.041667 | Joypurhat | 134 | 8:00 | 117 | 20:00
| Biani Bazar | 130 | 7:00 | 121 | 0.041667 | Sherpur(Bogura) | 135 | 6:00 | 127 | 20:00
| Comilla(s) | 128 | 6:00 | 120 | 18:00 | Mohastangor | 135 | 7:00 | 125 | 19:30
| Comilla(n) | 135 | 7:00 | 130 | 17:00 | Rangpur | 131 | 7:00 | 116 | 19:30
| Chandpur | 132 | 23:00 | 128 | 18:30 | Lalmonirhat | 130 | 6:00 | 115 | 19:30
| Feni | 130 | 14:00 | 125 | 18:00 | Saidpur | 132 | 5:00 | 116 | 20:00
| Chowmuhani | 130 | 8:00 | 123 | 23:00 | Purbasadipur | 130 | 7:00 | 113 | 20:00
| Ashuganj | 133 | 8:00 | 127 | 23:00 | Thakurgaon | 128 | 6:00 | 110 | 20:00
| Daudkandi | 132 | 7:00 | 126 | 13:00 | Palashbari | 131 | 7:00 | 120 | 18:30
| B.Baria | 130 | 7:00 | 123 | 22:00 | Barapukuria | 138 | 6:00 | 127 | 19:00
| Ramganj | 128 | 9:00 | 118 | 18:30 | Panchagar | 127 | 6:00 | 108 | 20:00
| Chaddagram | 133 | 9:00 | 128 | 19:30 | Joldhaka | 132 | 6:00 | 113 | 20:00
| PHP | 131 | 9:00 | 125 | 6:00 | Kurigram | 130 | 6:00 | 114 | 19:30
| Madanhat | 135 | 18:00 | 130 | 11:00

## L-Curve
Date | 2020-10-17
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 215 | 8107 | 4204 | 12311 |  |  |  | QF-LDC-11
0:30 | 161.5 | 7813 | 4038.5 | 11851.5 | Date: | 2020-10-17
1:00 | 108 | 7519 | 3873 | 11392
1:30 | 109 | 7394.5 | 3820.5 | 11215
2:00 | 110 | 7270 | 3768 | 11038
2:30 | 93 | 7189 | 3691.5 | 10880.5 | [5 empty] | Gen. at Eve. Peak | 12637 | 9500 MW (19:30 )
3:00 | 76 | 7108 | 3615 | 10723 | [6 empty] | 19:30
3:30 | 103 | 6978.5 | 3572 | 10550.5 | [5 empty] | Gen. at Day Peak | 9771 | 7952.5 MW (12:00 )
4:00 | 130 | 6849 | 3529 | 10378 | [6 empty] | 12:00
4:30 | 150.5 | 6803 | 3480 | 10283 | [5 empty] | Highest Generation | 12637
5:00 | 171 | 6757 | 3431 | 10188 | [6 empty] | 19:30
5:30 | 212 | 6547 | 3301 | 9848
6:00 | 253 | 6337 | 3171 | 9508
6:30 | 236.5 | 6161.5 | 3050 | 9211.5
7:00 | 220 | 5986 | 2929 | 8915
7:30 | 247 | 5967 | 2920 | 8887
8:00 | 274 | 5948 | 2911 | 8859
8:30 | 320 | 5938.5 | 2877.5 | 8816
9:00 | 366 | 5929 | 2844 | 8773
9:30 | 418 | 6026.5 | 2877 | 8903.5
10:00 | 470 | 6124 | 2910 | 9034
10:30 | 335 | 6297.5 | 2844 | 9141.5
11:00 | 200 | 6471 | 2778 | 9249
11:30 | 257.5 | 6652 | 2858 | 9510
12:00 | 315 | 6833 | 2938 | 9771
12:30 | 335 | 6843 | 3067 | 9910
13:00 | 355 | 6853 | 3196 | 10049
13:30 | 332.5 | 6931.5 | 3196 | 10127.5
14:00 | 310 | 7010 | 3196 | 10206
14:30 | 325 | 7107.5 | 3251 | 10358.5
15:00 | 340 | 7205 | 3306 | 10511
15:30 | 361 | 7071.5 | 3302.5 | 10374
16:00 | 382 | 6938 | 3299 | 10237
16:30 | 410 | 6843.5 | 3243 | 10086.5
17:00 | 438 | 6749 | 3187 | 9936
17:30 | 327.5 | 7306.5 | 3565.5 | 10872
18:00 | 217 | 7864 | 3944 | 11808
18:30 | 197.5 | 8029.5 | 4148 | 12177.5
19:00 | 178 | 8195 | 4352 | 12547
19:30 | 140 | 8316 | 4321 | 12637
20:00 | 92 | 8289 | 4305 | 12594 |  |  |  | Executive Engineer
20:30 | 116 | 8260 | 4288 | 12548 |  |  |  | Network Operation Division
21:00 | 140 | 8231 | 4271 | 12502
21:30 | 144 | 8190.5 | 4267 | 12457.5
22:00 | 148 | 8150 | 4263 | 12413 |  |  |  |  | Page 6 of 7
22:30 | 166 | 8138 | 4266 | 12404
23:00 | 184 | 8126 | 4269 | 12395
23:30 | 199.5 | 8116.5 | 4236.5 | 12353
24:00 | 215 | 8107 | 4204 | 12311
9500 MW (19:30 )
7952.5 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-10-17 |  | Energy | 257010436
[10 empty] | 2020-10-17 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3960 | 919 | 2105 | 3661 | 750 | 123 | 736 | 0 | 146
0:30 | 3980 | 918.5 | 2119.5 | 3321.5 | 740 | 122 | 552.5 | 0 | 142 | Date: | 2020-10-17
1:00 | 4000 | 918 | 2134 | 2982 | 730 | 121 | 369 | 0 | 138
1:30 | 3996 | 918 | 2100 | 2867.5 | 730 | 121 | 346.5 | 0 | 136 | [7 empty] | Total Energy | 257.0104 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 3992 | 918 | 2066 | 2753 | 730 | 121 | 324 | 0 | 134 | [7 empty] | Energy not Served | 0
2:30 | 3989.5 | 918 | 2063.5 | 2626 | 730 | 120 | 299.5 | 0 | 134 | [7 empty] | Energy Requirement | 257.0104
3:00 | 3987 | 918 | 2061 | 2499 | 730 | 119 | 275 | 0 | 134
3:30 | 3993 | 918 | 2066.5 | 2353.5 | 715 | 118.5 | 254 | 0 | 132 | [6 empty] | Shortage
4:00 | 3999 | 918 | 2072 | 2208 | 700 | 118 | 233 | 0 | 130
4:30 | 3982.5 | 918.5 | 2108 | 2143 | 700 | 117.5 | 184.5 | 0 | 129
5:00 | 3966 | 919 | 2144 | 2078 | 700 | 117 | 136 | 0 | 128
5:30 | 3946.5 | 918.5 | 2019.5 | 1891 | 695 | 117.5 | 136 | 0 | 124
6:00 | 3927 | 918 | 1895 | 1704 | 690 | 118 | 136 | 0 | 120
6:30 | 3790.5 | 918 | 1853.5 | 1620.5 | 660 | 119 | 136 | 0 | 113 |  |  |  |  | Coal
7:00 | 3654 | 918 | 1812 | 1537 | 630 | 120 | 136 | 0 | 106
7:30 | 3640 | 918 | 1805.5 | 1536.5 | 620 | 120.5 | 136 | 0 | 107 |  |  |  | Oil |  |  |  | ,
8:00 | 3626 | 918 | 1799 | 1536 | 610 | 121 | 136 | 0 | 108
8:30 | 3572.5 | 918 | 1808.5 | 1536 | 610 | 121 | 136 | 0 | 106
9:00 | 3519 | 918 | 1818 | 1536 | 610 | 121 | 136 | 0 | 104
9:30 | 3546 | 918 | 1909 | 1545 | 610 | 121.5 | 136 | 0 | 105
10:00 | 3573 | 918 | 2000 | 1554 | 610 | 122 | 136 | 0 | 106
10:30 | 3596.5 | 918 | 1979.5 | 1673.5 | 590 | 122 | 136 | 0 | 107
11:00 | 3620 | 918 | 1959 | 1793 | 570 | 122 | 136 | 0 | 108
11:30 | 3648 | 918 | 1988.5 | 1919.5 | 590 | 122 | 185.5 | 0 | 115
12:00 | 3676 | 918 | 2018 | 2046 | 610 | 122 | 235 | 0 | 122
12:30 | 3765.5 | 918.5 | 2026 | 2082.5 | 610 | 122 | 235 | 0 | 132
13:00 | 3855 | 919 | 2034 | 2119 | 610 | 122 | 235 | 0 | 142
13:30 | 3855 | 919 | 2034 | 2119 | 610 | 122 | 235 | 0 | 142
14:00 | 3855 | 919 | 2034 | 2119 | 610 | 122 | 235 | 0 | 142
14:30 | 3827.5 | 919 | 2027.5 | 2281.5 | 630 | 119.5 | 315.5 | 0 | 145
15:00 | 3800 | 919 | 2021 | 2444 | 650 | 117 | 396 | 0 | 148
15:30 | 3813 | 919 | 2000 | 2395 | 650 | 117 | 324 | 0 | 144
16:00 | 3826 | 919 | 1979 | 2346 | 650 | 117 | 252 | 0 | 140
16:30 | 3847.5 | 918.5 | 1941 | 2214 | 634.5 | 117 | 269 | 0 | 140
17:00 | 3869 | 918 | 1903 | 2082 | 619 | 117 | 286 | 0 | 140
17:30 | 3922.5 | 918.5 | 1951 | 2739 | 674.5 | 119.5 | 392 | 0 | 154
18:00 | 3976 | 919 | 1999 | 3396 | 730 | 122 | 498 | 0 | 168
18:30 | 3953.5 | 919 | 2013 | 3636 | 740 | 122 | 625 | 0 | 169
19:00 | 3931 | 919 | 2027 | 3876 | 750 | 122 | 752 | 0 | 170
19:30 | 3917 | 919 | 2076 | 3902 | 750 | 123 | 784 | 0 | 166
20:00 | 3907 | 919 | 2043 | 3908 | 750 | 123 | 792 | 0 | 152
20:30 | 3913.5 | 918.5 | 2065.5 | 3838.5 | 750 | 123.5 | 786.5 | 0 | 152
21:00 | 3920 | 918 | 2088 | 3769 | 750 | 124 | 781 | 0 | 152
21:30 | 3903 | 918.5 | 2091.5 | 3736.5 | 750 | 124 | 783 | 0 | 151
22:00 | 3886 | 919 | 2095 | 3704 | 750 | 124 | 785 | 0 | 150
22:30 | 3902.5 | 919 | 2090.5 | 3682.5 | 750 | 123.5 | 784 | 0 | 152
23:00 | 3919 | 919 | 2086 | 3661 | 750 | 123 | 783 | 0 | 154
23:30 | 3939.5 | 919 | 2095.5 | 3661 | 750 | 123 | 759.5 | 0 | 150 | Max Temp. in Dhaka |  | 35.7° C
24:00 | 3960 | 919 | 2105 | 3661 | 750 | 123 | 736 | 0 | 146
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
Note on W13: Author:

## Generation
g | 2020-10-17
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 86 | 86 | 84 | 83 | 82 | 83 | 85 | 86 | 86 | 87 | 87 | 87 | 87 | 87 | 82 | 82 | 82 | 87 |  | 87 | 88 | 88 | 89 | 89 | 88 | 88 | 1995071
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 840000
3 | Chattogram TPP-1 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2700000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 6 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 162284
| Teknaf 20MW PP (Solartech) | [6 empty] | 0 | 0 | 3 | 5 | 12 | 14 |  | 17 | 11 | 4 | 1 | [9 empty] | 76680
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 218 | 211 | 205 | 205 | 204 | 204 | 204 | 204 | 205 |  | 205 | 204 | 204 | 204 | 204 | 204 | 204 | 4889647
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 139 | 139 | 139 | 139 | 140 | 139 | 104 | 104 | 60 | [6 empty] | 10 | 139 | 140 |  | 140 | 140 | 139 | 139 | 138 | 139 | 139 | 2246999
10 | Sikalbaha 150MW GTPP(Oil) | [13 empty] | 145 | 144 | [11 empty] | 186801
| Dohazari -Kalaish 100 MW Peaking | 17 | [10 empty] | 51 | 51 | 51 | 68 | 68 | 68 | 102 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 1069560
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [17 empty] | 50 |  | 50 | 50 | 50 | 25 | 25 |  |  | 192192
14 | Titas 50 MW Peaking PP | [19 empty] | 42 | 42 | 40 | 41 | 41 | 41 | 41 | 231112
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 182 | 183 | 175 | 188 | 189 | 145 | 95 | 95 | 97 | 100 | 185 | 185 | 185 | 175 | 173 | 173 | 105 | 185 |  | 150 | 150 | 150 | 150 | 150 | 155 | 150 | 4025000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 285 | 285 | 245 | 95 | 60 | 60 | 60 | 60 | 60 | 60 | 80 | 190 | 200 | 200 | 200 | 215 | 230 | 235 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 4779816
19 | Ashuganj 195MW PP (APSCL-United) | 45 | 45 | 45 | 45 | 45 | 0 | [7 empty] | 8 | 8 | 8 | 8 | 45 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 368000
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | [25 empty] | 0 | 43000
23 | Ghorasal TPP Unit-5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2677500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4784864
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1929525
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 26 | 26 | 26 | 29 | 29 | 29 | 29 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 669888
33 | Ashuganj 225 MW CCPP | 212 | 212 | 212 | 206 | 206 | 209 | 181 | 181 | 182 | 202 | 190 | 182 | 193 | 180 | 180 | 180 | 180 | 204 |  | 180 | 189 | 197 | 197 | 194 | 196 | 192 | 4747000
34 | Ashuganj 450 MW CCPP(South) | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 355 | 355 | 350 | 355 | 350 | 355 | 360 | 355 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7723000
| Ashuganj 450 MW CCPP(North) | 310 | 300 | 300 | 300 | 300 | 300 | 300 | 280 | 280 | 355 | 320 | 300 | 310 | 300 | 300 | 300 | 300 | 300 |  | 270 | 260 | 260 | 270 | 260 | 275 | 275 | 7445600
35 | Ashuganj 55 MW PP (Precision) | 40 | 40 | 40 | 40 | 40 | 40 | 54 | 55 | 54 | 50 | 46 | 47 | 46 | 47 | 43 | 45 | 47 | 48 |  | 49 | 50 | 51 | 50 | 51 | 51 | 51 | 1132320
36 | Chandpur 150 MW CCPP | 87 | 86 | 86 | 95 | 96 | 88 | 87 | 85 | 95 | 95 | 95 | 88 | 94 | 89 | 90 | 85 | 86 | 85 |  | 87 | 95 | 86 | 95 | 90 | 95 | 88 | 2171640
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 420 | 370 | 370 | 370 | 370 | 370 | 350 | 330 | 330 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 |  | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 8983500
41 | Haripur 360MW CCPP(HPL) | 352 | 352 | 352 | 352 | 352 | 300 | 300 | 300 | 277 | 339 | 338 | 343 | 297 | 286 | 284 | 289 | 290 | 297 |  | 273 | 274 | 263 | 258 | 246 | 243 | 260 | 7239000
42 | RPCL 210MW CCPP | 157 | 157 | 157 | 157 | 157 | 158 | 158 | 157 | 154 | 149 | 149 | 148 | 147 | 147 | 148 | 150 | 150 | 149 |  | 152 | 151 | 152 | 152 | 153 | 154 | 155 | 3588080
43
44 | Fenchugonj CCPP Phase-1 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 84 | 82 | 82 | 82 | 82 | 81 | 82 | 82 | 83 | 82 |  | 84 | 82 | 83 | 82 | 83 | 84 | 85 | 1987000
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1020480
46 | Shajibazar 330 MW CCPP | 166 | 166 | 166 | 165 | 164 | 166 | 158 | 159 | 160 | 159 | 160 | 160 | 158 | 158 | 159 | 140 | 139 | 141 |  | 139 | 144 | 139 | 147 | 139 | 142 | 140 | 3442000
47 | Shahjibazar GTPP Unit- 8 & 9 | 65 | 65 | 65 | 65 | 65 | 65 | 40 | 40 | 53 | 52 | 62 | 63 | 59 | 62 | 50 | 50 | 65 | 64 |  | 63 | 63 | 63 | 63 | 61 | 63 | 63 | 1427904
48 | Shahjibazar 86MW PP (Shahjibazar) | 87 | 87 | 87 | 87 | 87 | 87 | 40 | 40 | 40 | 40 | 82 | 84 | 82 | 82 | 83 | 83 | 85 | 86 |  | 86 | 86 | 86 | 86 | 87 | 87 | 87 | 1892160
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | [14 empty] | 20 | 80 | 81 | 100 |  | 80 | 80 | 80 | 80 | 80 | 80 | 140 | 752890
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 242100
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 213000
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 47 | 47 | 47 | 47 | 47 | 42 | 44 | 47 | 47 | 47 | 47 | 47 | 16 | 35 |  | 44 | 50 | 50 | 50 | 50 | 50 | 50 | 1096800
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 8 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 529248
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 270 | 270 | 270 | 290 | 280 | 270 | 260 | 280 | 310 | 305 | 300 | 290 | 300 | 300 | 265 | 260 | 270 |  | 260 | 300 | 290 | 290 | 300 | 285 | 295 | 7035352
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 55 | 55 | 52 | 52 | 55 | 55 | 17 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1201182
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 |  | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 443568
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 436464
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 402660
63 | Impoprt (Tripura) | 138 | 134 | 134 | 130 | 128 | 120 | 106 | 108 | 104 | 106 | 108 | 122 | 142 | 142 | 148 | 140 | 140 | 168 |  | 170 | 166 | 152 | 152 | 150 | 154 | 146 | 3242880
64 | Malancha, Ctg. EPZ (United) | 40 | 42 | 42 | 41 | 42 | 40 | 37 | 10 | 2 | 2 | 2 | 4 | 8 | 2 | 2 | 2 | 4 | 4 |  | 12 | 6 | 8 | 20 | 31 | 34 | 33 | 457920
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 435888
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 5 | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 237060
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 |  | 26 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 732100
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 18 | 18 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 496890
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 20 | 20 | 20 | 18 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 586980
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 8 | 17 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 763600
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 787300
73 | Ghorashal 108MW PP (Regent) | 42 | 42 | 42 | 42 | 72 | 73 | 73 | 74 | 75 | 73 | 72 | 72 | 71 | 72 | 70 | 70 | 71 | 72 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 1567136
| Feni Lanka Power | 17 | 17 | 17 | 17 | [15 empty] | 7 | 17 | 17 | 17 | 17 | 17 | 17 | 166440
| Chowmuhani 113 MW | 110 | 110 | 104 | 103 | 103 | 103 | 102 | 96 | 98 | 96 | 94 | 101 | 101 | 100 | 101 | 101 | 101 | 100 |  | 101 | 101 | 100 | 101 | 100 | 100 | 100 | 2441880
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 193920
78 | Gazipur 52 MW PP | [17 empty] | 16 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 321648
79 | Kodda 150MW PP | 82 | 64 | 48 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 64 | 64 | 64 | 64 | 64 | 84 | 100 |  | 133 | 150 | 150 | 150 | 150 | 150 | 150 | 1764480
80 | Jamalpur 95 MW PP(Powerpac) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 41 | 40 | 40 | 40 | 40 | 40 | 40 | 24 | 32 |  | 32 | 32 | 32 | 40 | 41 | 41 | 40 | 964800
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | 52 | 52 | 25 | 25 | 25 | 25 | 25 | 25 | 42 | 52 | 52 | 52 | 16 | 16 | 25 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1033860
| Gazipur 100 MW PP | 87 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 80 | 87 | 86 | 86 | 86 | 68 | 86 |  | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 1723080
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 2 | 3 | 3 | 2 | 5 | 3 | 0 | 0 | [10 empty] | 22920
| Jodiac Power | 36 | 36 | 36 | 36 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 39 | 53 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 25 | 792111
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 79 | 79 | 79 | 79 | 79 | 86 | 67 | 64 |  | 80 | 80 | 85 | 97 | 97 | 97 | 97 | 1994424
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [17 empty] | 17 |  | 74 | 74 | 75 | 75 | 74 | 75 | 75 | 481208
86 | Meghnaghat CCPP(Summit) | 265 | 275 | 265 | 280 | 290 | 275 | 270 | 275 | 290 | 295 | 285 | 255 | 290 | 280 | 265 | 245 | 235 | 270 |  | 275 | 285 | 270 | 290 | 270 | 275 | 270 | 6693585
87 | Meghnaghat 100 MW(IEL) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 18 | 16 | 11 | 16 | 16 | 9 | 13 | 16 | 16 |  | 16 | 16 | 16 | 37 | 50 | 50 | 50 | 516480
| Meghnaghat 104 MW PP (OPCL) | 81 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 70 | 38 | 34 | 34 | 34 |  | 34 | 34 | 34 | 35 | 35 | 35 | 35 | 1391040
88 | Ghorashal 78.5 MW PP(MAX) | [5 empty] | 30 | 30 | 72 | 71 | 70 | 68 | 67 | 67 | 66 | 65 | 66 | 40 | 50 |  | 67 | 67 | 67 | 67 | 68 | 68 | 68 | 1165024
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [17 empty] | 60 |  | 100 | 100 | 100 | 100 | 100 | 60 | 30 | 503040
92 | Fenchuganj 44MW (Energyprima) | 47 | 47 | 47 | 47 | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 43 | 42 | 39 | 39 | 42 | 10 | 20 |  | 40 | 42 | 44 | 44 | 41 | 41 | 44 | 1004688
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 0 | [9 empty] | 1 | 14 | 12 |  | 9 | 9 | 12 | 35 | 35 | 35 | 35 | 475651
94 | Gagnagar 102 MW PP (Digital Power) | 7 | 7 | 7 | 24 | 24 | 50 | 64 | 64 | 64 | 64 | 80 | 94 | 94 | 94 | 94 | 94 | 58 | 80 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 1631952
95 | Patenga 50MW PP (Baraka) | 44 | 19 | 19 | 19 | 12 | 12 | 12 | 17 | 25 | 25 | 27 | 47 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 895200
96 | Chattogram 108 MW PP (ECPV) | 97 | 89 | 64 | 12 | 12 | 12 | 12 | 12 | 10 | 11 | 64 | 90 | 90 | 90 | 90 | 90 | 96 | 96 |  | 96 | 96 | 96 | 96 | 97 | 97 | 97 | 1632000
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 30 | 30 | 30 | 30 | 30 | 48 | 55 | 55 | 55 | 55 | 40 | 40 |  | 55 | 55 | 55 | 55 | 40 | 40 | 40 | 1131984
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 55 | 55 | 55 | 55 | 35 | 55 | 17 | 35 |  | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 1170807
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2636427
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 14600
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 35 | 17 | [7 empty] | 45 | 54 | 54 | 54 | 54 | 54 | 17 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 828360
104 | Keranigonj 300 MW PP (APR) | [14 empty] | 75 |  |  | 300 |  | 170 | 120 | 120 | 30 |  |  | 0 | 648344
105 | Bramhangoan 100 MW PP (Aggreko) | [14 empty] | 50 |  |  | 72 |  | 95 | 95 | 95 | 31 | 17 | 21 | 0 | 358894
106 | Mymensingh 200 MW PP (United) | 192 | 200 | 200 | 200 | 200 | 170 | 140 | 140 | 140 | 140 | 163 | 190 | 190 | 190 | 189 | 200 | 170 | 178 |  | 200 | 192 | 200 | 200 | 200 | 200 | 200 | 4399200
112 | Aurahati 100MW PP (Aggreko) | [14 empty] | 26 | [10 empty] | 0 | 31590
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 138 | 138 | 140 | 123 | 129 | 140 | 133 | 120 | 138 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3462910
115 | Juldah 100 MW PP Unit-3 (Acorn) | 78 | 78 | 78 | 70 | 70 | 10 | [7 empty] | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 630720
116 | Chandpur 200MW (Desh energy) | 120 | 70 | 50 | 34 | [13 empty] | 13 |  | 102 | 155 | 162 | 164 | 164 | 164 | 164 | 1270080
117 | Ashuganj 150MW PP (Midland) | 10 | 10 | 10 | 10 | 10 | [9 empty] | 2 | 60 | 103 | 115 |  | 127 | 127 | 127 | 128 | 128 | 135 | 135 | 1137455
118 | Bibiyana-III 400 MW CCPP | 420 | 421 | 424 | 420 | 420 | 421 | 424 | 422 | 417 | 411 | 411 | 414 | 407 | 411 | 407 | 413 | 413 | 376 |  | 413 | 416 | 417 | 414 | 418 | 419 | 420 | 9999000
| Jamalpur 115 MW PP (United) | 110 | 105 | 85 | 65 | 65 | 35 | 35 | 35 | 35 | 35 | 55 | 65 | 65 | 65 | 86 | 45 | 45 | 64 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 1897200
| Anwara 300 MW PP (United) | 162 | 162 | 162 | 162 | 162 | 109 | 106 | 106 | 106 | 106 | 142 | 142 | 142 | 142 | 160 | 160 | 125 | 161 |  | 161 | 178 | 178 | 179 | 180 | 180 | 180 | 3577964
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 30 | [7 empty] | 60 | 77 | 76 | 76 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1529280
120 | Eastern Zone Total | 7519 | 7270 | 7108 | 6849 | 6757 | 6337 | 5986 | 5948 | 5929 | 6124 | 6471 | 6833 | 6853 | 7010 | 7205 | 6938 | 6749 | 7864 |  | 8195 | 8316 | 8289 | 8231 | 8150 | 8126 | 8107 | 171462887
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [7 empty] | 23 |  | 32 | 32 | 32 | 32 | 32 | 42 | 42 | 16 | 98 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 992640
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 7 | 18 |  | 21 | 24 | 23 | 19 | 23 | 23 | 17 | 147410
| Khulna 225 MW CCPP | 200 | 190 | 180 | 170 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 140 |  | 200 | 210 | 215 | 215 | 215 | 215 | 215 | 3789120
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 681600
130
131
132
133
| Barisal 110 MW PP (Summit ) | 110 | 110 | 96 | 80 | 80 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 32 | 32 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 1522560
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 90 | 92 | 91 | 90 | 91 | 91 | 92 | 92 | 89 | 89 | 89 | 88 | 86 | 86 | 86 | 86 | 90 | 91 |  | 91 | 91 | 91 | 90 | 93 | 93 | 91 | 2159985
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 38 | 37 | 37 | 37 | 37 | 32 | 25 | 24 | 24 | 25 | 26 | 25 | 27 | 27 | 26 | 28 | 27 | 37 |  | 37 | 37 | 36 | 38 | 38 | 38 | 39 | 752925
141 | Noapara 100 MW PP (Bangla Trac) | 100 | 50 | 20 | [14 empty] | 19 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 840960
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 40 | 24 | [13 empty] | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 424500
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 10 | [8 empty] | 12544
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 918 | 918 | 918 | 918 | 919 | 918 | 918 | 918 | 918 | 918 | 918 | 918 | 919 | 919 | 919 | 919 | 918 | 919 |  | 919 | 919 | 919 | 918 | 919 | 919 | 919 | 22036363
147 | Bheramara 410 MW CCPP | 380 | 380 | 380 | 380 | 380 | 370 | 340 | 340 | 260 | 260 | 260 | 320 | 395 | 400 | 395 | 400 | 350 | 370 |  | 385 | 365 | 360 | 355 | 345 | 345 | 335 | 8612352
148 | Payra 1320 MW | 580 | 580 | 580 | 550 | 550 | 540 | 480 | 460 | 460 | 460 | 420 | 460 | 460 | 460 | 500 | 500 | 470 | 580 |  | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 12888800
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3666400
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 27 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 296512
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 219 | 220 | 220 | 220 | 219 | 214 | 158 | 144 | 144 | 157 | 155 | 156 | 205 | 186 | 189 | 177 | 177 | 170 |  | 173 | 173 | 173 | 173 | 177 | 176 | 183 | 4649409
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 185 | 185 | 185 | 186 | 186 | 177 | 157 | 157 | 157 | 170 | 150 | 157 | 201 | 197 | 194 | 186 | 187 | 177 |  | 220 | 215 | 213 | 208 | 203 | 201 | 199 | 4715618
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 390 | 389 | 385 | 398 | 424 | 309 | 298 | 300 | 334 | 345 | 274 | 329 | 402 | 381 | 399 | 378 | 371 | 361 |  | 408 | 413 | 394 | 409 | 404 | 409 | 400 | 8995091
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 7 | 10 |  | 42 | 42 | 42 | 42 | 42 | 42 |  | 211427
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 20 | 19 | 19 | 19 | 19 | 19 | 20 | 21 |  | 21 | 21 | 21 | 21 | 21 | 22 | 22 | 488640
163 | Bogura 20 MW PP (Energyprima) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 234828
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 232974
165 | Amnura 50 MW PP(Sinha) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 491950
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [17 empty] | 32 |  | 36 | 38 | 44 | 36 | 36 | 36 | 36 | 218092
168 | Santahar 50 MW Peaking PP | [17 empty] | 32 |  | 31 | 31 | 31 | 31 | 31 | 29 | 30 | 209338
169 | Natore 52 MW PP (Rajlanka) | [17 empty] | 35 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 365280
170 | Chapainawabganj 100 MW Peaking PP | 70 | 70 | 47 | 47 | [13 empty] | 27 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 808000
171 | Baghabari 200 MW PP (Paramount) | [17 empty] | 165 |  | 50 | 25 | 25 |  |  |  | 0 | 187972
| Bagura 113 MW PP (Confidence)-2 | 113 | 70 | [15 empty] | 21 |  | 105 | 113 | 113 | 113 | 113 | 113 | 113 | 943968
172 | Confidence Power Bogura Unit-1 113 MW | 109 | 109 | 109 | 109 | 109 | 70 | 35 | 35 | 35 | 35 | 35 | 35 | 50 | 90 | 109 | 109 | 109 | 109 |  | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 2058816
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 101 | 98 | 97 | 90 | 86 | 84 | 62 | 54 | 54 | 52 | 52 | 52 | 53 | 53 | 67 | 95 | 81 | 81 |  | 98 | 89 | 90 | 88 | 88 | 93 | 90 | 1870080
177 | Sympa Solar Power 8MW | [6 empty] | 1 | 2 | 4 | 5 | 6 | 6 | 6 | 5 | 4 | 3 | 1 | [9 empty] | 41395
178
178