## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-10-19 | Monday
|  |  | Date (day): | 2020-10-19 |  | Monday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13825.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14726 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-10-18 | 2020-10-19 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 100 | 100 | 100
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 115 | 115 | 115 | 75 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 200 | 200 | 165 |  | Gas shortage
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 67 | 0 | 0 | 0 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 73 | 72 | 72 | 72 | 36 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under S/D for dust in gas.
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 312 | 349 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 370 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 100 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 275 | 10 | 305 | 305
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 95 | 96 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 40 | 40 | 40 |  | 15 | Engine problem
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 88 | 50 | 88 |  | 12 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 0 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 120 | 120 | 100 | 150
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 94 | 94 | 94 | 94
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 150 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Engine problem
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 55 | 55 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 51 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 225 | 300 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 50 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 97 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 100 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 137 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 86 | 86 | 85 | 86 |  | 19 | Engine problem
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 35 | 17 | 17 | 17 | 87 |  | Fuel shortage
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 2789 | 3139 | 3456 | 3835 | 705 | 1208
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 115 | 115 | 115 | 115 | 65 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 11 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 15 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 122 | 120 | 120 | 120 | 110 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 204 | 210 | 221 | 221
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 139 | 139 | 145 | 145
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 7 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 102 | 102
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 90 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 22 | 22 | 22 | 22
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 21 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 7 | 21 | 10 | 20
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 40 | 97 | 97 | 97 |  | 11 | Engine problem
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 160 | 161 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 23 | 54 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 989 | 1326 | 1717 | 1702 | 355 | 109
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 80 | 80 | 80 | 80 | 49 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 |  | 134 | Under maint
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 184 | 197 | 225 | 225 |  |  | FGMO
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 300 | 360 | 360 |  |  | FGMO
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 300 | 350 | 350 |  |  | FGMO
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 29 | 30 | 30 | 15 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 30 | 5 | 5 | 5 | 50 |  | Gas shortage
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 120 | 137 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 25 | 50
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 85 | 79 | 90 | 90 |  | 57 | ST under shut down
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 181 | 200 | 200
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 19 | 22 | 22
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 108 | 146 | 165 | 173
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 21 | 22 | 22 | 22
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 50 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 17 | 0 | 17 | 97 |  | Engine problem & Fuel shortage
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 99 | 113 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1457 | 1786 | 1948 | 2198 | 577 | 191
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 149 | 140 | 150 | 150 | 52 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 40 | 48 | 48 | 48 |  | 47 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 190 | 200 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 109 | 115 | 115 | 115
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 509 | 523 | 534.6 | 533 | 52 | 47
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 84 | 82 | 85 | 85
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 43 | 43 | 43 | 43 |  | 47 | Unit-4 under shut down
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 |  | 54 | STG under maint.
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 140 | 158 | 160 | 160 |  | 170 | GT-2 S/D & ST Under maint.
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 44 | 28 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 41 | 47 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 63 | 64 | 65 | 65 |  |  | FGMO
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 86 | 87 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 140 | 140 | 140 | 140
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 270 | 310 | 341 | 341 |  |  | FGMO
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 419 | 418 | 400 | 400
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1482 | 1532 | 1571 | 1571 | 0 | 271
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 919 | 918 | 928 | 928
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 115 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 3 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 218 | 220 | 220
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 325 | 290 | 410 | 410
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 35 | 105 | 105 | 105
| 108 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1415 | 1789 | 1968 | 2124 | 0 | 0
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 18 | 36 | 33 | 33
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 93 | 95 | 95 | 95
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 490 | 570 | 580 | 600
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 601 | 811 | 818 | 838 | 0 | 194
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 36 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 20 | 20 | 20 | 20 | 30 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 50 | 50
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 152 | 172 | 225 | 225 |  |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 159 | 191 | 220 | 220 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 365 | 410 | 414 | 414 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 31 | 0 | 30
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 18 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 10 | 10 | 10 | 10
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 52 | 52 | 52
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 95 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 50 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 35 | 113 | 113 | 113
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 109 | 54 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 881 | 1351 | 1550 | 1670 | 461 | 0
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 48 | 105 | 105 | 105
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 204 | 255 | 263 | 255 | 294 | 40
|  | Total |  |  |  |  | 20383 | 19892 | 10327 | 12512 | 13825.6 | 14726 | 2444 | 2060
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9835.9062 | 11917 | 13168.1326 | 14025.7147
| A. |  | 2020-10-18 | (Yesterday) |  |  |  |  | Sunday
| 1 | Highest Generation : |  |  | 12512 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
| 2 | Minimum Generation : |  |  | 8928 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12512 | MW
| 3 | Day peak Generation : |  |  | 10327 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11917 | MW
| 4 | Evening peak Generation : |  |  | 12512 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 257.2734 | MKWHr | By Solar | 0.18354 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 139.3003 | MKWHr |  | By Oil: | 76.0409 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 13.9029 | MKWHr |  | By Hydro: | 2.8193 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2444 | MW | Dhaka | 4227 | 4227 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2060 | MW | Chittagong | 1124 | 1124 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4504 | MW | Khulna | 1532 | 1532 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1184.86 | MMCFD |  |  | Rajshahi | 1279 | 1279 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 162408067.264 | ii) Oil : | Taka | 624317405.81 | Comilla | 1158 | 1158 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 61415758 | Total | Taka | 848141231.074 | Mymensingh | 981 | 981 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.015 | MKWHr. | Sylhet | 525 | 525 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 90 | MW (E to W) at | 19:30 | hrs | Barisal | 341 | 341 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 13 | MW at | 5:00 | hrs | Rangpur | 750 | 750 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.4° C |  |  | Total | 11917 | 11917 |  | 0
| B. |  | 2020-10-19 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 34° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14726 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10500 | MW
| 4 | Reserve(Generation end) |  |  |  | 1926 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 263.1953 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8862 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.0407 | MKWHr. | ii) HVDC Flow at Peak Time |  | 918 | MW at | 19:30 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.9856 | MKWHr. | iii) Maximum HVDC Flow : |  | 919 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 102.16 |  | (b) Today: | 102.11 |  | (c) Rule Curve: |  | 107.7
.

## YesterdayGen
2020-10-18
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 115 | 200 | 72 | 68 | 0 | 295 |  | 0 | 420 | 265 | 75 | 97 | 40 | 0 | 0 | 150 | 0 | 7 | 94 | 150 | 55 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 16 | 0 | 88 | 35 | 115 | 0 | 8 | 204 | 0 | 140 | 0 |  | 0 | 0 | 102 | 0 | 97 | 50 | 20 | 34 | 0 | 80 | 0 | 275 | 300 | 192 | 8 | 85 | 29 | 52 | 0 | 35 | 0 | 0 | 52 | 19 | 11 | 33 | 21 | 142 | 157 | 40 | 17 | 0 | 85 | 43 | 50 | 44 | 110 | 140 | 63 | 86 | 0 | 140 | 0 | 0 | 10 | 285 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 22 | 164 | 135 | 421 | 115 | 86 | 0 | 0 | 180 | 18 | 0 | 17 | 101 | 100 | 0 | 35 |  | 919 | 0 | 330 | 0 | 115 | 195 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 0 | 0 | 95 | 20 | 0 | 0 | 24 | 29 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 183 | 0 | 91 | 0 | 198 | 0 | 390 | 35 | 0 | 113 | 0 | 88 | 0 | 0 | 109 | 580 |  | 7976 | 3895 | 11871 | 3949 | 919 | 2120 | 3317 | 730 | 123 | 571 | 142 | 0 | 0 | 102.16
2:00 | 0 | 0 | 0 | 115 | 200 | 72 | 69 | 0 | 310 |  | 0 | 420 | 270 | 98 | 97 | 40 | 0 | 0 | 160 | 0 | 7 | 94 | 114 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 86 | 35 | 115 | 0 | 8 | 204 | 0 | 140 | 0 |  | 0 | 0 | 34 | 0 | 97 | 36 | 20 | 35 | 0 | 80 | 0 | 275 | 300 | 180 | 8 | 96 | 29 | 51 | 0 | 35 | 0 | 0 | 52 | 19 | 11 | 33 | 21 | 136 | 155 | 40 | 17 | 0 | 85 | 43 | 50 | 44 | 110 | 139 | 63 | 87 | 0 | 140 | 0 | 0 | 10 | 280 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 22 | 50 | 137 | 421 | 115 | 86 | 0 | 0 | 180 | 17 | 0 | 0 | 101 | 100 | 0 | 35 |  | 918 | 0 | 330 | 0 | 115 | 135 | 0 | 0 | 0 | 0 | 24 | 0 | 38 | 110 | 0 | 0 | 0 | 0 | 0 | 42 | 20 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 183 | 0 | 93 | 0 | 199 | 0 | 400 | 35 | 0 | 113 | 0 | 89 | 0 | 0 | 109 | 580 |  | 7695 | 3726 | 11421 | 3956 | 918 | 2144 | 3091 | 730 | 121 | 325 | 136 | 0 | 0 | 102.16
3:00 | 0 | 0 | 0 | 115 | 200 | 72 | 69 | 0 | 320 |  | 0 | 420 | 265 | 100 | 97 | 40 | 0 | 0 | 150 | 0 | 7 | 94 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 84 | 35 | 115 | 0 | 0 | 204 | 0 | 140 | 0 |  | 0 | 0 | 34 | 0 | 91 | 12 | 20 | 35 | 0 | 80 | 0 | 275 | 300 | 174 | 8 | 88 | 29 | 51 | 0 | 35 | 0 | 0 | 25 | 2 | 11 | 33 | 21 | 134 | 157 | 40 | 17 | 0 | 87 | 43 | 50 | 44 | 110 | 144 | 63 | 87 | 0 | 140 | 0 | 0 | 10 | 290 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 22 | 0 | 142 | 426 | 115 | 86 | 0 | 0 | 180 | 17 | 0 | 0 | 101 | 100 | 0 | 35 |  | 919 | 0 | 325 | 0 | 83 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 184 | 0 | 95 | 0 | 198 | 0 | 389 | 35 | 0 | 113 | 0 | 89 | 0 | 0 | 109 | 580 |  | 7505 | 3587 | 11092 | 3924 | 919 | 2155 | 2908 | 731 | 119 | 202 | 134 | 0 | 0 | 102.16
4:00 | 0 | 0 | 0 | 115 | 200 | 72 | 69 | 0 | 326 |  | 0 | 420 | 270 | 100 | 97 | 40 | 0 | 0 | 160 | 0 | 7 | 94 | 16 | 0 | 0 | 0 | 0 | 0 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 83 | 35 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 34 | 0 | 48 | 12 | 20 | 28 | 0 | 80 | 0 | 275 | 300 | 183 | 8 | 93 | 29 | 51 | 0 | 43 | 0 | 0 | 25 | 16 | 11 | 33 | 21 | 134 | 157 | 40 | 17 | 0 | 87 | 43 | 50 | 44 | 110 | 140 | 63 | 87 | 0 | 140 | 0 | 0 | 10 | 275 | 24 | 8 | 0 | 295 | 0 | 0 | 200 | 0 | 149 | 0 | 22 | 0 | 142 | 426 | 115 | 50 | 0 | 0 | 180 | 17 | 0 | 0 | 100 | 100 | 0 | 35 |  | 919 | 0 | 325 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 183 | 0 | 95 | 0 | 199 | 0 | 402 | 35 | 0 | 0 | 0 | 92 | 0 | 0 | 109 | 580 |  | 7382 | 3406 | 10788 | 3957 | 919 | 2160 | 2600 | 730 | 118 | 170 | 134 | 0 | 0 | 102.16
5:00 | 0 | 0 | 0 | 115 | 200 | 72 | 70 | 0 | 326 |  | 0 | 420 | 285 | 100 | 97 | 40 | 0 | 0 | 155 | 0 | 45 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 81 | 35 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 34 | 0 | 12 | 12 | 20 | 28 | 0 | 80 | 0 | 275 | 300 | 185 | 8 | 96 | 29 | 51 | 0 | 43 | 0 | 0 | 0 | 16 | 0 | 33 | 21 | 120 | 157 | 40 | 17 | 0 | 87 | 43 | 50 | 41 | 110 | 142 | 64 | 87 | 0 | 140 | 0 | 0 | 10 | 280 | 24 | 2 | 0 | 30 | 0 | 0 | 200 | 0 | 149 | 0 | 22 | 0 | 142 | 423 | 85 | 50 | 0 | 0 | 180 | 17 | 0 | 0 | 98 | 100 | 0 | 35 |  | 919 | 0 | 325 | 0 | 7 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 183 | 0 | 94 | 0 | 199 | 0 | 415 | 35 | 0 | 0 | 0 | 87 | 0 | 0 | 109 | 560 |  | 6977 | 3368 | 10345 | 3940 | 919 | 2175 | 2195 | 710 | 116 | 170 | 120 | 0 | 0 | 102.16
6:00 | 0 | 0 | 0 | 115 | 200 | 72 | 69 | 0 | 326 |  | 0 | 350 | 275 | 100 | 80 | 40 | 0 | 0 | 85 | 0 | 95 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 81 | 35 | 115 | 0 | 0 | 204 | 0 | 138 | 0 |  | 0 | 0 | 27 | 0 | 12 | 12 | 20 | 26 | 0 | 80 | 0 | 275 | 300 | 190 | 8 | 87 | 29 | 52 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 33 | 21 | 102 | 157 | 40 | 17 | 0 | 86 | 43 | 47 | 41 | 110 | 140 | 40 | 87 | 0 | 140 | 0 | 0 | 10 | 270 | 24 | 5 | 0 | 30 | 0 | 0 | 150 | 0 | 149 | 0 | 22 | 0 | 100 | 430 | 8 | 34 | 0 | 0 | 125 | 17 | 0 | 0 | 102 | 100 | 0 | 35 |  | 919 | 0 | 325 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 200 | 0 | 350 | 35 | 0 | 0 | 0 | 39 | 0 | 0 | 35 | 530 |  | 6500 | 3006 | 9506 | 3836 | 919 | 1925 | 1765 | 680 | 116 | 163 | 102 | 0 | 0 | 102.16
7:00 | 0 | 0 | 0 | 115 | 200 | 72 | 40 | 0 | 284 |  | 0 | 330 | 295 | 100 | 65 | 40 | 0 | 0 | 85 | 0 | 100 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 83 | 35 | 115 | 0 | 0 | 204 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 12 | 12 | 20 | 23 | 0 | 80 | 0 | 275 | 300 | 178 | 8 | 92 | 29 | 52 | 0 | 43 | 0 | 0 | 0 | 0 | 11 | 33 | 21 | 86 | 156 | 40 | 20 | 0 | 87 | 43 | 14 | 10 | 110 | 140 | 40 | 40 | 0 | 140 | 0 | 0 | 10 | 270 | 24 | 8 | 0 | 15 | 0 | 0 | 150 | 0 | 139 | 1 | 22 | 0 | 70 | 428 | 8 | 34 | 0 | 1 | 51 | 17 | 0 | 0 | 75 | 70 | 0 | 35 |  | 919 | 0 | 290 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 150 | 0 | 375 | 17 | 0 | 0 | 0 | 35 | 0 | 1 | 35 | 520 |  | 6050 | 2878 | 8928 | 3697 | 919 | 1740 | 1559 | 670 | 118 | 136 | 86 | 3 | 0 | 102.15
8:00 | 0 | 0 | 0 | 115 | 200 | 72 | 40 | 0 | 282 |  | 0 | 330 | 275 | 100 | 65 | 40 | 0 | 0 | 85 | 0 | 100 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 84 | 35 | 115 | 0 | 0 | 204 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 13 | 12 | 20 | 2 | 0 | 80 | 0 | 275 | 300 | 183 | 8 | 94 | 29 | 52 | 0 | 43 | 0 | 0 | 0 | 15 | 11 | 33 | 21 | 92 | 154 | 32 | 20 | 1 | 84 | 43 | 14 | 10 | 110 | 142 | 40 | 40 | 0 | 140 | 0 | 0 | 0 | 290 | 8 | 8 | 0 | 17 | 0 | 0 | 150 | 0 | 149 | 9 | 22 | 0 | 75 | 424 | 8 | 34 | 0 | 0 | 52 | 17 | 0 | 0 | 75 | 70 | 0 | 35 |  | 919 | 0 | 290 | 0 | 5 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 24 | 0 | 150 | 0 | 390 | 17 | 0 | 0 | 0 | 33 | 0 | 2 | 35 | 520 |  | 6050 | 2913 | 8963 | 3686 | 919 | 1750 | 1579 | 670 | 119 | 136 | 92 | 12 | 0 | 102.15
9:00 | 0 | 0 | 0 | 115 | 200 | 72 | 60 | 0 | 259 |  | 0 | 330 | 275 | 100 | 75 | 40 | 0 | 0 | 85 | 0 | 100 | 64 | 48 | 0 | 0 | 0 | 0 | 17 | 17 | 55 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 86 | 35 | 115 | 0 | 0 | 204 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 40 | 12 | 20 | 2 | 0 | 80 | 0 | 275 | 280 | 210 | 8 | 91 | 29 | 30 | 0 | 43 | 0 | 0 | 5 | 15 | 11 | 33 | 20 | 88 | 152 | 32 | 20 | 1 | 87 | 43 | 42 | 29 | 110 | 139 | 65 | 84 | 0 | 140 | 0 | 0 | 10 | 270 | 16 | 8 | 0 | 45 | 0 | 0 | 163 | 0 | 149 | 15 | 22 | 0 | 97 | 425 | 23 | 49 | 0 | 2 | 104 | 17 | 0 | 0 | 75 | 100 | 0 | 35 |  | 919 | 0 | 290 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 85 | 0 | 161 | 0 | 337 | 17 | 0 | 34 | 0 | 33 | 0 | 3 | 35 | 500 |  | 6493 | 2936 | 9429 | 3772 | 919 | 1824 | 1866 | 650 | 121 | 168 | 88 | 21 | 0 | 102.15
10:00 | 0 | 0 | 0 | 115 | 200 | 72 | 68 | 0 | 228 |  | 0 | 400 | 275 | 100 | 82 | 40 | 0 | 0 | 90 | 0 | 100 | 80 | 48 | 0 | 0 | 0 | 0 | 17 | 17 | 55 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 87 | 35 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 40 | 13 | 20 | 2 | 0 | 80 | 0 | 275 | 290 | 216 | 8 | 85 | 29 | 30 | 0 | 35 | 0 | 0 | 8 | 15 | 11 | 33 | 20 | 90 | 150 | 40 | 20 | 2 | 86 | 43 | 42 | 44 | 110 | 145 | 65 | 84 | 0 | 140 | 0 | 0 | 10 | 290 | 24 | 8 | 0 | 105 | 0 | 0 | 191 | 0 | 149 | 17 | 22 | 0 | 100 | 420 | 82 | 69 | 0 | 3 | 106 | 17 | 0 | 0 | 75 | 100 | 0 | 35 |  | 919 | 0 | 310 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 91 | 0 | 156 | 0 | 398 | 17 | 0 | 35 | 0 | 35 | 0 | 3 | 35 | 490 |  | 6801 | 3010 | 9811 | 3807 | 919 | 1964 | 2076 | 640 | 122 | 168 | 90 | 25 | 0 | 102.15
11:00 | 0 | 0 | 0 | 115 | 200 | 72 | 68 | 0 | 257 |  | 0 | 400 | 275 | 100 | 95 | 40 | 0 | 0 | 120 | 0 | 100 | 94 | 48 | 0 | 0 | 0 | 0 | 17 | 17 | 55 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 87 | 35 | 115 | 0 | 0 | 228 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 40 | 18 | 20 | 4 | 0 | 80 | 0 | 280 | 285 | 215 | 8 | 86 | 29 | 30 | 0 | 35 | 0 | 0 | 8 | 16 | 11 | 33 | 20 | 98 | 149 | 40 | 0 | 2 | 83 | 43 | 39 | 44 | 110 | 141 | 64 | 86 | 0 | 140 | 0 | 0 | 10 | 290 | 24 | 8 | 0 | 130 | 0 | 0 | 182 | 0 | 133 | 14 | 22 | 0 | 103 | 418 | 107 | 86 | 0 | 4 | 156 | 17 | 0 | 0 | 77 | 100 | 0 | 35 |  | 919 | 0 | 330 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 155 | 0 | 93 | 0 | 162 | 0 | 405 | 17 | 0 | 35 | 0 | 33 | 0 | 6 | 50 | 490 |  | 6991 | 3066 | 10057 | 3861 | 919 | 2005 | 2218 | 640 | 122 | 168 | 98 | 26 | 0 | 102.14
12:00 | 0 | 0 | 0 | 115 | 200 | 73 | 67 | 0 | 312 |  | 0 | 400 | 275 | 100 | 95 | 40 | 0 | 0 | 120 | 0 | 100 | 94 | 48 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 87 | 35 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 7 | 0 | 0 | 40 | 15 | 20 | 7 | 0 | 80 | 0 | 280 | 300 | 184 | 8 | 85 | 29 | 30 | 0 | 43 | 0 | 0 | 8 | 18 | 11 | 33 | 21 | 108 | 149 | 40 | 20 | 1 | 84 | 43 | 44 | 41 | 110 | 140 | 63 | 86 | 0 | 140 | 0 | 0 | 10 | 270 | 24 | 8 | 0 | 225 | 0 | 0 | 190 | 0 | 137 | 11 | 22 | 0 | 120 | 419 | 109 | 86 | 0 | 4 | 160 | 23 | 0 | 0 | 99 | 100 | 0 | 35 |  | 919 | 0 | 325 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 93 | 0 | 159 | 0 | 365 | 35 | 0 | 35 | 0 | 48 | 0 | 6 | 109 | 490 |  | 7226 | 3101 | 10327 | 3831 | 919 | 2007 | 2503 | 640 | 122 | 175 | 108 | 22 | 0 | 102.14
13:00 | 0 | 0 | 0 | 115 | 200 | 73 | 66 | 0 | 309 |  | 0 | 400 | 275 | 100 | 96 | 40 | 0 | 0 | 120 | 0 | 98 | 94 | 48 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 19 | 25 | 22 | 0 | 33 | 0 | 0 | 88 | 35 | 115 | 0 | 0 | 204 | 0 | 140 | 0 |  | 0 | 8 | 0 | 0 | 40 | 19 | 20 | 11 | 0 | 80 | 0 | 370 | 300 | 180 | 8 | 86 | 29 | 30 | 0 | 51 | 0 | 0 | 8 | 19 | 11 | 33 | 21 | 112 | 149 | 40 | 17 | 2 | 86 | 43 | 28 | 44 | 110 | 140 | 63 | 87 | 0 | 140 | 0 | 0 | 10 | 290 | 24 | 8 | 0 | 300 | 0 | 0 | 190 | 0 | 146 | 19 | 22 | 0 | 138 | 421 | 99 | 86 | 0 | 5 | 161 | 36 | 0 | 0 | 103 | 100 | 0 | 20 |  | 919 | 0 | 320 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 17 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 93 | 0 | 159 | 0 | 363 | 105 | 0 | 35 | 0 | 56 | 0 | 6 | 109 | 490 |  | 7405 | 3175 | 10580 | 3875 | 919 | 2024 | 2679 | 640 | 123 | 176 | 112 | 32 | 10580 | 102.14
14:00 | 0 | 0 | 0 | 115 | 200 | 73 | 65 | 0 | 307 |  | 0 | 350 | 295 | 100 | 96 | 40 | 0 | 0 | 120 | 0 | 100 | 94 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 19 | 25 | 22 | 33 | 33 | 0 | 0 | 88 | 35 | 110 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 8 | 0 | 0 | 44 | 19 | 20 | 5 | 0 | 80 | 0 | 265 | 300 | 190 | 8 | 86 | 29 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 11 | 33 | 21 | 112 | 137 | 40 | 0 | 0 | 84 | 43 | 28 | 41 | 112 | 146 | 53 | 86 | 0 | 120 | 0 | 0 | 10 | 290 | 24 | 8 | 0 | 300 | 0 | 0 | 190 | 0 | 149 | 16 | 22 | 0 | 138 | 414 | 55 | 86 | 0 | 3 | 179 | 35 | 0 | 0 | 103 | 100 | 0 | 18 |  | 919 | 0 | 320 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 16 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 155 | 0 | 91 | 0 | 181 | 0 | 350 | 105 | 0 | 35 | 0 | 54 | 0 | 6 | 109 | 510 |  | 7115 | 3204 | 10319 | 3735 | 919 | 1924 | 2677 | 660 | 123 | 144 | 112 | 25 | 0 | 102.14
15:00 | 0 | 0 | 0 | 115 | 200 | 72 | 65 | 0 | 301 |  | 0 | 350 | 285 | 100 | 96 | 40 | 0 | 0 | 185 | 0 | 100 | 94 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 18 | 33 | 33 | 0 | 0 | 81 | 35 | 110 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 8 | 0 | 0 | 78 | 19 | 20 | 2 | 0 | 80 | 0 | 275 | 355 | 186 | 8 | 83 | 29 | 5 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 33 | 21 | 118 | 138 | 40 | 0 | 1 | 83 | 43 | 28 | 41 | 112 | 141 | 63 | 86 | 0 | 140 | 0 | 0 | 10 | 315 | 24 | 8 | 0 | 300 | 0 | 0 | 191 | 0 | 149 | 4 | 22 | 0 | 127 | 414 | 55 | 86 | 0 | 1 | 179 | 36 | 0 | 0 | 101 | 100 | 0 | 18 |  | 919 | 0 | 315 | 0 | 40 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 16 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 165 | 0 | 91 | 0 | 180 | 0 | 407 | 105 | 0 | 52 | 0 | 61 | 0 | 4 | 54 | 550 |  | 7337 | 3294 | 10631 | 3918 | 919 | 1986 | 2720 | 700 | 116 | 144 | 118 | 10 | 0 | 102.13
16:00 | 0 | 0 | 0 | 115 | 200 | 72 | 65 | 0 | 302 |  | 0 | 350 | 285 | 100 | 96 | 40 | 0 | 0 | 72 | 0 | 100 | 58 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 80 | 35 | 110 | 0 | 0 | 217 | 0 | 111 | 0 |  | 0 | 8 | 0 | 0 | 90 | 42 | 20 | 3 | 0 | 80 | 0 | 310 | 355 | 194 | 8 | 87 | 29 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 11 | 33 | 21 | 126 | 137 | 40 | 0 | 1 | 83 | 43 | 28 | 41 | 112 | 150 | 63 | 10 | 0 | 140 | 0 | 0 | 10 | 290 | 24 | 8 | 0 | 245 | 0 | 0 | 189 | 0 | 140 | 0 | 22 | 0 | 135 | 410 | 25 | 50 | 0 | 1 | 144 | 51 | 0 | 0 | 106 | 100 | 0 | 18 |  | 919 | 0 | 305 | 0 | 49 | 120 | 0 | 0 | 2 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 17 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 154 | 0 | 88 | 0 | 163 | 0 | 405 | 53 | 0 | 70 | 0 | 77 | 0 | 2 | 35 | 530 |  | 7044 | 3206 | 10250 | 3815 | 919 | 1893 | 2552 | 680 | 115 | 146 | 126 | 4 | 0 | 102.13
17:00 | 0 | 0 | 0 | 115 | 200 | 72 | 66 | 0 | 293 |  | 0 | 300 | 275 | 100 | 96 | 40 | 0 | 0 | 71 | 0 | 100 | 58 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 80 | 35 | 110 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 8 | 0 | 0 | 93 | 50 | 20 | 3 | 0 | 80 | 0 | 265 | 300 | 179 | 8 | 75 | 29 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 11 | 33 | 22 | 118 | 139 | 48 | 20 | 0 | 84 | 43 | 11 | 10 | 100 | 159 | 40 | 10 | 0 | 140 | 0 | 0 | 10 | 290 | 24 | 8 | 0 | 200 | 0 | 0 | 189 | 0 | 145 | 0 | 22 | 0 | 140 | 414 | 25 | 70 | 0 | 0 | 144 | 53 | 0 | 0 | 106 | 100 | 0 | 18 |  | 919 | 0 | 270 | 0 | 49 | 120 | 0 | 0 | 3 | 5 | 0 | 0 | 25 | 16 | 0 | 0 | 0 | 0 | 10 | 0 | 20 | 0 | 0 | 0 | 0 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 154 | 0 | 91 | 0 | 157 | 0 | 312 | 53 | 0 | 70 | 0 | 91 | 0 | 1 | 35 | 440 |  | 6794 | 3030 | 9824 | 3640 | 919 | 1685 | 2578 | 590 | 115 | 178 | 118 | 1 | 0 | 102.13
18:00 | 0 | 0 | 100 | 115 | 200 | 72 | 66 | 0 | 347 |  | 0 | 400 | 10 | 100 | 96 | 40 | 0 | 0 | 194 | 0 | 100 | 94 | 70 | 61 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 29 | 0 | 82 | 35 | 115 | 0 | 14 | 204 | 0 | 139 | 0 |  | 0 | 0 | 102 | 90 | 97 | 50 | 20 | 3 | 0 | 80 | 0 | 270 | 300 | 187 | 8 | 75 | 29 | 5 | 0 | 51 | 0 | 41 | 8 | 19 | 11 | 33 | 22 | 140 | 141 | 48 | 20 | 0 | 84 | 43 | 28 | 35 | 110 | 158 | 65 | 85 | 0 | 140 | 0 | 0 | 10 | 300 | 24 | 11 | 90 | 220 | 200 | 50 | 190 | 52 | 149 | 0 | 22 | 68 | 137 | 414 | 67 | 86 | 0 | 0 | 144 | 54 | 0 | 0 | 112 | 100 | 0 | 17 |  | 918 | 0 | 305 | 0 | 106 | 170 | 0 | 0 | 3 | 0 | 40 | 0 | 35 | 110 | 0 | 0 | 0 | 50 | 30 | 85 | 20 | 0 | 31 | 52 | 15 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 144 | 0 | 91 | 26 | 144 | 0 | 405 | 105 | 50 | 92 | 0 | 92 | 0 | 0 | 35 | 480 |  | 8097 | 3823 | 11920 | 3952 | 918 | 2079 | 3487 | 630 | 117 | 597 | 140 | 0 | 0 | 102.13
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 100 | 115 | 200 | 72 | 40 | 0 | 330 |  | 0 | 370 | 10 | 100 | 96 | 40 | 0 | 0 | 120 | 0 | 100 | 94 | 150 | 88 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 30 | 33 | 33 | 51 | 0 | 84 | 35 | 115 | 0 | 24 | 204 | 0 | 139 | 0 |  | 0 | 0 | 102 | 100 | 97 | 50 | 20 | 18 | 0 | 80 | 0 | 265 | 300 | 187 | 8 | 79 | 29 | 5 | 0 | 51 | 0 | 41 | 8 | 19 | 11 | 33 | 22 | 150 | 141 | 48 | 20 | 0 | 84 | 43 | 28 | 47 | 110 | 158 | 65 | 87 | 0 | 140 | 0 | 0 | 10 | 290 | 24 | 11 | 50 | 300 | 50 | 97 | 200 | 99 | 149 | 0 | 22 | 150 | 137 | 418 | 115 | 86 | 0 | 0 | 158 | 54 | 0 | 17 | 113 | 100 | 0 | 17 |  | 917 | 0 | 295 | 0 | 115 | 218 | 0 | 0 | 3 | 0 | 40 | 0 | 36 | 110 | 0 | 0 | 0 | 50 | 40 | 95 | 20 | 0 | 36 | 52 | 32 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 169 | 0 | 92 | 100 | 189 | 0 | 410 | 105 | 50 | 113 | 0 | 93 | 0 | 0 | 35 | 560 |  | 8275 | 4164 | 12439 | 3927 | 917 | 2032 | 3817 | 710 | 119 | 767 | 150 | 0 | 0 | 102.13
19:30 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 349 |  | 0 | 370 | 10 | 100 | 96 | 40 | 0 | 0 | 120 | 0 | 100 | 94 | 150 | 88 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 30 | 33 | 33 | 51 | 0 | 85 | 35 | 115 | 0 | 25 | 210 | 0 | 139 | 0 |  | 0 | 0 | 102 | 90 | 97 | 50 | 20 | 21 | 0 | 80 | 0 | 300 | 300 | 197 | 8 | 79 | 29 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 11 | 33 | 22 | 146 | 140 | 48 | 20 | 0 | 82 | 43 | 28 | 47 | 110 | 158 | 64 | 87 | 0 | 140 | 0 | 0 | 10 | 310 | 24 | 11 | 50 | 300 | 50 | 97 | 200 | 100 | 149 | 0 | 22 | 181 | 137 | 418 | 115 | 86 | 0 | 0 | 161 | 54 | 0 | 17 | 113 | 100 | 0 | 17 |  | 918 | 0 | 290 | 0 | 115 | 218 | 0 | 0 | 3 | 0 | 40 | 0 | 36 | 110 | 0 | 0 | 0 | 50 | 36 | 95 | 20 | 0 | 38 | 52 | 31 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 172 | 0 | 95 | 100 | 191 | 0 | 410 | 105 | 50 | 113 | 0 | 105 | 0 | 0 | 54 | 570 |  | 8306 | 4206 | 12512 | 3974 | 918 | 2037 | 3874 | 720 | 120 | 723 | 146 | 0 | 0 | 0
20:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 349 |  | 0 | 370 | 10 | 100 | 88 | 43 | 0 | 0 | 120 | 0 | 100 | 94 | 150 | 87 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 85 | 35 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 102 | 80 | 97 | 50 | 0 | 25 | 0 | 96 | 0 | 275 | 300 | 181 | 8 | 80 | 29 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 11 | 33 | 22 | 148 | 140 | 48 | 20 | 0 | 84 | 43 | 28 | 47 | 110 | 158 | 65 | 86 | 0 | 140 | 0 | 0 | 10 | 300 | 24 | 11 | 50 | 300 | 50 | 97 | 200 | 100 | 149 | 0 | 22 | 181 | 140 | 418 | 115 | 86 | 0 | 0 | 161 | 54 | 0 | 17 | 112 | 100 | 0 | 17 |  | 918 | 0 | 290 | 0 | 115 | 218 | 0 | 0 | 3 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 39 | 96 | 20 | 0 | 45 | 52 | 31 | 18 | 10 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 172 | 0 | 95 | 100 | 184 | 0 | 414 | 105 | 50 | 113 | 0 | 104 | 0 | 0 | 54 | 590 |  | 8262 | 4234 | 12496 | 3942 | 918 | 2036 | 3859 | 739 | 120 | 734 | 148 | 0 | 0 | 102.12
21:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 351 |  | 0 | 370 | 10 | 100 | 80 | 43 | 0 | 0 | 120 | 0 | 100 | 76 | 150 | 88 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 88 | 35 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 102 | 80 | 97 | 50 | 15 | 25 | 0 | 135 | 0 | 280 | 300 | 188 | 8 | 75 | 29 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 11 | 33 | 22 | 140 | 141 | 48 | 20 | 0 | 84 | 43 | 28 | 47 | 110 | 160 | 61 | 86 | 0 | 140 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 300 | 50 | 45 | 200 | 59 | 149 | 0 | 22 | 181 | 140 | 420 | 115 | 86 | 0 | 0 | 161 | 54 | 0 | 44 | 112 | 100 | 0 | 17 |  | 918 | 0 | 280 | 0 | 115 | 218 | 0 | 0 | 11 | 0 | 40 | 0 | 39 | 110 | 0 | 0 | 0 | 50 | 42 | 96 | 20 | 0 | 36 | 52 | 31 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 181 | 0 | 97 | 100 | 177 | 0 | 413 | 105 | 0 | 113 | 0 | 108 | 0 | 0 | 70 | 590 |  | 8180 | 4201 | 12381 | 3996 | 918 | 2040 | 3688 | 740 | 123 | 736 | 140 | 0 | 0 | 102.12
22:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 351 |  | 0 | 370 | 10 | 100 | 80 | 43 | 0 | 0 | 95 | 0 | 100 | 76 | 150 | 88 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 88 | 35 | 115 | 0 | 25 | 206 | 0 | 139 | 0 |  | 0 | 0 | 102 | 60 | 97 | 50 | 15 | 31 | 0 | 135 | 0 | 285 | 300 | 214 | 8 | 75 | 29 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 11 | 33 | 22 | 148 | 140 | 48 | 20 | 0 | 84 | 43 | 28 | 47 | 110 | 157 | 65 | 87 | 0 | 140 | 0 | 0 | 10 | 290 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 65 | 149 | 0 | 22 | 100 | 140 | 418 | 115 | 86 | 0 | 0 | 162 | 54 | 0 | 52 | 111 | 100 | 0 | 17 |  | 918 | 0 | 280 | 0 | 115 | 218 | 0 | 0 | 17 | 0 | 40 | 0 | 39 | 110 | 0 | 0 | 0 | 50 | 42 | 96 | 20 | 0 | 36 | 52 | 31 | 21 | 10 | 11 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 178 | 0 | 96 | 100 | 176 | 0 | 411 | 105 | 0 | 113 | 0 | 106 | 0 | 0 | 109 | 590 |  | 8009 | 4241 | 12250 | 3998 | 918 | 2037 | 3543 | 741 | 123 | 742 | 148 | 0 | 0 | 102.12
23:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 352 |  | 0 | 370 | 50 | 100 | 80 | 43 | 0 | 0 | 95 | 0 | 100 | 76 | 150 | 49 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 88 | 35 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 102 | 60 | 97 | 50 | 15 | 41 | 0 | 135 | 0 | 275 | 300 | 210 | 8 | 75 | 29 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 11 | 33 | 22 | 148 | 154 | 48 | 20 | 0 | 86 | 43 | 28 | 47 | 110 | 159 | 65 | 87 | 0 | 140 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 26 | 149 | 0 | 22 | 100 | 143 | 422 | 115 | 86 | 0 | 0 | 162 | 54 | 0 | 52 | 112 | 100 | 0 | 17 |  | 918 | 0 | 270 | 0 | 115 | 220 | 0 | 0 | 12 | 0 | 40 | 0 | 37 | 110 | 0 | 0 | 0 | 50 | 42 | 96 | 20 | 0 | 36 | 52 | 31 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 161 | 0 | 95 | 100 | 181 | 0 | 411 | 105 | 0 | 113 | 0 | 106 | 0 | 0 | 109 | 590 |  | 8002 | 4212 | 12214 | 3982 | 918 | 2055 | 3509 | 740 | 123 | 739 | 148 | 0 | 0 | 102.12
24:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 354 |  | 0 | 370 | 150 | 100 | 80 | 42 | 0 | 0 | 91 | 0 | 100 | 76 | 150 | 49 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 88 | 35 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 102 | 60 | 97 | 50 | 15 | 32 | 0 | 110 | 0 | 275 | 300 | 210 | 8 | 75 | 29 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 11 | 33 | 22 | 144 | 157 | 48 | 20 | 0 | 86 | 43 | 28 | 44 | 110 | 158 | 65 | 87 | 0 | 140 | 0 | 0 | 10 | 280 | 24 | 11 | 0 | 300 | 0 | 0 | 191 | 0 | 149 | 0 | 22 | 17 | 142 | 424 | 115 | 85 | 0 | 0 | 160 | 17 | 0 | 52 | 113 | 100 | 0 | 17 |  | 918 | 0 | 270 | 0 | 115 | 220 | 0 | 0 | 12 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 42 | 96 | 20 | 0 | 36 | 52 | 31 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 155 | 0 | 95 | 0 | 180 | 0 | 386 | 105 | 0 | 113 | 0 | 107 | 0 | 0 | 109 | 570 |  | 7884 | 4062 | 11946 | 3950 | 918 | 2001 | 3351 | 720 | 123 | 739 | 144 | 0 | 0 | 102.12
KWH | 0 | 0 | 649000 | 2677500 | 4815400 | 1708272 | 1185408 | 0 | 7374000 |  | 0 | 8170250 | 4912465 | 2414400 | 2177616 | 983027 | 0 | 0 | 3244000 | 0 | 1990080 | 1804608 | 1715040 | 603721 | 0 | 0 | 0 | 774720 | 1110908 | 1330025 | 431712 | 600000 | 659520 | 787900 | 829500 | 365016 | 0 | 1983316 | 836000 | 2800000 | 0 | 197881 | 4859490 | 0 | 3140840 | 0 |  | 0 | 43888 | 979405 | 513840 | 1588800 | 728640 | 443616 | 429600 | 0 | 2137320 | 0 | 7006000 | 7353000 | 4654000 | 200727 | 2027600 | 651384 | 660480 | 0 | 1096410 | 0 | 102720 | 335050 | 379152 | 236700 | 810800 | 538270 | 2985600 | 3480720 | 997440 | 377784 | 11700 | 2021000 | 1045560 | 806400 | 977472 | 2662772 | 3225000 | 1444416 | 1856640 | 0 | 3339140 | 0 | 0 | 235440 | 7053600 | 540480 | 203000 | 176640 | 5324289 | 332424 | 280173 | 4531200 | 382154 | 3553340 | 106110 | 530880 | 1218240 | 3109600 | 10092000 | 2071200 | 1796976 | 0 | 24359 | 3562909 | 795047 | 0 | 234840 | 2409120 | 2369280 | 0 | 653760 |  | 22040727 | 0 | 7605792 | 0 | 1374720 | 3694080 | 0 | 0 | 73660 | 896 | 346125 | 0 | 727327 | 1319136 | 0 | 0 | 0 | 333040 | 252167 | 763200 | 491920 | 0 | 247469 | 391680 | 244990 | 464400 | 235152 | 253062 | 0 | 0 | 370900 | 0 | 0 | 0 | 0 | 4196227 | 0 | 2004 | 617280 | 4485918 | 0 | 9411181 | 1525440 | 216639 | 1618176 | 0 | 1767360 | 0 | 41374 | 1761600 | 13532000 |  | 176867722 | 80405642 | 257273364 | 94042803 | 22040727 | 45257535 | 67590385 | 13902900 | 2819316 | 8450555 | 2985600 | 183543 | 0
Fuel Cost | 0 | 0 | 947540 | 3935925 | 5345094 | 2254919.04 | 2015193.6 | 0 | 7595220 |  | 0 | 8905572.5 | 5452836.15 | 18325296 | 15003774.24 | 8316408.42 | 0 | 0 | 5612120 | 0 | 14985302.4 | 16458024.96 | 16875993.6 | 5566307.62 | 0 | 0 | 0 | 5655456 | 8587318.84 | 13114046.5 | 323784 | 450000 | 0 | 0 | 0 | 3529704.72 | 0 | 535495.32 | 225720 | 5068000 | 0 | 1838314.49 | 5296844.1 | 0 | 5339428 | 0 |  | 0 | 424396.96 | 9500228.5 | 4907172 | 13822560 | 5770828.8 | 558956.16 | 1275912 | 0 | 3163233.6 | 0 | 5184440 | 7353000 | 4281680 | 258937.83 | 2331740 | 736063.92 | 924672 | 0 | 1874861.1 | 0 | 1037472 | 3199727.5 | 481523.04 | 177525 | 1418900 | 403702.5 | 22392000 | 3689563.2 | 9056755.2 | 479785.68 | 186498 | 3314440 | 1672896 | 1435392 | 1524856.32 | 3035560.08 | 3354000 | 2845499.52 | 3546182.4 | 0 | 5776712.2 | 0 | 0 | 480297.6 | 7124136 | 405360 | 154280 | 3004646.4 | 40251624.84 | 5644559.52 | 4684492.56 | 23562240 | 6389614.88 | 34964865.6 | 1240425.9 | 4326672 | 13217904 | 21922680 | 9385560 | 18889344 | 16981423.2 | 0 | 0 | 26935592.04 | 6924859.37 | 0 | 2343703.2 | 20646158.4 | 15779404.8 | 0 | 0 |  | 126954587.52 | 0 | 7986081.6 | 0 | 10805299.2 | 51199948.8 | 0 | 0 | 772693.4 | 9390.08 | 3606622.5 | 0 | 1127356.85 | 12874767.36 | 0 | 0 | 0 | 3277113.6 | 2562016.72 | 6754320 | 3787784 | 0 | 2397974.61 | 3795379.2 | 2376403 | 891648 | 364485.6 | 191567.934 | 0 | 0 | 2010278 | 0 | 0 | 0 | 0 | 5539019.64 | 0 | 3006 | 10499932.8 | 5248524.06 | 0 | 9317069.19 | 15925593.6 | 3685029.39 | 15356490.24 | 0 | 13714713.6 | 0 | 457182.7 | 13018224 | 59405480 |  | 604217157.32 | 395915983.194 | 1000133140.514 | 108452789.154 | 126954587.52 | 53955278.11 | 527129454.54 | 61415758 | 761215.32 | 97187951.27 | 22392000 | 1884106.6 | 0
Yesterday Day Peak | 0 | 0 | 0 | 115 | 200 | 73 | 67 | 0 | 312 |  | 0 | 400 | 275 | 100 | 95 | 40 | 0 | 0 | 120 | 0 | 100 | 94 | 48 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 87 | 35 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 7 | 0 | 0 | 40 | 15 | 20 | 7 | 0 | 80 | 0 | 280 | 300 | 184 | 8 | 85 | 29 | 30 | 0 | 43 | 0 | 0 | 8 | 18 | 11 | 33 | 21 | 108 | 149 | 40 | 20 | 1 | 84 | 43 | 44 | 41 | 110 | 140 | 63 | 86 | 0 | 140 | 0 | 0 | 10 | 270 | 24 | 8 | 0 | 225 | 0 | 0 | 190 | 0 | 137 | 11 | 22 | 0 | 120 | 419 | 109 | 86 | 0 | 4 | 160 | 23 | 0 | 0 | 99 | 100 | 0 | 35 |  | 919 | 0 | 325 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 93 | 0 | 159 | 0 | 365 | 35 | 0 | 35 | 0 | 48 | 0 | 6 | 109 | 490 |  | 10327 | DayPeak
Yesterday Evening Peak | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 349 | 0 | 0 | 370 | 10 | 100 | 96 | 40 | 0 | 0 | 120 | 0 | 100 | 94 | 150 | 88 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 30 | 33 | 33 | 51 | 0 | 85 | 35 | 115 | 0 | 25 | 210 | 0 | 139 | 0 | 0 | 0 | 0 | 102 | 90 | 97 | 50 | 20 | 21 | 0 | 80 | 0 | 300 | 300 | 197 | 8 | 79 | 29 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 11 | 33 | 22 | 146 | 140 | 48 | 20 | 0 | 82 | 43 | 28 | 47 | 110 | 158 | 64 | 87 | 0 | 140 | 0 | 0 | 10 | 310 | 24 | 11 | 50 | 300 | 50 | 97 | 200 | 100 | 149 | 0 | 22 | 181 | 137 | 418 | 115 | 86 | 0 | 0 | 161 | 54 | 0 | 17 | 113 | 100 | 0 | 17 |  | 918 | 0 | 290 | 0 | 115 | 218 | 0 | 0 | 3 | 0 | 40 | 0 | 36 | 110 | 0 | 0 | 0 | 50 | 36 | 95 | 20 | 0 | 38 | 52 | 31 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 172 | 0 | 95 | 100 | 191 | 0 | 410 | 105 | 50 | 113 | 0 | 105 | 0 | 0 | 54 | 570 |  | 12512 | EvPeak
Forecast for Evening | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 360 | 0 | 0 | 450 | 305 | 100 | 100 | 40 | 0 | 0 | 150 | 0 | 100 | 94 | 150 | 88 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 85 | 35 | 115 | 0 | 25 | 221 | 0 | 145 | 0 | 0 | 0 |  | 102 | 100 | 97 | 50 | 21 | 20 | 0 | 80 | 0 | 360 | 350 | 225 | 8 | 90 | 30 | 5 | 0 | 51 | 0 | 50 | 8 | 22 | 11 | 33 | 22 | 173 | 150 | 48 | 20 | 0 | 85 | 43 | 51 | 44 | 110 | 160 | 65 | 86 | 0 | 140 | 0 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 22 | 200 | 150 | 400 | 115 | 86 | 100 | 0 | 300 | 54 | 110 | 17 | 113 | 100 | 0 | 17 |  | 928 | 16 | 410 | 0 | 115 | 220 | 0 | 0 | 30 | 60 | 40 | 0 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 20 | 0 | 50 | 52 | 30 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 225 | 0 | 95 | 100 | 220 | 0 | 414 | 105 | 200 | 113 | 100 | 105 | 0 | 0 | 113 | 600
Forecast for Day | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 360 | 0 | 0 | 450 | 305 | 100 | 100 | 40 | 0 | 0 | 100 | 0 | 100 | 94 | 150 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 85 | 35 | 115 | 0 | 25 | 221 | 0 | 145 | 0 | 0 | 0 |  | 102 | 100 | 97 | 50 | 21 | 10 | 0 | 80 | 0 | 360 | 350 | 225 | 8 | 90 | 30 | 5 | 0 | 51 | 0 | 25 | 8 | 22 | 11 | 33 | 22 | 165 | 150 | 48 | 20 | 1.6 | 85 | 43 | 51 | 44 | 110 | 160 | 65 | 86 | 0 | 140 | 0 | 0 | 10 | 341 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 22 | 200 | 150 | 400 | 115 | 85 | 100 | 5 | 300 | 54 | 110 | 0 | 113 | 100 | 0 | 17 |  | 928 | 0 | 410 | 0 | 115 | 220 | 0 | 0 | 0 | 0 | 40 | 0 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 20 | 0 | 50 | 52 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 225 |  | 95 | 50 | 220 | 0 | 414 | 105 | 100 | 113 | 100 | 105 | 0 | 8 | 113 | 580
Generation at 08:00(Today) | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 320 | 0 | 0 | 350 | 220 |  | 48 | 15 | 0 | 0 | 75 | 0 | 16 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 19 | 25 | 9 | 33 | 33 | 0 | 0 | 82 | 35 | 115 | 0 | 0 | 209 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 19 | 6 | 0 | 80 | 0 | 295 | 300 | 216 | 8 | 75 | 26 | 5 | 0 | 51 | 0 | 0 | 8 | 16 | 11 | 33 | 15 | 90 | 154 | 48 | 20 | 0 | 86 | 43 | 28 | 20 | 110 | 159 | 40 | 20 | 0 | 140 | 0 | 0 | 10 | 290 | 24 | 0 | 0 | 15 | 0 | 0 | 200 | 0 | 149 | 4 | 22 | 0 | 60 | 420 | 8 | 68 | 0 | 1 | 70 | 17 | 0 | 0 | 26 | 100 | 0 | 17 | 0 | 919 | 0 | 290 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 95 | 0 | 130 | 0 | 344 | 53 | 0 | 0 | 0 | 41 | 0 | 2 | 35 | 500 | 0
199
| Minimum Generation |  | 8928 | 7:00
| Highest Generation |  | 12512 | 19:30
| Day Peak Generation |  | 10327 | 12:00
| Evening Peak Generation |  | 12512 | 19:30
| HVDC Max Flow |  | 919 | 1:00
| HVDC EvPeak Flow |  | 918 | 19:30
| Load factor L.F |  | 85.68%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-10-19
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-10-18 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10327 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 8862 | MW
Evening Peak Generation : |  | 12512 | MW Hour : | 19:30 | Available Max Generation : |  | 14726 | MW
E.P. Demand (at gen end) : |  | 12512 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 12800 | MW
Maximum Generation : |  | 12512 | MW Hour : | 19:30 | Reserve(Generation end) |  | 1926 | MW
Total Gen. (MKWH) : |  | 257.2734 | System Load Factor : | 85.68% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 13 | MW at | 5:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-10-19
Actual : | 102.11 | Ft.(MSL) , | Rule curve : | 107.7 | Ft.( MSL )
Gas Consumed : | Total = | 1184.86 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 162408067.264
: |  | Coal : | 61415758 | Oil : | 624317405.81 | Total : | 848141231.074
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4531.6031 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1545.2274 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1385.2265 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1251.9367 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1131.2095 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 912.8567 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 504.9792 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 234.8919 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 704.0665 |  |  | 0 | 0%
Total | 0 |  | 12201.9976 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Baghabari-71 MW,100 MW
3) Ghorasal Unit-1,2,3
4) Ashuganj unit-3,4
5) Kaptai-2,4
6) Raozan #2
7) Siddirganj-335 MW
8) Haripur 412 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Agargaon-Cantonment 132 kV Ckt-1 was under shut down from 08:49 to 12:33 for A/M.
b) HVDC filter 20DF24 was under shut down from 08:23 to 15:31 for A/M.
c) Saidpur 132/33 kV T-5 transformer was under shut down from 08:45 to 15:10 for A/M.
d) Palashbari 132/33 kV T-1 transformer was under shut down from 08:05 to 15:14 for A/M.
e) Jholdhaka 132/33 kV T-1 transformer was under shut down from 08:25 to 16:50 for A/M.
f) Kurigram 132/33 kV T-1 transformer was under shut down from 09:30 to 18:30 for A/M.
g) Thakurgaon 132/33 kV T-1 transformer was under shut down from 08:40 to 16:25 for A/M.
h) Sirajganj 132/33 kV T-3 transformer was under shut down from 09:35 to 17:46 for A/M.
i) Bheramara 230/132 kV T-1 transformer was under shut down from 08:44 to 15:42 for C/M.
j) Kishorganj 132/33 kV T-1 transformer was under shut down from 09:20 to 11:42 for C/M.
l) Kishorganj 132/33 kV T-2 transformer was under shut down from 11:50 to 12:40 for C/M.
m) Tangail 132/33 kV T-2 transformer was under shut down from 08:01 to 10:39 for A/M.
n) Hasnabad 230/132 kV T-2 transformer was under shut down from 09:40 to 16:46 for A/M.
o) Bogura 132/33 kV T-3 transformer was under shut down from 08:24 to 21:05 for A/M.
p) Sunamganj 132/33 kV T-1 transformer was under shut down from 08:50 to 16:22 for DS alignment.
q) Khulna©-Khulna-225 MW 132 kV Ckt-2 was under shut down from 11:28 to 12:41 due to high temperature
at CT DS at Khulna© end.
r) Agargaon-Cantonment 132 kV Ckt-2 was under shut down from 12:39 to 15:00 for A/M.
s) Khulna©-Khulna-225 MW 132 kV Ckt-1 was under shut down from 12:42 to 13:35 due to high temperature
at CT DS at Khulna© end.
t) Kaliakoir-Tangail 132 kV Ckt-2 tripped at 14:01 showing dist.Z2,Z3 at Kaliakoir end & dist.Z1 at Tangail
end and was switched on at 14:39.
u) Summit Megnaghat-305 MW CCPP ST tripped at 17:12 due to auxiliary failure.
v) Ghorasal #4 GT was synchronized at 17:25.
w) Mymensing 132/33 kV T-3 transformer was switched on at 15:55.
x) Baraulia-Hathazari 132 kV Ckt-1 & 2 are shut down since 06:05(19/10/20) for C/M.
y) Kabirpur 132 kV main Bus is under shut down since 06:26 to 06:39(19/10/20) for D/W. |  |  |  |  | About 60 MW power interruption occurred under Kabirpur S/S area
z) Kabirpur-Kaliakoir 132 kV Ckt-2 is shut down since 08:39(19/10/20) for D/W. |  |  |  |  | from 06:52 to 07:58.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-10-18 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 100 | 649000 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 115 | 2677500 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 4815400 | Machin problem.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 1185408 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 72 | 1708272 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 349 | 7374000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 370 | 8170250 | Frequency control.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 2414400
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 10 | 4912465 | Tripped at 17:12.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 96 | 2177616
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 40 | 983027 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 88 | 603721
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 431712 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 120 | 3244000
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 1990080
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under Maintenance
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 94 | 1804608 | Fuel Shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel Shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 774720
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1715040
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1110908
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1330025
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1259520 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 787900
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 829500
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 365016
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 5324289
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 50 | 332424 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 97 | 280173
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 100 | 382154
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3553340
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 86 | 1796976 | Engine problem
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 653760 | Fuel Shortage
| Dhaka area Total |  |  |  | 5895 | 3139 | 65637204
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 115 | 2800000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | S/D due to gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 197881
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 106110
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 728640
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 120 | 2819316 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 210 | 4859490
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 139 | 3140840
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Transformer overload
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 43888 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 979405
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 90 | 513840
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 22 | 530880 | Machin problem.
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 443616
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 21 | 429600
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 97 | 1588800 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 24359
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 161 | 3562909 | Transformer O/L.
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 795047
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Transformer O/L.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2369280
| Chattogram area Total |  |  |  | 2266 | 1326 | 25933901
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 80 | 2137320 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 197 | 4654000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 300 | 7006000 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 300 | 7353000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 651384 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 660480 | Gas shortage
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1096410
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 137 | 3109600
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 102720 | Reserve.
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 79 | 2027600
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 181 | 1218240 | Engine problem
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 379152
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 236700
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 146 | 2985600
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 810800
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 335050 | Fuel Shortage
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 22 | 538270
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 50 | 176640 | Low demand
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 234840 | Fuel Shortage
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 2409120
| Cumilla Area Total |  |  |  | 2980 | 1786 | 38323653
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 140 | 3480720 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 377784 | Engine problem
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 48 | 997440 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11700
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 4531200
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2071200 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 523 | 11470044
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 82 | 2021000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 1045560 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2662772 | Engine problem
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 158 | 3225000 | FGMO & GT-2 under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 28 | 806400 | Engine problem
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 47 | 977472
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 203000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 64 | 1444416 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 87 | 1856640
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 140 | 3339140 | Machin problem.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 540480
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7053600 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 418 | 10092000
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 235440
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1532 | 35502920
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 918 | 22040727
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 1374720
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 3 | 73660 | Low demand
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 218 | 3694080
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 896 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 290 | 7605792 | Gas shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 346125
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 617280
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1525440
107 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Line O/L.
| Khulna Area Total |  |  |  | 2284 | 1789 | 37278720
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1319136
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 36 | 727327
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 95 | 2004
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 570 | 13532000 | Line O/L.
| Barisal Area Total |  |  |  | 1054 | 811 | 15580467
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 333040
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 36 | 252167
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 20 | 491920 | Engine problem
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel Shortage
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 247469
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas Shortage
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 172 | 4196227 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 191 | 4485918 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 410 | 9411181 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 31 | 244990
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 18 | 464400
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 10 | 235152
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 253062
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 391680
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 95 | 763200
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 50 | 216639 | Low demand
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 1618176
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 54 | 1761600 | Engine problem
| Rajshahi Area Total |  |  |  | 2183 | 1351 | 25366821
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 370900 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 105 | 1767360 | Engine problem
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 41374
| Rangpur Area Total |  |  |  | 605 | 255 | 2179634
| Total |  |  |  | 19892 | 12512 | 257273364
| Eastern Grid Total |  |  |  | 13766 | 8306 | 176867722
| Western Grid Total |  |  |  | 6126 | 4206 | 80405642
| National Grid Total |  |  |  | 19892 | 12512 | 257273364
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-10-18
| (a) ENTIRE EASTERN GRID : |  | 8015 | MW | (b) ENTIRE WESTERN GRID : |  | 3902 | MW
| i) Dhaka area |  | 4227 | MW | i) Khulna area |  | 1532 | MW
| ii) Chittagong area |  | 1124 | MW | ii) Rajshahi area |  | 1279 | MW
| iii) Comilla area |  | 1158 | MW | iii) Barisal area |  | 341 | MW
| iv) Mymensingh area |  | 981 | MW | iv) Rangpur area |  | 750 | MW
| v) Sylhet area |  | 525 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11917 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 130 | 12:00 | Sherpur | 110 | 1:00 | Jhenida | 113 | 18:30
| Munsiganj | 126 | 23:00 | Srimongal | 51 | 21:00 | Bottail | 130 | 19:30
| Sonargaon | 84 | 20:00 | Shahjibazar | 120 | 21:00 | G.K Project | 57 | 19:30
| Shyampur | 198 | 10:00 | Fenchuganj | 44 | 21:00 | Faridpur | 194 | 0.79167
| Bhulta | 193 | 24:00 | Kulawara | 45 | 18:30 | Madaripur | 105 | 0.91667
| Madanganj | 54 | 11:00 | Sylhet | 147 | 18:00 | Sariatpur | 68 | 21:00
| Shitalakhya | 107 | 12:00 | Chatak | 32 | 20:00 | Gopalganj | 88 | 18:30
| Rahim steel | 21 | 17:00 | Sunamganj | 50 | 21:00 | Bagerhat | 100 | 18:00
| Matuail | 86 | 15:00 | Biani Bazar | 57 | 19:30 | Mongla | 32 | 1:00
| Ghorasal | 86 | 18:00 | Comilla (S) | 150 | 18:30 | Satkhira | 114 | 0.875
| Narsingdi | 174 | 20:00 | Comilla(N) | 125 | 19:00 | Gallamari | 48 | 1:00
| Haripur (SBU) | 108 | 10:00 | Chandpur | 104 | 21:00 | Magura | 52 | 0.8125
| Ullon | 62 | 19:30 | Feni | 114 | 18:30 | Norail | 41 | 19:00
| Hasnabad | 220 | 20:00 | Chowmuhani | 174 | 19:30 | Chuadanga | 95 | 19:30
| Magbazar | 107 | 15:00 | Ashuganj | 58 | 22:00 | Barisal(N) | 49 | 0.875
| Maniknagar | 106 | 16:00 | Daudkandi | 150 | 23:00 | Barisal (S) | 100 | 0.75
| Bangabhaban | 38 | 10:00 | B.Baria | 157 | 21:00 | Patuakhali | 122 | 0.041667
| Narinda | 90 | 16:00 | Ramganj | 108 | 21:00 | Bhandaria | 56 | 0.83333
| Dhanmondi | 193 | 13:00 | Chaddagram | 35 | 18:30 | Borhan Uddin | 43 | 1:00
| Lalbag | 94 | 13:00 | PHP | 9 | 19:30 | Ishurdi | 61 | 20:00
| Madartek | 75 | 23:00 | Madunaghat | 57 | 18:00 | Ruppur Paromanobik | 2 | 20:00
| Dhaka University |  |  | Hathazari | 102 | 0.75 | Natore | 124 | 21:00
| Fatullah | 42 | 0.66667 | Khulshi | 188 | 0 | Bogra | 155 | 21:00
| Mirpur | 110 | 18:00 | Halishahar | 144 | 0.625 | Noagaon | 118 | 21:00
| Kalyanpur | 111 | 18:00 | Baraulia | 169 | 0.95833 | Rajshahi | 150 | 21:00
| Gulshan | 140 | 18:00 | Sikalbaha | 27 | 0.75 | Rajshahi New | 14 | 21:00
| Uttara | 101 | 18:00 | Dohazari | 84 | 0.041667 | C.Nawabganj | 74 | 21:00
| Uttara New | 40 | 18:00 | Cox'sbazar | 104 | 0.79167 | Amnura | 46 | 21:00
| Kamrangirchar | 97 | 18:00 | Chandraghona | 42 | 0.16667 | Pabna | 128 | 19:30
| Savar | 145 | 18:00 | Kaptai | 4.2 | 0.83333 | Shahjadpur | 108 | 21:00
| Bhasantec | 147 | 18:00 | A. Khaer Stl. | 10 | 0.125 | Serajganj | 114 | 19:30
| Agargaon | 77 | 18:00 | Bakulia | 110 | 0.79167 | Niyamatpur | 56 | 21:00
| Satmosjid | 88 | 18:00 | Julda | 18 | 0.041667 | Joypurhat | 59 | 21:00
| Tongi | 120 | 0.625 | TK chemical | 29 | 0.83333 | Sherpur(Bogura) | 49 | 21:00
| Kabirpur | 236 | 18:00 | Modern Steel | 13 | 0.041667 | Mohastangor | 62 | 19:30
| Basundhara | 157 | 13:00 | Shahmirpur | 24 | 0.75 | Rangpur | 142 | 18:00
| Manikganj | 72 | 21:00 | Khagrachhari | 24 | 0 | Lalmonirhat | 48 | 20:00
| Joydevpur | 166 | 18:00 | Matarbari | 37 | 0.8125 | Saidpur | 101 | 18:00
| New Tongi | 111 | 15:00 | Baroiar Hat | 46 | 0.75 | Purbasadipur | 103 | 18:30
| Kodda | 237 | 18:30 | Rangamati | 12 | 0.75 | Thakurgaon | 79 | 20:00
| Dhamrai | 94 | 19:00 | Abul Khair 230 | 36 | 0.70833 | Palashbari | 123 | 19:00
| Rajendrapur | 106 | 18:30 | BSRM | 56 | 0.41667 | Barapukuria | 52 | 19:30
| Valuka | 116 | 9:00 | GPH Ispat | 71 | 0.375 | Panchagar | 50 | 21:00
| Tangail | 203 | 21:00 | Goalpara | 30 | 0.041667 | Joldhaka | 35 | 18:30
| Mymensing | 226 | 19:30 | Central s/s | 87 | 18:00 | Kurigram | 55 | 18:00
| Kishorganj | 156 | 20:00 | Noapara | 64 | 18:30
| Netrokona | 112 | 18:00 | Jessore | 112 | 18:30
| Jamalpur | 141 | 21:00 | Benapol | 50 | 18:00
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-10-18 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 407 | 6:00 | 397 | 11:00 | Kaliakoir | 398 | 0.20833 | 386 | 0.41667
| Bheramara | 394 | 6:00 | 387 | 1:00 | Bhulta | 376 | 0.25 | 358 | 0.66667
| Ashuganj(N) | 381 | 4:00 | 368 | 11:00 | Gopalganj | 408 | 0.70833 | 387 | 0.875
| Payra | 417 | 4:00 | 405 | 18:30
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 222 | 14:00 | Comilla (N) | 230 | 5:00 | 223 | 17:00
| Ishurdi | 233 | 9:00 | 224 | 21:00 | Hathazari | 224 | 24:00 | 219 | 15:00
| Ashuganj | 234 | 4:00 | 226 | 16:00 | Megnaghat | 224 | 6:00 | 214 | 16:00
| Serajganj | 230 | 4:00 | 225 | 18:30 | Fenchuganj | 241 | 3:00 | 235 | 1:00
| Baghabari | 238 | 5:00 | 235 | 19:30 | Siddhirganj | 223 | 6:00 | 213 | 15:00
| Barapukuria | 237 | 17:00 | 227 | 18:30 | Maniknagar | 222 | 3:00 | 211 | 16:00
| Bogra | 225 | 17:00 | 214 | 21:00 | Agargaon | 218 | 17:00 | 205 | 11:00
| Rajshahi | 222 | 24:00 | 214 | 3:00 | Barisal | 250 | 19:30 | 214 | 6:00
| Khulna South | 229 | 17:00 | 215 | 4:00 | AKSML | 220 | 1:00 | 215 | 15:00
| Rampura | 221 | 3:00 | 214 | 16:00 | BSRM | 221 | 1:00 | 216 | 10:00
| Haripur | 221 | 4:00 | 212 | 11:00 | Bibiyana | 241 | 3:00 | 234 | 11:00
| Hasnabad | 220 | 2:00 | 210 | 11:00 | Bhulta | 224 | 19:00 | 214 | 17:00
| Shyampur | 219 | 4:00 | 206 | 17:00 | Ashuganj (S) | 230 | 2:00 | 223 | 12:00
| Aminbazar | 218 | 4:00 | 207 | 11:00 | Kaliakoir | 220 | 3:00 | 208 | 17:00
| Tongi | 216 | 4:00 | 208 | 10:00 | GPH | 220 | 3:00 | 217 | 4:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 133 | 3:00 | 127 | 11:00 | Hathazari | 133 | 0.77083 | 131 | 0.041667
| Munsiganj | 133 | 6:00 | 127 | 12:00 | Khulshi | 133 | 0.83333 | 127 | 0.41667
| Sonargaon | 131 | 2:00 | 127 | 15:00 | Halishahar | 134 | 0.8125 | 128 | 0.41667
| Shyampur | 134 | 2:00 | 127 | 11:00 | Baraulia | 134 | 0.79167 | 127 | 0.375
| Bhulta | 126 | 6:00 | 120 | 11:00 | Sikalbaha | 135 | 18:30 | 130 | 0.45833
| Madanganj | 135 | 19:30 | 126 | 12:00 | Dohazari | 132 | 18:30 | 125 | 0.45833
| Shitalakhya | 143 | 20:00 | 128 | 16:00 | Cox'sbazar | 124 | 0.66667 | 118 | 0.041667
| Rahim steal | 133 | 4:00 | 127 | 11:00 | Chandraghona | 134 | 0 | 130 | 0.54167
| Matuail | 133 | 3:00 | 127 | 11:00 | Kaptai | 133 | 18:30 | 130 | 0.41667
| Ghorasal | 135 | 1:00 | 133 | 14:00 | A. Khaer Stl. | 132 | 0.875 | 127 | 13:00
| Narsinghdi | 130 | 8:00 | 121 | 12:00 | Bakulia | 134 | 0.875 | 128 | 0.45833
| Haripur (SBU) | 134 | 1:00 | 127 | 12:00 | Julda | 136 | 0.77083 | 129 | 0.29167
| Ullon | 135 | 4:00 | 127 | 11:00 | TK Chemical | 135 | 0.83333 | 129 | 10:00
| Hasnabad | 137 | 1:00 | 127 | 11:00 | Modern Steel | 133 | 0.75 | 128 | 0.41667
| Magbazar | 136 | 5:00 | 126 | 16:00 | Shahmirpur | 135 | 0.77083 | 129 | 0.45833
| Maniknagar | 133 | 4:00 | 124 | 16:00 | Khagrachhari | 133 | 0 | 129 | 0.45833
| Bangabhaban | 133 | 4:00 | 124 | 16:00 | Matarbari | 125 | 0.66667 | 120 | 0.20833
| Narinda | 133 | 4:00 | 124 | 16:00 | Baroiar Hat | 131 | 0.29167 | 127 | 0.041667
| Dhanmondi | 135 | 4:00 | 127 | 11:00 | Rangamati | 133 | 0.79167 | 130 | 10:00
| Lalbag | 138 | 20:00 | 122 | 16:00 | Goalpara S/S | 139 | 17:00 | 131 | 4:00
| Madartek | 135 | 3:00 | 126 | 16:00 | Khulna Central S/S | 139 | 0.95833 | 133 | 2:00
| Dhaka University |  |  |  |  | Noapara | 135 | 17:00 | 128 | 5:00
| Fatuiiah | 135 | 0.25 | 127 | 11:00 | Jessore | 131 | 17:00 | 125 | 21:00
| Mirpur | 133 | 6:00 | 123 | 10;00 | Benapol | 132 | 17:00 | 122 | 3:00
| Kalyanpur | 133 | 6:00 | 125 | 10;00 | Jhenida | 128 | 0.70833 | 117 | 21:00
| Gulshan | 135 | 6:00 | 127 | 10;00 | Bottail | 134 | 17:00 | 127 | 21:00
| Uttara | 132 | 6:00 | 123 | 10;00 | G.K Project | 141 | 0.70833 | 137 | 1:00
| Uttara New | 130 | 6:00 | 122 | 10;00 | Faridpur | 133 | 8:00 | 125 | 18:30
| Kamrangirchar | 134 | 6:00 | 123 | 10;00 | Madaripur | 138 | 0.70833 | 128 | 21:00
| Savar | 132 | 4:00 | 122 | 12:00 | Shariyatpur S/S | 137 | 0.41667 | 126 | 21:00
| Bhasantec | 135 | 6:00 | 134 | 12:00 | Gopalganj | 137 | 7:00 | 125 | 18:30
| Agargaon | 136 | 6:00 | 126 | 12:00 | Bagerhat | 135 | 13:00 | 122 | 4:00
| Satmosjid | 136 | 6:00 | 126 | 10;00 | Mongla | 132 | 0.625 | 122 | 3:00
| Tongi | 132 | 0.875 | 125 | 15:00 | Satkhira | 137 | 0.70833 | 128 | 3:00
| Kabirpur | 132 | 7:00 | 126 | 11:00 | Gallamari | 139 | 17:00 | 130 | 4:00
| Basundhara | 135 | 3:00 | 126 | 15:00 | Magura | 125 | 7:00 | 115 | 21:00
| Manikganj | 133 | 24:00 | 126 | 15:00 | Norail | 126 | 0.70833 | 114 | 21:00
| Joydevpur | 139 | 23:00 | 128 | 16:00 | Chuadanga | 122 | 17:00 | 106 | 21:00
| New Tongi | 131 | 1904-01-02 | 123 | 16:00 | Barisal(N) | 140 | 17:00 | 123 | 6:00
| Kodda | 139 | 18:30 | 126 | 0.66667 | Barisal (S) | 139 | 0.70833 | 119 | 6:00
| Dhamrai | 132 | 6:00 | 126 | 21:00 | Patuakhali(S) | 134 | 0.70833 | 122 | 6:00
| Rajendrapur | 137 | 15:00 | 126 | 16:00 | Bhandaria | 131 | 15:00 | 119 | 1:00
| Valuka | 123 | 11:00 | 110 | 18:00 | Ishurdi | 138 | 17:00 | 133 | 21:00
| Tangail | 130 | 6:00 | 120 | 19:30 | Ruppur Paromanobik | 136 | 6:00 | 132 | 21:00
| Mymensing | 127 | 10:00 | 114 | 18:00 | Natore | 136 | 8:00 | 130 | 21:00
| Kishorganj | 128 | 9:00 | 115 | 20:00 | Bogra | 136 | 17:00 | 127 | 21:00
| Netrokona | 124 | 11:00 | 110 | 18:00 | Noagaon | 132 | 17:00 | 119 | 21:00
| Jamalpur | 139 | 15:00 | 128 | 18:00 | Rajshahi | 135 | 17:00 | 129 | 5:00
| Sherpur | 138 | 15:00 | 126 | 1:00 | Rajshahi New | 136 | 17:00 | 130 | 4:00
| Srimongal | 137 | 9:00 | 131 | 0.91667 | C.Nawabganj | 133 | 17:00 | 127 | 4:00
| Shahjibazar | 135 | 9:00 | 129 | 0.66667 | Amnura | 134 | 17:00 | 129 | 5:00
| Fenchuganj | 135 | 5:00 | 131 | 0.041667 | Pabna | 134 | 6:00 | 130 | 21:00
| Khulawara | 135 | 6:00 | 130 | 0.041667 | Shahjadpur | 137 | 18:00 | 135 | 21:00
| Sylhet | 132 | 7:00 | 128 | 0.75 | Serajganj | 132 | 6:00 | 127 | 21:00
| Chatak | 130 | 8:00 | 122 | 1:00 | Niyamatpur | 129 | 7:00 | 116 | 21:00
| Sunamganj | 129 | 6:00 | 118 | 0.91667 | Joypurhat | 131 | 17:00 | 117 | 21:00
| Biani Bazar | 131 | 8:00 | 125 | 0.75 | Sherpur(Bogura) | 135 | 17:00 | 126 | 20:00
| Comilla(s) | 128 | 7:00 | 120 | 18:00 | Mohastangor | 135 | 17:00 | 124 | 21:00
| Comilla(n) | 135 | 7:00 | 130 | 15:00 | Rangpur | 132 | 17:00 | 116 | 18:30
| Chandpur | 135 | 18:30 | 130 | 0:00 | Lalmonirhat | 130 | 6:00 | 117 | 19:00
| Feni | 132 | 8:00 | 125 | 15:00 | Saidpur | 131 | 17:00 | 117 | 18:00
| Chowmuhani | 133 | 7:00 | 127 | 24:00 | Purbasadipur | 128 | 17:00 | 112 | 18:30
| Ashuganj | 134 | 7:00 | 130 | 18:00 | Thakurgaon | 126 | 17:00 | 112 | 18:30
| Daudkandi | 134 | 18:30 | 125 | 15:00 | Palashbari | 130 | 7:00 | 120 | 21:00
| B.Baria | 132 | 9:00 | 124 | 19:00 | Barapukuria | 137 | 17:00 | 127 | 19:30
| Ramganj | 130 | 9:00 | 122 | 24:00 | Panchagar | 124 | 17:00 | 106 | 18:30
| Chaddagram | 133 | 7:00 | 128 | 16:00 | Joldhaka | 130 | 7:00 | 114 | 18:30
| PHP | 131 | 8:00 | 126 | 15:00 | Kurigram | 126 | 6:00 | 112 | 18:30
| Madanhat | 135 | 6:00 | 132 | 7:00

## L-Curve
Date | 2020-10-18
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 120 | 7884 | 4062 | 11946 |  |  |  | QF-LDC-11
0:30 | 140 | 7930 | 3978.5 | 11908.5 | Date: | 2020-10-18
1:00 | 160 | 7976 | 3895 | 11871
1:30 | 146 | 7835.5 | 3810.5 | 11646
2:00 | 132 | 7695 | 3726 | 11421
2:30 | 93 | 7600 | 3656.5 | 11256.5 | [5 empty] | Gen. at Eve. Peak | 12512 | 12512 MW (19:30 )
3:00 | 54 | 7505 | 3587 | 11092 | [6 empty] | 19:30
3:30 | 45 | 7443.5 | 3496.5 | 10940 | [5 empty] | Gen. at Day Peak | 10327 | 10327 MW (12:00 )
4:00 | 36 | 7382 | 3406 | 10788 | [6 empty] | 12:00
4:30 | 24.5 | 7179.5 | 3387 | 10566.5 | [5 empty] | Highest Generation | 12512
5:00 | 13 | 6977 | 3368 | 10345 | [6 empty] | 19:30
5:30 | 69 | 6738.5 | 3187 | 9925.5
6:00 | 125 | 6500 | 3006 | 9506
6:30 | 157.5 | 6275 | 2942 | 9217
7:00 | 190 | 6050 | 2878 | 8928
7:30 | 227 | 6050 | 2895.5 | 8945.5
8:00 | 264 | 6050 | 2913 | 8963
8:30 | 242 | 6271.5 | 2924.5 | 9196
9:00 | 220 | 6493 | 2936 | 9429
9:30 | 287.5 | 6647 | 2973 | 9620
10:00 | 355 | 6801 | 3010 | 9811
10:30 | 340 | 6896 | 3038 | 9934
11:00 | 325 | 6991 | 3066 | 10057
11:30 | 278.5 | 7108.5 | 3083.5 | 10192
12:00 | 232 | 7226 | 3101 | 10327
12:30 | 184 | 7315.5 | 3138 | 10453.5
13:00 | 136 | 7405 | 3175 | 10580
13:30 | 162 | 7260 | 3189.5 | 10449.5
14:00 | 188 | 7115 | 3204 | 10319
14:30 | 243 | 7226 | 3249 | 10475
15:00 | 298 | 7337 | 3294 | 10631
15:30 | 354 | 7190.5 | 3250 | 10440.5
16:00 | 410 | 7044 | 3206 | 10250
16:30 | 385 | 6919 | 3118 | 10037
17:00 | 360 | 6794 | 3030 | 9824
17:30 | 222.5 | 7445.5 | 3426.5 | 10872
18:00 | 85 | 8097 | 3823 | 11920
18:30 | 77.5 | 8186 | 3993.5 | 12179.5
19:00 | 70 | 8275 | 4164 | 12439
19:30 | 90 | 8306 | 4206 | 12512
20:00 | 70 | 8262 | 4234 | 12496 |  |  |  | Executive Engineer
20:30 | 59 | 8221 | 4217.5 | 12438.5 |  |  |  | Network Operation Division
21:00 | 48 | 8180 | 4201 | 12381
21:30 | 96.5 | 8094.5 | 4221 | 12315.5
22:00 | 145 | 8009 | 4241 | 12250 |  |  |  |  | Page 6 of 7
22:30 | 174 | 8005.5 | 4226.5 | 12232
23:00 | 203 | 8002 | 4212 | 12214
23:30 | 161.5 | 7943 | 4137 | 12080
24:00 | 120 | 7884 | 4062 | 11946
12512 MW (19:30 )
10327 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-10-18 |  | Energy | 257273364
[10 empty] | 2020-10-18 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3950 | 918 | 2001 | 3509 | 720 | 123 | 739 | 0 | 144
0:30 | 3949.5 | 918.5 | 2060.5 | 3413 | 725 | 123 | 655 | 0 | 143 | Date: | 2020-10-18
1:00 | 3949 | 919 | 2120 | 3317 | 730 | 123 | 571 | 0 | 142
1:30 | 3952.5 | 918.5 | 2132 | 3204 | 730 | 122 | 448 | 0 | 139 | [7 empty] | Total Energy | 257.2734 | Total Energy Gen 257.273 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 257.273 MKWHr
2:00 | 3956 | 918 | 2144 | 3091 | 730 | 121 | 325 | 0 | 136 | [7 empty] | Energy not Served | 0
2:30 | 3940 | 918.5 | 2149.5 | 2999.5 | 730.5 | 120 | 263.5 | 0 | 135 | [7 empty] | Energy Requirement | 257.2734
3:00 | 3924 | 919 | 2155 | 2908 | 731 | 119 | 202 | 0 | 134
3:30 | 3940.5 | 919 | 2157.5 | 2754 | 730.5 | 118.5 | 186 | 0 | 134 | [6 empty] | Shortage
4:00 | 3957 | 919 | 2160 | 2600 | 730 | 118 | 170 | 0 | 134
4:30 | 3948.5 | 919 | 2167.5 | 2397.5 | 720 | 117 | 170 | 0 | 127
5:00 | 3940 | 919 | 2175 | 2195 | 710 | 116 | 170 | 0 | 120
5:30 | 3888 | 919 | 2050 | 1980 | 695 | 116 | 166.5 | 0 | 111
6:00 | 3836 | 919 | 1925 | 1765 | 680 | 116 | 163 | 0 | 102
6:30 | 3766.5 | 919 | 1832.5 | 1662 | 675 | 117 | 149.5 | 0 | 94 |  |  |  |  | Coal
7:00 | 3697 | 919 | 1740 | 1559 | 670 | 118 | 136 | 0 | 86
7:30 | 3691.5 | 919 | 1745 | 1569 | 670 | 118.5 | 136 | 0 | 89 |  |  |  | Oil |  |  |  | ,
8:00 | 3686 | 919 | 1750 | 1579 | 670 | 119 | 136 | 0 | 92
8:30 | 3729 | 919 | 1787 | 1722.5 | 660 | 120 | 152 | 0 | 90
9:00 | 3772 | 919 | 1824 | 1866 | 650 | 121 | 168 | 0 | 88
9:30 | 3789.5 | 919 | 1894 | 1971 | 645 | 121.5 | 168 | 0 | 89
10:00 | 3807 | 919 | 1964 | 2076 | 640 | 122 | 168 | 0 | 90
10:30 | 3834 | 919 | 1984.5 | 2147 | 640 | 122 | 168 | 0 | 94
11:00 | 3861 | 919 | 2005 | 2218 | 640 | 122 | 168 | 0 | 98
11:30 | 3846 | 919 | 2006 | 2360.5 | 640 | 122 | 171.5 | 0 | 103
12:00 | 3831 | 919 | 2007 | 2503 | 640 | 122 | 175 | 0 | 108
12:30 | 3853 | 919 | 2015.5 | 2591 | 640 | 122.5 | 175.5 | 0 | 110
13:00 | 3875 | 919 | 2024 | 2679 | 640 | 123 | 176 | 0 | 112
13:30 | 3875 | 919 | 2024 | 2679 | 640 | 123 | 176 | 0 | 112
14:00 | 3875 | 919 | 2024 | 2679 | 640 | 123 | 176 | 0 | 112
14:30 | 3896.5 | 919 | 2005 | 2699.5 | 670 | 119.5 | 160 | 0 | 115
15:00 | 3918 | 919 | 1986 | 2720 | 700 | 116 | 144 | 0 | 118
15:30 | 3866.5 | 919 | 1939.5 | 2636 | 690 | 115.5 | 145 | 0 | 122
16:00 | 3815 | 919 | 1893 | 2552 | 680 | 115 | 146 | 0 | 126
16:30 | 3727.5 | 919 | 1789 | 2565 | 635 | 115 | 162 | 0 | 122
17:00 | 3640 | 919 | 1685 | 2578 | 590 | 115 | 178 | 0 | 118
17:30 | 3796 | 918.5 | 1882 | 3032.5 | 610 | 116 | 387.5 | 0 | 129
18:00 | 3952 | 918 | 2079 | 3487 | 630 | 117 | 597 | 0 | 140
18:30 | 3939.5 | 917.5 | 2055.5 | 3652 | 670 | 118 | 682 | 0 | 145
19:00 | 3927 | 917 | 2032 | 3817 | 710 | 119 | 767 | 0 | 150
19:30 | 3974 | 918 | 2037 | 3874 | 720 | 120 | 723 | 0 | 146
20:00 | 3942 | 918 | 2036 | 3859 | 739 | 120 | 734 | 0 | 148
20:30 | 3969 | 918 | 2038 | 3773.5 | 739.5 | 121.5 | 735 | 0 | 144
21:00 | 3996 | 918 | 2040 | 3688 | 740 | 123 | 736 | 0 | 140
21:30 | 3997 | 918 | 2038.5 | 3615.5 | 740.5 | 123 | 739 | 0 | 144
22:00 | 3998 | 918 | 2037 | 3543 | 741 | 123 | 742 | 0 | 148
22:30 | 3990 | 918 | 2046 | 3526 | 740.5 | 123 | 740.5 | 0 | 148
23:00 | 3982 | 918 | 2055 | 3509 | 740 | 123 | 739 | 0 | 148
23:30 | 3966 | 918 | 2028 | 3509 | 730 | 123 | 739 | 0 | 146 | Max Temp. in Dhaka |  | 34.4° C
24:00 | 3950 | 918 | 2001 | 3509 | 720 | 123 | 739 | 0 | 144
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 257.273 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 257.273 MKWHr
Note on W13: Author:

## Generation
g | 2020-10-18
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 88 | 86 | 84 | 83 | 81 | 81 | 83 | 84 | 86 | 87 | 87 | 87 | 88 | 88 | 81 | 80 | 80 | 82 |  | 84 | 85 | 85 | 88 | 88 | 88 | 88 | 1983316
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 836000
3 | Chattogram TPP-1 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 110 | 110 | 110 | 110 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | 0 | [14 empty] | 14 |  | 24 | 25 | 25 | 25 | 25 | 25 | 25 | 197881
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 9 | 15 | 17 | 14 | 11 | 19 | 16 | 4 |  | 0 | [9 empty] | 106110
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 228 | 204 | 204 | 204 | 204 | 217 | 204 | 204 |  | 204 | 210 | 204 | 204 | 206 | 204 | 204 | 4859490
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 140 | 140 | 140 | 139 | 139 | 138 | 100 | 100 | 140 | 139 | 140 | 139 | 140 | 104 | 139 | 111 | 104 | 139 |  | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 3140840
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 102 | 34 | 34 | 34 | 34 | 27 |  |  |  | 0 | [7 empty] | 102 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 979405
12 | Hathazari 100 MW peaking PP | [11 empty] | 7 | 8 | 8 | 8 | 8 | 8 | [9 empty] | 43888
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [17 empty] | 90 |  | 50 | 50 | 50 |  |  |  |  | 176640
14 | Titas 50 MW Peaking PP | [17 empty] | 41 |  | 41 | [5 empty] | 0 | 102720
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 150 | 160 | 150 | 160 | 155 | 85 | 85 | 85 | 85 | 90 | 120 | 120 | 120 | 120 | 185 | 72 | 71 | 194 |  | 120 | 120 | 120 | 120 | 95 | 95 | 91 | 3244000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 300 | 300 | 300 | 295 | 30 | 30 | 15 | 17 | 45 | 105 | 130 | 225 | 300 | 300 | 300 | 245 | 200 | 220 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 5324289
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | [17 empty] | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 649000
23 | Ghorasal TPP Unit-5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2677500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4815400
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 96 | 135 | 135 | 135 | 110 | 2137320
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 651384
33 | Ashuganj 225 MW CCPP | 192 | 180 | 174 | 183 | 185 | 190 | 178 | 183 | 210 | 216 | 215 | 184 | 180 | 190 | 186 | 194 | 179 | 187 |  | 187 | 197 | 181 | 188 | 214 | 210 | 210 | 4654000
34 | Ashuganj 450 MW CCPP(South) | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 280 | 290 | 285 | 300 | 300 | 300 | 355 | 355 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7353000
| Ashuganj 450 MW CCPP(North) | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 280 | 280 | 370 | 265 | 275 | 310 | 265 | 270 |  | 265 | 300 | 275 | 280 | 285 | 275 | 275 | 7006000
35 | Ashuganj 55 MW PP (Precision) | 52 | 51 | 51 | 51 | 51 | 52 | 52 | 52 | 30 | 30 | 30 | 30 | 30 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 660480
36 | Chandpur 150 MW CCPP | 85 | 96 | 88 | 93 | 96 | 87 | 92 | 94 | 91 | 85 | 86 | 85 | 86 | 86 | 83 | 87 | 75 | 75 |  | 79 | 79 | 80 | 75 | 75 | 75 | 75 | 2027600
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 420 | 420 | 420 | 420 | 420 | 350 | 330 | 330 | 330 | 400 | 400 | 400 | 400 | 350 | 350 | 350 | 300 | 400 |  | 370 | 370 | 370 | 370 | 370 | 370 | 370 | 8170250
41 | Haripur 360MW CCPP(HPL) | 295 | 310 | 320 | 326 | 326 | 326 | 284 | 282 | 259 | 228 | 257 | 312 | 309 | 307 | 301 | 302 | 293 | 347 |  | 330 | 349 | 349 | 351 | 351 | 352 | 354 | 7374000
42 | RPCL 210MW CCPP | 157 | 155 | 157 | 157 | 157 | 157 | 156 | 154 | 152 | 150 | 149 | 149 | 149 | 137 | 138 | 137 | 139 | 141 |  | 141 | 140 | 140 | 141 | 140 | 154 | 157 | 3480720
43
44 | Fenchugonj CCPP Phase-1 | 85 | 85 | 87 | 87 | 87 | 86 | 87 | 84 | 87 | 86 | 83 | 84 | 86 | 84 | 83 | 83 | 84 | 84 |  | 84 | 82 | 84 | 84 | 84 | 86 | 86 | 2021000
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1045560
46 | Shajibazar 330 MW CCPP | 140 | 139 | 144 | 140 | 142 | 140 | 140 | 142 | 139 | 145 | 141 | 140 | 140 | 146 | 141 | 150 | 159 | 158 |  | 158 | 158 | 158 | 160 | 157 | 159 | 158 | 3225000
47 | Shahjibazar GTPP Unit- 8 & 9 | 63 | 63 | 63 | 63 | 64 | 40 | 40 | 40 | 65 | 65 | 64 | 63 | 63 | 53 | 63 | 63 | 40 | 65 |  | 65 | 64 | 65 | 61 | 65 | 65 | 65 | 1444416
48 | Shahjibazar 86MW PP (Shahjibazar) | 86 | 87 | 87 | 87 | 87 | 87 | 40 | 40 | 84 | 84 | 86 | 86 | 87 | 86 | 86 | 10 | 10 | 85 |  | 87 | 87 | 86 | 86 | 87 | 87 | 87 | 1856640
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 120 | 140 | 140 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3339140
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 235440
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 2 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 203000
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 47 | 14 | 14 | 42 | 42 | 39 | 44 | 28 | 28 | 28 | 28 | 11 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 806400
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 8 | 16 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 540480
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 280 | 290 | 275 | 280 | 270 | 270 | 290 | 270 | 290 | 290 | 270 | 290 | 290 | 315 | 290 | 290 | 300 |  | 290 | 310 | 300 | 300 | 290 | 300 | 280 | 7053600
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1330025
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 |  | 15 | 15 | 15 | 15 | 443616
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 22 |  |  |  | 22 | 22 | 22 | 22 | 22 | 431712
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 20 | 20 | 20 |  | 20 | 17 |  |  |  | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 377784
63 | Impoprt (Tripura) | 142 | 136 | 134 | 134 | 120 | 102 | 86 | 92 | 88 | 90 | 98 | 108 | 112 | 112 | 118 | 126 | 118 | 140 |  | 150 | 146 | 148 | 140 | 148 | 148 | 144 | 2985600
64 | Malancha, Ctg. EPZ (United) | 34 | 35 | 35 | 28 | 28 | 26 | 23 | 2 | 2 | 2 | 4 | 7 | 11 | 5 | 2 | 3 | 3 | 3 |  | 18 | 21 | 25 | 25 | 31 | 41 | 32 | 429600
65 | Feni 22MW PP (Doreen) | 19 | 19 | 2 | 16 | 16 | 0 |  | 15 | 15 | 15 | 16 | 18 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 379152
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 0 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 236700
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 810800
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 538270
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 22 | 22 | 18 | 30 | 30 | 22 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 659520
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 787900
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 829500
73 | Ghorashal 108MW PP (Regent) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 73 | 73 | 73 | 72 | 72 | 72 | 72 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 1708272
| Feni Lanka Power | 17 | 0 | [17 empty] | 17 | 17 | 17 | 44 | 52 | 52 | 52 | 234840
| Chowmuhani 113 MW | 101 | 101 | 101 | 100 | 98 | 102 | 75 | 75 | 75 | 75 | 77 | 99 | 103 | 103 | 101 | 106 | 106 | 112 |  | 113 | 113 | 112 | 112 | 111 | 112 | 113 | 2409120
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 7 | 7 | 7 | 7 | 45 | 95 | 100 | 100 | 100 | 100 | 100 | 100 | 98 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1990080
78 | Gazipur 52 MW PP | 16 | 0 | [15 empty] | 29 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 365016
79 | Kodda 150MW PP | 150 | 114 | 48 | 16 | 16 | 16 | 16 | 16 | 48 | 48 | 48 | 48 | 48 | 16 | 16 | 16 | 32 | 70 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 1715040
80 | Jamalpur 95 MW PP(Powerpac) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 32 | 32 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 48 | 48 |  | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 997440
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 25 | 25 | 0 |  |  |  | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 335050
| Gazipur 100 MW PP | 86 | 86 | 86 | 50 | 50 | 34 | 34 | 34 | 49 | 69 | 86 | 86 | 86 | 86 | 86 | 50 | 70 | 86 |  | 86 | 86 | 86 | 86 | 86 | 86 | 85 | 1796976
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 0 | 2 | 3 | 4 | 4 | 5 | 3 | 1 | 1 | [10 empty] | 24359
| Jodiac Power | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 23 | 36 | 35 | 36 | 51 | 53 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 17 | 795047
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | 97 | 97 | 97 | 97 | 97 | 80 | 65 | 65 | 75 | 82 | 95 | 95 | 96 | 96 | 96 | 96 | 96 | 96 |  | 96 | 96 | 88 | 80 | 80 | 80 | 80 | 2177616
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 55 | 0 | [15 empty] | 61 |  | 88 | 88 | 87 | 88 | 88 | 49 | 49 | 603721
86 | Meghnaghat CCPP(Summit) | 265 | 270 | 265 | 270 | 285 | 275 | 295 | 275 | 275 | 275 | 275 | 275 | 275 | 295 | 285 | 285 | 275 | 10 |  | 10 | 10 | 10 | 10 | 10 | 50 | 150 | 4912465
87 | Meghnaghat 100 MW(IEL) | 75 | 98 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2414400
| Meghnaghat 104 MW PP (OPCL) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 20 | 18 | 18 | 18 | 18 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 653760
88 | Ghorashal 78.5 MW PP(MAX) | 68 | 69 | 69 | 69 | 70 | 69 | 40 | 40 | 60 | 68 | 68 | 67 | 66 | 65 | 65 | 65 | 66 | 66 |  | 40 | [5 empty] | 0 | 1185408
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [17 empty] | 90 |  | 100 | 90 | 80 | 80 | 60 | 60 | 60 | 513840
92 | Fenchuganj 44MW (Energyprima) | 44 | 44 | 44 | 44 | 41 | 41 | 10 | 10 | 29 | 44 | 44 | 41 | 44 | 41 | 41 | 41 | 10 | 35 |  | 47 | 47 | 47 | 47 | 47 | 47 | 44 | 977472
93 | Ashuganj 51 MW PP (Midland) | 35 | 35 | 35 | 43 | 43 | 43 | 43 | 43 | 43 | 35 | 35 | 43 | 51 | 51 | 43 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1096410
94 | Gagnagar 102 MW PP (Digital Power) | 94 | 94 | 94 | 94 | 24 | 16 | 16 | 24 | 64 | 80 | 94 | 94 | 94 | 94 | 94 | 58 | 58 | 94 |  | 94 | 94 | 94 | 76 | 76 | 76 | 76 | 1804608
95 | Patenga 50MW PP (Baraka) | 50 | 36 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 13 | 18 | 15 | 19 | 19 | 19 | 42 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 728640
96 | Chattogram 108 MW PP (ECPV) | 97 | 97 | 91 | 48 | 12 | 12 | 12 | 13 | 40 | 40 | 40 | 40 | 40 | 44 | 78 | 90 | 93 | 97 |  | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 1588800
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 43 | 43 | 43 | 43 | 42 | 983027
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 17 | 17 | 17 | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1110908
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 112 | 112 | 112 | 100 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2662772
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 1 | 2 |  | 1 | 1 | 0 | [9 empty] | 11700
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 0 |  |  |  |  | 17 | 17 | 17 | 17 | 17 | 17 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 774720
104 | Keranigonj 300 MW PP (APR) | [17 empty] | 200 |  | 50 | 50 | 50 | 50 |  |  | 0 | 332424
105 | Bramhangoan 100 MW PP (Aggreko) | [17 empty] | 50 |  | 97 | 97 | 97 | 45 |  |  | 0 | 280173
106 | Mymensingh 200 MW PP (United) | 200 | 200 | 200 | 200 | 200 | 150 | 150 | 150 | 163 | 191 | 182 | 190 | 190 | 190 | 191 | 189 | 189 | 190 |  | 200 | 200 | 200 | 200 | 200 | 200 | 191 | 4531200
112 | Aurahati 100MW PP (Aggreko) | [17 empty] | 52 |  | 99 | 100 | 100 | 59 | 65 | 26 | 0 | 382154
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 149 | 149 | 149 | 149 | 139 | 149 | 149 | 149 | 133 | 137 | 146 | 149 | 149 | 140 | 145 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3553340
115 | Juldah 100 MW PP Unit-3 (Acorn) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 530880
116 | Chandpur 200MW (Desh energy) | 164 | 50 | 0 | [14 empty] | 68 |  | 150 | 181 | 181 | 181 | 100 | 100 | 17 | 1218240
117 | Ashuganj 150MW PP (Midland) | 135 | 137 | 142 | 142 | 142 | 100 | 70 | 75 | 97 | 100 | 103 | 120 | 138 | 138 | 127 | 135 | 140 | 137 |  | 137 | 137 | 140 | 140 | 140 | 143 | 142 | 3109600
118 | Bibiyana-III 400 MW CCPP | 421 | 421 | 426 | 426 | 423 | 430 | 428 | 424 | 425 | 420 | 418 | 419 | 421 | 414 | 414 | 410 | 414 | 414 |  | 418 | 418 | 418 | 420 | 418 | 422 | 424 | 10092000
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 85 | 8 | 8 | 8 | 23 | 82 | 107 | 109 | 99 | 55 | 55 | 25 | 25 | 67 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2071200
| Anwara 300 MW PP (United) | 180 | 180 | 180 | 180 | 180 | 125 | 51 | 52 | 104 | 106 | 156 | 160 | 161 | 179 | 179 | 144 | 144 | 144 |  | 158 | 161 | 161 | 161 | 162 | 162 | 160 | 3562909
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 70 | 70 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2369280
120 | Eastern Zone Total | 7976 | 7695 | 7505 | 7382 | 6977 | 6500 | 6050 | 6050 | 6493 | 6801 | 6991 | 7226 | 7405 | 7115 | 7337 | 7044 | 6794 | 8097 |  | 8275 | 8306 | 8262 | 8180 | 8009 | 8002 | 7884 | 176867722
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 115 | 115 | 83 | 16 | 7 | 0 |  | 5 | 16 | 16 | 16 | 16 | 16 | 16 | 40 | 49 | 49 | 106 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 1374720
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [15 empty] | 2 | 3 | 3 |  | 3 | 3 | 3 | 11 | 17 | 12 | 12 | 73660
| Khulna 225 MW CCPP | 195 | 135 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 170 |  | 218 | 218 | 218 | 218 | 218 | 220 | 220 | 3694080
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 35 | 105 | 105 | 105 | 53 | 53 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1525440
130
131
132
133
| Barisal 110 MW PP (Summit ) | 110 | 110 | 96 | 80 | 64 | 22 | 14 | 32 | [8 empty] | 16 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 1319136
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 91 | 93 | 95 | 95 | 94 | 0 |  | 24 | 85 | 91 | 93 | 93 | 93 | 91 | 91 | 88 | 91 | 91 |  | 92 | 95 | 95 | 97 | 96 | 95 | 95 | 2004
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 38 | 38 | 38 | 38 | 38 | 32 | 27 | 11 | 21 | 20 | 23 | 18 | 24 | 26 | 24 | 26 | 25 | 35 |  | 36 | 36 | 38 | 39 | 39 | 37 | 38 | 727327
141 | Noapara 100 MW PP (Bangla Trac) | [17 empty] | 26 |  | 100 | 100 | 100 | 100 | 100 | 100 | 0 | 617280
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 24 | 0 | [14 empty] | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 346125
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 5 | [9 empty] | 896
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 919 | 918 | 919 | 919 | 919 | 919 | 919 | 919 | 919 | 919 | 919 | 919 | 919 | 919 | 919 | 919 | 919 | 918 |  | 917 | 918 | 918 | 918 | 918 | 918 | 918 | 22040727
147 | Bheramara 410 MW CCPP | 330 | 330 | 325 | 325 | 325 | 325 | 290 | 290 | 290 | 310 | 330 | 325 | 320 | 320 | 315 | 305 | 270 | 305 |  | 295 | 290 | 290 | 280 | 280 | 270 | 270 | 7605792
148 | Payra 1320 MW | 580 | 580 | 580 | 580 | 560 | 530 | 520 | 520 | 500 | 490 | 490 | 490 | 490 | 510 | 550 | 530 | 440 | 480 |  | 560 | 570 | 590 | 590 | 590 | 590 | 570 | 13532000
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 151 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 149 | 150 | 151 | 150 | 150 | 370900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 333040
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 183 | 183 | 184 | 183 | 183 | 186 | 162 | 152 | 152 | 152 | 155 | 152 | 152 | 155 | 165 | 154 | 154 | 144 |  | 169 | 172 | 172 | 181 | 178 | 161 | 155 | 4196227
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 198 | 199 | 198 | 199 | 199 | 200 | 150 | 150 | 161 | 156 | 162 | 159 | 159 | 181 | 180 | 163 | 157 | 144 |  | 189 | 191 | 184 | 177 | 176 | 181 | 180 | 4485918
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 390 | 400 | 389 | 402 | 415 | 350 | 375 | 390 | 337 | 398 | 405 | 365 | 363 | 350 | 407 | 405 | 312 | 405 |  | 410 | 410 | 414 | 413 | 411 | 411 | 386 | 9411181
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 10 | 30 |  | 40 | 36 | 39 | 42 | 42 | 42 | 42 | 252167
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 20 | 17 | 16 | 16 | 17 | 18 | 18 |  | 18 | 18 | 18 | 18 | 21 | 21 | 21 | 464400
163 | Bogura 20 MW PP (Energyprima) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 235152
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 253062
165 | Amnura 50 MW PP(Sinha) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 491920
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [17 empty] | 31 |  | 36 | 38 | 45 | 36 | 36 | 36 | 36 | 247469
168 | Santahar 50 MW Peaking PP | 29 | 0 | [15 empty] | 15 |  | 32 | 31 | 31 | 31 | 31 | 31 | 31 | 244990
169 | Natore 52 MW PP (Rajlanka) | 24 | 0 | [15 empty] | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 391680
170 | Chapainawabganj 100 MW Peaking PP | 95 | 42 | 0 | [14 empty] | 85 |  | 95 | 95 | 96 | 96 | 96 | 96 | 96 | 763200
171 | Baghabari 200 MW PP (Paramount) | [17 empty] | 50 |  | 50 | 50 | 50 |  |  |  | 0 | 216639
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 0 |  |  |  |  | 34 | 35 | 35 | 35 | 35 | 35 | 52 | 70 | 70 | 92 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1618176
172 | Confidence Power Bogura Unit-1 113 MW | 109 | 109 | 109 | 109 | 109 | 35 | 35 | 35 | 35 | 35 | 50 | 109 | 109 | 109 | 54 | 35 | 35 | 35 |  | 35 | 54 | 54 | 70 | 109 | 109 | 109 | 1761600
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 88 | 89 | 89 | 92 | 87 | 39 | 35 | 33 | 33 | 35 | 33 | 48 | 56 | 54 | 61 | 77 | 91 | 92 |  | 93 | 105 | 104 | 108 | 106 | 106 | 107 | 1767360
177 | Sympa Solar Power 8MW | [6 empty] | 1 | 2 | 3 | 3 | 6 | 6 | 6 | 6 | 4 | 2 | 1 | [9 empty] | 41374
178
178