## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:September 2020
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | September 2020 |  | August 2020 |  | September 2019
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 12892 | 05/09/20 | 12577 | 31/08/20 | 12717 | 01/09/19 | 12893 | 29/05/19
|  |  | 19:30 |  | 19:30 |  | 21:00 |  | 21:00
2 | Minimum Generation (MW) | 7634 | 25/09/20 | 6840.9 | 01/08/20 | 6957 | 27/09/19 | - | -
|  |  | 9:00 |  | 9:00 |  | 8:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 12892 | 05/09/20 | 12577 | 31/08/20 | 12717 | 01/09/19 | 12893 | 29/05/19
|  |  | 19:30 |  | 19:30 |  | 21:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 10888 | 05/09/20 | 10843.5 | 31/08/20 | 10636.2 | 01/09/19 | 10888 | 05/09/20
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 12892 | 05/09/20 | 12577 | 31/08/20 | 12717 | 01/09/19 | 12893 | 29/05/19
|  |  | 19:30 |  | 19:30 |  | 21:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 11890.0667 |  | 11541.5161 |  | 11679.0667 |  | 11890.0667 | Sept'20
7 | Average Generation (MW) at Day Peak | 9851.3753 |  | 9323.5619 |  | 9378.1933 |  | 9851.3753 | Sept'20
8 | Maximum Power Import from India, BIPTC (MW) | 937 | 23/09/2020 | 945 | 04/08/2020 | 930 | 22/09/19 | 956 | 27/3/2019
|  |  | 1:30 |  | 17:00 |  | 17:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 184 | 07/09/2020 | 178 | 13/087/2020 | 194 | 19/09/19 | 194 | 12/06/19
|  |  | 18:30 |  | 22:00 |  | 20:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 2010-05-04
20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 3707.5 | 05/04/10
20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 3387.808 |  | 3338.6684 |  | 3805.7195 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 137.7396 |  | 112.5022 |  | 124.6645
22 | Net Generation of BPDB (MKWH) | 3250.0684 |  | 3226.1662 |  | 3681.055
23 | Net Generation of IPP & RPCL (MKWH) | 2551.8684 |  | 2591.1866 |  | 2209.5029
24 | Net Generation of REB (MKWH) | 139.565 |  | 150.3385 |  | 154.8794
24 | Net Generation of Rental Power Plant (MKWH) | 614.8876 |  | 569.7029 |  | 508.2955
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 6556.3894 |  | 6537.3941 |  | 6553.7328 |  | 6556.3894 | Sept'20
26 | Energy Generation by Gas (MKWH) | 4127.7738 |  | 4031.1453 |  | 4756.9561 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 388.8315 |  | 434.2084 |  | 171.5174 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1679.4648 |  | 1616.2719 |  | 1362.4513 |  | 1679.4648 | Sep-20
29 | Energy Generation by Hydro (MKWH) | 42.0017 |  | 89.1242 |  | 139.7935 |  | 151.4 | August-19
30 | Energy Generation by Solar (MKWH) | 4.8414 |  | 4.5842 |  | 22.5649 |  | 22.56 | 2019-09-16
31 | Energy Generation by Coal (MKWH) | 451.2158 |  | 474.5624 |  | 243.718 |  | 488.515 | July-20
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 764.6635 |  | 775.9511 |  | 762.6167 |  | 775.9511 | August-20
33 | Monthly Load Factor (%) | 80.3555 |  | 79.359 |  | 81.4703 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:September' 2020
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 12892 | 05/09/20 | 19:30
Generation Period
| Dhaka | MW | 4215
| Chattogram | MW | 1174
| Cumilla | MW | 1206
| Mymensingh | MW | 924
| Sylhet | MW | 517
a) | Total supply in East zone | MW | 8036
| Khulna | MW | 1551
| Barisal | MW | 364
| Rajshahi | MW | 1345
| Rangpur | MW | 741
b) | Total supply in West zone | MW | 4001
c) | Total supply in both zone ( a+b) | MW | 12037
Ref: | 27.21.0000.603.16.087.20.327 | Date: 15/10/2020
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:September' 2020
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 145 | 17/09/20 | 22:00
| b) Ishurdi end | MW | 255 | 29/09/20 | 17:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 620 | 29/09/20 | 17:00
| b) Ishurdi end | MW | 62 | 17/09/20 | 22:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | 0.14887 | 17/09/20
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | 0.132 | 17/09/20
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 0.53755
| b) Ishurdi end | MKWH | 68.9381
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 66.87
| b) Ishurdi end | MKWH | 0.52189
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 140 | 14/09/20 | 20:00
| b)Serajganj end | MW | 560 | 26/09/20 | 16:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 520 | 26/09/20 | 16:00
| b)Sirajganj end | MW | 120 | 14/09/20 | 20:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 0.668 | 15/09/20
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 0.664 | 15/09/20
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 4.952
| b)Sirajganj end | MKWH | 130.21
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 127.94
| b)Sirajganj end | MKWH | 4.95
30 | Transmission loss of EWI /NO-2 | % | 1.472
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishwardi.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/3 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: September 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Joydevpur | 132/33 kV Transformer-T3 | 2020-09-02 07:36 | 2020-09-02 08:11 | 1:14 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Tongi | 132/33 kV Transformers-T1 & T2 | 2020-09-03 02:04 | 2020-09-03 20:30 | 18:26 | E/O
| 132/33 kV Transformers-T2 | 2020-09-03 20:04 | 2020-09-03 20:30 | 0:26 | E/O | Due to 33 kV incoming CT PT & CB of T1 transformer burn | 122 | 52.8667 | Power interruption
| 132/33 kV Transformers-T-2 | 2020-09-04 11:42 | 2020-09-04 11:50 | 0:08 | E/O | Due to bursting of L/A | 0 | 0
| 132/33 kV Transformers-T-3 | 2020-09-04 11:42 | 2020-09-04 11:50 | 0:08 | E/O |  | 80 | 10.6667 | Power interruption
Mirpur | 132/33 kV Transformers-T-2 | 2020-09-05 10:44 | 2020-09-05 14:32 | 3:48 | E/O | Due to red-hot maintenance at 33 kV | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T-2 | 2020-09-08 13:15 | 2020-09-08 16:34 | 3:19 | E/O | Due to fire at T-1& T-3 | 420 | 1393 | Power interruption
| 132/33 kV Transformer-T-1 | 2020-09-09 10:24 | 2020-09-09 10:24 | 0:00 | E/O | Due to fire at 33kV incoming Breaker | 0 | 0 | No interruption
| 132/33 kV Transformer-T-3 & 33 kV Bus-2 | 2020-09-14 08:20 | 2020-09-14 09:53 | 1:33 | E/O | Due to red-hot maintenance | 10 | 15.5 | Power interruption
| 132/33 kV Transformers-T-1 | 2020-09-17 10:35 | 2020-09-17 10:49 | 0:14 | T | Tripped showing O/C & E/F relay | 110 | 25.6667 | Power interruption
| 132/33 kV Transformers-T-3 | 2020-09-17 10:35 | 2020-09-17 10:53 | 0:18 | T
Kaliakoir | 400/132 kV Transformer-T-2 | 2020-09-22 06:01 | 2020-09-22 07:22 | 1:21 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Joydevpur | 132/33 kV Transformers-T-4 | 2020-09-22 01:56 | 2020-09-22 02:28 | 0:32 | E/O | Due to 33 kV CB burn | 20 | 10.6667 | Power interruption
| 132/33 kV Transformers-T-3 | 2020-09-22 03:56 | 2020-09-22 06:12 | 2:16 | T | Tripped showing buchholz relay at 33 kV | 40 | 90.6667 | Power interruption
Mymensingh | 132/33 kV Transformer-T-1 with 33 kV Bus | 2020-09-24 07:18 | 2020-09-24 08:38 | 1:20 | E/O | Due to red-hot maintenance | 60 | 80 | Power interruption
Tongi | 230/132 kV Transformer-T-03 | 2020-09-29 08:58 | 2020-09-29 15:28 | 1:09 | E/O | Due to Oil leakage | 0 | 0 | No interruption
|  |  | Total : | 36:12 |  | Unserved Energy: |  | 1679.0333
Dhaka (South) Grid Circle :
Bhulta | 33 kV capacitor bank | 2020-09-04 21:21 | 2020-09-04 21:21 | 0:00 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Ghorashal | 230 kV bus section -3 & 4 | 2020-09-09 11:08 | 2020-09-09 11:08 | 0:00 | T | Tripped showing buchholz relay | 0 | 0 | No interruption
| 230/132 kV Transformer-OAT-12 | 2020-09-09 11:08 | 2020-09-09 12:35 | 1:27 | T |  | 0 | 0 | No interruption
| 132/33 kV Transformer-T-1 | 2020-09-11 02:48 | 2020-09-11 16:33 | 13:45 | E/O | Due to 33 kV Breaker problem | 0 | 0 | No interruption
Narsinghdi | 132/33 kV Transformer-T1 | 2020-09-18 11:20 | 2020-09-18 12:08 | 0:48 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Ghorashal | 230/132 kV Transformer-AT-2 | 2020-09-20 06:22 | 2020-09-20 12:06 | 1:09 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Narsinghdi | 132/33 kV Transformer-T2 | 2020-09-23 19:49 | 2020-09-23 20:57 | 1:08 | T | Tripped showing mechanical protection trip | 45 | 51 | Power interruption
Hasnabad | 132/33 kV Transformers-T1,T2 & T3 | 2020-09-24 06:49 | 2020-09-24 07:19 | 0:30 | T | Tripped showing 33 kV feeder fault | 135 | 67.5 | Power interruption
Satmosjid | 132/33 kV Transformer-T1 | 2020-09-26 05:19 | 2020-09-26 11:53 | 6:34 | T | Tripped showing differential relay | 0 | 0 | No interruption
|  |  | Total : | 25:21 |  | Unserved Energy: |  | 118.5
Chattogram Grid Circle :
Juldah | 132/33 kV Transformer-T2 | 2020-09-14 12:27 | 2020-09-14 13:36 | 1:09 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Halishahar | 132/33 kV Transformers-T1 | 2020-09-16 00:59 | 2020-09-16 02:22 | 1:23 | T | Tripped showing O/C relay | 115 | 159.0833 | Power interruption
| 132/33 kV Transformers-T2 | 2020-09-16 00:59 | 2020-09-16 04:48 | 3:49 | T
| 132/33 kV Transformers-T3 | 2020-09-16 00:59 | 2020-09-16 02:27 | 1:28 | T
| 132/33 kV Transformer-T-2 & 33 kV Bus | 2020-09-16 15:22 | 2020-09-16 16:35 | 1:13 | E/O | Due to red-hot maintenance at 33 kV bus | 0 | 0 | No interruption
Juldah | 132/33 kV Transformer-T1 | 2020-09-22 18:47 | 2020-09-22 21:32 | 2:45 | T | Tripped showing buchholz. relay at 33 kV side | 0 | 0 | No interruption
Matarbari | 132/33 kV Transformer-T1 | 2020-09-27 18:53 | 2020-09-27 21:35 | 2:42 | E/O | Due to red-hot maintenance at 33 kV | 0 | 0 | No interruption
Hathazari | 132/33 kV Transformer-T1 | 2020-09-27 23:05 | 2020-09-28 00:05 | 1:00 | E/O | Due to red-hot maintenance | 25 | 25 | Power interruption
| 132/33 kV Transformer-MT4 | 2020-09-30 11:02 | 2020-09-30 11:24 | 1:09 | E/O | Due to Oil leakage | 0 | 0 | No interruption
|  |  | Total : | 16:38 |  | Unserved Energy: |  | 184.0833
Cumilla Grid Circle :
Comilla(N) | 33 kV Bus | 2020-09-04 07:24 | 2020-09-04 08:42 | 1:18 | E/O | Due to red-hot maintenance | 43 | 55.9 | Power interruption
Fenchuganj | 132/33 kV Transformer-T2 | 2020-09-04 00:06 | 2020-09-04 01:05 | 0:59 | T | Tripped showing E/F. relay | 27 | 26.55 | Power interruption
Cumilla(N) | 132/33 kV Transformer-T3 | 2020-09-13 17:15 | 2020-09-13 17:22 | 0:07 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Chandpur | 132/33 kV Transformer-T-1 | 2020-09-15 09:53 | 2020-09-15 11:28 | 1:35 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Chowmuhani | 132/33 kV Transformers-T-1 &T2 | 2020-09-18 05:42 | 2020-09-18 06:05 | 0:23 | T | Tripped showing O/C relay at 33 kV side | 120 | 46 | Power interruption
Sylhet | 132/33 kV Transformer-T-1 | 2020-09-18 09:44 | 2020-09-18 10:10 | 0:26 | T | Tripped showing O/C & E/F relay at 33 kV side | 30 | 13 | Power interruption
Page: 2/3 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: September 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Shahjibazar | 132/33 kV Transformers- &T4 | 2020-09-20 18:11 | 2020-09-20 18:16 | 0:05 | T | Tripped showing O/C relay | 104 | 8.6667 | Power interruption
| 132/33 kV Transformer-T2 | 2020-09-20 18:11 | 2020-09-20 21:16 | 3:05 | T
Ramganj | 132/33 kV Transformer-T2 | 2020-09-20 21:30 | 2020-09-20 23:18 | 1:48 | E/O | Due to red-hot maintenance | 30 | 54 | Power interruption
Chowmuhani | 132/33 kV Transformers-T-1 &T2 | 2020-09-22 11:18 | 2020-09-22 11:31 | 0:13 | T | Tripped showing E/F relay at 33 kV side | 112 | 24.2667 | Power interruption
Sylhet | 132/33 kV Transformer-T2 | 2020-09-25 21:04 | 2020-09-27 13:55 | 40:51 | E/O | Due to 33 kV CB burst | 0 | 0 | No interruption
Sreemongal | 132/33 kV Transformer-T-1 | 2020-09-29 10:35 | 2020-09-29 11:03 | 0:28 | T | Tripped showing lockout relay | 15 | 7 | Power interruption
Shahjibazar | 132/33 kV Transformer-T-2 | 2020-09-29 10:24 | 2020-09-29 13:45 | 3:21 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Sylhet | 132 kV Bus section -3&4 | 2020-09-29 11:50 | 2020-09-29 16:04 | 4:14 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
| 132 kV Bus& 4 | 2020-09-30 07:23 | 2020-09-30 12:29 | 5:06 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
|  |  |  | 63:59 |  | Unserved Energy: |  | 235.3833
Khulna Grid Circle :
Faridpur | 132/33 kV Transformer-T1 | 2020-09-12 08:09 | 2020-09-12 09:07 | 0:58 | E/O | Due to red-hot maintenance at 33 kV side | 20 | 19.3333 | Power interruption
Patuakhali | 132/33 kV Transformer-T1 | 2020-09-16 19:56 | 2020-09-16 20:23 | 0:27 | E/O | Due to red-hot maintenance | 10 | 4.5 | Power interruption
Barishal(N) | 132/33 kV Transformer-T4 | 2020-09-20 10:32 | 2020-09-20 17:14 | 6:42 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Bhandaria | 132/33 kV Transformer-T1 | 2020-09-23 08:37 | 2020-09-23 10:12 | 1:35 | E/O | Due to red-hot maintenance | 10 | 15.8333 | Power interruption
Bagerhat | 132/33 kV Transformer-T1 | 2020-09-24 22:23 | 2020-09-25 09:34 | 11:11 | T | Tripped showing O/C relay at 132 side & 33 kV cable burst | 50 | 37.5 | Power interruption 22:23 to 23:08
| 132/33 kV Transformer-T2 | 2020-09-24 22:23 | 2020-09-24 23:05 | 0:42 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformers-T1 & T2 | 2020-09-26 11:55 | 2020-09-26 12:20 | 0:25 | T | Tripped showing O/C relay at 33 kV side | 38 | 15.8333 | Power interruption
Khulna © | 132/33 kV Transformer-T1 | 2020-09-28 10:10 | 2020-09-28 21:21 | 11:11 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Barishal(S) | 132/33 kV Transformer-T1 | 2020-09-29 08:20 | 2020-09-29 10:07 | 1:47 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Barishal(N) | 132/33 kV Transformer-T5 | 2020-09-29 13:20 | 2020-09-30 17:55 |  | T | Tripped showing PRD relay | 0 | 0 | No interruption
|  |  | Total : | 34:58 |  | Unserved Energy: |  | 93
HVDC Grid Circle :
Bottail | 132/33 kV Transformer-T1 | 2020-09-04 06:32 | 2020-09-04 06:57 | 0:25 | E/O | Due to red-hot maintenance at 33 kV side | 50 | 20.8333 | Power interruption
Bheramara | 230/132 kV Transformer-T-01 | 2020-09-13 10:35 | 2020-09-13 14:29 | 3:54 | T | Tripped showing buchholz relay | 0 | 0 | No interruption
Pabna | 132/33 kV Transformer-T3 | 2020-09-17 07:48 | 2020-09-17 07:48 | 0:00 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Benapole | 132/33 kV Transformers-T1 | 2020-09-22 19:19 | 2020-09-22 20:04 | 0:45 | T | Tripped showing E/F & O/C relay at 33 kV side | 40 | 30 | Power interruption
| 132/33 kV Transformers-T2 | 2020-09-22 19:19 | 2020-09-22 20:06 | 0:47 | T
Chuadanga | 132/33 kV Transformer-T2 with 33 kV Bus | 2020-09-26 07:13 | 2020-09-26 09:06 | 1:53 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-09-29 07:06 | 2020-09-29 09:43 | 2:37 | E/O | Due to red-hot maintenance at 33 kV side | 30 | 78.5 | Power interruption
|  |  | Total : | 10:21 |  |  |  | 129.3333
Bogura Grid Circle:
C.nawabganj | 132/33 kV Transformer-T4 | 2020-09-02 12:24 | 2020-09-02 12:34 | 0:10 | T | Tripped showing 33 kV feeder fault | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformers-T1 & T2 | 2020-09-05 07:19 | 2020-09-05 07:42 | 0:23 | E/O | Due to red-hot maintenance 33 kV side | 0 | 0 | No interruption
Barapukuria | 132/33 kV Transformer-T4 | 2020-09-05 15:14 | 2020-09-05 17:17 | 2:03 | T | Tripped showing 33 kV feeder fault | 0 | 0 | No interruption
Purbasadipur | 132/33 kV Transformer-T1 | 2020-09-06 13:06 | 2020-09-06 15:16 | 2:10 | E/O | Due to red-hot maintenance 33 kV side | 30 | 65 | Power interruption
Rajshahi | 132/33 kV Transformers-T1 | 2020-09-06 15:53 | 2020-09-06 16:03 | 0:10 | T | Tripped showing differential relay | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 & T3 | 2020-09-06 15:53 | 2020-09-06 16:03 | 0:10 | T |  | 90 | 15 | Power interruption
Purbasadipur | 132/33 kV Transformer-T2 & 33 kV bus | 2020-09-07 07:35 | 2020-09-07 08:51 | 1:16 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Niyamatpur | 132/33 kV Transformer-T3 | 2020-09-07 08:55 | 2020-09-07 16:38 | 7:43 | T | Tripped showing differential relay | 0 | 0 | No interruption
Barapukuria | 132/33 kV Transformer-T4 | 2020-09-11 17:50 | 2020-09-11 21:53 | 4:03 | T | Tripped showing Lockout relay at 33 kV side | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformers-T1 | 2020-09-13 08:45 | 2020-09-13 09:55 | 1:10 | E/O | Due to red-hot maintenance | 35 | 72.9167 | Power interruption 08:45 to 09:35
| 132/33 kV Transformers-T2 | 2020-09-13 08:45 | 2020-09-13 10:35 | 1:50 | E/O
Mohastanghor | 132/33 kV Transformer-T2 | 2020-09-13 10:31 | 2020-09-13 11:57 | 1:26 | E/O | Due to red-hot maintenance 33 kV side | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-09-13 11:45 | 2020-09-13 13:37 | 1:52 | E/O |  | 0 | 0 | No interruption
Page: 3/3 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: September 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle:
Naogaon | 132/33 kV Transformer-T-2 | 2020-09-13 17:59 | 2020-09-13 18:09 | 0:10 | T | Tripped showing O/C relay relay at 33 kV side | 25 | 4.1667 | Power interruption
Rangpur | 132/33 kV Transformer-T-3 & 33 kV Bus-2,3 | 2020-09-14 09:50 | 2020-09-14 11:02 | 1:12 | E/O | Due to red-hot maintenance at 33 kV side | 60 | 72 | Power interruption
Bogura | 132/33 kV Transformers-T1 | 2020-09-15 09:42 | 2020-09-15 10:21 | 0:39 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Barapukuria | 132/33 kV Transformer-T4 | 2020-09-16 18:00 | 2020-09-16 19:06 | 1:06 | T | Due to CB trip | 0 | 0 | No interruption
C.nawabganj | 132/33 kV Transformer-T4 | 2020-09-17 15:42 | 2020-09-17 16:03 | 0:21 | T | Tripped showing O/C relay at 33 kV side | 0 | 0 | No interruption
Bogura | 132/33 kV Transformers-T1 & T2 | 2020-09-18 07:05 | 2020-09-18 08:23 | 1:18 | T | Tripped showing O/C relay at 33 kV side | 25 | 32.5 | Power interruption
C.nawabganj | 132/33 kV Transformer-T2 | 2020-09-20 10:05 | 2020-09-20 11:44 | 1:39 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Rajshahi | 230/132 kV Transformer-T2 | 2020-09-21 22:01 | 2020-09-22 00:15 | 2:14 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Bogura | 132/33 kV Transformers-T1 | 2020-09-22 19:23 | 2020-09-22 20:21 | 0:58 | T | Tripped showing O/C relay at 33 kV side | 70 | 67.6667 | Power interruption
| 132/33 kV Transformers-T2 | 2020-09-22 19:23 | 2020-09-22 20:25 | 1:02 | T |  | 0 | 0
| 132/33 kV Transformers-T3 | 2020-09-23 12:48 | 2020-09-23 18:48 | 6:00 | T | Tripped showing O/C relay at 33 kV side
| 132/33 kV Transformers-T4 | 2020-09-23 12:48 | 2020-09-23 13:32 | 0:44 | T |  | 55 | 40.3333 | Power interruption
Barapukuria | 132/33 kV Transformer-T4 | 2020-09-24 11:15 | 2020-09-24 12:15 | 1:00 | T | Due to CB trip | 0 | 0 | No interruption
Bogura | 132/33 kV Transformers-T1 & T2 | 2020-09-24 13:33 | 2020-09-24 14:08 | 0:35 | T | Tripped showing 33 kV feeder fault | 60 | 35 | Power interruption
Barapukuria | 132/33 kV Transformer-T4 | 2020-09-25 12:50 | 2020-09-25 15:15 | 2:25 | T | Tripped showing O/C relay | 0 | 0 | No interruption
| 230/132 kV Transformer-TR1 | 2020-09-25 18:57 | 2020-09-25 19:11 | 0:14 | T | Tripped showing E/F & O/C relay | 0 | 0 | No interruption
Bogura | 132/33 kV Transformer-T-1 & 33 kV Bus | 2020-09-28 07:10 | 2020-09-28 08:41 | 1:31 | E/O | Due to red-hot maintenance 33 kV side | 0 | 0 | No interruption
| 132/33 kV Transformers-T3 | 2020-09-29 19:23 | 2020-09-29 21:46 | 2:23 | E/O | Due to CT bursting of 33 kV feeder
| 132/33 kV Transformers-T4 | 2020-09-29 19:23 | 2020-09-29 20:00 | 0:37 | E/O |  | 80 | 49.3333 | Power interruption
| 132/33 kV Transformer-T2 | 2020-09-29 05:38 | 2020-09-29 05:38 | 0:00 | T | Tripped showing differential relay | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformer-T2 with 33 kV Bus | 2020-09-29 07:05 | 2020-09-29 08:10 | 1:05 | E/O | Due to red-hot maintenance | 18 | 19.5 | Power interruption
Naogaon | 132/33 kV Transformer-T2 & 33 kV Bus | 2020-09-30 09:20 | 2020-09-30 10:50 | 1:30 | E/O | Due to red-hot maintenance | 10 | 15 | Power interruption
Saidpur | 132/33 kV Transformer-T4 | 2020-09-30 11:35 | 2020-09-30 12:15 | 0:40 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 53:49 |  | Unserved Energy: |  | 488.4167
Others :
AKSML | 230 kV Bus coupler | 2020-09-25 05:28 | 2020-09-25 07:02 | 1:34 | T | Tripped showing O/C relay | 0 | 0 | No interruption
| 2302/33 kV Transformer-T1 | 2020-09-25 05:30 | 2020-09-25 12:00 | 6:30 | T | Due to PT fault | 0 | 0 | No interruption
|  |  | Total : | 8:04 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 249:22 | Hours
T = Tripping
E/O = Emergency Outage
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/3 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: September 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mymensingh | Mymensingh-Netrakona 132 kV line-1 | 2020-09-01 07:40 | 2020-09-01 07:40 | 0:00 | T | Tripped showing dist.relay | 0 | 0 | No interruption
| Mymensingh -Jamalpur 132 kV line-1 | 2020-09-01 12:05 | 2020-09-01 12:15 | 0:10 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Aminbazar | Aminbazar-Savar 132 kV line-2 | 2020-09-01 18:49 | 2020-09-01 18:50 | 0:01 | T | Tripped showing AR.block and broken conductor trip | 0 | 0 | No interruption
| Aminbazar-Savar 132 kV line-2 | 2020-09-01 19:28 | 2020-09-01 19:42 | 0:14 | T |  | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-2 | 2020-09-07 12:53 | 2020-09-07 13:02 | 0:09 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Mymensingh RPCL | Mymensingh RPCL-Mymensingh S/S 132 kV line | 2020-09-09 11:08 | 2020-09-09 11:14 | 0:06 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kadda | Kadda-Rajendrapur 132 kV line-1 | 2020-09-10 11:11 | 2020-09-10 11:29 | 0:18 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-1 | 2020-09-10 10:24 | 2020-09-10 11:08 | 0:44 | T | Due to fire at 33 kV incoming breaker | 480 | 352 | Power interruption
Mymensingh | Mymensingh-Manikganj 132 kV line-1 | 2020-09-10 13:25 | 2020-09-10 13:37 | 0:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Joydevpur | 132 kV line-1 & Narsingdi 132 kV line | 2020-09-10 15:49 | 2020-09-10 21:05 | 5:16 | E/O | Due to flashing at Ghorashal 132 kV Bus | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-1 | 2020-09-11 11:57 | 2020-09-11 12:07 | 0:10 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Mymensingh-Jamalpur 132 kV line-1 | 2020-09-13 13:52 | 2020-09-13 14:03 | 0:11 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
| Mymensingh-Netrakona 132 kV line-1 | 2020-09-14 13:38 | 2020-09-14 13:45 | 0:07 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Mymensingh-Netrakona 132 kV line-2 | 2020-09-14 13:38 | 2020-09-14 15:08 | 1:30 | T |  | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-1 | 2020-09-14 14:10 | 2020-09-14 14:20 | 0:10 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Tongi-Kabirpur 132 kV line-2 | 2020-09-14 14:10 | 2020-09-14 14:22 | 0:12 | T |  | 0 | 0 | No interruption
Jamalpur | Jamalpur-UMPL 132 kV line-1 & 2 | 2020-09-17 10:35 | 2020-09-17 10:50 | 0:15 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Sherpur | Sherpur-UMPL 132 kV line-1 & 2 | 2020-09-17 10:35 | 2020-09-17 10:54 | 0:19 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV both Ckts | 2020-09-19 11:44 | 2020-09-19 11:55 | 0:11 | T | Tripped showing dist. relay | 423 | 77.55 | Power interruption
Kaliakoir | Kaliakoir-Tangail 132 kV line-1 | 2020-09-25 14:13 | 2020-09-25 14:33 | 0:20 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sherpur | Sherpur-UMPL 132 kV line-1 | 2020-09-26 16:38 | 2020-09-26 16:52 | 0:14 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
Joydevpur | Joydevpur-Kadda 132 kV line-1 | 2020-09-28 07:43 | 2020-09-28 08:04 | 0:21 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 11:10 |  | Unserved Energy: |  | 429.55
Dhaka (South) Grid Circle :
Haripur | Haripur-Bhulta 230 kV line-1 | 2020-09-02 19:43 | 2020-09-02 19:59 | 0:16 | T | Tripped showing Backup protection relay | 154 | 41.0667 | Power interruption
Siddhirganj | Siddhirganj 230 kV S/S-Siddhirganj 335 MW P.P 230 kV GT line | 2020-09-04 11:38 | 2020-09-04 14:53 | 3:15 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Hasnabad | Hasnabad-Lalbagh 132 kV line | 2020-09-05 11:14 | 2020-09-05 11:31 | 0:17 | T | Tripped showing dist. relay | 78 | 22.1 | Power interruption
Ghorashal | Ghorashal-Ashuganj 230 kV line-1 | 2020-09-09 11:08 | 2020-09-09 11:08 | 0:00 | T
| Ghorashal-Ashuganj 230 kV line-2 | 2020-09-09 11:08 | 2020-09-09 14:59 | 3:51 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ghorashal-Bhulta 230 kV line | 2020-09-09 11:08 | 2020-09-09 13:19 | 2:11 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ghorashal-Ishurdi 230 kV line-1 | 2020-09-09 11:08 | 2020-09-09 13:37 | 2:29 | T |  | 1564 | 3883.9333 | Power interruption
| Ghorashal-Tongi 230 kV line-1 | 2020-09-09 11:12 | 2020-09-09 16:21 | 5:09 | T |  | 0 | 0 | No interruption
| Ghorashal-Tongi 230 kV line-2 | 2020-09-09 11:12 | 2020-09-09 21:10 | 9:58 | T |  | 0 | 0 | No interruption
Haripur | Haripur-Narsingdi 132 kV line | 2020-09-09 15:55 | 2020-09-09 16:31 | 0:36 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hasnabad | Hasnabad-Sitalakhya 132 kV line | 2020-09-17 15:25 | 2020-09-17 15:34 | 0:09 | T | Tripped showing O/C & E/F. relay | 123 | 18.45 | No interruption
Shitalakhya | Shitalakhya-Madanganj 132 kV line | 2020-09-17 15:25 | 2020-09-17 15:41 | 0:16 | T |  | 0 | 0 | No interruption
Haripur | Haripur-Fatulla 132 kV line | 2020-09-17 15:25 | 2020-09-17 15:55 | 0:30 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hasnabad | Hasnabad-Brahmangaon 132 kV line | 2020-09-17 15:25 | 2020-09-17 16:15 | 0:50 | T | Tripped showing O/C & E/F. relay | 123 | 102.5 | No interruption
Haripur | Haripur-Siddhirganj 132 kV line-1 | 2020-09-18 09:55 | 2020-09-18 11:18 | 1:23 | T |  | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Cumilla(N) 230 kV line-2 | 2020-09-18 11:26 | 2020-09-18 15:22 | 3:56 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Madanganj | Madanganj-Haripur 132 kV line | 2020-09-22 17:17 | 2020-09-22 22:04 | 4:47 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 39:53 |  | Unserved Energy: |  | 4068.05
Page: 2/3 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: September 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Chittagong Grid Circle :
Hathazari | Hathazari-Kaptai 132 kV line-1 | 2020-09-03 12:13 | 2020-09-03 12:27 | 0:14 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Chandraghona | Chandraghona-Madunaghat 132 kV line-1 | 2020-09-09 20:24 | 2020-09-10 08:26 | 12:02 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
| Madunaghat-Chandraghona 132 kV line-2 | 2020-09-10 23:53 | 2020-09-11 16:26 |  | T | Due to CB trip | 0 | 0 | No interruption
Halishahar | Halishahar-Khulshi 132 kV line-1 |  | 2020-09-13 09:45 |  | T | Tripped showing SOTF. relay | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV line-1 | 2020-09-19 13:55 | 2020-09-19 14:14 | 0:19 | T | Tripped showing dist. E/F relay | 0 | 0 | No interruption
| Hathazari-Khulshi 132 kV line | 2020-09-19 23:55 | 2020-09-20 00:15 | 0:20 | T |  | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-T.K Chemical 132 kV line-1 | 2020-09-28 20:42 | 2020-09-29 14:00 |  | T | Tripped showing dist. relay | 0 | 0 | No interruption
Madunaghat | Madunaghat-T.K Chemical 132 kV line | 2020-09-28 20:40 | 2020-09-28 20:51 | 0:11 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
| Madunaghat-Sikalbaha 230 kV line-1 & 2 | 2020-09-28 20:58 | 2020-09-28 23:35 | 2:37 | T | Tripped showing O/C . relay | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Dohazari 132 kV line-1 | 2020-09-29 05:51 | 2020-09-29 07:13 | 1:22 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 17:05 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2020-09-01 10:16 | 2020-09-01 10:54 | 0:38 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Chatak | Chatak-Sunamganj 132 kV line | 2020-09-04 10:34 | 2020-09-04 10:50 | 0:16 | T | Tripped showing dist. relay | 26 | 6.9333 | Power interruption
Sylhet | Sylhet-Chatak 132 kV lin-1 | 2020-09-04 20:08 | 2020-09-04 20:29 | 0:21 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj P/S-Fenchuganj S/S 132 kV line | 2020-09-05 05:14 | 2020-09-05 05:52 | 0:38 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Feni | Feni-Choddagram 132 kV line-1 | 2020-09-08 11:43 | 2020-09-08 14:36 | 2:53 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
Sreemongal | Sreemongal-Fenchuganj 132 kV line | 2020-09-09 11:08 | 2020-09-09 11:51 | 0:43 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Ashuganj 132 kV line-3 | 2020-09-09 11:08 | 2020-09-09 11:32 | 0:24 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorashal 132 kV line-1 & 2 | 2020-09-10 05:23 | 2020-09-10 07:50 | 2:27 | T | Tripped showing power swing at Ashufanj end | 0 | 0 | No interruption
Cumilla | Cumilla-BSRM 230 kV line-2 | 2020-09-16 09:49 | 2020-09-16 14:05 | 4:16 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Chandpur | Chandpur-Cumilla(N) 132 kV line-2 | 2020-09-22 04:37 | 2020-09-22 04:49 | 0:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Chandpur 132 kV line-1 | 2020-09-25 20:48 | 2020-09-25 21:05 | 0:17 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Kulaura 132 kV line-1 & 2 | 2020-09-28 07:43 | 2020-09-28 08:40 | 0:57 | E/O | Due to bursting of PT | 22 | 20.9 | Power interruption
Fenchuganj P/S | Fenchuganj P/S-Chatak 132 kV line-1 | 2020-09-29 09:40 | 2020-09-29 10:50 | 1:10 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 15:12 |  | Unserved Energy: |  | 27.8333
Khulna Grid Circle :
Faridpur | Faridpur-Gopalganj 132 kV line-1 | 2020-09-01 08:11 | 2020-09-01 10:21 | 2:10 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Khulna(C) | Khulna©-Noapara 132 kV line-2 | 2020-09-02 13:22 | 2020-09-02 13:51 | 0:29 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line-2 | 2020-09-07 10:43 | 2020-09-07 13:42 | 2:59 | E/O | Due to Breaker problem | 0 | 0 | No interruption
Faridpur | Faridpur-Gopalganj (N) 132 kV line-2 | 2020-09-13 09:11 | 2020-09-13 09:22 | 0:11 | T | Tripped showing E/F & O/C relay | 0 | 0 | No interruption
Noapara | Noapara-Jessore 132 kV line-1 | 2020-09-20 07:50 | 2020-09-20 08:17 | 0:27 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 6:16 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Shahjadpur | Shahjadpur-Baghabari 132 kV line-2 | 2020-09-07 15:45 | 2020-09-07 18:00 | 2:15 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ishurdi | Ishurdi-Baghabari 230 kV both CKTs | 2020-09-09 11:37 | 2020-09-09 12:15 | 0:38 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bheramara | Bheramara HVDC-Bheramara 400 kV line-1 | 2020-09-17 16:42 | 2020-09-17 17:47 | 1:05 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ghorashal 230 kV line-2 | 2020-09-19 10:59 | 2020-09-19 11:34 | 0:35 | T | Tripped showing LZ-96,L8B & PD signal | 0 | 0 | No interruption
| Ishurdi-Bheramara 132 kV line-1 | 2020-09-20 08:55 | 2020-09-20 11:19 | 2:24 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ishurdi-Bheramara 132 kV line-2 | 2020-09-20 08:59 | 2020-09-20 10:28 | 1:29 | T | Tripped showing dist. & O/C relay | 0 | 0 | No interruption
Bheramara | Bheramara HVDC-Bheramara 230 kV line-1 | 2020-09-20 08:59 | 2020-09-20 09:28 | 0:29 | T | Tripped showing DT and CT received | 0 | 0 | No interruption
|  |  | Total : | 8:55 |  | Unserved Energy: |  | 0
Page: 3/3 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: September 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle:
Palashbari | Palashbari-Mohasthangarth 132 kV line-2 | 2020-09-07 08:45 | 2020-09-07 09:00 | 0:15 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Naogaon | Naogaon-Niyamatpur 132 kV line | 2020-09-09 23:45 | 2020-09-09 23:52 | 0:07 | T | Tripped showing dist. relay | 60 | 7 | Power interruption
Saidpur | Saidpur-Purbasadipur 132 kV line-2 | 2020-09-11 12:35 | 2020-09-11 12:50 | 0:15 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Saidpur-Saidpur P/S 132 kV line-2 | 2020-09-11 12:33 | 2020-09-11 12:48 | 0:15 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Purbasadipur | Purbasadipur-Thakurgaon 132 kV line-1 | 2020-09-12 02:44 | 2020-09-12 03:09 | 0:25 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bogura | Bogura-Barapukuria 230 kV line-1 | 2020-09-13 02:14 | 2020-09-13 07:35 | 5:21 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rangpur | Rangpur-Saidpur 132 kV line-1 | 2020-09-13 00:34 | 2020-09-13 01:21 | 0:47 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Rangpur-Saidpur 132 kV line-2 | 2020-09-13 00:39 | 2020-09-13 01:21 | 0:42 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Rangpur-Saidpur 132 kV line-2 | 2020-09-16 19:15 | 2020-09-16 19:34 | 0:19 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Thaurgaon | Thaurgaon-Purbasadipur 132 kV line-1 & 2 | 2020-09-25 11:34 | 2020-09-25 11:45 | 0:11 | T | Tripped showing dist. relay | 50 | 9.1667 | Power interruption
Saidpur | Saidpur-Jaldhaka 132 kV CKTS -1 & 2 | 2020-09-25 13:20 | 2020-09-25 13:30 | 0:10 | T | Tripped showing dist. relay | 9 | 1.5 | Power interruption
| Saidpur-Purbasadipur 132 kV line-1 | 2020-09-26 18:57 | 2020-09-26 19:02 | 0:05 | T | Tripped showing dist. relay | 87 | 7.25 | Power interruption
| Saidpur-Purbasadipur 132 kV line-2 | 2020-09-26 18:57 | 2020-09-26 19:03 | 0:06 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rangpur | Rangpur-Kurigram 132 kV CKt | 2020-09-27 08:07 | 2020-09-27 12:35 | 4:28 | T | Tripped showing dist. relay | 10 | 44.6667 | Power interruption
Mohastanghor | Mohastanghor-Palashbari 132 k line-1 & 2 | 2020-09-28 19:30 | 2020-09-28 19:49 | 0:19 | T | Tripped showing dist.& O/C relay | 150 | 47.5 | Power interruption
|  |  | Total : | 13:45 |  | Unserved Energy: |  | 117.0833
Others :
BSRM | BSRM-GPS 230 kV line-2 | 2020-09-25 05:28 | 2020-09-25 07:07 | 1:39 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 1:39 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 121:11 | Hours
T = Tripping | [7 empty] | Executive Engineer
E/O = Emergency Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/4 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:September 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Jamalpur | 132/33 kV Transformer-T-2 | 2020-09-01 06:03 | 2020-09-01 07:17 | 1:14 | S/O | Due to C/M work | 20 | 24.6667 | Power interruption
Joydevpur | 132/33 kV Transformer-T3 | 2020-09-02 05:51 | 2020-09-02 06:18 | 0:27 | S/O | Due to C/M work | 30 | 13.5 | Power interruption
| 132/33 kV Transformer-T3 | 2020-09-02 12:16 | 2020-09-02 18:34 | 6:18 | S/O | Due to B-phase winding temperature high | 40 | 252 | Power interruption
| 132/33 kV Transformer-T3 | 2020-09-03 22:28 | 2020-09-03 22:50 | 0:22 | S/O | Due to Overheatingm of B-phase | 20 | 7.3333 | Power interruption
Satmosjid | 132/33 kV Transformer-T2 | 2020-09-08 06:55 | 2020-09-08 09:45 | 2:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-1 & 2 |  | 2020-09-08 15:58 |  | S/O | After maintenance work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 |  | 2020-09-09 08:05 |  | S/O | After maintenance work | 0 | 0 | No interruption
Tongi | 132/33 kV Transformer-T1 | 2020-09-10 06:25 | 2020-09-10 07:50 | 1:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV Transformer-GT1 | 2020-09-10 06:30 | 2020-09-10 11:05 | 4:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T1 | 2020-09-11 06:30 | 2020-09-11 13:36 | 7:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T1 & 33 kV Bus | 2020-09-11 06:20 | 2020-09-11 10:15 | 3:55 | S/O | Due to replacement work | 0 | 0 | No interruption
Tanagil | 132/33 kV Transformer-T2 | 2020-09-11 08:08 | 2020-09-11 13:03 | 4:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T1 |  | 2020-09-12 02:52 |  | S/O | After maintenance work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2020-09-12 09:23 | 2020-09-12 12:22 | 2:59 | S/O | Due to protection work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 & 33 kV Bus | 2020-09-15 06:15 | 2020-09-15 09:32 | 3:17 | S/O | Due to maintenance work | 27 | 88.65 | Power interruption
Jamalpur | 132/33 kV Transformer-T3 | 2020-09-15 08:27 | 2020-09-15 10:57 | 2:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T3 | 2020-09-15 07:06 | 2020-09-15 11:16 | 4:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T2 | 2020-09-16 12:06 | 2020-09-16 16:12 | 4:06 | S/O | Due to C/M work | 10 | 41 | Power interruption
Manikganj | 132/33 kV Transformers-T2 & T3 | 2020-09-18 05:50 | 2020-09-18 08:54 | 3:04 | S/O | Due to D/W work | 0 | 0 | No interruption
Savar | 33 kV capacitor bank & 33 kV Bus-A | 2020-09-18 06:59 | 2020-09-18 06:59 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Joydevpur | 132/33 kV Transformer-T4 | 2020-09-18 06:02 | 2020-09-18 06:59 | 0:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T1 | 2020-09-18 10:02 | 2020-09-18 12:02 | 2:00 | S/O | Due to protection test | 25 | 50 | Power interruption
Dhamrai | 132/33 kV Transformer-T3 & 33 kV Bus-1 | 2020-09-18 08:04 | 2020-09-18 18:58 | 10:54 | S/O | Due to C/M work | 26 | 283.4 | Power interruption
Narsinghdi | 132/33 kV Transformer-T2 | 2020-09-18 10:00 | 2020-09-18 11:02 | 1:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Dhamrai | 132/33 kV Transformer-T1 | 2020-09-19 07:30 | 2020-09-19 07:57 | 0:27 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-09-19 08:00 | 2020-09-19 17:16 | 9:16 | S/O | Due to D/W work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T2 | 2020-09-19 11:21 | 2020-09-19 13:22 | 2:01 | S/O | Due to maintenance work | 0 | 0 | No interruption
Dhamrai | 132/33 kV Transformer-T1 | 2020-09-19 14:16 | 2020-09-19 18:42 | 4:26 | S/O | Due to project work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T2 | 2020-09-20 06:43 | 2020-09-20 07:56 | 1:13 | S/O | Due to C/M work | 15 | 18.25 | Power interruption
Netrakona | 132/33 kV Transformer-T3 | 2020-09-20 15:34 | 2020-09-20 16:36 | 1:02 | S/O | Due to maintenance work | 35 | 36.1667 | Power interruption
Mymensingh | 132/33 kV Transformer-T1 | 2020-09-21 06:25 | 2020-09-21 11:42 | 5:17 | S/O | Due to C/M work | 80 | 422.6667 | Power interruption
Tangail | 132/33 kV Transformer-T1 | 2020-09-21 08:20 | 2020-09-21 12:54 | 4:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T2 | 2020-09-21 13:30 | 2020-09-21 13:55 | 0:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | 33 kV Bus-A | 2020-09-22 09:33 | 2020-09-22 11:31 | 1:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T2 | 2020-09-23 07:07 | 2020-09-23 10:20 | 3:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformers-T-3 | 2020-09-23 07:11 | 2020-09-23 08:51 | 1:40 | S/O | Due to maintenance work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T4 | 2020-09-24 07:10 | 2020-09-24 09:28 | 2:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T-2 | 2020-09-24 10:07 | 2020-09-24 13:54 | 3:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 230/132 kV Transformer-T-2 | 2020-09-24 15:30 | 2020-09-24 17:40 | 2:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Manikganj | 132/33 kV Transformer-T3 | 2020-09-26 06:26 | 2020-09-26 12:06 | 5:40 | S/O | Due to D/W work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T3 | 2020-09-26 07:37 | 2020-09-26 09:45 | 2:08 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2020-09-26 07:37 | 2020-09-26 09:34 | 1:57 | S/O |  | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T1 | 2020-09-26 08:05 | 2020-09-26 18:05 | 10:00 | S/O | Due to D/W work | 20 | 200 | Power interruption
Mymensingh | 132/33 kV Transformer-T2 | 2020-09-26 19:12 | 2020-09-26 19:34 | 0:22 | S/O | Due to nutral atural grounding work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformers-T-3 & T4 with 33 kV Bus | 2020-09-26 07:18 | 2020-09-26 10:28 | 3:10 | S/O | Due to maintenance work | 25 | 79.5833 | Power interruption 07:18 to 10:29
Rajendrapur | 132/33 kV Transformer-T2 | 2020-09-27 10:00 | 2020-09-27 13:37 | 3:37 | S/O | Due to project work | 0 | 0 | No interruption
Manikganj | 132/33 kV Transformer-GT3 | 2020-09-28 06:20 | 2020-09-28 07:55 | 1:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajendrapur | 132/33 kV Transformers-T-1 | 2020-09-28 13:20 | 2020-09-28 13:55 | 0:35 | S/O | Due to protection work | 0 | 0
| 132/33 kV Transformers-T-2 | 2020-09-28 13:20 | 2020-09-28 13:47 | 0:27 | S/O |  | 98 | 44.1 | Power interruption
Mymensingh | 132/33 kV Transformer-T3 | 2020-09-29 07:10 | 2020-09-29 09:58 | 2:48 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV Bus-A | 2020-09-29 08:52 | 2020-09-29 16:52 | 8:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132 kV main Bus |  | 2020-09-29 11:19 |  | S/O | After maintenance work | 0 | 0 | No interruption
Rajendrapur | 132/33 kV Transformer-T-1 | 2020-09-30 09:06 | 2020-09-30 10:02 | 0:56 | S/O | Due to D/W work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV Transformer-GT-2 |  | 2020-09-30 16:51 |  | S/O | After maintenance work | 0 | 0 | No interruption
|  |  | Total : | 153:08 |  | Unserved Energy: |  | 1561.3167
Page: 2/4 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:September 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (South) Grid Circle :
Ghorashal | 230/132 kV Transformer-AT02 | 2020-09-02 07:22 | 2020-09-02 18:03 | 10:41 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | 132/33 kV Transformer-T1 | 2020-09-11 06:20 | 2020-09-11 11:05 | 4:45 | S/O | Due to C/M work | 15 | 71.25 | Power interruption
Aurahati P/P | Aurahati P/P-Kamragirchar 132 kV line | 2020-09-11 09:37 | 2020-09-11 09:37 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Ghorashal | 230/132 kV Transformer-T2 | 2020-09-13 07:37 | 2020-09-13 10:05 | 2:28 | S/O | Due to maintenance work | 0 | 0 | No interruption
Siddhirganj | 230/132 kV Transformer-MTR01 | 2020-09-14 07:13 | 2020-09-14 09:32 | 2:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | 132 kV capacitor Bank-1 |  | 2020-09-14 19:40 |  | S/O | After maintenance work | 0 | 0 | No interruption
| 132 kV capacitor Bank-1 |  | 2020-09-14 19:40 |  | S/O | Due to high temperature | 0 | 0 | No interruption
Sonargaon | 132/33 kV Transformer-T1 & 33 kV Bus | 2020-09-15 07:05 | 2020-09-15 09:20 | 2:15 | S/O | Due to maintenance work | 20 | 45 | Power interruption
Rampura | 132 kV capacitor bank-1 |  | 2020-09-15 16:23 |  | S/O | After maintenance work | 0 | 0 | No interruption
Narsinghdi | 132/33 kV Transformer-T3 | 2020-09-18 07:22 | 2020-09-18 09:46 | 2:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | 132/33 kV Transformer-T2 | 2020-09-24 14:13 | 2020-09-24 19:22 | 5:09 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorashal | 230/132 kV Transformer-T1 | 2020-09-25 06:29 | 2020-09-25 09:37 | 3:08 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230 kV Bus-2 | 2020-09-25 06:36 | 2020-09-25 09:28 | 2:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Maniknagar | 230/132 kV Transformer-Tr-1 | 2020-09-25 08:36 | 2020-09-25 17:38 | 9:02 | S/O | Due to C/M work | 5 | 45.1667 | Power interruption
| 230/132 kV Transformer-Tr-2 | 2020-09-26 08:32 | 2020-09-26 17:50 | 9:18 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 54:21 |  | Unserved Energy: |  | 161.4167
Chattogram Grid Circle :
Hathazari | 132 kV main Bus | 2020-09-01 02:06 | 2020-09-01 08:53 | 6:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Madunaghat | 132/33 kV Transformer-T2 | 2020-09-02 10:42 | 2020-09-02 15:12 | 4:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Baraulia | 132/33 kV Transformer-T1 | 2020-09-03 10:10 | 2020-09-03 11:45 | 1:35 | S/O | Due to DS system | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-09-03 12:20 | 2020-09-03 12:30 | 0:10 | S/O |  | 0 | 0 | No interruption
Madunaghat | 132/33 kV Transformer-T2 | 2020-09-04 08:42 | 2020-09-04 16:32 | 7:50 | S/O | Due to maintenance of 33 kV Bus | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-09-05 07:09 | 2020-09-05 18:04 | 10:55 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-09-09 10:45 | 2020-09-09 12:20 | 1:35 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-09-11 08:14 | 2020-09-11 20:59 | 12:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Bakuila | 132/33 kV Transformer-T2 | 2020-09-14 06:06 | 2020-09-14 06:54 | 0:48 | S/O | Due to C/M work | 0 | 0 | No interruption
Chandraghona | 132/33 kV Transformer-T1 | 2020-09-14 07:11 | 2020-09-14 08:55 | 1:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Halishahar | 132/33 kV Transformer-T3 & 33 kV Bus | 2020-09-18 07:34 | 2020-09-18 09:54 | 2:20 | S/O | Due to installation work | 20 | 46.6667 | Power interruption
| 132/33 kV Transformer-T1 | 2020-09-27 21:45 | 2020-09-27 22:14 | 0:29 | S/O | Due to maintenance work | 0 | 0 | No interruption
Agrabad | 132 kV Bus-1 | 2020-09-28 10:23 | 2020-09-28 10:23 | 0:00 | S/O | Due to maintenance work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-09-29 14:24 | 2020-09-29 14:43 | 0:19 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-09-29 14:46 | 2020-09-29 15:09 | 0:23 | S/O |  | 0 | 0 | No interruption
Khagrachari | 132/33 kV Transformer-T1 | 2020-09-30 17:01 | 2020-09-30 17:35 | 0:34 | S/O | Due to C/M work | 8 | 4.5333 | Power interruption
|  |  | Total : | 52:44 |  | Unserved Energy : |  | 51.2
Cumilla Grid Circle :
Kulaura | 132/33 kV Transformer-T1 | 2020-09-02 07:15 | 2020-09-02 08:38 | 1:23 | S/O | Due to C/M work | 15 | 20.75 | Power interruption
| 132/33 kV Transformer-T2 | 2020-09-02 07:15 | 2020-09-02 07:48 | 0:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Chandpur | 132/33 kV Transformer-T1 | 2020-09-06 10:18 | 2020-09-06 11:32 | 1:14 | S/O | Due to high temperature of Y-phase bushing | 0 | 0 | No interruption
Ashuganj | 230 kV Bus-2 | 2020-09-07 07:15 | 2020-09-07 16:52 | 9:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla (N) | 132/33 kV Transformer-T3 | 2020-09-08 10:08 | 2020-09-08 10:33 | 0:25 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2020-09-08 10:37 | 2020-09-08 11:23 | 0:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | 230 kV Bus-1 | 2020-09-08 09:50 | 2020-09-08 18:32 | 8:42 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV Bus-1 |  | 2020-09-10 17:00 |  | S/O | After maintenance work | 0 | 0 | No interruption
Feni | 132/33 kV Transformer-T1 | 2020-09-14 06:45 | 2020-09-14 06:45 | 0:00 | S/O | Due to DC Ckt unhelthy | 0 | 0 | No interruption
Daudkandi | 132/33 kV Transformer-T3 | 2020-09-14 07:01 | 2020-09-14 08:45 | 1:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Feni | 132/33 kV Transformer-T2 | 2020-09-14 10:51 | 2020-09-14 14:26 | 3:35 | S/O | Due to tap changer problem | 0 | 0 | No interruption
Ashuganj | 132 kV Bus-2 | 2020-09-15 06:14 | 2020-09-15 06:14 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV Bus-2 |  | 2020-09-15 15:36 |  | S/O | After maintenance work | 0 | 0 | No interruption
Kulaura | 132/33 kV Transformers-T1 | 2020-09-16 07:00 | 2020-09-16 12:22 | 5:22 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 | 2020-09-16 07:00 | 2020-09-16 13:24 | 6:24 |  |  | 0 | 0 | No interruption
Fenchuganj | 132 kV Bus-1 | 2020-09-18 09:11 | 2020-09-18 18:05 | 8:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Chowmuhani | 132/33 kV Transformer-T3 | 2020-09-18 07:58 | 2020-09-18 09:35 | 1:37 | S/O | Due to 33 kV loop remove | 30 | 48.5 | Power interruption
Shahjibazar | 132/33 kV Transformer-T2 | 2020-09-19 08:22 | 2020-09-19 13:56 | 5:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Feni | 132/33 kV Transformer-T2 | 2020-09-19 09:50 | 2020-09-19 15:36 | 5:46 | S/O | Due to maintenance work | 0 | 0 | No interruption
Page: 3/4 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:September 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Feni | 132/33 kV Transformer-T2 | 2020-09-19 21:40 | 2020-09-19 23:16 | 1:36 | S/O | Due to maintenance of CT | 0 | 0 | No interruption
Shahjibazar | 132/33 kV Transformer-T2 | 2020-09-20 07:00 |  |  | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV Transformers-T1 & T2 | 2020-09-21 08:18 | 2020-09-21 14:44 | 6:26 | S/O | Due to C/M work | 0 | 0 | No interruption
Chatak | 132/33 kV Transformer-T1 | 2020-09-21 11:22 | 2020-09-21 11:26 | 0:04 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-09-21 11:37 | 2020-09-21 11:47 | 0:10 | S/O | Due to C/M work | 5 | 0.83333 | Power interruption
| 132/33 kV Transformer-T3 | 2020-09-21 12:00 | 2020-09-21 12:08 | 0:08 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-09-21 16:39 | 2020-09-21 16:39 | 0:00 | S/O | Due to compressor problem | 0 | 0 | No interruption
Sylhet | 132/33 kV Transformer-T2 | 2020-09-23 07:08 | 2020-09-23 08:24 | 1:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Daudkandi | 132/33 kV Transformer-T3 with 33 kV bus | 2020-09-24 07:05 | 2020-09-24 08:12 | 1:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | 132 kV Bus-2 | 2020-09-24 07:08 | 2020-09-24 08:38 | 1:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahjibazar | 132/33 kV Transformers-T4 & T6 | 2020-09-27 11:09 | 2020-09-27 13:45 | 2:36 | S/O | Due to protection work | 0 | 0 | No interruption
Kulaura | 132/33 kV Transformer-T2 | 2020-09-30 06:03 | 2020-09-30 09:26 | 3:23 | S/O | Due to D/W work | 0 | 0 | No interruption
Sylhet | 132/33 kV Transformer-T1 | 2020-09-30 06:39 | 2020-09-30 13:27 | 6:48 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 86:40 |  | Unserved Energy : |  | 70.0833
Khulna Grid Circle :
Faridpur | 33 kV Bus section -4 | 2020-09-04 07:07 | 2020-09-04 08:17 | 1:10 | S/O | Due to 33 kV CB commissioning | 30 | 35 | Power interruption
Gopalganj | 400/132 kV Transformer-T01 | 2020-09-04 11:02 | 2020-09-04 13:03 | 2:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Goalpara | 33 kV Bus and 132/132 kV Transformer T2 & T6 | 2020-09-05 06:24 | 2020-09-05 11:05 | 4:41 | S/O | Due to C/M work | 0 | 0 | No interruption
| 34 kV Bus and 132/132 kV Transformer T6 | 2020-09-05 06:24 | 2020-09-05 13:14 | 6:50 | S/O |  | 0 | 0 | No interruption
Khulna© | 132/33 kV Transformer-T1 | 2020-09-06 08:21 | 2020-09-06 23:03 | 14:42 | S/O | Due to 33 kV feeder fault | 0 | 0 | No interruption
Chuadanga | 132/33 kV Transformer-T1 | 2020-09-06 22:22 | 2020-09-06 23:30 | 1:08 | S/O | Due to maintenance work by PBS | 45 | 51 | Power interruption
Khulna© | 132/33 kV Transformer-T3 | 2020-09-12 10:21 | 2020-09-12 11:54 | 1:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Barishal(N) | 132/33 kV Transformer-T4 | 2020-09-18 09:17 | 2020-09-18 15:29 | 6:12 | S/O | Due to D/W work | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T3 | 2020-09-28 10:25 | 2020-09-28 11:04 | 0:39 | S/O | Due to conductor armoring work | 7 | 4.55 | Power interruption
Noapara | 132/33 kV Transformer-T1 | 2020-09-28 10:51 | 2020-09-28 15:29 | 4:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Goalpara | 132/33 kV Transformer-T5 | 2020-09-30 07:06 | 2020-09-30 10:05 | 2:59 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 46:33 |  | Unserved Energy : |  | 90.55
HVDC Grid Circle :
Banapole | 132/33 kV Transformer-T-1 | 2020-09-23 07:35 | 2020-09-23 08:59 | 1:24 | S/O | Due to auxiliary Transformer fuse | 10 | 14 | Power interruption
Shahjadpur | 132/33 kV Transformer-T-1 |  | 2020-09-24 18:05 |  | S/O | After maintenance work | 0 | 0 | No interruption
Benapole | 132/33 kV Transformer-T-1 | 2020-09-25 07:27 | 2020-09-25 10:03 | 2:36 | S/O | Due to replacement work | 10 | 26 | Power interruption
Ishurdi | 230/132 kV Transformer-Tr1 | 2020-09-25 07:50 | 2020-09-25 12:07 | 4:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Pabna | 132/33 kV Transformer-T-3 | 2020-09-26 06:52 | 2020-09-26 08:56 | 2:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Chuadanga | 132/33 kV Transformer-T-1 | 2020-09-29 07:06 | 2020-09-29 07:06 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 10:21 |  | Unserved Energy : |  | 40
Bogura Grid Circle:
Rangpur | 33 kV Bus-2 & 3 | 2020-09-02 06:35 | 2020-09-02 07:42 | 1:07 | S/O | Due to C/M work | 70 | 78.1667 | Power interruption
Sherpur | 132/33 kV Transformer-T2 & T3 | 2020-09-05 07:40 | 2020-09-05 11:04 | 3:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | 132/33 kV Transformer-T3 | 2020-09-05 08:35 | 2020-09-05 15:35 | 7:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformer-T2 & 33 kV bus | 2020-09-07 00:13 | 2020-09-07 01:08 | 0:55 | S/O | Due to maintenance work | 40 | 36.6667 | Power interruption
Mohastanghor | 132/33 kV Transformer-T2 & 33 kV bus | 2020-09-08 07:41 | 2020-09-08 11:19 | 3:38 | S/O | Due to attending CT & its associate isolator | 15 | 54.5 | Power interruption
Barapukuria | 132/33 kV Transformer-T4 & Ckt-2 | 2020-09-12 11:35 | 2020-09-12 12:35 | 1:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Sirajganj | 132/33 kV Transformer-T-1 | 2020-09-13 21:11 | 2020-09-13 21:47 | 0:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformer-T-2 | 2020-09-16 07:02 | 2020-09-16 10:25 | 3:23 | S/O | Due to C/M work | 65 | 219.9167 | Power interruption
Purbasadipur | 132 kV Bus | 2020-09-16 09:29 | 2020-09-16 11:53 | 2:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Saidpur | 132/33 kV Transformers-T-2 | 2020-09-18 09:40 | 2020-09-18 18:15 | 8:35 | S/O | Due to D/W work | 45 | 386.25 | Power interruption
| 132/33 kV Transformers-T-3 | 2020-09-18 09:40 | 2020-09-18 18:17 | 8:37 | S/O
Natore | 132/33 kV Transformers-T1 & T2 | 2020-09-19 06:09 | 2020-09-19 10:40 | 4:31 | S/O | Due to maintenance work | 65 | 293.5833 | Power interruption
Palashbari | 132/33 kV Transformer-T-1 | 2020-09-19 06:33 | 2020-09-19 07:15 | 0:42 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T-2 | 2020-09-19 07:25 | 2020-09-19 14:23 | 6:58 | S/O |  | 0 | 0 | No interruption
Saidpur | 132/33 kV Transformer-T-3 | 2020-09-19 08:17 | 2020-09-19 09:20 | 1:03 | S/O | Due to D/W work | 0 | 0 | No interruption
C.nwabganj | 132/33 kV Transformer-T-4 | 2020-09-19 09:43 | 2020-09-19 11:54 | 2:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Amnura | 132/33 kV Transformer-T-1 | 2020-09-19 07:18 | 2020-09-19 08:05 | 0:47 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T-2 | 2020-09-19 08:12 | 2020-09-19 08:57 | 0:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV Transformer-T-1 & 33 kV Bus | 2020-09-19 20:32 | 2020-09-19 21:40 | 1:08 | S/O | Due to C/M work | 50 | 56.6667 | Power interruption
Page: 4/4 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:September 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle:
C.nwabganj | 132/33 kV Transformer-T-2 | 2020-09-20 21:26 | 2020-09-21 11:44 | 14:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi | 230/132 kV Transformer-T-2 was charged |  | 2020-09-20 21:03
Rangpur | 132/33 kV Transformer-T-2 | 2020-09-21 06:32 | 2020-09-21 08:45 | 2:13 |  |  | 60 | 133 | Power interruption
Ruppur | 132/33 kV Transformer-T-1 | 2020-09-21 08:48 | 2020-09-21 16:56 | 8:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi | 230/132 kV Transformer-T-1 |  | 2020-09-21 12:45 |  | S/O | After maintenance work | 0 | 0 | No interruption
| 230/132 kV Transformer-T-2 |  | 2020-09-22 16:45 |  | S/O | After maintenance work | 0 | 0 | No interruption
| 230/132 kV Transformer-T-1 | 2020-09-22 16:55 | 2020-09-22 16:55 | 0:00 | S/O | Due to testing of 132/33 kV Transformer T2 | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformer-T-2 | 2020-09-23 08:02 | 2020-09-23 16:45 | 8:43 | S/O | Due to D/W work | 60 | 523 | Power interruption
Bogura | 132/33 kV Transformer-T-2 | 2020-09-24 12:01 | 2020-09-24 12:54 | 0:53 | S/O | Due to 33kV feeder problem | 10 | 8.8333 | Power interruption
| 132/33 kV Transformer-T-1 & 33 kV Bus | 2020-09-25 15:09 | 2020-09-25 15:38 | 0:29 | S/O | Due to PBS work | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T-1 | 2020-09-26 08:05 | 2020-09-26 18:05 | 10:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Sherpur(Bogura) | 132/33 kV Transformer-T-1 | 2020-09-27 10:28 | 2020-09-27 17:30 | 7:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | 132/33 kV Transformer-T-1 | 2020-09-27 12:25 | 2020-09-27 15:59 | 3:34 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T-2 | 2020-09-27 16:21 | 2020-09-27 18:05 | 1:44 | S/O | Due to D/W work | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformers-T-1 & T2 | 2020-09-28 08:25 | 2020-09-28 09:55 | 1:30 | S/O | Due to C/M work | 50 | 75 | Power interruption
C.nawabganj | 132/33 kV Transformer-T-2 |  | 2020-09-29 15:05 |  | S/O | After maintenance work | 0 | 0 | No interruption
| 132/33 kV Transformer-T-3 | 2020-09-29 16:02 | 2020-09-29 17:40 | 1:38 | S/O | Due to project work | 0 | 0 | No interruption
|  |  | Total : | 118:56 |  | Unserved Energy : |  | 1865.5833
Others :
Ashuganj | 230/132 kV Transformer-OAT2 |  | 2020-09-15 09:15 |  | S/O | After maintenance work | 0 | 0 | No interruption
T.K chemical | 132/33 kV Transformer-T-1 |  | 2020-09-29 08:52 |  | S/O | After maintenance work | 0 | 0 | No interruption
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 522:43 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/3 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:September 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar | Aminbazar-Savar 132 kV line | 2020-09-01 09:30 |  |  | S/O | Due to maintenance work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Bibiyana(S) 230 kV line | 2020-09-01 11:56 | 2020-09-01 14:30 | 2:34 | S/O | Due maintenance work | 0 | 0 | No interruption
Jamalpur | Jamalpur S/S-Jamalpur 95 MW P/S 132 kV line | 2020-09-02 09:06 | 2020-09-02 11:15 | 2:09 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | Savar-Manikganj 132 kV line-1 |  | 2020-09-02 14:47 |  | S/O | After maintenance work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV lie-2 | 2020-09-03 09:05 | 2020-09-03 16:10 | 7:05 | S/O | Due to C/M work | 15 | 106.25 | Power interruption
Tangail | Tangail-Kaliakoir 132 kV line-1 | 2020-09-04 09:41 | 2020-09-04 11:52 | 2:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-2 | 2020-09-06 11:25 | 2020-09-06 14:17 | 2:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Bosila P/P 132 kV line | 2020-09-08 09:25 | 2020-09-08 21:15 | 0:42 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-1 |  | 2020-09-08 15:58 |  | S/O | After maintenance work | 0 | 0 | No interruption
| Mymensingh-Kishoreganj 132 kV line-2 |  | 2020-09-08 17:45 |  | S/O | After maintenance work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-1 |  | 2020-09-08 16:03 |  | S/O | After maintenance work | 0 | 0 | No interruption
| Mymensingh-Netrakona 132 kV line-2 |  | 2020-09-08 17:47 |  | S/O | After maintenance work | 0 | 0 | No interruption
Mymensingh | Mymensingh-RPCL 132 kV line-1 |  | 2020-09-08 16:04 |  | S/O | After maintenance work | 0 | 0 | No interruption
| Mymensingh-RPCL 132 kV line-2 |  | 2020-09-08 17:47 |  | S/O |  | 0 | 0 | No interruption
| Mymensingh-Jamalpur 132 kV line-1 |  | 2020-09-08 22:33 |  | S/O | After maintenance work | 0 | 0 | No interruption
| Mymensingh-Jamalpur 132 kV line-2 |  | 2020-09-08 15:59 |  | S/O |  | 0 | 0 | No interruption
Bibiyana | Bibiyana-Bibiyana P/P 230 kV line |  | 2020-09-16 16:03 |  | S/O | After maintenance work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-1 | 2020-09-18 12:32 | 2020-09-18 17:48 | 5:16 | S/O | Due to CB problem | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV line-1 | 2020-09-19 09:30 | 2020-09-19 20:14 | 10:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-2 | 2020-09-19 10:20 | 2020-09-19 13:47 | 3:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-1 | 2020-09-19 09:46 | 2020-09-19 13:47 | 4:01 | S/O | Due to C/M work | 0 | 0 | No interruption
| Mymensingh-Kishoreganj 132 kV line-2 | 2020-09-19 14:06 | 2020-09-19 14:55 | 0:49 | S/O | Due to tree trimming | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara sector-18 132 kV line | 2020-09-20 10:26 | 2020-09-20 14:33 | 4:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-1 | 2020-09-21 06:45 | 2020-09-21 11:42 | 4:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV line-1 | 2020-09-21 09:48 | 2020-09-21 17:53 | 8:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Bibiyana 400 kV CKt-1 | 2020-09-25 08:20 | 2020-09-25 16:26 | 8:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV line-1 | 2020-09-27 07:52 |  |  | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-2 | 2020-09-27 09:15 | 2020-09-27 15:27 | 6:12 | S/O | Due to replacement work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-1 | 2020-09-27 09:01 | 2020-09-27 12:56 | 3:55 | S/O | Due to compressor problem | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakir 132 kV line-1 | 2020-09-28 06:15 | 2020-09-28 10:03 | 3:48 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-1 | 2020-09-28 07:15 | 2020-09-28 14:31 | 7:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV line-1 | 2020-09-28 08:03 | 2020-09-28 18:19 | 10:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-1 |  | 2020-09-29 08:52 |  | S/O | After maintenance work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-1 | 2020-09-29 08:45 | 2020-09-29 17:15 | 8:30 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 107:02 |  | Unserved Energy: |  | 106.25
Dhaka (South) Grid Circle :
Madanganj | Madanganj-Madanganj P/S 132 kV line | 2020-09-01 07:41 | 2020-09-01 07:41 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 230 kV line-1 | 2020-09-02 12:52 | 2020-09-02 14:07 | 1:15 | S/O | Due to RTS work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Narsinghdi 132 kV line-1 | 2020-09-07 09:19 | 2020-09-07 13:06 | 3:47 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ghorashal-Ashuganj 132 kV line-1 |  | 2020-09-11 15:50 |  | S/O | After maintenance work | 0 | 0 | No interruption
| Ghorashal-Ashuganj 132 kV line-2 | 2020-09-12 07:29 | 2020-09-12 07:29 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj 132 kV line-1 | 2020-09-12 12:22 | 2020-09-12 15:32 | 3:10 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ghorashal-Ashuganj 132 kV line-1 |  | 2020-09-12 12:55 |  | S/O | After maintenance work | 0 | 0 | No interruption
| Ghorashal-Joyvevpur 132 kV line-2 | 2020-09-20 08:45 | 2020-09-20 11:42 | 2:57 | S/O | For safety outage | 0 | 0 | No interruption
Bhulta | Bhulta-Haripur 230 kV line-2 | 2020-09-21 10:31 | 2020-09-21 12:10 | 1:39 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Tongi 230 kV line-2 | 2020-09-25 06:20 | 2020-09-25 10:07 | 3:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj -Haripur 132 kV line-2 | 2020-09-28 07:57 | 2020-09-28 09:56 | 1:59 | S/O | Due to C/M work | 0 | 0 | No interruption
Sonargaon | Sonargaon-Daudkandi 132 kV line-1 | 2020-09-28 14:08 | 2020-09-28 16:43 | 2:35 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 21:09 |  | Unserved Energy: |  | 0
Page: 2/3 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:September 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Chattogram Grid Circle :
Kulshi | Kulshi-Rampur 132 kV line-1 | 2020-09-02 10:45 | 2020-09-04 12:48 | 50:03 | S/O | Due to C/M work | 0 | 0 | No interruption
| Kulshi-Rampur 132 kV line-2 | 2020-09-02 10:46 | 2020-09-03 19:10 | 32:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Halishahar | Halishahar-Rampur 132 kV line-2 | 2020-09-03 15:34 | 2020-09-03 19:25 | 3:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV line-2 | 2020-09-06 06:03 | 2020-09-06 07:20 | 1:17 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 87:35 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Ashuganj | Ashuganj-Ashuganj(S) 230 kV line-2 | 2020-09-02 09:27 | 2020-09-02 11:00 | 1:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-1 |  | 2020-09-05 20:49 |  | S/O | After maintenance work | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kV line-1 | 2020-09-06 09:10 | 2020-09-06 13:58 | 0:42 | S/O | Due to D/W work | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj P/S 132 kV line | 2020-09-06 09:07 | 2020-09-06 13:40 | 4:33 | S/O | Due to C/M work | 0 | 0 | No interruption
| Sylhet-Fenchuganj S/S 132 kV line | 2020-09-06 14:45 | 2020-09-06 16:59 | 2:14 | S/O | Due to protection relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2020-09-06 07:19 | 2020-09-06 07:19 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ashuganj-Ashuganj(S) 230 kV line-2 | 2020-09-08 09:28 | 2020-09-08 18:39 | 9:11 | S/O | Due to Cbus problem | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV line-2 | 2020-09-08 08:08 | 2020-09-08 18:32 | 10:24 | S/O | Due to Bus problem | 0 | 0 | No interruption
Feni | Feni-Chowddagram 132 kV line-1 | 2020-09-09 09:26 | 2020-09-09 14:49 | 5:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-2 | 2020-09-12 09:06 | 2020-09-12 12:14 | 3:08 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 kV line-2 | 2020-09-15 11:01 | 2020-09-15 13:40 | 2:39 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 kV line-1 | 2020-09-15 13:41 | 2020-09-15 15:48 | 2:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Chatak | Chatak-Sunamganj 132 kV line |  | 2020-09-15 14:44 |  | S/O | After maintenance work | 0 | 0 | No interruption
Bibiyana | Bibiyana 400kV-Bibiyana-3 400 kV ST line |  | 2020-09-20 14:07 |  |  | New connection
| Bibiyana 400 kV-Bibiyana-3 400 kV GT line |  | 2020-09-20 14:14
Bibiyana | Bibiyana-Kaliakoir 400 kV line-1 | 2020-09-24 08:22 | 2020-09-24 16:41 | 8:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Chattak 132 kV line-1 | 2020-09-29 09:40 | 2020-09-29 10:50 | 1:10 | S/O | Due to maintenance work | 0 | 0 | No interruption
| Sylhet-Chattak 132 kV line-2 | 2020-09-29 10:56 | 2020-09-29 16:17 | 5:21 | S/O | Due to maintenance work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Chattak 132 kV line-1 | 2020-09-29 16:24 | 2020-09-29 20:55 | 4:31 | S/O | Due to maintenance work | 0 | 0 | No interruption
Sylhet | Sylhet-Chattak 132 kV line-1 |  | 2020-09-29 17:53 |  | S/O | After maintenance work | 0 | 0 | No interruption
| Sylhet-Chattak 132 kV line-2 |  | 2020-09-29 13:42 |  | S/O | After maintenance work | 0 | 0 | No interruption
|  |  | Total : | 61:15 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Khulna(C) | Khulna©-Goalpara 132 kV line-1 | 2020-09-01 08:08 | 2020-09-01 09:08 | 1:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Khulna©-Khulna 225 MW 132 kV line-2 | 2020-09-01 09:24 | 2020-09-01 11:34 | 2:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line-1 | 2020-09-02 11:43 | 2020-09-02 11:58 | 0:15 | S/O | Due to meter installation work | 0 | 0 | No interruption
Faridpur | Faridpur-Bheramara 132 kV line-1 | 2020-09-03 15:04 | 2020-09-03 15:59 | 0:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Gopalganj | Gopalganj-Payra 400 kV line-2 | 2020-09-04 10:50 | 2020-09-04 13:41 | 2:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna(C) | Khulna©-KPCL 132 kV line-2 | 2020-09-09 07:25 | 2020-09-09 08:12 | 0:47 | S/O | Due to C/M work | 0 | 0 | No interruption
| Khulna©-NWPGCL 132 kV line-1 | 2020-09-10 07:11 | 2020-09-10 10:14 | 3:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna(C) | Khulna©-Goalpara 132 kV line-1 | 2020-09-12 07:25 | 2020-09-12 09:04 | 1:39 | S/O | Due to C/M work | 0 | 0 | No interruption
| Khulna©-Goalpara 132 kV line-2 | 2020-09-12 09:05 | 2020-09-12 10:10 | 1:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna(N) | Khulna(N)-Gopalpara 132 kV Ckt | 2020-09-19 06:31 | 2020-09-19 12:36 | 6:05 | S/O | Due to loop changing | 0 | 0 | No interruption
Khulna(C) | Khulna©-Noapara 132 kV line | 2020-09-26 09:42 | 2020-09-26 18:36 | 8:54 | S/O | Due to protection work | 0 | 0 | No interruption
| Khulna©-Noapara 132 kV line-1 | 2020-09-27 10:30 | 2020-09-27 14:54 | 4:24 | S/O | Due to protection work | 0 | 0 | No interruption
|  |  | Total : | 33:08 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Bheramara(GK) | Bheramara(GK)-Bheramara 230 kV line-1 & 2 | 2020-09-12 07:15 | 2020-09-12 10:40 | 3:25 | S/O | Due to D/W work | 39 | 133.25 | Power interruption
Ishurdi | Ishurdi-Pabna 132 kV line | 2020-09-15 08:04 | 2020-09-15 18:45 | 10:41 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ishurdi-Bheramara 132 kV line-1 | 2020-09-16 10:36 | 2020-09-16 17:07 | 6:31 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ishurdi-Bheramara 230 kV line | 2020-09-18 08:08 | 2020-09-18 16:05 | 7:57 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ishurdi-Baghabari 132 kV line-1 | 2020-09-19 08:01 | 2020-09-19 12:38 | 4:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Bheramara HVDC | Bheramara HVDC-Rajshahi 230 kV line-1 | 2020-09-19 12:16 | 2020-09-20 20:57 | 32:41 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bheramara HVDC-Rajshahi (new)230 kV line-1 |  | 2020-09-21 16:32 |  | S/O | After maintenance work | 0 | 0 | No interruption
Noapara | Noapara-Jessore 132 kV line-1 | 2020-09-20 11:59 | 2020-09-20 15:38 | 3:39 | S/O | Due to CT problem | 0 | 0 | No interruption
| Noapara-Jessore 132 kV line-1 | 2020-09-20 15:38 | 2020-09-20 17:01 | 1:23 | S/O |  | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ruppur 132 kV line-1 | 2020-09-22 09:21 | 2020-09-22 16:58 | 7:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Page: 3/3 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:September 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :
Ishurdi | Ishurdi-Ghorashal 230 kV line-1 | 2020-09-25 14:44 | 2020-09-25 17:49 | 3:05 | S/O | Due to removing kite | 0 | 0 | No interruption
Pabna | Pabna-Ishurdi 132 kV line | 2020-09-28 07:47 | 2020-09-28 09:52 | 2:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahjadpur | Shahjadpur-Baghabari 132 kV line-2 | 2020-09-30 07:19 | 2020-09-30 08:23 | 1:04 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 84:45 |  | Unserved Energy: |  | 133.25
Bogura Grid Circle :
Barapukuria | Barapukuria-Saidpur 132 kV line-2 | 2020-09-04 08:57 | 2020-09-04 11:08 | 2:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | Bogura-Bogura Confidence P.P 132 kV lin-1 | 2020-09-04 13:45 | 2020-09-04 15:10 | 1:25 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bogura-Sirajganj 230 kV line-1 | 2020-09-07 07:03 | 2020-09-07 12:26 | 5:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi(N) | Rajshahi(N)-Rajshahi 132 kV line-2 | 2020-09-19 08:03 | 2020-09-19 09:30 | 1:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | Bogura-Sirajganj 230 kV line-1 | 2020-09-21 07:20 | 2020-09-21 11:56 | 4:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi | Rajshahi-Bheramara HVDC 230 kV line-1 | 2020-09-21 10:22 | 2020-09-21 10:22 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogura | Bogura-Sirajganj 230 kV line-2 | 2020-09-22 09:25 | 2020-09-22 14:11 | 4:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Ruppur | Ruppur-Ishurdi 132 kV line-2 | 2020-09-22 09:16 | 2020-09-22 16:43 | 7:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura(O) | Bogura(O)-Bogura(N) 132 kV line-1 | 2020-09-23 07:28 | 2020-09-23 08:43 | 1:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | Bogura-Sherpur 132 kV line-1 | 2020-09-28 10:29 | 2020-09-28 11:00 | 0:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | Bogura-Barapukuria 230 kV line-1 | 2020-09-28 12:59 | 2020-09-28 13:55 | 0:56 | S/O | Due to right of way | 0 | 0 | No interruption
Purbasadipur | Purbasadipur-Thakurgaon 132 kV line-1 | 2020-09-28 16:26 | 2020-09-28 16:35 | 0:09 | S/O | Due to protection work | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV line-1 | 2020-09-28 15:03 | 2020-09-28 15:23 | 0:20 | S/O | Due to protection work | 0 | 0 | No interruption
|  |  | Total : | 30:26 |  | Unserved Energy: |  | 0
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 425:20 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:September' 2020
| Area | Previous Month (August 2020) |  |  |  | Current Month (September 2020)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 23 | 6 | 45 | 74 | 24 | 14 | 88 | 126
2 | Dhaka (South) Grid Circle. | 20 | 8 | 24 | 52 | 19 | 7 | 27 | 53
3 | Chattogram Grid Circle. | 14 | 6 | 12 | 32 | 13 | 6 | 20 | 39
4 | Cumilla Grid Circle. | 23 | 10 | 30 | 63 | 20 | 8 | 51 | 79
5 | Khulna Grid Circle. | 11 | 24 | 17 | 52 | 7 | 8 | 23 | 38
6 | HVDC Grid Circle | 15 | 6 | 7 | 28 | 10 | 4 | 18 | 32
7 | Bogura Grid Circle. | 17 | 25 | 32 | 74 | 34 | 17 | 48 | 99
8 | Others | 1 |  |  | 1 | 3 |  | 2 | 5
9 | Total | 124 | 85 | 167 | 376 | 130 | 64 | 277 | 471
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:September' 2020
| Area | Previous Month (August 2020) |  |  |  | Current Month (September 2020)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 449.08 |  | 647.98 | 1097.06 | 545.89 | 1562.7 | 1667.57 | 3776.16
2 | Dhaka (South) Grid Circle. | 95.7 | 308.98 | 70 | 474.68 | 4186.55 |  | 161.42 | 4347.97
3 | Chattogram Grid Circle. | 24.6 | 304.17 | 485.67 | 814.44 | 159.08 | 25 | 51.2 | 235.28
4 | Cumilla Grid Circle. | 1089.5167 | 306.84 | 171.77 | 1568.1267 | 132.41 | 130.8 | 70.08 | 333.29
5 | Khulna Grid Circle. | 5686.77 | 544.87 | 90.56 | 6322.2 | 53.33 | 39.67 | 90.55 | 183.55
6 | HVDC Grid Circle | 0.63 | 173.1 | 23.43 | 197.16 | 30 | 99.33 | 173.25 | 302.58
7 | Bogura Grid Circle. | 1973.93 | 347.75 | 112.93 | 2434.61 | 311.75 | 293.75 | 1865.58 | 2471.08
8 | Others | Energy unserved ( MWH ) due to Total: 0; Energy unserved ( MWH ) due to Total: 0
9 | Total | 9320.2267 | 1985.71 | 1602.34 | 12908.2767 | 5419.01 | 2151.25 | 4079.65 | 11649.91
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:September' 2020
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 7 | 13 | 21 | 6 |  | 14 | 3240.35
2 | Dhaka (South) | 5031.6 | 2 | 3 | 5 | 1 |  | 4 | 279.92
3 | Chattogram | 2042 | 2 | 2 | 4 |  | 2 | 2 | 235.28
4 | Khulna | 2434 | 5 | 3 | 8 | 2 | 3 | 3 | 183.55
5 | HVDC | 5954.3 | 3 | 2 | 5 | 1 | 1 | 3 | 169.33
6 | Bogura | 3145.6 | 12 | 11 | 23 | 2 | 4 | 17 | 2354
7 | Cumilla | 2981 | 8 | 3 | 11 | 5 | 1 | 5 | 305.46
8 | Others | -
| Total | 30390.1 | [6 empty] | 6767.89
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.93%
2 | Dhaka (South) | 99.94%
3 | Chattogram | 99.92%
4 | Khulna | 99.83%
5 | HVDC | 99.99% | [6 empty] | Executive Engineer
6 | Bogura | 99.76% | [6 empty] | Information Management Division
7 | Cumilla | 99.86% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:September' 2020
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 2 | 1 | 3 | 1 | 1 | 1 | 535.8
2 | Dhaka (South) | 990.29 |  | 5 | - | 5 | 3 | 1 | 1 | 4068.05
3 | Chattogram | 917 | - | - | - | - | - | - | - | -
4 | Khulna | 1238.4 | - | - | - | - | - | - | - | -
5 | HVDC | 1325 | 501 | - | 1 | 1 | - | - | 1 | 133.25
6 | Bogura | 1803.3 | - | 6 | - | 6 | 5 | - | 1 | 117.08
7 | Cumilla | 1648.16 | - | 2 |  | 2 | 1 |  | 1 | 27.8333
8 | Others | - |  | - | - | - | - | - | - | -
| Total | 10176.6215 | 501 | [6 empty] | 4882.0133
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.82%
3 | Chattogram | 99.93%
4 | Khulna | 99.97%
5 | Bheramara (HVDC) | 99.98% | [7 empty] | Executive Engineer
6 | Bogura | 99.94% | [7 empty] | Information Management Division
7 | Cumilla | 99.93% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:September' 2020
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2020-09-18 | 18 | - | 8 | 9hour 28 min | 1 | 57 min | - | - | 1 | 3hour 19min | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/2 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:September' 2020
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Tongi | 2 | 0:26 | 122 | 52.8667 | Due to tripping of 132/33 kV Transformer-T2
|  | 0:08 | 80 | 10.6667
Mymensingh | 3 | 3:19 | 420 | 1393 | Due to tripping of 132/33 kV Transformer-T2
|  | 1:33 | 10 | 15.5 | Due to tripping of 132/33 kV Transformer-T3
|  | 0:14 | 110 | 25.6667 | Due to tripping of 132/33 kV Transformer-T1
Joydevpur | 2 | 0:32 | 20 | 10.6667 | Due to 33 kV CB burn
|  | 2:16 | 40 | 90.6667 | Due to tripping of 132/33 kV Transformer-T3
Mymensingh | 3 | 1:20 | 60 | 80 | Due to red-hot maintenance of 132/33 kV Transformer T1
|  | 0:44 | 480 | 352 | Due to fire at 33 kV incoming breaker
|  | 0:11 | 423 | 77.55 | Due to tripping of Mymensingh-Kishoreganj 132 kV both CKts
Jamalpur | 1 | 1:14 | 20 | 24.6667
Joydevpur | 3 | 0:27 | 30 | 13.5 | Due to S/D of132/33 kV Transformer-T2
|  | 6:18 | 40 | 252 | Due to S/D of132/33 kV Transformer-T3
|  | 0:22 | 20 | 7.3333
Mymensingh | 1 | 3:17 | 27 | 88.65
Netrakona | 1 | 4:06 | 10 | 41 | Due to S/D of132/33 kV Transformer-T2
Mymensingh | 1 | 2:00 | 25 | 50 | Due to S/D of132/33 kV Transformer-T1
Dhamrai | 1 | 10:54 | 26 | 283.4 | Due to S/D of132/33 kV Transformer-T3
Kabirpur | 1 | 1:13 | 15 | 18.25 | Due to S/D of132/33 kV Transformer-T2
Netrakona | 1 | 1:02 | 35 | 36.1667 | Due to S/D of132/33 kV Transformer-T3
Mymensingh | 1 | 5:17 | 80 | 422.6667 | Due to S/D of132/33 kV Transformer-T1
Tangail | 1 | 10:00 | 20 | 200
Jamalpur | 1 | 3:11 | 25 | 79.5833 | Due to S/D of132/33 kV Transformers-T3 & T4
Rajendrapur | 1 | 0:27 | 98 | 44.1 | Due to S/D of132/33 kV Transformer-T2
Kabirpur | 1 | 7:05 | 15 | 106.25 | Due to S/D of kabirpur-Manikganj 132 kV line-2
Narsinghdi | 1 | 1:08 | 45 | 51 | Due to tripping of 132/33 kV Transformer-T2
Hasnabad | 1 | 0:30 | 135 | 67.5 | Due to tripping of 132/33 kV Transformers-T1 ,T2 & T3
Haripur | 1 | 0:16 | 154 | 41.0667 | Due to tripping of Haripur-Bhulta 230 kV line-1
Hasnabad | 1 | 0:17 | 78 | 22.1 | Due to tripping of Hasnabad-Lalbagh 132 kV line
Ghorashal | 1 | 2:29 | 1564 | 3883.9333 | Due to tripping of Ghorashal-Ishurdi 230 kV line-1
Hasnabad |  | 0:09 | 123 | 18.45 | Due to tripping of Hasnabad-Shitalakha 132 kV line
| 2 | 0:50 | 123 | 102.5 | Due to tripping of Hasnabad-Brahmangaon 132 kV line
Siddhirganj |  | 4:45 | 15 | 71.25 | Due to S/D of132/33 kV Transformer-T1
Sonargaon | 1 | 2:15 | 20 | 45 | Due to S/D of 132/33 kV Transformer T1
Maniknagar | 1 | 9:02 | 5 | 45.1667 | Due to S/D of 230/132 kV Transformer Tr-1
Halishahar | 1 | 1:23 | 115 | 159.0833 | Due to tripping of 132/33 kV Transformers-T1 & T2
Hathazari | 1 | 1:00 | 25 | 25 | Due to red-hot maintenance of 132/33 kV Transformer T1
Halishahar | 1 | 2:20 | 20 | 46.6667 | Due to S/D of132/33 kV Transformer-T3 & 33 kV Bus
Khagrachari | 1 | 0:34 | 8 | 4.5333 | Due to S/D of 132/33 kV Transformer T1
Comilla(N) | 1 | 1:18 | 43 | 55.9 | Due to red-hot maintenance of 33 kV Bus
Fenchuganj | 1 | 0:59 | 27 | 26.55 | Due to tripping of 132/33 kV Transformer-T2
Chowmuhani | 1 | 0:23 | 120 | 46 | Due to tripping of 132/33 kV Transformers-T1 ,& T2
Sylhet | 1 | 0:26 | 30 | 13 | Due to tripping of 132/33 kV Transformer-T1
Shahjibazar | 1 | 0:05 | 104 | 8.6667 | Due to tripping of 132/33 kV Transformers-T4 & T2
Ramganj | 1 | 1:48 | 30 | 54 | Due to red-hot maintenance of 132/33 kV Transformer T2
Chowmuhani | 1 | 0:13 | 112 | 24.2667 | Due to tripping of 132/33 kV Transformers-T1 ,& T2
Sreemongal |  | 0:28 | 15 | 7 | Due to tripping of 132/33 kV Transformer-T1
Chatak | 1 | 0:16 | 26 | 6.9333 | Due to tripping of Chatak -Sunamganj 132 kV line
Fenchuganj | 1 | 0:57 | 22 | 20.9 | Due to tripping of Fenchuganj-Kulaura 132 kV line
Kulaura | 1 | 1:23 | 15 | 20.75 | Due to S/D of 132/33 kV Transformer T1
Chowmuhani | 1 | 1:37 | 30 | 48.5 | Due to S/D of 132/33 kV Transformer T3
Chatak | 1 | 0:10 | 5 | 0.83333 | Due to S/D of 132/33 kV Transformer T2
Page: 2/2 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:September' 2020
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Faridpur | 1 | 0:58 | 20 | 19.3333 | Due to red-hot maintenance of 132/33 kV Transformer T1
Patuakhali | 1 | 0:27 | 10 | 4.5
Bhandaria | 1 | 1:35 | 10 | 15.8333 | Due to red-hot maintenance of 132/33 kV Transformer T1
Bagerhat | 1 | 0:45 | 50 | 37.5 | Due to tripping of 132/33 kV Transformer-T1
Madaripur | 1 | 0:25 | 38 | 15.8333 | Due to tripping of 132/33 kV Transformers-T1 ,& T2
Faridpur | 1 | 1:10 | 30 | 35 | Due to S/D of 33 kV Bus-4
Chuadanga | 1 | 1:08 | 45 | 51 | Due to S/D of 132/33 kV Transformer T1
Faridpur | 1 | 0:39 | 7 | 4.55 | Due to S/D of 132/33 kV Transformer T3
Bottail | 1 | 0:25 | 50 | 20.8333 | Due to red-hot maintenance of 132/33 kV Transformer T1
Benapole | 1 | 0:45 | 40 | 30 | Due to tripping of 132/33 kV Transformers-T1 ,& T2
Chuadanga | 1 | 2:37 | 30 | 78.5 | Due to red-hot maintenance of 132/33 kV Transformer T1
Banapole | 1 | 1:24 | 10 | 14 | Due to S/D of 132/33 kV Transformer T1
Benapole | 1 | 2:36 | 10 | 26
Bheramara(GK) | 1 | 3:25 | 39 | 133.25 | Due to S/D of Bheramara(GK)-Bheramara 230 kV line-1 & 2
Purbasadipur | 1 | 2:10 | 30 | 65 | Due to red-hot maintenance of 132/33 kV Transformer T1
Rajshahi | 1 | 0:10 | 90 | 15 | Due to tripping of 132/33 kV Transformers-T1 ,T2 & T3
Naogaon | 2 | 0:50 | 35 | 72.9167 | Due to red-hot maintenance of 132/33 kV Transformer T1
|  | 0:10 | 25 | 4.1667 | Due to tripping of 132/33 kV Transformer-T2
Rangpur |  | 1:12 | 60 | 72 | Due to red-hot maintenance of 132/33 kV Transformer T3
Bogura | 5 | 1:18 | 25 | 32.5 | Due to tripping of 132/33 kV Transformers-T1 ,& T2
|  | 0:58 | 70 | 67.6667
|  | 0:44 | 55 | 40.3333 | Due to tripping of 132/33 kV Transformer-T4
|  | 0:35 | 60 | 35 | Due to tripping of 132/33 kV Transformers-T1 ,& T2
|  | 0:37 | 80 | 49.3333 | Due to tripping of 132/33 kV Transformer-T4
Palashbari | 1 | 1:05 | 18 | 19.5 | Due to red-hot maintenance of 132/33 kV Transformer T2
Naogaon | 2 | 1:30 | 10 | 10.8333
|  | 0:07 | 60 | 7 | Due to tripping of Naogaon-Niyamatpur 132 kV line
Thaurgaon |  | 0:11 | 50 | 9.1667 | Due to tripping of Thaurgaon-Purbasadipur 132 kV line
Saidpur | 2 | 0:10 | 9 | 1.5 | Due to tripping of Saidpur-Juldhaka 132 kV line
|  | 0:05 | 87 | 7.25 | Due to tripping of Thaurgaon-Purbasadipur 132 kV line-1
Rangpur | 1 | 4:28 | 10 | 44.6667 | Due to tripping of Rangpur-Kurigram 132 kV line
Mohastanghor | 1 | 0:19 | 150 | 47.5 | Due to tripping of Mohastanghor-Palashbari 132 k line-1 & 2
Rangpur | 1 | 1:07 | 70 | 78.1667 | Due to S/D of 33 kV Bus-2 &3
Rajshahi | 1 | 0:55 | 40 | 36.6667 | Due to S/D of 132/33 kV Transformer T2
Mohastanghor | 1 | 3:38 | 15 | 54.5
Rangpur | 1 | 3:23 | 65 | 219.9167
Saidpur | 1 | 8:35 | 45 | 386.25 | Due to S/D of 132/33 kV Transformer T2
Natore | 1 | 4:31 | 65 | 293.5833 | Due to S/D of 132/33 kV Transformers T1 & T2
Purbasadipur | 1 | 1:08 | 50 | 56.6667 | Due to S/D of 132/33 kV Transformer T1
Rangpur | 1 | 2:13 | 60 | 133 | Due to S/D of 132/33 kV Transformer T2
Rangpur | 1 | 8:43 | 60 | 523 | Due to S/D of 132/33 kV Transformer T2
Bogura | 1 | 0:53 | 10 | 8.8333
Rangpur | 1 | 1:30 | 50 | 75 | Due to S/D of 132/33 kV Transformers T1 & T2
| Total Unserved energy : |  |  | 11645.75 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:September'2020
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 136 | 2 | 2020-09-01 | 12:00
2 | Munsiganj | 132 | 18 | 2020-09-01 | 0:00
3 | Sonargaon | 93 | 29 | 2020-09-01 | 20:00
4 | Shyampur | 206 | 12 | 2020-09-01 | 9:00
5 | Bhulta | 212 | 30 | 2020-09-01 | 21:00
6 | Madanganj | 65 | 29 | 2020-09-01 | 0:00
7 | Shitalakhya | 128 | 14 | 2020-09-01 | 13:00
8 | Rahim steel | 25 | 1 | 2020-09-01 | 17:00
9 | Matuail | 87 | 6 | 2020-09-01 | 10:00
10 | Ghorasal | 90 | 28 | 2020-09-01 | 22:00
11 | Narsingdi | 174 | 19 | 2020-09-01 | 20:00
12 | Haripur (SBU) | 116 | 8 | 2020-09-01 | 13:00
13 | Ullon | 69 | 5 | 2020-09-01 | 19:00
14 | Hasnabad | 220 | 19 | 2020-09-01 | 22:00
15 | Magbazar | 119 | 20 | 2020-09-01 | 15:00
16 | Maniknagar | 118 | 2 | 2020-09-01 | 12:00
17 | Bangabhaban | 40 | 6 | 2020-09-01 | 10:00
18 | Narinda | 98 | 1 | 2020-09-01 | 14:00
19 | Dhanmondi | 199 | 9 | 2020-09-01 | 13:00
20 | Lalbag | 94 | 9 | 2020-09-01 | 13:00
21 | Madartek | 83 | 19 | 2020-09-01 | 23:00
22 | Dhaka University | - | - | - | -
23 | Fatullah | 44 | 29 | 2020-09-01 | 9:00
24 | Mirpur | 113 | 19 | 2020-09-01 | 18:30
25 | Kalyanpur | 114 | 2 | 2020-09-01 | 18:00
26 | Gulshan | 150 | 6 | 2020-09-01 | 13:00
27 | Uttara | 97 | 17 | 2020-09-01 | 13:00
28 | Uttara(new) | 34 | 7 | 2020-09-01 | 12:00
29 | Kamrangirchar | 98 | 19 | 2020-09-01 | 19:00
30 | Savar | 150 | 16 | 2020-09-01 | 15:00
31 | Bhasantec | 165 | 17 | 2020-09-01 | 13:00
32 | Agargaon | 78 | 20 | 2020-09-01 | 14:00
33 | Satmosjid | 110 | 19 | 2020-09-01 | 18:30
34 | Tongi | 130 | 2 | 2020-09-01 | 11:00
35 | Kabirpur | 268 | 19 | 2020-09-01 | 16:00
36 | Basundhara | 160 | 8 | 2020-09-01 | 13:00
37 | Manikganj | 76 | 6 | 2020-09-01 | 21:00
38 | Joydevpur | 164 | 28 | 2020-09-01 | 15:00
39 | New Tongi | 124 | 5 | 2020-09-01 | 12:00
40 | Kodda | 294 | 30 | 2020-09-01 | 15:00
41 | Dhamrai | 104 | 16 | 2020-09-01 | 18:30
42 | Rajendrapur | 108 | 28 | 2020-09-01 | 19:00
43 | Valuka | 138 | 29 | 2020-09-01 | 18:30
44 | Tangail | 218 | 5 | 2020-09-01 | 20:00
45 | Mymensing | 241 | 5 | 2020-09-01 | 19:30
46 | Kishorganj | 154 | 30 | 2020-09-01 | 21:00
47 | Netrokona | 119 | 30 | 2020-09-01 | 19:30
48 | Jamalpur | 152 | 5 | 2020-09-01 | 19:30
49 | Sherpur | 116 | 5 | 2020-09-01 | 21:00
50 | Srimongal | 62 | 27 | 2020-09-01 | 18:30
Page: 2/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:September'2020
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
51 | Shahjibazar | 134 | 6 | 2020-09-01 | 22:00
52 | Fenchuganj | 54 | 9 | 2020-09-01 | 19:00
53 | Kulawara | 49 | 9 | 2020-09-01 | 19:00
54 | Sylhet | 145 | 20 | 2020-09-01 | 19:30
55 | Chatak | 35 | 19 | 2020-09-01 | 20:00
56 | Sunamganj | 51 | 9 | 2020-09-01 | 20:00
57 | Bianibazar | 76 | 19 | 2020-09-01 | 19:30
58 | Cumilla (S) | 192 | 19 | 2020-09-01 | 19:00
59 | Cumilla(N) | 135 | 29 | 2020-09-01 | 19:30
60 | Chandpur | 118 | 7 | 2020-09-01 | 21:00
61 | Feni | 134 | 18 | 2020-09-01 | 21:00
62 | Chowmuhani | 206 | 19 | 2020-09-01 | 23:00
63 | Ashuganj | 68 | 6 | 2020-09-01 | 0:00
64 | Daudkandi | 155 | 5 | 2020-09-01 | 20:00
65 | B.Baria | 170 | 18 | 2020-09-01 | 20:00
66 | Ramganj | 124 | 5 | 2020-09-01 | 22:00
67 | Chaddagram | 42 | 19 | 2020-09-01 | 19:00
68 | PHP | 13 | 19 | 2020-09-01 | 23:00
69 | Madanhat | 68 | 9 | 2020-09-01 | 15:00
70 | Hathazari | 108 | 7 | 2020-09-01 | 16:00
71 | Khulshi | 215 | 6 | 2020-09-01 | 16:00
72 | Halishahar | 148 | 6 | 2020-09-01 | 11:00
73 | Baraulia | 159 | 5 | 2020-09-01 | 13:00
74 | Sikalbaha | 32 | 30 | 2020-09-01 | 1:00
75 | Dohazari | 106 | 7 | 2020-09-01 | 19:00
76 | Cox'sbazar | 110 | 18 | 2020-09-01 | 18:30
77 | Chandraghona | 36 | 19 | 2020-09-01 | 12:00
78 | Kaptai | 20 | 19 | 2020-09-01 | 7:00
79 | A. Khaer Stl. | 106 | 7 | 2020-09-01 | 15:00
80 | Bakulia | 114 | 17 | 2020-09-01 | 18:00
81 | Julda | 29.2 | 7 | 2020-09-01 | 22:00
82 | TK chemical | 31.8 | 19 | 2020-09-01 | 21:00
83 | Modern Steel | 23.5 | 7 | 2020-09-01 | 1:00
84 | Shahmirpur | 35 | 19 | 2020-09-01 | 14:00
85 | Khagrachhari | 34 | 7 | 2020-09-01 | 22:00
86 | Matarbari | 38 | 7 | 2020-09-01 | 18:30
87 | Baroiar Hat | 58 | 19 | 2020-09-01 | 20:00
88 | Rangamati | 14 | 19 | 2020-09-01 | 18:30
89 | Abul Khair 230 | 176 | 17 | 2020-09-01 | 10:00
90 | BSRM | 156 | 29 | 2020-09-01 | 10:00
91 | GPH Ispat | 88 | 1 | 2020-09-01 | 3:00
92 | Goalpara | 38 | 6 | 2020-09-01 | 23:00
93 | Central s/s | 102 | 5 | 2020-09-01 | 19:00
94 | Noapara | 62 | 2 | 2020-09-01 | 19:00
95 | Jashore | 130 | 16 | 2020-09-01 | 19:30
96 | Benapol | 52 | 5 | 2020-09-01 | 22:00
97 | Jhenidah | 120 | 7 | 2020-09-01 | 19:00
98 | Bottail | 140 | 6 | 2020-09-01 | 19:00
Page: 2/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:September'2020
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
99 | G.K Project | 61 | 9 | 2020-09-01 | 19:00
100 | Faridpur | 202 | 5 | 2020-09-01 | 21:00
101 | Madaripur | 108 | 5 | 2020-09-01 | 22:00
102 | Sariatpur | 70 | 6 | 2020-09-01 | 22:00
103 | Gopalganj | 101 | 8 | 2020-09-01 | 19:00
104 | Bagerhat | 110 | 19 | 2020-09-01 | 22:00
105 | Mongla | 50 | 1 | 2020-09-01 | 1:00
106 | Satkhira | 118 | 19 | 2020-09-01 | 21:00
107 | Gallamari | 56 | 2 | 2020-09-01 | 12:00
108 | Magura | 58 | 6 | 2020-09-01 | 19:00
109 | Norail | 43 | 6 | 2020-09-01 | 22:00
110 | Chuadanga | 94 | 21 | 2020-09-01 | 21:00
111 | Barsal(N) | 49 | 20 | 2020-09-01 | 19:30
112 | Barsal(S) | 110 | 8 | 2020-09-01 | 22:00
113 | Patuakhali | 133 | 19 | 2020-09-01 | 21:00
114 | Bhandaria | 58 | 4 | 2020-09-01 | 21:00
115 | Borhan Uddin | 46 | 18 | 2020-09-01 | 22:00
116 | Ishurdi | 67 | 13 | 2020-09-01 | 18:30
117 | Ruppur Paromanobik | 3 | 30 | 2020-09-01 | 8:00
118 | Natore | 136 | 20 | 2020-09-01 | 21:00
119 | Bogura | 180 | 5 | 2020-09-01 | 21:00
120 | Naogaon | 136 | 5 | 2020-09-01 | 21:00
121 | Rajshahi | 155 | 5 | 2020-09-01 | 21:00
122 | Rajshahi New | 13 | 13 | 2020-09-01 | 21:00
123 | C.Nawabganj | 77 | 4 | 2020-09-01 | 21:00
124 | Amnura | 50 | 1 | 2020-09-01 | 2:00
125 | Pabna | 130 | 5 | 2020-09-01 | 21:00
126 | Shahjadpur | 111 | 9 | 2020-09-01 | 19:30
127 | Serajganj | 118 | 30 | 2020-09-01 | 20:00
128 | Niyamatpur | 63 | 5 | 2020-09-01 | 21:00
129 | Joypurhat | 63 | 28 | 2020-09-01 | 20:00
130 | Sherpur(Bogura) | 52 | 20 | 2020-09-01 | 21:00
131 | Mohastangar | 54 | 5 | 2020-09-01 | 19:30
132 | Rangpur | 160 | 20 | 2020-09-01 | 21:00
133 | Lalmonirhat | 61 | 3 | 2020-09-01 | 1:00
134 | Saidpur | 113 | 29 | 2020-09-01 | 19:00
135 | Purbasadipur | 109 | 2 | 2020-09-01 | 19:00
136 | Thakurgaon | 92 | 19 | 2020-09-01 | 21:00
137 | Palshbari | 130 | 19 | 2020-09-01 | 20:00
138 | Barapukuria | 55 | 5 | 2020-09-01 | 21:00
139 | Panchugar | 57 | 10 | 2020-09-01 | 21:00
140 | Joldhaka | 34 | 19 | 2020-09-01 | 21:00
141 | Kurigram | 60 | 9 | 2020-09-01 | 19:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:September' 2020
Area | MW | Date | Hour | Remarks
Dhaka | 47134 | 29.09.2020 | 22:00
Chattogram | 1396 | 17.09.2020 | 23:00
Khulna | 1579 | 05.09.2020 | 21:00
Rajshahi | 1363 | 05.09.2020 | 21:00
Cumilla | 1268 | 05.09.2020 | 21:00
Mymensingh | 1017 | 03.09.2020 | 22:00
Sylhet | 551 | 09.09.2020 | 19:30
Barisal | 437 | 16.09.2020 | 21:00
Rangpur | 817 | 08.09.2020 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: September'2020
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 401 | 5 | 2020-09-01 | 6:00 | 383 | 30 | 2020-09-01 | 16:00
2 | Bheramara | 400 | 401 | 11 | 2020-09-01 | 10:00 | 383 | 14 | 2020-09-01 | 22:00
3 | Ashuganj(N) | 400 | 400 | 4 | 2020-09-01 | 18:00 | 373 | 9 | 2020-09-01 | 12:00
4 | Payra | 400 | 425 | 17 | 2020-09-01 | 22:00 | 386 | 17 | 2020-09-01 | 11:00
5 | Kaliakoir | 400 | 383 | 1 | 2020-09-01 | 6:00 | 356 | 24 | 2020-09-01 | 15:00
6 | Bhulta | 400 | 395 | 21 | 2020-09-01 | 6:00 | 362 | 9 | 2020-09-01 | 11:00
7 | Gopalganj | 400 | 425 | 17 | 2020-09-01 | 17:00 | 384 | 18 | 2020-09-01 | 5:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 238 | 18 | 2020-09-01 | 18:00 | 224 | 16 | 2020-09-01 | 10:00
2 | Ishurdi | 230 | 240 | 26 | 2020-09-01 | 18:00 | 220 | 19 | 2020-09-01 | 10:00
3 | Ashuganj | 230 | 240 | 1 | 2020-09-01 | 4:00 | 226 | 8 | 2020-09-01 | 13:00
4 | Serajganj | 230 | 239 | 13 | 2020-09-01 | 17:00 | 225 | 2 | 2020-09-01 | 21:00
5 | Baghabari | 230 | 244 | 22 | 2020-09-01 | 18:00 | 229 | 3 | 2020-09-01 | 11:00
6 | Barapukuria | 230 | 243 | 26 | 2020-09-01 | 18:30 | 217 | 4 | 2020-09-01 | 1:00
7 | Bogura | 230 | 231 | 24 | 2020-09-01 | 14:00 | 212 | 20 | 2020-09-01 | 20:00
8 | Rajshahi | 230 | 235 | 21 | 2020-09-01 | 18:00 | 213 | 28 | 2020-09-01 | 1:00
9 | Khulna South | 230 | 240 | 3 | 2020-09-01 | 18:00 | 205 | 8 | 2020-09-01 | 20:00
10 | Rampura | 230 | 230 | 3 | 2020-09-01 | 3:00 | 212 | 9 | 2020-09-01 | 12:00
11 | Haripur | 230 | 231 | 3 | 2020-09-01 | 4:00 | 213 | 9 | 2020-09-01 | 12:00
12 | Hasnabad | 230 | 231 | 5 | 2020-09-01 | 7:00 | 213 | 9 | 2020-09-01 | 12:00
13 | Shyampur | 230 | 229 | 4 | 2020-09-01 | 18:00 | 210 | 21 | 2020-09-01 | 12:00
14 | Aminbazar | 230 | 230 | 1 | 2020-09-01 | 24:00 | 213 | 21 | 2020-09-01 | 10:00
15 | Tongi | 230 | 231 | 4 | 2020-09-01 | 12:00 | 212 | 12 | 2020-09-01 | 10:00
16 | Comilla (N) | 230 | 238 | 26 | 2020-09-01 | 12:00 | 224 | 21 | 2020-09-01 | 15:00
17 | Hathazari | 230 | 232 | 2 | 2020-09-01 | 18:00 | 213 | 4 | 2020-09-01 | 10:00
18 | Megnaghat | 230 | 234 | 4 | 2020-09-01 | 12:00 | 220 | 21 | 2020-09-01 | 16:00
19 | Fenchuganj | 230 | 241 | 4 | 2020-09-01 | 12:00 | 229 | 29 | 2020-09-01 | 18:00
20 | Siddhirganj | 230 | 233 | 1 | 2020-09-01 | 5:00 | 214 | 9 | 2020-09-01 | 12:00
21 | Maniknagar | 230 | 232 | 5 | 2020-09-01 | 7:00 | 213 | 9 | 2020-09-01 | 12:00
22 | Old Airport | 230 | 230 | 1 | 2020-09-01 | 6:00 | 210 | 21 | 2020-09-01 | 12:00
23 | Barisal | 230 | 250 | 17 | 2020-09-01 | 17:00 | 225 | 7 | 2020-09-01 | 20:00
24 | AKSML | 230 | 229 | 3 | 2020-09-01 | 11:00 | 210 | 4 | 2020-09-01 | 9:00
25 | BSRM | 230 | 229 | 1 | 2020-09-01 | 2:00 | 214 | 1 | 2020-09-01 | 15:00
26 | Bibiyana | 230 | 241 | 25 | 2020-09-01 | 18:30 | 227 | 30 | 2020-09-01 | 13:00
27 | Bhulta | 230 | 233 | 1 | 2020-09-01 | 19:00 | 213 | 9 | 2020-09-01 | 17:00
28 | Ashuganj (S) | 230 | 238 | 1 | 2020-09-01 | 4:00 | 226 | 20 | 2020-09-01 | 9:00
29 | Kaliakoir | 230 | 235 | 1 | 2020-09-01 | 6:00 | 218 | 12 | 2020-09-01 | 12:00
30 | GPH | 230 | 228 | 24 | 2020-09-01 | 8:00 | 211 | 4 | 2020-09-01 | 10:00
132 kV Substation
1 | Siddhirganj | 132 | 135 | 4 | 2020-09-01 | 0.5 | 122 | 9 | 2020-09-01 | 0.5
2 | Munsiganj | 132 | 139 | 22 | 2020-09-01 | 0.75 | 103 | 21 | 2020-09-01 | 0.083333
3 | Sonargaon | 132 | 136 | 2 | 2020-09-01 | 0.75 | 122 | 9 | 2020-09-01 | 0.5
4 | Shyampur | 132 | 138 | 13 | 2020-09-01 | 0.25 | 124 | 9 | 2020-09-01 | 0.5
5 | Bhulta | 132 | 130 | 4 | 2020-09-01 | 0.58333 | 116 | 13 | 2020-09-01 | 0.41667
6 | Madanganj | 132 | 139 | 28 | 2020-09-01 | 0.8125 | 121 | 12 | 2020-09-01 | 0.70833
7 | Shitalakhya | 132 | 144 | 2 | 2020-09-01 | 0.91667 | 126 | 12 | 2020-09-01 | 0.41667
8 | Rahim Steal | 132 | 135 | 4 | 2020-09-01 | 0.5 | 122 | 9 | 2020-09-01 | 0.5
9 | Matuail | 132 | 135 | 4 | 2020-09-01 | 0.5 | 122 | 9 | 2020-09-01 | 0.5
10 | Ghorasal | 132 | 140 | 1 | 2020-09-01 | 0.041667 | 126 | 26 | 2020-09-01 | 0.5
11 | Narsinghdi | 132 | 132 | 4 | 2020-09-01 | 0.5 | 116 | 9 | 2020-09-01 | 0.5
12 | Haripur (SBU) | 132 | 135 | 4 | 2020-09-01 | 0.5 | 123 | 9 | 2020-09-01 | 0.5
13 | Ullon | 132 | 136 | 25 | 2020-09-01 | 0.91667 | 121 | 9 | 2020-09-01 | 0.5
14 | Hasnabad | 132 | 139 | 1 | 2020-09-01 | 0.041667 | 126 | 10 | 2020-09-01 | 0.5
15 | Magbazar | 132 | 137 | 1 | 2020-09-01 | 0.70833 | 120 | 9 | 2020-09-01 | 0.5
16 | Maniknagar | 132 | 136 | 5 | 2020-09-01 | 0.20833 | 123 | 9 | 2020-09-01 | 0.5
17 | Bangabhaban | 132 | 136 | 5 | 2020-09-01 | 0.20833 | 123 | 9 | 2020-09-01 | 0.5
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: September'2020
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
18 | Narinda | 132 | 136 | 5 | 2020-09-01 | 0.20833 | 123 | 9 | 2020-09-01 | 0.5
19 | Dhanmondi | 132 | 136 | 26 | 2020-09-01 | 0.041667 | 121 | 9 | 2020-09-01 | 0.5
20 | Lalbag | 132 | 142 | 11 | 2020-09-01 | 1899-12-31 | 122 | 9 | 2020-09-01 | 0.5
21 | Madartek | 132 | 135 | 29 | 2020-09-01 | 0.16667 | 120 | 9 | 2020-09-01 | 0.5
22 | Dhaka University | 132 | - | - | - | - | - | - | - | -
23 | Fatullah | 132 | 136 | 4 | 2020-09-01 | 0.54167 | 124 | 9 | 2020-09-01 | 0.5
24 | Mirpur | 132 | 137 | 29 | 2020-09-01 | 0.25 | 122 | 9 | 2020-09-01 | 0.5
25 | Kalyanpur | 132 | 137 | 30 | 2020-09-01 | 0.125 | 123 | 5 | 2020-09-01 | 0.5
26 | Gulshan | 132 | 135 | 26 | 2020-09-01 | 0.041667 | 120 | 9 | 2020-09-01 | 0.5
27 | Uttara | 132 | 135 | 25 | 2020-09-01 | 0.79167 | 122 | 9 | 2020-09-01 | 0.5
28 | Uttara(New) | 132 | 137 | 4 | 2020-09-01 | 0.54167 | 124 | 6 | 2020-09-01 | 0.66667
29 | Kamrangirchar | 132 | 140 | 28 | 2020-09-01 | 0.83333 | 121 | 9 | 2020-09-01 | 0.5
30 | Savar | 132 | 136 | 19 | 2020-09-01 | 0.20833 | 122 | 5 | 2020-09-01 | 0.5
31 | Bhasantec | 132 | 139 | 29 | 2020-09-01 | 0.25 | 122 | 9 | 2020-09-01 | 0.5
32 | Agargaon | 132 | 140 | 29 | 2020-09-01 | 6;00 | 124 | 6 | 2020-09-01 | 0.66667
33 | Satmosjid | 132 | 140 | 30 | 2020-09-01 | 0.25 | 123 | 9 | 2020-09-01 | 0.5
34 | Tongi | 132 | 140 | 4 | 2020-09-01 | 0.5 | 127 | 10 | 2020-09-01 | 0.375
35 | Kabirpur | 132 | 138 | 4 | 2020-09-01 | 0.75 | 124 | 20 | 2020-09-01 | 0.58333
36 | Basundhara | 132 | 136 | 29 | 2020-09-01 | 0.25 | 120 | 9 | 2020-09-01 | 0.5
37 | Manikganj | 132 | 143 | 17 | 2020-09-01 | 0.875 | 126 | 15 | 2020-09-01 | 0.375
38 | Joydevpur | 132 | 143 | 2 | 2020-09-01 | 0.75 | 124 | 2 | 2020-09-01 | 0.83333
39 | New Tongi | 132 | 139 | 4 | 2020-09-01 | 0.5 | 126 | 21 | 2020-09-01 | 0.70833
40 | Kodda | 132 | 141 | 9 | 2020-09-01 | 0.54167 | 120 | 1 | 2020-09-01 | 0.66667
41 | Dhamrai | 132 | 137 | 4 | 2020-09-01 | 0.75 | 124 | 20 | 2020-09-01 | 0.77083
42 | Rajendrapur | 132 | 138 | 18 | 2020-09-01 | 0.75 | 120 | 10 | 2020-09-01 | 0.5
43 | Valuka | 132 | 135 | 7 | 2020-09-01 | 0.54167 | 107 | 30 | 2020-09-01 | 0.79167
44 | Tangail | 132 | 138 | 1 | 2020-09-01 | 0.33333 | 120 | 28 | 2020-09-01 | 0.79167
45 | Mymensing | 132 | 137 | 7 | 2020-09-01 | 0.54167 | 112 | 30 | 2020-09-01 | 0.83333
46 | Kishorganj | 132 | 135 | 7 | 2020-09-01 | 0.54167 | 116 | 9 | 2020-09-01 | 0.54167
47 | Netrokona | 132 | 136 | 7 | 2020-09-01 | 0.54167 | 106 | 10 | 2020-09-01 | 0.79167
48 | Jamalpur | 132 | 140 | 4 | 2020-09-01 | 0.5 | 112 | 20 | 2020-09-01 | 0.125
49 | Sherpur | 132 | 140 | 7 | 2020-09-01 | 0.54167 | 110 | 20 | 2020-09-01 | 0.041667
50 | Srimongal | 132 | 139 | 25 | 2020-09-01 | 0.625 | 129 | 29 | 2020-09-01 | 0.91667
51 | Shahjibazar | 132 | 137 | 1 | 2020-09-01 | 0.33333 | 125 | 9 | 2020-09-01 | 0.5
52 | Fenchuganj | 132 | 137 | 16 | 2020-09-01 | 0.25 | 125 | 29 | 2020-09-01 | 0.95833
53 | Khulawara | 132 | 136 | 26 | 2020-09-01 | 0.58333 | 124 | 29 | 2020-09-01 | 0.95833
54 | Sylhet | 132 | 135 | 8 | 2020-09-01 | 0.33333 | 115 | 29 | 2020-09-01 | 0.95833
55 | Chattak | 132 | 136 | 8 | 2020-09-01 | 0.58333 | 105 | 29 | 2020-09-01 | 0.77083
56 | Sunamganj | 132 | 134 | 8 | 2020-09-01 | 0.33333 | 110 | 29 | 2020-09-01 | 0.91667
57 | Biani Bazar | 132 | 134 | 8 | 2020-09-01 | 0.375 | 110 | 29 | 2020-09-01 | 0.75
58 | Comilla(South) | 132 | 129 | 21 | 2020-09-01 | 0.41667 | 118 | 30 | 2020-09-01 | 0.5
59 | Comilla (North) | 132 | 140 | 3 | 2020-09-01 | 0.5 | 127 | 21 | 2020-09-01 | 0.625
60 | Chandpur | 132 | 140 | 2 | 2020-09-01 | 0.75 | 122 | 7 | 2020-09-01 | 0.95833
61 | Feni | 132 | 140 | 2 | 2020-09-01 | 0.875 | 123 | 11 | 2020-09-01 | 0.91667
62 | Chowmuhani | 132 | 138 | 2 | 2020-09-01 | 0.75 | 120 | 5 | 2020-09-01 | 0.70833
63 | Ashuganj | 132 | 139 | 26 | 2020-09-01 | 0.29167 | 125 | 9 | 2020-09-01 | 0.54167
64 | Daudkandi | 132 | 139 | 17 | 2020-09-01 | 0.77083 | 123 | 9 | 2020-09-01 | 0.5
65 | Brahminbaria | 132 | 136 | 25 | 2020-09-01 | 0.29167 | 125 | 2 | 2020-09-01 | 0.91667
66 | Ramganj | 132 | 136 | 3 | 2020-09-01 | 0.54167 | 114 | 7 | 2020-09-01 | 0.91667
67 | Chaddagram | 132 | 139 | 2 | 2020-09-01 | 0.91667 | 124 | 11 | 2020-09-01 | 0.91667
68 | PHP | 132 | 138 | 1 | 2020-09-01 | 0.125 | 123 | 11 | 2020-09-01 | 0.91667
69 | Madanhat | 132 | 142 | 24 | 2020-09-01 | 0.77083 | 128 | 4 | 2020-09-01 | 0.41667
70 | Hathazari | 132 | 139 | 24 | 2020-09-01 | 0.79167 | 127 | 4 | 2020-09-01 | 0.41667
71 | Khulshi | 132 | 138 | 24 | 2020-09-01 | 0.79167 | 126 | 4 | 2020-09-01 | 0.33333
72 | Halishahar | 132 | 141 | 1 | 2020-09-01 | 0.125 | 127 | 14 | 2020-09-01 | 0.375
73 | Baraulia | 132 | 140 | 22 | 2020-09-01 | 0.79167 | 126 | 14 | 2020-09-01 | 0.375
74 | Sikalbaha | 132 | 141 | 1 | 2020-09-01 | 0.083333 | 127 | 14 | 2020-09-01 | 0.375
75 | Dohazari | 132 | 139 | 17 | 2020-09-01 | 0.66667 | 123 | 6 | 2020-09-01 | 0.375
76 | Cox'sbazar | 132 | 132 | 20 | 2020-09-01 | 0.70833 | 115 | 7 | 2020-09-01 | 0.77083
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: September'2020
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
77 | Chandraghona | 132 | 139 | 17 | 2020-09-01 | 0.75 | 127 | 4 | 2020-09-01 | 0.41667
78 | Kaptai | 132 | 138 | 24 | 2020-09-01 | 0.77083 | 125 | 30 | 2020-09-01 | 0.041667
79 | A. Khaer Stl. | 132 | 137 | 21 | 2020-09-01 | 0.875 | 125 | 14 | 2020-09-01 | 0.375
80 | Bakulia | 132 | 140 | 24 | 2020-09-01 | 0.79167 | 126 | 19 | 2020-09-01 | 0.41667
81 | Julda | 132 | 141 | 24 | 2020-09-01 | 0.79167 | 127 | 4 | 2020-09-01 | 0.41667
82 | TK Chemical | 132 | 140 | 1 | 2020-09-01 | 0.041667 | 128 | 4 | 2020-09-01 | 0.41667
83 | Modern Steel | 132 | 140 | 24 | 2020-09-01 | 0.79167 | 126 | 4 | 2020-09-01 | 0.41667
84 | Shahmirpur | 132 | 140 | 17 | 2020-09-01 | 0.75 | 127 | 26 | 2020-09-01 | 0.41667
85 | Khagrachhari | 132 | 138 | 20 | 2020-09-01 | 0.70833 | 127 | 4 | 2020-09-01 | 0.41667
86 | Matarbari | 132 | 136 | 2 | 2020-09-01 | 0.45833 | 120 | 4 | 2020-09-01 | 0.375
87 | Baroiar Hat | 132 | 138 | 16 | 2020-09-01 | 0.66667 | 125 | 7 | 2020-09-01 | 0
88 | Rangamati | 132 | 138 | 17 | 2020-09-01 | 0.70833 | 127 | 4 | 2020-09-01 | 0.41667
89 | Goalpara | 132 | 139 | 20 | 2020-09-01 | 0.33333 | 118 | 12 | 2020-09-01 | 0.58333
90 | Khulna Central | 132 | 139 | 20 | 2020-09-01 | 0.33333 | 121 | 7 | 2020-09-01 | 0.45833
91 | Noapara | 132 | 138 | 20 | 2020-09-01 | 0.33333 | 122 | 7 | 2020-09-01 | 0.45833
92 | Jessore | 132 | 136 | 20 | 2020-09-01 | 0.33333 | 116 | 12 | 2020-09-01 | 0.8125
93 | Benapol | 132 | 135 | 1 | 2020-09-01 | 0.375 | 112 | 12 | 2020-09-01 | 0.58333
94 | Jhenida | 132 | 137 | 17 | 2020-09-01 | 0.41667 | 109 | 12 | 2020-09-01 | 0.8125
95 | Bottail | 132 | 136 | 4 | 2020-09-01 | 0.75 | 122 | 12 | 2020-09-01 | 0.83333
96 | G.K Project | 132 | 142 | 4 | 2020-09-01 | 0.75 | 134 | 3 | 2020-09-01 | 0.83333
97 | Faridpur | 132 | 135 | 1 | 2020-09-01 | 0.54167 | 120 | 18 | 2020-09-01 | 0.83333
98 | Madaripur | 132 | 140 | 1 | 2020-09-01 | 0.29167 | 124 | 18 | 2020-09-01 | 0.45833
99 | Sariatpur | 132 | 139 | 5 | 2020-09-01 | 0.375 | 123 | 7 | 2020-09-01 | 0.83333
100 | Gopalganj | 132 | 145 | 17 | 2020-09-01 | 0.70833 | 121 | 6 | 2020-09-01 | 0.83333
101 | Bagerhat | 132 | 140 | 20 | 2020-09-01 | 0.29167 | 115 | 7 | 2020-09-01 | 0.41667
102 | Mongla | 132 | 137 | 20 | 2020-09-01 | 0.33333 | 108 | 7 | 2020-09-01 | 0.375
103 | Satkhira | 132 | 138 | 20 | 2020-09-01 | 0.29167 | 117 | 7 | 2020-09-01 | 0.45833
104 | Gallamari | 132 | 138 | 3 | 2020-09-01 | 0.41667 | 122 | 7 | 2020-09-01 | 0.41667
105 | Magura | 132 | 134 | 20 | 2020-09-01 | 0.33333 | 105 | 12 | 2020-09-01 | 0.8125
106 | Norail | 132 | 131 | 18 | 2020-09-01 | 0.75 | 102 | 12 | 2020-09-01 | 0.8125
107 | Chuadanga | 132 | 129 | 18 | 2020-09-01 | 0.70833 | 98 | 12 | 2020-09-01 | 0.79167
108 | Barisal(N) | 132 | 142 | 15 | 2020-09-01 | 0.25 | 127 | 7 | 2020-09-01 | 0.83333
109 | Barisal(S) | 132 | 140 | 2 | 2020-09-01 | 0.16667 | 116 | 7 | 2020-09-01 | 0.83333
110 | Patuakhali | 132 | 138 | 1 | 2020-09-01 | 0.58333 | 119 | 7 | 2020-09-01 | 0.91667
111 | Bhandaria | 132 | 138 | 20 | 2020-09-01 | 0.33333 | 110 | 7 | 2020-09-01 | 0.41667
112 | Ishurdi | 132 | 140 | 17 | 2020-09-01 | 0.75 | 123 | 16 | 2020-09-01 | 0.875
113 | Ruppur paromanobik | 132 | 139 | 2 | 2020-09-01 | 0.75 | 130 | 9 | 2020-09-01 | 0.875
114 | Natore | 132 | 141 | 17 | 2020-09-01 | 0.75 | 128 | 9 | 2020-09-01 | 0.875
115 | Bogra | 132 | 141 | 17 | 2020-09-01 | 0.75 | 127 | 3 | 2020-09-01 | 0.875
116 | Noagaon | 132 | 137 | 18 | 2020-09-01 | 0.5 | 119 | 20 | 2020-09-01 | 0.83333
117 | Rajshahi | 132 | 141 | 17 | 2020-09-01 | 0.70833 | 127 | 3 | 2020-09-01 | 0.8125
118 | Rajshahi New | 132 | 142 | 17 | 2020-09-01 | 0.70833 | 128 | 3 | 2020-09-01 | 0.20833
119 | C.Nawabganj | 132 | 142 | 17 | 2020-09-01 | 0.70833 | 125 | 3 | 2020-09-01 | 0.8125
120 | Amnura | 132 | 142 | 17 | 2020-09-01 | 0.70833 | 125 | 3 | 2020-09-01 | 0.20833
121 | Pabna | 132 | 138 | 18 | 2020-09-01 | 0.75 | 124 | 15 | 2020-09-01 | 0.45833
122 | Shahjadpur | 132 | 142 | 17 | 2020-09-01 | 0.77083 | 128 | 11 | 2020-09-01 | 0.83333
123 | Serajganj | 132 | 136 | 3 | 2020-09-01 | 0.75 | 126 | 9 | 2020-09-01 | 0.875
124 | Niyamatpur | 132 | 137 | 18 | 2020-09-01 | 0.33333 | 115 | 5 | 2020-09-01 | 0.875
125 | Joypurhat | 132 | 139 | 17 | 2020-09-01 | 0.77083 | 117 | 2 | 2020-09-01 | 0.875
126 | Sherpur(Bogura) | 132 | 139 | 17 | 2020-09-01 | 0.70833 | 126 | 5 | 2020-09-01 | 0.875
127 | Mohastangor | 132 | 139 | 18 | 2020-09-01 | 0.33333 | 123 | 20 | 2020-09-01 | 0.83333
128 | Rangpur | 132 | 137 | 17 | 2020-09-01 | 0.20833 | 104 | 28 | 2020-09-01 | 0.8125
129 | Lalmonirhat | 132 | 140 | 27 | 2020-09-01 | 0.16667 | 111 | 2 | 2020-09-01 | 0.8125
130 | Saidpur | 132 | 138 | 17 | 2020-09-01 | 0.20833 | 112 | 2 | 2020-09-01 | 0.79167
131 | Purbasadipur | 132 | 136 | 16 | 2020-09-01 | 0.5 | 108 | 2 | 2020-09-01 | 0.79167
132 | Thakurgaon | 132 | 137 | 16 | 2020-09-01 | 0.5 | 105 | 2 | 2020-09-01 | 0.79167
133 | Palashbari | 132 | 138 | 23 | 2020-09-01 | 0.625 | 115 | 1 | 2020-09-01 | 0.083333
134 | Barapukuria | 132 | 141 | 17 | 2020-09-01 | 0.25 | 117 | 4 | 2020-09-01 | 0.041667
135 | Panchagar | 132 | 136 | 16 | 2020-09-01 | 0.5 | 103 | 2 | 2020-09-01 | 0.79167
136 | Joldhaka | 132 | 138 | 17 | 2020-09-01 | 0.25 | 110 | 19 | 2020-09-01 | 0.91667
137 | Kurigram | 132 | 136 | 17 | 2020-09-01 | 0.29167 | 110 | 2 | 2020-09-01 | 1899-12-31
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:September' 2020
Name of the | Auto transofrmer |  | Recorded maximum load
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kV side ) | Date | Time | Remarks
| TR1 | 225 | 135 | 325
Hasnabad | TR2 | 225 | 125 | 325 | 10.09.2020 | 16:00
| TR3 | 225 | 120 | 320
| TR1 | 225 | 160 | 455
Tongi | TR2 | 225 | 160 | 455 | 23.09.2020 | 16:00
| TR3 | 225 | 160 | 455
Haripur | TR1 | 225 | 132 | 350 | 12.09.2020 | 06:00
| TR3 | 225 | 132 | 350
| TR1 | 225 | 185 | 530
Rampura | TR2 | 225 | 185 | 530 | 20.09.2020 | 15:00
| TR3 | 225 | 185 | 530
| TR1 | 225 | 148 | 450
Aminbazar | TR2 | 225 | 148 | 450 | 12.09.2020 | 10:00
| TR3 | 225 | 157 | 472
Maniknagar | 8 | 300 | 119 | 370 | 06.09.2020 | 16:00
| TR2 | 300 | 119 | 370
Cumilla (N) | TR1 | 225 | 172 | 530 | 17.09.2020 | 6:00
| TR2 | 225 | 172 | 512
Fenchuganj | AT2 | 300 | 210 | 582 | 29.09.2020 | 22:00
| MT1 | 150 | 89 | 255
Hathazari | MT2 | 150 | 89 | 255 | 26.09.2020 | 10:00
| MT3 | 150 | 89 | 255
| MT4 | 150 | 89 | 255
| TR1 | 225 | 110 | 280
Ishurdi | TR2 | 225 | 110 | 280 | 18.09.2020 | 21:00
| TR3 | 225 | 110 | 280
Khulna(S) | TR1 | 225 | 115 | 298
| TR2 | 225 | 115 | 298 | 07.09.2020 | 08:00
| TR3 | 300 | 146 | 377
Bogra | TR1 | 225 | 112 | 322 | 13.09.2020 | 2:00
| TR2 | 225 | 112 | 322
| TR3 | 225 | 151 | 425
Baghabari | TR1 | 300 | 141 | 380 | 15.09.2020 | 11:00
| TR2 | 225 | 105 | 283
Barapukuria | TR1 | 225 | 149 | 715 | 04.09.2020 | 19:00 | Due to unavailability of 230 kV side meters
| TR2 | 225 | 155 | 760 |  |  | 132 kV current is being provided
| TR6 | 300 | 196 | 974
Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:September' 2020
Name of the | Transofrmer |  | Recorded maximum load |  |  |  | Remarks
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 400 kV side ) | Date | Time
Kaliakoir | TR1(400/230 kV) | 520 | 127 | 249 | 09.09.2020 | 11:00
| TR2(400/230 kV) | 520 | 128.9 | 251
| TR1(400/132 kV) | 325 | 257.1 | 449 | 21.09.2020 | 20:30
| TR2(400/132 kV) | 325 | 258 | 445
Bibiyana | ICT1(400/230 kV) | 520 | 128 | 205 | 09.09.2020 | 11:00
| ICT2(400/230kV) | 520 | 127 | 205
Bhulta | ATR1(400/230 kV) | 520 | 279 | 500 | 09.09.2020 | 11:15
| ATR2(400/230kV) | 520 | 279 | 500
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:September' 2020 | [6 empty] | (For Evening Peak) | [7 empty] | Month:September' 2020 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-09-20 | 11453 | 11453 | - | - | - | - | - | - | - | - | - | - | - | - | 01-09-20 | 9415.63 | 9415.63 | - | - | - | - | - | - | - | - | - | - | - | -
02-09-20 | 11982 | 11982 | - | - | - | - | - | - | - | - | - | - | - | - | 02-09-20 | 10280.6 | 10280.6 | - | - | - | - | - | - | - | - | - | - | - | -
03-09-20 | 12427 | 12427 | - | - | - | - | - | - | - | - | - | - | - | - | 03-09-20 | 10641.73 | 10641.73 | - | - | - | - | - | - | - | - | - | - | - | -
04-09-20 | 12101 | 12101 | - | - | - | - | - | - | - | - | - | - | - | - | 04-09-20 | 9075.7 | 9075.7 | - | - | - | - | - | - | - | - | - | - | - | -
05-09-20 | 12892 | 12892 | - | - | - | - | - | - | - | - | - | - | - | - | 05-09-20 | 10311.2 | 10311.2 | - | - | - | - | - | - | - | - | - | - | - | -
06-09-20 | 12097 | 12097 | - | - | - | - | - | - | - | - | - | - | - | - | 06-09-20 | 10834 | 10834 | - | - | - | - | - | - | - | - | - | - | - | -
07-09-20 | 11771 | 11771 | - | - | - | - | - | - | - | - | - | - | - | - | 07-09-20 | 10047 | 10047 | - | - | - | - | - | - | - | - | - | - | - | -
08-09-20 | 12016 | 12016 | - | - | - | - | - | - | - | - | - | - | - | - | 08-09-20 | 10390.4 | 10390.4 | - | - | - | - | - | - | - | - | - | - | - | -
09-09-20 | 12493 | 12493 | - | - | - | - | - | - | - | - | - | - | - | - | 09-09-20 | 10370 | 10370 | - | - | - | - | - | - | - | - | - | - | - | -
10-09-20 | 11941 | 11941 | - | - | - | - | - | - | - | - | - | - | - | - | 10-09-20 | 9806 | 9806 | - | - | - | - | - | - | - | - | - | - | - | -
11-09-20 | 11259 | 11259 | - | - | - | - | - | - | - | - | - | - | - | - | 11-09-20 | 8559 | 8559 | - | - | - | - | - | - | - | - | - | - | - | -
12-09-20 | 12229 | 12229 | - | - | - | - | - | - | - | - | - | - | - | - | 12-09-20 | 9638 | 9638 | - | - | - | - | - | - | - | - | - | - | - | -
13-09-20 | 12345 | 12345 | - | - | - | - | - | - | - | - | - | - | - | - | 13-09-20 | 10506 | 10506 | - | - | - | - | - | - | - | - | - | - | - | -
14-09-20 | 12040 | 12040 | - | - | - | - | - | - | - | - | - | - | - | - | 14-09-20 | 10467 | 10467 | - | - | - | - | - | - | - | - | - | - | - | -
15-09-20 | 12080 | 12080 | - | - | - | - | - | - | - | - | - | - | - | - | 15-09-20 | 10377 | 10377 | - | - | - | - | - | - | - | - | - | - | - | -
16-09-20 | 11966 | 11966 | - | - | - | - | - | - | - | - | - | - | - | - | 16-09-20 | 10145 | 10145 | - | - | - | - | - | - | - | - | - | - | - | -
17-09-20 | 11554 | 11554 | - | - | - | - | - | - | - | - | - | - | - | - | 17-09-20 | 10144 | 10144 | - | - | - | - | - | - | - | - | - | - | - | -
18-09-20 | 11639 | 11639 | - | - | - | - | - | - | - | - | - | - | - | - | 18-09-20 | 8622 | 8622 | - | - | - | - | - | - | - | - | - | - | - | -
19-09-20 | 12725 | 12725 | - | - | - | - | - | - | - | - | - | - | - | - | 19-09-20 | 9719 | 9719 | - | - | - | - | - | - | - | - | - | - | - | -
20-09-20 | 12220 | 12220 | - | - | - | - | - | - | - | - | - | - | - | - | 20-09-20 | 10888 | 10888 | - | - | - | - | - | - | - | - | - | - | - | -
21-09-20 | 11925 | 11925 | - | - | - | - | - | - | - | - | - | - | - | - | 21-09-20 | 9987 | 9987 | - | - | - | - | - | - | - | - | - | - | - | -
22-09-20 | 11422 | 11422 | - | - | - | - | - | - | - | - | - | - | - | - | 22-09-20 | 9497 | 9497 | - | - | - | - | - | - | - | - | - | - | - | -
23-09-20 | 11384 | 11384 | - | - | - | - | - | - | - | - | - | - | - | - | 23-09-20 | 9468 | 9468 | - | - | - | - | - | - | - | - | - | - | - | -
24-09-20 | 11477 | 11477 | - | - | - | - | - | - | - | - | - | - | - | - | 24-09-20 | 9339 | 9339 | - | - | - | - | - | - | - | - | - | - | - | -
25-09-20 | 10262 | 10262 | - | - | - | - | - | - | - | - | - | - | - | - | 25-09-20 | 7853 | 7853 | - | - | - | - | - | - | - | - | - | - | - | -
26-09-20 | 10714 | 10714 | - | - | - | - | - | - | - | - | - | - | - | - | 26-09-20 | 9250 | 9250 | - | - | - | - | - | - | - | - | - | - | - | -
27-09-20 | 11499 | 11499 | - | - | - | - | - | - | - | - | - | - | - | - | 27-09-20 | 9260 | 9260 | - | - | - | - | - | - | - | - | - | - | - | -
28-09-20 | 12111 | 12111 | - | - | - | - | - | - | - | - | - | - | - | - | 28-09-20 | 10012.9 | 10012.9 | - | - | - | - | - | - | - | - | - | - | - | -
29-09-20 | 12250 | 12250 | - | - | - | - | - | - | - | - | - | - | - | - | 29-09-20 | 10215 | 10215 | - | - | - | - | - | - | - | - | - | - | - | -
30-09-20 | 12428 | 12428 | - | - | - | - | - | - | - | - | - | - | - | - | 30-09-20 | 10655 | 10655

## QF-LDC-38
page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:September' 2020
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 12892 | 05/09/20 | 19:30
2 | Maximum Day Peak Genaration | MW | 10888 | 05/09/20 | 12:00
3 | Maximum Evening Peak Demand | MW | 12892 | 05/09/20 | 19:30
4 | Minimum Generation | MW | 7634 | 25/09/20 | 9:00
5 | Average of the daily evening peak Genaration | MW | 11890.0667
6 | Average of the daily day peak Genaration | MW | 9851.3753
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 30 days in the month) | MW | -
11 | Total Generation | MKWH | 7458.7925
12 | Total Generation by BPDB | MKWH | 3387.808 | % of total Gen. | 45.42%
13 | Total Generation by IPP | MKWH | 2410.4166 | '' | 32.32%
14 | A) Total Generation by RPCL | MKWH | 141.4518 | '' | 1.896%
| B) Total Generation by REB | MKWH | 139.565 | " | 1.871%
| C) Total Generation by RENTAL | MKWH | 614.8876 | " | 8.244%
| D) Total Imported from India (BIPTC) | MKWH | 659.9956 | " | 8.849%
| E) Total Imported from Tripura, India (A.C) | MKWH | 104.6678 | " | 1.403%
15 | Fuel wise Generation.
| A) Gas | MKWH | 4127.7738 | % of total Gen. | 55.34%
| B) Oil | MKWH | 2068.2963 | '' | 27.73%
| C) Hydro | MKWH | 42.0017 | '' | 0.5631%
| D) Solar | MKWH | 4.8414 | '' | 0.06491%
| E) Coal | MKWH | 451.2158 | '' | 6.049%
| F) BIPTC (Import from India) | MKWH | 659.9956 | '' | 8.849%
| G) A.C (Import from Tripura, India) | MKWH | 104.6678 | '' | 1.403%
16 | Maximun of the daily total Generation . | MKWH | 267.7164 | 06-09-2020
17 | Monthly Load factor | % | 80.3555
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 24587.7624
| A) Gas | M.Taka | 4734.6449
| B) Liquid fuel | M.Taka | 17759.2496
| C) Coal | M.Taka | 2093.8679
| D) BIPTC (Import from India) | M.Taka | 3365.9777
| E) Tripura(Import from India) | M.Taka | 785.0088
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 1075.701 | 17/09/2020
| A) Gas | M.Taka | 184.3007 | 12/09/2020
| B) Liquid fuel | M.Taka | 888.3872 | 17/09/2020
| C) Coal | M.Taka | 80.2097 | 29/09/2020
| D) BIPTC (Import from India) | M.Taka | 114.0731 | 10-09-2020
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 3.4564
| B) Excluding Hydro & Solar | Taka/KWHR | 3.4779
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 105.76 | 30/09/2020 | 06:00
b) | Actual | FT (MSL) | 98.46 | 30/09/2020 | 06:00
22 | Peak Genaration of September 2019 | MW | 12717 | 01/09/19 | 21:00
23 | Peak Demand of September 2019 | MW | 12717 | 01/09/19 | 21:00
24 | Maximum peak Generation recorded upto 30/09/2020 | MW | 12893 | 29/05/19 | 21:00
25 | Maximum peak Demand recorded upto 30/09/2020 | MW | 12893 | 29/05/19 | 21:00
26 | Maximum load shed recorded upto 30/09/2020 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.