## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-10-21 | Wednesday
|  |  | Date (day): | 2020-10-21 |  | Wednesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13870.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14849 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-10-20 | 2020-10-21 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 115 | 115 | 115 | 75 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 200 | 200 | 165 |  | Gas shortage
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 71 | 72 | 72 | 72 | 36 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under S/D for dust in gas.
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 303 | 292 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 340 | 340 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 16 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 275 | 268 | 305 | 305
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 96 | 97 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 40 | 40 |  | 15 | Engine problem
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 26 | 24 | 50 | 88 |  | 12 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 151 | 175 | 115 | 165
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 97 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 85 | 20 | 94 | 94 |  |  | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 64 | 150 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 36 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Engine problem
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 55 | 55 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 51 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 225 | 300 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 108 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 25 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 52 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 149 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 86 | 86 | 85 | 86 |  | 19 | Engine problem
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 53 | 17 | 17 | 87 |  | Fuel shortage
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 2927 | 3152 | 3471 | 3850 | 705 | 1208
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 115 | 115 | 115 | 115 | 65 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 123 | 118 | 120 | 120 | 110 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 205 | 204 | 221 | 221
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 139 | 139 | 145 | 145
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 102 | 102
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 100 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 22 | 22 | 22 | 22
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 21 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 8 | 5 | 20
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 77 | 91 | 97 | 97 |  | 11 | Engine problem
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 142 | 160 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 54 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 1006 | 1308 | 1712 | 1702 | 355 | 109
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 80 | 70 | 80 | 80 | 49 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 |  | 134 | Under maint
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 189 | 205 | 225 | 225 |  |  | FGMO
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 295 | 360 | 360 |  |  | FGMO
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 260 | 350 | 350 |  |  | FGMO
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 5 | 30 | 30 | 15 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 35 | 51 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 140 | 142 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 41 | 25 | 50
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 82 | 81 | 90 | 90 |  | 57 | ST under shut down
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 149 | 200 | 200
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 48 | 140 | 165 | 173
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 43 | 25 | 52
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 15 | 22 | 22
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 70 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 100 | 0 | 17 | 97 |  | Engine problem & Fuel shortage
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 103 | 108 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1454 | 1851 | 1965 | 2242 | 533 | 191
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 104 | 101 | 150 | 150 | 52 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 14 | 17 | 20 | 20
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 32 | 32 | 48 | 48 |  | 47 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 190 | 189 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 35 | 115 | 115 | 115
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 377 | 454 | 534.6 | 533 | 52 | 47
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 82 | 71 | 85 | 85
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 43 | 43 | 43 | 43 |  | 47 | Unit-4 under shut down
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 |  | 54 | STG under maint.
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 158 | 158 | 160 | 160 |  | 170 | GT-2 S/D & ST Under maint.
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 25 | 25 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 43 | 46 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 64 | 65 | 65 |  |  | FGMO
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 87 | 87 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 20 | 192 | 140 | 200
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 20
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 25 | 25
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 300 | 341 | 341 |  |  | FGMO
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 413 | 419 | 400 | 400
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 264 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1657 | 1578 | 1589 | 1651 | 0 | 271
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 919 | 920 | 928 | 928
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 115 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 16 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 220 | 220 | 220
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 320 | 305 | 410 | 410
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 70 | 90 | 105 | 105
| 108 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 15 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1445 | 1821 | 1968 | 2124 | 0 | 0
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 14 | 38 | 33 | 33
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 93 | 93 | 95 | 95
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 490 | 540 | 580 | 580
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 597 | 781 | 818 | 818 | 0 | 194
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 42 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 20 | 20 | 20 | 20 | 30 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 36 | 50 | 50
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 153 | 178 | 225 | 225 |  |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 157 | 181 | 220 | 220 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 360 | 369 | 414 | 414 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 30
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 18 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 10 | 10 | 10 | 10
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 52 | 52 | 52
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 96 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 30 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 35 | 110 | 113 | 113
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 109 | 109 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 876 | 1344 | 1550 | 1670 | 461 | 0
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 149 | 150 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 75 | 99 | 105 | 109
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 229 | 249 | 263 | 259 | 294 | 40
|  | Total |  |  |  |  | 20383 | 19892 | 10568 | 12538 | 13870.6 | 14849 | 2400 | 2060
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10058.059 | 11933 | 13201.2976 | 14132.4866
| A. |  | 2020-10-20 | (Yesterday) |  |  |  |  | Tuesday
| 1 | Highest Generation : |  |  | 12538 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 8975 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12538 | MW
| 3 | Day peak Generation : |  |  | 10568 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11933 | MW
| 4 | Evening peak Generation : |  |  | 12538 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 263.3225 | MKWHr | By Solar | 0.22206 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 138.6408 | MKWHr |  | By Oil: | 80.2215 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 16.8561 | MKWHr |  | By Hydro: | 2.845 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2400 | MW | Dhaka | 4226 | 4226 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2060 | MW | Chittagong | 1215 | 1215 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4460 | MW | Khulna | 1507 | 1507 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1163.15 | MMCFD |  |  | Rajshahi | 1252 | 1252 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 161277369.6 | ii) Oil : | Taka | 637080862.4 | Comilla | 1142 | 1142 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 77774053 | Total | Taka | 876132285 | Mymensingh | 934 | 934 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.018 | MKWHr. | Sylhet | 540 | 540 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 84 | MW (E to W) at | 19:00 | hrs | Barisal | 339 | 339 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -30 | MW at | 3:00 | hrs | Rangpur | 778 | 778 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.2° C |  |  | Total | 11933 | 11933 |  | 0
| B. |  | 2020-10-21 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 32.6° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14849 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10200 | MW
| 4 | Reserve(Generation end) |  |  |  | 2049 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 268.825 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8976 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.0698 | MKWHr. | ii) HVDC Flow at Peak Time |  | 920 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.4672 | MKWHr. | iii) Maximum HVDC Flow : |  | 920 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 102.05 |  | (b) Today: | 102.04 |  | (c) Rule Curve: |  | 107.9
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-10-20
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 319 |  | 0 | 360 | 260 | 100 | 97 | 55 | 0 | 0 | 145 | 0 | 100 | 94 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 31 | 25 | 33 | 0 | 0 | 88 | 35 | 115 | 0 | 0 | 204 | 0 | 140 | 0 |  | 0 | 0 | 102 | 0 | 97 | 50 | 20 | 38 | 0 | 80 | 0 | 290 | 280 | 179 | 8 | 72 | 26 | 5 | 0 | 51 | 0 | 0 | 43 | 21 | 11 | 33 | 22 | 138 | 157 | 40 | 20 | 0 | 86 | 43 | 25 | 47 | 110 | 159 | 64 | 87 | 0 | 140 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 300 | 0 | 0 | 191 | 0 | 144 | 0 | 22 | 0 | 142 | 420 | 115 | 85 | 0 | 0 | 160 | 36 | 0 | 17 | 56 | 100 | 0 | 104 |  | 919 | 0 | 290 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 110 | 0 | 0 | 0 | 0 | 0 | 94 | 20 | 0 | 0 | 52 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 184 | 0 | 96 | 0 | 179 | 0 | 359 | 105 | 0 | 113 | 0 | 106 | 0 | 0 | 109 | 530 |  | 7825 | 3732 | 11557 | 3989 | 919 | 1957 | 3302 | 680 | 123 | 449 | 138 | 0 | 0 | 102.06
2:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 333 |  | 0 | 360 | 275 | 100 | 97 | 55 | 0 | 0 | 115 | 0 | 100 | 94 | 84 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 31 | 25 | 33 | 0 | 0 | 86 | 35 | 115 | 0 | 0 | 204 | 0 | 105 | 0 |  | 0 | 0 | 68 | 0 | 97 | 20 | 20 | 40 | 0 | 80 | 0 | 295 | 280 | 186 | 8 | 75 | 22 | 5 | 0 | 51 | 0 | 0 | 43 | 21 | 11 | 33 | 22 | 136 | 157 | 40 | 20 | 0 | 86 | 43 | 25 | 47 | 110 | 157 | 64 | 87 | 0 | 140 | 18 | 0 | 10 | 295 | 24 | 8 | 0 | 300 | 0 | 0 | 191 | 0 | 140 | 0 | 22 | 0 | 138 | 420 | 115 | 85 | 0 | 0 | 160 | 36 | 0 | 17 | 71 | 100 | 0 | 104 |  | 920 | 0 | 295 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 80 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 97 | 0 | 158 | 0 | 359 | 105 | 0 | 70 | 0 | 105 | 0 | 0 | 109 | 550 |  | 7685 | 3447 | 11132 | 3885 | 920 | 1969 | 3119 | 700 | 121 | 282 | 136 | 0 | 0 | 102.06
3:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 353 |  | 0 | 390 | 255 | 100 | 97 | 55 | 0 | 0 | 90 | 0 | 100 | 74 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 31 | 25 | 33 | 0 | 0 | 84 | 35 | 115 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 34 | 0 | 97 | 0 | 20 | 40 | 0 | 80 | 0 | 290 | 280 | 189 | 8 | 75 | 22 | 5 | 0 | 51 | 0 | 0 | 43 | 21 | 11 | 33 | 22 | 132 | 156 | 40 | 20 | 0 | 86 | 43 | 25 | 47 | 110 | 157 | 64 | 87 | 0 | 140 | 18 | 0 | 10 | 295 | 24 | 8 | 0 | 300 | 0 | 0 | 191 | 0 | 149 | 0 | 22 | 0 | 143 | 420 | 115 | 85 | 0 | 0 | 160 | 36 | 0 | 17 | 96 | 100 | 0 | 104 |  | 919 | 0 | 305 | 0 | 38 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 146 | 0 | 97 | 0 | 156 | 0 | 344 | 105 | 0 | 0 | 0 | 97 | 0 | 0 | 109 | 550 |  | 7625 | 3301 | 10926 | 3858 | 919 | 2004 | 2976 | 700 | 119 | 218 | 132 | 0 | 0 | 102.06
4:00 | 0 | 0 | 101 | 115 | 200 | 72 | 0 | 0 | 351 |  | 0 | 390 | 280 | 100 | 97 | 40 | 0 | 0 | 90 | 0 | 100 | 74 | 48 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 19 | 25 | 31 | 25 | 33 | 0 | 0 | 82 | 35 | 115 | 0 | 0 | 210 | 0 | 104 | 0 |  | 0 | 0 | 17 | 0 | 46 | 0 | 20 | 42 | 0 | 80 | 0 | 310 | 280 | 187 | 8 | 78 | 22 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 130 | 155 | 40 | 20 | 0 | 86 | 43 | 25 | 47 | 110 | 157 | 64 | 87 | 0 | 140 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 200 | 0 | 0 | 191 | 0 | 149 | 0 | 22 | 0 | 142 | 421 | 35 | 85 | 0 | 0 | 124 | 36 | 0 | 0 | 94 | 100 | 0 | 104 |  | 919 | 0 | 310 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 153 | 0 | 97 | 0 | 164 | 0 | 361 | 105 | 0 | 0 | 0 | 97 | 0 | 0 | 109 | 500 |  | 7264 | 3229 | 10493 | 3906 | 919 | 2021 | 2565 | 650 | 117 | 185 | 130 | 0 | 0 | 102.06
5:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 353 |  | 0 | 390 | 280 | 100 | 97 | 40 | 0 | 0 | 90 | 0 | 100 | 74 | 48 | 0 | 0 | 0 | 0 | 0 | 55 | 55 | 19 | 25 | 31 | 25 | 33 | 0 | 0 | 80 | 35 | 115 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 42 | 0 | 80 | 0 | 290 | 280 | 185 | 8 | 80 | 22 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 122 | 157 | 40 | 20 | 0 | 86 | 43 | 25 | 47 | 110 | 156 | 64 | 87 | 0 | 140 | 18 | 0 | 10 | 295 | 24 | 8 | 0 | 95 | 0 | 0 | 191 | 0 | 149 | 0 | 22 | 0 | 142 | 425 | 35 | 85 | 0 | 0 | 124 | 17 | 0 | 0 | 103 | 100 | 0 | 104 |  | 919 | 0 | 315 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 96 | 0 | 163 | 0 | 336 | 105 | 0 | 0 | 0 | 97 | 0 | 0 | 109 | 500 |  | 7031 | 3207 | 10238 | 3867 | 919 | 1993 | 2387 | 650 | 115 | 185 | 122 | 0 | 0 | 102.05
6:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 322 |  | 0 | 360 | 255 | 96 | 95 | 15 | 0 | 0 | 85 | 0 | 100 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 17 | 19 | 25 | 31 | 25 | 33 | 0 | 0 | 80 | 35 | 115 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 42 | 0 | 80 | 0 | 290 | 280 | 184 | 8 | 80 | 22 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 118 | 158 | 40 | 20 | 0 | 86 | 43 | 25 | 47 | 110 | 160 | 65 | 87 | 0 | 140 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 45 | 0 | 0 | 200 | 0 | 144 | 0 | 22 | 0 | 90 | 425 | 0 | 85 | 0 | 0 | 124 | 17 | 0 | 0 | 104 | 100 | 0 | 104 |  | 919 | 0 | 290 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 151 | 0 | 96 | 0 | 161 | 0 | 280 | 17 | 0 | 0 | 0 | 80 | 0 | 0 | 50 | 500 |  | 6647 | 2921 | 9568 | 3856 | 919 | 1858 | 1915 | 650 | 115 | 137 | 118 | 0 | 0 | 102.05
7:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 303 |  | 0 | 360 | 280 | 58 | 48 | 15 | 0 | 0 | 70 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 19 | 25 | 31 | 25 | 33 | 0 | 0 | 81 | 35 | 115 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 34 | 0 | 80 | 0 | 295 | 280 | 185 | 8 | 82 | 22 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 15 | 106 | 157 | 40 | 14 | 0 | 86 | 43 | 25 | 47 | 110 | 160 | 64 | 87 | 0 | 140 | 18 | 0 | 10 | 280 | 16 | 8 | 0 | 45 | 0 | 0 | 160 | 0 | 141 | 5 | 22 | 0 | 50 | 421 | 0 | 17 | 0 | 1 | 124 | 17 | 0 | 0 | 105 | 100 | 0 | 72 |  | 920 | 0 | 290 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 148 | 0 | 95 | 0 | 159 | 0 | 283 | 17 | 0 | 0 | 0 | 38 | 0 | 1 | 50 | 400 |  | 6236 | 2739 | 8975 | 3817 | 920 | 1830 | 1509 | 550 | 116 | 120 | 106 | 7 | 0 | 102.05
8:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 303 |  | 0 | 360 | 270 | 50 | 48 | 15 | 0 | 0 | 70 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 19 | 25 | 31 | 25 | 33 | 0 | 0 | 84 | 35 | 115 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 0 | 80 | 0 | 288 | 260 | 181 | 8 | 83 | 22 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 15 | 110 | 156 | 40 | 14 | 1 | 83 | 43 | 25 | 47 | 110 | 160 | 64 | 84 | 0 | 140 | 18 | 0 | 10 | 300 | 16 | 8 | 0 | 45 | 0 | 0 | 160 | 0 | 134 | 10 | 22 | 0 | 50 | 422 | 0 | 50 | 0 | 2 | 124 | 17 | 0 | 0 | 103 | 100 | 0 | 53 |  | 919 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 95 | 0 | 162 | 0 | 300 | 17 | 0 | 0 | 0 | 41 | 0 | 2 | 50 | 500 |  | 6195 | 2877 | 9072 | 3807 | 919 | 1833 | 1499 | 650 | 119 | 120 | 110 | 15 | 0 | 102.05
9:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 302 |  | 0 | 360 | 260 | 69 | 48 | 15 | 0 | 0 | 145 | 0 | 60 | 8 | 10 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 19 | 25 | 31 | 25 | 33 | 0 | 0 | 86 | 35 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 3 | 5 | 20 | 2 | 0 | 80 | 0 | 290 | 260 | 188 | 8 | 85 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 15 | 46 | 140 | 40 | 14 | 2 | 86 | 43 | 25 | 47 | 110 | 158 | 64 | 84 | 0 | 100 | 18 | 0 | 10 | 290 | 16 | 8 | 0 | 45 | 0 | 0 | 160 | 0 | 149 | 15 | 22 | 0 | 76 | 422 | 0 | 60 | 0 | 3 | 124 | 17 | 0 | 17 | 98 | 100 | 50 | 77 |  | 920 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 157 | 0 | 96 | 0 | 161 | 0 | 316 | 17 | 0 | 0 | 0 | 41 | 0 | 3 | 109 | 500 |  | 6379 | 2947 | 9326 | 3919 | 920 | 1827 | 1690 | 650 | 121 | 130 | 46 | 23 | 0 | 102.04
10:00 | 0 | 0 | 100 | 115 | 200 | 71 | 0 | 0 | 304 |  | 0 | 360 | 265 | 100 | 80 | 17 | 0 | 0 | 158 | 0 | 100 | 54 | 48 | 12 | 0 | 0 | 0 | 54 | 35 | 35 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 86 | 35 | 115 | 0 | 0 | 231 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 13 | 18 | 20 | 2 | 0 | 80 | 0 | 290 | 260 | 209 | 8 | 80 | 16 | 5 | 0 | 43 | 0 | 0 | 15 | 18 | 8 | 33 | 15 | 48 | 120 | 40 | 14 | 2 | 83 | 43 | 25 | 47 | 110 | 159 | 63 | 84 | 0 | 20 | 18 | 0 | 10 | 290 | 16 | 8 | 0 | 140 | 0 | 0 | 178 | 0 | 149 | 19 | 22 | 0 | 135 | 417 | 14 | 86 | 0 | 5 | 141 | 17 | 0 | 17 | 102 | 100 | 80 | 104 |  | 919 | 0 | 300 | 0 | 3 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 9 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 169 | 0 | 95 | 0 | 164 | 0 | 308 | 30 | 0 | 2 | 0 | 40 | 0 | 4 | 109 | 480 |  | 6913 | 2952 | 9865 | 3910 | 919 | 1813 | 2227 | 629 | 121 | 168 | 48 | 30 | 0 | 102.04
11:00 | 0 | 0 | 100 | 115 | 200 | 71 | 0 | 0 | 303 |  | 0 | 360 | 275 | 100 | 96 | 55 | 0 | 0 | 150 | 0 | 99 | 85 | 48 | 24 | 0 | 0 | 0 | 54 | 35 | 36 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 86 | 35 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 55 | 19 | 20 | 2 | 0 | 80 | 0 | 290 | 260 | 214 | 8 | 85 | 22 | 5 | 0 | 35 | 0 | 0 | 43 | 16 | 11 | 33 | 15 | 48 | 120 | 40 | 14 | 2 | 83 | 43 | 25 | 47 | 110 | 158 | 63 | 87 | 0 | 20 | 18 | 0 | 10 | 295 | 16 | 8 | 0 | 210 | 0 | 0 | 190 | 0 | 149 | 20 | 22 | 0 | 140 | 416 | 35 | 86 | 0 | 5 | 142 | 17 | 0 | 17 | 104 | 100 | 180 | 104 |  | 918 | 0 | 300 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 9 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 165 | 0 | 95 | 0 | 162 | 0 | 308 | 53 | 0 | 35 | 0 | 69 | 0 | 5 | 109 | 480 |  | 7282 | 3045 | 10327 | 3984 | 918 | 1812 | 2614 | 630 | 121 | 168 | 48 | 32 | 0 | 102.04
12:00 | 0 | 0 | 100 | 115 | 200 | 71 | 0 | 0 | 303 |  | 0 | 340 | 275 | 100 | 96 | 55 | 0 | 0 | 151 | 0 | 97 | 85 | 64 | 26 | 0 | 0 | 0 | 54 | 55 | 36 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 88 | 35 | 115 | 0 | 0 | 205 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 77 | 19 | 20 | 2 | 0 | 80 | 0 | 320 | 280 | 189 | 8 | 82 | 26 | 5 | 0 | 35 | 0 | 0 | 43 | 19 | 11 | 33 | 15 | 48 | 104 | 32 | 14 | 2 | 82 | 43 | 25 | 43 | 110 | 158 | 60 | 87 | 0 | 20 | 18 | 0 | 10 | 300 | 16 | 8 | 0 | 225 | 0 | 0 | 190 | 0 | 149 | 20 | 22 | 0 | 140 | 413 | 35 | 86 | 0 | 5 | 142 | 17 | 0 | 17 | 103 | 100 | 264 | 104 |  | 919 | 0 | 320 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 21 | 10 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 153 | 0 | 93 | 0 | 157 | 0 | 360 | 70 | 0 | 35 | 0 | 75 | 0 | 5 | 109 | 490 |  | 7421 | 3147 | 10568 | 4081 | 919 | 1837 | 2705 | 639 | 123 | 184 | 48 | 32 | 0 | 102.04
13:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 282 |  | 0 | 330 | 265 | 100 | 96 | 55 | 0 | 0 | 175 | 0 | 97 | 93 | 133 | 24 | 0 | 0 | 0 | 54 | 55 | 36 | 19 | 25 | 30 | 33 | 33 | 3 | 0 | 88 | 35 | 115 | 0 | 3 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 10 | 84 | 26 | 20 | 2 | 0 | 70 | 0 | 275 | 260 | 180 | 8 | 75 | 5 | 5 | 0 | 51 | 0 | 0 | 43 | 19 | 11 | 33 | 15 | 54 | 101 | 32 | 14 | 1 | 70 | 43 | 11 | 43 | 110 | 160 | 61 | 84 | 0 | 20 | 18 | 0 | 10 | 300 | 16 | 8 | 0 | 250 | 0 | 0 | 180 | 0 | 149 | 19 | 22 | 5 | 140 | 412 | 65 | 86 | 0 | 4 | 142 | 17 | 0 | 17 | 102 | 100 | 242 | 104 |  | 919 | 0 | 300 | 0 | 83 | 120 | 0 | 0 | 0 | 0 | 8 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 17 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 159 | 0 | 93 | 0 | 188 | 0 | 340 | 70 | 0 | 73 | 0 | 78 | 0 | 5 | 109 | 500 |  | 7413 | 3289 | 10702 | 3974 | 919 | 1787 | 2913 | 650 | 123 | 253 | 54 | 29 | 10702 | 102.04
14:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 292 |  | 0 | 330 | 258 | 75 | 96 | 55 | 0 | 0 | 68 | 0 | 98 | 93 | 150 | 23 | 0 | 0 | 0 | 54 | 55 | 36 | 19 | 25 | 30 | 33 | 33 | 36 | 0 | 88 | 35 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 51 | 22 | 86 | 50 | 20 | 2 | 0 | 70 | 0 | 275 | 260 | 192 | 8 | 76 | 5 | 5 | 0 | 51 | 0 | 0 | 43 | 16 | 11 | 33 | 15 | 56 | 98 | 32 | 14 | 2 | 70 | 43 | 19 | 46 | 110 | 158 | 51 | 84 | 0 | 70 | 18 | 0 | 10 | 270 | 16 | 8 | 0 | 285 | 0 | 0 | 180 | 0 | 142 | 16 | 22 | 20 | 140 | 419 | 85 | 86 | 0 | 2 | 142 | 17 | 0 | 17 | 100 | 100 | 100 | 104 |  | 919 | 0 | 340 | 0 | 83 | 120 | 0 | 0 | 0 | 0 | 8 | 0 | 19 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 20 | 0 | 26 | 52 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 145 | 0 | 93 | 0 | 130 | 0 | 295 | 90 | 0 | 113 | 0 | 83 | 0 | 4 | 109 | 500 |  | 7395 | 3391 | 10786 | 3745 | 919 | 1737 | 3135 | 650 | 123 | 397 | 56 | 24 | 0 | 102.04
15:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 304 |  | 0 | 330 | 290 | 18 | 96 | 55 | 0 | 0 | 150 | 0 | 98 | 93 | 150 | 26 | 0 | 0 | 0 | 54 | 55 | 36 | 19 | 25 | 30 | 33 | 33 | 51 | 0 | 88 | 35 | 115 | 0 | 25 | 205 | 0 | 139 | 0 |  | 0 | 0 | 49 | 30 | 90 | 50 | 20 | 2 | 0 | 70 | 0 | 280 | 260 | 195 | 8 | 81 | 5 | 5 | 0 | 0 | 0 | 13 | 34 | 16 | 11 | 33 | 15 | 56 | 98 | 32 | 14 | 1 | 70 | 43 | 19 | 46 | 110 | 160 | 63 | 84 | 0 | 90 | 18 | 0 | 10 | 300 | 16 | 8 | 0 | 300 | 0 | 0 | 180 | 0 | 149 | 12 | 22 | 51 | 46 | 414 | 85 | 86 | 0 | 1 | 142 | 21 | 0 | 17 | 100 | 90 | 269 | 63 |  | 919 | 0 | 300 | 0 | 49 | 120 | 0 | 0 | 0 | 0 | 8 | 0 | 24 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 20 | 0 | 36 | 25 | 0 | 21 | 10 | 11 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 130 | 0 | 93 | 0 | 130 | 0 | 344 | 90 | 0 | 70 | 0 | 84 | 0 | 3 | 109 | 470 |  | 7593 | 3267 | 10860 | 3984 | 919 | 1782 | 2940 | 621 | 123 | 418 | 56 | 17 | 0 | 102.04
16:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 292 |  | 0 | 330 | 280 | 16 | 96 | 55 | 0 | 0 | 195 | 0 | 98 | 50 | 100 | 34 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 51 | 0 | 87 | 35 | 115 | 0 | 25 | 205 | 0 | 139 | 0 |  | 0 | 8 | 51 | 20 | 90 | 50 | 20 | 3 | 0 | 70 | 0 | 275 | 260 | 186 | 8 | 81 | 5 | 5 | 0 | 48 | 0 | 41 | 34 | 19 | 11 | 33 | 15 | 46 | 100 | 32 | 14 | 1 | 72 | 43 | 19 | 44 | 110 | 158 | 62 | 84 | 0 | 135 | 18 | 0 | 10 | 280 | 16 | 8 | 0 | 286 | 0 | 0 | 187 | 0 | 149 | 7 | 22 | 51 | 103 | 412 | 65 | 86 | 0 | 1 | 142 | 39 | 0 | 17 | 97 | 90 | 0 | 53 |  | 919 | 0 | 250 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 16 | 0 | 0 | 0 | 50 | 0 | 0 | 20 | 0 | 36 | 25 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 137 | 0 | 65 | 0 | 144 | 0 | 357 | 53 | 0 | 35 | 0 | 72 | 0 | 2 | 70 | 420 |  | 7386 | 3028 | 10414 | 3764 | 919 | 1779 | 2797 | 570 | 122 | 406 | 46 | 11 | 0 | 102.04
17:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 292 |  | 0 | 330 | 270 | 16 | 96 | 55 | 0 | 0 | 70 | 0 | 98 | 40 | 82 | 23 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 51 | 0 | 83 | 35 | 115 | 0 | 25 | 204 | 0 | 70 | 0 |  | 0 | 8 | 51 | 20 | 94 | 50 | 20 | 4 | 0 | 70 | 0 | 275 | 260 | 180 | 8 | 78 | 5 | 5 | 0 | 51 | 0 | 41 | 43 | 19 | 11 | 33 | 15 | 40 | 100 | 32 | 17 | 0 | 71 | 43 | 22 | 20 | 110 | 160 | 40 | 40 | 0 | 163 | 18 | 0 | 10 | 285 | 24 | 11 | 0 | 300 | 0 | 0 | 150 | 0 | 149 | 1 | 22 | 51 | 142 | 417 | 45 | 86 | 0 | 0 | 105 | 50 | 0 | 17 | 65 | 90 | 0 | 53 |  | 919 | 0 | 250 | 0 | 16 | 120 | 0 | 0 | 3 | 0 | 8 | 0 | 21 | 16 | 0 | 0 | 0 | 50 | 10 | 18 | 20 | 0 | 36 | 25 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 150 | 0 | 52 | 0 | 160 | 0 | 305 | 53 | 0 | 35 | 0 | 80 | 0 | 1 | 70 | 420 |  | 7017 | 3030 | 10047 | 3615 | 919 | 1658 | 2706 | 570 | 118 | 419 | 40 | 2 | 0 | 102.04
18:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 312 |  | 0 | 340 | 270 | 16 | 97 | 55 | 0 | 0 | 150 | 0 | 100 | 45 | 150 | 24 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 21 | 33 | 33 | 51 | 0 | 83 | 35 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 17 | 102 | 100 | 90 | 50 | 20 | 4 | 0 | 70 | 0 | 295 | 260 | 213 | 8 | 81 | 5 | 5 | 0 | 51 | 0 | 41 | 43 | 19 | 11 | 33 | 15 | 134 | 100 | 32 | 17 | 0 | 71 | 43 | 25 | 35 | 110 | 158 | 65 | 87 | 0 | 164 | 18 | 0 | 10 | 270 | 24 | 11 | 70 | 300 | 109 | 25 | 163 | 53 | 149 | 0 | 22 | 85 | 142 | 417 | 73 | 86 | 0 | 0 | 159 | 43 | 0 | 35 | 77 | 100 | 0 | 53 |  | 919 | 0 | 310 | 0 | 85 | 180 | 0 | 0 | 7 | 0 | 40 | 0 | 35 | 110 | 0 | 0 | 0 | 50 | 42 | 96 | 20 | 0 | 36 | 52 | 32 | 0 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 142 | 0 | 90 | 32 | 153 | 0 | 375 | 90 | 30 | 50 | 0 | 92 | 0 | 0 | 100 | 440 |  | 8061 | 3779 | 11840 | 3880 | 919 | 1839 | 3607 | 590 | 118 | 753 | 134 | 0 | 0 | 102.04
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 292 |  | 0 | 340 | 268 | 16 | 97 | 55 | 0 | 0 | 175 | 0 | 100 | 20 | 150 | 24 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 51 | 0 | 83 | 35 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 102 | 100 | 91 | 50 | 20 | 8 | 0 | 70 | 0 | 295 | 260 | 205 | 8 | 81 | 5 | 5 | 0 | 51 | 0 | 41 | 43 | 19 | 11 | 33 | 15 | 140 | 101 | 32 | 17 | 0 | 71 | 43 | 25 | 46 | 110 | 158 | 64 | 87 | 0 | 192 | 18 | 0 | 10 | 300 | 24 | 11 | 70 | 300 | 108 | 25 | 189 | 52 | 149 | 0 | 22 | 149 | 142 | 419 | 115 | 86 | 0 | 0 | 160 | 54 | 0 | 100 | 108 | 100 | 0 | 53 |  | 920 | 0 | 305 | 0 | 115 | 220 | 0 | 0 | 16 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 42 | 96 | 20 | 0 | 36 | 52 | 32 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 178 | 0 | 93 | 100 | 181 | 0 | 369 | 90 | 30 | 110 | 15 | 99 | 0 | 0 | 109 | 540 |  | 8343 | 4195 | 12538 | 3995 | 920 | 1882 | 4008 | 690 | 118 | 785 | 140 | 0 | 0 | 102.04
19:30 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 282 |  | 0 | 340 | 285 | 16 | 97 | 55 | 0 | 0 | 180 | 0 | 100 | 18 | 150 | 24 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 30 | 33 | 33 | 51 | 0 | 83 | 35 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 102 | 100 | 56 | 50 | 20 | 11 | 0 | 70 | 0 | 295 | 260 | 203 | 8 | 82 | 5 | 5 | 0 | 51 | 0 | 41 | 43 | 19 | 11 | 33 | 15 | 140 | 100 | 36 | 17 | 0 | 71 | 43 | 25 | 46 | 110 | 160 | 64 | 87 | 0 | 192 | 18 | 0 | 10 | 300 | 24 | 11 | 70 | 300 | 33 | 30 | 189 | 52 | 149 | 0 | 22 | 163 | 142 | 419 | 115 | 86 | 0 | 0 | 161 | 54 | 0 | 84 | 113 | 100 | 0 | 53 |  | 918 | 0 | 295 | 0 | 115 | 220 | 0 | 0 | 17 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 42 | 96 | 20 | 0 | 36 | 52 | 32 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 180 | 0 | 92 | 100 | 178 | 0 | 395 | 90 | 30 | 113 | 15 | 99 | 0 | 0 | 109 | 550 |  | 8240 | 4224 | 12464 | 3970 | 918 | 1903 | 3929 | 700 | 118 | 786 | 140 | 0 | 0 | 102.04
20:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 282 |  | 0 | 340 | 260 | 16 | 97 | 55 | 0 | 0 | 180 | 0 | 100 | 20 | 150 | 40 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 30 | 33 | 33 | 51 | 0 | 85 | 35 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 100 | 100 | 35 | 50 | 20 | 15 | 0 | 70 | 0 | 295 | 260 | 200 | 8 | 80 | 5 | 5 | 0 | 51 | 0 | 41 | 43 | 19 | 11 | 33 | 22 | 136 | 101 | 40 | 20 | 0 | 71 | 43 | 25 | 46 | 110 | 160 | 64 | 86 | 0 | 192 | 18 | 0 | 10 | 280 | 24 | 11 | 70 | 300 | 33 | 50 | 189 | 52 | 149 | 0 | 22 | 163 | 142 | 420 | 115 | 86 | 0 | 0 | 161 | 54 | 0 | 100 | 113 | 100 | 0 | 53 |  | 919 | 0 | 280 | 0 | 115 | 220 | 0 | 0 | 17 | 0 | 40 | 0 | 39 | 110 | 0 | 0 | 0 | 50 | 42 | 96 | 20 | 0 | 45 | 52 | 32 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 176 | 0 | 96 | 100 | 175 | 0 | 398 | 90 | 30 | 113 | 15 | 97 | 0 | 0 | 109 | 550 |  | 8238 | 4219 | 12457 | 3955 | 919 | 1895 | 3939 | 700 | 120 | 793 | 136 | 0 | 0 | 102.04
21:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 283 |  | 0 | 340 | 260 | 16 | 97 | 55 | 0 | 0 | 180 | 0 | 100 | 22 | 150 | 88 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 51 | 0 | 86 | 35 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 100 | 100 | 11 | 50 | 20 | 21 | 0 | 70 | 0 | 295 | 260 | 211 | 8 | 82 | 5 | 5 | 0 | 51 | 0 | 41 | 43 | 19 | 11 | 33 | 22 | 138 | 101 | 40 | 20 | 0 | 71 | 43 | 25 | 46 | 110 | 158 | 64 | 86 | 0 | 192 | 18 | 0 | 10 | 300 | 24 | 11 | 70 | 300 | 33 | 50 | 189 | 51 | 149 | 0 | 22 | 163 | 142 | 420 | 115 | 86 | 0 | 0 | 161 | 54 | 0 | 17 | 113 | 100 | 0 | 53 |  | 919 | 0 | 265 | 0 | 115 | 220 | 0 | 0 | 17 | 0 | 40 | 0 | 39 | 110 | 0 | 0 | 0 | 50 | 42 | 96 | 20 | 0 | 36 | 52 | 32 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 168 | 0 | 97 | 100 | 164 | 0 | 396 | 90 | 30 | 113 | 15 | 97 | 0 | 0 | 109 | 560 |  | 8240 | 4185 | 12425 | 3951 | 919 | 1921 | 3881 | 710 | 121 | 784 | 138 | 0 | 0 | #REF!
22:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 293 |  | 0 | 340 | 270 | 16 | 97 | 55 | 0 | 0 | 180 | 0 | 100 | 24 | 150 | 87 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 51 | 0 | 86 | 35 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 102 | 90 | 6 | 50 | 20 | 21 | 0 | 70 | 0 | 295 | 260 | 213 | 8 | 75 | 5 | 5 | 0 | 43 | 0 | 41 | 43 | 19 | 11 | 33 | 22 | 136 | 120 | 40 | 20 | 0 | 71 | 43 | 25 | 46 | 110 | 158 | 64 | 86 | 0 | 192 | 18 | 0 | 10 | 285 | 24 | 11 | 70 | 300 | 32 | 0 | 189 | 0 | 149 | 0 | 22 | 163 | 142 | 425 | 115 | 86 | 0 | 0 | 161 | 54 | 0 | 17 | 113 | 100 | 0 | 53 |  | 918 | 0 | 255 | 0 | 115 | 220 | 0 | 0 | 17 | 0 | 40 | 0 | 39 | 110 | 0 | 0 | 0 | 50 | 42 | 96 | 20 | 0 | 36 | 52 | 32 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 162 | 0 | 97 | 100 | 158 | 0 | 347 | 90 | 30 | 113 | 15 | 98 | 0 | 0 | 109 | 560 |  | 8140 | 4114 | 12254 | 3948 | 918 | 1859 | 3776 | 710 | 121 | 786 | 136 | 0 | 0 | 102.04
23:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 304 |  | 0 | 350 | 270 | 16 | 97 | 55 | 0 | 0 | 140 | 0 | 100 | 16 | 150 | 22 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 51 | 0 | 87 | 35 | 115 | 0 | 25 | 213 | 0 | 139 | 0 |  | 0 | 0 | 102 | 90 | 6 | 50 | 20 | 25 | 0 | 70 | 0 | 310 | 260 | 214 | 8 | 75 | 5 | 5 | 0 | 51 | 0 | 41 | 36 | 13 | 11 | 33 | 22 | 134 | 120 | 40 | 20 | 0 | 71 | 43 | 25 | 46 | 110 | 158 | 64 | 86 | 0 | 192 | 18 | 0 | 10 | 285 | 24 | 11 | 0 | 300 | 0 | 0 | 189 | 0 | 149 | 0 | 22 | 120 | 142 | 419 | 115 | 86 | 0 | 0 | 161 | 54 | 0 | 17 | 113 | 100 | 0 | 53 |  | 919 | 0 | 245 | 0 | 115 | 220 | 0 | 0 | 17 | 0 | 40 | 0 | 39 | 110 | 0 | 0 | 0 | 50 | 42 | 96 | 20 | 0 | 36 | 52 | 32 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 162 | 0 | 97 | 100 | 153 | 0 | 396 | 90 | 0 | 113 | 15 | 99 | 0 | 0 | 109 | 560 |  | 7920 | 4120 | 12040 | 3906 | 919 | 1941 | 3522 | 710 | 122 | 786 | 134 | 0 | 0 | 102.04
24:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 327 |  | 0 | 350 | 295 | 16 | 97 | 55 | 0 | 0 | 97 | 0 | 100 | 16 | 150 | 32 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 51 | 0 | 87 | 35 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 102 | 90 | 6 | 50 | 20 | 30 | 0 | 70 | 0 | 295 | 260 | 209 | 8 | 75 | 5 | 5 | 0 | 51 | 0 | 41 | 35 | 13 | 11 | 33 | 22 | 144 | 120 | 40 | 20 | 0 | 72 | 43 | 25 | 46 | 110 | 160 | 64 | 86 | 0 | 192 | 18 | 0 | 10 | 305 | 24 | 11 | 0 | 300 | 0 | 0 | 189 | 0 | 149 | 0 | 22 | 120 | 142 | 423 | 115 | 85 | 0 | 0 | 161 | 37 | 0 | 17 | 112 | 100 | 0 | 54 |  | 919 | 0 | 240 | 0 | 115 | 210 | 0 | 0 | 17 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 42 | 96 | 20 | 0 | 36 | 52 | 32 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 96 | 0 | 148 | 0 | 336 | 90 | 0 | 113 | 15 | 100 | 0 | 0 | 109 | 560 |  | 7929 | 3935 | 11864 | 3827 | 919 | 1927 | 3439 | 710 | 122 | 776 | 144 | 0 | 0 | 102.04
KWH | 0 | 0 | 2408000 | 2740500 | 4796764 | 1704090 | 0 | 0 | 7367000 |  | 0 | 7370050 | 6535680 | 1446720 | 2178552 | 1123736 | 0 | 0 | 3442000 | 0 | 2289600 | 1211472 | 2227200 | 540766 | 0 | 0 | 0 | 982800 | 1214372 | 1095319 | 392436 | 600000 | 689580 | 719200 | 823300 | 548472 | 0 | 2005015 | 840000 | 2700000 | 0 | 306221 | 4920397 | 0 | 3054440 | 0 |  | 0 | 35621 | 1181440 | 717240 | 1178880 | 719040 | 462432 | 456480 | 0 | 1790995 | 0 | 7460400 | 6518000 | 4704000 | 200727 | 1861210 | 335376 | 143040 | 0 | 1147653 | 0 | 333672 | 741480 | 429516 | 249840 | 817600 | 466080 | 2467200 | 2903680 | 889920 | 388584 | 14400 | 1861000 | 1023720 | 567000 | 1088640 | 2645836 | 3448000 | 1488480 | 2020800 | 0 | 3042810 | 415000 | 0 | 246780 | 7200200 | 485568 | 219000 | 313536 | 5743307 | 296188 | 193155 | 4351200 | 243874 | 3569900 | 142965 | 539520 | 1210560 | 3041018 | 10048000 | 1699200 | 1919928 | 0 | 27720 | 3457527 | 794687 | 0 | 469680 | 2375520 | 2381760 | 1236300 | 1967040 |  | 22069818 | 0 | 7246368 | 0 | 1298880 | 3580800 | 0 | 0 | 117120 | 0 | 300750 | 0 | 684202 | 1212000 | 0 | 0 | 0 | 544240 | 289592 | 795720 | 383130 | 0 | 369478 | 542400 | 224480 | 486000 | 235728 | 242730 | 0 | 0 | 3665800 | 0 | 0 | 0 | 0 | 3984491 | 0 | 2221642 | 625920 | 4118945 | 0 | 8320145 | 1789920 | 149061 | 1465056 | 105696 | 1980480 | 0 | 36972 | 2380992 | 13190300 |  | 178663607 | 84658856 | 263322463 | 94534742 | 22069818 | 44106013 | 70522155 | 16856100 | 2845015 | 9699363 | 2467200 | 222057 | 0
Fuel Cost | 0 | 0 | 3515680 | 4028535 | 5324408.04 | 2249398.8 | 0 | 0 | 7588010 |  | 0 | 8033354.5 | 7254604.8 | 10980604.8 | 15010223.28 | 9506806.56 | 0 | 0 | 5954660 | 0 | 17240688 | 11048624.64 | 21915648 | 4985862.52 | 0 | 0 | 0 | 7174440 | 9387095.56 | 10799845.34 | 294327 | 450000 | 0 | 0 | 0 | 5303724.24 | 0 | 541354.05 | 226800 | 4887000 | 0 | 2844793.09 | 5363232.73 | 0 | 5192548 | 0 |  | 0 | 344455.07 | 11459968 | 6849642 | 10256256 | 5694796.8 | 582664.32 | 1355745.6 | 0 | 2650672.6 | 0 | 5520696 | 6518000 | 4327680 | 258937.83 | 2140391.5 | 378974.88 | 200256 | 0 | 1962486.63 | 0 | 3370087.2 | 7081134 | 545485.32 | 187380 | 1430800 | 349560 | 18504000 | 3077900.8 | 8080473.6 | 493501.68 | 229536 | 3052040 | 1637952 | 1009260 | 1698278.4 | 3016253.04 | 3585920 | 2932305.6 | 3859728 | 0 | 5264061.3 | 908850 | 0 | 503431.2 | 7272202 | 364176 | 166440 | 5333247.36 | 43419400.92 | 5029272.24 | 3229551.6 | 22626240 | 4077573.28 | 35127816 | 1671260.85 | 4397088 | 13134576 | 21439176.9 | 9344640 | 15496704 | 18143319.6 | 0 | 0 | 26138904.12 | 6921723.77 | 0 | 4687406.4 | 20358206.4 | 15862521.6 | 0 | 0 |  | 127122151.68 | 0 | 7608686.4 | 0 | 10209196.8 | 49629888 | 0 | 0 | 1228588.8 | 0 | 3133815 | 0 | 1060513.1 | 11829120 | 0 | 0 | 0 | 5355321.6 | 2942254.72 | 7042122 | 2950101 | 0 | 3580241.82 | 5255856 | 2177456 | 933120 | 365378.4 | 183746.61 | 0 | 0 | 19868636 | 0 | 0 | 0 | 0 | 5259528.12 | 0 | 3332463 | 10646899.2 | 4819165.65 | 0 | 8236943.55 | 18686764.8 | 2535527.61 | 13903381.44 | 997770.24 | 15368524.8 | 0 | 408540.6 | 17595530.88 | 57905417 |  | 602663277.36 | 422172650.82 | 1024835928.18 | 108341609.55 | 127122151.68 | 52935760.05 | 528034831.19 | 77774053 | 768154.05 | 109046031.21 | 18504000 | 2309337.45 | 0
Yesterday Day Peak | 0 | 0 | 100 | 115 | 200 | 71 | 0 | 0 | 303 |  | 0 | 340 | 275 | 100 | 96 | 55 | 0 | 0 | 151 | 0 | 97 | 85 | 64 | 26 | 0 | 0 | 0 | 54 | 55 | 36 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 88 | 35 | 115 | 0 | 0 | 205 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 77 | 19 | 20 | 2 | 0 | 80 | 0 | 320 | 280 | 189 | 8 | 82 | 26 | 5 | 0 | 35 | 0 | 0 | 43 | 19 | 11 | 33 | 15 | 48 | 104 | 32 | 14 | 2 | 82 | 43 | 25 | 43 | 110 | 158 | 60 | 87 | 0 | 20 | 18 | 0 | 10 | 300 | 16 | 8 | 0 | 225 | 0 | 0 | 190 | 0 | 149 | 20 | 22 | 0 | 140 | 413 | 35 | 86 | 0 | 5 | 142 | 17 | 0 | 17 | 103 | 100 | 264 | 104 |  | 919 | 0 | 320 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 21 | 10 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 153 | 0 | 93 | 0 | 157 | 0 | 360 | 70 | 0 | 35 | 0 | 75 | 0 | 5 | 109 | 490 |  | 10568 | DayPeak
Yesterday Evening Peak | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 292 | 0 | 0 | 340 | 268 | 16 | 97 | 55 | 0 | 0 | 175 | 0 | 100 | 20 | 150 | 24 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 51 | 0 | 83 | 35 | 115 | 0 | 25 | 204 | 0 | 139 | 0 | 0 | 0 | 0 | 102 | 100 | 91 | 50 | 20 | 8 | 0 | 70 | 0 | 295 | 260 | 205 | 8 | 81 | 5 | 5 | 0 | 51 | 0 | 41 | 43 | 19 | 11 | 33 | 15 | 140 | 101 | 32 | 17 | 0 | 71 | 43 | 25 | 46 | 110 | 158 | 64 | 87 | 0 | 192 | 18 | 0 | 10 | 300 | 24 | 11 | 70 | 300 | 108 | 25 | 189 | 52 | 149 | 0 | 22 | 149 | 142 | 419 | 115 | 86 | 0 | 0 | 160 | 54 | 0 | 100 | 108 | 100 | 0 | 53 |  | 920 | 0 | 305 | 0 | 115 | 220 | 0 | 0 | 16 | 0 | 40 | 0 | 38 | 110 | 0 | 0 | 0 | 50 | 42 | 96 | 20 | 0 | 36 | 52 | 32 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 178 | 0 | 93 | 100 | 181 | 0 | 369 | 90 | 30 | 110 | 15 | 99 | 0 | 0 | 109 | 540 |  | 12538 | EvPeak
Forecast for Evening | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 360 | 0 | 0 | 450 | 305 | 100 | 100 | 40 | 0 | 0 | 165 | 0 | 100 | 94 | 150 | 88 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 85 | 35 | 115 | 0 | 25 | 221 | 0 | 145 | 0 | 0 | 0 |  | 102 | 100 | 97 | 50 | 21 | 20 | 0 | 80 | 0 | 360 | 350 | 225 | 8 | 90 | 30 | 5 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 22 | 173 | 150 | 48 | 20 | 0 | 85 | 43 | 51 | 44 | 110 | 160 | 65 | 86 | 0 | 200 | 20 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 22 | 200 | 150 | 400 | 115 | 86 | 100 | 0 | 300 | 54 | 110 | 17 | 113 | 100 | 0 | 17 |  | 928 | 16 | 410 | 0 | 115 | 220 | 0 | 0 | 30 | 60 | 40 | 0 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 20 | 0 | 50 | 52 | 30 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 225 | 0 | 95 | 100 | 220 | 0 | 414 | 105 | 200 | 113 | 100 | 109 | 0 | 0 | 113 | 580
Forecast for Day | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 360 | 0 | 0 | 450 | 305 | 100 | 100 | 40 | 0 | 0 | 115 | 0 | 100 | 94 | 150 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 85 | 35 | 115 | 0 | 25 | 221 | 0 | 145 | 0 | 0 | 0 |  | 102 | 100 | 97 | 50 | 21 | 5 | 0 | 80 | 0 | 360 | 350 | 225 | 8 | 90 | 30 | 5 | 0 | 51 | 0 | 25 | 25 | 22 | 11 | 33 | 22 | 165 | 150 | 48 | 20 | 1.6 | 85 | 43 | 51 | 44 | 110 | 160 | 65 | 86 | 0 | 140 | 18 | 0 | 10 | 341 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 22 | 200 | 150 | 400 | 115 | 85 | 100 | 5 | 300 | 54 | 110 | 0 | 113 | 100 | 0 | 17 |  | 928 | 0 | 410 | 0 | 115 | 220 | 0 | 0 | 0 | 0 | 40 | 0 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 20 | 0 | 50 | 52 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 225 |  | 95 | 50 | 220 | 0 | 414 | 105 | 100 | 113 | 100 | 105 | 0 | 8 | 113 | 580
Generation at 08:00(Today) | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 347 | 0 | 0 | 420 | 250 |  | 48 | 15 | 0 | 0 | 115 | 0 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 30 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 86 | 35 | 115 | 0 | 0 | 204 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 4 | 0 | 80 | 0 | 275 | 260 | 217 | 8 | 75 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 15 | 110 | 142 | 40 | 0 | 0 | 74 | 43 | 25 | 46 | 110 | 160 | 64 | 86 | 0 | 165 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 95 | 0 | 0 | 199 | 0 | 149 | 1 | 11 | 0 | 20 | 427 | 0 | 34 | 0 | 2 | 138 | 17 | 0 | 0 | 106 | 100 | 0 | 53 | 0 | 919 | 0 | 285 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 151 | 0 | 53 | 0 | 158 | 0 | 291 | 17 | 0 | 0 | 0 | 0 | 0 | 2 | 50 | 460 | 0
199
| Minimum Generation |  | 8975 | 7:00
| Highest Generation |  | 12538 | 19:00
| Day Peak Generation |  | 10568 | 12:00
| Evening Peak Generation |  | 12538 | 19:00
| HVDC Max Flow |  | 920 | 2:00
| HVDC EvPeak Flow |  | 920 | 19:00
| Load factor L.F |  | 87.51%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-10-21
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-10-20 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10568 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 8976 | MW
Evening Peak Generation : |  | 12538 | MW Hour : | 19:00 | Available Max Generation : |  | 14849 | MW
E.P. Demand (at gen end) : |  | 12538 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 12800 | MW
Maximum Generation : |  | 12538 | MW Hour : | 19:00 | Reserve(Generation end) |  | 2049 | MW
Total Gen. (MKWH) : |  | 263.3225 | System Load Factor : | 87.51% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -30 | MW at | 3:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-10-21
Actual : | 102.04 | Ft.(MSL) , | Rule curve : | 107.9 | Ft.( MSL )
Gas Consumed : | Total = | 1163.15 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 161277369.6
: |  | Coal : | 77774053 | Oil : | 637080862.4 | Total : | 876132285
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4528.3803 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1544.1081 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1384.2195 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1251.0253 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1130.3867 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 912.1927 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 504.638 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 234.7218 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 703.5542 |  |  | 0 | 0%
Total | 0 |  | 12193.2265 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Baghabari-71 MW,100 MW
3) Ghorasal Unit-1,2,3
4) Ashuganj unit-3,4
5) Kaptai-2,4
6) Raozan #2
7) Siddirganj-335 MW
8) Haripur 412 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Madanganj-Munshiganj 132 kV Ckt-2 was shut down from 09:02 to 14:45 for A/M.
b) Haripur-HPL 230 kV Ckt-2 was under shut down from 08:15 to 16:20 for A/M.
c) Bogura(Old) 132/33 kV T4 transformer was under shut down from 08:32 to 18:06 for A/M.
d) Palashbari 132/33 kV T-2 transformer was under shut down from 08:10 to 14:56 for A/M.
e) Jaldhaka 132/33 kV T-2 transformer was under shut down from 08:45 to 16:45 for A/M.
f) Hasnabad 230/132 kV T02 transformer was under shut down from 10:21 to 17:24 for A/M.
g) Thakurgaon 132/33 kV T-1 transformer was under shut down from 08:38 to 15:28 for A/M.
h) Sirajganj 132/33 kV T-4 transformer was under shut down from 10:46 to 17:28 for A/M.
i) Kurigram 132/33 kV T-2 transformer was under shut down from 08:26 to 15:35 for A/M.
j) Rangamati-Khagrachari 132 kV Ckt-2 was under shut down from 08:42 to 14:45 for A/M.
k) Saver 33 kV Bus-A was under shut down from 08:17 to 10:49 due to Dhaka PBS work.
l) Sylhet 225 MW CCPP STG was synchronized at 13:35.
m) Ashuganj-Sirajganj 230 kV Ckt-1 tripped at 14:18 from both end showing Dist, RST,general trip,AR block,
TCSR, Z1 relays at Sirajganj end and was switched on at 5:18.
n) Hathazari 230/132 kV T01 transformer was under shut down from 17:40 to 19:37 due to 230 kV PT
R-phase vibration.
o) Ishwardi-Bheramara 132 kV Ckt-2 was under shut down from 15:45 to 16:48 due to oil leakage at PT.
p) Kaliakoir-Kabirpur 132 kV Ckt-1 was under shut down from 15:53 to 16:47 for D/W.
q) Kaliakoir-Kabirpur 132 kV Ckt-2 was switched on at 16:48.
r) Hathazari 230/132 kV T02 transformer was under shut down from 19:55 to 20:32 due to 230 kV PT vibration.
s) Kabirpur 132/33 kV T3 transformer was shut down at 06:36(21/10/2020) for C/M.
t) Kabirpur 132 kV Bus-1 was under shut down from 07:10(21/10/2020) to 07:54(21/10/2020) for C/M.
u) Kishoreganj 132/33 kv T1 transformer was under shut down from 22:45 to 23:27 due to Nandail-1 |  |  |  |  | About 50 MW power interruption occurred under Kishoreganj S/S area
feeder loop join R-phase red hot. |  |  |  |  | from 22:45 to 23:27.
v) Bakulia 132/33 kV T2 transformer tripped at 06:43(21/10/2020) showing Diff. relays at 132 kV end

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-10-20 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 100 | 2408000 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 115 | 2740500 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 4796764 | Machin problem.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 72 | 1704090 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 292 | 7367000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 340 | 7370050 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 16 | 1446720 | Fuel Shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 268 | 6535680 | Engine problem
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 97 | 2178552
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1123736
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 24 | 540766 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 392436
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 175 | 3442000
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 2289600
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under Maintenance
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 20 | 1211472 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel Shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 982800
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 2227200
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1214372
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1095319
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1289580 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 719200
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 823300
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 548472
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 5743307
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 108 | 296188 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 25 | 193155 | Low demand
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 52 | 243874 | Low demand
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3569900
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 86 | 1919928 | Engine problem
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 53 | 1967040 | Fuel Shortage
| Dhaka area Total |  |  |  | 5895 | 3152 | 68381001
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 115 | 2700000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 306221
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 142965
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 719040
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 118 | 2845015 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4920397
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 139 | 3054440
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Transformer overload
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 35621 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 1181440
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 717240
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 22 | 539520 | Engine problem
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 462432
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 8 | 456480
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 91 | 1178880 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27720
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 160 | 3457527 | Transformer O/L.
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 794687
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Transformer O/L.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2381760
| Chattogram area Total |  |  |  | 2266 | 1308 | 25921385
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 70 | 1790995 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 205 | 4704000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 295 | 7460400 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 260 | 6518000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 5 | 335376 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 143040 | Gas shortage
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1147653
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 142 | 3041018
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 41 | 333672
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 81 | 1861210 | ST Under maint
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 149 | 1210560 | Engine problem
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 429516
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 249840
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 140 | 2467200
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 817600
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 741480 | Engine problem
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 15 | 466080 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 70 | 313536 | Low demand
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 100 | 469680 | Engine problem
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 108 | 2375520
| Cumilla Area Total |  |  |  | 2980 | 1851 | 37077103
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 101 | 2903680 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 388584 | Engine problem
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 32 | 889920 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14400
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 189 | 4351200
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1699200 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 454 | 10246984
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 71 | 1861000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 1023720 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2645836 | Engine problem
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 158 | 3448000 | FGMO & GT-2 under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 25 | 567000 | Engine problem
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 46 | 1088640
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 219000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 64 | 1488480 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 87 | 2020800
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 192 | 3042810 | Machin problem.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 415000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 485568
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7200200 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 419 | 10048000
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 246780
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 1236300 | On test
| Sylhet Area Total |  |  |  | 1988 | 1578 | 37037134
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 920 | 22069818
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 1298880
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 16 | 117120
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 220 | 3580800
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 305 | 7246368 | Gas shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 300750
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 625920
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 90 | 1789920 | Engine problem
107 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 15 | 105696 | Line O/L.
| Khulna Area Total |  |  |  | 2284 | 1821 | 37135272
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1212000
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 38 | 684202
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 93 | 2221642
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 540 | 13190300 | Line O/L.
| Barisal Area Total |  |  |  | 1054 | 781 | 17308144
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 544240
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 42 | 289592
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 20 | 383130 | Engine problem
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel Shortage
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 36 | 369478
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas Shortage
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 178 | 3984491 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 181 | 4118945 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 369 | 8320145 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 224480
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 18 | 486000 | Engine problem
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 10 | 235728
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 242730
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 542400
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 96 | 795720
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 30 | 149061 | Low demand
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 110 | 1465056
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 2380992
| Rajshahi Area Total |  |  |  | 2183 | 1344 | 24532188
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3665800 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 99 | 1980480 | Engine problem
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 36972
| Rangpur Area Total |  |  |  | 605 | 249 | 5683252
| Total |  |  |  | 19892 | 12538 | 263322463
| Eastern Grid Total |  |  |  | 13766 | 8343 | 178663607
| Western Grid Total |  |  |  | 6126 | 4195 | 84658856
| National Grid Total |  |  |  | 19892 | 12538 | 263322463
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-10-20
| (a) ENTIRE EASTERN GRID : |  | 8057 | MW | (b) ENTIRE WESTERN GRID : |  | 3876 | MW
| i) Dhaka area |  | 4226 | MW | i) Khulna area |  | 1507 | MW
| ii) Chittagong area |  | 1215 | MW | ii) Rajshahi area |  | 1252 | MW
| iii) Comilla area |  | 1142 | MW | iii) Barisal area |  | 339 | MW
| iv) Mymensingh area |  | 934 | MW | iv) Rangpur area |  | 778 | MW
| v) Sylhet area |  | 540 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11933 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 132 | 12:00 | Sherpur | 112 | 19:00 | Jhenida | 112 | 18:30
| Munsiganj | 126 | 22:00 | Srimongal | 52 | 18:00 | Bottail | 130 | 19:00
| Sonargaon | 75 | 21:00 | Shahjibazar | 125 | 21:00 | G.K Project | 57 | 18:30
| Shyampur | 206 | 0:00 | Fenchuganj | 43 | 18:00 | Faridpur | 191 | 0.91667
| Bhulta | 193 | 12:00 | Kulawara | 46 | 18:30 | Madaripur | 103 | 0.875
| Madanganj | 54 | 14:00 | Sylhet | 148 | 18:30 | Sariatpur | 66 | 21:00
| Shitalakhya | 113 | 11:00 | Chatak | 29 | 19:30 | Gopalganj | 88 | 20:00
| Rahim steel | 17 | 19:00 | Sunamganj | 50 | 19:30 | Bagerhat | 103 | 19:30
| Matuail | 82 | 10:00 | Biani Bazar | 59 | 19:00 | Mongla | 38 | 8:00
| Ghorasal | 85 | 21:00 | Comilla (S) | 144 | 00.:00 | Satkhira | 113 | 0.875
| Narsingdi | 169 | 21:00 | Comilla(N) | 121 | 18:30 | Gallamari | 48 | 19:30
| Haripur (SBU) | 94 | 4:00 | Chandpur | 101 | 19:30 | Magura | 54 | 0.79167
| Ullon | 56 | 19:30 | Feni | 120 | 19:30 | Norail | 40 | 19:00
| Hasnabad | 205 | 21:00 | Chowmuhani | 186 | 19:00 | Chuadanga | 94 | 19:30
| Magbazar | 108 | 13:00 | Ashuganj | 59 | 23:00 | Barisal(N) | 47 | 0.875
| Maniknagar | 106 | 13:00 | Daudkandi | 151 | 22:00 | Barisal (S) | 100 | 0.8125
| Bangabhaban | 36 | 10:00 | B.Baria | 164 | 20:00 | Patuakhali | 118 | 0.95833
| Narinda | 90 | 13:00 | Ramganj | 118 | 21:00 | Bhandaria | 56 | 0.875
| Dhanmondi | 182 | 13:00 | Chaddagram | 51 | 20:00 | Borhan Uddin | 42 | 1:00
| Lalbag | 90 | 13:00 | PHP | 10 | 18:00 | Ishurdi | 63 | 18:00
| Madartek | 75 | 22:00 | Madunaghat | 56 | 18:30 | Ruppur Paromanobik | 2 | 1:00
| Dhaka University | 0 | #NUM! | Hathazari | 101 | 0.75 | Natore | 121 | 20:00
| Fatullah | 43 | 0.41667 | Khulshi | 213 | 0.5 | Bogra | 164 | 19:00
| Mirpur | 109 | 12:00 | Halishahar | 139 | 0.58333 | Noagaon | 117 | 19:30
| Kalyanpur | 108 | 19:00 | Baraulia | 155 | 0 | Rajshahi | 147 | 20:00
| Gulshan | 142 | 13:00 | Sikalbaha | 28 | 0.75 | Rajshahi New | 14 | 19:30
| Uttara | 104 | 13:00 | Dohazari | 90 | 0.83333 | C.Nawabganj | 78 | 20:00
| Uttara New | 33 | 15:00 | Cox'sbazar | 101 | 0.77083 | Amnura | 44 | 19:30
| Kamrangirchar | 96 | 18:30 | Chandraghona | 32 | 0.75 | Pabna | 122 | 19:30
| Savar | 145 | 16:00 | Kaptai | 4.5 | 0.75 | Shahjadpur | 108 | 20:00
| Bhasantec | 163 | 13:00 | A. Khaer Stl. | 0 | 0.041667 | Serajganj | 106 | 21:00
| Agargaon | 79 | 13:00 | Bakulia | 105 | 0.79167 | Niyamatpur | 58 | 20:00
| Satmosjid | 87 | 13:00 | Julda | 21 | 0.041667 | Joypurhat | 58 | 20:00
| Tongi | 104 | 0.75 | TK chemical | 19.6 | 0.77083 | Sherpur(Bogura) | 49 | 18:30
| Kabirpur | 231 | 18:00 | Modern Steel | 16 | 0.083333 | Mohastangor | 48 | 19:30
| Basundhara | 150 | 12:00 | Shahmirpur | 22 | 0.625 | Rangpur | 149 | 18:30
| Manikganj | 80 | 21:00 | Khagrachhari | 24 | 0.25 | Lalmonirhat | 49 | 18:00
| Joydevpur | 160 | 18:30 | Matarbari | 36.5 | 0.041667 | Saidpur | 106 | 18:30
| New Tongi | 110 | 12:00 | Baroiar Hat | 48 | 0.77083 | Purbasadipur | 102 | 20:00
| Kodda | 234 | 18:00 | Rangamati | 12 | 0.75 | Thakurgaon | 80 | 20:00
| Dhamrai | 66 | 20:00 | Abul Khair 230 | 10 | 0.33333 | Palashbari | 118 | 18:30
| Rajendrapur | 108 | 19:30 | BSRM | 151 | 0.54167 | Barapukuria | 50 | 20:00
| Valuka | 114 | 10:00 | GPH Ispat | 67 | 0.77083 | Panchagar | 53 | 19:30
| Tangail | 192 | 19:30 | Goalpara | 29 | 0.95833 | Joldhaka | 32 | 19:00
| Mymensing | 216 | 18:00 | Central s/s | 87 | 20:00 | Kurigram | 56 | 18:30
| Kishorganj | 146 | 24:00 | Noapara | 64 | 18:30
| Netrokona | 105 | 1:00 | Jessore | 107 | 19:30
| Jamalpur | 134 | 22:00 | Benapol | 50 | 22:00
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-10-20 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 406 | 13:00 | 397 | 10:00 | Kaliakoir | 395 | 0.375 | 385 | 0.45833
| Bheramara | 394 | 17:00 | 387 | 18:30 | Bhulta | 373 | 0.91667 | 358 | 0.45833
| Ashuganj(N) | 380 | 3:00 | 367 | 11:00 | Gopalganj | 404 | 0.375 | 388 | 0.79167
| Payra | 414 | 22:00 | 406 | 19:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 230 | 1:00 | Comilla (N) | 230 | 18:30 | 224 | 12:00
| Ishurdi | 233 | 6:00 | 224 | 11:00 | Hathazari | 225 | 19:00 | 219 | 10:00
| Ashuganj | 233 | 5:00 | 228 | 11:00 | Megnaghat | 224 | 6:00 | 213 | 13:00
| Serajganj | 229 | 6:00 | 225 | 4:00 | Fenchuganj | 239 | 22:00 | 233 | 16:00
| Baghabari | 238 | 5:00 | 234 | 18:30 | Siddhirganj | 223 | 22:00 | 212 | 12:00
| Barapukuria | 236 | 6:00 | 228 | 20:00 | Maniknagar | 221 | 22:00 | 210 | 11:00
| Bogra | 224 | 6:00 | 216 | 19:30 | Agargaon | 216 | 8:00 | 204 | 11:00
| Rajshahi | 225 | 17:00 | 216 | 11:00 | Barisal | 247 | 18:30 | 238 | 10:00
| Khulna South | 227 | 1:00 | 219 | 12:00 | AKSML | 223 | 18:30 | 215 | 10:00
| Rampura | 221 | 22:00 | 212 | 11:00 | BSRM | 223 | 21:00 | 218 | 10:00
| Haripur | 221 | 21:00 | 211 | 11:00 | Bibiyana | 239 | 6:00 | 234 | 16:00
| Hasnabad | 220 | 19:00 | 208 | 12:00 | Bhulta | 223 | 19:00 | 213 | 17:00
| Shyampur | 218 | 22:00 | 206 | 10:00 | Ashuganj (S) | 230 | 22:00 | 224 | 11:00
| Aminbazar | 218 | 24:00 | 206 | 11:00 | Kaliakoir | 231 | 13:00 | 209 | 11:00
| Tongi | 216 | 4:00 | 205 | 11:00 | GPH | 222 | 13:00 | 217 | 6:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 134 | 1:00 | 128 | 14:00 | Hathazari | 134 | 0.77083 | 131 | 0.125
| Munsiganj | 135 | 1:00 | 128 | 9:00 | Khulshi | 132 | 0.041667 | 128 | 0.45833
| Sonargaon | 135 | 5:00 | 130 | 16:00 | Halishahar | 133 | 0.041667 | 128 | 0.5
| Shyampur | 136 | 5:00 | 128 | 12:00 | Baraulia | 132 | 0.125 | 129 | 0.41667
| Bhulta | 129 | 6:00 | 121 | 13:00 | Sikalbaha | 135 | 18:00 | 131 | 0.20833
| Madanganj | 134 | 3:00 | 129 | 13:00 | Dohazari | 131 | 1:00 | 127 | 0.45833
| Shitalakhya | 142 | 2:00 | 130 | 9:00 | Cox'sbazar | 125 | 0.70833 | 119 | 0.45833
| Rahim steal | 135 | 4:00 | 128 | 15:00 | Chandraghona | 134 | 0.79167 | 131 | 0.125
| Matuail | 134 | 1:00 | 128 | 14:00 | Kaptai | 134 | 3:00 | 132 | 0.29167
| Ghorasal | 137 | 1:00 | 134 | 7:00 | A. Khaer Stl. | 132 | 0.20833 | 128 | 12:00
| Narsinghdi | 129 | 6:00 | 122 | 22:00 | Bakulia | 133 | 0.041667 | 129 | 0.41667
| Haripur (SBU) | 134 | 2:00 | 127 | 13:00 | Julda | 136 | 0.79167 | 130 | 0.41667
| Ullon | 137 | 3:00 | 128 | 13:00 | TK Chemical | 134 | 0.70833 | 130 | 12:00
| Hasnabad | 138 | 19:30 | 129 | 11:00 | Modern Steel | 132 | 0.70833 | 129 | 0.375
| Magbazar | 138 | 6:00 | 12 | 19:30 | Shahmirpur | 135 | 0.79167 | 130 | 0.33333
| Maniknagar | 135 | 5:00 | 125 | 13:00 | Khagrachhari | 132 | 0.25 | 129 | 0.41667
| Bangabhaban | 135 | 5:00 | 125 | 13:00 | Matarbari | 128 | 0.70833 | 121 | 0.95833
| Narinda | 135 | 5:00 | 125 | 13:00 | Baroiar Hat | 132 | 0.77083 | 128 | 0.95833
| Dhanmondi | 137 | 3:00 | 128 | 13:00 | Rangamati | 133 | 0.79167 | 130 | 10:00
| Lalbag | 138 | 22:00 | 125 | 12:00 | Goalpara S/S | 139 | 14:00 | 133 | 16:00
| Madartek | 136 | 3:00 | 127 | 12:00 | Khulna Central S/S | 139 | 0.58333 | 133 | 16:00
| Dhaka University | 0 | #NUM! | 0 | #NUM! | Noapara | 134 | 13:00 | 129 | 16:00
| Fatuiiah | 135 | 0.16667 | 128 | 13:00 | Jessore | 131 | 14:00 | 122 | 18:00
| Mirpur | 133 | 6:00 | 124 | 12:00 | Benapol | 131 | 11:00 | 125 | 16:00
| Kalyanpur | 134 | 5:00 | 127 | 12:00 | Jhenida | 128 | 0.58333 | 116 | 21:00
| Gulshan | 136 | 6:00 | 127 | 12:00 | Bottail | 134 | 6:00 | 127 | 18:00
| Uttara | 133 | 6:00 | 124 | 15:00 | G.K Project | 141 | 0.25 | 137 | 18:00
| Uttara New | 134 | 5:00 | 127 | 13:00 | Faridpur | 133 | 7:00 | 124 | 22:00
| Kamrangirchar | 136 | 3:00 | 126 | 13"00 | Madaripur | 127 | 0.20833 | 128 | 22:00
| Savar | 134 | 6:00 | 124 | 15:00 | Shariyatpur S/S | 136 | 0.25 | 124 | 22:00
| Bhasantec | 137 | 5:00 | 126 | 13:00 | Gopalganj | 135 | 4:00 | 125 | 18:00
| Agargaon | 138 | 6:00 | 128 | 12:00 | Bagerhat | 134 | 13:00 | 127 | 3:00
| Satmosjid | 137 | 5:00 | 128 | 12:00 | Mongla | 130 | 0.45833 | 124 | 18:00
| Tongi | 135 | 0.041667 | 129 | 15:00 | Satkhira | 136 | 0.375 | 130 | 19:30
| Kabirpur | 133 | 5:00 | 124 | 14:00 | Gallamari | 138 | 14:00 | 133 | 18:00
| Basundhara | 137 | 4:00 | 127 | 15:00 | Magura | 127 | 7:00 | 116 | 21:00
| Manikganj | 135 | 3:00 | 128 | 12:00 | Norail | 126 | 0.33333 | 114 | 18:30
| Joydevpur | 140 | 23:00 | 130 | 4:00 | Chuadanga | 123 | 6:00 | 107 | 21:00
| New Tongi | 134 | 0.20833 | 126 | 15:00 | Barisal(N) | 140 | 5:00 | 131 | 22:00
| Kodda | 139 | 24:00 | 130 | 0.33333 | Barisal (S) | 139 | 0.041667 | 130 | 22:00
| Dhamrai | 134 | 6:00 | 124 | 9:00 | Patuakhali(S) | 135 | 0.33333 | 124 | 22:00
| Rajendrapur | 137 | 24:00 | 125 | 9:00 | Bhandaria | 130 | 9:00 | 121 | 18:30
| Valuka | 126 | 6:00 | 110 | 18:30 | Ishurdi | 137 | 5:00 | 133 | 18:00
| Tangail | 132 | 6:00 | 120 | 19:00 | Ruppur Paromanobik | 136 | 5:00 | 133 | 18:00
| Mymensing | 129 | 6:00 | 112 | 18:30 | Natore | 137 | 14:00 | 132 | 12:00
| Kishorganj | 129 | 6:00 | 116 | 18:00 | Bogra | 136 | 6:00 | 129 | 18:00
| Netrokona | 127 | 8:00 | 110 | 18:00 | Noagaon | 132 | 6:00 | 123 | 18:30
| Jamalpur | 136 | 6:00 | 125 | 18:30 | Rajshahi | 136 | 17:00 | 131 | 11:00
| Sherpur | 134 | 7:00 | 123 | 18:00 | Rajshahi New | 137 | 17:00 | 132 | 3:00
| Srimongal | 136 | 6:00 | 131 | 0.77083 | C.Nawabganj | 133 | 1:00 | 129 | 10:00
| Shahjibazar | 134 | 6:00 | 129 | 0.75 | Amnura | 135 | 17:00 | 129 | 17:00
| Fenchuganj | 135 | 6:00 | 132 | 0.041667 | Pabna | 134 | 6:00 | 130 | 18:00
| Khulawara | 135 | 5:00 | 131 | 0.77083 | Shahjadpur | 138 | 6:00 | 134 | 18:00
| Sylhet | 132 | 6:00 | 129 | 0.75 | Serajganj | 133 | 6:00 | 128 | 19:00
| Chatak | 130 | 6:00 | 126 | 18:30 | Niyamatpur | 131 | 6:00 | 120 | 21:00
| Sunamganj | 130 | 7:00 | 123 | 0.041667 | Joypurhat | 132 | 17:00 | 120 | 18:30
| Biani Bazar | 131 | 7:00 | 126 | 0.79167 | Sherpur(Bogura) | 135 | 6:00 | 129 | 18:30
| Comilla(s) | 128 | 11:00 | 119 | 18:00 | Mohastangor | 135 | 14:00 | 126 | 18:30
| Comilla(n) | 135 | 7:00 | 131 | 15:00 | Rangpur | 129 | 9:00 | 118 | 18:30
| Chandpur | 132 | 23:00 | 130 | 13:00 | Lalmonirhat | 131 | 6:00 | 118 | 18:30
| Feni | 132 | 23:00 | 127 | 24:00 | Saidpur | 130 | 4:00 | 116 | 18:30
| Chowmuhani | 134 | 7:00 | 126 | 15:00 | Purbasadipur | 130 | 6:00 | 113 | 18:.30
| Ashuganj | 135 | 8:00 | 131 | 1:00 | Thakurgaon | 127 | 6:00 | 112 | 18:00
| Daudkandi | 133 | 18:00 | 127 | 15:00 | Palashbari | 131 | 17:00 | 121 | 18:00
| B.Baria | 130 | 7:00 | 124 | 21:00 | Barapukuria | 136 | 5:00 | 127 | 18:30
| Ramganj | 130 | 8:00 | 122 | 23:00 | Panchagar | 124 | 6:00 | 109 | 18:00
| Chaddagram | 134 | 19:00 | 128 | 1:00 | Joldhaka | 131 | 6:00 | 114 | 18:30
| PHP | 132 | 19:00 | 127 | 23:00 | Kurigram | 131 | 6:00 | 114 | 18:30
| Madanhat | 135 | 17:00 | 131 | 12:00

## L-Curve
Date | 2020-10-20
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 116 | 7929 | 3935 | 11864 |  |  |  | QF-LDC-11
0:30 | 131 | 7877 | 3833.5 | 11710.5 | Date: | 2020-10-20
1:00 | 146 | 7825 | 3732 | 11557
1:30 | 99.5 | 7755 | 3589.5 | 11344.5
2:00 | 53 | 7685 | 3447 | 11132
2:30 | 41.5 | 7655 | 3374 | 11029 | [5 empty] | Gen. at Eve. Peak | 12538 | 9500 MW (19:30 )
3:00 | 30 | 7625 | 3301 | 10926 | [6 empty] | 19:00
3:30 | 49 | 7444.5 | 3265 | 10709.5 | [5 empty] | Gen. at Day Peak | 10568 | 7952.5 MW (12:00 )
4:00 | 68 | 7264 | 3229 | 10493 | [6 empty] | 12:00
4:30 | 81 | 7147.5 | 3218 | 10365.5 | [5 empty] | Highest Generation | 12538
5:00 | 94 | 7031 | 3207 | 10238 | [6 empty] | 19:00
5:30 | 154 | 6839 | 3064 | 9903
6:00 | 214 | 6647 | 2921 | 9568
6:30 | 187 | 6441.5 | 2830 | 9271.5
7:00 | 160 | 6236 | 2739 | 8975
7:30 | 207 | 6215.5 | 2808 | 9023.5
8:00 | 254 | 6195 | 2877 | 9072
8:30 | 292 | 6287 | 2912 | 9199
9:00 | 330 | 6379 | 2947 | 9326
9:30 | 359 | 6646 | 2949.5 | 9595.5
10:00 | 388 | 6913 | 2952 | 9865
10:30 | 396.5 | 7097.5 | 2998.5 | 10096
11:00 | 405 | 7282 | 3045 | 10327
11:30 | 375 | 7351.5 | 3096 | 10447.5
12:00 | 345 | 7421 | 3147 | 10568
12:30 | 325.5 | 7417 | 3218 | 10635
13:00 | 306 | 7413 | 3289 | 10702
13:30 | 240 | 7404 | 3340 | 10744
14:00 | 174 | 7395 | 3391 | 10786
14:30 | 274 | 7494 | 3329 | 10823
15:00 | 374 | 7593 | 3267 | 10860
15:30 | 390 | 7489.5 | 3147.5 | 10637
16:00 | 406 | 7386 | 3028 | 10414
16:30 | 419 | 7201.5 | 3029 | 10230.5
17:00 | 432 | 7017 | 3030 | 10047
17:30 | 301 | 7539 | 3404.5 | 10943.5
18:00 | 170 | 8061 | 3779 | 11840
18:30 | 127 | 8202 | 3987 | 12189
19:00 | 84 | 8343 | 4195 | 12538
19:30 | 66 | 8240 | 4224 | 12464
20:00 | 40 | 8238 | 4219 | 12457 |  |  |  | Executive Engineer
20:30 | 42 | 8239 | 4202 | 12441 |  |  |  | Network Operation Division
21:00 | 44 | 8240 | 4185 | 12425
21:30 | 43 | 8190 | 4149.5 | 12339.5
22:00 | 42 | 8140 | 4114 | 12254 |  |  |  |  | Page 6 of 7
22:30 | 93 | 8030 | 4117 | 12147
23:00 | 144 | 7920 | 4120 | 12040
23:30 | 130 | 7924.5 | 4027.5 | 11952
24:00 | 116 | 7929 | 3935 | 11864
9500 MW (19:30 )
7952.5 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-10-20 |  | Energy | 263322463
[10 empty] | 2020-10-20 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3827 | 919 | 1927 | 3522 | 710 | 122 | 776 | 0 | 144
0:30 | 3908 | 919 | 1942 | 3412 | 695 | 122.5 | 612.5 | 0 | 141 | Date: | 2020-10-20
1:00 | 3989 | 919 | 1957 | 3302 | 680 | 123 | 449 | 0 | 138
1:30 | 3937 | 919.5 | 1963 | 3210.5 | 690 | 122 | 365.5 | 0 | 137 | [7 empty] | Total Energy | 263.3225 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 3885 | 920 | 1969 | 3119 | 700 | 121 | 282 | 0 | 136 | [7 empty] | Energy not Served | 0
2:30 | 3871.5 | 919.5 | 1986.5 | 3047.5 | 700 | 120 | 250 | 0 | 134 | [7 empty] | Energy Requirement | 263.3225
3:00 | 3858 | 919 | 2004 | 2976 | 700 | 119 | 218 | 0 | 132
3:30 | 3882 | 919 | 2012.5 | 2770.5 | 675 | 118 | 201.5 | 0 | 131 | [6 empty] | Shortage
4:00 | 3906 | 919 | 2021 | 2565 | 650 | 117 | 185 | 0 | 130
4:30 | 3886.5 | 919 | 2007 | 2476 | 650 | 116 | 185 | 0 | 126
5:00 | 3867 | 919 | 1993 | 2387 | 650 | 115 | 185 | 0 | 122
5:30 | 3861.5 | 919 | 1925.5 | 2151 | 650 | 115 | 161 | 0 | 120
6:00 | 3856 | 919 | 1858 | 1915 | 650 | 115 | 137 | 0 | 118
6:30 | 3836.5 | 919.5 | 1844 | 1712 | 600 | 115.5 | 128.5 | 0 | 112 |  |  |  |  | Coal
7:00 | 3817 | 920 | 1830 | 1509 | 550 | 116 | 120 | 0 | 106
7:30 | 3812 | 919.5 | 1831.5 | 1504 | 600 | 117.5 | 120 | 0 | 108 |  |  |  | Oil |  |  |  | ,
8:00 | 3807 | 919 | 1833 | 1499 | 650 | 119 | 120 | 0 | 110
8:30 | 3863 | 919.5 | 1830 | 1594.5 | 650 | 120 | 125 | 0 | 78
9:00 | 3919 | 920 | 1827 | 1690 | 650 | 121 | 130 | 0 | 46
9:30 | 3914.5 | 919.5 | 1820 | 1958.5 | 639.5 | 121 | 149 | 0 | 47
10:00 | 3910 | 919 | 1813 | 2227 | 629 | 121 | 168 | 0 | 48
10:30 | 3947 | 918.5 | 1812.5 | 2420.5 | 629.5 | 121 | 168 | 0 | 48
11:00 | 3984 | 918 | 1812 | 2614 | 630 | 121 | 168 | 0 | 48
11:30 | 4032.5 | 918.5 | 1824.5 | 2659.5 | 634.5 | 122 | 176 | 0 | 48
12:00 | 4081 | 919 | 1837 | 2705 | 639 | 123 | 184 | 0 | 48
12:30 | 4027.5 | 919 | 1812 | 2809 | 644.5 | 123 | 218.5 | 0 | 51
13:00 | 3974 | 919 | 1787 | 2913 | 650 | 123 | 253 | 0 | 54
13:30 | 3974 | 919 | 1787 | 2913 | 650 | 123 | 253 | 0 | 54
14:00 | 3974 | 919 | 1787 | 2913 | 650 | 123 | 253 | 0 | 54
14:30 | 3979 | 919 | 1784.5 | 2926.5 | 635.5 | 123 | 335.5 | 0 | 55
15:00 | 3984 | 919 | 1782 | 2940 | 621 | 123 | 418 | 0 | 56
15:30 | 3874 | 919 | 1780.5 | 2868.5 | 595.5 | 122.5 | 412 | 0 | 51
16:00 | 3764 | 919 | 1779 | 2797 | 570 | 122 | 406 | 0 | 46
16:30 | 3689.5 | 919 | 1718.5 | 2751.5 | 570 | 120 | 412.5 | 0 | 43
17:00 | 3615 | 919 | 1658 | 2706 | 570 | 118 | 419 | 0 | 40
17:30 | 3747.5 | 919 | 1748.5 | 3156.5 | 580 | 118 | 586 | 0 | 87
18:00 | 3880 | 919 | 1839 | 3607 | 590 | 118 | 753 | 0 | 134
18:30 | 3937.5 | 919.5 | 1860.5 | 3807.5 | 640 | 118 | 769 | 0 | 137
19:00 | 3995 | 920 | 1882 | 4008 | 690 | 118 | 785 | 0 | 140
19:30 | 3970 | 918 | 1903 | 3929 | 700 | 118 | 786 | 0 | 140
20:00 | 3955 | 919 | 1895 | 3939 | 700 | 120 | 793 | 0 | 136
20:30 | 3953 | 919 | 1908 | 3910 | 705 | 120.5 | 788.5 | 0 | 137
21:00 | 3951 | 919 | 1921 | 3881 | 710 | 121 | 784 | 0 | 138
21:30 | 3949.5 | 918.5 | 1890 | 3828.5 | 710 | 121 | 785 | 0 | 137
22:00 | 3948 | 918 | 1859 | 3776 | 710 | 121 | 786 | 0 | 136
22:30 | 3927 | 918.5 | 1900 | 3649 | 710 | 121.5 | 786 | 0 | 135
23:00 | 3906 | 919 | 1941 | 3522 | 710 | 122 | 786 | 0 | 134
23:30 | 3866.5 | 919 | 1934 | 3522 | 710 | 122 | 781 | 0 | 139 | Max Temp. in Dhaka |  | 34.2° C
24:00 | 3827 | 919 | 1927 | 3522 | 710 | 122 | 776 | 0 | 144
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
Note on W13: Author:

## Generation
g | 2020-10-20
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 88 | 86 | 84 | 82 | 80 | 80 | 81 | 84 | 86 | 86 | 86 | 88 | 88 | 88 | 88 | 87 | 83 | 83 |  | 83 | 83 | 85 | 86 | 86 | 87 | 87 | 2005015
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 840000
3 | Chattogram TPP-1 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2700000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [12 empty] | 3 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 306221
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 5 | 10 | 15 | 19 | 20 | 20 | 19 | 16 | 12 | 7 | 1 | [9 empty] | 142965
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 204 | 204 | 210 | 204 | 204 | 204 | 204 | 204 | 231 | 204 | 205 | 204 | 204 | 205 | 205 | 204 | 204 |  | 204 | 204 | 204 | 204 | 204 | 213 | 204 | 4920397
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 140 | 105 | 104 | 104 | 104 | 104 | 104 | 104 | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 70 | 139 |  | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 3054440
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 102 | 68 | 34 | 17 | 17 | 17 | [7 empty] | 51 | 49 | 51 | 51 | 102 |  | 102 | 102 | 100 | 100 | 102 | 102 | 102 | 1181440
12 | Hathazari 100 MW peaking PP | [15 empty] | 8 | 8 | 17 | [8 empty] | 35621
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [17 empty] | 70 |  | 70 | 70 | 70 | 70 | 70 |  |  | 313536
14 | Titas 50 MW Peaking PP | [14 empty] | 13 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 333672
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 145 | 115 | 90 | 90 | 90 | 85 | 70 | 70 | 145 | 158 | 150 | 151 | 175 | 68 | 150 | 195 | 70 | 150 |  | 175 | 180 | 180 | 180 | 180 | 140 | 97 | 3442000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 300 | 300 | 300 | 200 | 95 | 45 | 45 | 45 | 45 | 140 | 210 | 225 | 250 | 285 | 300 | 286 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 5743307
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 100 | 100 | 100 | 101 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2408000
23 | Ghorasal TPP Unit-5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2740500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4796764
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1790995
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 26 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 26 | 16 | 22 | 26 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 335376
33 | Ashuganj 225 MW CCPP | 179 | 186 | 189 | 187 | 185 | 184 | 185 | 181 | 188 | 209 | 214 | 189 | 180 | 192 | 195 | 186 | 180 | 213 |  | 205 | 203 | 200 | 211 | 213 | 214 | 209 | 4704000
34 | Ashuganj 450 MW CCPP(South) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 260 | 260 | 260 | 260 | 280 | 260 | 260 | 260 | 260 | 260 | 260 |  | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 6518000
| Ashuganj 450 MW CCPP(North) | 290 | 295 | 290 | 310 | 290 | 290 | 295 | 288 | 290 | 290 | 290 | 320 | 275 | 275 | 280 | 275 | 275 | 295 |  | 295 | 295 | 295 | 295 | 295 | 310 | 295 | 7460400
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 143040
36 | Chandpur 150 MW CCPP | 72 | 75 | 75 | 78 | 80 | 80 | 82 | 83 | 85 | 80 | 85 | 82 | 75 | 76 | 81 | 81 | 78 | 81 |  | 81 | 82 | 80 | 82 | 75 | 75 | 75 | 1861210
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 360 | 360 | 390 | 390 | 390 | 360 | 360 | 360 | 360 | 360 | 360 | 340 | 330 | 330 | 330 | 330 | 330 | 340 |  | 340 | 340 | 340 | 340 | 340 | 350 | 350 | 7370050
41 | Haripur 360MW CCPP(HPL) | 319 | 333 | 353 | 351 | 353 | 322 | 303 | 303 | 302 | 304 | 303 | 303 | 282 | 292 | 304 | 292 | 292 | 312 |  | 292 | 282 | 282 | 283 | 293 | 304 | 327 | 7367000
42 | RPCL 210MW CCPP | 157 | 157 | 156 | 155 | 157 | 158 | 157 | 156 | 140 | 120 | 120 | 104 | 101 | 98 | 98 | 100 | 100 | 100 |  | 101 | 100 | 101 | 101 | 120 | 120 | 120 | 2903680
43
44 | Fenchugonj CCPP Phase-1 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 83 | 86 | 83 | 83 | 82 | 70 | 70 | 70 | 72 | 71 | 71 |  | 71 | 71 | 71 | 71 | 71 | 71 | 72 | 1861000
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1023720
46 | Shajibazar 330 MW CCPP | 159 | 157 | 157 | 157 | 156 | 160 | 160 | 160 | 158 | 159 | 158 | 158 | 160 | 158 | 160 | 158 | 160 | 158 |  | 158 | 160 | 160 | 158 | 158 | 158 | 160 | 3448000
47 | Shahjibazar GTPP Unit- 8 & 9 | 64 | 64 | 64 | 64 | 64 | 65 | 64 | 64 | 64 | 63 | 63 | 60 | 61 | 51 | 63 | 62 | 40 | 65 |  | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 1488480
48 | Shahjibazar 86MW PP (Shahjibazar) | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 84 | 84 | 84 | 87 | 87 | 84 | 84 | 84 | 84 | 40 | 87 |  | 87 | 87 | 86 | 86 | 86 | 86 | 86 | 2020800
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 100 | 20 | 20 | 20 | 20 | 70 | 90 | 135 | 163 | 164 |  | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 3042810
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 415000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 246780
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 219000
55 | Fenchugonj 51 MW PP (Barakatullah) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 11 | 19 | 19 | 19 | 22 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 567000
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 485568
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 295 | 295 | 300 | 295 | 280 | 280 | 300 | 290 | 290 | 295 | 300 | 300 | 270 | 300 | 280 | 285 | 270 |  | 300 | 300 | 280 | 300 | 285 | 285 | 305 | 7200200
| Bibiyana South 400 MW | [8 empty] | 50 | 80 | 180 | 264 | 242 | 100 | 269 | [11 empty] | 1236300
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 17 | 35 | 35 | 36 | 36 | 36 | 36 | 36 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1095319
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 462432
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 |  |  | 19 | 19 | 19 | 19 | 392436
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 17 | 17 |  | 17 | 17 | 20 | 20 | 20 | 20 | 20 | 388584
63 | Impoprt (Tripura) | 138 | 136 | 132 | 130 | 122 | 118 | 106 | 110 | 46 | 48 | 48 | 48 | 54 | 56 | 56 | 46 | 40 | 134 |  | 140 | 140 | 136 | 138 | 136 | 134 | 144 | 2467200
64 | Malancha, Ctg. EPZ (United) | 38 | 40 | 40 | 42 | 42 | 42 | 34 | 8 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 4 | 4 |  | 8 | 11 | 15 | 21 | 21 | 25 | 30 | 456480
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 18 | 16 | 19 | 19 | 16 | 16 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 13 | 13 | 429516
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 249840
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 817600
68 | Cumilla 25 MW PP (Summit) | 22 | 22 | 22 | 22 | 22 | 22 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 22 | 22 | 22 | 22 | 22 | 466080
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 21 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 689580
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 719200
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 823300
73 | Ghorashal 108MW PP (Regent) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 71 | 71 | 71 | 72 | 72 | 72 | 72 | 72 | 72 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 1704090
| Feni Lanka Power | 17 | 17 | 17 | [5 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 |  | 100 | 84 | 100 | 17 | 17 | 17 | 17 | 469680
| Chowmuhani 113 MW | 56 | 71 | 96 | 94 | 103 | 104 | 105 | 103 | 98 | 102 | 104 | 103 | 102 | 100 | 100 | 97 | 65 | 77 |  | 108 | 113 | 113 | 113 | 113 | 113 | 112 | 2375520
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 60 | 100 | 99 | 97 | 97 | 98 | 98 | 98 | 98 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2289600
78 | Gazipur 52 MW PP | [12 empty] | 3 | 36 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 548472
79 | Kodda 150MW PP | 133 | 84 | 64 | 48 | 48 |  |  |  | 10 | 48 | 48 | 64 | 133 | 150 | 150 | 100 | 82 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 2227200
80 | Jamalpur 95 MW PP(Powerpac) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 36 | 40 | 40 | 40 | 40 | 40 | 889920
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | [6 empty] | 15 | 43 | 43 | 43 | 43 | 34 | 34 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 36 | 35 | 741480
| Gazipur 100 MW PP | 85 | 85 | 85 | 85 | 85 | 85 | 17 | 50 | 60 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 |  | 86 | 86 | 86 | 86 | 86 | 86 | 85 | 1919928
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 3 | 5 | 5 | 5 | 4 | 2 | 1 | 1 | [10 empty] | 27720
| Jodiac Power | 36 | 36 | 36 | 36 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 21 | 39 | 50 | 43 |  | 54 | 54 | 54 | 54 | 54 | 54 | 37 | 794687
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | 97 | 97 | 97 | 97 | 97 | 95 | 48 | 48 | 48 | 80 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 97 |  | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 2178552
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [9 empty] | 12 | 24 | 26 | 24 | 23 | 26 | 34 | 23 | 24 |  | 24 | 24 | 40 | 88 | 87 | 22 | 32 | 540766
86 | Meghnaghat CCPP(Summit) | 260 | 275 | 255 | 280 | 280 | 255 | 280 | 270 | 260 | 265 | 275 | 275 | 265 | 258 | 290 | 280 | 270 | 270 |  | 268 | 285 | 260 | 260 | 270 | 270 | 295 | 6535680
87 | Meghnaghat 100 MW(IEL) | 100 | 100 | 100 | 100 | 100 | 96 | 58 | 50 | 69 | 100 | 100 | 100 | 100 | 75 | 18 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 1446720
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 104 | 104 | 104 | 72 | 53 | 77 | 104 | 104 | 104 | 104 | 104 | 63 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 54 | 1967040
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [12 empty] | 10 | 22 | 30 | 20 | 20 | 100 |  | 100 | 100 | 100 | 100 | 90 | 90 | 90 | 717240
92 | Fenchuganj 44MW (Energyprima) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 43 | 43 | 46 | 46 | 44 | 20 | 35 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1088640
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 35 | 35 | 51 | 51 |  | 48 | 51 | 51 |  | 51 | 51 | 51 | 51 | 43 | 51 | 51 | 1147653
94 | Gagnagar 102 MW PP (Digital Power) | 94 | 94 | 74 | 74 | 74 | 24 | 8 | 8 | 8 | 54 | 85 | 85 | 93 | 93 | 93 | 50 | 40 | 45 |  | 20 | 18 | 20 | 22 | 24 | 16 | 16 | 1211472
95 | Patenga 50MW PP (Baraka) | 50 | 20 | [6 empty] | 5 | 18 | 19 | 19 | 26 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 719040
96 | Chattogram 108 MW PP (ECPV) | 97 | 97 | 97 | 46 |  |  |  |  | 3 | 13 | 55 | 77 | 84 | 86 | 90 | 90 | 94 | 90 |  | 91 | 56 | 35 | 11 | 6 | 6 | 6 | 1178880
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 40 | 40 | 15 | 15 | 15 | 15 | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1123736
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1214372
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2645836
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 2 | 2 | 2 | 2 | 1 | 2 | 1 | 1 | 0 | [9 empty] | 14400
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 17 | [5 empty] | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 982800
104 | Keranigonj 300 MW PP (APR) | [17 empty] | 109 |  | 108 | 33 | 33 | 33 | 32 |  | 0 | 296188
105 | Bramhangoan 100 MW PP (Aggreko) | [17 empty] | 25 |  | 25 | 30 | 50 | 50 |  |  | 0 | 193155
106 | Mymensingh 200 MW PP (United) | 191 | 191 | 191 | 191 | 191 | 200 | 160 | 160 | 160 | 178 | 190 | 190 | 180 | 180 | 180 | 187 | 150 | 163 |  | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 4351200
112 | Aurahati 100MW PP (Aggreko) | [17 empty] | 53 |  | 52 | 52 | 52 | 51 |  |  | 0 | 243874
114 | Kodda 149 MW PP Unit-1 (Summit) | 144 | 140 | 149 | 149 | 149 | 144 | 141 | 134 | 149 | 149 | 149 | 149 | 149 | 142 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3569900
115 | Juldah 100 MW PP Unit-3 (Acorn) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 539520
116 | Chandpur 200MW (Desh energy) | [12 empty] | 5 | 20 | 51 | 51 | 51 | 85 |  | 149 | 163 | 163 | 163 | 163 | 120 | 120 | 1210560
117 | Ashuganj 150MW PP (Midland) | 142 | 138 | 143 | 142 | 142 | 90 | 50 | 50 | 76 | 135 | 140 | 140 | 140 | 140 | 46 | 103 | 142 | 142 |  | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 3041018
118 | Bibiyana-III 400 MW CCPP | 420 | 420 | 420 | 421 | 425 | 425 | 421 | 422 | 422 | 417 | 416 | 413 | 412 | 419 | 414 | 412 | 417 | 417 |  | 419 | 419 | 420 | 420 | 425 | 419 | 423 | 10048000
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 35 | 35 |  |  |  |  | 14 | 35 | 35 | 65 | 85 | 85 | 65 | 45 | 73 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 1699200
| Anwara 300 MW PP (United) | 160 | 160 | 160 | 124 | 124 | 124 | 124 | 124 | 124 | 141 | 142 | 142 | 142 | 142 | 142 | 142 | 105 | 159 |  | 160 | 161 | 161 | 161 | 161 | 161 | 161 | 3457527
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 90 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2381760
120 | Eastern Zone Total | 7825 | 7685 | 7625 | 7264 | 7031 | 6647 | 6236 | 6195 | 6379 | 6913 | 7282 | 7421 | 7413 | 7395 | 7593 | 7386 | 7017 | 8061 |  | 8343 | 8240 | 8238 | 8240 | 8140 | 7920 | 7929 | 178663607
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 115 | 66 | 38 | [6 empty] | 3 | 16 | 16 | 83 | 83 | 49 | 16 | 16 | 85 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 1298880
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 3 | 7 |  | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 117120
| Khulna 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 180 |  | 220 | 220 | 220 | 220 | 220 | 220 | 210 | 3580800
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 105 | 105 | 105 | 17 | 17 | 17 | 17 | 30 | 53 | 70 | 70 | 90 | 90 | 53 | 53 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1789920
130
131
132
133
| Barisal 110 MW PP (Summit ) | 110 | 80 | 64 | 48 | 48 | 16 | [9 empty] | 16 | 16 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 1212000
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 96 | 97 | 97 | 97 | 96 | 96 | 95 | 95 | 96 | 95 | 95 | 93 | 93 | 93 | 93 | 65 | 52 | 90 |  | 93 | 92 | 96 | 97 | 97 | 97 | 96 | 2221642
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 38 | 38 | 38 | 33 | 34 | 31 | 28 | 23 | 17 | 19 | 19 | 14 | 15 | 19 | 24 | 21 | 21 | 35 |  | 38 | 38 | 39 | 39 | 39 | 39 | 38 | 684202
141 | Noapara 100 MW PP (Bangla Trac) | [17 empty] | 32 |  | 100 | 100 | 100 | 100 | 100 | 100 | 0 | 625920
142 | Noapara 40 MW PP (Khanjahan Ali) | [12 empty] | 8 | 8 | 8 | 8 | 8 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 300750
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [19 empty] | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 105696
146 | Bheramara HVDC | 919 | 920 | 919 | 919 | 919 | 919 | 920 | 919 | 920 | 919 | 918 | 919 | 919 | 919 | 919 | 919 | 919 | 919 |  | 920 | 918 | 919 | 919 | 918 | 919 | 919 | 22069818
147 | Bheramara 410 MW CCPP | 290 | 295 | 305 | 310 | 315 | 290 | 290 | 300 | 300 | 300 | 300 | 320 | 300 | 340 | 300 | 250 | 250 | 310 |  | 305 | 295 | 280 | 265 | 255 | 245 | 240 | 7246368
148 | Payra 1320 MW | 530 | 550 | 550 | 500 | 500 | 500 | 400 | 500 | 500 | 480 | 480 | 490 | 500 | 500 | 470 | 420 | 420 | 440 |  | 540 | 550 | 550 | 560 | 560 | 560 | 560 | 13190300
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 150 | 149 | 150 | 150 | 151 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3665800
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [13 empty] | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 544240
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 184 | 152 | 146 | 153 | 152 | 151 | 148 | 158 | 157 | 169 | 165 | 153 | 159 | 145 | 130 | 137 | 150 | 142 |  | 178 | 180 | 176 | 168 | 162 | 162 | 158 | 3984491
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 179 | 158 | 156 | 164 | 163 | 161 | 159 | 162 | 161 | 164 | 162 | 157 | 188 | 130 | 130 | 144 | 160 | 153 |  | 181 | 178 | 175 | 164 | 158 | 153 | 148 | 4118945
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 359 | 359 | 344 | 361 | 336 | 280 | 283 | 300 | 316 | 308 | 308 | 360 | 340 | 295 | 344 | 357 | 305 | 375 |  | 369 | 395 | 398 | 396 | 347 | 396 | 336 | 8320145
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 10 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 289592
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 |  |  | 18 | 21 | 22 | 22 | 22 | 22 | 22 | 486000
163 | Bogura 20 MW PP (Energyprima) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 235728
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 9 | 9 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 242730
165 | Amnura 50 MW PP(Sinha) | 20 | 20 | 20 | 20 | 20 | 20 | [5 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 383130
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [13 empty] | 26 | 36 | 36 | 36 | 36 |  | 36 | 36 | 45 | 36 | 36 | 36 | 36 | 369478
168 | Santahar 50 MW Peaking PP | [17 empty] | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 224480
169 | Natore 52 MW PP (Rajlanka) | 52 | [11 empty] | 17 | 52 | 25 | 25 | 25 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 542400
170 | Chapainawabganj 100 MW Peaking PP | 94 | 10 | [14 empty] | 18 | 96 |  | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 795720
171 | Baghabari 200 MW PP (Paramount) | [17 empty] | 30 |  | 30 | 30 | 30 | 30 | 30 |  | 0 | 149061
| Bagura 113 MW PP (Confidence)-2 | 113 | 70 | [7 empty] | 2 | 35 | 35 | 73 | 113 | 70 | 35 | 35 | 50 |  | 110 | 113 | 113 | 113 | 113 | 113 | 113 | 1465056
172 | Confidence Power Bogura Unit-1 113 MW | 109 | 109 | 109 | 109 | 109 | 50 | 50 | 50 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 70 | 70 | 100 |  | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 2380992
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 106 | 105 | 97 | 97 | 97 | 80 | 38 | 41 | 41 | 40 | 69 | 75 | 78 | 83 | 84 | 72 | 80 | 92 |  | 99 | 99 | 97 | 97 | 98 | 99 | 100 | 1980480
177 | Sympa Solar Power 8MW | [6 empty] | 1 | 2 | 3 | 4 | 5 | 5 | 5 | 4 | 3 | 2 | 1 | [9 empty] | 36972
178
178