## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-10-23 | Friday
|  |  | Date (day): | 2020-10-23 |  | Friday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13290.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14449 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-10-22 | 2020-10-23 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 115 | 115 | 115 | 75 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 200 | 200 | 165 |  | Gas shortage
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 71 | 72 | 72 | 72 | 36 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under S/D for dust in gas.
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 354 | 358 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 350 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 7 | 16 | 16
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 300 | 280 | 305 | 305
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 64 | 92 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 40 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 50 | 92 |  | 8 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 10 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 150 | 120 | 115 | 165 |  |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 7 | 7 | 7 |  |  | Fuel shortage.
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 8 | 16 | 16 |  |  | Fuel shortage.
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 78 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 42 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Engine problem
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 56 | 56 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 100 | 300 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 108 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 38 | 85 | 86 |  | 19 | Engine problem
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 17 | 17 | 17 | 87 |  | Fuel shortage
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 2276 | 2627 | 3231 | 3614 | 705 | 1189
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 115 | 115 | 115 | 115 | 65 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 0 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 11 | 48 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 122 | 121 | 120 | 120 | 110 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 217 | 203 | 221 | 221
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 142 | 139 | 145 | 145
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 8 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 102 | 102
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 22 | 22 | 22 | 22
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 21 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 23 | 10 | 20
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 97 | 97 |  | 11 | Engine problem
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 0 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 70 | 122 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 54 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 849 | 1001 | 1717 | 1702 | 355 | 109
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 70 | 70 | 80 | 80 | 49 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 |  | 134 | Under maint
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 170 | 219 | 225 | 225 |  |  | FGMO
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 260 | 360 | 360 |  |  | FGMO
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 250 | 350 | 350 |  |  | FGMO
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 5 | 5 | 5 | 40 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 10 | 143 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 25 | 50
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 90 | 90 | 90 |  | 57 | ST under shut down
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 200 | 200
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 20 | 22 | 22
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 0 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 106 | 102 | 165 | 173
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 16 | 0 | 33 | 33
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 25 | 52
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 20 | 22 | 22
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 0 | 17 | 17 | 97 |  | Engine problem & Fuel shortage
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 80 | 113 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1303 | 1356 | 1957 | 2217 | 558 | 191
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 121 | 104 | 160 | 160 | 42 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 24 | 24 | 48 | 48 |  | 47 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 100 | 200 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 55 | 115 | 115
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 266 | 403 | 544.6 | 543 | 42 | 47
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 58 | 73 | 85 | 85
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 43 | 43 | 43 | 43 |  | 47 | Unit-4 under shut down
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 |  | 54 | STG under maint.
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 158 | 158 | 160 | 160 |  | 170 | GT-2 S/D due to gas shortage.
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 14 | 45 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 46 | 50 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 5 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 40 | 65 | 65 |  |  | FGMO
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 20 | 87 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 140 | 140 | 151 | 200
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 20
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 16 | 25 | 25
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 275 | 341 | 341 |  |  | FGMO
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 419 | 0 | 400 | 400
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 185 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1596 | 1070 | 1600 | 1651 | 0 | 271
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 920 | 909 | 700 | 909
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 83 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 120 | 220 | 220
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 340 | 330 | 360 | 360
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 35 | 105 | 105
| 108 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1380 | 1477 | 1690 | 2055 | 0 | 0
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 48 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 13 | 16 | 33 | 33
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 43 | 75 | 95 | 95
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 350 | 470 | 500 | 500
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 406 | 609 | 738 | 738 | 0 | 194
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 20 | 20 | 20 | 20 | 30 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 130 | 167 | 225 | 225 |  |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 130 | 153 | 220 | 220 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 391 | 414 | 414 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 30
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 22 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 10 | 10 | 10 | 10
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 25 | 52 | 52
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 95 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 70 | 113 | 113
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 100 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 767 | 1064 | 1550 | 1670 | 461 | 0
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 36 | 79 | 105 | 109
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 191 | 229 | 263 | 259 | 294 | 40
|  | Total |  |  |  |  | 20383 | 19892 | 9034 | 9836 | 13290.6 | 14449 | 2415 | 2041
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8591.3009 | 9354 | 12639.312 | 13740.9461
| A. |  | 2020-10-22 | (Yesterday) |  |  |  |  | Thursday
| 1 | Highest Generation : |  |  | 10604 | MW at | 1:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 8238 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9836 | MW
| 3 | Day peak Generation : |  |  | 9034 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9354 | MW
| 4 | Evening peak Generation : |  |  | 9836 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 219.0754 | MKWHr | By Solar | 0.056997 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 131.3667 | MKWHr |  | By Oil: | 45.0328 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 15.0972 | MKWHr |  | By Hydro: | 2.9055 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2415 | MW | Dhaka | 3647 | 3647 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2041 | MW | Chittagong | 879 | 879 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4456 | MW | Khulna | 1135 | 1135 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1110.58 | MMCFD |  |  | Rajshahi | 1018 | 1018 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 152422813.274 | ii) Oil : | Taka | 324764862.5 | Comilla | 670 | 670 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 70080086 | Total | Taka | 547267761.774 | Mymensingh | 740 | 740 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.004 | MKWHr. | Sylhet | 381 | 381 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 140 | MW (E to W) at | 19:00 | hrs | Barisal | 181 | 181 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 18 | MW at | 2:00 | hrs | Rangpur | 703 | 703 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 27.7° C |  |  | Total | 9354 | 9354 |  | 0
| B. |  | 2020-10-23 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 31.2° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 8800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14449 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 6500 | MW
| 4 | Reserve(Generation end) |  |  |  | 5649 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 181.8053 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6388 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.0204 | MKWHr. | ii) HVDC Flow at Peak Time |  | 909 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.5958 | MKWHr. | iii) Maximum HVDC Flow : |  | 921 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 102.05 |  | (b) Today: | 102.36 |  | (c) Rule Curve: |  | 108
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-10-22
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 101 | 115 | 200 | 72 | 0 | 0 | 357 |  | 0 | 450 | 235 | 16 | 97 | 55 | 0 | 0 | 150 | 0 | 7 | 16 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 31 | 33 | 33 | 0 | 0 | 88 | 35 | 115 | 0 | 8 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 20 | 6 | 50 | 20 | 42 | 0 | 70 | 0 | 260 | 250 | 195 | 8 | 90 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 8 | 8 | 21 | 130 | 125 | 25 | 20 | 0 | 73 | 43 | 22 | 50 | 110 | 158 | 56 | 84 | 0 | 218 | 18 | 0 | 10 | 270 | 24 | 11 | 0 | 300 | 0 | 0 | 190 | 0 | 140 | 0 | 22 | 0 | 148 | 430 | 115 | 34 | 0 | 0 | 161 | 36 | 0 | 17 | 113 | 100 | 0 | 17 |  | 919 | 0 | 225 | 0 | 115 | 165 | 0 | 0 | 16 | 0 | 40 | 0 | 28 | 64 | 0 | 0 | 0 | 0 | 0 | 46 | 20 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 139 | 0 | 95 | 0 | 130 | 0 | 326 | 35 | 0 | 113 | 0 | 84 | 0 | 0 | 109 | 520 |  | 7221 | 3383 | 10604 | 3794 | 919 | 2012 | 2680 | 671 | 123 | 275 | 130 | 0 | 0 | 102.05
2:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 357 |  | 0 | 450 | 265 | 16 | 97 | 55 | 0 | 0 | 160 | 0 | 7 | 16 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 55 | 19 | 25 | 31 | 33 | 33 | 0 | 0 | 88 | 35 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 6 | 0 | 20 | 42 | 0 | 70 | 0 | 260 | 250 | 201 | 8 | 82 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 8 | 8 | 21 | 126 | 143 | 25 | 20 | 0 | 73 | 43 | 22 | 50 | 110 | 158 | 56 | 84 | 0 | 218 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 250 | 0 | 0 | 190 | 0 | 149 | 0 | 22 | 0 | 150 | 428 | 115 | 0 | 0 | 0 | 161 | 36 | 0 | 17 | 107 | 100 | 0 | 17 |  | 920 | 0 | 240 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 139 | 0 | 95 | 0 | 130 | 0 | 347 | 35 | 0 | 35 | 0 | 72 | 0 | 0 | 109 | 520 |  | 7016 | 3096 | 10112 | 3832 | 920 | 2038 | 2267 | 670 | 123 | 136 | 126 | 0 | 0 | 102.05
3:00 | 0 | 0 | 99 | 115 | 200 | 72 | 0 | 0 | 357 |  | 0 | 450 | 270 | 16 | 97 | 55 | 0 | 0 | 160 | 0 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 19 | 25 | 31 | 33 | 33 | 0 | 0 | 88 | 35 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 6 | 0 | 20 | 42 | 0 | 70 | 0 | 260 | 250 | 206 | 8 | 90 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 8 | 8 | 21 | 122 | 156 | 25 | 20 | 0 | 73 | 43 | 22 | 50 | 110 | 160 | 56 | 84 | 0 | 218 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 145 | 0 | 0 | 190 | 0 | 140 | 0 | 22 | 0 | 150 | 428 | 85 | 0 | 0 | 0 | 161 | 36 | 0 | 17 | 107 | 100 | 0 | 17 |  | 920 | 0 | 250 | 0 | 28 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 139 | 0 | 95 | 0 | 150 | 0 | 358 | 35 | 0 | 0 | 0 | 72 | 0 | 0 | 109 | 500 |  | 6867 | 3022 | 9889 | 3889 | 920 | 2043 | 2022 | 650 | 123 | 120 | 122 | 0 | 0 | 102.05
4:00 | 0 | 0 | 102 | 115 | 200 | 72 | 0 | 0 | 357 |  | 0 | 450 | 270 | 16 | 97 | 30 | 0 | 0 | 160 | 0 | 7 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 19 | 25 | 31 | 33 | 33 | 0 | 0 | 86 | 35 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 6 | 0 | 20 | 42 | 0 | 70 | 0 | 260 | 250 | 206 | 8 | 91 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 8 | 8 | 21 | 120 | 157 | 25 | 20 | 0 | 73 | 43 | 22 | 50 | 110 | 159 | 56 | 84 | 0 | 219 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 95 | 0 | 0 | 200 | 0 | 102 | 0 | 22 | 0 | 80 | 427 | 45 | 0 | 0 | 0 | 125 | 17 | 0 | 17 | 112 | 100 | 0 | 17 |  | 920 | 0 | 260 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 142 | 0 | 95 | 0 | 160 | 0 | 357 | 35 | 0 | 0 | 0 | 68 | 0 | 0 | 70 | 480 |  | 6606 | 2938 | 9544 | 3916 | 920 | 2053 | 1664 | 630 | 121 | 120 | 120 | 0 | 0 | 102.05
5:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 357 |  | 0 | 450 | 270 | 16 | 64 | 30 | 0 | 0 | 155 | 0 | 7 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 36 | 19 | 25 | 31 | 33 | 33 | 0 | 0 | 86 | 35 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 6 | 0 | 20 | 41 | 0 | 70 | 0 | 260 | 250 | 206 | 8 | 90 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 8 | 8 | 21 | 114 | 157 | 25 | 20 | 0 | 73 | 43 | 22 | 50 | 110 | 158 | 56 | 84 | 0 | 218 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 95 | 0 | 0 | 170 | 0 | 102 | 0 | 22 | 0 | 50 | 427 | 35 | 0 | 0 | 0 | 125 | 17 | 0 | 17 | 113 | 100 | 0 | 17 |  | 920 | 0 | 260 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 149 | 0 | 44 | 0 | 170 | 0 | 350 | 35 | 0 | 0 | 0 | 69 | 0 | 0 | 70 | 460 |  | 6468 | 2877 | 9345 | 3923 | 920 | 1993 | 1544 | 610 | 121 | 120 | 114 | 0 | 0 | 102.05
6:00 | 0 | 0 | 101 | 115 | 200 | 72 | 0 | 0 | 283 |  | 0 | 330 | 245 | 16 | 64 | 30 | 0 | 0 | 75 | 0 | 7 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 19 | 25 | 31 | 33 | 33 | 0 | 0 | 86 | 35 | 115 | 0 | 0 | 204 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 6 | 0 | 20 | 38 | 0 | 70 | 0 | 260 | 250 | 212 | 8 | 81 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 8 | 8 | 21 | 110 | 158 | 25 | 20 | 0 | 73 | 43 | 22 | 10 | 110 | 159 | 40 | 30 | 0 | 184 | 18 | 0 | 10 | 295 | 24 | 11 | 0 | 95 | 0 | 0 | 150 | 0 | 100 | 0 | 22 | 0 | 50 | 429 | 35 | 0 | 0 | 0 | 108 | 17 | 0 | 17 | 110 | 100 | 0 | 17 |  | 920 | 0 | 290 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 163 | 0 | 44 | 0 | 175 | 0 | 298 | 35 | 0 | 0 | 0 | 71 | 0 | 0 | 70 | 460 |  | 5913 | 2868 | 8781 | 3775 | 920 | 1647 | 1478 | 610 | 121 | 120 | 110 | 0 | 0 | 102.05
7:00 | 0 | 0 | 99 | 115 | 200 | 72 | 0 | 0 | 262 |  | 0 | 300 | 245 | 16 | 64 | 30 | 0 | 0 | 65 | 0 | 7 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 19 | 25 | 31 | 33 | 33 | 0 | 0 | 82 | 35 | 115 | 0 | 0 | 203 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 6 | 0 | 20 | 35 | 0 | 70 | 0 | 260 | 250 | 180 | 8 | 81 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 8 | 15 | 15 | 82 | 159 | 25 | 20 | 0 | 58 | 43 | 22 | 10 | 110 | 156 | 40 | 20 | 0 | 152 | 18 | 0 | 10 | 260 | 24 | 11 | 0 | 95 | 0 | 0 | 130 | 0 | 100 | 1 | 22 | 0 | 50 | 431 | 35 | 0 | 0 | 1 | 70 | 17 | 0 | 17 | 104 | 100 | 0 | 17 |  | 920 | 0 | 225 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 44 | 0 | 130 | 0 | 283 | 35 | 0 | 0 | 0 | 69 | 0 | 1 | 70 | 400 |  | 5629 | 2678 | 8307 | 3569 | 920 | 1534 | 1412 | 550 | 117 | 120 | 82 | 3 | 0 | 102.05
8:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 262 |  | 0 | 300 | 265 | 16 | 64 | 30 | 0 | 0 | 65 | 0 | 7 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 19 | 25 | 31 | 33 | 33 | 0 | 0 | 82 | 35 | 115 | 0 | 0 | 203 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 6 | 0 | 20 | 12 | 0 | 70 | 0 | 260 | 250 | 181 | 8 | 81 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 8 | 15 | 15 | 84 | 160 | 25 | 20 | 0 | 58 | 43 | 22 | 10 | 70 | 158 | 40 | 20 | 0 | 151 | 18 | 0 | 0 | 270 | 24 | 11 | 0 | 95 | 0 | 0 | 130 | 0 | 102 | 3 | 22 | 0 | 50 | 430 | 35 | 0 | 0 | 1 | 70 | 17 | 0 | 17 | 104 | 100 | 0 | 17 |  | 920 | 0 | 225 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 20 | 0 | 130 | 0 | 298 | 35 | 0 | 0 | 0 | 69 | 0 | 2 | 70 | 400 |  | 5595 | 2643 | 8238 | 3541 | 920 | 1466 | 1434 | 550 | 117 | 120 | 84 | 6 | 0 | 0
9:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 302 |  | 0 | 300 | 270 | 16 | 64 | 30 | 0 | 0 | 70 | 0 | 7 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 19 | 25 | 31 | 33 | 33 | 0 | 0 | 83 | 35 | 115 | 0 | 0 | 203 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 7 | 0 | 70 | 0 | 260 | 250 | 181 | 8 | 82 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 8 | 15 | 15 | 80 | 144 | 25 | 20 | 0 | 58 | 43 | 22 | 10 | 70 | 158 | 40 | 20 | 0 | 152 | 18 | 0 | 10 | 265 | 24 | 11 | 0 | 95 | 0 | 0 | 130 | 0 | 100 | 1 | 22 | 0 | 50 | 425 | 0 | 0 | 0 | 0 | 70 | 17 | 0 | 17 | 104 | 100 | 78 | 17 |  | 920 | 0 | 270 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 22 | 0 | 130 | 0 | 307 | 35 | 0 | 0 | 0 | 67 | 0 | 3 | 70 | 400 |  | 5653 | 2693 | 8346 | 3648 | 920 | 1512 | 1394 | 550 | 118 | 120 | 80 | 4 | 0 | 0
10:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 302 |  | 0 | 300 | 295 | 16 | 64 | 30 | 0 | 0 | 74 | 0 | 7 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 16 | 25 | 31 | 33 | 33 | 0 | 0 | 84 | 35 | 115 | 0 | 0 | 214 | 0 | 108 | 0 |  | 0 | 8 | 0 | 0 | 0 | 0 | 20 | 6 | 0 | 70 | 0 | 260 | 250 | 216 | 8 | 90 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 11 | 15 | 15 | 112 | 125 | 24 | 20 | 1 | 58 | 43 | 20 | 10 | 70 | 158 | 40 | 20 | 0 | 75 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 95 | 0 | 0 | 100 | 0 | 100 | 3 | 22 | 0 | 10 | 421 | 0 | 0 | 0 | 0 | 70 | 17 | 0 | 17 | 104 | 100 | 270 | 17 |  | 920 | 0 | 240 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 18 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 22 | 0 | 130 | 0 | 334 | 35 | 0 | 0 | 0 | 65 | 0 | 5 | 70 | 360 |  | 5861 | 2648 | 8509 | 3806 | 920 | 1559 | 1346 | 510 | 119 | 128 | 112 | 9 | 0 | 0
11:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 333 |  | 0 | 360 | 275 | 7 | 64 | 50 | 0 | 0 | 118 | 0 | 7 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 16 | 25 | 31 | 33 | 33 | 0 | 0 | 86 | 35 | 115 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 8 | 0 | 0 | 0 | 0 | 20 | 6 | 0 | 70 | 0 | 330 | 250 | 179 | 8 | 89 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 11 | 16 | 15 | 112 | 125 | 24 | 20 | 1 | 58 | 43 | 20 | 22 | 70 | 158 | 40 | 20 | 0 | 120 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 95 | 0 | 0 | 100 | 0 | 102 | 0 | 22 | 0 | 10 | 425 | 0 | 0 | 0 | 0 | 70 | 17 | 0 | 17 | 80 | 100 | 185 | 17 |  | 920 | 0 | 290 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 18 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 22 | 0 | 130 | 0 | 398 | 0 | 0 | 0 | 0 | 38 | 0 | 5 | 35 | 350 |  | 5993 | 2656 | 8649 | 3917 | 920 | 1727 | 1218 | 500 | 121 | 128 | 112 | 6 | 0 | 0
12:00 | 0 | 0 | 100 | 115 | 200 | 71 | 0 | 0 | 354 |  | 0 | 420 | 300 | 7 | 64 | 55 | 0 | 0 | 150 | 0 | 7 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 42 | 19 | 25 | 31 | 33 | 33 | 0 | 0 | 87 | 35 | 115 | 0 | 0 | 217 | 0 | 142 | 0 |  | 0 | 8 | 0 | 0 | 0 | 11 | 20 | 5 | 0 | 70 | 0 | 310 | 320 | 170 | 8 | 90 | 5 | 5 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 16 | 15 | 106 | 121 | 24 | 20 | 1 | 58 | 43 | 14 | 46 | 110 | 158 | 40 | 20 | 0 | 140 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 100 | 0 | 0 | 100 | 0 | 108 | 0 | 22 | 0 | 10 | 419 | 0 | 0 | 0 | 0 | 70 | 17 | 0 | 17 | 80 | 100 | 185 | 17 |  | 920 | 0 | 340 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 43 | 0 | 130 | 0 | 414 | 0 | 0 | 0 | 0 | 36 | 0 | 5 | 35 | 350 |  | 6290 | 2744 | 9034 | 4071 | 920 | 1906 | 1275 | 500 | 122 | 128 | 106 | 6 | 0 | 0
13:00 | 0 | 0 | 100 | 115 | 200 | 71 | 0 | 0 | 352 |  | 0 | 350 | 265 | 7 | 64 | 55 | 0 | 0 | 120 | 0 | 7 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 19 | 25 | 31 | 33 | 8 | 0 | 0 | 88 | 35 | 115 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 8 | 0 | 0 | 0 | 12 | 20 | 17 | 0 | 70 | 0 | 275 | 250 | 189 | 8 | 82 | 5 | 5 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 16 | 20 | 114 | 106 | 24 | 20 | 1 | 58 | 43 | 31 | 50 | 110 | 158 | 40 | 87 | 0 | 140 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 135 | 0 | 0 | 100 | 0 | 138 | 3 | 22 | 0 | 10 | 424 | 0 | 0 | 0 | 0 | 70 | 17 | 0 | 0 | 55 | 100 | 70 | 17 |  | 920 | 0 | 330 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 43 | 0 | 130 | 0 | 399 | 0 | 0 | 0 | 0 | 38 | 0 | 5 | 35 | 400 |  | 6036 | 2774 | 8810 | 3775 | 920 | 1912 | 1279 | 550 | 123 | 128 | 114 | 9 | 8810 | 0
14:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 272 |  | 0 | 320 | 285 | 7 | 64 | 55 | 0 | 0 | 70 | 0 | 7 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 19 | 25 | 31 | 33 | 17 | 0 | 0 | 88 | 35 | 115 | 0 | 8 | 205 | 0 | 104 | 0 |  | 0 | 8 | 0 | 0 | 0 | 12 | 20 | 11 | 0 | 70 | 0 | 285 | 250 | 190 | 8 | 90 | 5 | 5 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 16 | 15 | 104 | 103 | 24 | 20 | 1 | 58 | 43 | 37 | 50 | 110 | 159 | 40 | 87 | 0 | 110 | 18 | 0 | 10 | 290 | 16 | 8 | 0 | 145 | 0 | 0 | 100 | 0 | 149 | 0 | 22 | 0 | 10 | 423 | 0 | 0 | 0 | 0 | 70 | 19 | 0 | 0 | 55 | 100 | 0 | 17 |  | 920 | 0 | 295 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 43 | 0 | 130 | 0 | 375 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 35 | 390 |  | 5791 | 2687 | 8478 | 3566 | 920 | 1779 | 1312 | 540 | 123 | 128 | 104 | 6 | 0 | 0
15:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 272 |  | 0 | 320 | 265 | 7 | 48 | 55 | 0 | 0 | 140 | 0 | 7 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 19 | 25 | 31 | 33 | 17 | 0 | 0 | 91 | 35 | 115 | 0 | 8 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 20 | 8 | 0 | 70 | 0 | 260 | 250 | 191 | 8 | 80 | 5 | 5 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 0 | 16 | 110 | 103 | 24 | 20 | 1 | 58 | 43 | 37 | 50 | 110 | 158 | 40 | 87 | 0 | 100 | 18 | 0 | 10 | 290 | 16 | 8 | 0 | 95 | 0 | 0 | 100 | 0 | 149 | 0 | 22 | 0 | 15 | 426 | 0 | 0 | 0 | 0 | 70 | 35 | 0 | 0 | 55 | 100 | 0 | 17 |  | 919 | 0 | 295 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 20 | 0 | 130 | 0 | 340 | 0 | 0 | 0 | 0 | 40 | 0 | 3 | 35 | 370 |  | 5735 | 2605 | 8340 | 3577 | 919 | 1717 | 1247 | 520 | 126 | 120 | 110 | 4 | 0 | 0
16:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 273 |  | 0 | 320 | 265 | 7 | 48 | 30 | 0 | 0 | 118 | 0 | 7 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 19 | 25 | 31 | 33 | 17 | 0 | 0 | 91 | 35 | 115 | 0 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 20 | 11 | 0 | 70 | 0 | 260 | 250 | 204 | 8 | 81 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 0 | 0 | 9 | 102 | 104 | 24 | 22 | 1 | 58 | 43 | 14 | 20 | 110 | 159 | 40 | 40 | 0 | 100 | 18 | 0 | 10 | 280 | 16 | 8 | 0 | 95 | 0 | 0 | 60 | 0 | 145 | 0 | 22 | 0 | 32 | 425 | 0 | 0 | 0 | 0 | 52 | 36 | 0 | 0 | 35 | 50 | 0 | 17 |  | 920 | 0 | 295 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 21 | 0 | 130 | 0 | 342 | 0 | 0 | 0 | 0 | 40 | 0 | 2 | 35 | 370 |  | 5439 | 2600 | 8039 | 3551 | 920 | 1617 | 1080 | 520 | 126 | 120 | 102 | 3 | 0 | 0
17:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 273 |  | 0 | 320 | 285 | 7 | 48 | 30 | 0 | 0 | 98 | 0 | 7 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 19 | 25 | 31 | 33 | 33 | 0 | 0 | 89 | 35 | 115 | 0 | 0 | 209 | 0 | 103 | 0 |  | 0 | 0 | 24 | 0 | 0 | 12 | 20 | 25 | 0 | 70 | 0 | 275 | 250 | 170 | 8 | 90 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 0 | 0 | 9 | 56 | 104 | 24 | 22 | 0 | 56 | 43 | 14 | 20 | 110 | 158 | 40 | 40 | 0 | 70 | 18 | 0 | 10 | 285 | 16 | 8 | 0 | 95 | 0 | 0 | 60 | 0 | 132 | 0 | 22 | 0 | 40 | 216 | 2 | 2 | 0 | 0 | 52 | 34 | 0 | 0 | 35 | 50 | 0 | 17 |  | 920 | 0 | 295 | 0 | 11 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 22 | 0 | 130 | 0 | 368 | 17 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 350 |  | 5204 | 2626 | 7830 | 3300 | 920 | 1661 | 1120 | 500 | 124 | 149 | 56 | 0 | 0 | 0
18:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 340 |  | 0 | 350 | 255 | 7 | 55 | 32 | 0 | 0 | 145 | 0 | 7 | 8 | 82 | 13 | 0 | 0 | 0 | 54 | 55 | 55 | 10 | 25 | 23 | 33 | 33 | 0 | 0 | 87 | 35 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 68 | 10 | 0 | 21 | 20 | 20 | 0 | 70 | 0 | 260 | 250 | 217 | 8 | 80 | 5 | 5 | 0 | 43 | 0 | 0 | 8 | 20 | 0 | 0 | 9 | 94 | 105 | 24 | 20 | 0 | 73 | 43 | 45 | 35 | 110 | 158 | 40 | 87 | 0 | 140 | 18 | 0 | 10 | 300 | 16 | 11 | 0 | 187 | 0 | 0 | 100 | 0 | 149 | 0 | 22 | 8 | 66 | 0 | 31 | 53 | 0 | 0 | 122 | 45 | 0 | 0 | 65 | 100 | 0 | 17 |  | 921 | 0 | 325 | 0 | 74 | 120 | 0 | 0 | 0 | 0 | 8 | 0 | 12 | 64 | 0 | 0 | 0 | 0 | 0 | 90 | 20 | 0 | 0 | 10 | 18 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 137 | 0 | 50 | 0 | 155 | 0 | 376 | 35 | 0 | 16 | 0 | 57 | 0 | 0 | 72 | 390 |  | 6057 | 3143 | 9200 | 3325 | 921 | 1895 | 1925 | 540 | 122 | 378 | 94 | 0 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 358 |  | 0 | 350 | 280 | 7 | 92 | 40 | 0 | 0 | 120 | 0 | 7 | 8 | 78 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 10 | 25 | 31 | 33 | 33 | 0 | 0 | 86 | 35 | 115 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 34 | 0 | 0 | 48 | 20 | 23 | 0 | 70 | 0 | 260 | 250 | 219 | 8 | 90 | 5 | 5 | 0 | 43 | 0 | 0 | 8 | 20 | 0 | 0 | 20 | 102 | 104 | 24 | 20 | 0 | 73 | 43 | 45 | 50 | 110 | 158 | 40 | 87 | 0 | 140 | 18 | 0 | 10 | 275 | 16 | 5 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 22 | 0 | 143 | 0 | 55 | 38 | 0 | 0 | 122 | 54 | 0 | 0 | 113 | 100 | 0 | 17 |  | 909 | 0 | 330 | 0 | 83 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 95 | 20 | 0 | 0 | 25 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 167 | 0 | 75 | 0 | 153 | 0 | 391 | 35 | 0 | 70 | 0 | 79 | 0 | 0 | 100 | 470 |  | 6457 | 3379 | 9836 | 3356 | 909 | 1950 | 2451 | 620 | 121 | 327 | 102 | 0 | 0 | 0
19:30 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 358 |  | 0 | 350 | 285 | 35 | 97 | 48 | 0 | 0 | 150 | 0 | 7 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 10 | 25 | 31 | 33 | 33 | 0 | 0 | 84 | 35 | 115 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 34 | 0 | 0 | 19 | 20 | 27 | 0 | 70 | 0 | 280 | 260 | 218 | 8 | 90 | 5 | 5 | 0 | 43 | 0 | 0 | 8 | 21 | 0 | 0 | 20 | 104 | 104 | 24 | 20 | 0 | 73 | 43 | 45 | 50 | 110 | 157 | 40 | 87 | 0 | 140 | 18 | 0 | 10 | 300 | 16 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 22 | 0 | 150 | 0 | 55 | 35 | 0 | 0 | 122 | 54 | 0 | 0 | 113 | 100 | 0 | 17 |  | 910 | 0 | 325 | 0 | 83 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 48 | 0 | 0 | 0 | 0 | 0 | 24 | 20 | 0 | 0 | 25 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 167 | 0 | 75 | 0 | 152 | 0 | 400 | 35 | 0 | 70 | 0 | 80 | 0 | 0 | 109 | 460 |  | 6505 | 3313 | 9818 | 3415 | 910 | 1989 | 2445 | 610 | 119 | 226 | 104 | 0 | 0 | 0
20:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 359 |  | 0 | 350 | 275 | 30 | 97 | 55 | 0 | 0 | 150 | 0 | 7 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 12 | 25 | 31 | 33 | 33 | 0 | 0 | 84 | 35 | 115 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 21 | 0 | 70 | 0 | 280 | 260 | 220 | 8 | 89 | 5 | 5 | 0 | 43 | 0 | 0 | 8 | 21 | 11 | 0 | 22 | 108 | 104 | 25 | 22 | 0 | 73 | 43 | 45 | 50 | 110 | 160 | 40 | 87 | 0 | 140 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 22 | 0 | 150 | 0 | 55 | 17 | 0 | 0 | 122 | 54 | 0 | 0 | 113 | 100 | 0 | 17 |  | 910 | 0 | 320 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 48 | 0 | 0 | 0 | 0 | 0 | 24 | 20 | 0 | 0 | 8 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 167 | 0 | 88 | 0 | 152 | 0 | 374 | 35 | 0 | 70 | 0 | 78 | 0 | 0 | 109 | 500 |  | 6456 | 3296 | 9752 | 3431 | 910 | 1958 | 2384 | 650 | 119 | 192 | 108 | 0 | 0 | 0
21:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 359 |  | 0 | 350 | 275 | 87 | 97 | 55 | 0 | 0 | 150 | 0 | 7 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 19 | 25 | 31 | 33 | 33 | 0 | 0 | 84 | 35 | 115 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 70 | 0 | 280 | 260 | 195 | 8 | 89 | 5 | 5 | 0 | 43 | 0 | 0 | 8 | 21 | 11 | 0 | 22 | 106 | 104 | 25 | 22 | 0 | 73 | 43 | 47 | 50 | 110 | 157 | 40 | 87 | 0 | 140 | 18 | 0 | 10 | 285 | 16 | 11 | 0 | 245 | 0 | 0 | 200 | 0 | 149 | 0 | 22 | 0 | 150 | 15 | 35 | 17 | 0 | 0 | 125 | 54 | 0 | 0 | 113 | 100 | 0 | 17 |  | 910 | 0 | 320 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 24 | 20 | 0 | 0 | 0 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 167 | 0 | 95 | 0 | 163 | 0 | 367 | 35 | 0 | 35 | 0 | 84 | 0 | 0 | 109 | 500 |  | 6382 | 3241 | 9623 | 3416 | 910 | 1949 | 2281 | 650 | 119 | 192 | 106 | 0 | 0 | #REF!
22:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 360 |  | 0 | 350 | 250 | 93 | 97 | 55 | 0 | 0 | 140 | 0 | 7 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 55 | 19 | 25 | 31 | 33 | 33 | 0 | 0 | 86 | 35 | 115 | 0 | 0 | 203 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 70 | 0 | 260 | 260 | 163 | 8 | 80 | 5 | 5 | 0 | 43 | 0 | 0 | 8 | 21 | 11 | 0 | 22 | 112 | 107 | 25 | 20 | 0 | 73 | 43 | 47 | 50 | 110 | 156 | 40 | 87 | 0 | 140 | 18 | 0 | 10 | 270 | 16 | 11 | 0 | 195 | 0 | 0 | 200 | 0 | 149 | 0 | 22 | 0 | 150 | 15 | 35 | 0 | 0 | 0 | 125 | 54 | 0 | 17 | 113 | 100 | 0 | 35 |  | 911 | 0 | 315 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 167 | 0 | 97 | 0 | 161 | 0 | 345 | 17 | 0 | 0 | 0 | 78 | 0 | 0 | 109 | 440 |  | 6229 | 3006 | 9235 | 3339 | 911 | 1943 | 2067 | 590 | 121 | 152 | 112 | 0 | 0 | 102.2
23:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 359 |  | 0 | 350 | 270 | 93 | 97 | 15 | 0 | 0 | 145 | 0 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 19 | 25 | 32 | 33 | 33 | 0 | 0 | 86 | 35 | 115 | 0 | 0 | 203 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 70 | 0 | 260 | 260 | 154 | 8 | 90 | 5 | 5 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 0 | 22 | 108 | 107 | 25 | 22 | 0 | 73 | 43 | 47 | 50 | 110 | 158 | 40 | 87 | 0 | 140 | 18 | 0 | 10 | 270 | 16 | 11 | 0 | 80 | 0 | 0 | 200 | 0 | 149 | 0 | 22 | 0 | 150 | 144 | 0 | 0 | 0 | 0 | 125 | 17 | 0 | 0 | 113 | 60 | 0 | 35 |  | 911 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 167 | 0 | 97 | 0 | 157 | 0 | 306 | 17 | 0 | 0 | 0 | 79 | 0 | 0 | 109 | 500 |  | 6033 | 3006 | 9039 | 3480 | 911 | 1908 | 1741 | 650 | 121 | 120 | 108 | 0 | 0 | 102.22
24:00 | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 359 |  | 0 | 350 | 270 | 100 | 30 | 0 | 0 | 0 | 120 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 19 | 25 | 32 | 33 | 33 | 0 | 0 | 86 | 35 | 115 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 0 | 70 | 0 | 260 | 260 | 154 | 8 | 90 | 5 | 5 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 0 | 20 | 102 | 127 | 25 | 20 | 0 | 73 | 43 | 47 | 50 | 110 | 158 | 40 | 87 | 0 | 140 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 45 | 0 | 0 | 160 | 0 | 126 | 0 | 0 | 0 | 10 | 253 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 0 | 113 | 100 | 0 | 35 |  | 911 | 0 | 335 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 165 | 0 | 96 | 0 | 158 | 0 | 330 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 70 | 500 |  | 5774 | 2950 | 8724 | 3618 | 911 | 1951 | 1251 | 650 | 121 | 120 | 102 | 0 | 0 | 102.24
KWH | 0 | 0 | 2404000 | 2709000 | 4795036 | 1704090 | 0 | 0 | 7776000 |  | 0 | 8394000 | 6514269 | 656640 | 1760952 | 1013546 | 0 | 0 | 3223000 | 0 | 197760 | 244512 | 396480 | 46680 | 0 | 0 | 0 | 252000 | 627876 | 1103202 | 406008 | 600000 | 711000 | 814600 | 758800 | 0 | 0 | 2065484 | 840000 | 2700000 | 0 | 37665 | 4874186 | 0 | 2913678 | 0 |  | 0 | 45552 | 155390 | 52440 | 50880 | 224640 | 407712 | 583200 | 0 | 1652465 | 0 | 6782900 | 6266000 | 4642000 | 200727 | 2031330 | 126648 | 139680 | 0 | 1120389 | 0 | 0 | 191563 | 472752 | 181800 | 181200 | 429970 | 2595840 | 2920280 | 595200 | 434916 | 4200 | 1566000 | 1041000 | 699600 | 968976 | 2589381 | 3497000 | 1053984 | 1579200 | 0 | 3632980 | 416000 | 0 | 243900 | 7008000 | 478560 | 246096 | 0 | 3680835 | 0 | 0 | 3585600 | 0 | 3110830 | 14175 | 526080 | 28800 | 2003927 | 7743000 | 877200 | 229200 | 0 | 3601 | 2458909 | 0 | 0 | 234840 | 2261280 | 2296320 | 701570 | 487680 |  | 22020364 | 0 | 7081920 | 0 | 536640 | 3077760 | 0 | 0 | 0 | 0 | 60750 | 0 | 356260 | 356448 | 0 | 0 | 0 | 0 | 0 | 280928 | 376220 | 0 | 0 | 80160 | 26533 | 493200 | 238896 | 218862 | 0 | 0 | 3692600 | 0 | 0 | 0 | 0 | 3720609 | 0 | 1408 | 8640 | 3954264 | 0 | 8478640 | 560640 | 0 | 448032 | 0 | 1494720 | 0 | 35021 | 1776576 | 11404600 |  | 148294662 | 70780691 | 219075353 | 88791126 | 22020364 | 42575547 | 41050152 | 15097200 | 2905484 | 3982643 | 2595840 | 56997 | 0
Fuel Cost | 0 | 0 | 3509840 | 3982230 | 5322489.96 | 2249398.8 | 0 | 0 | 8009280 |  | 0 | 9149460 | 7230838.59 | 4983897.6 | 12132959.28 | 8574599.16 | 0 | 0 | 5575790 | 0 | 1489132.8 | 2229949.44 | 3901363.2 | 430389.6 | 0 | 0 | 0 | 1839600 | 4853481.48 | 10877571.72 | 304506 | 450000 | 0 | 0 | 0 | 0 | 0 | 557680.68 | 226800 | 4887000 | 0 | 349907.85 | 5312862.74 | 0 | 4953252.6 | 0 |  | 0 | 440487.84 | 1507283 | 500802 | 442656 | 1779148.8 | 513717.12 | 1732104 | 0 | 2445648.2 | 0 | 5019346 | 6266000 | 4270640 | 258937.83 | 2336029.5 | 143112.24 | 195552 | 0 | 1915865.19 | 0 | 0 | 1829426.65 | 600395.04 | 136350 | 317100 | 322477.5 | 19468800 | 3095496.8 | 5404416 | 552343.32 | 66948 | 2568240 | 1665600 | 1245288 | 1511602.56 | 2951894.34 | 3636880 | 2076348.48 | 3016272 | 0 | 6285055.4 | 911040 | 0 | 497556 | 7078080 | 358920 | 187032.96 | 0 | 27827112.6 | 0 | 0 | 18645120 | 0 | 30610567.2 | 165705.75 | 4287552 | 312480 | 14127685.35 | 7200990 | 8000064 | 2165940 | 0 | 0 | 18589352.04 | 0 | 0 | 2343703.2 | 19379169.6 | 15293491.2 | 0 | 0 |  | 126837296.64 | 0 | 7436016 | 0 | 4217990.4 | 42657753.6 | 0 | 0 | 0 | 0 | 633015 | 0 | 552203 | 3478932.48 | 0 | 0 | 0 | 0 | 0 | 2486212.8 | 2896894 | 0 | 0 | 776750.4 | 257370.1 | 946944 | 370288.8 | 165678.534 | 0 | 0 | 20013892 | 0 | 0 | 0 | 0 | 4911203.88 | 0 | 2112 | 146966.4 | 4626488.88 | 0 | 8393853.6 | 5853081.6 | 0 | 4251823.68 | 0 | 11599027.2 | 0 | 386982.05 | 13128896.64 | 50066194 |  | 377884107.21 | 317093867.684 | 694977974.894 | 102346121.154 | 126837296.64 | 50076692.12 | 273514391.96 | 70080086 | 784480.68 | 51250470.54 | 19468800 | 619635.8 | 0
Yesterday Day Peak | 0 | 0 | 100 | 115 | 200 | 71 | 0 | 0 | 354 |  | 0 | 420 | 300 | 7 | 64 | 55 | 0 | 0 | 150 | 0 | 7 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 42 | 19 | 25 | 31 | 33 | 33 | 0 | 0 | 87 | 35 | 115 | 0 | 0 | 217 | 0 | 142 | 0 |  | 0 | 8 | 0 | 0 | 0 | 11 | 20 | 5 | 0 | 70 | 0 | 310 | 320 | 170 | 8 | 90 | 5 | 5 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 16 | 15 | 106 | 121 | 24 | 20 | 1 | 58 | 43 | 14 | 46 | 110 | 158 | 40 | 20 | 0 | 140 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 100 | 0 | 0 | 100 | 0 | 108 | 0 | 22 | 0 | 10 | 419 | 0 | 0 | 0 | 0 | 70 | 17 | 0 | 17 | 80 | 100 | 185 | 17 |  | 920 | 0 | 340 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 43 | 0 | 130 | 0 | 414 | 0 | 0 | 0 | 0 | 36 | 0 | 5 | 35 | 350 |  | 9034 | DayPeak
Yesterday Evening Peak | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 358 | 0 | 0 | 350 | 280 | 7 | 92 | 40 | 0 | 0 | 120 | 0 | 7 | 8 | 78 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 10 | 25 | 31 | 33 | 33 | 0 | 0 | 86 | 35 | 115 | 0 | 0 | 203 | 0 | 139 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 48 | 20 | 23 | 0 | 70 | 0 | 260 | 250 | 219 | 8 | 90 | 5 | 5 | 0 | 43 | 0 | 0 | 8 | 20 | 0 | 0 | 20 | 102 | 104 | 24 | 20 | 0 | 73 | 43 | 45 | 50 | 110 | 158 | 40 | 87 | 0 | 140 | 18 | 0 | 10 | 275 | 16 | 5 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 22 | 0 | 143 | 0 | 55 | 38 | 0 | 0 | 122 | 54 | 0 | 0 | 113 | 100 | 0 | 17 |  | 909 | 0 | 330 | 0 | 83 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 95 | 20 | 0 | 0 | 25 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 167 | 0 | 75 | 0 | 153 | 0 | 391 | 35 | 0 | 70 | 0 | 79 | 0 | 0 | 100 | 470 |  | 9836 | EvPeak
Forecast for Evening | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 360 | 0 | 0 | 450 | 305 | 16 | 100 | 55 | 0 | 0 | 165 | 0 | 7 | 16 | 150 | 92 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 85 | 35 | 115 | 0 | 25 | 221 | 0 | 145 | 0 | 0 | 0 |  | 102 | 100 | 97 | 50 | 21 | 20 | 0 | 80 | 0 | 360 | 350 | 225 | 8 | 90 | 5 | 5 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 22 | 173 | 160 | 48 | 20 | 0 | 85 | 43 | 51 | 44 | 110 | 160 | 65 | 86 | 0 | 200 | 20 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 22 | 200 | 150 | 400 | 115 | 86 | 100 | 0 | 300 | 54 | 110 | 17 | 113 | 100 | 0 | 17 |  | 909 | 16 | 360 | 0 | 115 | 220 | 0 | 0 | 30 | 60 | 40 | 0 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 20 | 0 | 50 | 52 | 30 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 225 | 0 | 95 | 100 | 220 | 0 | 414 | 105 | 200 | 113 | 100 | 109 | 0 | 0 | 113 | 500
Forecast for Day | 0 | 0 | 100 | 115 | 200 | 72 | 0 | 0 | 360 | 0 | 0 | 450 | 305 | 16 | 100 | 55 | 0 | 0 | 115 | 0 | 7 | 16 | 150 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 85 | 35 | 115 | 0 | 25 | 221 | 0 | 145 | 0 | 0 | 0 |  | 102 | 100 | 97 | 50 | 21 | 10 | 0 | 80 | 0 | 360 | 350 | 225 | 8 | 90 | 5 | 5 | 0 | 51 | 0 | 25 | 25 | 22 | 11 | 33 | 22 | 165 | 160 | 48 | 20 | 1.6 | 85 | 43 | 51 | 44 | 110 | 160 | 65 | 86 | 0 | 151 | 18 | 0 | 10 | 341 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 22 | 200 | 150 | 400 | 115 | 85 | 100 | 5 | 300 | 54 | 110 | 17 | 113 | 100 | 0 | 17 |  | 700 | 0 | 360 | 0 | 115 | 220 | 0 | 0 | 0 | 0 | 40 | 0 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 20 | 0 | 50 | 52 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 225 |  | 95 | 50 | 220 | 0 | 414 | 105 | 100 | 113 | 100 | 105 | 0 | 8 | 113 | 500
Generation at 08:00(Today) | 0 | 0 | 100 | 115 | 200 | 22 | 0 | 0 | 282 | 0 | 0 | 320 | 240 |  | 15 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 25 | 26 | 33 | 33 | 0 | 0 | 82 | 35 | 115 | 0 | 0 | 203 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 0 | 70 | 0 | 260 | 240 | 151 | 8 | 80 | 5 | 5 | 0 | 10 | 0 | 0 | 0 | 21 | 5 | 0 | 9 | 66 | 161 | 25 | 22 | 0 | 43 | 42 | 11 | 10 | 100 | 156 | 40 | 10 | 0 | 80 | 0 | 0 | 10 | 220 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 37 | 0 | 0 | 0 | 0 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 671 | 0 | 255 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 133 | 0 | 33 | 0 | 145 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 310 | 0
199
| Minimum Generation |  | 8238 | 8:00
| Highest Generation |  | 10604 | 1:00
| Day Peak Generation |  | 9034 | 12:00
| Evening Peak Generation |  | 9836 | 19:00
| HVDC Max Flow |  | 921 | 18:00
| HVDC EvPeak Flow |  | 909 | 19:00
| Load factor L.F |  | 86.08%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-10-23
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-10-22 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9034 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 6388 | MW
Evening Peak Generation : |  | 9836 | MW Hour : | 19:00 | Available Max Generation : |  | 14449 | MW
E.P. Demand (at gen end) : |  | 9836 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 8800 | MW
Maximum Generation : |  | 10604 | MW Hour : | 1:00 | Reserve(Generation end) |  | 5649 | MW
Total Gen. (MKWH) : |  | 219.0754 | System Load Factor : | 86.08% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 18 | MW at | 2:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-10-23
Actual : | 102.36 | Ft.(MSL) , | Rule curve : | 108 | Ft.( MSL )
Gas Consumed : | Total = | 1110.58 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 152422813.274
: |  | Coal : | 70080086 | Oil : | 324764862.5 | Total : | 547267761.774
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3127.3363 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1057.518 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 946.4409 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 854.8128 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 772.6896 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 623.5181 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 356.2966 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 160.7418 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 480.8515 |  |  | 0 | 0%
Total | 0 |  | 8380.2056 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Baghabari-71 MW,100 MW
3) Ghorasal Unit-1,2,3
4) Ashuganj unit-3,4
5) Kaptai-2,4
6) Raozan #2
7) Siddirganj-335 MW
8) Haripur 412 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Bibiyana(South)-3 400 MW CCPP GT was synchronized at 08:46 & was shut down at 13:12 rejection test.
b) Ghorasal-Ishwardi 230 kV Ckt-1 tripped at 12:50 from both end showing PD-3,DT at Ghorasal end &
Dist. Z1 T-phase at Ishwardi end and was switched on at 13:27.
c) Sylhet 132/33 kV T2 transformer was under shut down from 09:50 to 12:30 due to replacing clamp &
bushing at 132 kv end.
d) Tongi-Bashundhara 132 kV Ckt-1 was under shut down from 08:18 to 16:35 for A/M.
e) Agargaon-Satmosjid 132 kV Ckt-1 was under shut down from 08:47 to 13:14 for A/M.
f) Patuakhali 132/33 kV T-1 transformer was under shut down from 13:38 to 16:57 due to sparking was
found from control panel.
g) Rangamati-Chandraghona 132 kV Ckt-1 was under shut down from 09:04 to 15:27 for A/M.
h) Kallyanpur 132/33 kV T3 transformer was shut down at 09:23 to 16:37 for C/M.
i) Mohasthangarh 132/33 kV T1 transformer was shut down at 09:04 to 15:47 for A/M.
j) Bogura 230/132 kV T03 transformer was shut down at 08:33 to 12:31 for C/M.
k) Polashbari 132/33 kV T-3 transformer was under shut down from 08:05 to 14:18 for A/M.
l) Rajshahi 230/132 kV T-1 transformer was switched on at 15:53.
m) Rajshahi-Bheramara 230 kV Ckt-2 was switched on at 16:08.
n) Rajshahi-Bheramara 230 kV Ckt-1 was shut down at 17:13 for project work.
o) Cumilla(N) 132/33 kV T-3 transformer tripped at 19:22 due to 33 kV feeder fault and was switched on
at 19:36.
p) Haripur-Ullon 132 kV Ckt tripped at 19:58 from both showing Dist Z1,B-phase and was switched on
at 20:42.
q) Payra unit-2 was synchronized at 18:54.
r) Bibiyana-3 tripped at 17:46 and was synchronized at 20:34.
s) Jaldhaka-Bottail 132 kV Ckt-2 tripped at 05:30(23/10/2020) showing Dist. Z1 3-phase at Jaldhaka end &
E/F relay at Bottail and was switched on at 05:50(23/10/2020).
t) Payra unit-1 was shut down at 01:29(23/10/2020) for inspection.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-10-22 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 100 | 2404000 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 115 | 2709000 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 4795036 | Machin problem.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 72 | 1704090 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 358 | 7776000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 350 | 8394000 | Frequency control
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 7 | 656640 | Fuel Shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 280 | 6514269
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 92 | 1760952
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 40 | 1013546 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 46680 | Reserve.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 10 | 406008 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 120 | 3223000
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 7 | 197760 | Fuel Shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under Maintenance
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 8 | 244512 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel Shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 252000
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 78 | 396480 | Line O/L.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 627876
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1103202
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 56 | 1311000 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 814600
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 758800
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 3680835
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3110830
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 38 | 229200 | Low demand
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 487680 | Fuel Shortage
| Dhaka area Total |  |  |  | 5895 | 2627 | 54617996
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 115 | 2700000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 37665 | Reserve.
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 14175
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 48 | 224640
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 121 | 2905484 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4874186
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 139 | 2913678
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Transformer overload
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 45552 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 155390 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 52440 | Reserve.
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 22 | 526080 | Engine problem
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 407712
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 23 | 583200
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 50880 | Fuel Shortage
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 3601
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 122 | 2458909 | Transformer O/L.
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 0
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Transformer O/L.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2296320
| Chattogram area Total |  |  |  | 2266 | 1001 | 20249912
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 70 | 1652465 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 219 | 4642000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 260 | 6782900 | Gas shortage
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 250 | 6266000 | Gas shortage
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 5 | 126648 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 139680 | Gas shortage
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 1120389
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 143 | 2003927
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2031330 | ST Under maint
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 28800 | Reserve.
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 472752
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 181800 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 102 | 2595840
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 0 | 181200 | Reserve.
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 191563 | Fuel Shortage
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 429970 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 234840 | Fuel Shortage
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 2261280
| Cumilla Area Total |  |  |  | 2980 | 1356 | 31544111
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 104 | 2920280 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 434916
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 24 | 595200 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 4200
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 3585600
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 55 | 877200 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 403 | 8417396
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 73 | 1566000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 1041000 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2589381 | Engine problem
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 158 | 3497000 | FGMO & GT-2 under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 45 | 699600 | Engine problem
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 968976
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 246096
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 40 | 1053984 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 87 | 1579200
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 140 | 3632980 | Machin problem.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 416000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 478560
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 275 | 7008000 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 7743000 | Machin problem.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 243900
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 701570 | On test
| Sylhet Area Total |  |  |  | 1988 | 1070 | 33465247
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 909 | 22020364
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 83 | 536640 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 120 | 3077760 | Low demand
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 330 | 7081920 | Gas shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 60750 | Reserve.
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 8640 | Reserve.
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 35 | 560640
107 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Line O/L.
| Khulna Area Total |  |  |  | 2284 | 1477 | 33346714
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 356448
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 16 | 356260
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 75 | 1408
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 470 | 11404600 | Line O/L.
| Barisal Area Total |  |  |  | 1054 | 609 | 12118716
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 20 | 376220 | Engine problem
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel Shortage
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas Shortage
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 167 | 3720609 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 153 | 3954264 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 391 | 8478640 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 26533 | Reserve.
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 493200
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 10 | 238896
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 218862
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 25 | 80160 | Low demand
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 95 | 280928
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 70 | 448032 | Low demand
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 100 | 1776576
| Rajshahi Area Total |  |  |  | 2183 | 1064 | 20092920
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3692600 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 79 | 1494720 | Engine problem
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 35021
| Rangpur Area Total |  |  |  | 605 | 229 | 5222341
| Total |  |  |  | 19892 | 9836 | 219075353
| Eastern Grid Total |  |  |  | 13766 | 6457 | 148294662
| Western Grid Total |  |  |  | 6126 | 3379 | 70780691
| National Grid Total |  |  |  | 19892 | 9836 | 219075353
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-10-22
| (a) ENTIRE EASTERN GRID : |  | 6317 | MW | (b) ENTIRE WESTERN GRID : |  | 3037 | MW
| i) Dhaka area |  | 3647 | MW | i) Khulna area |  | 1135 | MW
| ii) Chittagong area |  | 879 | MW | ii) Rajshahi area |  | 1018 | MW
| iii) Comilla area |  | 670 | MW | iii) Barisal area |  | 181 | MW
| iv) Mymensingh area |  | 740 | MW | iv) Rangpur area |  | 703 | MW
| v) Sylhet area |  | 381 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 9354 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 124 | 10:00 | Sherpur | 100 | 1:00 | Jhenida | 89 | 18:00
| Munsiganj | 108 | 1:00 | Srimongal | 43 | 18:30 | Bottail | 106 | 18:00
| Sonargaon | 75 | 1:00 | Shahjibazar | 109 | 1:00 | G.K Project | 48 | 1:00
| Shyampur | 194 | 12:00 | Fenchuganj | 32 | 2:00 | Faridpur | 167 | 0.041667
| Bhulta | 180 | 1:00 | Kulawara | 32 | 1:00 | Madaripur | 80 | 0.041667
| Madanganj | 45 | 24:00 | Sylhet | 118 | 18:00 | Sariatpur | 54 | 1:00
| Shitalakhya | 111 | 12:00 | Chatak | 22 | 21:00 | Gopalganj | 66 | 1:00
| Rahim steel | 14 | 7:00 | Sunamganj | 33 | 1:00 | Bagerhat | 75 | 19:30
| Matuail | 78 | 10:00 | Biani Bazar | 53 | 1:00 | Mongla | 28 | 1:00
| Ghorasal | 75 | 1:00 | Comilla (S) | 114 | 13:00 | Satkhira | 84 | 0.041667
| Narsingdi | 147 | 1:00 | Comilla(N) | 74 | 18:00 | Gallamari | 41 | 13:00
| Haripur (SBU) | 104 | 18:00 | Chandpur | 77 | 21:00 | Magura | 42 | 0.041667
| Ullon | 52 | 12:00 | Feni | 81 | 21:00 | Norail | 30 | 1:00
| Hasnabad | 181 | 1:00 | Chowmuhani | 102 | 23:00 | Chuadanga | 84 | 1:00
| Magbazar | 92 | 10:00 | Ashuganj | 49 | 23:00 | Barisal(N) | 33 | 0.041667
| Maniknagar | 94 | 10:00 | Daudkandi | 108 | 23:00 | Barisal (S) | 80 | 0.041667
| Bangabhaban | 30 | 10:00 | B.Baria | 118 | 19:00 | Patuakhali | 68 | 0.041667
| Narinda | 84 | 18:00 | Ramganj | 48 | 22:00 | Bhandaria | 38 | 0.79167
| Dhanmondi | 165 | 12:00 | Chaddagram | 20 | 22:00 | Borhan Uddin | 28 | 23:00
| Lalbag | 85 | 12:00 | PHP | 9 | 21:00 | Ishurdi | 52 | 1:00
| Madartek | 64 | 1:00 | Madunaghat | 53 | 14:00 | Ruppur Paromanobik | 2 | 1:00
| Dhaka University |  |  | Hathazari | 80 | 0.041667 | Natore | 102 | 1:00
| Fatullah | 37 | 0.125 | Khulshi | 188 | 0.45833 | Bogra | 145 | 1:00
| Mirpur | 93 | 18:00 | Halishahar | 119 | 0.375 | Noagaon | 110 | 1:00
| Kalyanpur | 78 | 18:00 | Baraulia | 133 | 0.5 | Rajshahi | 122 | 3:00
| Gulshan | 116 | 12:00 | Sikalbaha | 22 | 0.041667 | Rajshahi New | 10 | 20:00
| Uttara | 88 | 13:00 | Dohazari | 74 | 0.041667 | C.Nawabganj | 65 | 19:30
| Uttara New | 29 | 18:00 | Cox'sbazar | 83 | 0.75 | Amnura | 42 | 1:00
| Kamrangirchar | 86 | 18:00 | Chandraghona | 24 | 0.041667 | Pabna | 102 | 1:00
| Savar | 130 | 12:00 | Kaptai | 3.4 | 0.8125 | Shahjadpur | 84 | 1:00
| Bhasantec | 138 | 12:00 | A. Khaer Stl. | 0 | 0.041667 | Serajganj | 74 | 1:00
| Agargaon | 67 | 11:00 | Bakulia | 89 | 0.625 | Niyamatpur | 50 | 20:00
| Satmosjid | 86 | 18:00 | Julda | 18 | 0.041667 | Joypurhat | 52 | 1:00
| Tongi | 104 | 0.41667 | TK chemical | 16.5 | 0.54167 | Sherpur(Bogura) | 38 | 19:00
| Kabirpur | 206 | 18:30 | Modern Steel | 15 | 0.66667 | Mohastangor | 42 | 19:00
| Basundhara | 119 | 18:00 | Shahmirpur | 19 | 0.041667 | Rangpur | 129 | 18:30
| Manikganj | 66 | 1:00 | Khagrachhari | 18 | 0.75 | Lalmonirhat | 52 | 19:00
| Joydevpur | 134 | 15:00 | Matarbari | 27 | 0.041667 | Saidpur | 92 | 18:30
| New Tongi | 102 | 11:00 | Baroiar Hat | 32 | 0.041667 | Purbasadipur | 93 | 18:30
| Kodda | 197 | 16:00 | Rangamati | 10 | 0.75 | Thakurgaon | 76 | 19:30
| Dhamrai | 82 | 18:00 | Abul Khair 230 | 13 | 0.16667 | Palashbari | 106 | 18:30
| Rajendrapur | 90 | 18:00 | BSRM | 156 | 0.625 | Barapukuria | 52 | 1:00
| Valuka | 92 | 1:00 | GPH Ispat | 71 | 0.25 | Panchagar | 49 | 19:00
| Tangail | 160 | 1:00 | Goalpara | 26 | 0.041667 | Joldhaka | 28 | 19:00
| Mymensing | 194 | 1:00 | Central s/s | 69 | 1:00 | Kurigram | 51 | 18:30
| Kishorganj | 130 | 1:00 | Noapara | 46 | 1:00
| Netrokona | 84 | 20:00 | Jessore | 91 | 18:30
| Jamalpur | 125 | 1:00 | Benapol | 40 | 18:30
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-10-22 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 416 | 22:00 | 399 | 10:00 | Kaliakoir | 408 | 0.625 | 387 | 0.5
| Bheramara | 394 | 22:00 | 390 | 18:00 | Bhulta | 381 | 0.875 | 358 | 0.5
| Ashuganj(N) | 386 | 20:00 | 366 | 10:00 | Gopalganj | 412 | 0.25 | 398 | 0.91667
| Payra | 414 | 22:00 | 407 | 18:30
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 230 | 1:00 | Comilla (N) | 234 | 21:00 | 222 | 11:00
| Ishurdi | 236 | 7:00 | 227 | 12:00 | Hathazari | 226 | 18:30 | 218 | 10:00
| Ashuganj | 236 | 20:00 | 225 | 10:00 | Megnaghat | 228 | 22:00 | 218 | 11:00
| Serajganj | 230 | 6:00 | 225 | 12:00 | Fenchuganj | 245 | 21:00 | 235 | 10:00
| Baghabari | 238 | 2:00 | 235 | 11:00 | Siddhirganj | 226 | 21:00 | 212 | 12:00
| Barapukuria | 238 | 6:00 | 230 | 18:30 | Maniknagar | 225 | 21:00 | 210 | 12:00
| Bogra | 227 | 5:00 | 220 | 21:00 | Agargaon | 221 | 15:00 | 205 | 12:00
| Rajshahi | 226 | 16:00 | 217 | 12:00 | Barisal | 250 | 18:30 | 239 | 22:00
| Khulna South | 228 | 7:00 | 221 | 4:00 | AKSML | 222 | 18:00 | 215 | 10:00
| Rampura | 224 | 22:00 | 213 | 12:00 | BSRM | 224 | 21:00 | 216 | 3:00
| Haripur | 225 | 23:00 | 211 | 11:00 | Bibiyana | 243 | 22:00 | 235 | 2:00
| Hasnabad | 220 | 19:30 | 210 | 13:00 | Bhulta | 229 | 19:00 | 213 | 17:00
| Shyampur | 222 | 22:00 | 207 | 12:00 | Ashuganj (S) | 233 | 22:00 | 223 | 12:00
| Aminbazar | 221 | 20:00 | 208 | 10:00 | Kaliakoir | 224 | 19:30 | 210 | 10:00
| Tongi | 224 | 19:30 | 204 | 12:00 | GPH | 222 | 19:30 | 216 | 10:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 137 | 22:00 | 125 | 12:00 | Hathazari | 135 | 0.75 | 130 | 0.41667
| Munsiganj | 137 | 22:00 | 124 | 12:00 | Khulshi | 133 | 0.75 | 128 | 0.125
| Sonargaon | 135 | 21:00 | 124 | 15:00 | Halishahar | 135 | 0.77083 | 128 | 0.41667
| Shyampur | 137 | 22:00 | 126 | 12:00 | Baraulia | 135 | 0.75 | 129 | 0.45833
| Bhulta | 129 | 22:00 | 119 | 11:00 | Sikalbaha | 136 | 18:00 | 130 | 0.375
| Madanganj | 134 | 21:00 | 123 | 12:00 | Dohazari | 135 | 18:30 | 127 | 0.45833
| Shitalakhya | 141 | 22:00 | 127 | 10:00 | Cox'sbazar | 130 | 0.77083 | 121 | 0
| Rahim steal | 136 | 21:00 | 125 | 12:00 | Chandraghona | 136 | 0.75 | 130 | 0.875
| Matuail | 137 | 22:00 | 125 | 12:00 | Kaptai | 134 | 19:00 | 132 | 0.041667
| Ghorasal | 135 | 8:00 | 133 | 11:00 | A. Khaer Stl. | 133 | 0.75 | 129 | 2:00
| Narsinghdi | 131 | 22:00 | 120 | 12:00 | Bakulia | 134 | 0.77083 | 129 | 0.375
| Haripur (SBU) | 136 | 21:00 | 125 | 12:00 | Julda | 136 | 0.75 | 130 | 0.33333
| Ullon | 139 | 22:00 | 128 | 11:00 | TK Chemical | 136 | 0.77083 | 130 | 7:00
| Hasnabad | 137 | 21:00 | 128 | 10:00 | Modern Steel | 134 | 0.77083 | 128 | 0.41667
| Magbazar | 138 | 22:00 | 128 | 12:00 | Shahmirpur | 135 | 0.75 | 130 | 0.41667
| Maniknagar | 136 | 24:00 | 124 | 12:00 | Khagrachhari | 135 | 0.75 | 130 | 0.041667
| Bangabhaban | 136 | 24:00 | 124 | 12:00 | Matarbari | 132 | 0.70833 | 120 | 0.083333
| Narinda | 136 | 24:00 | 124 | 12:00 | Baroiar Hat | 138 | 0.54167 | 128 | 0.041667
| Dhanmondi | 139 | 22:00 | 128 | 11:00 | Rangamati | 135 | 0.75 | 130 | 2:00
| Lalbag | 137 | 22:00 | 123 | 12:00 | Goalpara S/S | 138 | 5:00 | 134 | 12:00
| Madartek | 138 | 22:00 | 128 | 10:00 | Khulna Central S/S | 138 | 0.29167 | 134 | 12:00
| Dhaka University |  |  |  |  | Noapara | 137 | 7:00 | 131 | 1:00
| Fatuiiah | 138 | 0.91667 | 126 | 10:00 | Jessore | 132 | 6:00 | 127 | 18:00
| Mirpur | 135 | 21:00 | 124 | 12:00 | Benapol | 134 | 7:00 | 128 | 1:00
| Kalyanpur | 136 | 21:00 | 125 | 12:00 | Jhenida | 131 | 0.29167 | 124 | 18:30
| Gulshan | 138 | 22:00 | 127 | 12:00 | Bottail | 136 | 5:00 | 130 | 1:00
| Uttara | 135 | 22:00 | 124 | 13:00 | G.K Project | 142 | 0.375 | 139 | 3:00
| Uttara New | 136 | 21:00 | 125 | 12:00 | Faridpur | 136 | 9:00 | 129 | 1:00
| Kamrangirchar | 136 | 21:00 | 123 | 10:00 | Madaripur | 140 | 0.29167 | 133 | 21:00
| Savar | 134 | 21:00 | 121 | 12:00 | Shariyatpur S/S | 140 | 0.66667 | 129 | 2:00
| Bhasantec | 137 | 21:00 | 125 | 12:00 | Gopalganj | 140 | 15:00 | 131 | 1:00
| Agargaon | 139 | 22:00 | 127 | 12:00 | Bagerhat | 139 | 10:00 | 132 | 15:00
| Satmosjid | 138 | 22:00 | 126 | 12:00 | Mongla | 133 | 0.70833 | 129 | 2:00
| Tongi | 139 | 0.8125 | 127 | 12:00 | Satkhira | 138 | 0.29167 | 132 | 4:00
| Kabirpur | 136 | 22:00 | 123 | 11:00 | Gallamari | 138 | 7:00 | 133 | 10:00
| Basundhara | 139 | 22:00 | 127 | 12:00 | Magura | 132 | 6:00 | 122 | 1:00
| Manikganj | 140 | 19:30 | 128 | 2:00 | Norail | 129 | 0.25 | 121 | 1:00
| Joydevpur | 140 | 21:00 | 131 | 12:00 | Chuadanga | 127 | 7:00 | 114 | 1:00
| New Tongi | 138 | 0.8125 | 126 | 12:00 | Barisal(N) | 141 | 15:00 | 133 | 23:00
| Kodda | 137 | 19:00 | 122 | 0.5 | Barisal (S) | 141 | 0.66667 | 133 | 22:00
| Dhamrai | 135 | 22:00 | 127 | 12:00 | Patuakhali(S) | 139 | 0.79167 | 128 | 23:00
| Rajendrapur | 134 | 19:00 | 123 | 16:00 | Bhandaria | 136 | 7:00 | 128 | 3:00
| Valuka | 130 | 7:00 | 115 | 1:00 | Ishurdi | 138 | 7:00 | 134 | 1:00
| Tangail | 134 | 20:00 | 126 | 1:00 | Ruppur Paromanobik | 138 | 5:00 | 135 | 1:00
| Mymensing | 132 | 8:00 | 119 | 1:00 | Natore | 137 | 17:00 | 132 | 12:00
| Kishorganj | 131 | 8:00 | 119 | 1:00 | Bogra | 138 | 5:00 | 129 | 12:00
| Netrokona | 130 | 7:00 | 116 | 1:00 | Noagaon | 132 | 7:00 | 124 | 12:00
| Jamalpur | 139 | 18:30 | 129 | 16:00 | Rajshahi | 136 | 6:00 | 130 | 12:00
| Sherpur | 138 | 8:00 | 127 | 16:00 | Rajshahi New | 137 | 13:00 | 132 | 12:00
| Srimongal | 136 | 7:00 | 133 | 0.041667 | C.Nawabganj | 135 | 17:00 | 128 | 12:00
| Shahjibazar | 135 | 15:00 | 130 | 0.5 | Amnura | 138 | 1:00 | 128 | 12:00
| Fenchuganj | 137 | 21:00 | 133 | 0.66667 | Pabna | 136 | 6:00 | 131 | 1:00
| Khulawara | 135 | 18:00 | 132 | 0.041667 | Shahjadpur | 138 | 17:00 | 135 | 1:00
| Sylhet | 134 | 7:00 | 131 | 0.5 | Serajganj | 135 | 7:00 | 130 | 1:00
| Chatak | 132 | 6:00 | 129 | 17:00 | Niyamatpur | 130 | 6:00 | 121 | 12:00
| Sunamganj | 132 | 8:00 | 129 | 0.041667 | Joypurhat | 134 | 8:00 | 124 | 12:00
| Biani Bazar | 132 | 7:00 | 128 | 0.041667 | Sherpur(Bogura) | 136 | 1:00 | 130 | 12:00
| Comilla(s) | 129 | 6:00 | 124 | 10:00 | Mohastangor | 136 | 7:00 | 128 | 12:00
| Comilla(n) | 137 | 21:00 | 132 | 11:00 | Rangpur | 135 | 6:00 | 121 | 18:30
| Chandpur | 136 | 23:00 | 130 | 1:00 | Lalmonirhat | 135 | 6:00 | 119 | 19:00
| Feni | 137 | 18:00 | 129 | 14:00 | Saidpur | 133 | 6:00 | 121 | 18:30
| Chowmuhani | 135 | 18:30 | 129 | 13:00 | Purbasadipur | 131 | 7:00 | 119 | 18:30
| Ashuganj | 136 | 23:00 | 130 | 2:00 | Thakurgaon | 129 | 5:00 | 120 | 18:00
| Daudkandi | 134 | 21:00 | 126 | 12:00 | Palashbari | 132 | 7:00 | 125 | 18:00
| B.Baria | 132 | 18:30 | 129 | 11:00 | Barapukuria | 138 | 6:00 | 130 | 18:30
| Ramganj | 130 | 23:00 | 124 | 14:00 | Panchagar | 126 | 6:00 | 118 | 18:00
| Chaddagram | 136 | 18:30 | 130 | 10:00 | Joldhaka | 133 | 6:00 | 120 | 18:00
| PHP | 135 | 18:00 | 129 | 10:00 | Kurigram | 132 | 6:00 | 118 | 18:30
| Madanhat | 136 | 18:00 | 131 | 9:00

## L-Curve
Date | 2020-10-22
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 248 | 5774 | 2950 | 8724 |  |  |  | QF-LDC-11
0:30 | 160 | 6497.5 | 3166.5 | 9664 | Date: | 2020-10-22
1:00 | 72 | 7221 | 3383 | 10604
1:30 | 45 | 7118.5 | 3239.5 | 10358
2:00 | 18 | 7016 | 3096 | 10112
2:30 | 47 | 6941.5 | 3059 | 10000.5 | [5 empty] | Gen. at Eve. Peak | 9836 | 9836 MW (19:00 )
3:00 | 76 | 6867 | 3022 | 9889 | [6 empty] | 19:00
3:30 | 111 | 6736.5 | 2980 | 9716.5 | [5 empty] | Gen. at Day Peak | 9034 | 9034 MW (12:00 )
4:00 | 146 | 6606 | 2938 | 9544 | [6 empty] | 12:00
4:30 | 166 | 6537 | 2907.5 | 9444.5 | [5 empty] | Highest Generation | 10604
5:00 | 186 | 6468 | 2877 | 9345 | [6 empty] | 1:00
5:30 | 301 | 6190.5 | 2872.5 | 9063
6:00 | 416 | 5913 | 2868 | 8781
6:30 | 369 | 5771 | 2773 | 8544
7:00 | 322 | 5629 | 2678 | 8307
7:30 | 357.5 | 5612 | 2660.5 | 8272.5
8:00 | 393 | 5595 | 2643 | 8238
8:30 | 475 | 5624 | 2668 | 8292
9:00 | 557 | 5653 | 2693 | 8346
9:30 | 529.5 | 5757 | 2670.5 | 8427.5
10:00 | 502 | 5861 | 2648 | 8509
10:30 | 482 | 5927 | 2652 | 8579
11:00 | 462 | 5993 | 2656 | 8649
11:30 | 435 | 6141.5 | 2700 | 8841.5
12:00 | 408 | 6290 | 2744 | 9034
12:30 | 394 | 6163 | 2759 | 8922
13:00 | 380 | 6036 | 2774 | 8810
13:30 | 392.5 | 5913.5 | 2730.5 | 8644
14:00 | 405 | 5791 | 2687 | 8478
14:30 | 449 | 5763 | 2646 | 8409
15:00 | 493 | 5735 | 2605 | 8340
15:30 | 522 | 5587 | 2602.5 | 8189.5
16:00 | 551 | 5439 | 2600 | 8039
16:30 | 551.5 | 5321.5 | 2613 | 7934.5
17:00 | 552 | 5204 | 2626 | 7830
17:30 | 368.5 | 5630.5 | 2884.5 | 8515
18:00 | 185 | 6057 | 3143 | 9200
18:30 | 162.5 | 6257 | 3261 | 9518
19:00 | 140 | 6457 | 3379 | 9836
19:30 | 47 | 6505 | 3313 | 9818
20:00 | 85 | 6456 | 3296 | 9752 |  |  |  | Executive Engineer
20:30 | 91 | 6419 | 3268.5 | 9687.5 |  |  |  | Network Operation Division
21:00 | 97 | 6382 | 3241 | 9623
21:30 | 110.5 | 6305.5 | 3123.5 | 9429
22:00 | 124 | 6229 | 3006 | 9235 |  |  |  |  | Page 6 of 7
22:30 | 147 | 6131 | 3006 | 9137
23:00 | 170 | 6033 | 3006 | 9039
23:30 | 209 | 5903.5 | 2978 | 8881.5
24:00 | 248 | 5774 | 2950 | 8724
9836 MW (19:00 )
9034 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-10-22 |  | Energy | 219075353
[10 empty] | 2020-10-22 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3618 | 911 | 1951 | 1741 | 650 | 121 | 120 | 0 | 102
0:30 | 3706 | 915 | 1981.5 | 2210.5 | 660.5 | 122 | 197.5 | 0 | 116 | Date: | 2020-10-22
1:00 | 3794 | 919 | 2012 | 2680 | 671 | 123 | 275 | 0 | 130
1:30 | 3813 | 919.5 | 2025 | 2473.5 | 670.5 | 123 | 205.5 | 0 | 128 | [7 empty] | Total Energy | 219.0754 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 3832 | 920 | 2038 | 2267 | 670 | 123 | 136 | 0 | 126 | [7 empty] | Energy not Served | 0
2:30 | 3860.5 | 920 | 2040.5 | 2144.5 | 660 | 123 | 128 | 0 | 124 | [7 empty] | Energy Requirement | 219.0754
3:00 | 3889 | 920 | 2043 | 2022 | 650 | 123 | 120 | 0 | 122
3:30 | 3902.5 | 920 | 2048 | 1843 | 640 | 122 | 120 | 0 | 121 | [6 empty] | Shortage
4:00 | 3916 | 920 | 2053 | 1664 | 630 | 121 | 120 | 0 | 120
4:30 | 3919.5 | 920 | 2023 | 1604 | 620 | 121 | 120 | 0 | 117
5:00 | 3923 | 920 | 1993 | 1544 | 610 | 121 | 120 | 0 | 114
5:30 | 3849 | 920 | 1820 | 1511 | 610 | 121 | 120 | 0 | 112
6:00 | 3775 | 920 | 1647 | 1478 | 610 | 121 | 120 | 0 | 110
6:30 | 3672 | 920 | 1590.5 | 1445 | 580 | 119 | 120 | 0 | 96 |  |  |  |  | Coal
7:00 | 3569 | 920 | 1534 | 1412 | 550 | 117 | 120 | 0 | 82
7:30 | 3555 | 920 | 1500 | 1423 | 550 | 117 | 120 | 0 | 83 |  |  |  | Oil |  |  |  | ,
8:00 | 3541 | 920 | 1466 | 1434 | 550 | 117 | 120 | 0 | 84
8:30 | 3594.5 | 920 | 1489 | 1414 | 550 | 117.5 | 120 | 0 | 82
9:00 | 3648 | 920 | 1512 | 1394 | 550 | 118 | 120 | 0 | 80
9:30 | 3727 | 920 | 1535.5 | 1370 | 530 | 118.5 | 124 | 0 | 96
10:00 | 3806 | 920 | 1559 | 1346 | 510 | 119 | 128 | 0 | 112
10:30 | 3861.5 | 920 | 1643 | 1282 | 505 | 120 | 128 | 0 | 112
11:00 | 3917 | 920 | 1727 | 1218 | 500 | 121 | 128 | 0 | 112
11:30 | 3994 | 920 | 1816.5 | 1246.5 | 500 | 121.5 | 128 | 0 | 109
12:00 | 4071 | 920 | 1906 | 1275 | 500 | 122 | 128 | 0 | 106
12:30 | 3923 | 920 | 1909 | 1277 | 525 | 122.5 | 128 | 0 | 110
13:00 | 3775 | 920 | 1912 | 1279 | 550 | 123 | 128 | 0 | 114
13:30 | 3775 | 920 | 1912 | 1279 | 550 | 123 | 128 | 0 | 114
14:00 | 3775 | 920 | 1912 | 1279 | 550 | 123 | 128 | 0 | 114
14:30 | 3676 | 919.5 | 1814.5 | 1263 | 535 | 124.5 | 124 | 0 | 112
15:00 | 3577 | 919 | 1717 | 1247 | 520 | 126 | 120 | 0 | 110
15:30 | 3564 | 919.5 | 1667 | 1163.5 | 520 | 126 | 120 | 0 | 106
16:00 | 3551 | 920 | 1617 | 1080 | 520 | 126 | 120 | 0 | 102
16:30 | 3425.5 | 920 | 1639 | 1100 | 510 | 125 | 134.5 | 0 | 79
17:00 | 3300 | 920 | 1661 | 1120 | 500 | 124 | 149 | 0 | 56
17:30 | 3312.5 | 920.5 | 1778 | 1522.5 | 520 | 123 | 263.5 | 0 | 75
18:00 | 3325 | 921 | 1895 | 1925 | 540 | 122 | 378 | 0 | 94
18:30 | 3340.5 | 915 | 1922.5 | 2188 | 580 | 121.5 | 352.5 | 0 | 98
19:00 | 3356 | 909 | 1950 | 2451 | 620 | 121 | 327 | 0 | 102
19:30 | 3415 | 910 | 1989 | 2445 | 610 | 119 | 226 | 0 | 104
20:00 | 3431 | 910 | 1958 | 2384 | 650 | 119 | 192 | 0 | 108
20:30 | 3423.5 | 910 | 1953.5 | 2332.5 | 650 | 119 | 192 | 0 | 107
21:00 | 3416 | 910 | 1949 | 2281 | 650 | 119 | 192 | 0 | 106
21:30 | 3377.5 | 910.5 | 1946 | 2174 | 620 | 120 | 172 | 0 | 109
22:00 | 3339 | 911 | 1943 | 2067 | 590 | 121 | 152 | 0 | 112
22:30 | 3409.5 | 911 | 1925.5 | 1904 | 620 | 121 | 136 | 0 | 110
23:00 | 3480 | 911 | 1908 | 1741 | 650 | 121 | 120 | 0 | 108
23:30 | 3549 | 911 | 1929.5 | 1741 | 650 | 121 | 120 | 0 | 105 | Max Temp. in Dhaka |  | 27.7° C
24:00 | 3618 | 911 | 1951 | 1741 | 650 | 121 | 120 | 0 | 102
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
Note on W13: Author:

## Generation
g | 2020-10-22
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 88 | 88 | 88 | 86 | 86 | 86 | 82 | 82 | 83 | 84 | 86 | 87 | 88 | 88 | 91 | 91 | 89 | 87 |  | 86 | 84 | 84 | 84 | 86 | 86 | 86 | 2065484
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 840000
3 | Chattogram TPP-1 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2700000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | [11 empty] | 0 | 8 | 8 | [10 empty] | 0 | 37665
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 1 | 3 | 1 | 3 | 0 |  | 3 | 0 | [12 empty] | 14175
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 204 | 204 | 204 | 204 | 204 | 203 | 203 | 203 | 214 | 203 | 217 | 203 | 205 | 203 | 203 | 209 | 204 |  | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 4874186
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 139 | 139 | 139 | 139 | 139 | 70 | 70 | 70 | 70 | 108 | 139 | 142 | 139 | 104 | 104 | 104 | 103 | 139 |  | 139 | 139 | 139 | 139 | 140 | 140 | 139 | 2913678
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 24 | 68 |  | 34 | 34 |  |  |  |  | 0 | 155390
12 | Hathazari 100 MW peaking PP | [9 empty] | 8 | 8 | 8 | 8 | 8 | [12 empty] | 45552
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [23 empty] | 0 |  |  | 0
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 150 | 160 | 160 | 160 | 155 | 75 | 65 | 65 | 70 | 74 | 118 | 150 | 120 | 70 | 140 | 118 | 98 | 145 |  | 120 | 150 | 150 | 150 | 140 | 145 | 120 | 3223000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 300 | 250 | 145 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 100 | 135 | 145 | 95 | 95 | 95 | 187 |  | 300 | 300 | 300 | 245 | 195 | 80 | 45 | 3680835
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 101 | 100 | 99 | 102 | 100 | 101 | 99 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2404000
23 | Ghorasal TPP Unit-5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2709000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4795036
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1652465
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 126648
33 | Ashuganj 225 MW CCPP | 195 | 201 | 206 | 206 | 206 | 212 | 180 | 181 | 181 | 216 | 179 | 170 | 189 | 190 | 191 | 204 | 170 | 217 |  | 219 | 218 | 220 | 195 | 163 | 154 | 154 | 4642000
34 | Ashuganj 450 MW CCPP(South) | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 320 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 260 | 260 | 260 | 260 | 260 | 260 | 6266000
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 330 | 310 | 275 | 285 | 260 | 260 | 275 | 260 |  | 260 | 280 | 280 | 280 | 260 | 260 | 260 | 6782900
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 139680
36 | Chandpur 150 MW CCPP | 90 | 82 | 90 | 91 | 90 | 81 | 81 | 81 | 82 | 90 | 89 | 90 | 82 | 90 | 80 | 81 | 90 | 80 |  | 90 | 90 | 89 | 89 | 80 | 90 | 90 | 2031330
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 330 | 300 | 300 | 300 | 300 | 360 | 420 | 350 | 320 | 320 | 320 | 320 | 350 |  | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 8394000
41 | Haripur 360MW CCPP(HPL) | 357 | 357 | 357 | 357 | 357 | 283 | 262 | 262 | 302 | 302 | 333 | 354 | 352 | 272 | 272 | 273 | 273 | 340 |  | 358 | 358 | 359 | 359 | 360 | 359 | 359 | 7776000
42 | RPCL 210MW CCPP | 125 | 143 | 156 | 157 | 157 | 158 | 159 | 160 | 144 | 125 | 125 | 121 | 106 | 103 | 103 | 104 | 104 | 105 |  | 104 | 104 | 104 | 104 | 107 | 107 | 127 | 2920280
43
44 | Fenchugonj CCPP Phase-1 | 73 | 73 | 73 | 73 | 73 | 73 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 56 | 73 |  | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 1566000
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1041000
46 | Shajibazar 330 MW CCPP | 158 | 158 | 160 | 159 | 158 | 159 | 156 | 158 | 158 | 158 | 158 | 158 | 158 | 159 | 158 | 159 | 158 | 158 |  | 158 | 157 | 160 | 157 | 156 | 158 | 158 | 3497000
47 | Shahjibazar GTPP Unit- 8 & 9 | 56 | 56 | 56 | 56 | 56 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 1053984
48 | Shahjibazar 86MW PP (Shahjibazar) | 84 | 84 | 84 | 84 | 84 | 30 | 20 | 20 | 20 | 20 | 20 | 20 | 87 | 87 | 87 | 40 | 40 | 87 |  | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 1579200
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 218 | 218 | 218 | 219 | 218 | 184 | 152 | 151 | 152 | 75 | 120 | 140 | 140 | 110 | 100 | 100 | 70 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3632980
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 416000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 243900
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 11 |  | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 246096
55 | Fenchugonj 51 MW PP (Barakatullah) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 14 | 31 | 37 | 37 | 14 | 14 | 45 |  | 45 | 45 | 45 | 47 | 47 | 47 | 47 | 699600
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 24 | 478560
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 280 | 280 | 290 | 290 | 295 | 260 | 270 | 265 | 290 | 290 | 300 | 290 | 290 | 290 | 280 | 285 | 300 |  | 275 | 300 | 290 | 285 | 270 | 270 | 290 | 7008000
| Bibiyana South 400 MW | [8 empty] | 78 | 270 | 185 | 185 | 70 | [13 empty] | 701570
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 36 | 35 | 35 | 35 | 35 | 35 | 35 | 42 | 55 | 55 | 55 | 35 | 35 | 55 |  | 55 | 55 | 55 | 55 | 55 | 35 | 17 | 1103202
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 |  |  |  | 20 | 407712
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 10 |  | 10 | 10 | 12 | 19 | 19 | 19 | 19 | 406008
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 22 | 22 | 20 |  | 20 | 20 | 22 | 22 | 20 | 22 | 20 | 434916
63 | Impoprt (Tripura) | 130 | 126 | 122 | 120 | 114 | 110 | 82 | 84 | 80 | 112 | 112 | 106 | 114 | 104 | 110 | 102 | 56 | 94 |  | 102 | 104 | 108 | 106 | 112 | 108 | 102 | 2595840
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 41 | 38 | 35 | 12 | 7 | 6 | 6 | 5 | 17 | 11 | 8 | 11 | 25 | 20 |  | 23 | 27 | 21 | 12 | 40 | 42 | 42 | 583200
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 20 |  | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 472752
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | [6 empty] | 11 | 11 | 11 | 11 | 11 | 181800
67 | Jangalia 33MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 15 | 15 | 15 | 15 | 16 | 16 | 16 | 16 | [11 empty] | 0 | 181200
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 15 | 15 | 15 | 15 | 15 | 15 | 20 | 15 | 16 | 9 | 9 | 9 |  | 20 | 20 | 22 | 22 | 22 | 22 | 20 | 429970
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 23 |  | 31 | 31 | 31 | 31 | 31 | 32 | 32 | 711000
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 814600
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 8 | 17 | 17 | 17 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 758800
73 | Ghorashal 108MW PP (Regent) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 71 | 71 | 72 | 72 | 72 | 72 | 72 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 1704090
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [11 empty] | 17 |  | 0 | 234840
| Chowmuhani 113 MW | 113 | 107 | 107 | 112 | 113 | 110 | 104 | 104 | 104 | 104 | 80 | 80 | 55 | 55 | 55 | 35 | 35 | 65 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2261280
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 197760
78 | Gazipur 52 MW PP | [26 empty] | 0
79 | Kodda 150MW PP | 48 | 16 | [14 empty] | 5 | 82 |  | 78 | 48 | 48 | 48 | 32 |  | 0 | 396480
80 | Jamalpur 95 MW PP(Powerpac) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 25 | 25 | 25 | 25 | 25 | 595200
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 |  |  | 191563
| Gazipur 100 MW PP | 34 | [15 empty] | 2 | 53 |  | 38 | 35 | 17 | 17 |  |  | 0 | 229200
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 3601
| Jodiac Power | 36 | 36 | 36 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 19 | 35 | 36 | 34 | 45 |  | 54 | 54 | 54 | 54 | 54 | 17 | 17 | 0
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | 97 | 97 | 97 | 97 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 48 | 48 | 48 | 55 |  | 92 | 97 | 97 | 97 | 97 | 97 | 30 | 1760952
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [17 empty] | 13 | [7 empty] | 0 | 46680
86 | Meghnaghat CCPP(Summit) | 235 | 265 | 270 | 270 | 270 | 245 | 245 | 265 | 270 | 295 | 275 | 300 | 265 | 285 | 265 | 265 | 285 | 255 |  | 280 | 285 | 275 | 275 | 250 | 270 | 270 | 6514269
87 | Meghnaghat 100 MW(IEL) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 35 | 30 | 87 | 93 | 93 | 100 | 656640
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 487680
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 20 | [16 empty] | 10 | [7 empty] | 0 | 52440
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 50 | 50 | 50 | 10 | 10 | 10 | 10 | 10 | 22 | 46 | 50 | 50 | 50 | 20 | 20 | 35 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 968976
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 51 | 51 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1120389
94 | Gagnagar 102 MW PP (Digital Power) | 16 | 16 | 16 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 16 | 0 | 244512
95 | Patenga 50MW PP (Baraka) | 50 | [10 empty] | 11 | 12 | 12 | 12 | 12 | 12 | 21 |  | 48 | 19 | 19 |  |  |  | 0 | 224640
96 | Chattogram 108 MW PP (ECPV) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | [11 empty] | 0 | 0 |  |  |  |  | 0 | 50880
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 50 | 55 | 55 | 55 | 55 | 30 | 30 | 32 |  | 40 | 48 | 55 | 55 | 55 | 15 | 0 | 1013546
100 | Manikganj 55 MW PP (Northern) | 55 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 55 |  | 55 | 55 | 55 | 55 | 17 | 17 | 0 | 627876
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 70 | 70 | 70 | 70 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2589381
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 |  | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [10 empty] | 4200
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 17 | [15 empty] | 54 |  | 54 | 17 | 17 | 17 | 17 |  | 17 | 252000
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 190 | 190 | 190 | 200 | 170 | 150 | 130 | 130 | 130 | 100 | 100 | 100 | 100 | 100 | 100 | 60 | 60 | 100 |  | 200 | 200 | 200 | 200 | 200 | 200 | 160 | 3585600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 140 | 149 | 140 | 102 | 102 | 100 | 100 | 102 | 100 | 100 | 102 | 108 | 138 | 149 | 149 | 145 | 132 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 126 | 3110830
115 | Juldah 100 MW PP Unit-3 (Acorn) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 526080
116 | Chandpur 200MW (Desh energy) | [17 empty] | 8 | [8 empty] | 28800
117 | Ashuganj 150MW PP (Midland) | 148 | 150 | 150 | 80 | 50 | 50 | 50 | 50 | 50 | 10 | 10 | 10 | 10 | 10 | 15 | 32 | 40 | 66 |  | 143 | 150 | 150 | 150 | 150 | 150 | 10 | 2003927
118 | Bibiyana-III 400 MW CCPP | 430 | 428 | 428 | 427 | 427 | 429 | 431 | 430 | 425 | 421 | 425 | 419 | 424 | 423 | 426 | 425 | 216 |  |  | 0 | 0 | 0 | 15 | 15 | 144 | 253 | 7743000
| Jamalpur 115 MW PP (United) | 115 | 115 | 85 | 45 | 35 | 35 | 35 | 35 | [8 empty] | 2 | 31 |  | 55 | 55 | 55 | 35 | 35 |  | 0 | 877200
| Anwara 300 MW PP (United) | 161 | 161 | 161 | 125 | 125 | 108 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 52 | 52 | 122 |  | 122 | 122 | 122 | 125 | 125 | 125 | 54 | 2458909
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 100 |  | 100 | 100 | 100 | 100 | 100 | 60 | 100 | 2296320
120 | Eastern Zone Total | 7221 | 7016 | 6867 | 6606 | 6468 | 5913 | 5629 | 5595 | 5653 | 5861 | 5993 | 6290 | 6036 | 5791 | 5735 | 5439 | 5204 | 6057 |  | 6457 | 6505 | 6456 | 6382 | 6229 | 6033 | 5774 | 148294662
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 115 | 66 | 28 | [13 empty] | 11 | 74 |  | 83 | 83 | 66 | 66 |  |  | 0 | 536640
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 16
| Khulna 225 MW CCPP | 165 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 3077760
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | [6 empty] | 17 | 35 |  | 35 | 35 | 35 | 35 | 17 | 17 | 0 | 560640
130
131
132
133
| Barisal 110 MW PP (Summit ) | 64 | 32 | 16 | [14 empty] | 64 |  | 48 | 48 | 48 | 16 | 16 | 10 | 0 | 356448
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 95 | 95 | 95 | 95 | 44 | 44 | 44 | 20 | 22 | 22 | 22 | 43 | 43 | 43 | 20 | 21 | 22 | 50 |  | 75 | 75 | 88 | 95 | 97 | 97 | 96 | 1408
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 28 | 23 | 17 | 18 | 17 | 9 | 10 | 14 | 9 | 11 | 12 | 13 | 14 | 14 | 14 | 8 | 6 | 12 |  | 16 | 17 | 14 | 18 | 18 | 20 | 20 | 356260
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 8640
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | [16 empty] | 8 | [7 empty] | 0 | 60750
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 919 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 919 | 920 | 920 | 921 |  | 909 | 910 | 910 | 910 | 911 | 911 | 911 | 22020364
147 | Bheramara 410 MW CCPP | 225 | 240 | 250 | 260 | 260 | 290 | 225 | 225 | 270 | 240 | 290 | 340 | 330 | 295 | 295 | 295 | 295 | 325 |  | 330 | 325 | 320 | 320 | 315 | 320 | 335 | 7081920
148 | Payra 1320 MW | 520 | 520 | 500 | 480 | 460 | 460 | 400 | 400 | 400 | 360 | 350 | 350 | 400 | 390 | 370 | 370 | 350 | 390 |  | 470 | 460 | 500 | 500 | 440 | 500 | 500 | 11404600
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 151 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3692600
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 139 | 139 | 139 | 142 | 149 | 163 | 158 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 137 |  | 167 | 167 | 167 | 167 | 167 | 167 | 165 | 3720609
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 130 | 130 | 150 | 160 | 170 | 175 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 155 |  | 153 | 152 | 152 | 163 | 161 | 157 | 158 | 3954264
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 326 | 347 | 358 | 357 | 350 | 298 | 283 | 298 | 307 | 334 | 398 | 414 | 399 | 375 | 340 | 342 | 368 | 376 |  | 391 | 400 | 374 | 367 | 345 | 306 | 330 | 8478640
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 20 | 22 | 22 | 21 | 22 | 22 | 22 |  | 22 | 22 | 22 | 21 | 21 | 22 | 22 | 493200
163 | Bogura 20 MW PP (Energyprima) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 238896
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 218862
165 | Amnura 50 MW PP(Sinha) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  |  |  |  | 20 |  | 20 | 20 | 20 | 20 | 20 |  | 0 | 376220
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [17 empty] | 18 | [8 empty] | 26533
169 | Natore 52 MW PP (Rajlanka) | [17 empty] | 10 |  | 25 | 25 | 8 |  |  |  | 0 | 80160
170 | Chapainawabganj 100 MW Peaking PP | 46 | [16 empty] | 90 |  | 95 | 24 | 24 | 24 |  |  | 0 | 280928
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 35 | [15 empty] | 16 |  | 70 | 70 | 70 | 35 |  |  | 0 | 448032
172 | Confidence Power Bogura Unit-1 113 MW | 109 | 109 | 109 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 72 |  | 100 | 109 | 109 | 109 | 109 | 109 | 70 | 1776576
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 84 | 72 | 72 | 68 | 69 | 71 | 69 | 69 | 67 | 65 | 38 | 36 | 38 | 40 | 40 | 40 | 35 | 57 |  | 79 | 80 | 78 | 84 | 78 | 79 | 55 | 1494720
177 | Sympa Solar Power 8MW | [6 empty] | 1 | 2 | 3 | 5 | 5 | 5 | 5 | 5 | 3 | 2 | 0 | [9 empty] | 35021
178
178