## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-10-29 | Thursday
|  |  | Date (day): | 2020-10-29 |  | Thursday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13840.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14942 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-10-28 | 2020-10-29 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 150 | 150 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 115 | 115 | 115 | 75 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 200 | 200 | 165 |  | Gas shortage
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 60 | 78 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 32 | 32 | 68 | 68 | 40 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under S/D for dust in gas.
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 283 | 285 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 100 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 260 | 275 | 305 | 305
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 97 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 40 | 40 | 40 |  | 15 | Engine problem
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 50 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19 |  | 3 | Engine problem
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 155 | 130 | 200 | 200
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 102 | 102 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 150 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 46 | 55 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 51 | 51 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 245 | 300 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 16 | 149 | 134 | 134 |  | 15 | Engine problem
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 88 | 88 | 88 | 88 |  | 17 | Engine problem
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 2286 | 3052 | 3590 | 3948 | 622 | 1392
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 115 | 115 | 120 | 120 | 60 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 8 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 157 | 158 | 160 | 160 | 70 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 230 | 204 | 221 | 221
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 139 | 104 | 145 | 145
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 102 | 102
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 22 | 22 | 22 | 22
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 20 | 20 | 20
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 16 | 8 | 30
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 90 | 90 | 90 |  | 18 | Engine problem
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 122 | 162 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 53 | 54 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 1031 | 1205 | 1752 | 1749 | 310 | 116
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 80 | 80 | 80 | 80 | 49 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 |  | 134 | Under maint
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 182 | 188 | 225 | 225 |  |  | FGMO
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 275 | 250 | 360
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 310 | 350 | 350 |  |  | FGMO
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 29 | 29 | 29 | 16 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 130 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 25 | 50
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 74 | 75 | 75 | 75 |  | 68 | ST under maint.
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 164 | 164
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 130 | 160 | 163 | 172
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 52 | 25 | 52
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 20 | 20 | 20 |  | 5 | Engine problem
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 34 | 17 | 114
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 36 | 113 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1192 | 1585 | 1808 | 2276 | 437 | 215
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 102 | 103 | 150 | 150 | 52 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 17 | 25 | 25 | 25 |  | 70 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 50 | 180 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
|  | Mymensingh PV 50 MW Solar PP |  | Solar | IPP | 0 | 50 MW | 50 MW | 46 | 0 | 40 | 0
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 353 | 445 | 553.6 | 512 | 52 | 70
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 84 | 87 | 86 | 86
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Unit-4 under shut down
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 |  | 54 | STG under maint.
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 159 | 156 | 160 | 160 |  | 170 | GT-2 S/D due to gas shortage.
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 11 | 53 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 5 | 50 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 63 | 51 | 65 | 65 |  |  | FGMO
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 84 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 178 | 170 | 180 | 200
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 310 | 341 | 341 |  |  | FGMO
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 403 | 401 | 400 | 400
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 9 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 268 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1746 | 1564 | 1617 | 1637 | 0 | 284
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 932 | 932 | 938 | 938
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 99 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 16 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 220 | 220
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 345 | 345 | 410 | 410
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 90 | 105 | 105 | 105
| 108 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Bhola Nutan Biddut BD LTD (GAS) |  | Gas/HSD | IPP | 0 | 220 MW | 220 MW | 0 | 0 | 0 | 0
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1367 | 1537 | 1978 | 2134 | 0 | 0
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 64 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 16 | 27 | 33 | 33
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 86 | 92 | 95 | 95
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 470 | 570 | 500 | 530
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 572 | 753 | 738 | 768 | 0 | 194
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 20 | 20 | 20 |  | 30 | Engine problem
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 50 | 50
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 182 | 155 | 225 | 225 |  |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 193 | 161 | 220 | 220 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 401 | 419 | 414 | 414 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 32
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 18 | 18 | 18 |  | 4 | Engine problem
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 10 | 10 | 10 | 10
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 24 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 35 | 113 | 113
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 109 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 816 | 992 | 1546 | 1668 | 431 | 34
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 149 | 150 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 98 | 100 | 100 |  | 13
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 155 | 248 | 258 | 250 | 294 | 53
|  | Total |  |  |  |  | 20383 | 19892 | 9518 | 11381 | 13840.6 | 14942 | 2146 | 2358
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9103.1922 | 10885 | 13237.4072 | 14290.8066
| A. |  | 2020-10-28 | (Yesterday) |  |  |  |  | Wednesday
| 1 | Highest Generation : |  |  | 11381 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
| 2 | Minimum Generation : |  |  | 7680 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11381 | MW
| 3 | Day peak Generation : |  |  | 9518 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10885 | MW
| 4 | Evening peak Generation : |  |  | 11381 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 227.8844 | MKWHr | By Solar | 0.51874 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 137.3931 | MKWHr |  | By Oil: | 43.9044 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 16.6976 | MKWHr |  | By Hydro: | 3.7595 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2146 | MW | Dhaka | 3966 | 3966 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2358 | MW | Chittagong | 1097 | 1097 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4504 | MW | Khulna | 1263 | 1263 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1147.44 | MMCFD |  |  | Rajshahi | 1078 | 1078 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 160892320.16 | ii) Oil : | Taka | 298530791.18 | Comilla | 1048 | 1048 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 77088950 | Total | Taka | 536512061.34 | Mymensingh | 898 | 898 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.015 | MKWHr. | Sylhet | 593 | 593 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 48 | MW (E to W) at | 19:30 | hrs | Barisal | 298 | 298 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -3 | MW at | 20:00 | hrs | Rangpur | 644 | 644 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 33.4° C |  |  | Total | 10885 | 10885 |  | 0
| B. |  | 2020-10-29 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 33.7° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 11800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14942 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 9600 | MW
| 4 | Reserve(Generation end) |  |  |  | 3142 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 236.2742 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7802 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.3462 | MKWHr. | ii) HVDC Flow at Peak Time |  | 932 | MW at | 19:30 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.265 | MKWHr. | iii) Maximum HVDC Flow : |  | 933 | MW at | 14:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 103.98 |  | (b) Today: | 103.97 |  | (c) Rule Curve: |  | 108.7
.

## YesterdayGen
2020-10-28
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Mymensingh PV 50 MW Solar PP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 150 | 115 | 200 | 52 | 0 | 0 | 302 |  | 0 | 320 | 270 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 31 | 33 | 33 | 0 | 0 | 85 | 70 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 40 | 19 | 42 | 0 | 80 | 0 | 260 | 270 | 218 | 8 | 73 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 138 | 106 | 17 | 22 | 0 | 86 | 30 | 50 | 50 | 110 | 159 | 64 | 84 | 0 | 204 | 18 | 0 | 10 | 295 | 24 | 11 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 22 | 0 | 30 | 400 | 115 | 105 | 0 | 0 | 161 | 17 | 0 | 0 | 65 | 100 | 0 | 104 | 0 |  | 931 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 2 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 183 | 0 | 95 | 0 | 187 | 0 | 380 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 570 | 0 | 0 |  | 6217 | 2970 | 9187 | 4098 | 931 | 1911 | 1234 | 720 | 155 | 0 | 138 | 0 | 0 | 103.98
2:00 | 0 | 0 | 150 | 115 | 200 | 52 | 0 | 0 | 302 |  | 0 | 380 | 275 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 16 | 25 | 31 | 33 | 33 | 0 | 0 | 83 | 70 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 0 | 80 | 0 | 260 | 270 | 218 | 8 | 72 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 138 | 107 | 17 | 22 | 0 | 86 | 30 | 50 | 50 | 110 | 158 | 64 | 84 | 0 | 204 | 18 | 0 | 10 | 275 | 24 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 115 | 70 | 0 | 0 | 87 | 17 | 0 | 0 | 35 | 100 | 0 | 104 | 0 |  | 931 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 2 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 183 | 0 | 94 | 0 | 187 | 0 | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 0 | 0 |  | 5978 | 2882 | 8860 | 4087 | 931 | 1943 | 898 | 710 | 153 | 0 | 138 | 0 | 0 | 103.98
3:00 | 0 | 0 | 150 | 115 | 200 | 52 | 0 | 0 | 302 |  | 0 | 380 | 250 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 25 | 31 | 33 | 33 | 0 | 0 | 84 | 70 | 115 | 0 | 0 | 204 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 0 | 80 | 0 | 260 | 270 | 219 | 8 | 74 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 134 | 108 | 17 | 22 | 0 | 86 | 30 | 50 | 50 | 110 | 159 | 40 | 60 | 0 | 204 | 18 | 0 | 10 | 280 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 115 | 70 | 0 | 0 | 87 | 17 | 0 | 0 | 35 | 100 | 0 | 47 | 0 |  | 931 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 2 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 160 | 0 | 95 | 0 | 165 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 0 | 0 |  | 5757 | 2817 | 8574 | 3964 | 931 | 1909 | 772 | 710 | 154 | 0 | 134 | 0 | 0 | 103.98
4:00 | 0 | 0 | 151 | 115 | 200 | 52 | 0 | 0 | 315 |  | 0 | 350 | 265 | 0 | 0 | 0 | 0 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 31 | 33 | 33 | 0 | 0 | 85 | 70 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 0 | 80 | 0 | 265 | 270 | 205 | 8 | 74 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 130 | 107 | 17 | 22 | 0 | 86 | 30 | 22 | 20 | 110 | 158 | 40 | 20 | 0 | 204 | 18 | 0 | 10 | 290 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 115 | 70 | 0 | 0 | 87 | 17 | 0 | 0 | 35 | 100 | 0 | 34 | 0 |  | 931 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 2 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 148 | 0 | 78 | 0 | 155 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 0 |  | 5635 | 2696 | 8331 | 3901 | 931 | 1715 | 799 | 700 | 155 | 0 | 130 | 0 | 0 | 103.98
5:00 | 0 | 0 | 150 | 115 | 200 | 52 | 0 | 0 | 302 |  | 0 | 350 | 275 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 28 | 33 | 33 | 0 | 0 | 87 | 70 | 115 | 0 | 0 | 204 | 0 | 138 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 0 | 80 | 0 | 260 | 270 | 180 | 8 | 80 | 29 | 5 | 0 | 10 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 128 | 107 | 17 | 22 | 0 | 86 | 30 | 11 | 10 | 110 | 159 | 40 | 10 | 0 | 177 | 18 | 0 | 10 | 285 | 24 | 3 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 115 | 70 | 0 | 0 | 88 | 17 | 0 | 0 | 35 | 100 | 0 | 19 | 0 |  | 930 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 2 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 78 | 0 | 156 | 0 | 324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 |  | 5467 | 2675 | 8142 | 3825 | 930 | 1657 | 795 | 650 | 157 | 0 | 128 | 0 | 0 | 103.98
6:00 | 0 | 0 | 150 | 115 | 200 | 12 | 0 | 0 | 302 |  | 0 | 350 | 240 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 28 | 33 | 33 | 3 | 0 | 88 | 70 | 115 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 38 | 0 | 80 | 0 | 260 | 270 | 180 | 8 | 73 | 29 | 5 | 0 | 10 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 112 | 109 | 17 | 22 | 0 | 86 | 30 | 11 | 10 | 110 | 159 | 40 | 10 | 0 | 177 | 18 | 0 | 10 | 280 | 24 | 5 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 85 | 88 | 0 | 0 | 34 | 17 | 0 | 0 | 35 | 100 | 0 | 17 | 0 |  | 931 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 2 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 58 | 0 | 155 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 0 | 0 |  | 5163 | 2580 | 7743 | 3684 | 931 | 1553 | 695 | 610 | 158 | 0 | 112 | 0 | 0 | 103.98
7:00 | 0 | 0 | 150 | 115 | 200 | 12 | 0 | 0 | 302 |  | 0 | 320 | 280 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 8 | 25 | 28 | 33 | 33 | 16 | 0 | 89 | 70 | 115 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 35 | 0 | 80 | 0 | 270 | 270 | 188 | 8 | 86 | 24 | 5 | 0 | 10 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 94 | 107 | 17 | 22 | 0 | 87 | 30 | 11 | 10 | 110 | 158 | 40 | 10 | 0 | 177 | 18 | 0 | 10 | 290 | 24 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 305 | 55 | 88 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 60 | 0 | 17 | 5 |  | 931 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 2 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 46 | 0 | 155 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 460 | 0 | 0 |  | 5060 | 2620 | 7680 | 3725 | 931 | 1569 | 585 | 610 | 159 | 0 | 94 | 7 | 0 | 109.98
8:00 | 0 | 0 | 150 | 115 | 200 | 12 | 0 | 0 | 303 |  | 0 | 320 | 285 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 28 | 33 | 33 | 16 | 0 | 88 | 70 | 115 | 0 | 0 | 217 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 7 | 0 | 80 | 0 | 285 | 270 | 198 | 8 | 81 | 24 | 5 | 0 | 10 | 0 | 0 | 0 | 19 | 11 | 33 | 15 | 108 | 106 | 17 | 22 | 1 | 87 | 30 | 11 | 10 | 110 | 158 | 40 | 10 | 0 | 177 | 18 | 0 | 10 | 300 | 24 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 314 | 55 | 88 | 0 | 2 | 0 | 17 | 0 | 0 | 0 | 60 | 0 | 17 | 19 |  | 930 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 2 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 141 | 0 | 46 | 0 | 166 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 460 | 0 | 0 |  | 5126 | 2658 | 7784 | 3809 | 930 | 1554 | 590 | 609 | 158 | 0 | 108 | 26 | 0 | 109.98
9:00 | 0 | 0 | 150 | 115 | 200 | 32 | 0 | 0 | 303 |  | 0 | 320 | 265 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 22 | 33 | 33 | 32 | 0 | 88 | 70 | 115 | 0 | 0 | 204 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 8 | 19 | 2 | 0 | 80 | 0 | 260 | 270 | 180 | 8 | 80 | 24 | 5 | 0 | 30 | 0 | 0 | 0 | 19 | 11 | 33 | 15 | 112 | 104 | 17 | 22 | 2 | 87 | 30 | 11 | 5 | 110 | 158 | 65 | 82 | 0 | 192 | 18 | 0 | 10 | 310 | 24 | 8 | 0 | 15 | 0 | 0 | 0 | 0 | 4 | 11 | 22 | 0 | 0 | 352 | 55 | 88 | 0 | 3 | 65 | 17 | 0 | 0 | 11 | 100 | 0 | 27 | 38 |  | 929 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 2 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 157 | 0 | 46 | 0 | 165 | 0 | 307 | 53 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 460 | 0 | 0 |  | 5554 | 2662 | 8216 | 3891 | 929 | 1627 | 833 | 609 | 158 | 0 | 112 | 57 | 0 | 109.98
10:00 | 0 | 0 | 150 | 115 | 200 | 32 | 0 | 0 | 304 |  | 0 | 320 | 285 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 21 | 33 | 33 | 52 | 0 | 88 | 70 | 115 | 0 | 0 | 205 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 17 | 3 | 0 | 80 | 0 | 265 | 270 | 216 | 8 | 81 | 24 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 15 | 116 | 102 | 17 | 22 | 2 | 86 | 30 | 11 | 5 | 110 | 158 | 63 | 82 | 0 | 178 | 18 | 0 | 10 | 310 | 24 | 8 | 0 | 110 | 0 | 0 | 17 | 0 | 16 | 16 | 22 | 0 | 0 | 353 | 67 | 88 | 0 | 4 | 71 | 17 | 0 | 0 | 36 | 100 | 0 | 97 | 45 |  | 931 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 162 | 0 | 45 | 0 | 160 | 0 | 344 | 53 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 460 | 0 | 0 |  | 5989 | 2699 | 8688 | 3915 | 931 | 1678 | 1210 | 609 | 158 | 0 | 116 | 71 | 0 | 109.98
11:00 | 0 | 0 | 150 | 115 | 200 | 32 | 0 | 0 | 303 |  | 0 | 320 | 280 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 21 | 33 | 33 | 52 | 0 | 89 | 70 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 17 | 2 | 0 | 80 | 0 | 265 | 270 | 186 | 8 | 81 | 24 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 15 | 120 | 101 | 17 | 22 | 2 | 83 | 30 | 11 | 5 | 110 | 159 | 63 | 82 | 0 | 178 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 205 | 0 | 0 | 50 | 0 | 16 | 20 | 22 | 0 | 0 | 402 | 115 | 88 | 0 | 5 | 71 | 29 | 0 | 0 | 36 | 100 | 0 | 104 | 49 |  | 931 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 165 | 0 | 63 | 0 | 175 | 0 | 345 | 53 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 460 | 0 | 0 |  | 6223 | 2737 | 8960 | 3951 | 931 | 1666 | 1444 | 609 | 159 | 0 | 120 | 80 | 0 | 109.98
12:00 | 0 | 0 | 150 | 115 | 200 | 32 | 0 | 0 | 283 |  | 0 | 300 | 260 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 21 | 33 | 33 | 51 | 0 | 87 | 70 | 115 | 0 | 0 | 230 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 17 | 2 | 0 | 80 | 0 | 260 | 270 | 182 | 8 | 74 | 26 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 15 | 130 | 102 | 17 | 22 | 1 | 84 | 30 | 11 | 5 | 110 | 159 | 63 | 82 | 0 | 178 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 245 | 0 | 0 | 50 | 0 | 16 | 19 | 22 | 0 | 0 | 403 | 115 | 88 | 0 | 5 | 122 | 53 | 0 | 0 | 36 | 100 | 268 | 104 | 46 |  | 932 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 182 | 0 | 86 | 0 | 193 | 0 | 401 | 90 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 470 | 0 | 0 |  | 6608 | 2910 | 9518 | 4312 | 932 | 1716 | 1575 | 619 | 157 | 0 | 130 | 77 | 0 | 109.98
13:00 | 0 | 0 | 150 | 115 | 200 | 32 | 0 | 0 | 278 |  | 0 | 290 | 275 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 16 | 33 | 33 | 51 | 0 | 87 | 70 | 115 | 0 | 0 | 206 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 6 | 50 | 12 | 5 | 0 | 80 | 0 | 270 | 355 | 194 | 8 | 75 | 26 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 15 | 134 | 100 | 17 | 22 | 2 | 85 | 30 | 14 | 5 | 110 | 157 | 62 | 82 | 0 | 178 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 245 | 0 | 0 | 55 | 0 | 17 | 6 | 22 | 0 | 26 | 404 | 115 | 88 | 0 | 4 | 140 | 39 | 0 | 0 | 40 | 100 | 100 | 104 | 24 |  | 932 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 195 | 0 | 87 | 0 | 193 | 0 | 409 | 90 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 480 | 0 | 0 |  | 6543 | 2947 | 9490 | 4232 | 932 | 1728 | 1636 | 629 | 157 | 0 | 134 | 42 | 9490 | 109.98
14:00 | 0 | 0 | 150 | 115 | 200 | 32 | 0 | 0 | 289 |  | 0 | 300 | 265 | 0 | 2 | 0 | 0 | 0 | 75 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 16 | 0 | 33 | 51 | 0 | 87 | 70 | 115 | 0 | 0 | 204 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 46 | 50 | 14 | 4 | 0 | 80 | 0 | 260 | 315 | 184 | 8 | 75 | 29 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 15 | 138 | 101 | 17 | 22 | 2 | 85 | 30 | 14 | 5 | 110 | 159 | 63 | 82 | 0 | 177 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 245 | 0 | 0 | 96 | 0 | 50 | 17 | 22 | 0 | 71 | 404 | 115 | 88 | 0 | 3 | 142 | 54 | 0 | 0 | 105 | 100 | 267 | 104 | 43 |  | 933 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 169 | 0 | 85 | 0 | 171 | 0 | 335 | 90 | 0 | 0 | 0 | 6 | 0 | 4 | 35 | 480 | 0 | 0 |  | 6759 | 2790 | 9549 | 4039 | 933 | 1673 | 1910 | 630 | 157 | 0 | 138 | 69 | 0 | 103.98
15:00 | 0 | 0 | 150 | 115 | 200 | 32 | 0 | 0 | 294 |  | 0 | 300 | 255 | 0 | 30 | 15 | 0 | 0 | 73 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 20 | 0 | 33 | 51 | 0 | 87 | 70 | 115 | 0 | 0 | 205 | 0 | 139 | 0 |  | 0 | 0 | 17 | 0 | 51 | 50 | 19 | 2 | 0 | 80 | 0 | 275 | 300 | 190 | 8 | 75 | 29 | 5 | 0 | 43 | 0 | 0 | 0 | 0 | 11 | 33 | 15 | 142 | 100 | 17 | 22 | 1 | 82 | 30 | 11 | 5 | 110 | 158 | 60 | 82 | 0 | 184 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 245 | 0 | 0 | 100 | 0 | 52 | 11 | 22 | 0 | 118 | 404 | 115 | 88 | 0 | 2 | 142 | 54 | 0 | 0 | 113 | 100 | 0 | 104 | 31 |  | 933 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 167 | 0 | 88 | 0 | 165 | 0 | 410 | 90 | 0 | 0 | 0 | 51 | 0 | 3 | 90 | 490 | 0 | 0 |  | 6645 | 3041 | 9686 | 3902 | 933 | 1738 | 2109 | 640 | 157 | 17 | 142 | 48 | 0 | 103.98
16:00 | 0 | 0 | 150 | 115 | 200 | 32 | 0 | 0 | 306 |  | 0 | 300 | 260 | 0 | 30 | 40 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 20 | 9 | 33 | 51 | 0 | 86 | 70 | 115 | 0 | 0 | 205 | 0 | 104 | 0 |  | 0 | 0 | 17 | 0 | 17 | 50 | 19 | 3 | 0 | 80 | 0 | 275 | 350 | 179 | 8 | 72 | 29 | 5 | 0 | 43 | 0 | 0 | 0 | 0 | 11 | 33 | 18 | 140 | 101 | 17 | 22 | 0 | 84 | 30 | 14 | 5 | 110 | 159 | 60 | 82 | 0 | 184 | 18 | 0 | 9 | 290 | 24 | 11 | 0 | 245 | 0 | 0 | 80 | 0 | 50 | 7 | 22 | 0 | 128 | 403 | 115 | 88 | 0 | 1 | 142 | 54 | 0 | 0 | 110 | 100 | 0 | 104 | 14 |  | 932 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 155 | 0 | 90 | 0 | 157 | 0 | 320 | 90 | 0 | 0 | 0 | 76 | 0 | 2 | 70 | 500 | 0 | 0 |  | 6558 | 2953 | 9511 | 3825 | 932 | 1663 | 2095 | 650 | 156 | 26 | 140 | 24 | 0 | 103.98
17:00 | 0 | 0 | 150 | 115 | 200 | 32 | 0 | 0 | 307 |  | 0 | 310 | 255 | 0 | 30 | 55 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 18 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 20 | 33 | 33 | 51 | 0 | 87 | 70 | 115 | 0 | 0 | 205 | 0 | 70 | 0 |  | 0 | 8 | 17 | 0 | 17 | 50 | 19 | 7 | 0 | 80 | 0 | 275 | 295 | 179 | 8 | 75 | 29 | 5 | 0 | 43 | 0 | 0 | 0 | 0 | 11 | 33 | 15 | 134 | 102 | 17 | 22 | 0 | 86 | 30 | 14 | 5 | 110 | 158 | 40 | 10 | 0 | 137 | 18 | 0 | 9 | 290 | 24 | 11 | 0 | 245 | 0 | 0 | 60 | 0 | 52 | 0 | 22 | 0 | 132 | 402 | 115 | 88 | 0 | 0 | 105 | 54 | 0 | 0 | 84 | 100 | 0 | 104 | 1 |  | 932 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 8 | 5 | 0 | 0 | 19 | 16 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 150 | 0 | 92 | 0 | 150 | 0 | 314 | 105 | 0 | 0 | 0 | 56 | 0 | 0 | 35 | 460 | 0 | 0 |  | 6285 | 2810 | 9095 | 3607 | 932 | 1603 | 2004 | 610 | 157 | 47 | 134 | 1 | 0 | 103.98
18:00 | 0 | 0 | 140 | 115 | 200 | 32 | 0 | 0 | 306 |  | 0 | 310 | 255 | 25 | 30 | 55 | 0 | 0 | 0 | 0 | 50 | 102 | 120 | 100 | 0 | 0 | 0 | 54 | 55 | 0 | 0 | 25 | 20 | 33 | 33 | 51 | 0 | 87 | 70 | 115 | 0 | 15 | 205 | 0 | 113 | 0 |  | 0 | 8 | 102 | 40 | 65 | 50 | 20 | 3 | 0 | 80 | 0 | 275 | 310 | 179 | 8 | 70 | 29 | 5 | 0 | 43 | 0 | 0 | 25 | 0 | 11 | 33 | 15 | 162 | 104 | 17 | 22 | 0 | 86 | 30 | 50 | 29 | 110 | 158 | 64 | 84 | 0 | 170 | 18 | 0 | 9 | 250 | 24 | 3 | 0 | 260 | 0 | 0 | 110 | 0 | 72 | 0 | 22 | 30 | 128 | 402 | 115 | 88 | 0 | 0 | 157 | 54 | 0 | 114 | 108 | 100 | 0 | 104 | 0 |  | 931 | 0 | 410 | 0 | 96 | 0 | 0 | 0 | 16 | 0 | 40 | 0 | 27 | 64 | 0 | 0 | 0 | 43 | 0 | 60 | 20 | 0 | 31 | 32 | 21 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 143 | 0 | 95 | 5 | 154 | 0 | 353 | 105 | 0 | 57 | 0 | 59 | 0 | 0 | 90 | 450 | 0 | 0 |  | 7341 | 3491 | 10832 | 3820 | 931 | 1742 | 3019 | 600 | 157 | 401 | 162 | 0 | 0 | 103.98
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 150 | 115 | 200 | 32 | 0 | 0 | 303 |  | 0 | 300 | 260 | 97 | 70 | 40 | 0 | 0 | 116 | 0 | 90 | 102 | 140 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 28 | 33 | 33 | 51 | 0 | 88 | 70 | 115 | 0 | 8 | 205 | 0 | 139 | 0 |  | 0 | 8 | 102 | 10 | 90 | 50 | 20 | 10 | 0 | 80 | 0 | 275 | 310 | 179 | 8 | 70 | 29 | 5 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 33 | 20 | 156 | 104 | 25 | 22 | 0 | 87 | 30 | 53 | 50 | 110 | 158 | 51 | 84 | 0 | 170 | 18 | 0 | 9 | 290 | 24 | 11 | 0 | 300 | 0 | 0 | 180 | 0 | 136 | 0 | 22 | 0 | 128 | 401 | 115 | 88 | 0 | 0 | 162 | 54 | 0 | 52 | 113 | 100 | 0 | 104 | 0 |  | 931 | 0 | 345 | 0 | 99 | 0 | 0 | 0 | 16 | 0 | 40 | 0 | 27 | 64 | 0 | 0 | 0 | 0 | 0 | 48 | 20 | 0 | 35 | 8 | 0 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 156 | 0 | 95 | 20 | 161 | 0 | 394 | 105 | 0 | 35 | 0 | 100 | 0 | 0 | 109 | 530 | 0 | 0 |  | 7804 | 3527 | 11331 | 3973 | 931 | 1841 | 3243 | 680 | 158 | 349 | 156 | 0 | 0 | 103.98
19:30 | 0 | 0 | 150 | 115 | 200 | 32 | 0 | 0 | 285 |  | 0 | 300 | 275 | 100 | 97 | 40 | 0 | 0 | 130 | 0 | 100 | 102 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 30 | 33 | 33 | 51 | 0 | 88 | 70 | 115 | 0 | 8 | 204 | 0 | 104 | 0 |  | 0 | 0 | 102 | 0 | 90 | 50 | 20 | 16 | 0 | 80 | 0 | 275 | 310 | 188 | 8 | 75 | 29 | 5 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 33 | 20 | 160 | 103 | 25 | 22 | 0 | 87 | 30 | 53 | 50 | 110 | 156 | 51 | 84 | 0 | 170 | 18 | 0 | 9 | 310 | 24 | 11 | 0 | 300 | 0 | 0 | 180 | 0 | 149 | 0 | 22 | 0 | 130 | 401 | 115 | 88 | 0 | 0 | 162 | 54 | 0 | 34 | 113 | 100 | 0 | 104 | 0 |  | 932 | 0 | 345 | 0 | 99 | 0 | 0 | 0 | 16 | 0 | 40 | 0 | 27 | 64 | 0 | 0 | 0 | 0 | 0 | 24 | 20 | 0 | 30 | 0 | 0 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 155 | 0 | 92 | 0 | 161 | 0 | 419 | 105 | 0 | 35 | 0 | 98 | 0 | 0 | 109 | 570 | 0 | 0 |  | 7851 | 3530 | 11381 | 3963 | 932 | 1871 | 3255 | 720 | 158 | 322 | 160 | 0 | 0 | 0
20:00 | 0 | 0 | 150 | 115 | 200 | 32 | 0 | 0 | 283 |  | 0 | 300 | 250 | 100 | 97 | 40 | 0 | 0 | 130 | 0 | 100 | 102 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 51 | 0 | 89 | 70 | 115 | 0 | 8 | 204 | 0 | 104 | 0 |  | 0 | 0 | 102 | 0 | 90 | 50 | 20 | 19 | 0 | 80 | 0 | 275 | 310 | 180 | 8 | 75 | 29 | 5 | 0 | 43 | 0 | 0 | 52 | 16 | 11 | 33 | 21 | 158 | 105 | 25 | 22 | 0 | 87 | 30 | 53 | 50 | 110 | 160 | 51 | 84 | 0 | 170 | 18 | 0 | 9 | 290 | 24 | 11 | 0 | 300 | 0 | 0 | 180 | 0 | 149 | 0 | 22 | 0 | 132 | 401 | 115 | 88 | 0 | 0 | 162 | 54 | 0 | 34 | 113 | 100 | 0 | 104 | 0 |  | 932 | 0 | 345 | 0 | 103 | 0 | 0 | 0 | 16 | 0 | 40 | 0 | 31 | 64 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 0 | 0 | 0 | 0 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 155 | 0 | 92 | 0 | 159 | 0 | 388 | 105 | 0 | 35 | 0 | 98 | 0 | 0 | 109 | 570 | 0 | 0 |  | 7824 | 3461 | 11285 | 3957 | 932 | 1825 | 3256 | 720 | 159 | 278 | 158 | 0 | 0 | 103.98
21:00 | 0 | 0 | 100 | 115 | 200 | 32 | 0 | 0 | 272 |  | 0 | 300 | 285 | 20 | 97 | 30 | 0 | 0 | 180 | 0 | 40 | 102 | 82 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 19 | 25 | 31 | 33 | 33 | 51 | 0 | 89 | 70 | 115 | 0 | 8 | 215 | 0 | 140 | 0 |  | 0 | 0 | 34 | 0 | 90 | 50 | 20 | 29 | 0 | 80 | 0 | 305 | 310 | 200 | 8 | 75 | 29 | 5 | 0 | 43 | 0 | 0 | 52 | 13 | 11 | 33 | 21 | 150 | 104 | 25 | 22 | 0 | 86 | 30 | 53 | 50 | 110 | 158 | 51 | 84 | 0 | 170 | 18 | 0 | 9 | 310 | 24 | 11 | 0 | 200 | 0 | 0 | 180 | 0 | 96 | 0 | 22 | 0 | 137 | 402 | 115 | 88 | 0 | 0 | 162 | 54 | 0 | 0 | 113 | 100 | 0 | 104 | 0 |  | 932 | 0 | 380 | 0 | 115 | 0 | 0 | 0 | 16 | 0 | 40 | 0 | 31 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 166 | 0 | 93 | 0 | 167 | 0 | 415 | 105 | 0 | 0 | 0 | 100 | 0 | 0 | 109 | 580 | 0 | 0 |  | 7456 | 3522 | 10978 | 4103 | 932 | 1872 | 2900 | 730 | 159 | 132 | 150 | 0 | 0 | #REF!
22:00 | 0 | 0 | 100 | 115 | 200 | 32 | 0 | 0 | 261 |  | 0 | 300 | 265 | 0 | 97 | 30 | 0 | 0 | 180 | 0 | 0 | 102 | 82 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 31 | 33 | 33 | 51 | 0 | 90 | 70 | 115 | 0 | 8 | 204 | 0 | 140 | 0 |  | 0 | 0 | 34 | 0 | 90 | 50 | 20 | 35 | 0 | 80 | 0 | 275 | 310 | 181 | 8 | 75 | 29 | 5 | 0 | 43 | 0 | 0 | 52 | 13 | 11 | 33 | 21 | 152 | 104 | 25 | 22 | 0 | 86 | 30 | 53 | 50 | 110 | 157 | 51 | 84 | 0 | 170 | 18 | 0 | 9 | 310 | 24 | 11 | 0 | 200 | 0 | 0 | 180 | 0 | 52 | 0 | 22 | 0 | 137 | 402 | 115 | 88 | 0 | 0 | 162 | 54 | 0 | 0 | 113 | 100 | 0 | 104 | 0 |  | 932 | 0 | 345 | 0 | 74 | 0 | 0 | 0 | 16 | 0 | 40 | 0 | 34 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 165 | 0 | 94 | 0 | 166 | 0 | 416 | 105 | 0 | 0 | 0 | 100 | 0 | 0 | 109 | 570 | 0 | 0 |  | 7252 | 3439 | 10691 | 4005 | 932 | 1872 | 2718 | 720 | 160 | 132 | 152 | 0 | 0 | 103.98
23:00 | 0 | 0 | 100 | 115 | 200 | 32 | 4 | 0 | 262 |  | 0 | 300 | 240 | 0 | 97 | 30 | 0 | 0 | 180 | 0 | 0 | 102 | 64 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 19 | 25 | 31 | 33 | 33 | 51 | 0 | 90 | 70 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 34 | 0 | 72 | 50 | 20 | 42 | 0 | 80 | 0 | 280 | 310 | 181 | 8 | 71 | 29 | 5 | 0 | 43 | 0 | 0 | 52 | 13 | 11 | 33 | 21 | 148 | 106 | 25 | 22 | 0 | 87 | 30 | 53 | 50 | 110 | 157 | 52 | 84 | 0 | 170 | 18 | 0 | 9 | 280 | 24 | 11 | 0 | 200 | 0 | 0 | 180 | 0 | 50 | 0 | 22 | 0 | 137 | 402 | 115 | 88 | 0 | 0 | 162 | 54 | 0 | 0 | 113 | 100 | 0 | 104 | 0 |  | 932 | 0 | 345 | 0 | 49 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 34 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 155 | 0 | 94 | 0 | 156 | 0 | 383 | 105 | 0 | 0 | 0 | 98 | 0 | 0 | 109 | 550 | 0 | 0 |  | 7143 | 3299 | 10442 | 3989 | 932 | 1821 | 2578 | 700 | 160 | 114 | 148 | 0 | 0 | 103.98
24:00 | 0 | 0 | 0 | 115 | 200 | 55 | 50 | 0 | 302 |  | 0 | 300 | 255 | 0 | 64 | 15 | 0 | 0 | 180 | 0 | 0 | 50 | 48 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 19 | 25 | 31 | 33 | 33 | 51 | 0 | 90 | 70 | 115 | 0 | 0 | 204 | 0 | 140 | 0 |  | 0 | 0 | 17 | 0 | 0 | 50 | 20 | 42 | 0 | 80 | 0 | 280 | 310 | 181 | 8 | 73 | 29 | 20 | 0 | 43 | 0 | 0 | 52 | 13 | 11 | 33 | 21 | 138 | 106 | 25 | 22 | 0 | 87 | 30 | 53 | 50 | 110 | 158 | 52 | 84 | 0 | 170 | 18 | 0 | 9 | 275 | 24 | 11 | 0 | 95 | 0 | 0 | 100 | 0 | 37 | 0 | 22 | 0 | 135 | 402 | 115 | 87 | 0 | 0 | 161 | 54 | 0 | 0 | 113 | 100 | 0 | 104 | 0 |  | 931 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 18 | 10 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 155 | 0 | 94 | 0 | 156 | 0 | 390 | 105 | 0 | 0 | 0 | 76 | 0 | 0 | 70 | 550 | 0 | 0 |  | 6764 | 3120 | 9884 | 3885 | 931 | 1945 | 2061 | 699 | 160 | 65 | 138 | 0 | 0 | 103.98
KWH | 0 | 0 | 3357000 | 2740500 | 4786436 | 854136 | 61152 | 0 | 7052000 |  | 0 | 7058500 | 6451375 | 276480 | 694368 | 370995 | 0 | 0 | 2926000 | 0 | 299520 | 1451376 | 672480 | 156407 | 0 | 0 | 0 | 1171800 | 214924 | 298807 | 305460 | 600000 | 606240 | 740600 | 822400 | 834756 | 0 | 2059456 | 1700000 | 2800000 | 0 | 60156 | 4926097 | 0 | 3079278 | 0 |  | 0 | 24184 | 479124 | 43560 | 683520 | 823200 | 434976 | 510720 | 0 | 1909735 | 0 | 6812000 | 7090000 | 4659000 | 217454 | 1785180 | 632304 | 156960 | 0 | 966690 | 0 | 0 | 340805 | 340056 | 237960 | 796900 | 483810 | 3264960 | 2430840 | 449280 | 496692 | 14750 | 2033000 | 720480 | 700800 | 707976 | 2674063 | 3316000 | 1305408 | 1607040 | 0 | 4305480 | 407000 | 0 | 230040 | 7169200 | 572112 | 196000 | 0 | 3522762 | 0 | 0 | 1946400 | 0 | 885600 | 110025 | 384960 | 60480 | 1488727 | 9210000 | 2560800 | 2082684 | 0 | 29160 | 2664655 | 898656 | 0 | 200640 | 1695120 | 2362560 | 620200 | 2033280 | 323790 |  | 22346181 | 0 | 8498304 | 0 | 521280 | 0 | 0 | 0 | 116040 | 2432 | 194250 | 0 | 519678 | 431040 | 0 | 0 | 0 | 69266 | 0 | 102877 | 137190 | 0 | 70508 | 42240 | 25380 | 474240 | 229212 | 157500 | 0 | 0 | 3676200 | 0 | 0 | 0 | 0 | 4055545 | 0 | 1938006 | 34560 | 4226245 | 0 | 8842454 | 1509600 | 0 | 189408 | 0 | 880320 | 0 | 41011 | 993600 | 13021400 | 0 | 0 |  | 154538457 | 73345967 | 227884424 | 95422738 | 22346181 | 41970321 | 42342141 | 16697600 | 3759456 | 1562291 | 3264960 | 518736 | 0
Fuel Cost | 0 | 0 | 4901220 | 4028535 | 5312943.96 | 1127459.52 | 103958.4 | 0 | 7263560 |  | 0 | 7693765 | 7161026.25 | 2098483.2 | 4784195.52 | 3138617.7 | 0 | 0 | 5061980 | 0 | 2255385.6 | 13236549.12 | 6617203.2 | 1442072.54 | 0 | 0 | 0 | 8554140 | 1661362.52 | 2946237.02 | 229095 | 450000 | 0 | 0 | 0 | 8072090.52 | 0 | 556053.12 | 459000 | 5068000 | 0 | 558849.24 | 5369445.73 | 0 | 5234772.6 | 0 |  | 0 | 233859.28 | 4647502.8 | 415998 | 5946624 | 6519744 | 548069.76 | 1516838.4 | 0 | 2826407.8 | 0 | 5040880 | 7090000 | 4286280 | 280515.66 | 2052957 | 714503.52 | 219744 | 0 | 1653039.9 | 0 | 0 | 3254687.75 | 431871.12 | 178470 | 1394575 | 362857.5 | 24487200 | 2576690.4 | 4079462.4 | 630798.84 | 235115 | 3334120 | 1152768 | 1247424 | 1104442.56 | 3048431.82 | 3448640 | 2571653.76 | 3069446.4 | 0 | 7448480.4 | 891330 | 0 | 469281.6 | 7240892 | 429084 | 148960 | 0 | 26632080.72 | 0 | 0 | 10121280 | 0 | 8714304 | 1286192.25 | 3137424 | 656208 | 10495525.35 | 8565300 | 23354496 | 19681363.8 | 0 | 0 | 20144791.8 | 7827293.76 | 0 | 2002387.2 | 14527178.4 | 15734649.6 | 0 | 0 | 0 |  | 128714002.56 | 0 | 8923219.2 | 0 | 4097260.8 | 0 | 0 | 0 | 1217259.6 | 25487.36 | 2024085 | 0 | 805500.9 | 4206950.4 | 0 | 0 | 0 | 681577.44 | 0 | 910461.45 | 1056363 | 0 | 683222.52 | 409305.6 | 246186 | 910540.8 | 355278.6 | 119227.5 | 0 | 0 | 19925004 | 0 | 0 | 0 | 0 | 5353319.4 | 0 | 2907009 | 587865.6 | 4944706.65 | 0 | 8754029.46 | 15760224 | 0 | 1797481.92 | 0 | 6831283.2 | 0 | 453171.55 | 7342704 | 57163946 | 0 | 0 |  | 405496122.31 | 287206673.51 | 692702795.82 | 111121162.14 | 128714002.56 | 49771158.02 | 283268031.53 | 77088950 | 1015053.12 | 15262759.65 | 24487200 | 1974478.8 | 0
Yesterday Day Peak | 0 | 0 | 150 | 115 | 200 | 32 | 0 | 0 | 283 |  | 0 | 300 | 260 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 21 | 33 | 33 | 51 | 0 | 87 | 70 | 115 | 0 | 0 | 230 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 17 | 2 | 0 | 80 | 0 | 260 | 270 | 182 | 8 | 74 | 26 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 15 | 130 | 102 | 17 | 22 | 1 | 84 | 30 | 11 | 5 | 110 | 159 | 63 | 82 | 0 | 178 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 245 | 0 | 0 | 50 | 0 | 16 | 19 | 22 | 0 | 0 | 403 | 115 | 88 | 0 | 5 | 122 | 53 | 0 | 0 | 36 | 100 | 268 | 104 | 46 |  | 932 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 182 | 0 | 86 | 0 | 193 | 0 | 401 | 90 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 470 | 0 | 0 |  | 9518 | DayPeak
Yesterday Evening Peak | 0 | 0 | 150 | 115 | 200 | 32 | 0 | 0 | 285 | 0 | 0 | 300 | 275 | 100 | 97 | 40 | 0 | 0 | 130 | 0 | 100 | 102 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 30 | 33 | 33 | 51 | 0 | 88 | 70 | 115 | 0 | 8 | 204 | 0 | 104 | 0 | 0 | 0 | 0 | 102 | 0 | 90 | 50 | 20 | 16 | 0 | 80 | 0 | 275 | 310 | 188 | 8 | 75 | 29 | 5 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 33 | 20 | 160 | 103 | 25 | 22 | 0 | 87 | 30 | 53 | 50 | 110 | 156 | 51 | 84 | 0 | 170 | 18 | 0 | 9 | 310 | 24 | 11 | 0 | 300 | 0 | 0 | 180 | 0 | 149 | 0 | 22 | 0 | 130 | 401 | 115 | 88 | 0 | 0 | 162 | 54 | 0 | 34 | 113 | 100 | 0 | 104 | 0 |  | 932 | 0 | 345 | 0 | 99 | 0 | 0 | 0 | 16 | 0 | 40 | 0 | 27 | 64 | 0 | 0 | 0 | 0 | 0 | 24 | 20 | 0 | 30 | 0 | 0 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 155 | 0 | 92 | 0 | 161 | 0 | 419 | 105 | 0 | 35 | 0 | 98 | 0 | 0 | 109 | 570 | 0 | 0 |  | 11381 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 115 | 200 | 68 | 78 | 0 | 360 | 0 | 0 | 450 | 305 | 100 | 100 | 40 | 0 | 0 | 200 | 0 | 100 | 100 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 52 | 0 | 90 | 70 | 120 | 0 | 25 | 221 | 0 | 145 | 0 | 0 | 0 |  | 102 | 100 | 90 | 50 | 20 | 30 | 0 | 80 | 0 | 360 | 350 | 225 | 8 | 75 | 29 | 5 | 0 | 43 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 172 | 150 | 25 | 22 | 0 | 86 | 30 | 51 | 44 | 110 | 160 | 65 | 86 | 0 | 200 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 134 | 0 | 22 | 164 | 150 | 400 | 115 | 88 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 104 |  |  | 938 | 16 | 410 | 0 | 115 | 220 | 0 | 0 | 30 | 60 | 40 | 0 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 20 | 0 | 50 | 52 | 32 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 225 | 0 | 95 | 100 | 220 | 0 | 414 | 105 | 200 | 113 | 100 | 100 | 0 | 0 | 113 | 530 | 0
Forecast for Day | 0 | 0 | 0 | 115 | 200 | 68 | 60 | 0 | 360 | 0 | 0 | 450 | 305 | 100 | 100 | 40 | 0 | 0 | 200 | 0 | 100 | 100 | 150 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 52 | 0 | 90 | 70 | 120 | 0 | 25 | 221 | 0 | 145 | 0 | 0 | 0 |  | 102 | 100 | 90 | 50 | 20 | 8 | 0 | 80 | 0 | 250 | 350 | 225 | 8 | 75 | 29 | 5 | 0 | 43 | 0 | 25 | 25 | 22 | 11 | 33 | 20 | 163 | 150 | 25 | 22 | 1.6 | 86 | 30 | 51 | 44 | 110 | 160 | 65 | 86 | 0 | 180 | 18 | 0 | 10 | 341 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 134 | 20 | 22 | 164 | 150 | 400 | 115 | 88 | 100 | 5 | 300 | 54 | 110 | 17 | 113 | 100 | 0 | 104 | 40 |  | 938 | 0 | 410 | 0 | 115 | 220 | 0 | 0 | 0 | 0 | 40 | 0 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 20 | 0 | 50 | 52 | 0 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 225 |  | 95 | 50 | 220 | 0 | 414 | 105 | 100 | 113 | 100 | 100 | 0 | 8 | 113 | 500 | 0
Generation at 08:00(Today) | 0 | 0 | 0 | 115 | 200 | 68 | 40 | 0 | 302 | 0 | 0 | 370 | 275 |  | 0 | 0 | 0 | 0 | 122 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 40 | 17 | 17 | 19 | 25 | 31 | 33 | 33 | 26 | 0 | 92 | 70 | 115 | 0 | 0 | 207 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 0 | 80 | 0 | 285 | 310 | 190 | 8 | 80 | 26 | 10 | 0 | 10 | 0 | 0 | 0 | 16 | 11 | 0 | 15 | 100 | 106 | 25 | 22 | 1 | 86 | 30 | 11 | 10 | 110 | 156 | 51 | 10 | 0 | 171 | 18 | 0 | 9 | 310 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 10 | 22 | 0 | 1 | 341 | 25 | 72 | 0 | 2 | 50 | 17 | 0 | 0 | 27 | 50 | 0 | 19 | 26 | 0 | 932 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 174 | 0 | 25 | 0 | 183 | 0 | 380 | 17 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 430 | 0 | 0 | 0
199
| Minimum Generation |  | 7680 | 7:00
| Highest Generation |  | 11381 | 19:30
| Day Peak Generation |  | 9518 | 12:00
| Evening Peak Generation |  | 11381 | 19:30
| HVDC Max Flow |  | 933 | 14:00
| HVDC EvPeak Flow |  | 932 | 19:30
| Load factor L.F |  | 83.43%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-10-29
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-10-28 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9518 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 7802 | MW
Evening Peak Generation : |  | 11381 | MW Hour : | 19:30 | Available Max Generation : |  | 14942 | MW
E.P. Demand (at gen end) : |  | 11381 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 11800 | MW
Maximum Generation : |  | 11381 | MW Hour : | 19:30 | Reserve(Generation end) |  | 3142 | MW
Total Gen. (MKWH) : |  | 227.8844 | System Load Factor : | 83.43% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -3 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-10-29
Actual : | 103.97 | Ft.(MSL) , | Rule curve : | 108.7 | Ft.( MSL )
Gas Consumed : | Total = | 1147.44 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 160892320.16
: |  | Coal : | 77088950 | Oil : | 298530791.18 | Total : | 536512061.34
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4198.5336 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1429.5506 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1281.1537 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1157.7453 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1046.1743 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 844.2302 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 469.7141 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 217.3047 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 651.1235 |  |  | 0 | 0%
Total | 0 |  | 11295.5301 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Baghabari-71 & 100 MW
3) Ghorasal Unit-1,2,3,4
4) Ashuganj unit-3,5
5) Kaptai-2
6) Raozan #2
7) Siddirganj-335 MW
8) Haripur 412 MW
9) Chandpur-163 MW STG
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Shahjibazar 132/33 kV T-2 transformer was under shut down from 08:18 to 16:58 for A/M.
b) Rangamati-Chandraghona 132 kV Ckt-2 was under shut down from 08:44 to 14:16 for A/M.
c) Tongi-Bashundhara 132 kV Ckt-2 was under shut down from 08:28 to 16:50 for A/M.
d) Tongi 132/33 kV T-1 transformer was under shut down at 09:15 for A/M.
e) Mohastanghor 132/33 kV T-2 transformer was under shut down from 09:21 to 13:19 for A/M.
f) Palashbari 132 kV Bus-A was under shut down from 08:35 to 11:44 for A/M.
g) Panchaghar 132/33 kV T-1 transformer was under shut down from 08:03 to 16:58 for A/M.
h) Madaripur 132/33 kV T-2 transformer was under shut down from 07:57 to 14:26 for A/M.
i) Fenchuganj 230/132 kV T-2 transformer was under shut down from 08:53 to 16:26 for A/M.
j) Ashuganj-Kishorganj 132 kV Ckt-1 was under shut down from 09:53 to 13:27 for D/W.
k) HVDC 10CF22 was under shut down from 09:25 to 14:38 for A/M.
l) Saidpur 132/33 kV T-2 transformer was under shut down from 13:15 to 14:45 for D/W.
m) Ashuganj-Kishorganj 132 kV Ckt-2 was under shut down from 13:28 to 14:49 for D/W.
n) Bibiyana(South)-400 MW was shut down at 14:34 for test.
o) Siddirganj GT-1 & GT-2 were shut down at 15:09 & 15:13 due to problem with instrument air compressor
and were synchronized at
p) Barapukuria 132 kV Bus-2 tripped at 15:20 due to bus bar protection trip and was switched on at 15:30.
q) Ghorasal #4 was shut down at 23:14 due to maintenance.
r) Madunaghat-Chandraghona 132 kV Ckt-2 is under shut down since 07:36(29/10/20) for A/M.
s) Chatak 132/33 kV T2 transformer is under shut down since 06:26(29/10/20) for A/M.
t) Mymensing 33 kV Bus section-3 is under shut down since 07:18(29/10/20) for C/M. |  |  |  |  | About 30 MW power interruption occurred under Mymensing S/S area
v) Kaliakoir-Kabirpur 132 kV Ckt-1 was under shut down from 06:33 to 08:35(29/10/20) for C/M. |  |  |  |  | since 07:18(29/10/20).
w) Savar-Manikganj P/S 132 kV Ckt-1 was under shut down from 06:16 to 07:17(29/10/20) for C/M.
x) Savar-Manikganj P/S 132 kV Ckt-2 is under shut down since 07:45(29/10/20) for C/M.
y) Tongi-Bashundhara 132 kV Ckt-2 is under shut down since 07:56(29/10/20) for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-10-28 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 150 | 3357000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 115 | 2740500 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 4786436 | Machin problem.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 61152 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 32 | 854136 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 285 | 7052000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7058500 | Gas shortae
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 276480
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 275 | 6451375 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 97 | 694368
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 40 | 370995 | High Voltage.
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 156407 | Reserve.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 305460
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 130 | 2926000 | Frequency control
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 299520
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under Maintenance
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1451376
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel Shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1171800
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 672480
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 214924
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 298807 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1206240 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 740600
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 822400
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 834756
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 3522762
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 885600
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 88 | 2082684
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2033280
| Dhaka area Total |  |  |  | 5895 | 3052 | 53328038
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 115 | 2800000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 8 | 60156 | Low demand
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 110025
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 823200
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 158 | 3759456 | Unit-2 under maint
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4926097
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 104 | 3079278 | Gas shortage
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 24184 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 479124
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 43560 | Reserve.
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 22 | 384960 | Engine problem
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 434976
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 16 | 510720
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 90 | 683520 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 29160
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 162 | 2664655 | Transformer O/L
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 898656
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2362560
| Chattogram area Total |  |  |  | 2266 | 1205 | 24074287
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 80 | 1909735
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 188 | 4659000 | Gas shortage
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 275 | 6812000 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 310 | 7090000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 632304 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 156960 | Gas shortage
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 966690
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 130 | 1488727 | Engine problem
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 75 | 1785180 | ST Under maint
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 60480 | Reserve.
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 340056
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 237960
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 160 | 3264960
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 796900
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 340805
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 483810
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 34 | 200640 | Low demand
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 1695120
| Cumilla Area Total |  |  |  | 2980 | 1585 | 33138781
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 103 | 2430840 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 496692
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 25 | 449280 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14750
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 180 | 1946400
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2560800 | #REF!
| Mymensingh PV 50 MW Solar PP |  | IPP | 0 | 50 MW | 0 | 323790
| Mymensingh Area Total |  |  |  | 637 | 445 | 8222552
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 87 | 2033000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 720480 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2674063 | ST Under maint
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 156 | 3316000 | FGMO & GT-2 under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 700800
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 707976
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 196000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 51 | 1305408 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1607040
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 170 | 4305480
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 407000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 572112
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7169200 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 401 | 9210000
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 230040
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 620200 | On test
| Sylhet Area Total |  |  |  | 1988 | 1564 | 35774799
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 932 | 22346181
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 521280 | Engine problem
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 16 | 116040 | Low demand
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 2432 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 345 | 8498304 | Gas shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 194250
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 34560 | Reserve.
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1509600
107 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Bhola Nutan Biddut BD LTD (GAS) |  | IPP | 0 | 220 MW | 0 | 0 | On test
| Khulna Area Total |  |  |  | 2284 | 1537 | 33222647
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 64 | 431040 | Line O/L
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 27 | 519678
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 92 | 1938006
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 570 | 13021400
| Barisal Area Total |  |  |  | 1054 | 753 | 15910124
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 69266 | Reserve.
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 20 | 137190 | Fuel Shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel Shortage
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 70508 | Low demand
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas Shortage
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 155 | 4055545 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 161 | 4226245 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 419 | 8842454 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 25380 | Reserve.
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 18 | 474240
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 10 | 229212
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 157500
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 42240 | Reserve.
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 24 | 102877 | Low demand
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 35 | 189408 | Low demand
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 993600
| Rajshahi Area Total |  |  |  | 2183 | 992 | 19615665
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3676200 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 98 | 880320 | Engine problem
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 41011
| Rangpur Area Total |  |  |  | 605 | 248 | 4597531
| Total |  |  |  | 19892 | 11381 | 227884424
| Eastern Grid Total |  |  |  | 13766 | 7851 | 154538457
| Western Grid Total |  |  |  | 6126 | 3530 | 73345967
| National Grid Total |  |  |  | 19892 | 11381 | 227884424
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-10-28
| (a) ENTIRE EASTERN GRID : |  | 7602 | MW | (b) ENTIRE WESTERN GRID : |  | 3283 | MW
| i) Dhaka area |  | 3966 | MW | i) Khulna area |  | 1263 | MW
| ii) Chittagong area |  | 1097 | MW | ii) Rajshahi area |  | 1078 | MW
| iii) Comilla area |  | 1048 | MW | iii) Barisal area |  | 298 | MW
| iv) Mymensingh area |  | 898 | MW | iv) Rangpur area |  | 644 | MW
| v) Sylhet area |  | 593 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 10885 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 124 | 18:00 | Sherpur | 98 | 18:30 | Jhenida | 93 | 18:30
| Munsiganj | 114 | 19:30 | Srimongal | 48 | 18:30 | Bottail | 110 | 18:30
| Sonargaon | 80 | 19:00 | Shahjibazar | 111 | 18:30 | G.K Project | 44 | 18:30
| Shyampur | 186 | 12:00 | Fenchuganj | 40 | 18:00 | Faridpur | 157 | 0.75
| Bhulta | 184 | 1:00 | Kulawara | 43 | 18:00 | Madaripur | 86 | 0.91667
| Madanganj | 60 | 19:30 | Sylhet | 128 | 18:00 | Sariatpur | 54 | 19:30
| Shitalakhya | 107 | 11:00 | Chatak | 28 | 18:00 | Gopalganj | 79 | 18:30
| Rahim steel | 15 | 10:00 | Sunamganj | 47 | 18:30 | Bagerhat | 91 | 18:30
| Matuail | 76 | 10:00 | Biani Bazar | 61 | 18:00 | Mongla | 32 | 11:00
| Ghorasal | 79 | 21:00 | Comilla (S) | 162 | 18:00 | Satkhira | 88 | 0.77083
| Narsingdi | 156 | 18:00 | Comilla(N) | 107 | 20:00 | Gallamari | 50 | 13:00
| Haripur (SBU) | 100 | 16:00 | Chandpur | 93 | 18:30 | Magura | 42 | 0.75
| Ullon | 56 | 19:00 | Feni | 112 | 18:30 | Norail | 36 | 18:30
| Hasnabad | 190 | 20:00 | Chowmuhani | 162 | 18:30 | Chuadanga | 79 | 18:30
| Magbazar | 95 | 13:00 | Ashuganj | 55 | 23:00 | Barisal(N) | 38 | 0.83333
| Maniknagar | 90 | 16:00 | Daudkandi | 134 | 22:00 | Barisal (S) | 92 | 0.75
| Bangabhaban | 32 | 13:00 | B.Baria | 145 | 19:30 | Patuakhali | 100 | 0.95833
| Narinda | 86 | 18:00 | Ramganj | 100 | 22:00 | Bhandaria | 48 | 0.79167
| Dhanmondi | 164 | 13:00 | Chaddagram | 34 | 19:30 | Borhan Uddin | 36 | 21:00
| Lalbag | 86 | 17:00 | PHP | 10 | 13:00 | Ishurdi | 53 | 18:00
| Madartek | 70 | 23:00 | Madunaghat | 52 | 18:30 | Ruppur Paromanobik | 2 | 20:00
| Dhaka University |  |  | Hathazari | 97 | 0.75 | Natore | 99 | 18:00
| Fatullah | 39 | 0.41667 | Khulshi | 222 | 0.54167 | Bogra | 147 | 18:30
| Mirpur | 100 | 18:00 | Halishahar | 133 | 0.45833 | Noagaon | 100 | 18:30
| Kalyanpur | 90 | 19:00 | Baraulia | 153 | 0.41667 | Rajshahi | 119 | 19:00
| Gulshan | 122 | 14:00 | Sikalbaha | 26 | 0.79167 | Rajshahi New | 12 | 18:00
| Uttara | 86 | 18:30 | Dohazari | 78 | 0.8125 | C.Nawabganj | 62 | 20:00
| Uttara New | 32 | 18:30 | Cox'sbazar | 101 | 0.75 | Amnura | 38 | 18:00
| Kamrangirchar | 89 | 18:00 | Chandraghona | 30 | 0.75 | Pabna | 109 | 18:30
| Savar | 145 | 19:00 | Kaptai | 4.4 | 0.77083 | Shahjadpur | 91 | 20:00
| Bhasantec | 147 | 18:00 | A. Khaer Stl. | 0 | 0.041667 | Serajganj | 94 | 19:00
| Agargaon | 69 | 13:00 | Bakulia | 109 | 0.625 | Niyamatpur | 48 | 18:30
| Satmosjid | 91 | 18:00 | Julda | 21 | 0.29167 | Joypurhat | 50 | 18:30
| Tongi | 96 | 0.75 | TK chemical | 27 | 0.875 | Sherpur(Bogura) | 44 | 18:00
| Kabirpur | 228 | 15:00 | Modern Steel | 16 | 0.041667 | Mohastangor | 42 | 18:30
| Basundhara | 121 | 18:00 | Shahmirpur | 23 | 0.66667 | Rangpur | 129 | 18:30
| Manikganj | 72 | 21:00 | Khagrachhari | 22 | 0.70833 | Lalmonirhat | 49 | 18:30
| Joydevpur | 156 | 18:00 | Matarbari | 37 | 0.8125 | Saidpur | 95 | 18:00
| New Tongi | 106 | 18:00 | Baroiar Hat | 36 | 0.75 | Purbasadipur | 86 | 18:00
| Kodda | 241 | 18:00 | Rangamati | 12 | 0.75 | Thakurgaon | 68 | 18:30
| Dhamrai | 92 | 18:00 | Abul Khair 230 | 10 | 0.125 | Palashbari | 105 | 18:00
| Rajendrapur | 92 | 18:30 | BSRM | 159 | 0.20833 | Barapukuria | 45 | 19:30
| Valuka | 106 | 15:00 | GPH Ispat | 58 | 0.083333 | Panchagar | 45 | 19:30
| Tangail | 174 | 19:30 | Goalpara | 24 | 0.77083 | Joldhaka | 21 | 18:30
| Mymensing | 196 | 19:00 | Central s/s | 75 | 18:30 | Kurigram | 49 | 18:00
| Kishorganj | 131 | 20:00 | Noapara | 51 | 18:30
| Netrokona | 102 | 19:30 | Jessore | 98 | 18:30
| Jamalpur | 116 | 19:00 | Benapol | 40 | 18:00
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-10-28 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 808 | 20:00 | 399 | 12:00 | Kaliakoir | 402 | 0.20833 | 380 | 0.5
| Bheramara | 408 | 8:00 | 398 | 18:00 | Bhulta | 375 | 0.83333 | 361 | 0.41667
| Ashuganj(N) | 383 | 6:00 | 368 | 12:00 | Gopalganj | 413 | 0.25 | 383 | 0.875
| Payra | 417 | 19:30 | 402 | 21:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 228 | 1:00 | 222 | 10:00 | Comilla (N) | 232 | 20:00 | 222 | 12:00
| Ishurdi | 236 | 1:00 | 225 | 13:00 | Hathazari | 224 | 20:00 | 218 | 10:00
| Ashuganj | 235 | 20:00 | 225 | 12:00 | Megnaghat | 226 | 5:00 | 218 | 8:00
| Serajganj | 230 | 1:00 | 224 | 12:00 | Fenchuganj | 244 | 20:00 | 236 | 12:00
| Baghabari | 240 | 5:00 | 236 | 13:00 | Siddhirganj | 225 | 15:00 | 215 | 16:00
| Barapukuria | 239 | 6:00 | 232 | 13:00 | Maniknagar | 214 | 20:00 | 213 | 12:00
| Bogra | 226 | 5:00 | 217 | 13:00 | Agargaon | 222 | 5:00 | 211 | 12:00
| Rajshahi | 226 | 4:00 | 216 | 13:00 | Barisal | 252 | 18:00 | 230 | 21:00
| Khulna South | 231 | 6:00 | 215 | 13:00 | AKSML | 222 | 20:00 | 214 | 2:00
| Rampura | 222 | 20:00 | 217 | 11:00 | BSRM | 223 | 19:00 | 214 | 10:00
| Haripur | 223 | 20:00 | 214 | 12:00 | Bibiyana | 243 | 19:00 | 235 | 14:00
| Hasnabad | 222 | 23:00 | 210 | 12:00 | Bhulta | 225 | 19:00 | 216 | 17:00
| Shyampur | 222 | 19:30 | 220 | 12:00 | Ashuganj (S) | 232 | 20:00 | 224 | 15:00
| Aminbazar | 222 | 22:00 | 213 | 10:00 | Kaliakoir | 224 | 20:00 | 215 | 11:00
| Tongi | 218 | 19:30 | 208 | 9:00 | GPH | 221 | 20:00 | 214 | 10:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 133 | 21:00 | 127 | 15:00 | Hathazari | 133 | 0.75 | 130 | 0.041667
| Munsiganj | 136 | 19:30 | 126 | 11:00 | Khulshi | 132 | 0.79167 | 127 | 0.16667
| Sonargaon | 136 | 20:00 | 126 | 16:00 | Halishahar | 134 | 0.77083 | 127 | 0.33333
| Shyampur | 135 | 18:30 | 128 | 12:00 | Baraulia | 133 | 0.75 | 127 | 0.33333
| Bhulta | 127 | 19:30 | 121 | 12:00 | Sikalbaha | 134 | 0.75 | 129 | 0.041667
| Madanganj | 132 | 1:00 | 125 | 13:00 | Dohazari | 132 | 0.75 | 125 | 0.041667
| Shitalakhya | 143 | 18:00 | 129 | 9:00 | Cox'sbazar | 123 | 0.375 | 115 | 0.041667
| Rahim steal | 135 | 20:00 | 127 | 15:00 | Chandraghona | 133 | 0.75 | 130 | 0.083333
| Matuail | 133 | 21:00 | 127 | 15:00 | Kaptai | 133 | 0.75 | 130 | 0.29167
| Ghorasal | 136 | 1:00 | 132 | 9:00 | A. Khaer Stl. | 133 | 0.77083 | 127 | 0.45833
| Narsinghdi | 128 | 19:00 | 123 | 16:00 | Bakulia | 132 | 0.83333 | 127 | 0.33333
| Haripur (SBU) | 135 | 18:30 | 127 | 15:00 | Julda | 135 | 0.75 | 129 | 0.041667
| Ullon | 132 | 4:00 | 125 | 10:00 | TK Chemical | 134 | 0.8125 | 129 | 0.77083
| Hasnabad | 138 | 18:00 | 129 | 11:00 | Modern Steel | 133 | 0.77083 | 128 | 0.33333
| Magbazar | 132 | 4:00 | 125 | 10:00 | Shahmirpur | 134 | 0.75 | 128 | 0.33333
| Maniknagar | 133 | 3:00 | 127 | 12:00 | Khagrachhari | 132 | 0.70833 | 129 | 0.083333
| Bangabhaban | 133 | 3:00 | 127 | 12:00 | Matarbari | 125 | 0.75 | 117 | 0.083333
| Narinda | 133 | 3:00 | 127 | 12:00 | Baroiar Hat | 133 | 0.75 | 127 | 0.29167
| Dhanmondi | 132 | 4:00 | 125 | 10:00 | Rangamati | 133 | 0.75 | 129 | 0.45833
| Lalbag | 137 | 18:00 | 126 | 10:00 | Goalpara S/S | 137 | 17:00 | 130 | 13:00
| Madartek | 131 | 6:00 | 124 | 15:00 | Khulna Central S/S | 137 | 5:00 | 129 | 0.54167
| Dhaka University |  |  |  |  | Noapara | 138 | 6:00 | 126 | 0.54167
| Fatuiiah | 136 | 19:00 | 129 | 9:00 | Jessore | 136 | 6:00 | 122 | 0.54167
| Mirpur | 136 | 5:00 | 129 | 12:00 | Benapol | 136 | 0.25 | 122 | 0.54167
| Kalyanpur | 137 | 20:00 | 129 | 13:00 | Jhenida | 134 | 6:00 | 118 | 0.8125
| Gulshan | 130 | 5:00 | 124 | 11:00 | Bottail | 137 | 0.20833 | 126 | 0.8125
| Uttara | 133 | 19:00 | 125 | 10:00 | G.K Project | 139 | 0.25 | 135 | 0.5
| Uttara New | 135 | 20:00 | 126 | 12:00 | Faridpur | 134 | 0.20833 | 124 | 0.875
| Kamrangirchar | 135 | 18:00 | 125 | 9:00 | Madaripur | 141 | 0.20833 | 129 | 0.875
| Savar | 135 | 19:00 | 128 | 14:00 | Shariyatpur S/S | 140 | 6:00 | 125 | 0.875
| Bhasantec | 133 | 6:00 | 126 | 12:00 | Gopalganj | 140 | 0.20833 | 125 | 0.79167
| Agargaon | 135 | 20:00 | 127 | 12:00 | Bagerhat | 137 | 6:00 | 127 | 0.54167
| Satmosjid | 134 | 20:00 | 127 | 12:00 | Mongla | 132 | 1:00 | 125 | 0.54167
| Tongi | 136 | 19:30 | 129 | 9:00 | Satkhira | 140 | 6:00 | 129 | 13:00
| Kabirpur | 132 | 8:00 | 125 | 12:00 | Gallamari | 141 | 0.25 | 130 | 0.54167
| Basundhara | 130 | 22:00 | 124 | 13:00 | Magura | 135 | 6:00 | 117 | 0.83333
| Manikganj | 138 | 19:00 | 130 | 15:00 | Norail | 130 | 0.20833 | 115 | 0.8125
| Joydevpur | 138 | 20:00 | 130 | 13:00 | Chuadanga | 131 | 6:00 | 111 | 0.8125
| New Tongi | 136 | 21:00 | 127 | 10:00 | Barisal(N) | 142 | 5:00 | 129 | 21:00
| Kodda | 137 | 20:00 | 123 | 4:00 | Barisal (S) | 142 | 0.20833 | 129 | 0.625
| Dhamrai | 135 | 6:00 | 125 | 12:00 | Patuakhali(S) | 141 | 0.25 | 123 | 0.875
| Rajendrapur | 134 | 20:00 | 121 | 13:00 | Bhandaria | 132 | 0.041667 | 125 | 0.5
| Valuka | 124 | 5:00 | 110 | 19:00 | Ishurdi | 137 | 6:00 | 132 | 20:00
| Tangail | 134 | 5:00 | 123 | 18:00 | Ruppur Paromanobik | 136 | 17:00 | 132 | 14:00
| Mymensing | 127 | 6:00 | 114 | 18:00 | Natore | 138 | 6:00 | 131 | 13:00
| Kishorganj | 126 | 5:00 | 117 | 18:30 | Bogra | 137 | 6:00 | 130 | 13:00
| Netrokona | 125 | 6:00 | 112 | 18:00 | Noagaon | 131 | 6:00 | 125 | 13:00
| Jamalpur | 135 | 20:00 | 125 | 9:00 | Rajshahi | 137 | 6:00 | 132 | 13:00
| Sherpur | 134 | 15:00 | 122 | 7:00 | Rajshahi New | 138 | 17:00 | 132 | 13:00
| Srimongal | 134 | 1:00 | 132 | 9:00 | C.Nawabganj | 136 | 4:00 | 130 | 13:00
| Shahjibazar | 132 | 9:00 | 129 | 18:00 | Amnura | 137 | 18:00 | 129 | 13:00
| Fenchuganj | 136 | 4:00 | 131 | 14:00 | Pabna | 136 | 5:00 | 130 | 19:30
| Khulawara | 134 | 1:00 | 130 | 13:00 | Shahjadpur | 137 | 6:00 | 133 | 20:00
| Sylhet | 133 | 1:00 | 130 | 15:00 | Serajganj | 135 | 6:00 | 128 | 13:00
| Chatak | 132 | 4:00 | 127 | 18:00 | Niyamatpur | 131 | 6:00 | 122 | 13:00
| Sunamganj | 131 | 7:00 | 125 | 18:00 | Joypurhat | 135 | 6:00 | 124 | 13:00
| Biani Bazar | 131 | 6:00 | 128 | 18:30 | Sherpur(Bogura) | 136 | 6:00 | 130 | 12:00
| Comilla(s) | 128 | 5:00 | 122 | 18:00 | Mohastangor | 136 | 6:00 | 129 | 13:00
| Comilla(n) | 136 | 20:00 | 130 | 12:00 | Rangpur | 133 | 6:00 | 123 | 13:00
| Chandpur | 133 | 18:00 | 128 | 13:00 | Lalmonirhat | 132 | 6:00 | 123 | 18:30
| Feni | 134 | 18:00 | 127 | 16:00 | Saidpur | 134 | 6:00 | 119 | 15:00
| Chowmuhani | 132 | 19:30 | 125 | 8:00 | Purbasadipur | 130 | 3:00 | 120 | 18:00
| Ashuganj | 132 | 8:00 | 129 | 18:30 | Thakurgaon | 132 | 6:00 | 118 | 18:00
| Daudkandi | 132 | 18:30 | 126 | 12:00 | Palashbari | 134 | 6:00 | 125 | 18:00
| B.Baria | 129 | 8:00 | 124 | 18:30 | Barapukuria | 139 | 6:00 | 132 | 18:00
| Ramganj | 128 | 18:30 | 122 | 23:00 | Panchagar | 129 | 4:00 | 114 | 18:00
| Chaddagram | 134 | 18:00 | 127 | 3:00 | Joldhaka | 133 | 6:00 | 119 | 18:00
| PHP | 133 | 18:00 | 124 | 2:00 | Kurigram | 132 | 6:00 | 121 | 18:30
| Madanhat | 135 | 18:00 | 130 | 8:00

## L-Curve
Date | 2020-10-28
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 355 | 6764 | 3120 | 9884 |  |  |  | QF-LDC-11
0:30 | 384 | 6490.5 | 3045 | 9535.5 | Date: | 2020-10-28
1:00 | 413 | 6217 | 2970 | 9187
1:30 | 419 | 6097.5 | 2926 | 9023.5
2:00 | 425 | 5978 | 2882 | 8860
2:30 | 447.5 | 5867.5 | 2849.5 | 8717 | [5 empty] | Gen. at Eve. Peak | 11381 | 11381 MW (19:30 )
3:00 | 470 | 5757 | 2817 | 8574 | [6 empty] | 19:30
3:30 | 487 | 5696 | 2756.5 | 8452.5 | [5 empty] | Gen. at Day Peak | 9518 | 9518 MW (12:00 )
4:00 | 504 | 5635 | 2696 | 8331 | [6 empty] | 12:00
4:30 | 503 | 5551 | 2685.5 | 8236.5 | [5 empty] | Highest Generation | 11381
5:00 | 502 | 5467 | 2675 | 8142 | [6 empty] | 19:30
5:30 | 526.5 | 5315 | 2627.5 | 7942.5
6:00 | 551 | 5163 | 2580 | 7743
6:30 | 507.5 | 5111.5 | 2600 | 7711.5
7:00 | 464 | 5060 | 2620 | 7680
7:30 | 487 | 5093 | 2639 | 7732
8:00 | 510 | 5126 | 2658 | 7784
8:30 | 524 | 5340 | 2660 | 8000
9:00 | 538 | 5554 | 2662 | 8216
9:30 | 544 | 5771.5 | 2680.5 | 8452
10:00 | 550 | 5989 | 2699 | 8688
10:30 | 522.5 | 6106 | 2718 | 8824
11:00 | 495 | 6223 | 2737 | 8960
11:30 | 474 | 6415.5 | 2823.5 | 9239
12:00 | 453 | 6608 | 2910 | 9518
12:30 | 419.5 | 6575.5 | 2928.5 | 9504
13:00 | 386 | 6543 | 2947 | 9490
13:30 | 350 | 6651 | 2868.5 | 9519.5
14:00 | 314 | 6759 | 2790 | 9549
14:30 | 452 | 6702 | 2915.5 | 9617.5
15:00 | 590 | 6645 | 3041 | 9686
15:30 | 558 | 6601.5 | 2997 | 9598.5
16:00 | 526 | 6558 | 2953 | 9511
16:30 | 484.5 | 6421.5 | 2881.5 | 9303
17:00 | 443 | 6285 | 2810 | 9095
17:30 | 315 | 6813 | 3150.5 | 9963.5
18:00 | 187 | 7341 | 3491 | 10832
18:30 | 123.5 | 7572.5 | 3509 | 11081.5
19:00 | 60 | 7804 | 3527 | 11331
19:30 | 48 | 7851 | 3530 | 11381
20:00 | 3 | 7824 | 3461 | 11285 |  |  |  | Executive Engineer
20:30 | 109.5 | 7640 | 3491.5 | 11131.5 |  |  |  | Network Operation Division
21:00 | 216 | 7456 | 3522 | 10978
21:30 | 238.5 | 7354 | 3480.5 | 10834.5
22:00 | 261 | 7252 | 3439 | 10691 |  |  |  |  | Page 6 of 7
22:30 | 290 | 7197.5 | 3369 | 10566.5
23:00 | 319 | 7143 | 3299 | 10442
23:30 | 337 | 6953.5 | 3209.5 | 10163
24:00 | 355 | 6764 | 3120 | 9884
11381 MW (19:30 )
9518 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-10-28 |  | Energy | 227884424
[10 empty] | 2020-10-28 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3885 | 931 | 1945 | 2578 | 699 | 160 | 65 | 0 | 138
0:30 | 3991.5 | 931 | 1928 | 1906 | 709.5 | 157.5 | 32.5 | 0 | 138 | Date: | 2020-10-28
1:00 | 4098 | 931 | 1911 | 1234 | 720 | 155 | 0 | 0 | 138
1:30 | 4092.5 | 931 | 1927 | 1066 | 715 | 154 | 0 | 0 | 138 | [7 empty] | Total Energy | 227.8844 | Total Energy Gen 227.884 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 227.884 MKWHr
2:00 | 4087 | 931 | 1943 | 898 | 710 | 153 | 0 | 0 | 138 | [7 empty] | Energy not Served | 0
2:30 | 4025.5 | 931 | 1926 | 835 | 710 | 153.5 | 0 | 0 | 136 | [7 empty] | Energy Requirement | 227.8844
3:00 | 3964 | 931 | 1909 | 772 | 710 | 154 | 0 | 0 | 134
3:30 | 3932.5 | 931 | 1812 | 785.5 | 705 | 154.5 | 0 | 0 | 132 | [6 empty] | Shortage
4:00 | 3901 | 931 | 1715 | 799 | 700 | 155 | 0 | 0 | 130
4:30 | 3863 | 930.5 | 1686 | 797 | 675 | 156 | 0 | 0 | 129
5:00 | 3825 | 930 | 1657 | 795 | 650 | 157 | 0 | 0 | 128
5:30 | 3754.5 | 930.5 | 1605 | 745 | 630 | 157.5 | 0 | 0 | 120
6:00 | 3684 | 931 | 1553 | 695 | 610 | 158 | 0 | 0 | 112
6:30 | 3704.5 | 931 | 1561 | 640 | 610 | 158.5 | 0 | 0 | 103 |  |  |  |  | Coal
7:00 | 3725 | 931 | 1569 | 585 | 610 | 159 | 0 | 0 | 94
7:30 | 3767 | 930.5 | 1561.5 | 587.5 | 609.5 | 158.5 | 0 | 0 | 101 |  |  |  | Oil |  |  |  | ,
8:00 | 3809 | 930 | 1554 | 590 | 609 | 158 | 0 | 0 | 108
8:30 | 3850 | 929.5 | 1590.5 | 711.5 | 609 | 158 | 0 | 0 | 110
9:00 | 3891 | 929 | 1627 | 833 | 609 | 158 | 0 | 0 | 112
9:30 | 3903 | 930 | 1652.5 | 1021.5 | 609 | 158 | 0 | 0 | 114
10:00 | 3915 | 931 | 1678 | 1210 | 609 | 158 | 0 | 0 | 116
10:30 | 3933 | 931 | 1672 | 1327 | 609 | 158.5 | 0 | 0 | 118
11:00 | 3951 | 931 | 1666 | 1444 | 609 | 159 | 0 | 0 | 120
11:30 | 4131.5 | 931.5 | 1691 | 1509.5 | 614 | 158 | 0 | 0 | 125
12:00 | 4312 | 932 | 1716 | 1575 | 619 | 157 | 0 | 0 | 130
12:30 | 4272 | 932 | 1722 | 1605.5 | 624 | 157 | 0 | 0 | 132
13:00 | 4232 | 932 | 1728 | 1636 | 629 | 157 | 0 | 0 | 134
13:30 | 4232 | 932 | 1728 | 1636 | 629 | 157 | 0 | 0 | 134
14:00 | 4232 | 932 | 1728 | 1636 | 629 | 157 | 0 | 0 | 134
14:30 | 4067 | 932.5 | 1733 | 1872.5 | 634.5 | 157 | 8.5 | 0 | 138
15:00 | 3902 | 933 | 1738 | 2109 | 640 | 157 | 17 | 0 | 142
15:30 | 3863.5 | 932.5 | 1700.5 | 2102 | 645 | 156.5 | 21.5 | 0 | 141
16:00 | 3825 | 932 | 1663 | 2095 | 650 | 156 | 26 | 0 | 140
16:30 | 3716 | 932 | 1633 | 2049.5 | 630 | 156.5 | 36.5 | 0 | 137
17:00 | 3607 | 932 | 1603 | 2004 | 610 | 157 | 47 | 0 | 134
17:30 | 3713.5 | 931.5 | 1672.5 | 2511.5 | 605 | 157 | 224 | 0 | 148
18:00 | 3820 | 931 | 1742 | 3019 | 600 | 157 | 401 | 0 | 162
18:30 | 3896.5 | 931 | 1791.5 | 3131 | 640 | 157.5 | 375 | 0 | 159
19:00 | 3973 | 931 | 1841 | 3243 | 680 | 158 | 349 | 0 | 156
19:30 | 3963 | 932 | 1871 | 3255 | 720 | 158 | 322 | 0 | 160
20:00 | 3957 | 932 | 1825 | 3256 | 720 | 159 | 278 | 0 | 158
20:30 | 4030 | 932 | 1848.5 | 3078 | 725 | 159 | 205 | 0 | 154
21:00 | 4103 | 932 | 1872 | 2900 | 730 | 159 | 132 | 0 | 150
21:30 | 4054 | 932 | 1872 | 2809 | 725 | 159.5 | 132 | 0 | 151
22:00 | 4005 | 932 | 1872 | 2718 | 720 | 160 | 132 | 0 | 152
22:30 | 3997 | 932 | 1846.5 | 2648 | 710 | 160 | 123 | 0 | 150
23:00 | 3989 | 932 | 1821 | 2578 | 700 | 160 | 114 | 0 | 148
23:30 | 3937 | 931.5 | 1883 | 2578 | 699.5 | 160 | 89.5 | 0 | 143 | Max Temp. in Dhaka |  | 33.4° C
24:00 | 3885 | 931 | 1945 | 2578 | 699 | 160 | 65 | 0 | 138
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 227.884 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 227.884 MKWHr
Note on W13: Author:

## Generation
g | 2020-10-28
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 85 | 83 | 84 | 85 | 87 | 88 | 89 | 88 | 88 | 88 | 89 | 87 | 87 | 87 | 87 | 86 | 87 | 87 |  | 88 | 88 | 89 | 89 | 90 | 90 | 90 | 2059456
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1700000
3 | Chattogram TPP-1 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 15 |  | 8 | 8 | 8 | 8 | 8 |  | 0 | 60156
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 2 | 11 | 16 | 20 | 19 | 6 | 17 | 11 | 7 | 0 | [9 empty] | 110025
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 217 | 204 | 205 | 204 | 230 | 206 | 204 | 205 | 205 | 205 | 205 |  | 205 | 204 | 204 | 215 | 204 | 204 | 204 | 4926097
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 139 | 139 | 140 | 139 | 138 | 104 | 104 | 104 | 140 | 139 | 139 | 139 | 140 | 70 | 139 | 104 | 70 | 113 |  | 139 | 104 | 104 | 140 | 140 | 139 | 140 | 3079278
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [14 empty] | 17 | 17 | 17 | 102 |  | 102 | 102 | 102 | 34 | 34 | 34 | 17 | 479124
12 | Hathazari 100 MW peaking PP | [16 empty] | 8 | 8 |  | 8 | [5 empty] | 0 | 24184
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 160 | 155 | 150 | 118 | 120 | 68 | 75 | 75 | 115 | 120 | 120 | 155 | 155 | 75 | 73 |  |  |  |  | 116 | 130 | 130 | 180 | 180 | 180 | 180 | 2926000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [8 empty] | 15 | 110 | 205 | 245 | 245 | 245 | 245 | 245 | 245 | 260 |  | 300 | 300 | 300 | 200 | 200 | 200 | 95 | 3522762
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 150 | 150 | 150 | 151 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 140 |  | 150 | 150 | 150 | 100 | 100 | 100 | 0 | 3357000
23 | Ghorasal TPP Unit-5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2740500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4786436
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1909735
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 29 | 29 | 29 | 29 | 29 | 29 | 24 | 24 | 24 | 24 | 24 | 26 | 26 | 29 | 29 | 29 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 632304
33 | Ashuganj 225 MW CCPP | 218 | 218 | 219 | 205 | 180 | 180 | 188 | 198 | 180 | 216 | 186 | 182 | 194 | 184 | 190 | 179 | 179 | 179 |  | 179 | 188 | 180 | 200 | 181 | 181 | 181 | 4659000
34 | Ashuganj 450 MW CCPP(South) | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 355 | 315 | 300 | 350 | 295 | 310 |  | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 7090000
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 260 | 265 | 260 | 260 | 270 | 285 | 260 | 265 | 265 | 260 | 270 | 260 | 275 | 275 | 275 | 275 |  | 275 | 275 | 275 | 305 | 275 | 280 | 280 | 6812000
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 20 | 156960
36 | Chandpur 150 MW CCPP | 73 | 72 | 74 | 74 | 80 | 73 | 86 | 81 | 80 | 81 | 81 | 74 | 75 | 75 | 75 | 72 | 75 | 70 |  | 70 | 75 | 75 | 75 | 75 | 71 | 73 | 1785180
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 320 | 380 | 380 | 350 | 350 | 350 | 320 | 320 | 320 | 320 | 320 | 300 | 290 | 300 | 300 | 300 | 310 | 310 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7058500
41 | Haripur 360MW CCPP(HPL) | 302 | 302 | 302 | 315 | 302 | 302 | 302 | 303 | 303 | 304 | 303 | 283 | 278 | 289 | 294 | 306 | 307 | 306 |  | 303 | 285 | 283 | 272 | 261 | 262 | 302 | 7052000
42 | RPCL 210MW CCPP | 106 | 107 | 108 | 107 | 107 | 109 | 107 | 106 | 104 | 102 | 101 | 102 | 100 | 101 | 100 | 101 | 102 | 104 |  | 104 | 103 | 105 | 104 | 104 | 106 | 106 | 2430840
43 | Mymensingh PV 50 MW Solar PP | [5 empty] | 0 | 5 | 19 | 38 | 45 | 49 | 46 | 24 | 43 | 31 | 14 | 1 | [9 empty] | 323790
44 | Fenchugonj CCPP Phase-1 | 86 | 86 | 86 | 86 | 86 | 86 | 87 | 87 | 87 | 86 | 83 | 84 | 85 | 85 | 82 | 84 | 86 | 86 |  | 87 | 87 | 87 | 86 | 86 | 87 | 87 | 2033000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720480
46 | Shajibazar 330 MW CCPP | 159 | 158 | 159 | 158 | 159 | 159 | 158 | 158 | 158 | 158 | 159 | 159 | 157 | 159 | 158 | 159 | 158 | 158 |  | 158 | 156 | 160 | 158 | 157 | 157 | 158 | 3316000
47 | Shahjibazar GTPP Unit- 8 & 9 | 64 | 64 | 40 | 40 | 40 | 40 | 40 | 40 | 65 | 63 | 63 | 63 | 62 | 63 | 60 | 60 | 40 | 64 |  | 51 | 51 | 51 | 51 | 51 | 52 | 52 | 1305408
48 | Shahjibazar 86MW PP (Shahjibazar) | 84 | 84 | 60 | 20 | 10 | 10 | 10 | 10 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 10 | 84 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 1607040
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 204 | 204 | 204 | 204 | 177 | 177 | 177 | 177 | 192 | 178 | 178 | 178 | 178 | 177 | 184 | 184 | 137 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4305480
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 407000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 230040
54 | Hobiganj 11MW PP Cofidence-E | 11 | 8 |  |  | 3 | 5 | 5 | 5 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 3 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 196000
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 22 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 14 | 14 | 11 | 14 | 14 | 50 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 700800
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 572112
57 | Bibiana-II 341 MW CCPP (Summit) | 295 | 275 | 280 | 290 | 285 | 280 | 290 | 300 | 310 | 310 | 280 | 290 | 300 | 300 | 290 | 290 | 290 | 250 |  | 290 | 310 | 290 | 310 | 310 | 280 | 275 | 7169200
| Bibiyana South 400 MW | [11 empty] | 268 | 100 | 267 | [12 empty] | 620200
58 | Nababganj 55 MW PP (Southern power ) | [19 empty] | 35 | 35 | 55 | 55 | 55 | 35 | 35 | 298807
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 17 | 17 | 17 | 12 | 14 | 19 | 19 | 19 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 434976
61 | Narshingdi 22 MW PP (Doreen) | 19 | 16 |  |  |  |  | 8 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 305460
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 496692
63 | Impoprt (Tripura) | 138 | 138 | 134 | 130 | 128 | 112 | 94 | 108 | 112 | 116 | 120 | 130 | 134 | 138 | 142 | 140 | 134 | 162 |  | 156 | 160 | 158 | 150 | 152 | 148 | 138 | 3264960
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 38 | 35 | 7 | 2 | 3 | 2 | 2 | 5 | 4 | 2 | 3 | 7 | 3 |  | 10 | 16 | 19 | 29 | 35 | 42 | 42 | 510720
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | [5 empty] | 19 | 19 | 16 | 13 | 13 | 13 | 13 | 340056
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 237960
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 796900
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 18 | 15 | 15 |  | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 483810
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 31 | 31 | 28 | 28 | 28 | 28 | 22 | 21 | 21 | 21 | 16 | 16 | 20 | 20 | 20 | 20 |  | 28 | 30 | 30 | 31 | 31 | 31 | 31 | 606240
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  |  | 9 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 740600
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 822400
73 | Ghorashal 108MW PP (Regent) | 52 | 52 | 52 | 52 | 52 | 12 | 12 | 12 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 55 | 854136
| Feni Lanka Power | [17 empty] | 114 |  | 52 | 34 | 34 |  |  |  | 0 | 200640
| Chowmuhani 113 MW | 65 | 35 | 35 | 35 | 35 | 35 |  |  | 11 | 36 | 36 | 36 | 40 | 105 | 113 | 110 | 84 | 108 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1695120
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [17 empty] | 50 |  | 90 | 100 | 100 | 40 |  |  | 0 | 299520
78 | Gazipur 52 MW PP | [5 empty] | 3 | 16 | 16 | 32 | 52 | 52 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 834756
79 | Kodda 150MW PP | [17 empty] | 120 |  | 140 | 150 | 150 | 82 | 82 | 64 | 48 | 672480
80 | Jamalpur 95 MW PP(Powerpac) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 449280
81 | Jangalia 52 MW PP (Lakdanavi) | [17 empty] | 25 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 340805
| Gazipur 100 MW PP | 105 | 70 | 70 | 70 | 70 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 |  | 88 | 88 | 88 | 88 | 88 | 88 | 87 | 2082684
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 2 | 3 | 4 | 5 | 5 | 4 | 3 | 2 | 1 | [10 empty] | 29160
| Jodiac Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 29 | 53 | 39 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 898656
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | [13 empty] | 2 | 30 | 30 | 30 | 30 |  | 70 | 97 | 97 | 97 | 97 | 97 | 64 | 694368
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [16 empty] | 18 | 100 | [7 empty] | 0 | 156407
86 | Meghnaghat CCPP(Summit) | 270 | 275 | 250 | 265 | 275 | 240 | 280 | 285 | 265 | 285 | 280 | 260 | 275 | 265 | 255 | 260 | 255 | 255 |  | 260 | 275 | 250 | 285 | 265 | 240 | 255 | 6451375
87 | Meghnaghat 100 MW(IEL) | [17 empty] | 25 |  | 97 | 100 | 100 | 20 |  |  | 0 | 276480
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 47 | 34 | 19 | 17 | 17 | 17 | 27 | 97 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 2033280
88 | Ghorashal 78.5 MW PP(MAX) | [24 empty] | 4 | 50 | 61152
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [17 empty] | 40 |  | 10 | [5 empty] | 0 | 43560
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 50 | 20 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 29 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 707976
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 10 | 10 | 10 | 10 | 30 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 966690
94 | Gagnagar 102 MW PP (Digital Power) | 24 | [8 empty] | 58 | 102 | 102 | 102 | 102 | 102 | 102 | 84 | 102 |  | 102 | 102 | 102 | 102 | 102 | 102 | 50 | 1451376
95 | Patenga 50MW PP (Baraka) | 40 | [7 empty] | 8 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 823200
96 | Chattogram 108 MW PP (ECPV) | [12 empty] | 6 | 46 | 51 | 17 | 17 | 65 |  | 90 | 90 | 90 | 90 | 90 | 72 | 0 | 683520
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | [14 empty] | 15 | 40 | 55 | 55 |  | 40 | 40 | 40 | 30 | 30 | 30 | 15 | 370995
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 55 |  | 55 | 55 | 55 | 17 |  |  | 0 | 214924
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2674063
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 2 | 2 | 2 | 1 | 2 | 2 | 1 | 0 | 0 | [9 empty] | 14750
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 10 | 35 | 35 | 35 | 35 | 35 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1171800
104 | Keranigonj 300 MW PP (APR) | [25 empty] | 0 | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 40 | 24 | 24 | 24 | 24 | 24 |  |  |  | 17 | 50 | 50 | 55 | 96 | 100 | 80 | 60 | 110 |  | 180 | 180 | 180 | 180 | 180 | 180 | 100 | 1946400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [8 empty] | 4 | 16 | 16 | 16 | 17 | 50 | 52 | 50 | 52 | 72 |  | 136 | 149 | 149 | 96 | 52 | 50 | 37 | 885600
115 | Juldah 100 MW PP Unit-3 (Acorn) | 22 | [7 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 384960
116 | Chandpur 200MW (Desh energy) | [17 empty] | 30 | [7 empty] | 0 | 60480
117 | Ashuganj 150MW PP (Midland) | 30 | [11 empty] | 26 | 71 | 118 | 128 | 132 | 128 |  | 128 | 130 | 132 | 137 | 137 | 137 | 135 | 1488727
118 | Bibiyana-III 400 MW CCPP | 400 | 401 | 375 | 377 | 353 | 303 | 305 | 314 | 352 | 353 | 402 | 403 | 404 | 404 | 404 | 403 | 402 | 402 |  | 401 | 401 | 401 | 402 | 402 | 402 | 402 | 9210000
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 115 | 85 | 55 | 55 | 55 | 67 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2560800
| Anwara 300 MW PP (United) | 161 | 87 | 87 | 87 | 88 | 34 |  |  | 65 | 71 | 71 | 122 | 140 | 142 | 142 | 142 | 105 | 157 |  | 162 | 162 | 162 | 162 | 162 | 162 | 161 | 2664655
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 60 | 60 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2362560
120 | Eastern Zone Total | 6217 | 5978 | 5757 | 5635 | 5467 | 5163 | 5060 | 5126 | 5554 | 5989 | 6223 | 6608 | 6543 | 6759 | 6645 | 6558 | 6285 | 7341 |  | 7804 | 7851 | 7824 | 7456 | 7252 | 7143 | 6764 | 154538457
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [17 empty] | 96 |  | 99 | 99 | 103 | 115 | 74 | 49 | 0 | 521280
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 8 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 |  | 116040
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | [7 empty] | 53 | 53 | 53 | 90 | 90 | 90 | 90 | 90 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1509600
130
131
132
133 | Bhola Nutan Biddut BD LTD (GAS)
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [16 empty] | 16 | 64 |  | 64 | 64 | 64 | 64 | 64 | 64 | 16 | 431040
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 95 | 94 | 95 | 78 | 78 | 58 | 46 | 46 | 46 | 45 | 63 | 86 | 87 | 85 | 88 | 90 | 92 | 95 |  | 95 | 92 | 92 | 93 | 94 | 94 | 94 | 1938006
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 25 | 24 | 22 | 21 | 19 | 18 | 15 | 15 | 14 | 14 | 15 | 16 | 18 | 19 | 20 | 18 | 19 | 27 |  | 27 | 27 | 31 | 31 | 34 | 34 | 32 | 519678
141 | Noapara 100 MW PP (Bangla Trac) | [17 empty] | 5 |  | 20 | [5 empty] | 0 | 34560
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 40 |  | 40 | 40 | 40 | 40 | 40 |  |  | 194250
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 5 | [9 empty] | 2432
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 931 | 931 | 931 | 931 | 930 | 931 | 931 | 930 | 929 | 931 | 931 | 932 | 932 | 933 | 933 | 932 | 932 | 931 |  | 931 | 932 | 932 | 932 | 932 | 932 | 931 | 22346181
147 | Bheramara 410 MW CCPP | 345 | 345 | 340 | 340 | 345 | 345 | 345 | 370 | 345 | 345 | 345 | 345 | 345 | 270 | 345 | 345 | 270 | 410 |  | 345 | 345 | 345 | 380 | 345 | 345 | 340 | 8498304
148 | Payra 1320 MW | 570 | 560 | 560 | 550 | 500 | 460 | 460 | 460 | 460 | 460 | 460 | 470 | 480 | 480 | 490 | 500 | 460 | 450 |  | 530 | 570 | 570 | 580 | 570 | 550 | 550 | 13021400
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 149 | 149 | 149 | 149 | 149 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 3676200
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [15 empty] | 9 | 9 | 43 | [8 empty] | 69266
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 183 | 183 | 160 | 148 | 140 | 140 | 140 | 141 | 157 | 162 | 165 | 182 | 195 | 169 | 167 | 155 | 150 | 143 |  | 156 | 155 | 155 | 166 | 165 | 155 | 155 | 4055545
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 187 | 187 | 165 | 155 | 156 | 155 | 155 | 166 | 165 | 160 | 175 | 193 | 193 | 171 | 165 | 157 | 150 | 154 |  | 161 | 161 | 159 | 167 | 166 | 156 | 156 | 4226245
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 380 | 374 | 360 | 290 | 324 | 290 | 344 | 345 | 307 | 344 | 345 | 401 | 409 | 335 | 410 | 320 | 314 | 353 |  | 394 | 419 | 388 | 415 | 416 | 383 | 390 | 8842454
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 474240
163 | Bogura 20 MW PP (Energyprima) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 229212
164 | Ullapara 11 MW PP (Summit) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 157500
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 137190
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [17 empty] | 31 |  | 35 | 30 | [5 empty] | 70508
168 | Santahar 50 MW Peaking PP | [17 empty] | 21 | [7 empty] | 0 | 25380
169 | Natore 52 MW PP (Rajlanka) | [17 empty] | 32 |  | 8 | [5 empty] | 0 | 42240
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 60 |  | 48 | 24 | 10 |  |  |  |  | 102877
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [17 empty] | 57 |  | 35 | 35 | 35 |  |  |  | 0 | 189408
172 | Confidence Power Bogura Unit-1 113 MW | 35 | [12 empty] | 35 | 90 | 70 | 35 | 90 |  | 109 | 109 | 109 | 109 | 109 | 109 | 70 | 993600
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | [22 empty] | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | [13 empty] | 6 | 51 | 76 | 56 | 59 |  | 100 | 98 | 98 | 100 | 100 | 98 | 76 | 880320
177 | Sympa Solar Power 8MW | [6 empty] | 1 | 2 | 3 | 4 | 4 | 6 | 6 | 4 | 3 | 2 | 0 | [9 empty] | 41011
178
178