## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-10-30 | Friday
|  |  | Date (day): | 2020-10-30 |  | Friday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13786.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14868 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-10-29 | 2020-10-30 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 115 | 115 | 115 | 75 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 200 | 200 | 165 |  | Gas shortage
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 68 | 69 | 78 | 78
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 72 | 75 | 75 | 75 | 33 |  | Machine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under S/D for dust in gas.
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 289 | 293 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 320 | 320 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 35 | 95 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 270 | 240 | 305 | 305
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 64 | 97 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 35 | 55 | 40 | 40 |  | 15 | Engine problem
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 96 | 50 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19 |  | 3 | Engine problem
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 155 | 120 | 200 | 200
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 45 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 102 | 102 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 150 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 49 | 55 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 51 | 51 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 165 | 300 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 82 | 135 | 134 | 134 |  | 15 | Engine problem
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 87 | 87 | 88 | 88 |  | 17 | Engine problem
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 17 | 17
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 2533 | 3088 | 3528 | 3868 | 537 | 1392
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 115 | 115 | 120 | 120 | 60 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 162 | 158 | 160 | 160 | 70 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 205 | 204 | 221 | 221
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 139 | 139 | 145 | 145
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 102 | 102
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 70 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 22 | 22 | 22 | 22
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 15 | 30 | 30
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 81 | 90 | 90 |  | 18 | Engine problem
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 158 | 142 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 90 | 100 | 100
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 1053 | 1287 | 1774 | 1749 | 310 | 116
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 80 | 80 | 80 | 80 | 49 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 |  | 134 | Under maint
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 178 | 185 | 225 | 225 |  |  | FGMO
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 275 | 360 | 360
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 275 | 350 | 350 |  |  | FGMO
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 10 | 29 | 29 | 16 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 43 | 43 |  | 8 | Engine problem
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 75 | 142 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 42 | 25 | 50
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 75 | 70 | 75 | 75 |  | 68 | ST under maint.
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 79 | 164 | 164
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 13 | 13 | 22 | 22
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 98 | 164 | 163 | 173
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 10 | 52 | 25 | 52
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 21 | 20 | 20 |  | 5 | Engine problem
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 114 | 17 | 114
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 92 | 113 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1250 | 1743 | 1918 | 2277 | 437 | 215
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 101 | 103 | 150 | 150 | 52 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 25 | 25 | 25 | 25 |  | 70 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 16 | 195 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
|  | Mymensingh PV 50 MW Solar PP |  | Solar | IPP | 0 | 50 MW | 50 MW | 43 | 0 | 40 | 0
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 324 | 460 | 553.6 | 512 | 52 | 70
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 86 | 86 | 86 | 86
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Unit-4 under shut down
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 |  | 54 | STG under maint.
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 160 | 159 | 160 | 160 |  | 170 | GT-2 S/D due to gas shortage.
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 53 | 53 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 48 | 49 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 50 | 65 | 65 | 65 |  |  | FGMO
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 84 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 171 | 204 | 180 | 200
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 290 | 341 | 341 |  |  | FGMO
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 403 | 415 | 400 | 400
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1557 | 1608 | 1617 | 1637 | 0 | 284
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 932 | 932 | 943 | 943
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 115 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 220 | 220
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 345 | 345 | 410 | 410
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 88 | 105 | 105 | 105
| 108 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Bhola Nutan Biddut BD LTD (GAS) |  | Gas/HSD | IPP | 0 | 220 MW | 220 MW | 0 | 40 | 0 | 0
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1365 | 1577 | 1983 | 2139 | 0 | 0
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 32 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 25 | 32 | 33 | 33
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 85 | 95 | 95 | 95
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 460 | 622 | 500 | 530
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 570 | 781 | 738 | 768 | 0 | 194
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 32 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 20 | 20 | 20 |  | 30 | Engine problem
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 31 | 50 | 50
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 186 | 185 | 225 | 225 |  |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 173 | 171 | 220 | 220 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 365 | 380 | 285 | 414 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 32
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 10 | 10 | 10 | 10
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 52 | 52 | 52
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 96 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 92 | 113 | 113
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 80 | 109 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 840 | 1289 | 1417 | 1668 | 431 | 34
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 41 | 102 | 100 | 100 |  | 13
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 197 | 252 | 258 | 250 | 294 | 53
|  | Total |  |  |  |  | 20383 | 19892 | 9689 | 12085 | 13786.6 | 14868 | 2061 | 2358
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9182.3018 | 11453 | 13065.6127 | 14090.4596
| A. |  | 2020-10-29 | (Yesterday) |  |  |  |  | Thursday
| 1 | Highest Generation : |  |  | 12085 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 7802 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12085 | MW
| 3 | Day peak Generation : |  |  | 9689 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11453 | MW
| 4 | Evening peak Generation : |  |  | 12085 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 236.9241 | MKWHr | By Solar | 0.57181 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 137.4844 | MKWHr |  | By Oil: | 52.9452 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 16.7321 | MKWHr |  | By Hydro: | 3.7216 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2061 | MW | Dhaka | 4220 | 4220 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2358 | MW | Chittagong | 1265 | 1265 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4419 | MW | Khulna | 1332 | 1332 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1147.44 | MMCFD |  |  | Rajshahi | 1132 | 1132 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 161984018.472 | ii) Oil : | Taka | 375545289.46 | Comilla | 1121 | 1121 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 77220217 | Total | Taka | 614749524.932 | Mymensingh | 903 | 903 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 509 | 509 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 197 | MW (E to W) at | 19:00 | hrs | Barisal | 299 | 299 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 107 | MW at | 22:00 | hrs | Rangpur | 672 | 672 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.5° C |  |  | Total | 11453 | 11453 |  | 0
| B. |  | 2020-10-30 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 35.0° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 11300 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14868 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 8500 | MW
| 4 | Reserve(Generation end) |  |  |  | 3568 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 221.5343 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7368 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.3585 | MKWHr. | ii) HVDC Flow at Peak Time |  | 932 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.1104 | MKWHr. | iii) Maximum HVDC Flow : |  | 933 | MW at | 5:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 103.97 |  | (b) Today: | 103.91 |  | (c) Rule Curve: |  | 108.8
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-10-29
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Mymensingh PV 50 MW Solar PP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 115 | 200 | 66 | 74 | 0 | 302 |  | 0 | 320 | 265 | 0 | 15 | 0 | 0 | 0 | 180 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 19 | 25 | 31 | 28 | 33 | 25 | 0 | 86 | 70 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 42 | 0 | 80 | 0 | 280 | 310 | 180 | 8 | 76 | 29 | 20 | 0 | 43 | 0 | 0 | 0 | 13 | 11 | 33 | 21 | 136 | 106 | 25 | 22 | 0 | 87 | 30 | 53 | 50 | 110 | 156 | 52 | 84 | 0 | 170 | 18 | 0 | 9 | 275 | 24 | 11 | 0 | 30 | 0 | 0 | 50 | 0 | 0 | 0 | 22 | 0 | 80 | 402 | 115 | 87 | 0 | 0 | 162 | 54 | 0 | 0 | 113 | 100 | 0 | 104 | 0 |  | 932 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 155 | 0 | 94 | 0 | 155 | 0 | 410 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 0 |  | 6386 | 2958 | 9344 | 3878 | 932 | 2019 | 1507 | 700 | 156 | 16 | 136 | 0 | 0 | 103.97
2:00 | 0 | 0 | 0 | 115 | 200 | 67 | 74 | 0 | 302 |  | 0 | 340 | 255 | 0 | 10 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 19 | 25 | 31 | 28 | 33 | 25 | 0 | 83 | 70 | 115 | 0 | 0 | 204 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 42 | 0 | 80 | 0 | 280 | 310 | 180 | 8 | 74 | 29 | 30 | 0 | 43 | 0 | 0 | 0 | 13 | 11 | 33 | 21 | 132 | 106 | 25 | 22 | 0 | 87 | 30 | 53 | 50 | 110 | 158 | 52 | 84 | 0 | 170 | 18 | 0 | 9 | 290 | 24 | 8 | 0 | 30 | 0 | 0 | 24 | 0 | 0 | 0 | 22 | 0 | 30 | 402 | 115 | 87 | 0 | 0 | 88 | 54 | 0 | 0 | 85 | 100 | 0 | 104 | 0 |  | 932 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 155 | 0 | 94 | 0 | 156 | 0 | 394 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 0 |  | 6196 | 2909 | 9105 | 3882 | 932 | 2046 | 1245 | 699 | 153 | 16 | 132 | 0 | 0 | 103.97
3:00 | 0 | 0 | 0 | 115 | 200 | 65 | 74 | 0 | 302 |  | 0 | 360 | 265 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 19 | 25 | 31 | 28 | 33 | 25 | 0 | 84 | 70 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 42 | 20 | 42 | 0 | 80 | 0 | 280 | 310 | 180 | 8 | 76 | 29 | 30 | 0 | 43 | 0 | 0 | 0 | 13 | 8 | 33 | 21 | 130 | 106 | 25 | 22 | 0 | 86 | 30 | 53 | 50 | 110 | 158 | 52 | 84 | 0 | 170 | 18 | 0 | 9 | 270 | 24 | 8 | 0 | 15 | 0 | 0 | 24 | 0 | 0 | 0 | 22 | 0 | 0 | 377 | 115 | 82 | 0 | 0 | 34 | 54 | 0 | 0 | 65 | 100 | 0 | 104 | 0 |  | 932 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 155 | 0 | 94 | 0 | 156 | 0 | 394 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 0 | 0 |  | 5987 | 2824 | 8811 | 3824 | 932 | 2042 | 1060 | 669 | 154 | 0 | 130 | 0 | 0 | 103.97
4:00 | 0 | 0 | 0 | 115 | 200 | 65 | 74 | 0 | 302 |  | 0 | 370 | 270 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 19 | 25 | 31 | 28 | 33 | 8 | 0 | 85 | 70 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 0 | 80 | 0 | 280 | 310 | 180 | 8 | 75 | 29 | 30 | 0 | 43 | 0 | 0 | 0 | 13 | 8 | 0 | 21 | 128 | 106 | 25 | 22 | 0 | 86 | 30 | 53 | 50 | 110 | 159 | 52 | 84 | 0 | 170 | 18 | 0 | 9 | 265 | 24 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 22 | 0 | 0 | 339 | 85 | 70 | 0 | 0 | 16 | 54 | 0 | 0 | 65 | 100 | 0 | 97 | 0 |  | 931 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 155 | 0 | 65 | 0 | 155 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 0 | 0 |  | 5765 | 2753 | 8518 | 3752 | 931 | 1995 | 888 | 669 | 155 | 0 | 128 | 0 | 0 | 103.97
5:00 | 0 | 0 | 0 | 115 | 200 | 65 | 74 | 0 | 302 |  | 0 | 370 | 265 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 19 | 25 | 31 | 28 | 33 | 8 | 0 | 86 | 70 | 115 | 0 | 0 | 204 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 0 | 80 | 0 | 280 | 310 | 180 | 8 | 77 | 29 | 30 | 0 | 43 | 0 | 0 | 0 | 13 | 8 | 0 | 21 | 122 | 106 | 25 | 22 | 0 | 87 | 30 | 53 | 50 | 110 | 158 | 52 | 50 | 0 | 170 | 18 | 0 | 9 | 290 | 24 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 22 | 0 | 0 | 342 | 65 | 70 | 0 | 0 | 16 | 54 | 0 | 0 | 45 | 100 | 0 | 50 | 0 |  | 933 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 154 | 0 | 45 | 0 | 155 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 0 | 0 |  | 5619 | 2715 | 8334 | 3727 | 933 | 1946 | 780 | 670 | 156 | 0 | 122 | 0 | 0 | 103.97
6:00 | 0 | 0 | 0 | 115 | 200 | 65 | 74 | 0 | 302 |  | 0 | 370 | 245 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 19 | 25 | 31 | 28 | 33 | 8 | 0 | 88 | 70 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0 | 80 | 0 | 280 | 310 | 180 | 8 | 76 | 29 | 10 | 0 | 43 | 0 | 0 | 0 | 13 | 0 | 0 | 8 | 110 | 108 | 25 | 22 | 0 | 87 | 30 | 53 | 50 | 110 | 160 | 52 | 50 | 0 | 170 | 18 | 0 | 9 | 280 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 22 | 0 | 0 | 341 | 45 | 70 | 0 | 0 | 0 | 17 | 0 | 0 | 45 | 30 | 0 | 33 | 0 |  | 933 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 155 | 0 | 34 | 0 | 155 | 0 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 0 | 0 |  | 5381 | 2635 | 8016 | 3703 | 933 | 1878 | 604 | 630 | 158 | 0 | 110 | 0 | 0 | 103.97
7:00 | 0 | 0 | 0 | 115 | 200 | 65 | 40 | 0 | 302 |  | 0 | 370 | 280 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 19 | 25 | 31 | 28 | 33 | 18 | 0 | 92 | 70 | 115 | 0 | 0 | 210 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 34 | 0 | 80 | 0 | 300 | 310 | 195 | 8 | 85 | 26 | 10 | 0 | 10 | 0 | 0 | 0 | 16 | 8 | 0 | 15 | 100 | 106 | 25 | 22 | 0 | 87 | 30 | 11 | 10 | 110 | 158 | 51 | 10 | 0 | 170 | 18 | 0 | 9 | 265 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 4 | 22 | 0 | 0 | 342 | 35 | 70 | 0 | 1 | 0 | 17 | 0 | 0 | 27 | 10 | 0 | 17 | 12 |  | 932 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 155 | 0 | 25 | 0 | 156 | 0 | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 430 | 0 | 0 |  | 5224 | 2578 | 7802 | 3722 | 932 | 1703 | 585 | 580 | 162 | 0 | 100 | 18 | 0 | 103.97
8:00 | 0 | 0 | 0 | 115 | 200 | 68 | 40 | 0 | 302 |  | 0 | 370 | 275 | 0 | 0 | 0 | 0 | 0 | 122 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 40 | 17 | 17 | 19 | 25 | 31 | 33 | 33 | 26 | 0 | 92 | 70 | 115 | 0 | 0 | 207 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 0 | 80 | 0 | 285 | 310 | 190 | 8 | 80 | 26 | 10 | 0 | 10 | 0 | 0 | 0 | 16 | 11 | 0 | 15 | 100 | 106 | 25 | 22 | 1 | 86 | 30 | 11 | 10 | 110 | 156 | 51 | 10 | 0 | 171 | 18 | 0 | 9 | 310 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 10 | 22 | 0 | 1 | 341 | 25 | 72 | 0 | 2 | 50 | 17 | 0 | 0 | 27 | 50 | 0 | 19 | 26 |  | 932 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 174 | 0 | 25 | 0 | 183 | 0 | 380 | 17 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 430 | 0 | 0 |  | 5391 | 2648 | 8039 | 3739 | 932 | 1731 | 754 | 580 | 162 | 0 | 100 | 41 | 0 | 103.96
9:00 | 0 | 0 | 0 | 115 | 200 | 68 | 50 | 0 | 303 |  | 0 | 350 | 250 | 1 | 12 | 7 | 0 | 0 | 120 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 19 | 25 | 10 | 33 | 33 | 51 | 0 | 92 | 70 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 37 | 20 | 5 | 0 | 80 | 0 | 280 | 310 | 182 | 8 | 75 | 27 | 30 | 0 | 16 | 0 | 0 | 0 | 16 | 11 | 0 | 15 | 104 | 106 | 25 | 22 | 2 | 86 | 30 | 33 | 14 | 110 | 158 | 51 | 84 | 0 | 171 | 18 | 0 | 9 | 300 | 24 | 5 | 0 | 18 | 0 | 0 | 0 | 0 | 67 | 15 | 22 | 0 | 10 | 386 | 43 | 87 | 0 | 3 | 50 | 51 | 0 | 0 | 27 | 88 | 0 | 104 | 39 |  | 932 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 159 | 0 | 25 | 0 | 171 | 0 | 335 | 53 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 430 | 0 | 0 |  | 5879 | 2613 | 8492 | 3721 | 932 | 1790 | 1141 | 580 | 162 | 0 | 104 | 62 | 0 | 103.96
10:00 | 0 | 0 | 0 | 115 | 200 | 68 | 70 | 0 | 303 |  | 0 | 320 | 285 | 7 | 15 | 15 | 0 | 0 | 120 | 0 | 7 | 50 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 19 | 25 | 30 | 33 | 33 | 51 | 0 | 92 | 70 | 115 | 0 | 0 | 216 | 0 | 142 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 3 | 0 | 80 | 0 | 300 | 280 | 210 | 8 | 80 | 27 | 30 | 0 | 35 | 0 | 0 | 0 | 16 | 8 | 0 | 15 | 108 | 102 | 25 | 22 | 2 | 86 | 30 | 47 | 25 | 110 | 160 | 50 | 84 | 0 | 171 | 18 | 0 | 9 | 290 | 24 | 8 | 0 | 95 | 0 | 0 | 0 | 0 | 100 | 18 | 22 | 0 | 10 | 404 | 75 | 87 | 0 | 4 | 53 | 54 | 0 | 0 | 27 | 100 | 0 | 104 | 46 |  | 932 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 169 | 0 | 25 | 0 | 164 | 0 | 398 | 53 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 430 | 0 | 0 |  | 6221 | 2681 | 8902 | 3797 | 932 | 1876 | 1373 | 580 | 162 | 0 | 108 | 74 | 0 | 103.96
11:00 | 0 | 0 | 0 | 115 | 200 | 72 | 69 | 0 | 293 |  | 0 | 320 | 280 | 15 | 18 | 15 | 0 | 0 | 150 | 0 | 18 | 84 | 10 | 0 | 0 | 0 | 0 | 54 | 35 | 17 | 19 | 25 | 10 | 33 | 33 | 51 | 0 | 92 | 70 | 115 | 0 | 0 | 205 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 3 | 0 | 80 | 0 | 285 | 280 | 154 | 8 | 80 | 27 | 10 | 0 | 43 | 0 | 0 | 0 | 13 | 8 | 0 | 15 | 88 | 100 | 25 | 22 | 2 | 86 | 30 | 50 | 49 | 110 | 158 | 50 | 84 | 0 | 171 | 18 | 0 | 9 | 310 | 24 | 11 | 0 | 130 | 0 | 0 | 10 | 0 | 78 | 19 | 22 | 0 | 20 | 404 | 100 | 87 | 0 | 5 | 105 | 54 | 0 | 0 | 55 | 100 | 0 | 104 | 53 |  | 932 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 203 | 0 | 54 | 0 | 177 | 0 | 400 | 70 | 0 | 0 | 0 | 9 | 0 | 6 | 25 | 430 | 0 | 0 |  | 6376 | 2861 | 9237 | 3813 | 932 | 1936 | 1631 | 580 | 162 | 10 | 88 | 85 | 0 | 103.96
12:00 | 0 | 0 | 0 | 115 | 200 | 72 | 68 | 0 | 289 |  | 0 | 320 | 270 | 35 | 64 | 35 | 0 | 0 | 155 | 0 | 45 | 102 | 16 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 19 | 25 | 24 | 33 | 33 | 51 | 0 | 92 | 70 | 115 | 0 | 0 | 205 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 5 | 0 | 80 | 0 | 260 | 280 | 178 | 8 | 75 | 10 | 5 | 0 | 43 | 0 | 0 | 10 | 13 | 8 | 0 | 15 | 98 | 101 | 25 | 22 | 2 | 86 | 30 | 53 | 48 | 110 | 160 | 50 | 84 | 0 | 171 | 18 | 0 | 9 | 300 | 24 | 11 | 0 | 165 | 0 | 0 | 16 | 0 | 82 | 18 | 22 | 0 | 75 | 403 | 115 | 87 | 0 | 5 | 158 | 54 | 0 | 0 | 92 | 100 | 0 | 104 | 43 |  | 932 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 186 | 0 | 85 | 0 | 173 | 0 | 365 | 88 | 0 | 0 | 0 | 41 | 0 | 6 | 80 | 460 | 0 | 0 |  | 6717 | 2972 | 9689 | 3790 | 932 | 1917 | 2090 | 610 | 162 | 16 | 98 | 74 | 0 | 103.96
13:00 | 0 | 0 | 0 | 115 | 200 | 72 | 68 | 0 | 283 |  | 0 | 320 | 250 | 82 | 80 | 55 | 0 | 0 | 154 | 0 | 90 | 102 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 30 | 33 | 33 | 51 | 0 | 88 | 70 | 115 | 0 | 0 | 205 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 2 | 50 | 20 | 7 | 0 | 80 | 0 | 260 | 280 | 212 | 8 | 75 | 10 | 5 | 0 | 43 | 0 | 0 | 25 | 13 | 8 | 0 | 15 | 106 | 82 | 25 | 20 | 2 | 86 | 30 | 53 | 46 | 110 | 160 | 50 | 84 | 0 | 171 | 18 | 0 | 9 | 300 | 24 | 11 | 0 | 195 | 0 | 0 | 31 | 0 | 80 | 13 | 22 | 0 | 117 | 403 | 115 | 87 | 0 | 4 | 162 | 54 | 0 | 0 | 113 | 100 | 0 | 104 | 52 |  | 932 | 0 | 340 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 184 | 0 | 90 | 0 | 187 | 0 | 356 | 90 | 0 | 0 | 0 | 74 | 0 | 6 | 109 | 470 | 0 | 0 |  | 6991 | 3054 | 10045 | 3815 | 932 | 1907 | 2415 | 619 | 158 | 16 | 106 | 77 | 10045 | 103.96
14:00 | 0 | 0 | 0 | 115 | 200 | 72 | 40 | 0 | 284 |  | 0 | 320 | 285 | 98 | 88 | 55 | 0 | 0 | 120 | 0 | 99 | 102 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 30 | 33 | 33 | 51 | 0 | 86 | 70 | 115 | 0 | 0 | 212 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 28 | 50 | 20 | 4 | 0 | 80 | 0 | 280 | 280 | 211 | 8 | 75 | 10 | 5 | 0 | 43 | 0 | 0 | 28 | 13 | 11 | 0 | 19 | 108 | 83 | 25 | 22 | 1 | 84 | 30 | 53 | 46 | 110 | 159 | 50 | 84 | 0 | 171 | 18 | 0 | 9 | 290 | 24 | 11 | 0 | 195 | 0 | 0 | 40 | 0 | 80 | 17 | 22 | 0 | 130 | 404 | 115 | 87 | 0 | 4 | 162 | 54 | 0 | 0 | 113 | 100 | 0 | 104 | 44 |  | 932 | 0 | 300 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 164 | 0 | 88 | 0 | 172 | 0 | 340 | 105 | 0 | 0 | 0 | 89 | 0 | 5 | 109 | 470 | 0 | 0 |  | 7030 | 3016 | 10046 | 3705 | 932 | 1849 | 2590 | 619 | 156 | 16 | 108 | 71 | 0 | 103.96
15:00 | 0 | 0 | 0 | 115 | 200 | 72 | 50 | 0 | 288 |  | 0 | 320 | 260 | 100 | 97 | 55 | 0 | 0 | 120 | 0 | 99 | 102 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 26 | 33 | 33 | 51 | 0 | 87 | 70 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 30 | 50 | 20 | 2 | 0 | 80 | 0 | 275 | 330 | 213 | 8 | 71 | 10 | 5 | 0 | 43 | 0 | 0 | 43 | 13 | 11 | 33 | 20 | 112 | 83 | 25 | 22 | 1 | 82 | 30 | 53 | 47 | 110 | 158 | 50 | 84 | 0 | 204 | 18 | 0 | 9 | 300 | 24 | 11 | 0 | 243 | 0 | 0 | 40 | 0 | 85 | 9 | 22 | 0 | 140 | 403 | 115 | 87 | 0 | 2 | 142 | 54 | 0 | 0 | 112 | 100 | 0 | 104 | 30 |  | 933 | 0 | 340 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 18 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 159 | 0 | 91 | 0 | 169 | 0 | 394 | 105 | 0 | 0 | 0 | 99 | 0 | 3 | 109 | 470 | 0 | 0 |  | 7208 | 3135 | 10343 | 3866 | 933 | 1929 | 2665 | 620 | 157 | 16 | 112 | 45 | 0 | 103.96
16:00 | 0 | 0 | 0 | 115 | 200 | 72 | 60 | 0 | 292 |  | 0 | 320 | 280 | 75 | 64 | 15 | 0 | 0 | 120 | 0 | 70 | 102 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 19 | 25 | 21 | 33 | 33 | 51 | 0 | 88 | 70 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 5 | 0 | 80 | 0 | 275 | 300 | 210 | 8 | 76 | 10 | 5 | 0 | 10 | 0 | 0 | 25 | 0 | 11 | 33 | 20 | 108 | 100 | 25 | 22 | 0 | 81 | 30 | 50 | 47 | 110 | 159 | 50 | 40 | 0 | 204 | 18 | 0 | 9 | 290 | 24 | 11 | 0 | 245 | 0 | 0 | 40 | 0 | 82 | 6 | 22 | 0 | 140 | 403 | 115 | 87 | 0 | 1 | 142 | 54 | 0 | 0 | 113 | 100 | 0 | 104 | 13 |  | 932 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 18 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 156 | 0 | 93 | 0 | 162 | 0 | 334 | 105 | 0 | 0 | 0 | 35 | 0 | 2 | 35 | 470 | 25 | 0 |  | 6888 | 2925 | 9813 | 3832 | 932 | 1823 | 2302 | 620 | 158 | 16 | 108 | 22 | 0 | 103.96
17:00 | 0 | 0 | 0 | 115 | 200 | 23 | 40 | 0 | 298 |  | 0 | 320 | 250 | 71 | 64 | 15 | 0 | 0 | 75 | 0 | 65 | 102 | 82 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 19 | 25 | 21 | 33 | 33 | 51 | 0 | 88 | 70 | 115 | 0 | 0 | 204 | 0 | 70 | 0 |  | 0 | 0 | 29 | 0 | 12 | 50 | 20 | 12 | 0 | 80 | 0 | 275 | 295 | 180 | 8 | 70 | 10 | 5 | 0 | 10 | 0 | 0 | 28 | 0 | 8 | 33 | 20 | 124 | 102 | 25 | 22 | 0 | 82 | 30 | 53 | 48 | 110 | 158 | 51 | 40 | 0 | 180 | 18 | 0 | 10 | 270 | 24 | 3 | 0 | 249 | 0 | 0 | 40 | 0 | 84 | 0 | 22 | 0 | 140 | 352 | 115 | 87 | 0 | 0 | 106 | 54 | 0 | 52 | 113 | 90 | 0 | 104 | 1 |  | 932 | 0 | 320 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 7 | 15 | 0 | 20 | 0 | 18 | 8 | 11 | 18 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 156 | 0 | 95 | 0 | 145 | 0 | 258 | 90 | 0 | 8 | 0 | 35 | 0 | 0 | 35 | 400 | 30 | 0 |  | 6677 | 2809 | 9486 | 3552 | 932 | 1682 | 2325 | 550 | 158 | 162 | 124 | 1 | 0 | 103.95
18:00 | 0 | 0 | 0 | 115 | 200 | 75 | 60 | 0 | 304 |  | 0 | 320 | 285 | 93 | 85 | 45 | 0 | 0 | 120 | 0 | 100 | 102 | 145 | 43 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 28 | 33 | 33 | 51 | 0 | 88 | 70 | 115 | 0 | 20 | 218 | 0 | 140 | 0 |  | 0 | 0 | 102 | 40 | 52 | 50 | 20 | 10 | 0 | 80 | 0 | 310 | 275 | 205 | 8 | 75 | 10 | 5 | 0 | 22 | 0 | 16 | 50 | 0 | 11 | 33 | 21 | 164 | 102 | 25 | 22 | 0 | 85 | 30 | 53 | 37 | 110 | 157 | 63 | 84 | 0 | 204 | 18 | 0 | 10 | 270 | 24 | 3 | 0 | 287 | 0 | 0 | 82 | 0 | 113 | 0 | 22 | 33 | 142 | 416 | 115 | 87 | 0 | 0 | 143 | 54 | 0 | 114 | 113 | 90 | 0 | 104 | 0 |  | 931 | 0 | 390 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 35 | 45 | 0 | 0 | 0 | 50 | 15 | 97 | 20 | 0 | 30 | 35 | 32 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 170 | 0 | 95 | 0 | 157 | 0 | 400 | 105 | 0 | 90 | 0 | 60 | 0 | 0 | 90 | 400 | 40 | 0 |  | 7847 | 3631 | 11478 | 3938 | 931 | 1966 | 3284 | 550 | 158 | 487 | 164 | 0 | 0 | 103.95
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 115 | 200 | 75 | 69 | 0 | 293 |  | 0 | 320 | 240 | 95 | 97 | 55 | 0 | 0 | 120 | 0 | 100 | 102 | 150 | 96 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 30 | 33 | 33 | 51 | 0 | 88 | 70 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 102 | 70 | 81 | 50 | 20 | 15 | 0 | 80 | 0 | 275 | 275 | 185 | 8 | 70 | 10 | 5 | 0 | 51 | 0 | 42 | 52 | 13 | 11 | 33 | 21 | 164 | 103 | 25 | 22 | 0 | 86 | 30 | 53 | 49 | 110 | 159 | 65 | 84 | 0 | 204 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 300 | 0 | 0 | 195 | 0 | 135 | 0 | 22 | 79 | 142 | 415 | 115 | 87 | 0 | 0 | 142 | 54 | 0 | 114 | 113 | 90 | 0 | 104 | 0 |  | 932 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 32 | 32 | 0 | 0 | 0 | 50 | 32 | 96 | 20 | 0 | 31 | 52 | 32 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 171 | 0 | 380 | 105 | 0 | 92 | 0 | 102 | 0 | 0 | 109 | 622 | 40 | 0 |  | 8186 | 3899 | 12085 | 3875 | 932 | 2007 | 3642 | 772 | 158 | 535 | 164 | 0 | 0 | 103.95
19:30 | 0 | 0 | 0 | 115 | 200 | 75 | 69 | 0 | 287 |  | 0 | 320 | 275 | 100 | 97 | 55 | 0 | 0 | 160 | 0 | 100 | 102 | 150 | 50 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 30 | 33 | 33 | 51 | 0 | 88 | 70 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 102 | 30 | 84 | 50 | 20 | 22 | 0 | 70 | 0 | 260 | 260 | 177 | 8 | 76 | 10 | 5 | 0 | 51 | 0 | 42 | 52 | 13 | 11 | 33 | 21 | 162 | 103 | 25 | 22 | 0 | 86 | 30 | 53 | 49 | 110 | 157 | 63 | 84 | 0 | 204 | 18 | 0 | 10 | 305 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 22 | 17 | 142 | 417 | 115 | 87 | 0 | 0 | 143 | 54 | 0 | 114 | 113 | 90 | 0 | 104 | 0 |  | 932 | 0 | 350 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 33 | 32 | 0 | 0 | 0 | 50 | 35 | 96 | 20 | 0 | 31 | 52 | 32 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 159 | 0 | 95 | 0 | 162 | 0 | 337 | 105 | 0 | 92 | 0 | 109 | 0 | 0 | 109 | 622 | 40 | 0 |  | 8111 | 3837 | 11948 | 3841 | 932 | 1981 | 3564 | 772 | 158 | 538 | 162 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 115 | 200 | 76 | 69 | 0 | 283 |  | 0 | 320 | 255 | 100 | 97 | 55 | 0 | 0 | 160 | 0 | 100 | 102 | 150 | 61 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 30 | 33 | 33 | 51 | 0 | 89 | 70 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 102 | 30 | 84 | 50 | 20 | 22 | 0 | 70 | 0 | 260 | 260 | 168 | 8 | 71 | 10 | 5 | 0 | 51 | 0 | 25 | 52 | 13 | 11 | 33 | 21 | 162 | 103 | 25 | 20 | 0 | 86 | 30 | 53 | 49 | 110 | 157 | 63 | 84 | 0 | 204 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 22 | 17 | 142 | 416 | 115 | 87 | 0 | 0 | 143 | 54 | 0 | 114 | 113 | 90 | 0 | 104 | 0 |  | 932 | 0 | 345 | 0 | 116 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 33 | 32 | 0 | 0 | 0 | 50 | 25 | 96 | 20 | 0 | 30 | 52 | 31 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 156 | 0 | 96 | 0 | 168 | 0 | 303 | 105 | 0 | 94 | 0 | 109 | 0 | 0 | 109 | 622 | 40 | 0 |  | 8051 | 3793 | 11844 | 3822 | 932 | 1930 | 3558 | 772 | 159 | 509 | 162 | 0 | 0 | 103.95
21:00 | 0 | 0 | 0 | 115 | 200 | 76 | 70 | 0 | 272 |  | 0 | 320 | 270 | 100 | 97 | 55 | 0 | 0 | 190 | 0 | 100 | 102 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 30 | 33 | 33 | 51 | 0 | 89 | 70 | 115 | 0 | 25 | 204 | 0 | 139 | 0 |  | 0 | 0 | 102 | 0 | 84 | 50 | 20 | 30 | 0 | 70 | 0 | 260 | 260 | 159 | 8 | 50 | 5 | 0 | 0 | 51 | 0 | 0 | 52 | 13 | 11 | 33 | 21 | 156 | 103 | 25 | 20 | 0 | 85 | 30 | 53 | 49 | 110 | 157 | 63 | 84 | 0 | 204 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 22 | 0 | 142 | 416 | 115 | 87 | 0 | 0 | 143 | 54 | 0 | 114 | 113 | 90 | 0 | 104 | 0 |  | 932 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 48 | 0 | 0 | 0 | 0 | 0 | 96 | 20 | 0 | 30 | 52 | 0 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 151 | 0 | 95 | 0 | 162 | 0 | 345 | 105 | 0 | 94 | 0 | 109 | 0 | 0 | 109 | 622 | 30 | 0 |  | 7904 | 3725 | 11629 | 3805 | 932 | 1947 | 3480 | 772 | 159 | 378 | 156 | 0 | 0 | #REF!
22:00 | 0 | 0 | 0 | 115 | 200 | 76 | 70 | 0 | 272 |  | 0 | 320 | 255 | 100 | 97 | 55 | 0 | 0 | 185 | 0 | 100 | 102 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 37 | 19 | 25 | 30 | 33 | 33 | 51 | 0 | 89 | 70 | 115 | 0 | 8 | 204 | 0 | 139 | 0 |  | 0 | 0 | 102 | 0 | 84 | 50 | 20 | 35 | 0 | 70 | 0 | 270 | 260 | 158 | 8 | 52 | 5 | 0 | 0 | 51 | 0 | 0 | 52 | 13 | 11 | 33 | 21 | 160 | 103 | 25 | 20 | 0 | 86 | 30 | 53 | 49 | 110 | 157 | 63 | 84 | 0 | 204 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 146 | 0 | 22 | 0 | 142 | 416 | 115 | 87 | 0 | 0 | 162 | 54 | 0 | 114 | 113 | 100 | 0 | 104 | 0 |  | 932 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 151 | 0 | 96 | 0 | 162 | 0 | 309 | 105 | 0 | 35 | 0 | 109 | 0 | 0 | 109 | 622 | 0 | 0 |  | 7926 | 3455 | 11381 | 3812 | 932 | 1897 | 3397 | 772 | 159 | 252 | 160 | 0 | 0 | 103.95
23:00 | 0 | 0 | 0 | 115 | 200 | 76 | 71 | 0 | 287 |  | 0 | 340 | 280 | 75 | 97 | 40 | 0 | 0 | 150 | 0 | 86 | 102 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 30 | 33 | 33 | 51 | 0 | 89 | 70 | 115 | 0 | 8 | 205 | 0 | 139 | 0 |  | 0 | 0 | 102 | 0 | 52 | 50 | 20 | 42 | 0 | 70 | 0 | 270 | 260 | 158 | 8 | 52 | 5 | 2 | 0 | 51 | 0 | 0 | 52 | 13 | 11 | 33 | 21 | 158 | 103 | 25 | 20 | 0 | 86 | 30 | 53 | 50 | 110 | 158 | 65 | 84 | 0 | 204 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 200 | 0 | 0 | 180 | 0 | 118 | 0 | 22 | 0 | 142 | 415 | 115 | 86 | 0 | 0 | 162 | 54 | 0 | 62 | 113 | 100 | 0 | 104 | 0 |  | 933 | 0 | 350 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 96 | 0 | 163 | 0 | 343 | 105 | 0 | 0 | 0 | 106 | 0 | 0 | 70 | 622 | 0 | 0 |  | 7664 | 3332 | 10996 | 3787 | 933 | 1965 | 2970 | 772 | 159 | 252 | 158 | 0 | 0 | 103.94
24:00 | 0 | 0 | 0 | 115 | 200 | 76 | 70 | 0 | 312 |  | 0 | 340 | 285 | 0 | 97 | 40 | 0 | 0 | 150 | 0 | 45 | 102 | 82 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 19 | 25 | 30 | 33 | 33 | 51 | 0 | 90 | 70 | 115 | 0 | 8 | 212 | 0 | 139 | 0 |  | 0 | 0 | 68 | 0 | 51 | 50 | 20 | 40 | 0 | 70 | 0 | 270 | 260 | 155 | 8 | 51 | 5 | 2 | 0 | 51 | 0 | 0 | 52 | 13 | 11 | 33 | 21 | 150 | 103 | 25 | 21 | 0 | 86 | 30 | 53 | 50 | 110 | 158 | 64 | 84 | 0 | 204 | 18 | 0 | 10 | 310 | 24 | 11 | 0 | 95 | 0 | 0 | 150 | 0 | 54 | 0 | 22 | 0 | 142 | 417 | 115 | 86 | 0 | 0 | 161 | 54 | 0 | 52 | 113 | 100 | 0 | 104 | 0 |  | 932 | 0 | 365 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 164 | 0 | 95 | 0 | 174 | 0 | 374 | 105 | 0 | 0 | 0 | 75 | 0 | 0 | 70 | 622 | 0 | 0 |  | 7235 | 3262 | 10497 | 3830 | 932 | 2046 | 2457 | 772 | 160 | 150 | 150 | 0 | 0 | 103.94
KWH | 0 | 0 | 0 | 2709000 | 4786936 | 1582818 | 1517824 | 0 | 7024000 |  | 0 | 7189500 | 6399855 | 1120320 | 1265784 | 653305 | 0 | 0 | 3629000 | 0 | 1157760 | 1536624 | 1147200 | 245441 | 0 | 0 | 0 | 1201320 | 651640 | 691984 | 435492 | 600000 | 648360 | 795400 | 813400 | 983580 | 0 | 2037638 | 1684000 | 2700000 | 0 | 130039 | 4816370 | 0 | 3248116 | 0 |  | 0 | 0 | 701839 | 128040 | 587520 | 957120 | 475056 | 555840 | 0 | 1870155 | 0 | 7024900 | 7093000 | 4460000 | 200727 | 1728960 | 442224 | 372000 | 0 | 967444 | 0 | 82608 | 546442 | 297396 | 212760 | 440300 | 515590 | 3110400 | 2347160 | 598080 | 479556 | 14200 | 2001000 | 721080 | 1125000 | 1038816 | 2649600 | 3548000 | 1294848 | 1749120 | 0 | 4424400 | 405000 | 0 | 217440 | 7225500 | 567408 | 198000 | 0 | 3587998 | 0 | 0 | 1672800 | 0 | 1701500 | 138510 | 538560 | 160800 | 1998909 | 9336000 | 2398800 | 2001264 | 0 | 30480 | 2536691 | 1222695 | 0 | 670320 | 2094960 | 2155200 | 0 | 2285760 | 346870 |  | 22358545 | 0 | 8390880 | 0 | 750720 | 0 | 0 | 0 | 0 | 0 | 196125 | 0 | 655646 | 341856 | 0 | 0 | 0 | 167728 | 88267 | 389352 | 189410 | 0 | 124850 | 211680 | 114000 | 425280 | 229608 | 208476 | 0 | 0 | 3656600 | 0 | 0 | 0 | 0 | 4149691 | 0 | 1804397 | 0 | 4224464 | 0 | 8710309 | 1716960 | 0 | 471168 | 0 | 1171200 | 0 | 41755 | 1199136 | 13075500 | 205120 | 0 |  | 161655352 | 75268723 | 236924075 | 92038378 | 22358545 | 45445989 | 50129366 | 16732100 | 3721638 | 2815844 | 3110400 | 571815 | 0
Fuel Cost | 0 | 0 | 0 | 3982230 | 5313498.96 | 2089319.76 | 2580300.8 | 0 | 7234720 |  | 0 | 7836555 | 7103839.05 | 8503228.8 | 8721251.76 | 5526960.3 | 0 | 0 | 6278170 | 0 | 8717932.8 | 14014010.88 | 11288448 | 2262966.02 | 0 | 0 | 0 | 8769636 | 5037177.2 | 6822962.24 | 326619 | 450000 | 0 | 0 | 0 | 9511218.6 | 0 | 550162.26 | 454680 | 4887000 | 0 | 1208062.31 | 5249843.3 | 0 | 5521797.2 | 0 |  | 0 | 0 | 6807838.3 | 1222782 | 5111424 | 7580390.4 | 598570.56 | 1650844.8 | 0 | 2767829.4 | 0 | 5198426 | 7093000 | 4103200 | 258937.83 | 1988304 | 499713.12 | 520800 | 0 | 1654329.24 | 0 | 834340.8 | 5218521.1 | 377692.92 | 159570 | 770525 | 386692.5 | 23328000 | 2487989.6 | 5430566.4 | 609036.12 | 226348 | 3281640 | 1153728 | 2002500 | 1620552.96 | 3020544 | 3689920 | 2550850.56 | 3340819.2 | 0 | 7654212 | 886950 | 0 | 443577.6 | 7297755 | 425556 | 150480 | 0 | 27125264.88 | 0 | 0 | 8698560 | 0 | 16742760 | 1619181.9 | 4389264 | 1744680 | 14092308.45 | 8682480 | 21877056 | 18911944.8 | 0 | 0 | 19177383.96 | 10649673.45 | 0 | 6689793.6 | 17953807.2 | 14353632 | 0 | 0 | 0 |  | 128785219.2 | 0 | 8810424 | 0 | 5900659.2 | 0 | 0 | 0 | 0 | 0 | 2043622.5 | 0 | 1016251.3 | 3336514.56 | 0 | 0 | 0 | 1650443.52 | 896792.72 | 3445765.2 | 1458457 | 0 | 1209796.5 | 2051179.2 | 1105800 | 816537.6 | 355892.4 | 157816.332 | 0 | 0 | 19818772 | 0 | 0 | 0 | 0 | 5477592.12 | 0 | 2706595.5 | 0 | 4942622.88 | 0 | 8623205.91 | 17925062.4 | 0 | 4471384.32 | 0 | 9088512 | 0 | 461392.75 | 8861615.04 | 57401445 | 0 | 0 |  | 467355137.89 | 302819371.152 | 770174509.042 | 106913979.572 | 128785219.2 | 55070038.9 | 348306064.42 | 77220217 | 1004842.26 | 27239225.04 | 23328000 | 2306922.65 | 0
Yesterday Day Peak | 0 | 0 | 0 | 115 | 200 | 72 | 68 | 0 | 289 |  | 0 | 320 | 270 | 35 | 64 | 35 | 0 | 0 | 155 | 0 | 45 | 102 | 16 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 19 | 25 | 24 | 33 | 33 | 51 | 0 | 92 | 70 | 115 | 0 | 0 | 205 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 5 | 0 | 80 | 0 | 260 | 280 | 178 | 8 | 75 | 10 | 5 | 0 | 43 | 0 | 0 | 10 | 13 | 8 | 0 | 15 | 98 | 101 | 25 | 22 | 2 | 86 | 30 | 53 | 48 | 110 | 160 | 50 | 84 | 0 | 171 | 18 | 0 | 9 | 300 | 24 | 11 | 0 | 165 | 0 | 0 | 16 | 0 | 82 | 18 | 22 | 0 | 75 | 403 | 115 | 87 | 0 | 5 | 158 | 54 | 0 | 0 | 92 | 100 | 0 | 104 | 43 |  | 932 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 186 | 0 | 85 | 0 | 173 | 0 | 365 | 88 | 0 | 0 | 0 | 41 | 0 | 6 | 80 | 460 | 0 | 0 |  | 9689 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 115 | 200 | 75 | 69 | 0 | 293 | 0 | 0 | 320 | 240 | 95 | 97 | 55 | 0 | 0 | 120 | 0 | 100 | 102 | 150 | 96 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 30 | 33 | 33 | 51 | 0 | 88 | 70 | 115 | 0 | 25 | 204 | 0 | 139 | 0 | 0 | 0 | 0 | 102 | 70 | 81 | 50 | 20 | 15 | 0 | 80 | 0 | 275 | 275 | 185 | 8 | 70 | 10 | 5 | 0 | 51 | 0 | 42 | 52 | 13 | 11 | 33 | 21 | 164 | 103 | 25 | 22 | 0 | 86 | 30 | 53 | 49 | 110 | 159 | 65 | 84 | 0 | 204 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 300 | 0 | 0 | 195 | 0 | 135 | 0 | 22 | 79 | 142 | 415 | 115 | 87 | 0 | 0 | 142 | 54 | 0 | 114 | 113 | 90 | 0 | 104 | 0 |  | 932 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 32 | 32 | 0 | 0 | 0 | 50 | 32 | 96 | 20 | 0 | 31 | 52 | 32 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 171 | 0 | 380 | 105 | 0 | 92 | 0 | 102 | 0 | 0 | 109 | 622 | 40 | 0 |  | 12085 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 115 | 200 | 75 | 78 | 0 | 360 | 0 | 0 | 450 | 305 | 100 | 100 | 40 | 0 | 0 | 200 | 0 | 100 | 100 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 52 | 0 | 90 | 70 | 120 | 0 | 25 | 221 | 0 | 145 | 0 | 0 | 0 |  | 102 | 100 | 90 | 50 | 20 | 30 | 0 | 80 | 0 | 360 | 350 | 225 | 8 | 75 | 29 | 5 | 0 | 43 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 173 | 150 | 25 | 22 | 0 | 86 | 30 | 51 | 44 | 110 | 160 | 65 | 86 | 0 | 200 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 134 | 0 | 22 | 164 | 150 | 400 | 115 | 88 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 17 |  |  | 943 | 16 | 410 | 0 | 115 | 220 | 0 | 0 | 30 | 60 | 40 | 0 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 20 | 0 | 50 | 52 | 32 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 225 | 0 | 95 | 100 | 220 | 0 | 414 | 105 | 200 | 113 | 100 | 100 | 0 | 0 | 113 | 530 | 0
Forecast for Day | 0 | 0 | 0 | 115 | 200 | 75 | 78 | 0 | 360 | 0 | 0 | 450 | 305 | 100 | 100 | 40 | 0 | 0 | 200 | 0 | 100 | 100 | 150 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 52 | 0 | 90 | 70 | 120 | 0 | 25 | 221 | 0 | 145 | 0 | 0 | 0 |  | 102 | 100 | 90 | 50 | 20 | 30 | 0 | 80 | 0 | 360 | 350 | 225 | 8 | 75 | 29 | 5 | 0 | 43 | 0 | 25 | 25 | 22 | 11 | 33 | 20 | 163 | 150 | 25 | 22 | 1.6 | 86 | 30 | 51 | 44 | 110 | 160 | 65 | 86 | 0 | 180 | 18 | 0 | 10 | 341 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 134 | 20 | 22 | 164 | 150 | 400 | 115 | 88 | 100 | 5 | 300 | 54 | 110 | 17 | 113 | 100 | 0 | 17 | 40 |  | 943 | 0 | 410 | 0 | 115 | 220 | 0 | 0 | 0 | 0 | 40 | 0 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 20 | 0 | 50 | 52 | 0 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 225 |  | 95 | 50 | 220 | 0 | 285 | 105 | 100 | 113 | 100 | 100 | 0 | 8 | 113 | 500 | 0
Generation at 08:00(Today) | 0 | 0 | 0 | 115 | 200 | 32 | 40 | 0 | 262 | 0 | 0 | 300 | 275 |  | 0 | 0 | 0 | 0 | 74 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 16 | 25 | 28 | 28 | 33 | 52 | 0 | 90 | 70 | 115 | 0 | 0 | 204 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 20 | 40 | 0 | 70 | 0 | 265 | 255 | 174 | 8 | 80 | 5 | 2 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 33 | 15 | 98 | 106 | 25 | 22 | 1 | 86 | 30 | 11 | 10 | 110 | 157 | 40 | 10 | 0 | 164 | 18 | 0 | 10 | 300 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 5 | 22 | 0 | 0 | 304 | 85 | 86 | 0 | 2 | 70 | 54 | 0 | 0 | 0 | 100 | 0 | 17 | 26 | 0 | 932 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 55 | 0 | 164 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 400 | 0 | 0 | 0
199
| Minimum Generation |  | 7802 | 7:00
| Highest Generation |  | 12085 | 19:00
| Day Peak Generation |  | 9689 | 12:00
| Evening Peak Generation |  | 12085 | 19:00
| HVDC Max Flow |  | 933 | 5:00
| HVDC EvPeak Flow |  | 932 | 19:00
| Load factor L.F |  | 81.69%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-10-30
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-10-29 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9689 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 7368 | MW
Evening Peak Generation : |  | 12085 | MW Hour : | 19:00 | Available Max Generation : |  | 14868 | MW
E.P. Demand (at gen end) : |  | 12085 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 11300 | MW
Maximum Generation : |  | 12085 | MW Hour : | 19:00 | Reserve(Generation end) |  | 3568 | MW
Total Gen. (MKWH) : |  | 236.9241 | System Load Factor : | 81.69% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 107 | MW at | 22:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-10-30
Actual : | 103.91 | Ft.(MSL) , | Rule curve : | 108.8 | Ft.( MSL )
Gas Consumed : | Total = | 1147.44 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 161984018.472
: |  | Coal : | 77220217 | Oil : | 375545289.46 | Total : | 614749524.932
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3987.4593 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1356.2434 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1215.2001 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1098.054 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 992.2855 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 800.74 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 447.3657 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 206.1593 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 617.5722 |  |  | 0 | 0%
Total | 0 |  | 10721.0794 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Baghabari-71 & 100 MW
3) Ghorasal Unit-1,2,3,4
4) Ashuganj unit-3,5
5) Kaptai-2
6) Raozan #2
7) Siddirganj-335 MW
8) Haripur 412 MW
9) Chandpur-163 MW STG
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Polashbari 132 kV B-Bus was under shut down from 08:10 to 12:20 for A/M.
b) Saidpur 132/33 kV T-4 transformer was under shut down from 09:40 to 13:05 for meter replacement work.
c) Rangamati-Chandraghona 132 kV Ckt-2 was under shut down from 09:00 to 14:44 for A/M.
d) HVDC Bheramara shunt capacitor 10CO4A-01 was under shut down from 09:05 to 16:18 for A/M.
e) Fenchuganj 132/33 kV T-2 transformer was under shut down from 09:08 to 12:16 for A/M.
f) Tongi 132/33 kV T-1 transformer was switched on at 17:20.
g) Noapara 132/33 kV T-1 & T-2 transformers were under shut down from 21:51 to 22:53 for R/H maintenance |  |  |  |  | About 34 MW power interruption occurred under Noapara S/S area
at Y-phase, REB feeder-5 of Bus section-1. |  |  |  |  | from 21:51 to 22:53.
h) Sherpur 132/33 kV T-3 transformer tripped at 22:58 from 33 kV side showing O/C,E/F relay due to 33 kV PBS |  |  |  |  | About 35 MW power interruption occurred under Sherpur S/S area
feeder fault and was switched on at 23:30. |  |  |  |  | from 22:58 to 23:30.
i) Sirajganj unit-4 CCPP ST tripped at 05:37(30/10/2020) due to tripping of boiler.
j) Kaliakoir 400/132 kV T02 transformer was under shut down from 06:29(30/10/2020) to 08:53 for C/M.
k) Hathazari 132 kV Bus section-1 was shut down at 06:29(30/10/2020) for D/W.
l) Gazipur summit-2 300 MW -Tongi S/S & Gazipur summit-2 300 MW-Kaliakoir 230 kV Ckts were shut down at
06:52(30/10/2020) for C/M at P.P. end.
m) Siddhirganj 132/33 kV T-2 transformer was under shut down from 07:13(30/10/2020) to 08:58 for C/M. |  |  |  |  | About 5 MW power interruption occurred under Siddhirganj S/S area
from 07:13(30/10/2020) to 08:58.
n) Bagerhat 132 kV Bus & Magura 132 kV Bus were under shut down from 06:39(30/10/2020) to 10:35 for D/W. |  |  |  |  | About 65 MW power interruption occurred under Bagerhat S/S area
from 06:39(30/10/2020) to 10:35.
o) Magura 132/33 kV T-1 & T-2 transformers tripped at 06:57(30/10/2020) from 33 kV sides showing O/C ,E/F |  |  |  |  | About 20 MW power interruption occurred under Magura S/S area
relay due to auxiliary failure(PBS). |  |  |  |  | from 06:57(30/10/2020) to 07:22.
p) Bottail-Jhenaidah 132 kV Ckt was under shut down from 07:08(30/10/2020) to 09:31.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-10-29 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 115 | 2709000 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 4786936 | Machin problem.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 69 | 1517824
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 75 | 1582818 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 293 | 7024000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 320 | 7189500 | Gas shortae
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 95 | 1120320
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 240 | 6399855 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 97 | 1265784
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 653305
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 96 | 245441
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 435492
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 120 | 3629000 | Frequency control
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 1157760
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under Maintenance
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1536624
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel Shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1201320
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1147200
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 651640
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 691984 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1248360 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 795400
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 813400
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 983580
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 3587998
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 135 | 1701500 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 87 | 2001264 | Engine problem
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2285760
| Dhaka area Total |  |  |  | 5895 | 3088 | 58363065
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 115 | 2700000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 130039
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 138510
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 957120
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 158 | 3721638 | Unit-2 under maint
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4816370
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 139 | 3248116 | Gas shortage
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 701839
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 70 | 128040 | Low demand
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 22 | 538560 | Engine problem
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 475056
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 15 | 555840
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 81 | 587520 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 30480
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 142 | 2536691 | Transformer O/L
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1222695
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 90 | 2155200 | Engine problem
| Chattogram area Total |  |  |  | 2266 | 1287 | 24643714
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 80 | 1870155
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 185 | 4460000 | Gas shortage
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 275 | 7024900 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 275 | 7093000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 10 | 442224 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 372000 | Gas shortage
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 967444
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 142 | 1998909 | Engine problem
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 42 | 82608
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1728960 | ST Under maint
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 79 | 160800 | Low demand
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 13 | 297396
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 212760
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 164 | 3110400
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 440300
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 546442
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 515590
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 670320
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 2094960
| Cumilla Area Total |  |  |  | 2980 | 1743 | 34289895
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 103 | 2347160 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 479556
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 25 | 598080 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14200
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 195 | 1672800
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2398800 | #REF!
| Mymensingh PV 50 MW Solar PP |  | IPP | 0 | 50 MW | 0 | 346870
| Mymensingh Area Total |  |  |  | 637 | 460 | 7857466
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 86 | 2001000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 721080 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2649600 | ST Under maint
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 159 | 3548000 | FGMO & GT-2 under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1125000
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 49 | 1038816
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 198000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 65 | 1294848 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1749120
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 204 | 4424400
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 405000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 567408
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7225500 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 415 | 9336000
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 217440
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1608 | 36501212
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 932 | 22358545
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 750720
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 345 | 8390880 | Gas shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 196125
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1716960
107 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Bhola Nutan Biddut BD LTD (GAS) |  | IPP | 0 | 220 MW | 40 | 205120 | On test
| Khulna Area Total |  |  |  | 2284 | 1577 | 33618350
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 341856 | Line O/L
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 32 | 655646
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 95 | 1804397
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 622 | 13075500
| Barisal Area Total |  |  |  | 1054 | 781 | 15877399
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 167728
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 32 | 88267
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 20 | 189410 | Fuel Shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel Shortage
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 31 | 124850 | Low demand
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas Shortage
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 185 | 4149691 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 171 | 4224464 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 380 | 8710309 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 114000
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 18 | 425280
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 10 | 229608
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 208476
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 211680
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 96 | 389352
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 92 | 471168 | Engine problem
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 1199136
| Rajshahi Area Total |  |  |  | 2183 | 1289 | 20903419
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3656600 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 102 | 1171200
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 41755
| Rangpur Area Total |  |  |  | 605 | 252 | 4869555
| Total |  |  |  | 19892 | 12085 | 236924075
| Eastern Grid Total |  |  |  | 13766 | 8186 | 161655352
| Western Grid Total |  |  |  | 6126 | 3899 | 75268723
| National Grid Total |  |  |  | 19892 | 12085 | 236924075
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-10-29
| (a) ENTIRE EASTERN GRID : |  | 8018 | MW | (b) ENTIRE WESTERN GRID : |  | 3435 | MW
| i) Dhaka area |  | 4220 | MW | i) Khulna area |  | 1332 | MW
| ii) Chittagong area |  | 1265 | MW | ii) Rajshahi area |  | 1132 | MW
| iii) Comilla area |  | 1121 | MW | iii) Barisal area |  | 299 | MW
| iv) Mymensingh area |  | 903 | MW | iv) Rangpur area |  | 672 | MW
| v) Sylhet area |  | 509 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11453 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 114 | 18:30 | Sherpur | 104 | 18:00 | Jhenida | 94 | 18:00
| Munsiganj | 118 | 19:00 | Srimongal | 51 | 19:30 | Bottail | 106 | 18:00
| Sonargaon | 78 | 19:30 | Shahjibazar | 116 | 19:00 | G.K Project | 47 | 18:30
| Shyampur | 188 | 0:00 | Fenchuganj | 43 | 18:00 | Faridpur | 170 | 0.77083
| Bhulta | 191 | 19:00 | Kulawara | 43 | 19:00 | Madaripur | 91 | 0.91667
| Madanganj | 57 | 15:00 | Sylhet | 133 | 19:30 | Sariatpur | 60 | 21:00
| Shitalakhya | 112 | 12:00 | Chatak | 29 | 20:00 | Gopalganj | 82 | 18:30
| Rahim steel | 20 | 10:00 | Sunamganj | 47 | 20:00 | Bagerhat | 94 | 18:00
| Matuail | 78 | 9:00 | Biani Bazar | 61 | 18:30 | Mongla | 34 | 12:00
| Ghorasal | 79 | 19:00 | Comilla (S) | 166 | 18:30 | Satkhira | 93 | 0.8125
| Narsingdi | 159 | 19:30 | Comilla(N) | 107 | 20:00 | Gallamari | 44 | 18:00
| Haripur (SBU) | 100 | 12:00 | Chandpur | 92 | 21:00 | Magura | 46 | 0.77083
| Ullon | 58 | 18:00 | Feni | 114 | 19:30 | Norail | 37 | 18:00
| Hasnabad | 200 | 19:30 | Chowmuhani | 180 | 19:00 | Chuadanga | 81 | 18:30
| Magbazar | 101 | 15:00 | Ashuganj | 55 | 0:00 | Barisal(N) | 41 | 0.83333
| Maniknagar | 98 | 11:00 | Daudkandi | 144 | 22:00 | Barisal (S) | 88 | 0.77083
| Bangabhaban | 36 | 12:00 | B.Baria | 152 | 18:30 | Patuakhali | 107 | 0.875
| Narinda | 82 | 16:00 | Ramganj | 104 | 20:00 | Bhandaria | 50 | 0.8125
| Dhanmondi | 169 | 13:00 | Chaddagram | 38 | 19:00 | Borhan Uddin | 38 | 21:00
| Lalbag | 86 | 16:00 | PHP | 9 | 19:00 | Ishurdi | 55 | 20:00
| Madartek | 73 | 19:30 | Madunaghat | 55 | 18:30 | Ruppur Paromanobik | 2 | 20:00
| Dhaka University |  |  | Hathazari | 99 | 0.83333 | Natore | 105 | 20:00
| Fatullah | 44 | 0.5 | Khulshi | 216 | 0.625 | Bogra | 156 | 18:30
| Mirpur | 104 | 18:00 | Halishahar | 143 | 0.58333 | Noagaon | 105 | 20:00
| Kalyanpur | 90 | 18:00 | Baraulia | 146 | 0.625 | Rajshahi | 124 | 20:00
| Gulshan | 132 | 13:00 | Sikalbaha | 27 | 0.75 | Rajshahi New | 13 | 20:00
| Uttara | 89 | 18:00 | Dohazari | 88 | 0.83333 | C.Nawabganj | 62 | 19:00
| Uttara New | 34 | 18:30 | Cox'sbazar | 102 | 0.77083 | Amnura | 40 | 20:00
| Kamrangirchar | 92 | 18:30 | Chandraghona | 32 | 0.75 | Pabna | 110 | 18:00
| Savar | 145 | 15:00 | Kaptai | 4.5 | 0.75 | Shahjadpur | 97 | 19:00
| Bhasantec | 152 | 13:00 | A. Khaer Stl. | 0 | 0.041667 | Serajganj | 91 | 19:00
| Agargaon | 72 | 13:00 | Bakulia | 107 | 0.77083 | Niyamatpur | 49 | 19:00
| Satmosjid | 97 | 18:00 | Julda | 23 | 0.75 | Joypurhat | 53 | 19:30
| Tongi | 106 | 0.625 | TK chemical | 28 | 0.75 | Sherpur(Bogura) | 44 | 19:00
| Kabirpur | 228 | 15:00 | Modern Steel | 15 | 0.083333 | Mohastangor | 44 | 19:00
| Basundhara | 142 | 12:00 | Shahmirpur | 24 | 0.58333 | Rangpur | 126 | 19:00
| Manikganj | 76 | 20:00 | Khagrachhari | 24 | 0.83333 | Lalmonirhat | 48 | 18:00
| Joydevpur | 159 | 18:30 | Matarbari | 36 | 0.75 | Saidpur | 94 | 18:00
| New Tongi | 104 | 18:00 | Baroiar Hat | 36 | 0.75 | Purbasadipur | 88 | 18:30
| Kodda | 248 | 15:00 | Rangamati | 12 | 0.75 | Thakurgaon | 66 | 18:00
| Dhamrai | 92 | 18:30 | Abul Khair 230 | 7 | 0.16667 | Palashbari | 106 | 18:00
| Rajendrapur | 96 | 22:00 | BSRM | 159 | 0.58333 | Barapukuria | 45 | 20:00
| Valuka | 92 | 11:00 | GPH Ispat | 20 | 0.75 | Panchagar | 48 | 18:00
| Tangail | 186 | 18:00 | Goalpara | 24 | 0.54167 | Joldhaka | 21 | 18:00
| Mymensing | 209 | 18:30 | Central s/s | 78 | 19:00 | Kurigram | 48 | 19:00
| Kishorganj | 135 | 18:30 | Noapara | 51 | 18:30
| Netrokona | 102 | 18:00 | Jessore | 110 | 18:00
| Jamalpur | 123 | 19:00 | Benapol | 36 | 18:00
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-10-29 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 409 | 20:00 | 401 | 18:00 | Kaliakoir | 394 | 0.70833 | 384 | 0.41667
| Bheramara | 408 | 6:00 | 397 | 18:00 | Bhulta | 375 | 0.83333 | 361 | 0.41667
| Ashuganj(N) | 381 | 7:00 | 370 | 11:00 | Gopalganj | 410 | 0.70833 | 388 | 0.79167
| Payra | 417 | 19:30 | 405 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 6:00 | 228 | 1:00 | Comilla (N) | 231 | 18:00 | 225 | 10:00
| Ishurdi | 236 | 6:00 | 226 | 12:00 | Hathazari | 222 | 17:00 | 218 | 10:00
| Ashuganj | 234 | 21:00 | 227 | 10:00 | Megnaghat | 222 | 19:00 | 219 | 12:00
| Serajganj | 231 | 17:00 | 226 | 10:00 | Fenchuganj | 241 | 22:00 | 237 | 12:00
| Baghabari | 240 | 17:00 | 236 | 10:00 | Siddhirganj | 226 | 22:00 | 215 | 10:00
| Barapukuria | 238 | 4:00 | 232 | 18:30 | Maniknagar | 223 | 22:00 | 213 | 10:00
| Bogra | 227 | 17:00 | 221 | 10:00 | Agargaon | 221 | 17:00 | 212 | 10:00
| Rajshahi | 226 | 6:00 | 216 | 24:00 | Barisal | 247 | 18:30 | 231 | 1:00
| Khulna South | 232 | 17:00 | 214 | 12:00 | AKSML | 220 | 20:00 | 215 | 3:00
| Rampura | 222 | 22:00 | 216 | 10:00 | BSRM | 222 | 18:30 | 215 | 7:00
| Haripur | 222 | 23:00 | 215 | 10:00 | Bibiyana | 240 | 22:00 | 234 | 11:00
| Hasnabad | 222 | 19:30 | 215 | 10:00 | Bhulta | 226 | 19:00 | 217 | 17:00
| Shyampur | 221 | 19:30 | 220 | 10:00 | Ashuganj (S) | 232 | 22:00 | 224 | 10:00
| Aminbazar | 223 | 21:00 | 214 | 10:00 | Kaliakoir | 224 | 20:00 | 215 | 10:00
| Tongi | 218 | 4:00 | 208 | 10:00 | GPH | 220 | 20:00 | 214 | 7:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 135 | 20:00 | 127 | 10:00 | Hathazari | 133 | 0.77083 | 130 | 0.20833
| Munsiganj | 135 | 19:00 | 127 | 10:00 | Khulshi | 132 | 0.77083 | 127 | 0.5
| Sonargaon | 135 | 17:00 | 127 | 10:00 | Halishahar | 133 | 0.77083 | 128 | 0.29167
| Shyampur | 132 | 19:30 | 125 | 10:00 | Baraulia | 133 | 0.75 | 129 | 0.41667
| Bhulta | 127 | 18:00 | 122 | 10:00 | Sikalbaha | 135 | 0.77083 | 129 | 0.29167
| Madanganj | 132 | 19:00 | 127 | 10:00 | Dohazari | 132 | 0.77083 | 126 | 0.16667
| Shitalakhya | 142 | 19:00 | 131 | 10:00 | Cox'sbazar | 125 | 0.70833 | 118 | 0.041667
| Rahim steal | 134 | 18:00 | 128 | 10:00 | Chandraghona | 134 | 0.83333 | 131 | 0.16667
| Matuail | 135 | 20:00 | 127 | 10:00 | Kaptai | 133 | 0.041667 | 130 | 0.29167
| Ghorasal | 135 | 23:00 | 132 | 10:00 | A. Khaer Stl. | 132 | 0.79167 | 127 | 0.41667
| Narsinghdi | 130 | 17:00 | 124 | 10:00 | Bakulia | 133 | 0.77083 | 127 | 0.33333
| Haripur (SBU) | 134 | 21:00 | 127 | 9:00 | Julda | 135 | 0.77083 | 131 | 0.375
| Ullon | 130 | 1:00 | 126 | 11:00 | TK Chemical | 133 | 0.79167 | 129 | 0.25
| Hasnabad | 138 | 18:30 | 132 | 10:00 | Modern Steel | 133 | 0.75 | 128 | 0.25
| Magbazar | 132 | 4:00 | 118 | 19:00 | Shahmirpur | 134 | 0.75 | 129 | 0.25
| Maniknagar | 134 | 22:00 | 128 | 10:00 | Khagrachhari | 132 | 0.83333 | 129 | 0.25
| Bangabhaban | 134 | 22:00 | 128 | 10:00 | Matarbari | 128 | 0.375 | 120 | 0.041667
| Narinda | 134 | 22:00 | 128 | 10:00 | Baroiar Hat | 134 | 0.79167 | 126 | 0.41667
| Dhanmondi | 130 | 1:00 | 126 | 11:00 | Rangamati | 133 | 0.8125 | 129 | 0.41667
| Lalbag | 137 | 19:00 | 127 | 10:00 | Goalpara S/S | 139 | 17:00 | 128 | 13:00
| Madartek | 131 | 22:00 | 124 | 10:00 | Khulna Central S/S | 140 | 17:00 | 129 | 0.5
| Dhaka University |  |  |  |  | Noapara | 137 | 17:00 | 124 | 0.54167
| Fatuiiah | 133 | 22:00 | 126 | 10:00 | Jessore | 134 | 17:00 | 120 | 0.54167
| Mirpur | 137 | 6:00 | 129 | 6:00 | Benapol | 133 | 0.70833 | 122 | 0.54167
| Kalyanpur | 136 | 21:00 | 130 | 10:00 | Jhenida | 131 | 6:00 | 117 | 0.77083
| Gulshan | 131 | 22:00 | 124 | 11:00 | Bottail | 135 | 0.25 | 125 | 0.77083
| Uttara | 134 | 22:00 | 126 | 11:00 | G.K Project | 140 | 0.25 | 135 | 0.79167
| Uttara New | 135 | 22:00 | 128 | 11:00 | Faridpur | 134 | 0.29167 | 124 | 0.83333
| Kamrangirchar | 136 | 20:00 | 128 | 11:00 | Madaripur | 136 | 0.29167 | 130 | 0.77083
| Savar | 135 | 21:00 | 129 | 11:00 | Shariyatpur S/S | 136 | 8:00 | 127 | 0.8125
| Bhasantec | 133 | 6:00 | 127 | 11:00 | Gopalganj | 137 | 0.29167 | 126 | 0.79167
| Agargaon | 134 | 6:00 | 128 | 11:00 | Bagerhat | 138 | 17:00 | 125 | 0.5
| Satmosjid | 133 | 6:00 | 128 | 11:00 | Mongla | 135 | 17:00 | 123 | 0.5
| Tongi | 136 | 21:00 | 130 | 10:00 | Satkhira | 138 | 17:00 | 127 | 13:00
| Kabirpur | 132 | 6:00 | 125 | 18:00 | Gallamari | 141 | 0.70833 | 130 | 0.5
| Basundhara | 131 | 22:00 | 124 | 11:00 | Magura | 130 | 6:00 | 115 | 0.77083
| Manikganj | 138 | 21:00 | 130 | 8:00 | Norail | 129 | 0.25 | 114 | 0.77083
| Joydevpur | 139 | 18:00 | 131 | 15:00 | Chuadanga | 127 | 6:00 | 110 | 0.77083
| New Tongi | 136 | 2:00 | 129 | 15:00 | Barisal(N) | 140 | 17:00 | 132 | 2:00
| Kodda | 136 | 21:00 | 125 | 8:00 | Barisal (S) | 139 | 0.70833 | 130 | 0.041667
| Dhamrai | 132 | 6:00 | 125 | 18:00 | Patuakhali(S) | 139 | 0.70833 | 125 | 0.83333
| Rajendrapur | 134 | 20:00 | 124 | 5:00 | Bhandaria | 134 | 0.70833 | 121 | 0.77083
| Valuka | 122 | 8:00 | 110 | 18:30 | Ishurdi | 138 | 17:00 | 132 | 18:30
| Tangail | 130 | 5:00 | 121 | 18:00 | Ruppur Paromanobik | 137 | 6:00 | 133 | 12:00
| Mymensing | 125 | 9:00 | 113 | 18:00 | Natore | 139 | 17:00 | 132 | 12:00
| Kishorganj | 126 | 9:00 | 115 | 18:30 | Bogra | 137 | 6:00 | 132 | 12:00
| Netrokona | 123 | 9:00 | 110 | 18:00 | Noagaon | 133 | 17:00 | 127 | 12:00
| Jamalpur | 134 | 23:00 | 123 | 10:00 | Rajshahi | 138 | 17:00 | 132 | 12:00
| Sherpur | 132 | 23:00 | 121 | 8:00 | Rajshahi New | 138 | 17:00 | 132 | 12:00
| Srimongal | 135 | 3:00 | 132 | 18:00 | C.Nawabganj | 136 | 17:00 | 129 | 12:00
| Shahjibazar | 132 | 4:00 | 129 | 18:30 | Amnura | 136 | 17:00 | 128 | 14:00
| Fenchuganj | 137 | 6:00 | 134 | 1:00 | Pabna | 136 | 17:00 | 129 | 12:00
| Khulawara | 135 | 1:00 | 133 | 18:00 | Shahjadpur | 139 | 6:00 | 134 | 12:00
| Sylhet | 133 | 4:00 | 131 | 18:00 | Serajganj | 135 | 17:00 | 130 | 12:00
| Chatak | 132 | 7:00 | 128 | 20:00 | Niyamatpur | 133 | 17:00 | 125 | 18:00
| Sunamganj | 131 | 6:00 | 126 | 19:30 | Joypurhat | 135 | 17:00 | 126 | 11:00
| Biani Bazar | 132 | 6:00 | 128 | 18:00 | Sherpur(Bogura) | 137 | 17:00 | 132 | 18:30
| Comilla(s) | 127 | 6:00 | 120 | 18:00 | Mohastangor | 136 | 17:00 | 131 | 18:30
| Comilla(n) | 135 | 18:30 | 132 | 7:00 | Rangpur | 133 | 5:00 | 124 | 18:30
| Chandpur | 135 | 17:00 | 127 | 23:00 | Lalmonirhat | 133 | 15:00 | 125 | 19:00
| Feni | 135 | 20:00 | 128 | 16:00 | Saidpur | 134 | 6:00 | 127 | 18:30
| Chowmuhani | 135 | 11:00 | 128 | 22:00 | Purbasadipur | 132 | 6:00 | 122 | 18:00
| Ashuganj | 133 | 9:00 | 129 | 18:30 | Thakurgaon | 132 | 6:00 | 122 | 18:00
| Daudkandi | 132 | 17:00 | 127 | 10:00 | Palashbari | 134 | 17:00 | 127 | 18:00
| B.Baria | 130 | 9:00 | 124 | 22:00 | Barapukuria | 138 | 17:00 | 132 | 18:30
| Ramganj | 130 | 19:30 | 122 | 17:00 | Panchagar | 130 | 6:00 | 119 | 18:30
| Chaddagram | 134 | 18:30 | 128 | 3:00 | Joldhaka | 133 | 6:00 | 123 | 18:00
| PHP | 134 | 20:00 | 126 | 3:00 | Kurigram | 131 | 6:00 | 122 | 18:00
| Madanhat | 135 | 19:30 | 130 | 6:00

## L-Curve
Date | 2020-10-29
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 314 | 7235 | 3262 | 10497 |  |  |  | QF-LDC-11
0:30 | 347 | 6810.5 | 3110 | 9920.5 | Date: | 2020-10-29
1:00 | 380 | 6386 | 2958 | 9344
1:30 | 400 | 6291 | 2933.5 | 9224.5
2:00 | 420 | 6196 | 2909 | 9105
2:30 | 440 | 6091.5 | 2866.5 | 8958 | [5 empty] | Gen. at Eve. Peak | 12085 | 9500 MW (19:30 )
3:00 | 460 | 5987 | 2824 | 8811 | [6 empty] | 19:00
3:30 | 431.5 | 5876 | 2788.5 | 8664.5 | [5 empty] | Gen. at Day Peak | 9689 | 7952.5 MW (12:00 )
4:00 | 403 | 5765 | 2753 | 8518 | [6 empty] | 12:00
4:30 | 465 | 5692 | 2734 | 8426 | [5 empty] | Highest Generation | 12085
5:00 | 527 | 5619 | 2715 | 8334 | [6 empty] | 19:00
5:30 | 535.5 | 5500 | 2675 | 8175
6:00 | 544 | 5381 | 2635 | 8016
6:30 | 489.5 | 5302.5 | 2606.5 | 7909
7:00 | 435 | 5224 | 2578 | 7802
7:30 | 461 | 5307.5 | 2613 | 7920.5
8:00 | 487 | 5391 | 2648 | 8039
8:30 | 464 | 5635 | 2630.5 | 8265.5
9:00 | 441 | 5879 | 2613 | 8492
9:30 | 495.5 | 6050 | 2647 | 8697
10:00 | 550 | 6221 | 2681 | 8902
10:30 | 521 | 6298.5 | 2771 | 9069.5
11:00 | 492 | 6376 | 2861 | 9237
11:30 | 475 | 6546.5 | 2916.5 | 9463
12:00 | 458 | 6717 | 2972 | 9689
12:30 | 408 | 6854 | 3013 | 9867
13:00 | 358 | 6991 | 3054 | 10045
13:30 | 396.5 | 7010.5 | 3035 | 10045.5
14:00 | 435 | 7030 | 3016 | 10046
14:30 | 441 | 7119 | 3075.5 | 10194.5
15:00 | 447 | 7208 | 3135 | 10343
15:30 | 461.5 | 7048 | 3030 | 10078
16:00 | 476 | 6888 | 2925 | 9813
16:30 | 448 | 6782.5 | 2867 | 9649.5
17:00 | 420 | 6677 | 2809 | 9486
17:30 | 333 | 7262 | 3220 | 10482
18:00 | 246 | 7847 | 3631 | 11478
18:30 | 221.5 | 8016.5 | 3765 | 11781.5
19:00 | 197 | 8186 | 3899 | 12085
19:30 | 210 | 8111 | 3837 | 11948
20:00 | 166 | 8051 | 3793 | 11844 |  |  |  | Executive Engineer
20:30 | 181.5 | 7977.5 | 3759 | 11736.5 |  |  |  | Network Operation Division
21:00 | 197 | 7904 | 3725 | 11629
21:30 | 152 | 7915 | 3590 | 11505
22:00 | 107 | 7926 | 3455 | 11381 |  |  |  |  | Page 6 of 7
22:30 | 162.5 | 7795 | 3393.5 | 11188.5
23:00 | 218 | 7664 | 3332 | 10996
23:30 | 266 | 7449.5 | 3297 | 10746.5
24:00 | 314 | 7235 | 3262 | 10497
9500 MW (19:30 )
7952.5 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-10-29 |  | Energy | 236924075
[10 empty] | 2020-10-29 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3830 | 932 | 2046 | 2970 | 772 | 160 | 150 | 0 | 150
0:30 | 3854 | 932 | 2032.5 | 2238.5 | 736 | 158 | 83 | 0 | 143 | Date: | 2020-10-29
1:00 | 3878 | 932 | 2019 | 1507 | 700 | 156 | 16 | 0 | 136
1:30 | 3880 | 932 | 2032.5 | 1376 | 699.5 | 154.5 | 16 | 0 | 134 | [7 empty] | Total Energy | 236.9241 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 3882 | 932 | 2046 | 1245 | 699 | 153 | 16 | 0 | 132 | [7 empty] | Energy not Served | 0
2:30 | 3853 | 932 | 2044 | 1152.5 | 684 | 153.5 | 8 | 0 | 131 | [7 empty] | Energy Requirement | 236.9241
3:00 | 3824 | 932 | 2042 | 1060 | 669 | 154 | 0 | 0 | 130
3:30 | 3788 | 931.5 | 2018.5 | 974 | 669 | 154.5 | 0 | 0 | 129 | [6 empty] | Shortage
4:00 | 3752 | 931 | 1995 | 888 | 669 | 155 | 0 | 0 | 128
4:30 | 3739.5 | 932 | 1970.5 | 834 | 669.5 | 155.5 | 0 | 0 | 125
5:00 | 3727 | 933 | 1946 | 780 | 670 | 156 | 0 | 0 | 122
5:30 | 3715 | 933 | 1912 | 692 | 650 | 157 | 0 | 0 | 116
6:00 | 3703 | 933 | 1878 | 604 | 630 | 158 | 0 | 0 | 110
6:30 | 3712.5 | 932.5 | 1790.5 | 594.5 | 605 | 160 | 0 | 0 | 105 |  |  |  |  | Coal
7:00 | 3722 | 932 | 1703 | 585 | 580 | 162 | 0 | 0 | 100
7:30 | 3730.5 | 932 | 1717 | 669.5 | 580 | 162 | 0 | 0 | 100 |  |  |  | Oil |  |  |  | ,
8:00 | 3739 | 932 | 1731 | 754 | 580 | 162 | 0 | 0 | 100
8:30 | 3730 | 932 | 1760.5 | 947.5 | 580 | 162 | 0 | 0 | 102
9:00 | 3721 | 932 | 1790 | 1141 | 580 | 162 | 0 | 0 | 104
9:30 | 3759 | 932 | 1833 | 1257 | 580 | 162 | 0 | 0 | 106
10:00 | 3797 | 932 | 1876 | 1373 | 580 | 162 | 0 | 0 | 108
10:30 | 3805 | 932 | 1906 | 1502 | 580 | 162 | 5 | 0 | 98
11:00 | 3813 | 932 | 1936 | 1631 | 580 | 162 | 10 | 0 | 88
11:30 | 3801.5 | 932 | 1926.5 | 1860.5 | 595 | 162 | 13 | 0 | 93
12:00 | 3790 | 932 | 1917 | 2090 | 610 | 162 | 16 | 0 | 98
12:30 | 3802.5 | 932 | 1912 | 2252.5 | 614.5 | 160 | 16 | 0 | 102
13:00 | 3815 | 932 | 1907 | 2415 | 619 | 158 | 16 | 0 | 106
13:30 | 3815 | 932 | 1907 | 2415 | 619 | 158 | 16 | 0 | 106
14:00 | 3815 | 932 | 1907 | 2415 | 619 | 158 | 16 | 0 | 106
14:30 | 3840.5 | 932.5 | 1918 | 2540 | 619.5 | 157.5 | 16 | 0 | 109
15:00 | 3866 | 933 | 1929 | 2665 | 620 | 157 | 16 | 0 | 112
15:30 | 3849 | 932.5 | 1876 | 2483.5 | 620 | 157.5 | 16 | 0 | 110
16:00 | 3832 | 932 | 1823 | 2302 | 620 | 158 | 16 | 0 | 108
16:30 | 3692 | 932 | 1752.5 | 2313.5 | 585 | 158 | 89 | 0 | 116
17:00 | 3552 | 932 | 1682 | 2325 | 550 | 158 | 162 | 0 | 124
17:30 | 3745 | 931.5 | 1824 | 2804.5 | 550 | 158 | 324.5 | 0 | 144
18:00 | 3938 | 931 | 1966 | 3284 | 550 | 158 | 487 | 0 | 164
18:30 | 3906.5 | 931.5 | 1986.5 | 3463 | 661 | 158 | 511 | 0 | 164
19:00 | 3875 | 932 | 2007 | 3642 | 772 | 158 | 535 | 0 | 164
19:30 | 3841 | 932 | 1981 | 3564 | 772 | 158 | 538 | 0 | 162
20:00 | 3822 | 932 | 1930 | 3558 | 772 | 159 | 509 | 0 | 162
20:30 | 3813.5 | 932 | 1938.5 | 3519 | 772 | 159 | 443.5 | 0 | 159
21:00 | 3805 | 932 | 1947 | 3480 | 772 | 159 | 378 | 0 | 156
21:30 | 3808.5 | 932 | 1922 | 3438.5 | 772 | 159 | 315 | 0 | 158
22:00 | 3812 | 932 | 1897 | 3397 | 772 | 159 | 252 | 0 | 160
22:30 | 3799.5 | 932.5 | 1931 | 3183.5 | 772 | 159 | 252 | 0 | 159
23:00 | 3787 | 933 | 1965 | 2970 | 772 | 159 | 252 | 0 | 158
23:30 | 3808.5 | 932.5 | 2005.5 | 2970 | 772 | 159.5 | 201 | 0 | 154 | Max Temp. in Dhaka |  | 34.5° C
24:00 | 3830 | 932 | 2046 | 2970 | 772 | 160 | 150 | 0 | 150
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
Note on W13: Author:

## Generation
g | 2020-10-29
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 86 | 83 | 84 | 85 | 86 | 88 | 92 | 92 | 92 | 92 | 92 | 92 | 88 | 86 | 87 | 88 | 88 | 88 |  | 88 | 88 | 89 | 89 | 89 | 89 | 90 | 2037638
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1684000
3 | Chattogram TPP-1 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2700000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 20 |  | 25 | 25 | 25 | 25 | 8 | 8 | 8 | 130039
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 4 | 10 | 15 | 18 | 19 | 18 | 13 | 17 | 9 | 6 | 0 | [9 empty] | 138510
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 204 | 204 | 204 | 204 | 204 | 210 | 207 | 204 | 216 | 205 | 205 | 205 | 212 | 204 | 204 | 204 | 218 |  | 204 | 204 | 204 | 204 | 204 | 205 | 212 | 4816370
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 139 | 140 | 139 | 139 | 140 | 139 | 139 | 139 | 139 | 142 | 139 | 139 | 139 | 104 | 139 | 139 | 70 | 140 |  | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 3248116
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 29 | 102 |  | 102 | 102 | 102 | 102 | 102 | 102 | 68 | 701839
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [17 empty] | 16 |  | 42 | 42 | 25 |  |  |  | 0 | 82608
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 180 | 180 | 150 | 150 | 120 | 120 | 120 | 122 | 120 | 120 | 150 | 155 | 154 | 120 | 120 | 120 | 75 | 120 |  | 120 | 160 | 160 | 190 | 185 | 150 | 150 | 3629000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 30 | 30 | 15 | [5 empty] | 18 | 95 | 130 | 165 | 195 | 195 | 243 | 245 | 249 | 287 |  | 300 | 300 | 300 | 300 | 300 | 200 | 95 | 3587998
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2709000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4786936
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 70 | 70 | 70 | 70 | 70 | 70 | 1870155
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 29 | 29 | 29 | 29 | 29 | 29 | 26 | 26 | 27 | 27 | 27 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 442224
33 | Ashuganj 225 MW CCPP | 180 | 180 | 180 | 180 | 180 | 180 | 195 | 190 | 182 | 210 | 154 | 178 | 212 | 211 | 213 | 210 | 180 | 205 |  | 185 | 177 | 168 | 159 | 158 | 158 | 155 | 4460000
34 | Ashuganj 450 MW CCPP(South) | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 280 | 280 | 280 | 280 | 280 | 330 | 300 | 295 | 275 |  | 275 | 260 | 260 | 260 | 260 | 260 | 260 | 7093000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 300 | 285 | 280 | 300 | 285 | 260 | 260 | 280 | 275 | 275 | 275 | 310 |  | 275 | 260 | 260 | 260 | 270 | 270 | 270 | 7024900
35 | Ashuganj 55 MW PP (Precision) | 20 | 30 | 30 | 30 | 30 | 10 | 10 | 10 | 30 | 30 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 0 | 0 | 2 | 2 | 372000
36 | Chandpur 150 MW CCPP | 76 | 74 | 76 | 75 | 77 | 76 | 85 | 80 | 75 | 80 | 80 | 75 | 75 | 75 | 71 | 76 | 70 | 75 |  | 70 | 76 | 71 | 50 | 52 | 52 | 51 | 1728960
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 320 | 340 | 360 | 370 | 370 | 370 | 370 | 370 | 350 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  | 320 | 320 | 320 | 320 | 320 | 340 | 340 | 7189500
41 | Haripur 360MW CCPP(HPL) | 302 | 302 | 302 | 302 | 302 | 302 | 302 | 302 | 303 | 303 | 293 | 289 | 283 | 284 | 288 | 292 | 298 | 304 |  | 293 | 287 | 283 | 272 | 272 | 287 | 312 | 7024000
42 | RPCL 210MW CCPP | 106 | 106 | 106 | 106 | 106 | 108 | 106 | 106 | 106 | 102 | 100 | 101 | 82 | 83 | 83 | 100 | 102 | 102 |  | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 2347160
43 | Mymensingh PV 50 MW Solar PP | [5 empty] | 0 | 12 | 26 | 39 | 46 | 53 | 43 | 52 | 44 | 30 | 13 | 1 | [9 empty] | 346870
44 | Fenchugonj CCPP Phase-1 | 87 | 87 | 86 | 86 | 87 | 87 | 87 | 86 | 86 | 86 | 86 | 86 | 86 | 84 | 82 | 81 | 82 | 85 |  | 86 | 86 | 86 | 85 | 86 | 86 | 86 | 2001000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 721080
46 | Shajibazar 330 MW CCPP | 156 | 158 | 158 | 159 | 158 | 160 | 158 | 156 | 158 | 160 | 158 | 160 | 160 | 159 | 158 | 159 | 158 | 157 |  | 159 | 157 | 157 | 157 | 157 | 158 | 158 | 3548000
47 | Shahjibazar GTPP Unit- 8 & 9 | 52 | 52 | 52 | 52 | 52 | 52 | 51 | 51 | 51 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 51 | 63 |  | 65 | 63 | 63 | 63 | 63 | 65 | 64 | 1294848
48 | Shahjibazar 86MW PP (Shahjibazar) | 84 | 84 | 84 | 84 | 50 | 50 | 10 | 10 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 40 | 40 | 84 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 1749120
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 204 | 204 | 180 | 204 |  | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 4424400
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 405000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 217440
54 | Hobiganj 11MW PP Cofidence-E | 11 | 8 | 8 | 8 | 8 | 8 | 8 |  | 5 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 3 | 3 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 198000
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 11 | 11 | 33 | 47 | 50 | 53 | 53 | 53 | 53 | 50 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1125000
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 567408
57 | Bibiana-II 341 MW CCPP (Summit) | 275 | 290 | 270 | 265 | 290 | 280 | 265 | 310 | 300 | 290 | 310 | 300 | 300 | 290 | 300 | 290 | 270 | 270 |  | 290 | 305 | 290 | 280 | 290 | 280 | 310 | 7225500
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 37 | 35 | 35 | 691984
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 475056
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 435492
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 20 | 20 | 20 | 20 | 21 | 479556
63 | Impoprt (Tripura) | 136 | 132 | 130 | 128 | 122 | 110 | 100 | 100 | 104 | 108 | 88 | 98 | 106 | 108 | 112 | 108 | 124 | 164 |  | 164 | 162 | 162 | 156 | 160 | 158 | 150 | 3110400
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 40 | 34 | 8 | 5 | 3 | 3 | 5 | 7 | 4 | 2 | 5 | 12 | 10 |  | 15 | 22 | 22 | 30 | 35 | 42 | 40 | 555840
65 | Feni 22MW PP (Doreen) | 13 | 13 | 13 | 13 | 13 | 13 | 16 | 16 | 16 | 16 | 13 | 13 | 13 | 13 | 13 |  |  |  |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 297396
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 8 | 8 | 8 |  | 8 | 11 | 11 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 212760
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | [11 empty] | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 440300
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 8 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 19 | 20 | 20 | 20 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 515590
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 10 | 30 | 10 | 24 | 30 | 30 | 26 | 21 | 21 | 28 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 648360
71 | Maona 33 MW PP(Summit) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 795400
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 813400
73 | Ghorashal 108MW PP (Regent) | 66 | 67 | 65 | 65 | 65 | 65 | 65 | 68 | 68 | 68 | 72 | 72 | 72 | 72 | 72 | 72 | 23 | 75 |  | 75 | 75 | 76 | 76 | 76 | 76 | 76 | 1582818
| Feni Lanka Power | [16 empty] | 52 | 114 |  | 114 | 114 | 114 | 114 | 114 | 62 | 52 | 670320
| Chowmuhani 113 MW | 113 | 85 | 65 | 65 | 45 | 45 | 27 | 27 | 27 | 27 | 55 | 92 | 113 | 113 | 112 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2094960
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [8 empty] | 0 | 7 | 18 | 45 | 90 | 99 | 99 | 70 | 65 | 100 |  | 100 | 100 | 100 | 100 | 100 | 86 | 45 | 1157760
78 | Gazipur 52 MW PP | 25 | 25 | 25 | 8 | 8 | 8 | 18 | 26 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 983580
79 | Kodda 150MW PP | 16 | 16 | [8 empty] | 10 | 16 | 16 | 16 | 16 | 16 | 82 | 145 |  | 150 | 150 | 150 | 150 | 150 | 150 | 82 | 1147200
80 | Jamalpur 95 MW PP(Powerpac) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 598080
81 | Jangalia 52 MW PP (Lakdanavi) | [11 empty] | 10 | 25 | 28 | 43 | 25 | 28 | 50 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 546442
| Gazipur 100 MW PP | 87 | 87 | 82 | 70 | 70 | 70 | 70 | 72 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 |  | 87 | 87 | 87 | 87 | 87 | 86 | 86 | 2001264
| Kaptai 7 MW Solar PP | [6 empty] | 1 | 2 | 3 | 4 | 5 | 5 | 4 | 4 | 2 | 1 | [10 empty] | 30480
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 17 | 17 | 17 | 51 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1222695
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | 15 | 10 | [6 empty] | 12 | 15 | 18 | 64 | 80 | 88 | 97 | 64 | 64 | 85 |  | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 1265784
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [17 empty] | 43 |  | 96 | 50 | 61 |  |  |  | 0 | 245441
86 | Meghnaghat CCPP(Summit) | 265 | 255 | 265 | 270 | 265 | 245 | 280 | 275 | 250 | 285 | 280 | 270 | 250 | 285 | 260 | 280 | 250 | 285 |  | 240 | 275 | 255 | 270 | 255 | 280 | 285 | 6399855
87 | Meghnaghat 100 MW(IEL) | [8 empty] | 1 | 7 | 15 | 35 | 82 | 98 | 100 | 75 | 71 | 93 |  | 95 | 100 | 100 | 100 | 100 | 75 | 0 | 1120320
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 97 | 50 | 33 | 17 | 19 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 2285760
88 | Ghorashal 78.5 MW PP(MAX) | 74 | 74 | 74 | 74 | 74 | 74 | 40 | 40 | 50 | 70 | 69 | 68 | 68 | 40 | 50 | 60 | 40 | 60 |  | 69 | 69 | 69 | 70 | 70 | 71 | 70 | 1517824
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [17 empty] | 40 |  | 70 | 30 | 30 |  |  |  | 0 | 128040
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 50 | 50 | 50 | 50 | 10 | 10 | 14 | 25 | 49 | 48 | 46 | 46 | 47 | 47 | 48 | 37 |  | 49 | 49 | 49 | 49 | 49 | 50 | 50 | 1038816
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 10 | 10 | 16 | 35 | 43 | 43 | 43 | 43 | 43 | 10 | 10 | 22 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 967444
94 | Gagnagar 102 MW PP (Digital Power) | 16 | [6 empty] | 24 | 50 | 50 | 84 | 102 | 102 | 102 | 102 | 102 | 102 | 102 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 1536624
95 | Patenga 50MW PP (Baraka) | 50 | 50 | 42 | [5 empty] | 37 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 957120
96 | Chattogram 108 MW PP (ECPV) | [12 empty] | 2 | 28 | 30 |  | 12 | 52 |  | 81 | 84 | 84 | 84 | 84 | 52 | 51 | 587520
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | [8 empty] | 7 | 15 | 15 | 35 | 55 | 55 | 55 | 15 | 15 | 45 |  | 55 | 55 | 55 | 55 | 55 | 40 | 40 | 653305
100 | Manikganj 55 MW PP (Northern) | [7 empty] | 17 | 17 | 17 | 35 | 35 | 55 | 55 | 55 | 17 | 35 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 0 | 651640
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2649600
102 | Sarishabari 3 MW Solar Plant | [7 empty] | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [10 empty] | 14200
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 35 | 35 | 35 | 17 | 40 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1201320
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 50 | 24 | 24 | 24 | 8 | [5 empty] | 10 | 16 | 31 | 40 | 40 | 40 | 40 | 82 |  | 195 | 200 | 200 | 200 | 200 | 180 | 150 | 1672800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [5 empty] | 12 | 30 | 30 | 67 | 100 | 78 | 82 | 80 | 80 | 85 | 82 | 84 | 113 |  | 135 | 149 | 149 | 149 | 146 | 118 | 54 | 1701500
115 | Juldah 100 MW PP Unit-3 (Acorn) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 538560
116 | Chandpur 200MW (Desh energy) | [16 empty] | 0 | 33 |  | 79 | 17 | 17 |  |  |  | 0 | 160800
117 | Ashuganj 150MW PP (Midland) | 80 | 30 | [5 empty] | 1 | 10 | 10 | 20 | 75 | 117 | 130 | 140 | 140 | 140 | 142 |  | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 1998909
118 | Bibiyana-III 400 MW CCPP | 402 | 402 | 377 | 339 | 342 | 341 | 342 | 341 | 386 | 404 | 404 | 403 | 403 | 404 | 403 | 403 | 352 | 416 |  | 415 | 417 | 416 | 416 | 416 | 415 | 417 | 9336000
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 85 | 65 | 45 | 35 | 25 | 43 | 75 | 100 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2398800
| Anwara 300 MW PP (United) | 162 | 88 | 34 | 16 | 16 |  |  | 50 | 50 | 53 | 105 | 158 | 162 | 162 | 142 | 142 | 106 | 143 |  | 142 | 143 | 143 | 143 | 162 | 162 | 161 | 2536691
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 30 | 10 | 50 | 88 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 90 |  | 90 | 90 | 90 | 90 | 100 | 100 | 100 | 2155200
120 | Eastern Zone Total | 6386 | 6196 | 5987 | 5765 | 5619 | 5381 | 5224 | 5391 | 5879 | 6221 | 6376 | 6717 | 6991 | 7030 | 7208 | 6888 | 6677 | 7847 | 0 | 8186 | 8111 | 8051 | 7904 | 7926 | 7664 | 7235 | 161655352
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [12 empty] | 6 | 32 | 32 |  | 16 | 115 |  | 115 | 115 | 116 | 115 | 115 | 85 | 32 | 750720
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 70 | 17 |  |  |  |  | 17 | 53 | 53 | 70 | 88 | 90 | 105 | 105 | 105 | 90 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1716960
130
131
132
133 | Bhola Nutan Biddut BD LTD (GAS) | [15 empty] | 25 | 30 | 40 |  | 40 | 40 | 40 | 30 |  |  | 0 | 205120
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [17 empty] | 45 |  | 32 | 32 | 32 | 48 | 80 | 64 | 32 | 341856
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 94 | 94 | 94 | 65 | 45 | 34 | 25 | 25 | 25 | 25 | 54 | 85 | 90 | 88 | 91 | 93 | 95 | 95 |  | 95 | 95 | 96 | 95 | 96 | 96 | 95 | 1804397
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 31 | 28 | 26 | 27 | 27 | 25 | 22 | 22 | 22 | 23 | 24 | 25 | 25 | 25 | 25 | 25 | 24 | 35 |  | 32 | 33 | 33 | 36 | 36 | 34 | 33 | 655646
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 40 |  | 40 | 40 | 40 | 40 | 40 |  |  | 196125
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 932 | 932 | 932 | 931 | 933 | 933 | 932 | 932 | 932 | 932 | 932 | 932 | 932 | 932 | 933 | 932 | 932 | 931 |  | 932 | 932 | 932 | 932 | 932 | 933 | 932 | 22358545
147 | Bheramara 410 MW CCPP | 340 | 345 | 345 | 345 | 345 | 340 | 300 | 300 | 300 | 300 | 345 | 345 | 340 | 300 | 340 | 345 | 320 | 390 |  | 345 | 350 | 345 | 345 | 345 | 350 | 365 | 8390880
148 | Payra 1320 MW | 550 | 550 | 520 | 520 | 520 | 480 | 430 | 430 | 430 | 430 | 430 | 460 | 470 | 470 | 470 | 470 | 400 | 400 |  | 622 | 622 | 622 | 622 | 622 | 622 | 622 | 13075500
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 149 | 149 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 149 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3656600
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [16 empty] | 7 | 50 |  | 50 | 50 | 50 |  |  |  |  | 167728
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 155 | 155 | 155 | 155 | 154 | 155 | 155 | 174 | 159 | 169 | 203 | 186 | 184 | 164 | 159 | 156 | 156 | 170 |  | 185 | 159 | 156 | 151 | 151 | 152 | 164 | 4149691
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 155 | 156 | 156 | 155 | 155 | 155 | 156 | 183 | 171 | 164 | 177 | 173 | 187 | 172 | 169 | 162 | 145 | 157 |  | 171 | 162 | 168 | 162 | 162 | 163 | 174 | 4224464
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 410 | 394 | 394 | 370 | 350 | 327 | 374 | 380 | 335 | 398 | 400 | 365 | 356 | 340 | 394 | 334 | 258 | 400 |  | 380 | 337 | 303 | 345 | 309 | 343 | 374 | 8710309
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 15 | 15 |  | 32 | 35 | 25 |  |  |  |  | 88267
162 | Bogra 22 MW PP (GBB) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 425280
163 | Bogura 20 MW PP (Energyprima) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 229608
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 208476
165 | Amnura 50 MW PP(Sinha) | [14 empty] | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 0 | 189410
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [16 empty] | 18 | 30 |  | 31 | 31 | 30 | 30 |  |  |  | 124850
168 | Santahar 50 MW Peaking PP | [16 empty] | 11 | 32 |  | 32 | 32 | 31 |  |  |  | 0 | 114000
169 | Natore 52 MW PP (Rajlanka) | [16 empty] | 8 | 35 |  | 52 | 52 | 52 | 52 |  |  | 0 | 211680
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 97 |  | 96 | 96 | 96 | 96 |  |  |  | 389352
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [16 empty] | 8 | 90 |  | 92 | 92 | 94 | 94 | 35 |  | 0 | 471168
172 | Confidence Power Bogura Unit-1 113 MW | [10 empty] | 25 | 80 | 109 | 109 | 109 | 35 | 35 | 90 |  | 109 | 109 | 109 | 109 | 109 | 70 | 70 | 1199136
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | [10 empty] | 9 | 41 | 74 | 89 | 99 | 35 | 35 | 60 |  | 102 | 109 | 109 | 109 | 109 | 106 | 75 | 1171200
177 | Sympa Solar Power 8MW | [6 empty] | 1 | 2 | 3 | 4 | 6 | 6 | 6 | 5 | 3 | 2 | 0 | [9 empty] | 41755
178
178