## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-11-04 | Wednesday
|  |  | Date (day): | 2020-11-04 |  | Wednesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13784.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14697 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-11-03 | 2020-11-04 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 130 | 150 | 150 | 150
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 115 | 115 | 115 | 75 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 200 | 200 | 165 |  | Gas shortage
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 |  |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 52 | 51 | 51 | 51 |  | 57 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under S/D for dust in gas.
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 323 | 312 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 380 | 350 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 41 | 100 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 155 | 155 | 155 | 155 |  | 150 | GT-2 Under maint.
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 72 | 98 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 50 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19 |  | 3 | Engine problem
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 170 | 145 | 200 | 200
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 102 | 94 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 150 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 37 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 55 | 56 | 56 | 56 |  | 24 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 28 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 51 | 51 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 170 | 285 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 81 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 67 | 88 | 88 |  | 17 | Engine problem
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 90 | 72 | 72 | 72 |  | 32 | Engine problem
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 2513 | 2986 | 3512 | 3852 | 504 | 1420
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 115 | 115 | 120 | 120 | 60 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 0 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 160 | 158 | 160 | 160 | 70 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 204 | 204 | 221 | 221
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 139 | 139 | 145 | 145
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 102 | 102
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 8 | 10 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 22 | 22 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 20 | 20 | 20
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 21 | 10 | 20
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 86 | 90 | 90 |  | 18 | Engine problem
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 140 | 162 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 40 | 54 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 1002 | 1226 | 1832 | 1817 | 310 | 116
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 70 | 70 | 70 | 70 | 59 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 |  | 134 | Under maint
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 160 | 149 | 225 | 225 |  |  | FGMO
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 250 | 250 | 300 | 300
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 230 | 230 | 300 | 320 |  |  | FGMO
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 0 | 0 | 5 | 5 | 40 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 2 | 2 | 5 | 5 | 50 |  | Gas shortage
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 127 | 142 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 52 | 90 | 90 |  | 68 | ST under maint.
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 100 | 165 | 165
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 102 | 152 | 163 | 173
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 52 | 52 | 52
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 21 | 20 | 21
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 38 | 48 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1163 | 1379 | 1889 | 2170 | 471 | 210
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 97 | 100 | 120 | 130 | 72 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 25 | 25 | 25 | 25 |  | 70 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 8 | 192 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 108 | 109 | 115 | 115
|  | Mymensingh PV 50 MW Solar PP |  | Solar | IPP | 50 | 0 | 0 | 41 | 0 | 40 | 0
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 303 | 448 | 523.6 | 492 | 72 | 70
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 44 | 44 | 44 | 44
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Unit-4 under shut down
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 |  | 54 | STG under maint.
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 159 | 157 | 160 | 160 |  | 170 | GT-2 S/D due to gas shortage.
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 25 | 47 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 46 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 63 | 63 | 65 | 65 |  |  | FGMO
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 87 | 87 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 192 | 205 | 200 | 200
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 25 | 25
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 275 | 300 | 341 | 341 |  |  | FGMO
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 404 | 402 | 400 | 400
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1483 | 1546 | 1595 | 1595 | 0 | 284
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 891 | 891 | 900 | 900
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 115 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 9 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 220 | 220
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 340 | 345 | 410 | 410
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 0 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 90 | 70 | 90 | 90 |  | 15 | Engine problem
| 108 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1321 | 1570 | 1875 | 2081 | 0 | 15
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 80 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 24 | 33 | 33 | 33
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 55 | 96 | 95 | 95
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 470 | 660 | 660 | 660
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 38 | 38 | 38 | 38
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 587 | 907 | 936 | 936 | 0 | 194
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 65 | 60 | 65 | 65
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 33 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 18 | 43 | 43 | 43 |  | 30 | Engine problem
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 39 | 50 | 50
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 144 | 148 | 144 | 148 |  | 75 | ST Under maint
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 162 | 153 | 225 | 225 |  |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 165 | 157 | 220 | 220 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 0 | 0 | 0 | 0 |  | 414 | Under maint.
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 33 | 0 | 33
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 7 | 10 | 10 | 10
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 52 | 52 | 52
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 88 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 70 | 109 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 660 | 1117 | 1364 | 1491 | 150 | 523
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 149 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 64 | 99 | 100 | 113
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 218 | 248 | 258 | 263 | 294 | 40
|  | Total |  |  |  |  | 20383 | 19892 | 9250 | 11427 | 13784.6 | 14697 | 1801 | 2872
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8706.0252 | 10755 | 12973.9541 | 13832.6976
| A. |  | 2020-11-03 | (Yesterday) |  |  |  |  | Tuesday
| 1 | Highest Generation : |  |  | 11427 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
| 2 | Minimum Generation : |  |  | 7846 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11427 | MW
| 3 | Day peak Generation : |  |  | 9250 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10755 | MW
| 4 | Evening peak Generation : |  |  | 11427 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 228.3587 | MKWHr | By Solar | 0.3249 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 132.5202 | MKWHr |  | By Oil: | 50.6842 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 16.7297 | MKWHr |  | By Hydro: | 3.8044 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1801 | MW | Dhaka | 4013 | 4013 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2872 | MW | Chittagong | 1071 | 1071 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4673 | MW | Khulna | 1358 | 1358 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1115.78 | MMCFD |  |  | Rajshahi | 1009 | 1009 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 159035280.554 | ii) Oil : | Taka | 376559946.65 | Comilla | 1034 | 1034 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 77222556 | Total | Taka | 612817783.204 | Mymensingh | 869 | 869 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.012 | MKWHr. | Sylhet | 475 | 475 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 317 | MW (E to W) at | 19:30 | hrs | Barisal | 308 | 308 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 91 | MW at | 1:00 | hrs | Rangpur | 618 | 618 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 31.6° C |  |  | Total | 10755 | 10755 |  | 0
| B. |  | 2020-11-04 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 31.8° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 11700 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14697 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 9400 | MW
| 4 | Reserve(Generation end) |  |  |  | 2997 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 233.8143 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7657 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.4691 | MKWHr. | ii) HVDC Flow at Peak Time |  | 891 | MW at | 19:30 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.8262 | MKWHr. | iii) Maximum HVDC Flow : |  | 906 | MW at | 4:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 104.24 |  | (b) Today: | 104.24 |  | (c) Rule Curve: |  | 108.7
.

## YesterdayGen
2020-11-03
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Mymensingh PV 50 MW Solar PP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 160 | 115 | 200 | 51 | 0 | 0 | 356 |  | 0 | 380 | 155 | 66 | 30 | 15 | 0 | 0 | 155 | 0 | 50 | 102 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 31 | 28 | 33 | 25 | 0 | 92 | 70 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 42 | 0 | 70 | 0 | 250 | 230 | 118 | 8 | 50 | 0 | 2 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 124 | 122 | 25 | 22 | 0 | 44 | 30 | 50 | 50 | 110 | 158 | 54 | 87 | 0 | 185 | 18 | 0 | 10 | 280 | 24 | 5 | 0 | 145 | 0 | 0 | 7 | 0 | 0 | 0 | 50 | 0 | 142 | 376 | 115 | 86 | 0 | 0 | 162 | 54 | 0 | 0 | 113 | 90 | 0 | 90 | 0 |  | 905 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 156 | 0 | 53 | 0 | 158 | 0 | 0 | 90 | 0 | 0 | 0 | 98 | 0 | 0 | 109 | 550 | 37 | 0 |  | 6601 | 2921 | 9522 | 3967 | 905 | 1604 | 1978 | 700 | 162 | 82 | 124 | 0 | 0 | 104.21
2:00 | 0 | 0 | 160 | 115 | 200 | 51 | 0 | 0 | 356 |  | 0 | 380 | 155 | 0 | 0 | 14 | 0 | 0 | 156 | 0 | 24 | 102 | 82 | 0 | 0 | 0 | 0 | 54 | 35 | 0 | 19 | 25 | 31 | 28 | 33 | 0 | 0 | 90 | 70 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 42 | 20 | 42 | 0 | 70 | 0 | 250 | 230 | 119 | 8 | 50 | 0 | 2 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 120 | 142 | 25 | 22 | 0 | 44 | 30 | 50 | 50 | 110 | 159 | 54 | 87 | 0 | 151 | 18 | 0 | 10 | 300 | 24 | 5 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 50 | 0 | 142 | 376 | 115 | 86 | 0 | 0 | 162 | 54 | 0 | 0 | 112 | 100 | 0 | 90 | 0 |  | 905 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 158 | 0 | 53 | 0 | 160 | 0 | 0 | 90 | 0 | 0 | 0 | 85 | 0 | 0 | 109 | 550 | 37 | 0 |  | 6292 | 2911 | 9203 | 3950 | 905 | 1633 | 1653 | 700 | 160 | 82 | 120 | 0 | 0 | 104.22
3:00 | 0 | 0 | 160 | 115 | 200 | 51 | 0 | 0 | 356 |  | 0 | 390 | 155 | 0 | 0 | 14 | 0 | 0 | 156 | 0 | 0 | 68 | 48 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 31 | 28 | 33 | 0 | 0 | 88 | 70 | 115 | 0 | 0 | 204 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 30 | 20 | 42 | 0 | 70 | 0 | 250 | 230 | 125 | 8 | 51 | 0 | 2 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 120 | 142 | 25 | 22 | 0 | 44 | 30 | 50 | 50 | 110 | 159 | 54 | 87 | 0 | 151 | 18 | 0 | 10 | 305 | 24 | 5 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 50 | 0 | 142 | 352 | 115 | 86 | 0 | 0 | 161 | 54 | 0 | 0 | 65 | 100 | 0 | 90 | 0 |  | 905 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 158 | 0 | 53 | 0 | 160 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 550 | 37 | 0 |  | 6102 | 2769 | 8871 | 3951 | 905 | 1648 | 1341 | 700 | 158 | 48 | 120 | 0 | 0 | 104.23
4:00 | 0 | 0 | 160 | 115 | 200 | 51 | 0 | 0 | 356 |  | 0 | 390 | 155 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 32 | 48 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 31 | 28 | 33 | 0 | 0 | 86 | 70 | 115 | 0 | 0 | 204 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 30 | 20 | 42 | 0 | 70 | 0 | 250 | 230 | 126 | 8 | 52 | 0 | 2 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 116 | 142 | 25 | 22 | 0 | 44 | 30 | 50 | 50 | 110 | 158 | 54 | 87 | 0 | 151 | 18 | 0 | 10 | 300 | 24 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 100 | 327 | 115 | 86 | 0 | 0 | 124 | 54 | 0 | 0 | 65 | 100 | 0 | 90 | 0 |  | 906 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 159 | 0 | 53 | 0 | 161 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 37 | 0 |  | 5931 | 2723 | 8654 | 3914 | 906 | 1644 | 1170 | 700 | 156 | 48 | 116 | 0 | 0 | 104.23
5:00 | 0 | 0 | 160 | 115 | 200 | 51 | 0 | 0 | 356 |  | 0 | 400 | 155 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 32 | 16 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 31 | 28 | 33 | 0 | 0 | 84 | 70 | 115 | 0 | 0 | 204 | 0 | 142 | 0 |  | 0 | 0 | 0 | 0 | 0 | 30 | 20 | 42 | 0 | 70 | 0 | 250 | 230 | 135 | 8 | 52 | 0 | 2 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 112 | 142 | 25 | 22 | 0 | 44 | 30 | 50 | 50 | 110 | 158 | 54 | 87 | 0 | 151 | 18 | 0 | 10 | 295 | 24 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 60 | 329 | 115 | 70 | 0 | 0 | 87 | 54 | 0 | 0 | 26 | 100 | 0 | 90 | 0 |  | 906 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 155 | 0 | 52 | 0 | 157 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 38 | 0 |  | 5778 | 2712 | 8490 | 3918 | 906 | 1646 | 1038 | 700 | 154 | 16 | 112 | 0 | 0 | 104.24
6:00 | 0 | 0 | 160 | 115 | 200 | 51 | 0 | 0 | 357 |  | 0 | 400 | 155 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 31 | 28 | 33 | 0 | 0 | 86 | 70 | 115 | 0 | 0 | 204 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 22 | 20 | 42 | 0 | 70 | 0 | 250 | 230 | 136 | 8 | 50 | 0 | 2 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 110 | 147 | 25 | 22 | 0 | 44 | 30 | 50 | 50 | 110 | 158 | 66 | 87 | 0 | 151 | 18 | 0 | 10 | 300 | 24 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 10 | 329 | 85 | 35 | 0 | 0 | 16 | 54 | 0 | 0 | 8 | 50 | 0 | 90 | 0 |  | 905 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 161 | 0 | 52 | 0 | 163 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 37 | 0 |  | 5458 | 2674 | 8132 | 3944 | 905 | 1653 | 694 | 670 | 156 | 0 | 110 | 0 | 0 | 104.24
7:00 | 0 | 0 | 160 | 115 | 200 | 51 | 0 | 0 | 357 |  | 0 | 390 | 155 | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 30 | 28 | 33 | 0 | 0 | 88 | 70 | 115 | 0 | 0 | 226 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 20 | 40 | 0 | 70 | 0 | 250 | 230 | 130 | 8 | 51 | 0 | 2 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 98 | 146 | 25 | 22 | 0 | 44 | 30 | 50 | 50 | 110 | 159 | 65 | 30 | 0 | 151 | 18 | 0 | 10 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5 | 10 | 0 | 10 | 329 | 85 | 35 | 0 | 0 | 16 | 17 | 0 | 0 | 8 | 50 | 0 | 42 | 3 |  | 905 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 163 | 0 | 53 | 0 | 165 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 520 | 37 | 0 |  | 5197 | 2649 | 7846 | 3908 | 905 | 1582 | 516 | 670 | 158 | 0 | 98 | 9 | 0 | 104.25
8:00 | 0 | 0 | 147 | 115 | 200 | 52 | 0 | 0 | 300 |  | 0 | 380 | 120 | 2 | 0 | 12 | 0 | 0 | 110 | 0 | 2 | 50 | 0 | 0 | 0 | 0 | 0 | 45 | 17 | 0 | 19 | 25 | 30 | 28 | 33 | 10 | 0 | 88 | 70 | 115 | 0 | 0 | 204 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 22 | 20 | 12 | 0 | 70 | 0 | 250 | 230 | 131 | 8 | 50 | 0 | 2 | 0 | 43 | 0 | 0 | 1 | 19 | 8 | 33 | 18 | 90 | 126 | 25 | 22 | 0 | 44 | 30 | 50 | 50 | 110 | 157 | 40 | 87 | 0 | 191 | 18 | 0 | 10 | 285 | 16 | 5 | 0 | 37 | 0 | 0 | 7 | 0 | 42 | 2 | 22 | 0 | 26 | 330 | 100 | 0 | 0 | 1 | 82 | 26 | 0 | 0 | 35 | 90 | 0 | 65 | 8 |  | 891 | 0 | 290 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 175 | 0 | 24 | 0 | 177 | 0 | 0 | 53 | 0 | 0 | 0 | 8 | 0 | 2 | 30 | 440 | 37 | 0 |  | 5420 | 2538 | 7958 | 3779 | 891 | 1499 | 938 | 590 | 158 | 0 | 90 | 13 | 0 | 104.25
9:00 | 0 | 0 | 160 | 115 | 200 | 52 | 0 | 0 | 282 |  | 0 | 380 | 120 | 15 | 20 | 55 | 0 | 0 | 75 | 0 | 14 | 64 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 30 | 28 | 33 | 46 | 0 | 89 | 70 | 115 | 0 | 0 | 218 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 6 | 0 | 70 | 0 | 250 | 230 | 131 | 8 | 51 | 0 | 2 | 0 | 43 | 0 | 0 | 8 | 19 | 8 | 33 | 15 | 88 | 101 | 25 | 22 | 1 | 44 | 30 | 50 | 50 | 110 | 157 | 40 | 87 | 0 | 205 | 18 | 0 | 10 | 270 | 16 | 5 | 0 | 145 | 0 | 0 | 8 | 0 | 102 | 1 | 22 | 0 | 100 | 330 | 108 | 0 | 0 | 1 | 87 | 39 | 0 | 0 | 85 | 100 | 0 | 90 | 27 |  | 890 | 0 | 290 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 100 | 0 | 130 | 0 | 23 | 0 | 130 | 0 | 0 | 53 | 0 | 0 | 0 | 40 | 0 | 3 | 35 | 440 | 38 | 0 |  | 5914 | 2486 | 8400 | 3644 | 890 | 1460 | 1536 | 590 | 159 | 0 | 88 | 33 | 0 | 104.25
10:00 | 0 | 0 | 160 | 115 | 200 | 52 | 0 | 0 | 282 |  | 0 | 380 | 120 | 16 | 50 | 55 | 0 | 0 | 140 | 0 | 24 | 64 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 30 | 28 | 33 | 51 | 0 | 90 | 70 | 115 | 0 | 0 | 232 | 0 | 100 | 0 |  | 0 | 0 | 0 | 8 | 0 | 50 | 18 | 4 | 0 | 70 | 0 | 250 | 230 | 126 | 8 | 50 | 0 | 2 | 0 | 43 | 0 | 0 | 8 | 19 | 8 | 33 | 15 | 94 | 101 | 25 | 20 | 2 | 44 | 30 | 25 | 47 | 110 | 160 | 40 | 87 | 0 | 205 | 18 | 0 | 10 | 270 | 16 | 5 | 0 | 145 | 0 | 0 | 8 | 0 | 94 | 0 | 22 | 0 | 100 | 401 | 108 | 0 | 0 | 1 | 89 | 54 | 0 | 0 | 85 | 100 | 0 | 90 | 26 |  | 890 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 7 | 11 | 0 | 0 | 150 | 0 | 0 | 100 | 0 | 138 | 0 | 23 | 0 | 142 | 0 | 0 | 53 | 0 | 0 | 0 | 40 | 0 | 4 | 35 | 440 | 38 | 0 |  | 6096 | 2553 | 8649 | 3872 | 890 | 1427 | 1583 | 590 | 160 | 0 | 94 | 33 | 0 | 104.25
11:00 | 0 | 0 | 160 | 115 | 200 | 52 | 0 | 0 | 323 |  | 0 | 380 | 155 | 20 | 63 | 55 | 0 | 0 | 150 | 0 | 60 | 75 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 10 | 19 | 25 | 30 | 28 | 33 | 51 | 0 | 90 | 70 | 115 | 0 | 0 | 206 | 0 | 139 | 0 |  | 0 | 0 | 0 | 8 | 0 | 50 | 18 | 4 | 0 | 70 | 0 | 250 | 230 | 152 | 8 | 50 | 0 | 2 | 0 | 43 | 0 | 0 | 8 | 19 | 8 | 33 | 15 | 94 | 99 | 25 | 20 | 2 | 44 | 30 | 25 | 47 | 110 | 160 | 65 | 87 | 0 | 206 | 18 | 0 | 10 | 270 | 16 | 0 | 0 | 145 | 0 | 0 | 8 | 0 | 81 | 0 | 22 | 0 | 105 | 402 | 108 | 0 | 0 | 3 | 120 | 54 | 0 | 0 | 80 | 100 | 0 | 90 | 28 |  | 890 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 7 | 11 | 0 | 0 | 150 | 0 | 0 | 120 | 0 | 186 | 0 | 55 | 0 | 162 | 0 | 0 | 70 | 0 | 0 | 0 | 38 | 0 | 5 | 50 | 470 | 38 | 0 |  | 6337 | 2708 | 9045 | 4009 | 890 | 1494 | 1740 | 620 | 160 | 0 | 94 | 38 | 0 | 104.26
12:00 | 0 | 0 | 130 | 115 | 200 | 52 | 0 | 0 | 323 |  | 0 | 380 | 155 | 41 | 72 | 40 | 0 | 0 | 170 | 0 | 100 | 102 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 19 | 25 | 30 | 28 | 33 | 51 | 0 | 90 | 70 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 8 | 0 | 50 | 18 | 4 | 0 | 70 | 0 | 250 | 230 | 160 | 8 | 50 | 0 | 2 | 0 | 43 | 0 | 0 | 8 | 19 | 8 | 33 | 15 | 102 | 97 | 25 | 22 | 2 | 44 | 30 | 25 | 50 | 110 | 159 | 63 | 87 | 0 | 192 | 18 | 0 | 10 | 275 | 16 | 0 | 0 | 170 | 0 | 0 | 8 | 0 | 81 | 0 | 22 | 0 | 127 | 404 | 108 | 0 | 0 | 2 | 140 | 40 | 0 | 0 | 38 | 100 | 0 | 90 | 41 |  | 891 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 7 | 11 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 162 | 0 | 55 | 0 | 165 | 0 | 0 | 90 | 0 | 0 | 0 | 64 | 0 | 4 | 70 | 470 | 38 | 0 |  | 6464 | 2786 | 9250 | 3993 | 891 | 1511 | 1924 | 620 | 160 | 0 | 102 | 49 | 0 | #REF!
13:00 | 0 | 0 | 130 | 115 | 200 | 52 | 0 | 0 | 323 |  | 0 | 360 | 155 | 41 | 98 | 40 | 0 | 0 | 180 | 0 | 100 | 102 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 19 | 25 | 27 | 28 | 17 | 51 | 0 | 90 | 70 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 8 | 0 | 50 | 20 | 10 | 0 | 70 | 0 | 250 | 230 | 157 | 8 | 50 | 0 | 2 | 0 | 43 | 0 | 0 | 8 | 19 | 8 | 25 | 15 | 102 | 97 | 25 | 22 | 2 | 44 | 30 | 25 | 50 | 110 | 158 | 60 | 86 | 0 | 192 | 18 | 0 | 10 | 305 | 16 | 5 | 0 | 195 | 0 | 0 | 8 | 0 | 90 | 0 | 22 | 0 | 130 | 403 | 108 | 0 | 0 | 2 | 143 | 54 | 0 | 0 | 46 | 100 | 0 | 90 | 45 |  | 890 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 7 | 11 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 183 | 0 | 88 | 0 | 207 | 0 | 0 | 90 | 0 | 0 | 0 | 62 | 0 | 4 | 70 | 470 | 36 | 0 |  | 6569 | 2891 | 9460 | 4053 | 890 | 1556 | 2010 | 620 | 160 | 16 | 102 | 53 | 9460 | 104.26
14:00 | 0 | 0 | 160 | 115 | 200 | 53 | 0 | 0 | 303 |  | 0 | 360 | 155 | 41 | 98 | 45 | 0 | 0 | 155 | 0 | 100 | 102 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 19 | 25 | 29 | 28 | 17 | 25 | 0 | 92 | 70 | 115 | 0 | 0 | 215 | 0 | 106 | 0 |  | 0 | 0 | 0 | 8 | 0 | 50 | 20 | 4 | 0 | 70 | 0 | 250 | 230 | 151 | 8 | 50 | 0 | 2 | 0 | 43 | 0 | 0 | 8 | 19 | 8 | 33 | 15 | 106 | 97 | 25 | 22 | 2 | 44 | 30 | 25 | 50 | 110 | 158 | 40 | 86 | 0 | 203 | 18 | 0 | 10 | 270 | 16 | 5 | 0 | 195 | 0 | 0 | 8 | 0 | 100 | 8 | 22 | 0 | 140 | 415 | 115 | 0 | 0 | 1 | 143 | 54 | 0 | 0 | 47 | 100 | 0 | 90 | 35 |  | 890 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 142 | 0 | 166 | 0 | 92 | 0 | 171 | 0 | 0 | 90 | 0 | 0 | 0 | 72 | 0 | 5 | 70 | 470 | 38 | 0 |  | 6509 | 2869 | 9378 | 3998 | 890 | 1508 | 2027 | 620 | 162 | 16 | 106 | 51 | 0 | 104.26
15:00 | 0 | 0 | 150 | 115 | 200 | 53 | 0 | 0 | 322 |  | 0 | 360 | 155 | 41 | 98 | 55 | 0 | 0 | 185 | 0 | 100 | 94 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 37 | 19 | 25 | 29 | 28 | 33 | 25 | 0 | 89 | 70 | 115 | 0 | 0 | 210 | 0 | 107 | 0 |  | 0 | 0 | 0 | 8 | 0 | 50 | 18 | 3 | 0 | 70 | 0 | 250 | 230 | 147 | 8 | 50 | 0 | 2 | 0 | 43 | 0 | 0 | 8 | 19 | 8 | 33 | 18 | 120 | 98 | 25 | 22 | 1 | 43 | 30 | 25 | 50 | 110 | 159 | 62 | 84 | 0 | 205 | 18 | 0 | 10 | 305 | 16 | 5 | 0 | 195 | 0 | 0 | 8 | 0 | 110 | 6 | 22 | 0 | 143 | 404 | 115 | 0 | 0 | 3 | 143 | 54 | 0 | 0 | 47 | 100 | 0 | 90 | 26 |  | 890 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 10 | 11 | 0 | 0 | 149 | 0 | 0 | 143 | 0 | 190 | 0 | 92 | 0 | 192 | 0 | 0 | 90 | 0 | 0 | 0 | 82 | 0 | 2 | 109 | 490 | 38 | 0 |  | 6621 | 2971 | 9592 | 4082 | 890 | 1555 | 2093 | 639 | 159 | 16 | 120 | 38 | 0 | 104.26
16:00 | 0 | 0 | 150 | 115 | 200 | 53 | 0 | 0 | 283 |  | 0 | 330 | 155 | 41 | 64 | 15 | 0 | 0 | 150 | 0 | 70 | 94 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 37 | 19 | 25 | 29 | 28 | 33 | 25 | 0 | 89 | 70 | 115 | 0 | 0 | 205 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 4 | 0 | 70 | 0 | 250 | 230 | 142 | 8 | 50 | 0 | 2 | 0 | 43 | 0 | 0 | 8 | 19 | 8 | 33 | 18 | 116 | 98 | 25 | 22 | 0 | 43 | 30 | 25 | 50 | 110 | 158 | 63 | 86 | 0 | 205 | 18 | 0 | 10 | 300 | 16 | 0 | 0 | 195 | 0 | 0 | 8 | 0 | 107 | 6 | 22 | 0 | 143 | 404 | 115 | 0 | 0 | 1 | 106 | 54 | 0 | 0 | 47 | 100 | 0 | 90 | 9 |  | 891 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 10 | 11 | 0 | 0 | 148 | 0 | 0 | 143 | 0 | 178 | 0 | 92 | 0 | 191 | 0 | 0 | 90 | 0 | 0 | 0 | 90 | 0 | 1 | 70 | 490 | 38 | 0 |  | 6324 | 2933 | 9257 | 4024 | 891 | 1486 | 1910 | 638 | 159 | 16 | 116 | 17 | 0 | 104.27
17:00 | 0 | 0 | 150 | 115 | 200 | 51 | 0 | 0 | 283 |  | 0 | 330 | 155 | 41 | 64 | 15 | 0 | 0 | 70 | 0 | 60 | 94 | 48 | 0 | 0 | 0 | 0 | 54 | 17 | 37 | 19 | 25 | 29 | 33 | 33 | 25 | 0 | 87 | 70 | 115 | 0 | 0 | 204 | 0 | 70 | 0 |  | 0 | 0 | 22 | 0 | 0 | 50 | 20 | 12 | 0 | 70 | 0 | 250 | 230 | 131 | 8 | 50 | 0 | 2 | 0 | 43 | 0 | 0 | 8 | 19 | 8 | 33 | 18 | 118 | 98 | 25 | 15 | 0 | 44 | 30 | 25 | 50 | 110 | 158 | 40 | 86 | 0 | 191 | 18 | 0 | 10 | 310 | 16 | 0 | 0 | 215 | 0 | 0 | 60 | 0 | 125 | 0 | 22 | 2 | 142 | 352 | 115 | 0 | 0 | 0 | 106 | 54 | 0 | 0 | 47 | 100 | 0 | 78 | 1 |  | 890 | 0 | 340 | 0 | 40 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 22 | 0 | 0 | 0 | 60 | 0 | 5 | 0 | 18 | 0 | 24 | 13 | 16 | 18 | 10 | 11 | 0 | 0 | 149 | 0 | 0 | 135 | 0 | 164 | 0 | 95 | 0 | 173 | 0 | 0 | 0 | 0 | 1 | 0 | 76 | 0 | 0 | 70 | 490 | 38 | 0 |  | 6231 | 2860 | 9091 | 3737 | 890 | 1503 | 1929 | 639 | 157 | 117 | 118 | 1 | 0 | 104.27
18:00 | 0 | 0 | 150 | 115 | 200 | 51 | 0 | 0 | 312 |  | 0 | 360 | 155 | 85 | 76 | 31 | 0 | 0 | 145 | 0 | 80 | 94 | 150 | 72 | 0 | 0 | 0 | 54 | 55 | 37 | 19 | 25 | 20 | 33 | 33 | 40 | 0 | 87 | 70 | 115 | 0 | 22 | 204 | 0 | 139 | 0 |  | 0 | 0 | 85 | 40 | 97 | 50 | 20 | 11 | 0 | 70 | 0 | 250 | 230 | 136 | 8 | 50 | 0 | 2 | 0 | 43 | 0 | 50 | 32 | 19 | 8 | 33 | 18 | 152 | 98 | 25 | 22 | 0 | 44 | 30 | 34 | 46 | 110 | 157 | 65 | 86 | 0 | 205 | 18 | 0 | 10 | 290 | 16 | 5 | 0 | 265 | 60 | 25 | 136 | 48 | 149 | 0 | 22 | 114 | 142 | 401 | 115 | 2 | 0 | 0 | 142 | 54 | 0 | 0 | 48 | 100 | 0 | 72 | 0 |  | 889 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 5 | 4 | 40 | 0 | 32 | 74 | 0 | 0 | 60 | 50 | 8 | 70 | 43 | 0 | 37 | 52 | 33 | 18 | 10 | 11 | 0 | 0 | 149 | 0 | 0 | 110 | 0 | 156 | 0 | 96 | 12 | 171 | 0 | 0 | 0 | 0 | 75 | 0 | 92 | 0 | 0 | 109 | 615 | 38 | 0 |  | 7589 | 3519 | 11108 | 3946 | 889 | 1557 | 3151 | 764 | 157 | 492 | 152 | 0 | 0 | 104.27
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 150 | 115 | 200 | 51 | 0 | 0 | 312 |  | 0 | 350 | 155 | 100 | 98 | 55 | 0 | 0 | 145 | 0 | 100 | 94 | 150 | 50 | 0 | 0 | 0 | 54 | 55 | 37 | 19 | 25 | 31 | 33 | 33 | 51 | 0 | 88 | 70 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 85 | 10 | 88 | 50 | 20 | 20 | 0 | 70 | 0 | 250 | 230 | 136 | 8 | 51 | 0 | 2 | 0 | 43 | 0 | 25 | 43 | 19 | 8 | 33 | 21 | 146 | 101 | 25 | 22 | 0 | 44 | 30 | 47 | 46 | 110 | 158 | 63 | 86 | 0 | 205 | 18 | 0 | 10 | 260 | 16 | 11 | 0 | 275 | 0 | 0 | 192 | 0 | 149 | 0 | 22 | 100 | 142 | 401 | 109 | 55 | 0 | 0 | 162 | 54 | 0 | 0 | 48 | 100 | 0 | 72 | 0 |  | 891 | 0 | 340 | 0 | 115 | 0 | 0 | 0 | 9 | 0 | 40 | 0 | 32 | 80 | 0 | 0 | 60 | 50 | 11 | 88 | 43 | 0 | 37 | 52 | 33 | 18 | 10 | 11 | 0 | 0 | 149 | 0 | 0 | 144 | 0 | 174 | 0 | 97 | 77 | 173 | 0 | 0 | 17 | 0 | 110 | 0 | 96 | 0 | 0 | 109 | 660 | 38 | 0 |  | 7570 | 3764 | 11334 | 4018 | 891 | 1540 | 3284 | 809 | 158 | 488 | 146 | 0 | 0 | 104.27
19:30 | 0 | 0 | 150 | 115 | 200 | 51 | 0 | 0 | 312 |  | 0 | 350 | 155 | 100 | 98 | 55 | 0 | 0 | 145 | 0 | 100 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 37 | 19 | 25 | 31 | 33 | 33 | 51 | 0 | 88 | 70 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 85 | 10 | 86 | 50 | 20 | 21 | 0 | 70 | 0 | 250 | 230 | 149 | 8 | 52 | 0 | 2 | 0 | 43 | 0 | 0 | 52 | 19 | 8 | 33 | 21 | 152 | 100 | 25 | 22 | 0 | 44 | 30 | 47 | 46 | 110 | 157 | 63 | 87 | 0 | 205 | 18 | 0 | 10 | 300 | 16 | 11 | 0 | 285 | 0 | 0 | 192 | 0 | 149 | 0 | 22 | 100 | 142 | 402 | 109 | 67 | 0 | 0 | 162 | 54 | 0 | 0 | 48 | 100 | 0 | 72 | 0 |  | 891 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 9 | 0 | 40 | 0 | 33 | 80 | 0 | 0 | 60 | 50 | 33 | 88 | 43 | 0 | 39 | 52 | 33 | 18 | 10 | 11 | 0 | 0 | 149 | 0 | 0 | 148 | 0 | 153 | 0 | 96 | 100 | 157 | 0 | 0 | 70 | 0 | 113 | 0 | 99 | 0 | 0 | 109 | 660 | 38 | 0 |  | 7585 | 3842 | 11427 | 4003 | 891 | 1582 | 3345 | 809 | 158 | 487 | 152 | 0 | 0 | 0
20:00 | 0 | 0 | 150 | 115 | 200 | 51 | 0 | 0 | 310 |  | 0 | 350 | 155 | 100 | 98 | 55 | 0 | 0 | 113 | 0 | 100 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 37 | 19 | 25 | 31 | 33 | 33 | 51 | 0 | 88 | 70 | 115 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 68 | 10 | 86 | 50 | 20 | 27 | 0 | 70 | 0 | 250 | 230 | 154 | 8 | 51 | 0 | 2 | 0 | 43 | 0 | 0 | 45 | 19 | 8 | 33 | 21 | 150 | 100 | 25 | 22 | 0 | 44 | 30 | 47 | 46 | 110 | 157 | 64 | 87 | 0 | 204 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 286 | 0 | 0 | 196 | 0 | 149 | 0 | 22 | 17 | 140 | 402 | 109 | 67 | 0 | 0 | 162 | 54 | 0 | 0 | 61 | 100 | 0 | 72 | 0 |  | 891 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 3 | 0 | 40 | 0 | 33 | 80 | 0 | 0 | 60 | 31 | 25 | 93 | 43 | 0 | 45 | 52 | 32 | 18 | 10 | 11 | 0 | 0 | 149 | 0 | 0 | 148 | 0 | 152 | 0 | 97 | 0 | 157 | 0 | 0 | 90 | 0 | 113 | 0 | 102 | 0 | 0 | 109 | 660 | 37 | 0 |  | 7457 | 3741 | 11198 | 3973 | 891 | 1576 | 3194 | 809 | 158 | 447 | 150 | 0 | 0 | 104.27
21:00 | 0 | 0 | 150 | 115 | 200 | 51 | 0 | 0 | 310 |  | 0 | 350 | 155 | 100 | 98 | 55 | 0 | 0 | 120 | 0 | 100 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 37 | 19 | 25 | 31 | 33 | 33 | 51 | 0 | 90 | 70 | 115 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 34 | 0 | 86 | 50 | 20 | 32 | 0 | 70 | 0 | 250 | 230 | 155 | 8 | 50 | 0 | 2 | 0 | 43 | 0 | 0 | 52 | 19 | 8 | 33 | 21 | 146 | 100 | 25 | 22 | 0 | 44 | 30 | 49 | 50 | 110 | 158 | 64 | 87 | 0 | 204 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 286 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 142 | 402 | 109 | 67 | 0 | 0 | 162 | 54 | 0 | 0 | 105 | 100 | 0 | 72 | 0 |  | 891 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 80 | 0 | 0 | 65 | 0 | 0 | 10 | 43 | 0 | 0 | 25 | 0 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 148 | 0 | 155 | 0 | 95 | 0 | 161 | 0 | 0 | 90 | 0 | 70 | 0 | 110 | 0 | 0 | 109 | 660 | 38 | 0 |  | 7548 | 3431 | 10979 | 3993 | 891 | 1585 | 3200 | 810 | 160 | 194 | 146 | 0 | 0 | #REF!
22:00 | 0 | 0 | 150 | 115 | 200 | 51 | 0 | 0 | 306 |  | 0 | 350 | 155 | 100 | 98 | 55 | 0 | 0 | 120 | 0 | 100 | 94 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 37 | 19 | 25 | 31 | 33 | 33 | 51 | 0 | 91 | 70 | 115 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 15 | 50 | 20 | 40 | 0 | 70 | 0 | 250 | 230 | 155 | 8 | 50 | 0 | 2 | 0 | 43 | 0 | 0 | 25 | 19 | 0 | 33 | 21 | 144 | 102 | 25 | 22 | 0 | 44 | 30 | 50 | 50 | 110 | 158 | 63 | 84 | 0 | 204 | 17 | 0 | 10 | 280 | 24 | 11 | 0 | 286 | 0 | 0 | 200 | 0 | 102 | 0 | 100 | 0 | 142 | 415 | 115 | 86 | 0 | 0 | 162 | 54 | 0 | 0 | 106 | 100 | 0 | 72 | 0 |  | 890 | 0 | 340 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 96 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 148 | 0 | 151 | 0 | 76 | 0 | 156 | 0 | 0 | 90 | 0 | 0 | 0 | 110 | 0 | 0 | 109 | 660 | 38 | 0 |  | 7364 | 3258 | 10622 | 3992 | 890 | 1559 | 2951 | 810 | 161 | 115 | 144 | 0 | 0 | 0
23:00 | 0 | 0 | 150 | 115 | 200 | 51 | 0 | 0 | 320 |  | 0 | 350 | 155 | 72 | 80 | 30 | 0 | 0 | 120 | 0 | 88 | 102 | 100 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 31 | 33 | 33 | 51 | 0 | 92 | 70 | 115 | 0 | 0 | 213 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 12 | 50 | 20 | 42 | 0 | 70 | 0 | 250 | 230 | 157 | 8 | 50 | 0 | 2 | 0 | 43 | 0 | 0 | 25 | 19 | 8 | 33 | 21 | 140 | 122 | 25 | 22 | 0 | 44 | 30 | 50 | 50 | 110 | 159 | 65 | 84 | 0 | 205 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 130 | 0 | 0 | 160 | 0 | 0 | 0 | 100 | 0 | 142 | 416 | 115 | 86 | 0 | 0 | 162 | 54 | 0 | 0 | 105 | 100 | 0 | 72 | 0 |  | 891 | 0 | 365 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 80 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 148 | 0 | 154 | 0 | 76 | 0 | 158 | 0 | 0 | 90 | 0 | 0 | 0 | 112 | 0 | 0 | 109 | 660 | 37 | 0 |  | 7011 | 3214 | 10225 | 4068 | 891 | 1572 | 2482 | 810 | 162 | 100 | 140 | 0 | 0 | 0
24:00 | 0 | 0 | 150 | 115 | 200 | 51 | 0 | 0 | 330 |  | 0 | 350 | 155 | 50 | 70 | 30 | 0 | 0 | 120 | 0 | 50 | 102 | 50 | 0 | 0 | 0 | 0 | 54 | 35 | 17 | 19 | 25 | 31 | 33 | 33 | 51 | 0 | 93 | 70 | 115 | 0 | 0 | 210 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 12 | 50 | 20 | 42 | 0 | 70 | 0 | 250 | 230 | 157 | 8 | 50 | 0 | 2 | 0 | 43 | 0 | 0 | 8 | 19 | 8 | 33 | 21 | 138 | 122 | 25 | 22 | 0 | 44 | 30 | 50 | 50 | 110 | 157 | 65 | 84 | 0 | 205 | 17 | 0 | 10 | 300 | 24 | 11 | 0 | 80 | 0 | 0 | 120 | 0 | 0 | 0 | 100 | 0 | 142 | 412 | 115 | 86 | 0 | 0 | 162 | 54 | 0 | 0 | 105 | 100 | 0 | 72 | 0 |  | 891 | 0 | 345 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 48 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 148 | 0 | 157 | 0 | 77 | 0 | 160 | 0 | 0 | 90 | 0 | 0 | 0 | 102 | 0 | 0 | 109 | 660 | 36 | 0 |  | 6783 | 3126 | 9909 | 4043 | 891 | 1604 | 2210 | 810 | 163 | 50 | 138 | 0 | 0 | 0
KWH | 0 | 0 | 3656000 | 2740500 | 4781036 | 1227363 | 0 | 0 | 7678000 |  | 0 | 7659750 | 3595025 | 1021440 | 1422216 | 829778 | 0 | 0 | 3659000 | 0 | 1417920 | 1870704 | 1306560 | 145351 | 0 | 0 | 0 | 1227600 | 643433 | 448126 | 420948 | 600000 | 688140 | 788000 | 810900 | 746508 | 0 | 2116407 | 1688000 | 2800000 | 0 | 43228 | 4918134 | 0 | 3003324 | 0 |  | 0 | 0 | 298681 | 141480 | 436800 | 1055040 | 475392 | 565440 | 0 | 1662360 | 0 | 6359400 | 5621000 | 3425000 | 217454 | 1190590 | 0 | 61440 | 0 | 1023160 | 0 | 81072 | 349939 | 464076 | 186300 | 756900 | 476810 | 2826240 | 2653480 | 594240 | 497232 | 11750 | 1034000 | 721200 | 987600 | 1185408 | 2662772 | 3541000 | 1366272 | 2025600 | 0 | 4512030 | 402000 | 0 | 246780 | 7235200 | 463176 | 123000 | 0 | 3673308 | 50909 | 21694 | 1432800 | 42326 | 1678900 | 32265 | 988800 | 349920 | 2867054 | 9111000 | 2656800 | 985968 | 0 | 14280 | 3041018 | 1211719 | 0 | 0 | 1633800 | 2327040 | 0 | 1973760 | 235950 |  | 21469090 | 0 | 8553312 | 0 | 699840 | 0 | 0 | 0 | 24950 | 2304 | 118875 | 0 | 601422 | 510720 | 0 | 0 | 1530000 | 135056 | 46322 | 258424 | 369270 | 0 | 110255 | 181920 | 103914 | 425280 | 219528 | 238032 | 0 | 0 | 3669100 | 0 | 0 | 3486400 | 0 | 4118509 | 0 | 1542991 | 163200 | 4216609 | 0 | 0 | 1726560 | 0 | 423072 | 0 | 1514880 | 0 | 30659 | 1683648 | 13060600 | 903900 | 0 |  | 156220016 | 72138642 | 228358658 | 96051062 | 21469090 | 36469088 | 48316629 | 16729700 | 3804407 | 2367538 | 2826240 | 324904 | 0
Fuel Cost | 0 | 0 | 5337760 | 4028535 | 5306949.96 | 1620119.16 | 0 | 0 | 7908340 |  | 0 | 8349127.5 | 3990477.75 | 7752729.6 | 9799068.24 | 7019921.88 | 0 | 0 | 6330070 | 0 | 10676937.6 | 17060820.48 | 12856550.4 | 1340136.22 | 0 | 0 | 0 | 8961480 | 4973737.09 | 4418522.36 | 315711 | 450000 | 0 | 0 | 0 | 7218732.36 | 0 | 571429.89 | 455760 | 5068000 | 0 | 401588.12 | 5360766.06 | 0 | 5105650.8 | 0 |  | 0 | 0 | 2897205.7 | 1351134 | 3800160 | 8355916.8 | 598993.92 | 1679356.8 | 0 | 2460292.8 | 0 | 4705956 | 5621000 | 3151000 | 280515.66 | 1369178.5 | 0 | 86016 | 0 | 1749603.6 | 0 | 818827.2 | 3341917.45 | 589376.52 | 139725 | 1324575 | 357607.5 | 21196800 | 2812688.8 | 5395699.2 | 631484.64 | 187295 | 1695760 | 1153920 | 1757928 | 1849236.48 | 3035560.08 | 3682640 | 2691555.84 | 3868896 | 0 | 7805811.9 | 880380 | 0 | 503431.2 | 7307552 | 347382 | 93480 | 0 | 27770208.48 | 864434.82 | 362723.68 | 7450560 | 707690.72 | 16520376 | 377177.85 | 8058720 | 3796632 | 20212730.7 | 8473230 | 24230016 | 9317397.6 | 0 | 0 | 22990096.08 | 10554072.49 | 0 | 0 | 14001666 | 15498086.4 | 0 | 0 | 0 |  | 123661958.4 | 0 | 8980977.6 | 0 | 5500742.4 | 0 | 0 | 0 | 261725.5 | 24145.92 | 1238677.5 | 0 | 932204.1 | 4984627.2 | 0 | 0 | 3136500 | 1328951.04 | 470631.52 | 2287052.4 | 2843379 | 0 | 1068370.95 | 1762804.8 | 1007965.8 | 816537.6 | 340268.4 | 180190.224 | 0 | 0 | 19886522 | 0 | 0 | 4079088 | 0 | 5436431.88 | 0 | 2314486.5 | 2776032 | 4933432.53 | 0 | 0 | 18025286.4 | 0 | 4014953.28 | 0 | 11755468.8 | 0 | 338781.95 | 12442158.72 | 57336034 | 0 | 0 |  | 455440599.88 | 304166386.414 | 759606986.294 | 114636101.474 | 123661958.4 | 44399179.08 | 353538520.22 | 77222556 | 1027189.89 | 23021426.43 | 21196800 | 903254.8 | 0
Yesterday Day Peak | 0 | 0 | 130 | 115 | 200 | 52 | 0 | 0 | 323 |  | 0 | 380 | 155 | 41 | 72 | 40 | 0 | 0 | 170 | 0 | 100 | 102 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 19 | 25 | 30 | 28 | 33 | 51 | 0 | 90 | 70 | 115 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 8 | 0 | 50 | 18 | 4 | 0 | 70 | 0 | 250 | 230 | 160 | 8 | 50 | 0 | 2 | 0 | 43 | 0 | 0 | 8 | 19 | 8 | 33 | 15 | 102 | 97 | 25 | 22 | 2 | 44 | 30 | 25 | 50 | 110 | 159 | 63 | 87 | 0 | 192 | 18 | 0 | 10 | 275 | 16 | 0 | 0 | 170 | 0 | 0 | 8 | 0 | 81 | 0 | 22 | 0 | 127 | 404 | 108 | 0 | 0 | 2 | 140 | 40 | 0 | 0 | 38 | 100 | 0 | 90 | 41 |  | 891 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 7 | 11 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 162 | 0 | 55 | 0 | 165 | 0 | 0 | 90 | 0 | 0 | 0 | 64 | 0 | 4 | 70 | 470 | 38 | 0 |  | 9250 | DayPeak
Yesterday Evening Peak | 0 | 0 | 150 | 115 | 200 | 51 | 0 | 0 | 312 | 0 | 0 | 350 | 155 | 100 | 98 | 55 | 0 | 0 | 145 | 0 | 100 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 37 | 19 | 25 | 31 | 33 | 33 | 51 | 0 | 88 | 70 | 115 | 0 | 0 | 204 | 0 | 139 | 0 | 0 | 0 | 0 | 85 | 10 | 86 | 50 | 20 | 21 | 0 | 70 | 0 | 250 | 230 | 149 | 8 | 52 | 0 | 2 | 0 | 43 | 0 | 0 | 52 | 19 | 8 | 33 | 21 | 152 | 100 | 25 | 22 | 0 | 44 | 30 | 47 | 46 | 110 | 157 | 63 | 87 | 0 | 205 | 18 | 0 | 10 | 300 | 16 | 11 | 0 | 285 | 0 | 0 | 192 | 0 | 149 | 0 | 22 | 100 | 142 | 402 | 109 | 67 | 0 | 0 | 162 | 54 | 0 | 0 | 48 | 100 | 0 | 72 | 0 |  | 891 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 9 | 0 | 40 | 0 | 33 | 80 | 0 | 0 | 60 | 50 | 33 | 88 | 43 | 0 | 39 | 52 | 33 | 18 | 10 | 11 | 0 | 0 | 149 | 0 | 0 | 148 | 0 | 153 | 0 | 96 | 100 | 157 | 0 | 0 | 70 | 0 | 113 | 0 | 99 | 0 | 0 | 109 | 660 | 38 | 0 |  | 11427 | EvPeak
Forecast for Evening | 0 | 0 | 150 | 115 | 200 | 51 | 0 | 0 | 360 | 0 | 0 | 450 | 155 | 100 | 100 | 55 | 0 | 0 | 200 | 0 | 100 | 100 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 31 | 33 | 33 | 52 | 0 | 90 | 70 | 120 | 0 | 25 | 221 | 0 | 145 | 0 | 0 | 0 |  | 102 | 100 | 90 | 50 | 20 | 20 | 0 | 70 | 0 | 300 | 320 | 225 | 8 | 90 | 5 | 5 | 0 | 43 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 173 | 130 | 25 | 22 | 0 | 44 | 30 | 51 | 44 | 110 | 160 | 65 | 86 | 0 | 200 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 165 | 150 | 400 | 115 | 88 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 72 | 0 |  | 900 | 16 | 410 | 0 | 115 | 220 | 0 | 0 | 30 | 60 | 40 | 0 | 33 | 110 | 0 | 0 | 65 | 50 | 40 | 100 | 43 | 0 | 50 | 52 | 33 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 148 | 0 | 225 | 0 | 95 | 100 | 220 | 0 | 0 | 90 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 660 | 38
Forecast for Day | 0 | 0 | 150 | 115 | 200 | 51 | 0 | 0 | 360 | 0 | 0 | 450 | 155 | 100 | 100 | 55 | 0 | 0 | 200 | 0 | 100 | 100 | 150 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 31 | 33 | 33 | 52 | 0 | 90 | 70 | 120 | 0 | 25 | 221 | 0 | 145 | 0 | 0 | 0 |  | 102 | 100 | 90 | 50 | 20 | 10 | 0 | 70 | 0 | 300 | 300 | 225 | 8 | 90 | 5 | 5 | 0 | 43 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 163 | 120 | 25 | 22 | 1.6 | 44 | 30 | 51 | 44 | 110 | 160 | 65 | 86 | 0 | 200 | 18 | 0 | 10 | 341 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 165 | 150 | 400 | 115 | 88 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 72 | 40 |  | 900 | 0 | 410 | 0 | 115 | 220 | 0 | 0 | 0 | 0 | 40 | 0 | 33 | 110 | 0 | 0 | 65 | 0 | 0 | 100 | 43 | 0 | 50 | 52 | 0 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 225 |  | 95 | 0 | 220 | 0 | 0 | 90 | 100 | 113 | 100 | 100 | 0 | 8 | 113 | 660 | 38
Generation at 08:00(Today) | 0 | 0 | 150 | 115 | 200 | 51 | 0 | 0 | 300 | 0 | 0 | 380 | 155 |  | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 31 | 33 | 33 | 12 | 0 | 90 | 70 | 115 | 0 | 0 | 203 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 20 | 15 | 0 | 70 | 0 | 250 | 230 | 177 | 8 | 50 | 0 | 2 | 0 | 43 | 0 | 0 | 0 | 19 | 3 | 33 | 14 | 100 | 125 | 25 | 22 | 1 | 44 | 30 | 47 | 50 | 110 | 157 | 34 | 82 | 0 | 170 | 18 | 0 | 10 | 280 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 6 | 88 | 0 | 1 | 330 | 55 | 8 | 0 | 0 | 40 | 39 | 0 | 0 | 8 | 100 | 0 | 48 | 17 | 0 | 908 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 159 | 0 | 75 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 480 | 38 | 0 | 0
199
| Minimum Generation |  | 7846 | 7:00
| Highest Generation |  | 11427 | 19:30
| Day Peak Generation |  | 9250 | 12:00
| Evening Peak Generation |  | 11427 | 19:30
| HVDC Max Flow |  | 906 | 4:00
| HVDC EvPeak Flow |  | 891 | 19:30
| Load factor L.F |  | 83.27%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-11-04
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-11-03 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9250 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 7657 | MW
Evening Peak Generation : |  | 11427 | MW Hour : | 19:30 | Available Max Generation : |  | 14697 | MW
E.P. Demand (at gen end) : |  | 11427 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 11700 | MW
Maximum Generation : |  | 11427 | MW Hour : | 19:30 | Reserve(Generation end) |  | 2997 | MW
Total Gen. (MKWH) : |  | 228.3587 | System Load Factor : | 83.27% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 91 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-11-04
Actual : | 104.24 | Ft.(MSL) , | Rule curve : | 108.7 | Ft.( MSL )
Gas Consumed : | Total = | 1115.78 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 159035280.554
: |  | Coal : | 77222556 | Oil : | 376559946.65 | Total : | 612817783.204
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4099.3403 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1395.1002 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1250.1591 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1129.6937 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1020.8495 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 823.7922 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 459.2116 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 212.067 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 635.3562 |  |  | 0 | 0%
Total | 0 |  | 11025.5697 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-2 | 10) Sirajganj #1 CCPP STG
2) Baghabari-100 MW
3) Ghorasal Unit-1,2,3
4) Ashuganj unit-3,5
5) Kaptai-2
6) Raozan #2
7) Siddirganj-335 MW
8) Haripur 412 MW
9) Chandpur-163 MW STG
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Tongi-Uttara 3rd phase 132 kV Ckt-1 was under shut down from 08:38 to 15:40 for A/M.
b) Megnaghat-Shyampur 230 kV Ckt-1 was under shut down from 09:21 to 17:01 for A/M.
c) Mymensing-Netrokona 132 kV Ckt-1 was under shut down from 09:10 to 21:26 for D/W.
d) Sherpur 132/33 kV T-2 transformer was under shut down from 09:03 to 16:39 for A/M.
e) Joydevpur 132/33 kV T-2 transformer was under shut down from 08:33 to 14:52 for A/M.
f) Barishal 230/132 kV T-2 transformer was under shut down from 08:21 to 17:16 for A/M.
g) Khulna(S) 230/132 kV T-2 transformer was under shut down from 08:45 to 11:19 for A/M.
h) Khulna(S) 230/132 kV T-1 transformer was under shut down from 11:22 to 16:50 for high temperature of
132 kV Y-phase isolator.
i) Satkhira 132/33 kV T-2 transformer was under shut down from 09:36 to 17:26 for A/M.
j) Shahjibazar 132/33 kV T-4 & T-6 transformers were under shut down from 09:24 to 13:25 for A/M.
k) Cumilla(S) 132/33 kV T-4 transformer was under shut down from 12:56 to 15:06 for A/M.
l) Cumilla(S) 132/33 kV T-3 transformer was under shut down from 10:27 to 12:54 for A/M.
m) Haripur-Siddirganj 230 kV Ckt-2 was under shut down from 09:09 to 15:08 for A/M.
n) Kaliakoir 400/230 kV T-2 transformer was under shut down from 10:34 to 16:29 for A/M.
o) Jamalpur 132/33 kV T-1 transformer was under shut down from 09:01 to 16:30 for A/M.
p) Kishorganj 132/33 kV T-1 transformer was under shut down from 09:20 to 16:39 for A/M.
q) Panchaghar 132/33 kV T-1 transformer was under shut down from 08:09 to 16:31 for A/M.
r) Natore-Bogura 132 kV Ckt-1 was under shut down from 09:22 to 16:39 for A/M.
s) Chandraghona-Madunaghat 132 kV Ckt-2 was under shut down from 07:54 to 14:23 for A/M.
t) Tangail 132/33 kV T-1 transformer was under shut down from 07:54 to 16:44 for A/M.
u) Purbasadipur 132/33 kV T-3 transformer tripped at 12:30 due to 132 kV CB gas pressure low and was
switched on at 18:35.
v) Kodda-RPCL-100 MW 132 kV Ckt was under shut down from 07:54 to 16:40 for D/W.
w) Tongi-Kaliakoir 230 kV Ckt was under shut down from 15:42 to 16:42 for relay test.
x) Hasnabad 132/33 kV T-2 transformer was shut down at 18:29 due to LT CT Y-phase noise problem and
was switched on at 21:44.
y) Chatak 132/33 kV T-1 transformer is under shut down since 06:25(4/11/20) for A/M.
z) Sirajganj #1 GT tripped at 07:33(4/11/20) due to gas booster problem.
aa) Khulna(S) 132/33 kV T-2 transformer is under shut down since 07:32(4/11/20) for A/M.
ab) Kamrangirchar 132/33 kV T-1 transformer is under shut down since 07:50(4/11/20) due to replacing 132
kV R-phase loop.
ac) Tangail 132/33 kV T-1 transformer is under shut down since 07:58(4/11/20) for A/M.
m) Joypurhat 132/33 kV T-1 transformer was under shut down from 08:52 to 14:16 for A/M.
n) Barishal 230/132 kV T-1 transformer was under shut down from 08:32 to 17:00 for A/M.
o) Benapole 132/33 kV T-1 transformer was under shut down from 07:47 to 15:30 for A/M.
p) Khulna(S) 230/132 kV T-1 transformer was under shut down from 08:27 to 14:07 for A/M.
q) Satkhira 132/33 kV T-1 transformer was under shut down from 08:55 to 16:21 for A/M.\r)
r) Ishurdi-Pabna 132 kV Ckt was under shut down from 08:21 to 16:44 for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-11-03 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 150 | 3656000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 115 | 2740500 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 4781036 | Machin problem.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 51 | 1227363 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 312 | 7678000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 350 | 7659750 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 1021440
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 155 | 3595025 | GT-2 under shut down
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 98 | 1422216 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 829778
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 145351
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 420948 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 145 | 3659000 | Frequency control
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 1417920
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under Maintenance
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 94 | 1870704
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel Shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1227600
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1306560
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 643433
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 37 | 448126 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 56 | 1288140 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 788000
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 810900
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 746508
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 285 | 3673308 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 50909 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 21694 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 42326 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 1678900
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 67 | 985968 | D/W by PGCB
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 72 | 1973760 | Engine problem
| Dhaka area Total |  |  |  | 5895 | 2986 | 57811163
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 115 | 2800000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 43228 | Reserve.
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 32265
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1055040
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 158 | 3804407 | Unit-2 under maint
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4918134
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 139 | 3003324
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 298681
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 141480 | High voltage
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 22 | 988800 | Fuel Shortage
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 475392
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 21 | 565440
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 86 | 436800 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 14280
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 162 | 3041018 | Transformer O/L
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1211719
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2327040
| Chattogram area Total |  |  |  | 2266 | 1226 | 25157048
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 70 | 1662360 | Gas Shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 149 | 3425000 | Gas shortage.
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 250 | 6359400 | Gas Shortage
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 230 | 5621000 | Gas Shortage
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 0 | 0 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 2 | 61440 | Gas shortage
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 1023160
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 142 | 2867054 | Engine problem
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 81072 | Reserve.
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 52 | 1190590 | ST Under maint and Gas shortage
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 100 | 349920 | Low demand
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 464076
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 186300
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 152 | 2826240
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 756900
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 349939
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 476810
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 48 | 1633800 | Engine problem
| Cumilla Area Total |  |  |  | 2980 | 1379 | 29552515
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 100 | 2653480 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 497232
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 25 | 594240 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11750
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 192 | 1432800
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 109 | 2656800 | #REF!
| Mymensingh PV 50 MW Solar PP |  | IPP | 50 | 0 | 0 | 235950
| Mymensingh Area Total |  |  |  | 637 | 448 | 8082252
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 44 | 1034000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 721200 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2662772 | ST Under maint
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 157 | 3541000 | FGMO & GT-2 under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 47 | 987600
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 46 | 1185408
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 123000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 63 | 1366272 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 87 | 2025600
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 205 | 4512030
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 402000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 463176
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7235200 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 402 | 9111000
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 246780
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1546 | 35617038
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 891 | 21469090
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 699840
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 9 | 24950 | Low demand
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 2304 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 345 | 8553312 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 118875
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 163200
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 70 | 1726560 | Fuel shortage
107 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1570 | 32758131
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 80 | 510720 | Line O/L
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 33 | 601422
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 96 | 1542991
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 660 | 13060600
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 38 | 903900
| Barisal Area Total |  |  |  | 1054 | 907 | 16619633
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 60 | 1530000 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 135056 | Reserve.
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 33 | 46322 | Reserve.
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 43 | 369270 | Engine problem
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel Shortage
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 39 | 110255
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 148 | 3486400 | STG under rmaint.
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 153 | 4118509 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 157 | 4216609 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 0 | 0 | Under maint.
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 33 | 103914 | Reserve.
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 18 | 425280 | Engine problem
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 10 | 219528
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 238032
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 181920
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 88 | 258424
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 423072
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 1683648
| Rajshahi Area Total |  |  |  | 2183 | 1117 | 17546239
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 149 | 3669100 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 99 | 1514880
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 30659
| Rangpur Area Total |  |  |  | 605 | 248 | 5214639
| Total |  |  |  | 19892 | 11427 | 228358658
| Eastern Grid Total |  |  |  | 13766 | 7585 | 156220016
| Western Grid Total |  |  |  | 6126 | 3842 | 72138642
| National Grid Total |  |  |  | 19892 | 11427 | 228358658
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-11-03
| (a) ENTIRE EASTERN GRID : |  | 7462 | MW | (b) ENTIRE WESTERN GRID : |  | 3293 | MW
| i) Dhaka area |  | 4013 | MW | i) Khulna area |  | 1358 | MW
| ii) Chittagong area |  | 1071 | MW | ii) Rajshahi area |  | 1009 | MW
| iii) Comilla area |  | 1034 | MW | iii) Barisal area |  | 308 | MW
| iv) Mymensingh area |  | 869 | MW | iv) Rangpur area |  | 618 | MW
| v) Sylhet area |  | 475 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 10755 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 120 | 16:00 | Sherpur | 102 | 18:30 | Jhenida | 96 | 18:30
| Munsiganj | 130 | 21:00 | Srimongal | 46 | 18:00 | Bottail | 108 | 18:00
| Sonargaon | 80 | 0:00 | Shahjibazar | 110 | 22:00 | G.K Project | 41 | 18:30
| Shyampur | 194 | 12:00 | Fenchuganj | 44 | 18:30 | Faridpur | 164 | 0.79167
| Bhulta | 184 | 19:00 | Kulawara | 43 | 18:00 | Madaripur | 87 | 0.83333
| Madanganj | 53 | 2:00 | Sylhet | 125 | 18:00 | Sariatpur | 65 | 19:30
| Shitalakhya | 107 | 11:00 | Chatak | 30 | 19:30 | Gopalganj | 80 | 20:00
| Rahim steel | 12 | 1:00 | Sunamganj | 41 | 18:30 | Bagerhat | 89 | 20:00
| Matuail | 87 | 12:00 | Biani Bazar | 55 | 19:00 | Mongla | 36 | 12:00
| Ghorasal | 80 | 18:30 | Comilla (S) | 152 | 18:00 | Satkhira | 104 | 0.8125
| Narsingdi | 158 | 20:00 | Comilla(N) | 99 | 18:30 | Gallamari | 46 | 13:00
| Haripur (SBU) | 110 | 18:30 | Chandpur | 90 | 20:00 | Magura | 44 | 0.75
| Ullon | 66 | 14:00 | Feni | 103 | 18:00 | Norail | 39 | 18:30
| Hasnabad | 194 | 22:00 | Chowmuhani | 154 | 19:30 | Chuadanga | 75 | 18:00
| Magbazar | 103 | 14:00 | Ashuganj | 54 | 0:00 | Barisal(N) | 39 | 0.8125
| Maniknagar | 98 | 12:00 | Daudkandi | 132 | 20:00 | Barisal (S) | 90 | 0.83333
| Bangabhaban | 34 | 11:00 | B.Baria | 146 | 21:00 | Patuakhali | 100 | 0.875
| Narinda | 88 | 18:00 | Ramganj | 92 | 19:30 | Bhandaria | 49 | 0.8125
| Dhanmondi | 129 | 13:00 | Chaddagram | 32 | 19:00 | Borhan Uddin | 36 | 21:00
| Lalbag | 85 | 13:00 | PHP | 10 | 12:00 | Ishurdi | 50 | 18:00
| Madartek | 64 | 18:30 | Madunaghat | 55 | 14:00 | Ruppur Paromanobik | 2 | 18:00
| Dhaka University |  |  | Hathazari | 95 | 0.75 | Natore | 102 | 18:30
| Fatullah | 41 | 0.41667 | Khulshi | 198 | 0.41667 | Bogra | 152 | 18:30
| Mirpur | 103 | 18:00 | Halishahar | 125 | 0.625 | Noagaon | 94 | 19:30
| Kalyanpur | 87 | 18:00 | Baraulia | 122 | 0 | Rajshahi | 111 | 18:30
| Gulshan | 124 | 10:00 | Sikalbaha | 25 | 0.75 | Rajshahi New | 13 | 18:00
| Uttara | 88 | 18:00 | Dohazari | 70 | 0.75 | C.Nawabganj | 57 | 19:00
| Uttara New | 33 | 18:00 | Cox'sbazar | 91 | 0.77083 | Amnura | 34 | 18:00
| Kamrangirchar | 88 | 12:00 | Chandraghona | 26 | 0.75 | Pabna | 105 | 18:30
| Savar | 137 | 18:00 | Kaptai | 4 | 0.75 | Shahjadpur | 92 | 18:00
| Bhasantec | 146 | 18:00 | A. Khaer Stl. | 0 | 0.041667 | Serajganj | 85 | 19:00
| Agargaon | 67 | 13:00 | Bakulia | 92 | 0.625 | Niyamatpur | 41 | 18:30
| Satmosjid | 91 | 18:00 | Julda | 21 | 0.5 | Joypurhat | 48 | 18:30
| Tongi | 95 | 0.54167 | TK chemical | 23.8 | 0.79167 | Sherpur(Bogura) | 40 | 19:00
| Kabirpur | 246 | 18:30 | Modern Steel | 16 | 0.33333 | Mohastangor | 36 | 20:00
| Basundhara | 136 | 13:00 | Shahmirpur | 21 | 0.75 | Rangpur | 122 | 19:00
| Manikganj | 72 | 21:00 | Khagrachhari | 22 | 0.041667 | Lalmonirhat | 49 | 19:00
| Joydevpur | 148 | 18:30 | Matarbari | 34 | 0.8125 | Saidpur | 88 | 18:00
| New Tongi | 100 | 18:00 | Baroiar Hat | 26 | 0.75 | Purbasadipur | 81 | 18:30
| Kodda | 219 | 18:30 | Rangamati | 12 | 0.75 | Thakurgaon | 62 | 18:30
| Dhamrai | 90 | 18:30 | Abul Khair 230 | 153 | 0.70833 | Palashbari | 100 | 19:30
| Rajendrapur | 98 | 18:30 | BSRM | 150 | 0.041667 | Barapukuria | 40 | 20:00
| Valuka | 94 | 18:30 | GPH Ispat | 87 | 0.041667 | Panchagar | 45 | 18:00
| Tangail | 182 | 18:30 | Goalpara | 26 | 0.91667 | Joldhaka | 20 | 18:00
| Mymensing | 202 | 18:00 | Central s/s | 84 | 19:30 | Kurigram | 46 | 18:00
| Kishorganj | 124 | 22:00 | Noapara | 54 | 18:30
| Netrokona | 97 | 20:00 | Jessore | 108 | 18:00
| Jamalpur | 112 | 19:00 | Benapol | 48 | 19:30
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-11-03 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 409 | 8:00 | 401 | 10:00 | Kaliakoir | 396 | 0.33333 | 385 | 0.66667
| Bheramara | 403 | 8:00 | 397 | 18:00 | Bhulta | 376 | 0.33333 | 363 | 0.66667
| Ashuganj(N) | 383 | 8:00 | 372 | 12:00 | Gopalganj | 412 | 0.33333 | 386 | 0.875
| Payra | 420 | 1:00 | 404 | 21:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 228 | 14:00 | Comilla (N) | 233 | 8:00 | 227 | 12:00
| Ishurdi | 237 | 6:00 | 224 | 12:00 | Hathazari | 225 | 9:00 | 219 | 16:00
| Ashuganj | 235 | 1:00 | 228 | 15:00 | Megnaghat | 227 | 1:00 | 220 | 10:00
| Serajganj | 230 | 2:00 | 225 | 12:00 | Fenchuganj | 242 | 1:00 | 238 | 15:00
| Baghabari | 240 | 5:00 | 237 | 11:00 | Siddhirganj | 225 | 1:00 | 217 | 12:00
| Barapukuria | 229 | 17:00 | 225 | 18:00 | Maniknagar | 223 | 1:00 | 215 | 12:00
| Bogra | 228 | 20:00 | 221 | 13:00 | Agargaon | 220 | 16:00 | 210 | 12:00
| Rajshahi | 226 | 19:30 | 216 | 13:00 | Barisal | 245 | 8:00 | 236 | 1:00
| Khulna South | 230 | 6:00 | 211 | 18:00 | AKSML | 222 | 2:00 | 216 | 13:00
| Rampura | 223 | 1:00 | 216 | 12:00 | BSRM | 223 | 19:30 | 216 | 15:00
| Haripur | 225 | 1:00 | 215 | 16:00 | Bibiyana | 244 | 1:00 | 236 | 19:00
| Hasnabad | 220 | 1:00 | 210 | 12:00 | Bhulta | 225 | 19:00 | 217 | 17:00
| Shyampur | 223 | 1:00 | 220 | 16:00 | Ashuganj (S) | 232 | 1:00 | 224 | 16:00
| Aminbazar | 223 | 1:00 | 212 | 11:00 | Kaliakoir | 222 | 1:00 | 215 | 20:00
| Tongi | 220 | 1:00 | 210 | 11:00 | GPH | 220 | 1:00 | 217 | 4:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 135 | 22:00 | 130 | 10:00 | Hathazari | 133 | 0.29167 | 131 | 0.20833
| Munsiganj | 136 | 1:00 | 129 | 6:00 | Khulshi | 132 | 0.77083 | 129 | 0.58333
| Sonargaon | 135 | 20:00 | 130 | 5:00 | Halishahar | 134 | 0.77083 | 129 | 0.58333
| Shyampur | 133 | 21:00 | 127 | 12:00 | Baraulia | 135 | 0.77083 | 130 | 0.16667
| Bhulta | 128 | 1:00 | 124 | 12:00 | Sikalbaha | 136 | 0.77083 | 132 | 0.25
| Madanganj | 136 | 22:00 | 130 | 6:00 | Dohazari | 133 | 0.79167 | 127 | 0.083333
| Shitalakhya | 142 | 18:00 | 131 | 7:00 | Cox'sbazar | 126 | 0.33333 | 118 | 0.91667
| Rahim steal | 134 | 1:00 | 130 | 10:00 | Chandraghona | 135 | 0.33333 | 132 | 0.29167
| Matuail | 135 | 22:00 | 130 | 10:00 | Kaptai | 134 | 0.041667 | 132 | 0.20833
| Ghorasal | 137 | 1:00 | 134 | 10:00 | A. Khaer Stl. | 133 | 0.83333 | 129 | 0.58333
| Narsinghdi | 131 | 7:00 | 125 | 11:00 | Bakulia | 133 | 0.77083 | 130 | 0.45833
| Haripur (SBU) | 135 | 1:00 | 130 | 11:00 | Julda | 135 | 0.75 | 131 | 0.66667
| Ullon | 132 | 1:00 | 124 | 10:00 | TK Chemical | 134 | 0.375 | 131 | 0.16667
| Hasnabad | 137 | 18:00 | 128 | 15:00 | Modern Steel | 133 | 0.33333 | 130 | 0.625
| Magbazar | 132 | 3:00 | 122 | 19:30 | Shahmirpur | 135 | 0.75 | 130 | 0.58333
| Maniknagar | 134 | 8:00 | 128 | 11:00 | Khagrachhari | 133 | 0.041667 | 131 | 0.54167
| Bangabhaban | 134 | 8:00 | 128 | 11:00 | Matarbari | 130 | 0.29167 | 121 | 0.91667
| Narinda | 134 | 8:00 | 128 | 11:00 | Baroiar Hat | 134 | 0.33333 | 128 | 0.58333
| Dhanmondi | 132 | 1:00 | 124 | 10:00 | Rangamati | 133 | 0.041667 | 131 | 0.625
| Lalbag | 134 | 1:00 | 125 | 12:00 | Goalpara S/S | 139 | 8:00 | 130 | 12:00
| Madartek | 131 | 8:00 | 123 | 12:00 | Khulna Central S/S | 137 | 9:00 | 128 | 0.58333
| Dhaka University |  |  |  |  | Noapara | 137 | 5:00 | 126 | 0.5
| Fatuiiah | 133 | 1:00 | 128 | 11:00 | Jessore | 134 | 6:00 | 122 | 0.54167
| Mirpur | 135 | 1:00 | 126 | 12:00 | Benapol | 134 | 0.25 | 117 | 0.75
| Kalyanpur | 134 | 1:00 | 129 | 12:00 | Jhenida | 132 | 5:00 | 116 | 0.75
| Gulshan | 131 | 1:00 | 123 | 12:00 | Bottail | 135 | 0.25 | 124 | 0.75
| Uttara | 132 | 1:00 | 127 | 13:00 | G.K Project | 140 | 0.33333 | 134 | 0.75
| Uttara New | 135 | 20:00 | 126 | 12:00 | Faridpur | 137 | 0.33333 | 125 | 0.75
| Kamrangirchar | 133 | 1:00 | 126 | 12:00 | Madaripur | 140 | 0.20833 | 128 | 0.75
| Savar | 134 | 1:00 | 127 | 12:00 | Shariyatpur S/S | 138 | 5:00 | 128 | 0.77083
| Bhasantec | 133 | 1:00 | 126 | 12:00 | Gopalganj | 141 | 0.33333 | 125 | 0.77083
| Agargaon | 134 | 1:00 | 127 | 12:00 | Bagerhat | 133 | 8:00 | 116 | 0.75
| Satmosjid | 134 |  | 127 | 13:00 | Mongla | 130 | 20:00 | 113 | 0.75
| Tongi | 137 | 21:00 | 130 | 15:00 | Satkhira | 135 | 7:00 | 122 | 18:00
| Kabirpur | 132 | 5:00 | 125 | 18:00 | Gallamari | 139 | 0.29167 | 128 | 0.75
| Basundhara | 131 | 8:00 | 123 | 12:00 | Magura | 130 | 7:00 | 115 | 0.75
| Manikganj | 136 | 21:00 | 127 | 12:00 | Norail | 129 | 0.29167 | 113 | 0.75
| Joydevpur | 140 | 18:00 | 130 | 11:00 | Chuadanga | 128 | 7:00 | 109 | 0.75
| New Tongi | 136 | 21:00 | 128 | 16:00 | Barisal(N) | 138 | 8:00 | 131 | 21:00
| Kodda | 137 | 21:00 | 124 | 12:00 | Barisal (S) | 137 | 0.33333 | 130 | 0.5
| Dhamrai | 133 | 8:00 | 126 | 18:00 | Patuakhali(S) | 135 | 0.33333 | 125 | 0.875
| Rajendrapur | 135 | 21:00 | 123 | 12:00 | Bhandaria | 135 | 0.29167 | 122 | 0.041667
| Valuka | 126 | 8:00 | 114 | 18:00 | Ishurdi | 137 | 6:00 | 132 | 18:00
| Tangail | 132 | 5:00 | 122 | 18:30 | Ruppur Paromanobik | 138 | 8:00 | 131 | 18:00
| Mymensing | 129 | 8:00 | 116 | 18:00 | Natore | 137 | 19:30 | 132 | 13:00
| Kishorganj | 128 | 8:00 | 119 | 18:00 | Bogra | 137 | 19:30 | 132 | 9:00
| Netrokona | 126 | 7:00 | 111 | 19:30 | Noagaon | 132 | 19:30 | 127 | 13:00
| Jamalpur | 140 | 17:00 | 126 | 1:00 | Rajshahi | 137 | 19:30 | 131 | 13:00
| Sherpur | 138 | 17:00 | 122 | 1:00 | Rajshahi New | 139 | 17:00 | 132 | 14:00
| Srimongal | 137 | 8:00 | 132 | 9:00 | C.Nawabganj | 138 | 19:30 | 130 | 13:00
| Shahjibazar | 136 | 8:00 | 129 | 19:30 | Amnura | 140 | 19:00 | 130 | 12:00
| Fenchuganj | 137 | 6:00 | 133 | 18:30 | Pabna | 135 | 6:00 | 130 | 18:00
| Khulawara | 137 | 8:00 | 133 | 18:00 | Shahjadpur | 137 | 6:00 | 134 | 16:00
| Sylhet | 135 | 7:00 | 131 | 18:00 | Serajganj | 134 | 7:00 | 132 | 19:00
| Chatak | 134 | 8:00 | 128 | 18:00 | Niyamatpur | 132 | 1:00 | 126 | 16:00
| Sunamganj | 133 | 8:00 | 127 | 18:00 | Joypurhat | 135 | 18:30 | 126 | 13:00
| Biani Bazar | 134 | 8:00 | 129 | 15:00 | Sherpur(Bogura) | 136 | 18:30 | 132 | 16:00
| Comilla(s) | 128 | 5:00 | 122 | 15:00 | Mohastangor | 136 | 20:00 | 131 | 13:00
| Comilla(n) | 138 | 8:00 | 133 | 11:00 | Rangpur | 128 | 17:00 | 122 | 18:00
| Chandpur | 136 | 18:00 | 128 | 20:00 | Lalmonirhat | 130 | 17:00 | 123 | 18:00
| Feni | 133 | 8:00 | 129 | 12:00 | Saidpur | 128 | 9:00 | 122 | 18:00
| Chowmuhani | 134 | 8:00 | 125 | 14:00 | Purbasadipur | 128 | 5:00 | 118 | 18:00
| Ashuganj | 135 | 8:00 | 131 | 18:00 | Thakurgaon | 126 | 6:00 | 117 | 18:00
| Daudkandi | 133 | 18:00 | 128 | 12:00 | Palashbari | 131 | 17:00 | 126 | 18:00
| B.Baria | 130 | 7:00 | 125 | 21:00 | Barapukuria | 129 | 17:00 | 125 | 18:00
| Ramganj | 132 | 8:00 | 121 | 23:00 | Panchagar | 124 | 6:00 | 116 | 18:00
| Chaddagram | 133 | 18:00 | 130 | 11:00 | Joldhaka | 127 | 5:00 | 118 | 18:00
| PHP | 134 | 8:00 | 127 | 15:00 | Kurigram | 127 | 17:00 | 119 | 18:00
| Madanhat | 136 | 18:00 | 132 | 13:00

## L-Curve
Date | 2020-11-03
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 377 | 6783 | 3126 | 9909 |  |  |  | QF-LDC-11
0:30 | 234 | 6692 | 3023.5 | 9715.5 | Date: | 2020-11-03
1:00 | 91 | 6601 | 2921 | 9522
1:30 | 118 | 6446.5 | 2916 | 9362.5
2:00 | 145 | 6292 | 2911 | 9203
2:30 | 143.5 | 6197 | 2840 | 9037 | [5 empty] | Gen. at Eve. Peak | 11427 | 11427 MW (19:30 )
3:00 | 142 | 6102 | 2769 | 8871 | [6 empty] | 19:30
3:30 | 178.5 | 6016.5 | 2746 | 8762.5 | [5 empty] | Gen. at Day Peak | 9250 | 9250 MW (12:00 )
4:00 | 215 | 5931 | 2723 | 8654 | [6 empty] | 12:00
4:30 | 241 | 5854.5 | 2717.5 | 8572 | [5 empty] | Highest Generation | 11427
5:00 | 267 | 5778 | 2712 | 8490 | [6 empty] | 19:30
5:30 | 330.5 | 5618 | 2693 | 8311
6:00 | 394 | 5458 | 2674 | 8132
6:30 | 367 | 5327.5 | 2661.5 | 7989
7:00 | 340 | 5197 | 2649 | 7846
7:30 | 260 | 5308.5 | 2593.5 | 7902
8:00 | 180 | 5420 | 2538 | 7958
8:30 | 263.5 | 5667 | 2512 | 8179
9:00 | 347 | 5914 | 2486 | 8400
9:30 | 349.5 | 6005 | 2519.5 | 8524.5
10:00 | 352 | 6096 | 2553 | 8649
10:30 | 399.5 | 6216.5 | 2630.5 | 8847
11:00 | 447 | 6337 | 2708 | 9045
11:30 | 415 | 6400.5 | 2747 | 9147.5
12:00 | 383 | 6464 | 2786 | 9250
12:30 | 350 | 6516.5 | 2838.5 | 9355
13:00 | 317 | 6569 | 2891 | 9460
13:30 | 351 | 6539 | 2880 | 9419
14:00 | 385 | 6509 | 2869 | 9378
14:30 | 444 | 6565 | 2920 | 9485
15:00 | 503 | 6621 | 2971 | 9592
15:30 | 514 | 6472.5 | 2952 | 9424.5
16:00 | 525 | 6324 | 2933 | 9257
16:30 | 501 | 6277.5 | 2896.5 | 9174
17:00 | 477 | 6231 | 2860 | 9091
17:30 | 315.5 | 6910 | 3189.5 | 10099.5
18:00 | 154 | 7589 | 3519 | 11108
18:30 | 214 | 7579.5 | 3641.5 | 11221
19:00 | 274 | 7570 | 3764 | 11334
19:30 | 317 | 7585 | 3842 | 11427
20:00 | 268 | 7457 | 3741 | 11198 |  |  |  | Executive Engineer
20:30 | 184.5 | 7502.5 | 3586 | 11088.5 |  |  |  | Network Operation Division
21:00 | 101 | 7548 | 3431 | 10979
21:30 | 126.5 | 7456 | 3344.5 | 10800.5
22:00 | 152 | 7364 | 3258 | 10622 |  |  |  |  | Page 6 of 7
22:30 | 242.5 | 7187.5 | 3236 | 10423.5
23:00 | 333 | 7011 | 3214 | 10225
23:30 | 355 | 6897 | 3170 | 10067
24:00 | 377 | 6783 | 3126 | 9909
11427 MW (19:30 )
9250 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-11-03 |  | Energy | 228358658
[10 empty] | 2020-11-03 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4043 | 891 | 1604 | 2482 | 810 | 163 | 50 | 0 | 138
0:30 | 4005 | 898 | 1604 | 2230 | 755 | 162.5 | 66 | 0 | 131 | Date: | 2020-11-03
1:00 | 3967 | 905 | 1604 | 1978 | 700 | 162 | 82 | 0 | 124
1:30 | 3958.5 | 905 | 1618.5 | 1815.5 | 700 | 161 | 82 | 0 | 122 | [7 empty] | Total Energy | 228.3587 | Total Energy Gen 228.359 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 228.359 MKWHr
2:00 | 3950 | 905 | 1633 | 1653 | 700 | 160 | 82 | 0 | 120 | [7 empty] | Energy not Served | 0
2:30 | 3950.5 | 905 | 1640.5 | 1497 | 700 | 159 | 65 | 0 | 120 | [7 empty] | Energy Requirement | 228.3587
3:00 | 3951 | 905 | 1648 | 1341 | 700 | 158 | 48 | 0 | 120
3:30 | 3932.5 | 905.5 | 1646 | 1255.5 | 700 | 157 | 48 | 0 | 118 | [6 empty] | Shortage
4:00 | 3914 | 906 | 1644 | 1170 | 700 | 156 | 48 | 0 | 116
4:30 | 3916 | 906 | 1645 | 1104 | 700 | 155 | 32 | 0 | 114
5:00 | 3918 | 906 | 1646 | 1038 | 700 | 154 | 16 | 0 | 112
5:30 | 3931 | 905.5 | 1649.5 | 866 | 685 | 155 | 8 | 0 | 111
6:00 | 3944 | 905 | 1653 | 694 | 670 | 156 | 0 | 0 | 110
6:30 | 3926 | 905 | 1617.5 | 605 | 670 | 157 | 0 | 0 | 104 |  |  |  |  | Coal
7:00 | 3908 | 905 | 1582 | 516 | 670 | 158 | 0 | 0 | 98
7:30 | 3843.5 | 898 | 1540.5 | 727 | 630 | 158 | 0 | 0 | 94 |  |  |  | Oil |  |  |  | ,
8:00 | 3779 | 891 | 1499 | 938 | 590 | 158 | 0 | 0 | 90
8:30 | 3711.5 | 890.5 | 1479.5 | 1237 | 590 | 158.5 | 0 | 0 | 89
9:00 | 3644 | 890 | 1460 | 1536 | 590 | 159 | 0 | 0 | 88
9:30 | 3758 | 890 | 1443.5 | 1559.5 | 590 | 159.5 | 0 | 0 | 91
10:00 | 3872 | 890 | 1427 | 1583 | 590 | 160 | 0 | 0 | 94
10:30 | 3940.5 | 890 | 1460.5 | 1661.5 | 605 | 160 | 0 | 0 | 94
11:00 | 4009 | 890 | 1494 | 1740 | 620 | 160 | 0 | 0 | 94
11:30 | 4001 | 890.5 | 1502.5 | 1832 | 620 | 160 | 0 | 0 | 98
12:00 | 3993 | 891 | 1511 | 1924 | 620 | 160 | 0 | 0 | 102
12:30 | 4023 | 890.5 | 1533.5 | 1967 | 620 | 160 | 8 | 0 | 102
13:00 | 4053 | 890 | 1556 | 2010 | 620 | 160 | 16 | 0 | 102
13:30 | 4053 | 890 | 1556 | 2010 | 620 | 160 | 16 | 0 | 102
14:00 | 4053 | 890 | 1556 | 2010 | 620 | 160 | 16 | 0 | 102
14:30 | 4067.5 | 890 | 1555.5 | 2051.5 | 629.5 | 159.5 | 16 | 0 | 111
15:00 | 4082 | 890 | 1555 | 2093 | 639 | 159 | 16 | 0 | 120
15:30 | 4053 | 890.5 | 1520.5 | 2001.5 | 638.5 | 159 | 16 | 0 | 118
16:00 | 4024 | 891 | 1486 | 1910 | 638 | 159 | 16 | 0 | 116
16:30 | 3880.5 | 890.5 | 1494.5 | 1919.5 | 638.5 | 158 | 66.5 | 0 | 117
17:00 | 3737 | 890 | 1503 | 1929 | 639 | 157 | 117 | 0 | 118
17:30 | 3841.5 | 889.5 | 1530 | 2540 | 701.5 | 157 | 304.5 | 0 | 135
18:00 | 3946 | 889 | 1557 | 3151 | 764 | 157 | 492 | 0 | 152
18:30 | 3982 | 890 | 1548.5 | 3217.5 | 786.5 | 157.5 | 490 | 0 | 149
19:00 | 4018 | 891 | 1540 | 3284 | 809 | 158 | 488 | 0 | 146
19:30 | 4003 | 891 | 1582 | 3345 | 809 | 158 | 487 | 0 | 152
20:00 | 3973 | 891 | 1576 | 3194 | 809 | 158 | 447 | 0 | 150
20:30 | 3983 | 891 | 1580.5 | 3197 | 809.5 | 159 | 320.5 | 0 | 148
21:00 | 3993 | 891 | 1585 | 3200 | 810 | 160 | 194 | 0 | 146
21:30 | 3992.5 | 890.5 | 1572 | 3075.5 | 810 | 160.5 | 154.5 | 0 | 145
22:00 | 3992 | 890 | 1559 | 2951 | 810 | 161 | 115 | 0 | 144
22:30 | 4030 | 890.5 | 1565.5 | 2716.5 | 810 | 161.5 | 107.5 | 0 | 142
23:00 | 4068 | 891 | 1572 | 2482 | 810 | 162 | 100 | 0 | 140
23:30 | 4055.5 | 891 | 1588 | 2482 | 810 | 162.5 | 75 | 0 | 139 | Max Temp. in Dhaka |  | 31.6° C
24:00 | 4043 | 891 | 1604 | 2482 | 810 | 163 | 50 | 0 | 138
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 228.359 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 228.359 MKWHr
Note on W13: Author:

## Generation
g | 2020-11-03
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 92 | 90 | 88 | 86 | 84 | 86 | 88 | 88 | 89 | 90 | 90 | 90 | 90 | 92 | 89 | 89 | 87 | 87 |  | 88 | 88 | 88 | 90 | 91 | 92 | 93 | 2116407
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1688000
3 | Chattogram TPP-1 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 22 | [8 empty] | 43228
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 5 | 2 | 1 | 0 |  |  |  | 8 | 6 | 6 | 0 | [9 empty] | 32265
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 204 | 204 | 204 | 204 | 204 | 226 | 204 | 218 | 232 | 206 | 204 | 204 | 215 | 210 | 205 | 204 | 204 |  | 204 | 204 | 203 | 203 | 203 | 213 | 210 | 4918134
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 139 | 139 | 140 | 140 | 142 | 140 | 100 | 100 | 100 | 100 | 139 | 139 | 139 | 106 | 107 | 105 | 70 | 139 |  | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 3003324
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 22 | 85 |  | 85 | 85 | 68 | 34 |  |  |  | 298681
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [17 empty] | 50 |  | 25 | [6 empty] | 81072
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 155 | 156 | 156 | 156 | 155 | 155 | 123 | 110 | 75 | 140 | 150 | 170 | 180 | 155 | 185 | 150 | 70 | 145 |  | 145 | 145 | 113 | 120 | 120 | 120 | 120 | 3659000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 145 | 0 | [5 empty] | 37 | 145 | 145 | 145 | 170 | 195 | 195 | 195 | 195 | 215 | 265 |  | 275 | 285 | 286 | 286 | 286 | 130 | 80 | 3673308
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 147 | 160 | 160 | 160 | 130 | 130 | 160 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3656000
23 | Ghorasal TPP Unit-5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2740500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4781036
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1662360
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | Ashuganj 225 MW CCPP | 118 | 119 | 125 | 126 | 135 | 136 | 130 | 131 | 131 | 126 | 152 | 160 | 157 | 151 | 147 | 142 | 131 | 136 |  | 136 | 149 | 154 | 155 | 155 | 157 | 157 | 3425000
34 | Ashuganj 450 MW CCPP(South) | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 5621000
| Ashuganj 450 MW CCPP(North) | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6359400
35 | Ashuganj 55 MW PP (Precision) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 61440
36 | Chandpur 150 MW CCPP | 50 | 50 | 51 | 52 | 52 | 50 | 51 | 50 | 51 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 51 | 52 | 51 | 50 | 50 | 50 | 50 | 1190590
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 380 | 380 | 390 | 390 | 400 | 400 | 390 | 380 | 380 | 380 | 380 | 380 | 360 | 360 | 360 | 330 | 330 | 360 |  | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 7659750
41 | Haripur 360MW CCPP(HPL) | 356 | 356 | 356 | 356 | 356 | 357 | 357 | 300 | 282 | 282 | 323 | 323 | 323 | 303 | 322 | 283 | 283 | 312 |  | 312 | 312 | 310 | 310 | 306 | 320 | 330 | 7678000
42 | RPCL 210MW CCPP | 122 | 142 | 142 | 142 | 142 | 147 | 146 | 126 | 101 | 101 | 99 | 97 | 97 | 97 | 98 | 98 | 98 | 98 |  | 101 | 100 | 100 | 100 | 102 | 122 | 122 | 2653480
43 | Mymensingh PV 50 MW Solar PP | [6 empty] | 3 | 8 | 27 | 26 | 28 | 41 | 45 | 35 | 26 | 9 | 1 | [9 empty] | 235950
44 | Fenchugonj CCPP Phase-1 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 43 | 44 | 44 |  | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 1034000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 721200
46 | Shajibazar 330 MW CCPP | 158 | 159 | 159 | 158 | 158 | 158 | 159 | 157 | 157 | 160 | 160 | 159 | 158 | 158 | 159 | 158 | 158 | 157 |  | 158 | 157 | 157 | 158 | 158 | 159 | 157 | 3541000
47 | Shahjibazar GTPP Unit- 8 & 9 | 54 | 54 | 54 | 54 | 54 | 66 | 65 | 40 | 40 | 40 | 65 | 63 | 60 | 40 | 62 | 63 | 40 | 65 |  | 63 | 63 | 64 | 64 | 63 | 65 | 65 | 1366272
48 | Shahjibazar 86MW PP (Shahjibazar) | 87 | 87 | 87 | 87 | 87 | 87 | 30 | 87 | 87 | 87 | 87 | 87 | 86 | 86 | 84 | 86 | 86 | 86 |  | 86 | 87 | 87 | 87 | 84 | 84 | 84 | 2025600
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 185 | 151 | 151 | 151 | 151 | 151 | 151 | 191 | 205 | 205 | 206 | 192 | 192 | 203 | 205 | 205 | 191 | 205 |  | 205 | 205 | 204 | 204 | 204 | 205 | 205 | 4512030
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 17 | 18 | 17 | 402000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 246780
54 | Hobiganj 11MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  |  | 5 | 5 | 5 |  |  | 5 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 123000
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 34 |  | 47 | 47 | 47 | 49 | 50 | 50 | 50 | 987600
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 24 | 24 | 24 | 463176
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 300 | 305 | 300 | 295 | 300 | 300 | 285 | 270 | 270 | 270 | 275 | 305 | 270 | 305 | 300 | 310 | 290 |  | 260 | 300 | 290 | 290 | 280 | 280 | 300 | 7235200
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | [10 empty] | 10 | 35 | 35 | 35 | 37 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 17 | 17 | 448126
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 20 | 20 | 18 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 475392
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 420948
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 22 | 22 | 22 | 22 | 22 | 15 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 497232
63 | Impoprt (Tripura) | 124 | 120 | 120 | 116 | 112 | 110 | 98 | 90 | 88 | 94 | 94 | 102 | 102 | 106 | 120 | 116 | 118 | 152 |  | 146 | 152 | 150 | 146 | 144 | 140 | 138 | 2826240
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 40 | 12 | 6 | 4 | 4 | 4 | 10 | 4 | 3 | 4 | 12 | 11 |  | 20 | 21 | 27 | 32 | 40 | 42 | 42 | 565440
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 464076
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 |  | 8 | 8 | 186300
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 756900
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 15 | 15 | 15 | 15 | 15 | 15 | 18 | 18 | 18 | 18 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 476810
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 31 | 31 | 31 | 31 | 30 | 30 | 30 | 30 | 30 | 30 | 27 | 29 | 29 | 29 | 29 | 20 |  | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 688140
71 | Maona 33 MW PP(Summit) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 788000
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 17 | 17 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 810900
73 | Ghorashal 108MW PP (Regent) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 52 | 52 | 52 | 52 | 52 | 52 | 53 | 53 | 53 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1227363
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | 113 | 112 | 65 | 65 | 26 | 8 | 8 | 35 | 85 | 85 | 80 | 38 | 46 | 47 | 47 | 47 | 47 | 48 |  | 48 | 48 | 61 | 105 | 106 | 105 | 105 | 1633800
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 50 | 24 | 0 |  |  |  |  | 2 | 14 | 24 | 60 | 100 | 100 | 100 | 100 | 70 | 60 | 80 |  | 100 | 100 | 100 | 100 | 100 | 88 | 50 | 1417920
78 | Gazipur 52 MW PP | 25 | 0 | [5 empty] | 10 | 46 | 51 | 51 | 51 | 51 | 25 | 25 | 25 | 25 | 40 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 746508
79 | Kodda 150MW PP | 82 | 82 | 48 | 48 | 16 | 0 | [6 empty] | 16 | 16 | 16 | 16 | 48 | 150 |  | 150 | 150 | 150 | 150 | 115 | 100 | 50 | 1306560
80 | Jamalpur 95 MW PP(Powerpac) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 594240
81 | Jangalia 52 MW PP (Lakdanavi) | [7 empty] | 1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 32 |  | 43 | 52 | 45 | 52 | 25 | 25 | 8 | 349939
| Gazipur 100 MW PP | 86 | 86 | 86 | 86 | 70 | 35 | 35 | [10 empty] | 2 |  | 55 | 67 | 67 | 67 | 86 | 86 | 86 | 985968
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 1 | 1 | 1 | 3 | 2 | 2 | 1 | 3 | 1 | [10 empty] | 14280
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 17 | 26 | 39 | 54 | 54 | 40 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1211719
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | 30 | 0 | [6 empty] | 20 | 50 | 63 | 72 | 98 | 98 | 98 | 64 | 64 | 76 |  | 98 | 98 | 98 | 98 | 98 | 80 | 70 | 1422216
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [17 empty] | 72 |  | 50 | [6 empty] | 145351
86 | Meghnaghat CCPP(Summit) | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 120 | 120 | 120 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 |  | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 3595025
87 | Meghnaghat 100 MW(IEL) | 66 | 0 | [5 empty] | 2 | 15 | 16 | 20 | 41 | 41 | 41 | 41 | 41 | 41 | 85 |  | 100 | 100 | 100 | 100 | 100 | 72 | 50 | 1021440
| Meghnaghat 104 MW PP (OPCL) | 90 | 90 | 90 | 90 | 90 | 90 | 42 | 65 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 78 | 72 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 1973760
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [9 empty] | 8 | 8 | 8 | 8 | 8 | 8 |  |  | 40 |  | 10 | 10 | 10 |  |  |  |  | 141480
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 47 | 50 | 50 | 50 | 50 | 50 | 50 | 46 |  | 46 | 46 | 46 | 50 | 50 | 50 | 50 | 1185408
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1023160
94 | Gagnagar 102 MW PP (Digital Power) | 102 | 102 | 68 | 32 | 32 | 7 | 7 | 50 | 64 | 64 | 75 | 102 | 102 | 102 | 94 | 94 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 102 | 102 | 1870704
95 | Patenga 50MW PP (Baraka) | 50 | 42 | 30 | 30 | 30 | 22 | 12 | 22 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1055040
96 | Chattogram 108 MW PP (ECPV) | [17 empty] | 97 |  | 88 | 86 | 86 | 86 | 15 | 12 | 12 | 436800
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | 15 | 14 | 14 | 0 |  |  |  | 12 | 55 | 55 | 55 | 40 | 40 | 45 | 55 | 15 | 15 | 31 |  | 55 | 55 | 55 | 55 | 55 | 30 | 30 | 829778
100 | Manikganj 55 MW PP (Northern) | 55 | 35 | 0 |  |  |  |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 643433
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2662772
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [10 empty] | 11750
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 17 | 17 | 45 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1227600
104 | Keranigonj 300 MW PP (APR) | [17 empty] | 60 | [8 empty] | 50909
105 | Bramhangoan 100 MW PP (Aggreko) | [17 empty] | 25 | [8 empty] | 21694
106 | Mymensingh 200 MW PP (United) | 7 | 7 | 7 | 0 |  |  |  | 7 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 60 | 136 |  | 192 | 192 | 196 | 200 | 200 | 160 | 120 | 1432800
112 | Aurahati 100MW PP (Aggreko) | [17 empty] | 48 | [8 empty] | 42326
114 | Kodda 149 MW PP Unit-1 (Summit) | [6 empty] | 10 | 42 | 102 | 94 | 81 | 81 | 90 | 100 | 110 | 107 | 125 | 149 |  | 149 | 149 | 149 | 149 | 102 |  |  | 1678900
115 | Juldah 100 MW PP Unit-3 (Acorn) | 50 | 50 | 50 | 50 | 50 | 50 | 10 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 100 | 100 | 100 | 100 | 988800
116 | Chandpur 200MW (Desh energy) | [16 empty] | 2 | 114 |  | 100 | 100 | 17 |  |  |  |  | 349920
117 | Ashuganj 150MW PP (Midland) | 142 | 142 | 142 | 100 | 60 | 10 | 10 | 26 | 100 | 100 | 105 | 127 | 130 | 140 | 143 | 143 | 142 | 142 |  | 142 | 142 | 140 | 142 | 142 | 142 | 142 | 2867054
118 | Bibiyana-III 400 MW CCPP | 376 | 376 | 352 | 327 | 329 | 329 | 329 | 330 | 330 | 401 | 402 | 404 | 403 | 415 | 404 | 404 | 352 | 401 |  | 401 | 402 | 402 | 402 | 415 | 416 | 412 | 9111000
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 115 | 85 | 85 | 100 | 108 | 108 | 108 | 108 | 108 | 115 | 115 | 115 | 115 | 115 |  | 109 | 109 | 109 | 109 | 115 | 115 | 115 | 2656800
| Anwara 300 MW PP (United) | 162 | 162 | 161 | 124 | 87 | 16 | 16 | 82 | 87 | 89 | 120 | 140 | 143 | 143 | 143 | 106 | 106 | 142 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3041018
| Juldah unit-2 (Acorn) | 90 | 100 | 100 | 100 | 100 | 50 | 50 | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2327040
120 | Eastern Zone Total | 6601 | 6292 | 6102 | 5931 | 5778 | 5458 | 5197 | 5420 | 5914 | 6096 | 6337 | 6464 | 6569 | 6509 | 6621 | 6324 | 6231 | 7589 | 0 | 7570 | 7585 | 7457 | 7548 | 7364 | 7011 | 6783 | 156220016
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [7 empty] | 9 | 16 | [7 empty] | 40 | 115 |  | 115 | 115 | 115 | 115 | 107 | 49 | 16 | 699840
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [17 empty] | 5 |  | 9 | 9 | 3 |  |  |  |  | 24950
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 90 | 90 | 90 | 90 | 90 | 70 | 17 | 53 | 53 | 53 | 70 | 90 | 90 | 90 | 90 | 90 |  |  |  | 17 | 70 | 90 | 90 | 90 | 90 | 90 | 1726560
130
131
132
133 | Bhola Nutan Biddut BD LTD (GAS) | 37 | 37 | 37 | 37 | 38 | 37 | 37 | 37 | 38 | 38 | 38 | 38 | 36 | 38 | 38 | 38 | 38 | 38 |  | 38 | 38 | 37 | 38 | 38 | 37 | 36 | 903900
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [17 empty] | 74 |  | 80 | 80 | 80 | 80 | 96 | 80 | 48 | 510720
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 53 | 53 | 53 | 53 | 52 | 52 | 53 | 24 | 23 | 23 | 55 | 55 | 88 | 92 | 92 | 92 | 95 | 96 |  | 97 | 96 | 97 | 95 | 76 | 76 | 77 | 1542991
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 27 | 26 | 26 | 27 | 24 | 26 | 23 | 21 | 21 | 21 | 15 | 24 | 23 | 26 | 22 | 24 | 22 | 32 |  | 32 | 33 | 33 | 32 | 33 | 31 | 33 | 601422
141 | Noapara 100 MW PP (Bangla Trac) | [17 empty] | 12 |  | 77 | 100 | [5 empty] | 163200
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 40 |  | 40 | 40 | 40 |  |  |  |  | 118875
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 2 | 4 | [8 empty] | 2304
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 905 | 905 | 905 | 906 | 906 | 905 | 905 | 891 | 890 | 890 | 890 | 891 | 890 | 890 | 890 | 891 | 890 | 889 |  | 891 | 891 | 891 | 891 | 890 | 891 | 891 | 21469090
147 | Bheramara 410 MW CCPP | 350 | 340 | 360 | 345 | 345 | 345 | 370 | 290 | 290 | 355 | 340 | 340 | 355 | 365 | 365 | 370 | 340 | 345 |  | 340 | 345 | 345 | 345 | 340 | 365 | 345 | 8553312
148 | Payra 1320 MW | 550 | 550 | 550 | 550 | 550 | 520 | 520 | 440 | 440 | 440 | 470 | 470 | 470 | 470 | 490 | 490 | 490 | 615 |  | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 13060600
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 148 | 149 | 149 |  | 149 | 149 | 149 | 150 | 150 | 150 | 150 | 3669100
153 | Baghabari 71 MW GTPP | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 70 | 70 | 65 | 65 | 65 | 65 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 65 | 65 | 65 | 65 | 1530000
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 50 |  | 50 | 50 | 31 |  |  |  |  | 135056
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 130 | 100 | 100 | 120 | 144 | 144 | 142 | 143 | 143 | 135 | 110 |  | 144 | 148 | 148 | 148 | 148 | 148 | 148 | 3486400
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 156 | 158 | 158 | 159 | 155 | 161 | 163 | 175 | 130 | 138 | 186 | 162 | 183 | 166 | 190 | 178 | 164 | 156 |  | 174 | 153 | 152 | 155 | 151 | 154 | 157 | 4118509
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 158 | 160 | 160 | 161 | 157 | 163 | 165 | 177 | 130 | 142 | 162 | 165 | 207 | 171 | 192 | 191 | 173 | 171 |  | 173 | 157 | 157 | 161 | 156 | 158 | 160 | 4216609
Sirajgonj 225MW CCPP Unit-3 (Oil)
Sirajgonj 400 MW CCPP Unit-4
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 5 | 8 |  | 11 | 33 | 25 |  |  |  |  | 46322
162 | Bogra 22 MW PP (GBB) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 425280
163 | Bogura 20 MW PP (Energyprima) |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 7 | 7 | 7 | 7 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 219528
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 238032
165 | Amnura 50 MW PP(Sinha) | [8 empty] | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 43 |  | 43 | 43 | 43 | 43 |  |  |  | 369270
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [16 empty] | 24 | 37 |  | 37 | 39 | 45 |  |  |  |  | 110255
168 | Santahar 50 MW Peaking PP | [16 empty] | 16 | 33 |  | 33 | 33 | 32 |  |  |  |  | 103914
169 | Natore 52 MW PP (Rajlanka) | [16 empty] | 13 | 52 |  | 52 | 52 | 52 | 25 |  |  |  | 181920
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 70 |  | 88 | 88 | 93 | 10 |  |  |  | 258424
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [16 empty] | 1 | 75 |  | 110 | 113 | 113 | 70 |  |  |  | 423072
172 | Confidence Power Bogura Unit-1 113 MW | 109 | 109 | 35 | 0 |  |  |  | 30 | 35 | 35 | 50 | 70 | 70 | 70 | 109 | 70 | 70 | 109 |  | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 1683648
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 98 | 85 | 0 |  |  |  |  | 8 | 40 | 40 | 38 | 64 | 62 | 72 | 82 | 90 | 76 | 92 |  | 96 | 99 | 102 | 110 | 110 | 112 | 102 | 1514880
177 | Sympa Solar Power 8MW | [6 empty] | 1 | 2 | 3 | 4 | 5 | 4 | 4 | 5 | 2 | 1 | 0 | [9 empty] | 30659
178
178