## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-11-07 | Saturday
|  |  | Date (day): | 2020-11-07 |  | Saturday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12584.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13980 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-11-06 | 2020-11-07 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 120 | 100 | 150
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 115 | 115 | 115 | 75 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 200 | 200 | 165 |  | Gas shortage
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 51 | 51 | 51 |  | 57 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under S/D for dust in gas.
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 327 | 317 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 360 | 400 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 150 | 132 | 155 | 155 |  | 150 | GT-2 Under maint.
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 50 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 16 | 16 | 16 |  | 6 | Engine problem
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 82 | 150 | 150 | 200
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 7 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 17 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 38 | 49 | 56 | 56 |  | 24 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 28 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 8 | 25 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 35 | 36 | 88 | 88 |  | 17 | Engine problem
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 53 | 90 | 90 |  | 14 | Engine problem
|  | Manikgonj 162MW PP |  | HFO | IPP | 9*18 | 0 | 0 | 5 | 0 | 0 | 0
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 1457 | 1716 | 3427 | 3867 | 582 | 1405
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 115 | 160 | 160 | 160 | 70 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 70 | 125 | 145 | 145
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 102 | 102
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 60 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 34 | 42 | 10 | 20
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 90 | 90 |  | 18 | Engine problem
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 51 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 54 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 10 | 60 | 100 | 100
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 411 | 742 | 1611 | 1596 | 310 | 116
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 30 | 80 | 80 | 55 |  | Gas Shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 70 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 100
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 142 | 163 | 225 | 225 |  |  | FGMO
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 295 | 275 | 0 | 0 |  | 360 | Under maint.
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 230 | 270 | 0 | 0 |  | 360 | Under maint.
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 5 | 20 | 20 | 25 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 2 | 2 | 50 | 50
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 0 | 68 | 127 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 10 | 51 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 73 | 90 | 90 |  | 68 | ST under maint and gas shortage
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 165 | 165
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 21 | 22 | 22
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 5 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 74 | 94 | 163 | 173
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 10 | 20 | 20 | 21
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 0 | 114 |  | Fuel shortage
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 45 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 931 | 1095 | 1245 | 1674 | 450 | 788
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 122 | 159 | 149 | 130 | 72 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 22 | 22 | 22
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 25 | 25 | 25 | 25 |  | 70 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 7 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 16 | 115 | 115 | 115
|  | Mymensingh PV 50 MW Solar PP |  | Solar | IPP | 50 | 0 | 0 | 50 | 0 | 40 | 0
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 235 | 328 | 552.6 | 492 | 72 | 70
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 20 | 30 | 30 | 30
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 20 | 30 | 30 | 30 |  | 60 | Unit-4 under shut down
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 |  | 54 | STG under maint.
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 133 | 159 | 160 | 160 |  | 170 | GT-2 S/D due to gas shortage.
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 8 | 47 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 5 | 47 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 65 | 69 | 65 | 65 |  |  | FGMO
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 87 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 131 | 157 | 200 | 200
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 18 | 18 | 18
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 24 | 25 | 25
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 315 | 341 | 341 |  |  | FGMO
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 252 | 338 | 400 | 400
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 9 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1064 | 1451 | 1581 | 1581 | 0 | 284
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 908 | 908 | 917 | 917
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 380 | 345 | 410 | 410
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 105 | 105 | 105
| 108 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1288 | 1358 | 1687 | 2113 | 0 | 0
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 18 | 25 | 33 | 33
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 88 | 95 | 95
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 250 | 400 | 600 | 660
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 36 | 0 | 0 | 0
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 304 | 529 | 838 | 898 | 0 | 194
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 50 | 70 | 70 | 70 | 30 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 42 | 43 |  | 7 | Engine problem
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 75 | 90 | 144 | 144 |  | 75 | ST Under maint
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 153 | 200 | 225 | 225 |  |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 138 | 204 | 220 | 220 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 0 | 0 | 0 | 0 |  | 414 | Under maint.
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 33
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 0 | 22 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 9 | 10 | 10
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 113 | 113
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 424 | 606 | 1372 | 1496 | 151 | 496
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 113 | 113
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 155 | 150 | 271 | 263 | 294 | 40
|  | Total |  |  |  |  | 20383 | 19892 | 6269 | 7975 | 12584.6 | 13980 | 1859 | 3393
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 5853.1629 | 7446 | 11749.8347 | 13052.6746
| A. |  | 2020-11-06 | (Yesterday) |  |  |  |  | Friday
| 1 | Highest Generation : |  |  | 7975 | MW at | 20:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
| 2 | Minimum Generation : |  |  | 5806 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 7975 | MW
| 3 | Day peak Generation : |  |  | 6269 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 7446 | MW
| 4 | Evening peak Generation : |  |  | 7975 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 161.1064 | MKWHr | By Solar | 0.5014 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 112.6232 | MKWHr |  | By Oil: | 11.0032 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 11.594 | MKWHr |  | By Hydro: | 3.4325 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1859 | MW | Dhaka | 2599 | 2599 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3393 | MW | Chittagong | 848 | 848 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5252 | MW | Khulna | 936 | 936 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 957.02 | MMCFD |  |  | Rajshahi | 758 | 758 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 132852709.071 | ii) Oil : | Taka | 65822660.56 | Comilla | 655 | 655 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 54687545 | Total | Taka | 253362914.631 | Mymensingh | 611 | 611 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.046 | MKWHr. | Sylhet | 320 | 320 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 70 | MW (E to W) at | 20:00 | hrs | Barisal | 236 | 236 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -36 | MW at | 18:00 | hrs | Rangpur | 483 | 483 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 31° C |  |  | Total | 7446 | 7446 |  | 0
| B. |  | 2020-11-07 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 29.7° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13980 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 7200 | MW
| 4 | Reserve(Generation end) |  |  |  | 4780 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 185.8532 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5524 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 20.0495 | MKWHr. | ii) HVDC Flow at Peak Time |  | 908 | MW at | 20:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.9027 | MKWHr. | iii) Maximum HVDC Flow : |  | 909 | MW at | 22:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 104.46 |  | (b) Today: | 104.45 |  | (c) Rule Curve: |  | 108.4
.

## YesterdayGen
2020-11-06
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Mymensingh PV 50 MW Solar PP | Manikgonj 162MW PP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 150 | 115 | 200 | 51 | 0 | 0 | 293 |  | 0 | 340 | 145 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 32 | 25 | 33 | 0 | 0 | 90 | 70 | 120 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 20 | 41 | 0 | 70 | 0 | 280 | 250 | 165 | 8 | 50 | 10 | 2 | 0 | 10 | 0 | 0 | 0 | 19 | 0 | 8 | 15 | 86 | 108 | 25 | 0 | 0 | 30 | 30 | 5 | 5 | 110 | 156 | 40 | 10 | 0 | 204 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 401 | 8 | 52 | 0 | 0 | 51 | 54 | 0 | 0 | 0 | 100 | 0 | 17 | 0 | 0 |  | 717 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 5 | 0 | 0 | 150 | 0 | 0 | 153 | 0 | 158 | 0 | 22 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 36 | 0 |  | 4765 | 2281 | 7046 | 3668 | 717 | 1235 | 580 | 600 | 160 | 0 | 86 | 0 | 0 | 104.46
2:00 | 0 | 0 | 98 | 115 | 200 | 12 | 0 | 0 | 321 |  | 0 | 350 | 140 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 32 | 25 | 33 | 0 | 0 | 90 | 70 | 120 | 0 | 0 | 0 | 0 | 142 | 0 |  | 0 | 0 | 0 | 0 | 0 | 5 | 20 | 42 | 0 | 70 | 0 | 280 | 250 | 163 | 8 | 50 | 10 | 2 | 0 | 10 | 0 | 0 | 0 | 19 | 0 | 8 | 15 | 82 | 129 | 25 | 0 | 0 | 30 | 30 | 5 | 5 | 110 | 160 | 40 | 10 | 0 | 160 | 0 | 0 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 400 | 0 | 17 | 0 | 0 | 16 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 |  | 717 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 148 | 0 | 0 | 100 | 0 | 159 | 0 | 23 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 35 | 0 |  | 4434 | 2209 | 6643 | 3529 | 717 | 1220 | 337 | 598 | 160 | 0 | 82 | 0 | 0 | 104.46
3:00 | 0 | 0 | 107 | 115 | 200 | 12 | 0 | 0 | 293 |  | 0 | 350 | 130 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 32 | 25 | 33 | 0 | 0 | 90 | 70 | 120 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 0 | 70 | 0 | 280 | 250 | 162 | 8 | 51 | 10 | 2 | 0 | 10 | 0 | 0 | 0 | 19 | 0 | 8 | 12 | 80 | 130 | 25 | 0 | 0 | 30 | 30 | 5 | 5 | 110 | 159 | 40 | 10 | 0 | 158 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 400 | 0 | 17 | 0 | 0 | 16 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 |  | 717 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 77 | 0 | 159 | 0 | 22 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 37 | 0 |  | 4400 | 2122 | 6522 | 3487 | 717 | 1207 | 322 | 549 | 160 | 0 | 80 | 0 | 0 | 104.46
4:00 | 0 | 0 | 98 | 115 | 200 | 12 | 0 | 0 | 258 |  | 0 | 370 | 140 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 32 | 25 | 33 | 0 | 0 | 85 | 70 | 120 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 0 | 70 | 0 | 280 | 250 | 162 | 8 | 50 | 10 | 2 | 0 | 10 | 0 | 0 | 0 | 19 | 0 | 8 | 12 | 76 | 129 | 25 | 0 | 0 | 30 | 30 | 5 | 5 | 110 | 157 | 40 | 10 | 0 | 158 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 303 | 0 | 17 | 0 | 0 | 16 | 17 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 |  | 717 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 73 | 0 | 139 | 0 | 22 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 35 | 0 |  | 4263 | 2026 | 6289 | 3280 | 717 | 1200 | 312 | 549 | 155 | 0 | 76 | 0 | 0 | 104.46
5:00 | 0 | 0 | 99 | 115 | 200 | 12 | 0 | 0 | 259 |  | 0 | 350 | 140 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 32 | 25 | 33 | 0 | 0 | 85 | 70 | 120 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 0 | 70 | 0 | 280 | 250 | 162 | 8 | 50 | 10 | 2 | 0 | 10 | 0 | 0 | 0 | 19 | 0 | 8 | 12 | 74 | 129 | 25 | 0 | 0 | 20 | 30 | 5 | 5 | 110 | 157 | 40 | 10 | 0 | 158 | 0 | 0 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 304 | 0 | 17 | 0 | 0 | 16 | 17 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 |  | 716 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 73 | 0 | 142 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 36 | 0 |  | 4165 | 1946 | 6111 | 3251 | 716 | 1124 | 292 | 499 | 155 | 0 | 74 | 0 | 0 | 104.46
6:00 | 0 | 0 | 100 | 115 | 200 | 12 | 0 | 0 | 253 |  | 0 | 330 | 145 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 32 | 0 | 33 | 0 | 0 | 85 | 70 | 120 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 0 | 70 | 0 | 280 | 250 | 162 | 8 | 50 | 10 | 2 | 0 | 10 | 0 | 0 | 0 | 19 | 0 | 8 | 0 | 70 | 148 | 25 | 0 | 0 | 20 | 20 | 5 | 5 | 110 | 158 | 53 | 10 | 0 | 152 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 305 | 0 | 17 | 0 | 0 | 16 | 17 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 |  | 717 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 73 | 0 | 130 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 35 | 0 |  | 4109 | 1875 | 5984 | 3193 | 717 | 1133 | 277 | 439 | 155 | 0 | 70 | 0 | 0 | 104.46
7:00 | 0 | 0 | 100 | 115 | 200 | 12 | 0 | 0 | 253 |  | 0 | 300 | 140 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 32 | 20 | 33 | 0 | 0 | 84 | 70 | 120 | 0 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 0 | 70 | 0 | 250 | 230 | 143 | 8 | 50 | 10 | 2 | 0 | 10 | 0 | 0 | 0 | 19 | 0 | 8 | 8 | 64 | 147 | 25 | 20 | 0 | 20 | 20 | 8 | 5 | 110 | 133 | 40 | 10 | 0 | 138 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 10 | 0 | 0 | 305 | 16 | 42 | 0 | 1 | 16 | 17 | 0 | 0 | 0 | 10 | 0 | 0 | 5 | 0 |  | 717 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 70 | 0 | 136 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 36 | 0 |  | 4024 | 1782 | 5806 | 3076 | 717 | 1095 | 293 | 399 | 154 | 0 | 64 | 8 | 0 | 104.46
8:00 | 0 | 0 | 100 | 115 | 200 | 12 | 0 | 0 | 254 |  | 0 | 300 | 125 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 28 | 0 | 33 | 0 | 0 | 87 | 70 | 120 | 0 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 0 | 70 | 0 | 250 | 230 | 141 | 8 | 50 | 10 | 2 | 0 | 10 | 0 | 0 | 0 | 19 | 0 | 8 | 8 | 64 | 149 | 25 | 20 | 1 | 20 | 20 | 5 | 5 | 110 | 134 | 40 | 10 | 0 | 164 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 305 | 37 | 52 | 0 | 2 | 16 | 17 | 0 | 0 | 0 | 10 | 0 | 0 | 20 | 0 |  | 717 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 90 | 0 | 152 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 250 | 36 | 0 |  | 4065 | 1911 | 5976 | 3204 | 717 | 1101 | 309 | 400 | 157 | 0 | 64 | 24 | 0 | 104.46
9:00 | 0 | 0 | 100 | 115 | 200 | 12 | 0 | 0 | 260 |  | 0 | 320 | 133 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 24 | 16 | 33 | 0 | 0 | 88 | 70 | 120 | 0 | 0 | 0 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 33 | 0 | 70 | 0 | 265 | 230 | 141 | 8 | 50 | 10 | 2 | 0 | 10 | 0 | 0 | 0 | 19 | 0 | 8 | 8 | 62 | 128 | 25 | 20 | 1 | 20 | 20 | 5 | 5 | 110 | 132 | 40 | 10 | 0 | 130 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 251 | 75 | 52 | 0 | 3 | 16 | 17 | 0 | 0 | 0 | 10 | 0 | 0 | 33 | 0 |  | 717 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 90 | 0 | 139 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 250 | 38 | 0 |  | 3999 | 1880 | 5879 | 3069 | 717 | 1079 | 355 | 400 | 158 | 0 | 62 | 39 | 0 | 104.46
10:00 | 0 | 0 | 120 | 115 | 200 | 12 | 0 | 0 | 226 |  | 0 | 280 | 140 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 25 | 25 | 33 | 0 | 0 | 90 | 70 | 120 | 0 | 0 | 0 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 37 | 0 | 70 | 0 | 265 | 230 | 141 | 8 | 70 | 10 | 2 | 0 | 10 | 0 | 0 | 0 | 19 | 0 | 8 | 8 | 62 | 127 | 25 | 20 | 2 | 20 | 20 | 5 | 5 | 110 | 135 | 40 | 10 | 0 | 131 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 240 | 35 | 35 | 0 | 4 | 0 | 17 | 0 | 0 | 0 | 10 | 0 | 0 | 44 | 0 |  | 809 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 75 | 0 | 130 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 250 | 42 | 0 |  | 3846 | 1899 | 5745 | 2977 | 809 | 989 | 279 | 400 | 160 | 0 | 62 | 69 | 0 | 104.46
11:00 | 0 | 0 | 100 | 115 | 200 | 12 | 0 | 0 | 309 |  | 0 | 300 | 140 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 13 | 25 | 25 | 0 | 0 | 80 | 35 | 120 | 0 | 0 | 0 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 37 | 0 | 70 | 0 | 285 | 230 | 142 | 8 | 50 | 10 | 2 | 0 | 10 | 0 | 0 | 0 | 19 | 0 | 0 | 10 | 68 | 125 | 25 | 20 | 2 | 20 | 20 | 5 | 5 | 110 | 135 | 65 | 10 | 0 | 131 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 232 | 16 | 35 | 0 | 5 | 0 | 17 | 0 | 0 | 0 | 10 | 0 | 0 | 49 | 0 |  | 908 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 75 | 0 | 130 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 250 | 35 | 0 |  | 3884 | 2017 | 5901 | 2968 | 908 | 1119 | 243 | 400 | 115 | 0 | 68 | 80 | 0 | 104.46
12:00 | 0 | 0 | 100 | 115 | 200 | 12 | 0 | 0 | 327 |  | 0 | 360 | 150 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 13 | 25 | 8 | 0 | 0 | 80 | 35 | 120 | 0 | 0 | 0 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 34 | 0 | 70 | 0 | 295 | 230 | 142 | 8 | 50 | 10 | 2 | 0 | 10 | 0 | 0 | 0 | 19 | 11 | 0 | 10 | 74 | 122 | 25 | 20 | 2 | 20 | 20 | 8 | 5 | 110 | 133 | 65 | 10 | 0 | 131 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 252 | 16 | 35 | 0 | 5 | 0 | 17 | 0 | 0 | 0 | 10 | 0 | 0 | 50 | 5 |  | 908 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 75 | 0 | 153 | 0 | 0 | 0 | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 250 | 36 | 0 |  | 4098 | 2171 | 6269 | 3182 | 908 | 1250 | 258 | 400 | 115 | 0 | 74 | 82 | 0 | #REF!
13:00 | 0 | 0 | 120 | 115 | 200 | 40 | 0 | 0 | 348 |  | 0 | 380 | 130 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 25 | 13 | 25 | 25 | 0 | 0 | 81 | 35 | 120 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 0 | 70 | 0 | 270 | 270 | 141 | 8 | 50 | 10 | 2 | 0 | 10 | 0 | 0 | 0 | 21 | 8 | 0 | 10 | 80 | 124 | 25 | 20 | 2 | 20 | 20 | 8 | 5 | 110 | 159 | 63 | 10 | 0 | 145 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 304 | 20 | 35 | 0 | 4 | 0 | 17 | 0 | 0 | 0 | 10 | 0 | 0 | 46 | 9 |  | 908 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 100 | 0 | 171 | 0 | 1 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 250 | 35 | 0 |  | 4391 | 2243 | 6634 | 3466 | 908 | 1337 | 251 | 400 | 116 | 0 | 80 | 76 | 6634 | 104.46
14:00 | 0 | 0 | 117 | 115 | 200 | 51 | 0 | 0 | 227 |  | 0 | 300 | 132 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 5 | 25 | 25 | 0 | 0 | 81 | 35 | 120 | 0 | 0 | 0 | 0 | 107 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 0 | 70 | 0 | 260 | 270 | 141 | 8 | 50 | 10 | 2 | 0 | 32 | 0 | 0 | 0 | 21 | 11 | 0 | 10 | 76 | 124 | 25 | 20 | 2 | 20 | 20 | 5 | 5 | 110 | 159 | 51 | 10 | 0 | 145 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 304 | 35 | 36 | 0 | 3 | 0 | 17 | 0 | 0 | 0 | 10 | 0 | 0 | 37 | 11 |  | 908 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 100 | 0 | 146 | 0 | 34 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 250 | 35 | 0 |  | 4077 | 2200 | 6277 | 3282 | 908 | 1150 | 283 | 400 | 116 | 0 | 76 | 62 | 0 | 104.46
15:00 | 0 | 0 | 120 | 115 | 200 | 12 | 0 | 0 | 227 |  | 0 | 280 | 130 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 10 | 25 | 25 | 0 | 0 | 80 | 35 | 120 | 0 | 0 | 0 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0 | 70 | 0 | 275 | 270 | 142 | 8 | 50 | 10 | 2 | 0 | 15 | 0 | 0 | 0 | 21 | 11 | 0 | 12 | 70 | 154 | 25 | 20 | 1 | 20 | 20 | 5 | 5 | 110 | 158 | 40 | 10 | 0 | 120 | 0 | 0 | 0 | 280 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 304 | 35 | 36 | 0 | 2 | 0 | 17 | 0 | 0 | 0 | 10 | 0 | 0 | 24 | 13 |  | 908 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 100 | 0 | 134 | 0 | 35 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 250 | 36 | 0 |  | 3981 | 2163 | 6144 | 3239 | 908 | 1087 | 283 | 400 | 115 | 0 | 70 | 42 | 0 | 104.46
16:00 | 0 | 0 | 130 | 115 | 200 | 12 | 0 | 0 | 227 |  | 0 | 280 | 122 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 10 | 25 | 25 | 0 | 0 | 80 | 35 | 120 | 0 | 0 | 0 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 35 | 0 | 70 | 0 | 280 | 270 | 141 | 8 | 50 | 10 | 2 | 0 | 15 | 0 | 0 | 0 | 0 | 11 | 0 | 12 | 72 | 154 | 25 | 0 | 0 | 20 | 20 | 8 | 5 | 110 | 157 | 40 | 5 | 0 | 120 | 0 | 0 | 0 | 270 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 304 | 27 | 36 | 0 | 1 | 0 | 17 | 0 | 0 | 0 | 10 | 0 | 0 | 9 | 33 |  | 908 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 70 | 0 | 130 | 0 | 24 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 250 | 0 | 0 |  | 3919 | 2023 | 5942 | 3122 | 908 | 1021 | 287 | 400 | 115 | 0 | 72 | 17 | 0 | 104.46
17:00 | 0 | 0 | 113 | 115 | 200 | 12 | 0 | 0 | 227 |  | 0 | 280 | 140 | 0 | 0 | 1 | 0 | 0 | 38 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 4 | 0 | 25 | 11 | 25 | 25 | 0 | 0 | 90 | 35 | 120 | 0 | 0 | 0 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 0 | 70 | 0 | 295 | 270 | 141 | 8 | 51 | 10 | 2 | 0 | 15 | 0 | 0 | 0 | 0 | 8 | 0 | 12 | 72 | 155 | 25 | 0 | 0 | 20 | 20 | 8 | 5 | 110 | 157 | 40 | 5 | 0 | 122 | 18 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 10 | 0 | 2 | 304 | 27 | 36 | 0 | 0 | 13 | 17 | 0 | 0 | 0 | 10 | 0 | 0 | 1 | 33 |  | 908 | 0 | 285 | 0 | 12 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 19 | 10 | 0 | 50 | 0 | 0 | 0 | 4 | 3 | 0 | 0 | 0 | 8 | 3 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 70 | 0 | 130 | 0 | 24 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 |  | 3999 | 2066 | 6065 | 3125 | 908 | 1050 | 367 | 400 | 125 | 17 | 72 | 1 | 0 | 104.46
18:00 | 0 | 0 | 116 | 115 | 200 | 51 | 0 | 0 | 257 |  | 0 | 350 | 110 | 7 | 10 | 18 | 0 | 0 | 70 | 14 | 58 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 0 | 25 | 11 | 28 | 25 | 12 | 0 | 91 | 35 | 120 | 0 | 0 | 0 | 0 | 104 | 0 |  | 0 | 0 | 51 | 0 | 10 | 14 | 20 | 42 | 0 | 70 | 0 | 265 | 270 | 179 | 8 | 70 | 10 | 2 | 0 | 25 | 0 | 0 | 12 | 21 | 11 | 33 | 12 | 94 | 161 | 25 | 0 | 0 | 20 | 30 | 45 | 23 | 110 | 158 | 40 | 87 | 0 | 130 | 18 | 0 | 9 | 260 | 24 | 5 | 0 | 31 | 0 | 0 | 62 | 0 | 25 | 0 | 60 | 0 | 38 | 305 | 73 | 36 | 0 | 0 | 83 | 38 | 0 | 0 | 29 | 60 | 0 | 0 | 0 | 17 |  | 908 | 0 | 285 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 60 | 0 | 70 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 29 | 22 | 7 | 11 | 0 | 0 | 150 | 0 | 0 | 70 | 0 | 137 | 0 | 55 | 0 | 137 | 0 | 0 | 105 | 0 | 0 | 0 | 20 | 0 | 0 | 30 | 300 | 0 | 0 |  | 5170 | 2506 | 7676 | 3376 | 908 | 1377 | 1249 | 450 | 126 | 96 | 94 | 0 | 0 | 104.46
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 120 | 115 | 200 | 51 | 0 | 0 | 288 |  | 0 | 350 | 145 | 0 | 10 | 0 | 0 | 0 | 120 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 24 | 28 | 25 | 16 | 0 | 90 | 70 | 120 | 0 | 0 | 0 | 0 | 106 | 0 |  | 0 | 0 | 0 | 0 | 0 | 40 | 20 | 42 | 10 | 70 | 0 | 310 | 270 | 155 | 8 | 73 | 10 | 2 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 33 | 19 | 94 | 158 | 25 | 22 | 0 | 30 | 30 | 47 | 47 | 110 | 158 | 40 | 87 | 0 | 149 | 18 | 0 | 9 | 260 | 24 | 8 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 60 | 0 | 30 | 304 | 115 | 36 | 0 | 0 | 50 | 54 | 0 | 0 | 76 | 60 | 0 | 38 | 0 | 0 |  | 908 | 0 | 290 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 9 | 11 | 0 | 0 | 150 | 0 | 0 | 70 | 0 | 157 | 0 | 70 | 0 | 159 | 0 | 0 | 105 | 0 | 0 | 0 | 40 | 0 | 0 | 35 | 330 | 0 | 0 |  | 5286 | 2515 | 7801 | 3593 | 908 | 1478 | 1088 | 480 | 160 | 0 | 94 | 0 | 0 | 104.46
19:30 | 0 | 0 | 120 | 115 | 200 | 51 | 0 | 0 | 287 |  | 0 | 350 | 145 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 24 | 28 | 25 | 0 | 0 | 90 | 70 | 120 | 0 | 0 | 0 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 42 | 15 | 65 | 0 | 290 | 270 | 129 | 8 | 73 | 5 | 2 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 33 | 19 | 96 | 160 | 25 | 22 | 0 | 30 | 30 | 47 | 47 | 110 | 157 | 40 | 87 | 0 | 157 | 18 | 0 | 9 | 315 | 24 | 11 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 60 | 0 | 30 | 304 | 115 | 36 | 0 | 0 | 50 | 54 | 0 | 0 | 85 | 60 | 0 | 53 | 0 | 0 |  | 908 | 0 | 290 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 32 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 9 | 11 | 0 | 0 | 150 | 0 | 0 | 70 | 0 | 211 | 0 | 78 | 0 | 205 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 |  | 5309 | 2589 | 7898 | 3652 | 908 | 1541 | 1021 | 520 | 160 | 0 | 96 | 0 | 0 | 0
20:00 | 0 | 0 | 120 | 115 | 200 | 51 | 0 | 0 | 317 |  | 0 | 400 | 132 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 24 | 28 | 25 | 0 | 0 | 90 | 70 | 120 | 0 | 0 | 0 | 0 | 125 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 42 | 30 | 0 | 0 | 275 | 270 | 163 | 8 | 73 | 5 | 2 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 33 | 20 | 94 | 159 | 25 | 22 | 0 | 30 | 30 | 47 | 47 | 110 | 159 | 69 | 87 | 0 | 157 | 18 | 0 | 9 | 315 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 60 | 0 | 0 | 338 | 115 | 36 | 0 | 0 | 51 | 54 | 0 | 0 | 45 | 60 | 0 | 53 | 0 | 0 |  | 908 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 9 | 11 | 0 | 0 | 150 | 0 | 0 | 90 | 0 | 200 | 0 | 88 | 0 | 204 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 |  | 5332 | 2643 | 7975 | 3800 | 908 | 1630 | 833 | 550 | 160 | 0 | 94 | 0 | 0 | 104.46
21:00 | 0 | 0 | 120 | 115 | 200 | 51 | 0 | 0 | 318 |  | 0 | 400 | 132 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 28 | 28 | 25 | 0 | 0 | 92 | 70 | 120 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 45 | 20 | 42 | 50 | 0 | 0 | 275 | 270 | 175 | 8 | 74 | 5 | 2 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 33 | 21 | 96 | 161 | 25 | 22 | 0 | 30 | 30 | 47 | 47 | 110 | 158 | 69 | 87 | 0 | 158 | 18 | 0 | 9 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 30 | 0 | 0 | 340 | 75 | 36 | 0 | 0 | 51 | 54 | 0 | 0 | 8 | 40 | 0 | 53 | 0 | 0 |  | 907 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 9 | 11 | 0 | 0 | 150 | 0 | 0 | 135 | 0 | 178 | 0 | 87 | 0 | 193 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 35 | 0 |  | 5213 | 2658 | 7871 | 3850 | 907 | 1630 | 666 | 560 | 162 | 0 | 96 | 0 | 0 | #REF!
22:00 | 0 | 0 | 120 | 115 | 200 | 51 | 0 | 0 | 319 |  | 0 | 400 | 120 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 28 | 28 | 25 | 0 | 0 | 92 | 70 | 120 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 55 | 0 | 0 | 270 | 270 | 180 | 8 | 70 | 5 | 2 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 33 | 18 | 90 | 163 | 25 | 22 | 0 | 30 | 30 | 47 | 47 | 110 | 159 | 69 | 50 | 0 | 158 | 18 | 0 | 9 | 270 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 35 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 42 | 0 | 0 |  | 909 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 9 | 8 | 0 | 0 | 150 | 0 | 0 | 150 | 0 | 177 | 0 | 88 | 0 | 179 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 35 | 0 |  | 4867 | 2577 | 7444 | 3848 | 909 | 1585 | 320 | 530 | 162 | 0 | 90 | 0 | 0 | 104.46
23:00 | 0 | 0 | 112 | 115 | 200 | 51 | 0 | 0 | 319 |  | 0 | 400 | 120 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 32 | 28 | 25 | 0 | 0 | 92 | 70 | 120 | 0 | 0 | 0 | 0 | 144 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 60 | 0 | 0 | 0 | 270 | 218 | 0 | 70 | 5 | 2 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 33 | 15 | 86 | 162 | 25 | 22 | 0 | 30 | 30 | 47 | 47 | 110 | 158 | 70 | 20 | 0 | 158 | 18 | 0 | 9 | 270 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 35 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 |  | 909 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 5 | 0 | 0 | 149 | 0 | 0 | 150 | 0 | 182 | 0 | 89 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 34 | 0 |  | 4553 | 2548 | 7101 | 3627 | 909 | 1545 | 243 | 529 | 162 | 0 | 86 | 0 | 0 | 104.46
24:00 | 0 | 0 | 120 | 115 | 200 | 51 | 0 | 0 | 318 |  | 0 | 400 | 120 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 32 | 28 | 25 | 0 | 0 | 92 | 70 | 120 | 0 | 0 | 0 | 0 | 143 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 65 | 0 | 0 | 0 | 270 | 179 | 0 | 70 | 5 | 2 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 33 | 15 | 80 | 162 | 25 | 22 | 0 | 30 | 30 | 5 | 5 | 110 | 158 | 69 | 5 | 0 | 158 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 8 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 909 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 8 | 5 | 0 | 0 | 149 | 0 | 0 | 150 | 0 | 183 | 0 | 43 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 36 | 0 |  | 4187 | 2466 | 6653 | 3440 | 909 | 1346 | 187 | 529 | 162 | 0 | 80 | 0 | 0 | 104.46
KWH | 0 | 0 | 2694000 | 2772000 | 4794573 | 673272 | 0 | 0 | 6633000 |  | 0 | 8223750 | 3269178 | 14400 | 27840 | 39200 | 0 | 0 | 2107000 | 24000 | 128592 | 20160 | 0 | 0 | 0 | 0 | 439560 | 20288 | 64391 | 89316 | 600000 | 565020 | 601100 | 695200 | 32220 | 0 | 2016524 | 1416000 | 2800000 | 0 | 0 | 0 | 0 | 2746638 | 0 |  | 0 | 0 | 60983 | 0 | 18240 | 164640 | 472944 | 1032480 | 227378 | 1365510 | 0 | 6428000 | 6233000 | 3821000 | 200727 | 1341020 | 274392 | 61920 | 0 | 690695 | 0 | 0 | 18115 | 430308 | 88200 | 330700 | 339250 | 1902720 | 3279000 | 589440 | 309636 | 12850 | 579000 | 588120 | 379200 | 451080 | 2751218 | 3370000 | 1183680 | 586560 | 0 | 3525480 | 113000 | 0 | 50940 | 7035450 | 105466 | 57000 | 0 | 55200 | 0 | 0 | 192000 | 0 | 45792 | 108540 | 508800 | 0 | 132145 | 7202000 | 943200 | 869304 | 0 | 29880 | 391418 | 586650 | 0 | 0 | 185640 | 823680 | 0 | 239040 | 319280 | 110880 |  | 20049455 | 0 | 7575840 | 0 | 119040 | 0 | 0 | 0 | 0 | 1280 | 0 | 0 | 480900 | 134400 | 0 | 1449000 | 0 | 0 | 0 | 65456 | 34640 | 0 | 0 | 0 | 24029 | 141120 | 58068 | 171073 | 0 | 0 | 3679500 | 0 | 0 | 2466700 | 0 | 3899864 | 0 | 768476 | 0 | 3960182 | 0 | 0 | 441120 | 0 | 0 | 0 | 61440 | 0 | 30854 | 106752 | 7914500 | 752730 | 0 |  | 106720013 | 54386419 | 161106432 | 81651590 | 20049455 | 30971586 | 10831245 | 11594000 | 3432524 | 171908 | 1902720 | 501404 | 0
Fuel Cost | 0 | 0 | 3933240 | 4074840 | 5321976.03 | 888719.04 | 0 | 0 | 6831990 |  | 0 | 8963887.5 | 3628787.58 | 109296 | 191817.6 | 331632 | 0 | 0 | 3645110 | 180720 | 1172759.04 | 198374.4 | 0 | 0 | 0 | 0 | 3208788 | 156826.24 | 634895.26 | 66987 | 450000 | 0 | 0 | 0 | 311567.4 | 0 | 544461.48 | 382320 | 5068000 | 0 | 0 | 0 | 0 | 4669284.6 | 0 |  | 0 | 0 | 591535.1 | 0 | 158688 | 1303948.8 | 595909.44 | 3066465.6 | 336519.44 | 2020954.8 | 0 | 4756720 | 6233000 | 3515320 | 258937.83 | 1542173 | 310062.96 | 86688 | 0 | 1181088.45 | 0 | 0 | 172998.25 | 546491.16 | 66150 | 578725 | 254437.5 | 14270400 | 3475740 | 5352115.2 | 393237.72 | 204829 | 949560 | 940992 | 674976 | 703684.8 | 3136388.52 | 3504800 | 2331849.6 | 1120329.6 | 0 | 6099080.4 | 247470 | 0 | 103917.6 | 7105804.5 | 79099.5 | 43320 | 0 | 417312 | 0 | 0 | 998400 | 0 | 450593.28 | 1268832.6 | 4146720 | 0 | 931622.25 | 6697860 | 8601984 | 8214922.8 | 0 | 0 | 2959120.08 | 5109721.5 | 0 | 0 | 1590934.8 | 5485708.8 | 0 | 0 | 0 | 0 |  | 115484860.8 | 0 | 7954632 | 0 | 935654.4 | 0 | 0 | 0 | 0 | 13414.4 | 0 | 0 | 745395 | 1311744 | 0 | 2970450 | 0 | 0 | 0 | 579285.6 | 266728 | 0 | 0 | 0 | 233081.3 | 270950.4 | 90005.4 | 129502.261 | 0 | 0 | 19942890 | 0 | 0 | 2886039 | 0 | 5147820.48 | 0 | 1152714 | 0 | 4633412.94 | 0 | 0 | 4605292.8 | 0 | 0 | 0 | 476774.4 | 0 | 340936.7 | 788897.28 | 34744655 | 0 | 0 |  | 180154419.05 | 205705136.161 | 385859555.211 | 96470766.831 | 115484860.8 | 36381942.24 | 64206969.76 | 54687545 | 926781.48 | 1615690.8 | 14270400 | 1814598.3 | 0
Yesterday Day Peak | 0 | 0 | 100 | 115 | 200 | 12 | 0 | 0 | 327 |  | 0 | 360 | 150 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 13 | 25 | 8 | 0 | 0 | 80 | 35 | 120 | 0 | 0 | 0 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 34 | 0 | 70 | 0 | 295 | 230 | 142 | 8 | 50 | 10 | 2 | 0 | 10 | 0 | 0 | 0 | 19 | 11 | 0 | 10 | 74 | 122 | 25 | 20 | 2 | 20 | 20 | 8 | 5 | 110 | 133 | 65 | 10 | 0 | 131 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 252 | 16 | 35 | 0 | 5 | 0 | 17 | 0 | 0 | 0 | 10 | 0 | 0 | 50 | 5 |  | 908 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 75 | 0 | 153 | 0 | 0 | 0 | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 250 | 36 | 0 |  | 6269 | DayPeak
Yesterday Evening Peak | 0 | 0 | 120 | 115 | 200 | 51 | 0 | 0 | 317 | 0 | 0 | 400 | 132 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 24 | 28 | 25 | 0 | 0 | 90 | 70 | 120 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 42 | 30 | 0 | 0 | 275 | 270 | 163 | 8 | 73 | 5 | 2 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 33 | 20 | 94 | 159 | 25 | 22 | 0 | 30 | 30 | 47 | 47 | 110 | 159 | 69 | 87 | 0 | 157 | 18 | 0 | 9 | 315 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 60 | 0 | 0 | 338 | 115 | 36 | 0 | 0 | 51 | 54 | 0 | 0 | 45 | 60 | 0 | 53 | 0 | 0 |  | 908 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 9 | 11 | 0 | 0 | 150 | 0 | 0 | 90 | 0 | 200 | 0 | 88 | 0 | 204 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 |  | 7975 | EvPeak
Forecast for Evening | 0 | 0 | 150 | 115 | 200 | 51 | 0 | 0 | 360 | 0 | 0 | 450 | 155 | 100 | 100 | 55 | 0 | 0 | 200 | 100 | 100 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 31 | 33 | 33 | 52 | 0 | 90 | 70 | 120 | 0 | 25 | 0 | 0 | 145 | 0 | 0 | 0 |  | 102 | 100 | 90 | 50 | 20 | 20 | 80 | 0 | 100 | 0 | 0 | 225 | 68 | 90 | 20 | 50 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 173 | 130 | 25 | 22 | 0 | 30 | 30 | 51 | 44 | 110 | 160 | 65 | 86 | 0 | 200 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 165 | 150 | 400 | 115 | 88 | 100 | 0 | 300 | 54 | 110 | 0 | 113 | 100 | 0 | 90 | 0 |  |  | 917 | 16 | 410 | 0 | 115 | 220 | 0 | 0 | 30 | 60 | 40 | 0 | 33 | 110 | 0 | 70 | 0 | 50 | 40 | 100 | 43 | 0 | 50 | 52 | 33 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 225 | 0 | 95 | 100 | 220 | 0 | 0 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 660 | 0
Forecast for Day | 0 | 0 | 100 | 115 | 200 | 51 | 0 | 0 | 360 | 0 | 0 | 450 | 155 | 100 | 100 | 55 | 0 | 0 | 150 | 100 | 100 | 150 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 31 | 33 | 33 | 52 | 0 | 90 | 70 | 120 | 0 | 25 | 0 | 0 | 145 | 0 | 0 | 0 |  | 102 | 100 | 90 | 50 | 20 | 10 | 80 | 0 | 0 | 0 | 0 | 225 |  | 90 | 20 | 50 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 163 | 149 | 25 | 22 | 1.6 | 30 | 30 | 51 | 44 | 110 | 160 | 65 | 86 | 0 | 200 | 18 | 0 | 10 | 341 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 165 | 150 | 400 | 115 | 88 | 100 | 5 | 300 | 54 | 110 | 0 | 113 | 100 | 0 | 90 | 40 |  |  | 917 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 33 | 110 | 0 | 70 | 0 | 0 | 0 | 100 | 42 | 0 | 50 | 52 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 225 |  | 95 | 0 | 220 | 0 | 0 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 600 | 0
Generation at 08:00(Today) | 0 | 0 | 100 | 115 | 200 | 12 | 0 | 0 | 308 | 0 | 0 | 370 | 145 |  | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 23 | 28 | 25 | 0 | 0 | 89 | 70 | 120 | 0 | 0 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 16 | 80 | 0 | 0 | 0 | 320 | 196 | 0 | 90 | 20 | 2 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 33 | 10 | 60 | 161 | 0 | 20 | 1 | 30 | 30 | 5 | 5 | 110 | 157 | 67 | 5 | 0 | 164 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 330 | 0 | 32 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 24 | 0 | 0 | 710 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 100 | 0 | 162 | 0 | 23 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 250 | 36 | 0 | 0
199
| Minimum Generation |  | 5806 | 7:00
| Highest Generation |  | 7975 | 20:00
| Day Peak Generation |  | 6269 | 12:00
| Evening Peak Generation |  | 7975 | 20:00
| HVDC Max Flow |  | 909 | 22:00
| HVDC EvPeak Flow |  | 908 | 20:00
| Load factor L.F |  | 84.17%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-11-07
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-11-06 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6269 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5524 | MW
Evening Peak Generation : |  | 7975 | MW Hour : | 20:00 | Available Max Generation : |  | 13980 | MW
E.P. Demand (at gen end) : |  | 7975 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 9200 | MW
Maximum Generation : |  | 7975 | MW Hour : | 20:00 | Reserve(Generation end) |  | 4780 | MW
Total Gen. (MKWH) : |  | 161.1064 | System Load Factor : | 84.17% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -36 | MW at | 18:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-11-07
Actual : | 104.45 | Ft.(MSL) , | Rule curve : | 108.4 | Ft.( MSL )
Gas Consumed : | Total = | 957.02 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 132852709.071
: |  | Coal : | 54687545 | Oil : | 65822660.56 | Total : | 253362914.631
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3210.1142 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1086.2672 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 972.3062 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 878.2223 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 793.8234 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 640.5739 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 365.0611 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 165.1127 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 494.0094 |  |  | 0 | 0%
Total | 0 |  | 8605.4904 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-2 | 10) Sirajganj #1 CCPP STG
|  |  |  | 2) Baghabari-100 MW | 11) Summit Meghnaghat GT-2
|  |  |  | 3) Ghorasal Unit-1,2,3 | 12) Ashuganj(N)-360 MW
|  |  |  | 4) Ashuganj unit-3 | 13) Ashuganj(S)-360 MW
5) Kaptai-2
6) Raozan #2,5
7) Siddirganj-335 MW
8) Haripur 412 MW
9) Chandpur-163 MW STG
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Megnaghat-Cumilla(N) 230 kV Ckt-1 was under shut down from 10:17 to 16:42 for A/M.
b) Rampura 230/132 kV T-1 transformer was under shut down from 10:09 to 11:00 for D/W.
c) TK Chemical-Sikalbaha 132 kV Ckt was under shut down from 08:54 to 14:51 for C/M.
d) Halishahar 132/33 kV T-1 transformer was under shut down from 07:54 to 14:52 for A/M.
e) Rangpur-Lalmonirhat 132 kV Ckt was under shut down from 08:01 to 16:13 for A/M. |  |  |  |  | About 35 MW power interruption occurred under Lalmonirhat S/S
from 08:01 to 16:13.
f) Shariatpur 132/33 kV T-2 transformer was shut down at 12:53 for oil leakage maintenance.
g) Kaptai #4 was shut down at 10:19 for low demand.
h) Ashuganj #3 was synchronized at 18:54.
i) Ashuganj #4 was shut down at 19:45 due to low gas shortage.
j) Ashuganj(N)-360 MW was shut down at 22:23 for water pipe line leakage.
k) Sonargaon 132/33 kV T-1 & T-2 transformers tripped at 04:08(7/11/20) showing PRD, Buccholz relay and |  |  |  |  | About 48 MW power interruption occurred under Sonargaon S/S area
T-1 transformer was switched on at 04:27(7/11/20). |  |  |  |  | from 04:08 to 04:27(7/11/20).
l) Megnaghat-Shyampur 230 kV Ckt-2 is under shut down since 07:17(7/11/20) for A/M.
m) Kabirpur-Kaliakoir 132 kV Ckt-1 is under shut down since 06:02(7/11/20) for D/W.
n) Netrokona 132/33 kv T-3 transformer is under shut down since 06:30(7/11/20) for C/M.
o) Khulna© 132/33 kV T-3 is under shut down since 07:34(7/11/20) for A/M.
p) Kulaura 32/33 kV T-2 is under shut down since 07:22(7/11/20) for A/M.
q) Khulna(S) 132/33 kV T-3 is under shut down since 07:51(7/11/20) for A/M.
r) Benapole 132 kV Bus-A is under shut down since 07:51(7/11/20) for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-11-06 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 120 | 2694000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 115 | 2772000 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 4794573 | Machin problem.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 51 | 673272 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 317 | 6633000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 8223750 | Frequency control
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 14400 | Reserve.
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 132 | 3269178 | GT-2 under shut down
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 27840 | Reserve.
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 39200 | Reserve.
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 16 | 89316 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 150 | 2107000 | Frequency control
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 24000 | Reserve.
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under Maintenance
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 7 | 128592 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel Shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 439560 | Low demand
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 20160 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 20288 | Reserve.
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 64391 | Reserve.
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 49 | 1165020 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 28 | 601100 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 695200
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 32220 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 55200 | Reserve.
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 45792 | Reserve.
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 36 | 869304 | Low demand
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 53 | 239040 | Low demand
| Manikgonj 162MW PP |  | IPP | 9*18 | 0 | 0 | 110880
| Dhaka area Total |  |  |  | 5895 | 1716 | 35848276
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2800000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve.
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 108540
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 164640
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 160 | 3432524 | Unit-2 under maint
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 125 | 2746638
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 60983 | Reserve.
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 60 | 508800 | Low demand
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 472944
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 1032480
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 18240 | Reserve.
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 29880
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 51 | 391418 | Transformer O/L
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 586650
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 60 | 823680 | Low demand
| Chattogram area Total |  |  |  | 2266 | 742 | 13177417
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 30 | 227378 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 1365510 | Gas Shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 163 | 3821000 | Gas shortage.
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 275 | 6428000 | Gas Shortage
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 6233000 | Gas Shortage
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 5 | 274392 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 2 | 61920 | Gas shortage
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 690695
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 132145 | Reserve.
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 73 | 1341020 | ST Under maint
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve.
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 430308
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 5 | 88200 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 94 | 1902720
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 330700
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 18115 | Reserve.
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 339250 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Under maint.
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 45 | 185640 | Low demand
| Cumilla Area Total |  |  |  | 2980 | 1095 | 24070720
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 159 | 3279000 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 309636
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 25 | 589440 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12850
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 7 | 192000
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 943200 | #REF!
| Mymensingh PV 50 MW Solar PP |  | IPP | 50 | 0 | 0 | 319280
| Mymensingh Area Total |  |  |  | 637 | 328 | 5645406
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 579000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 588120 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2751218 | ST Under maint
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 159 | 3370000 | FGMO & GT-2 under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 47 | 379200
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 47 | 451080
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 57000 | Engine problem
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 69 | 1183680 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 87 | 586560
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 157 | 3525480
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 113000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 105466
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7035450 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 338 | 7202000
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 50940
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1451 | 27978194
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 908 | 20049455
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 119040 | Reserve.
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 1280 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 345 | 7575840 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Reserve.
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 441120
107 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1358 | 28186735
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 134400 | Line O/L
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 25 | 480900 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 88 | 768476 | Engine problem
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 400 | 7914500
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 0 | 752730
| Barisal Area Total |  |  |  | 1054 | 529 | 10051006
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 70 | 1449000 | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 34640 | Reserve.
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel Shortage
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 90 | 2466700 | STG under rmaint.
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 200 | 3899864 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 204 | 3960182 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 0 | 0 | Under maint.
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 24029 | Reserve.
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 141120 | Engine problem
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 9 | 58068
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 171073
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve.
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 65456 | Reserve.
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 0 | Reserve.
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 106752 | Reserve.
| Rajshahi Area Total |  |  |  | 2183 | 606 | 12376884
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3679500 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 0 | 61440
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 30854
| Rangpur Area Total |  |  |  | 605 | 150 | 3771794
| Total |  |  |  | 19892 | 7975 | 161106432
| Eastern Grid Total |  |  |  | 13766 | 5332 | 106720013
| Western Grid Total |  |  |  | 6126 | 2643 | 54386419
| National Grid Total |  |  |  | 19892 | 7975 | 161106432
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-11-06
| (a) ENTIRE EASTERN GRID : |  | 5033 | MW | (b) ENTIRE WESTERN GRID : |  | 2413 | MW
| i) Dhaka area |  | 2599 | MW | i) Khulna area |  | 936 | MW
| ii) Chittagong area |  | 848 | MW | ii) Rajshahi area |  | 758 | MW
| iii) Comilla area |  | 655 | MW | iii) Barisal area |  | 236 | MW
| iv) Mymensingh area |  | 611 | MW | iv) Rangpur area |  | 483 | MW
| v) Sylhet area |  | 320 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 7446 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 90 | 18:00 | Sherpur | 76 | 18:00 | Jhenida | 73 | 18:00
| Munsiganj | 82 | 20:00 | Srimongal | 35 | 18:00 | Bottail | 76 | 18:00
| Sonargaon | 54 | 2:00 | Shahjibazar | 79 | 18:00 | G.K Project | 32 | 18:00
| Shyampur | 164 | 10:00 | Fenchuganj | 27 | 18:00 | Faridpur | 117 | 0.8125
| Bhulta | 149 | 1:00 | Kulawara | 30 | 19:30 | Madaripur | 59 | 0.83333
| Madanganj | 53 | 2:00 | Sylhet | 83 | 18:00 | Sariatpur | 40 | 21:00
| Shitalakhya | 76 | 1:00 | Chatak | 19 | 18:00 | Gopalganj | 56 | 18:30
| Rahim steel | 4 | 6:00 | Sunamganj | 28 | 18:00 | Bagerhat | 73 | 18:30
| Matuail | 60 | 1:00 | Biani Bazar | 39 | 18:30 | Mongla | 30 | 1:00
| Ghorasal | 50 | 18:30 | Comilla (S) | 96 | 19:00 | Satkhira | 70 | 0.75
| Narsingdi | 117 | 20:00 | Comilla(N) | 61 | 18:30 | Gallamari | 35 | 13:00
| Haripur (SBU) | 75 | 3:00 | Chandpur | 65 | 21:00 | Magura | 34 | 0.75
| Ullon | 54 | 18:00 | Feni | 77 | 20:00 | Norail | 26 | 18:00
| Hasnabad | 125 | 18:30 | Chowmuhani | 104 | 18:00 | Chuadanga | 61 | 18:00
| Magbazar | 61 | 12:00 | Ashuganj | 37 | 20:00 | Barisal(N) | 29 | 0.83333
| Maniknagar | 60 | 18:00 | Daudkandi | 90 | 19:30 | Barisal (S) | 68 | 0.875
| Bangabhaban | 12 | 17:00 | B.Baria | 101 | 19:30 | Patuakhali | 77 | 0.875
| Narinda | 52 | 13:00 | Ramganj | 64 | 18:30 | Bhandaria | 40 | 0.8125
| Dhanmondi | 81 | 18:00 | Chaddagram | 23 | 19:30 | Borhan Uddin | 27 | 21:00
| Lalbag | 58 | 1:00 | PHP | 9 | 19:30 | Ishurdi | 39 | 18:30
| Madartek | 49 | 18:00 | Madunaghat | 37 | 18:00 | Ruppur Paromanobik | 2 | 1:00
| Dhaka University |  |  | Hathazari | 67 | 0.75 | Natore | 70 | 19:00
| Fatullah | 32 | 0.041667 | Khulshi | 140 | 0.041667 | Bogra | 111 | 19:00
| Mirpur | 70 | 18:30 | Halishahar | 90 | 0.75 | Noagaon | 75 | 19:00
| Kalyanpur | 66 | 18:00 | Baraulia | 118 | 0.083333 | Rajshahi | 89 | 18:30
| Gulshan | 72 | 18:00 | Sikalbaha | 18 | 0.77083 | Rajshahi New | 9 | 18:30
| Uttara | 68 | 18:00 | Dohazari | 57 | 0.75 | C.Nawabganj | 46 | 20:00
| Uttara New | 21 | 18:00 | Cox'sbazar | 77 | 0.75 | Amnura | 30 | 18:00
| Kamrangirchar | 54 | 18:00 | Chandraghona | 22 | 0.75 | Pabna | 72 | 19:30
| Savar | 77 | 18:30 | Kaptai | 4 | 0.75 | Shahjadpur | 62 | 18:00
| Bhasantec | 102 | 18:30 | A. Khaer Stl. | 0 | 0.041667 | Serajganj | 51 | 18:00
| Agargaon | 46 | 18:30 | Bakulia | 78 | 0.5 | Niyamatpur | 36 | 18:00
| Satmosjid | 70 | 18:30 | Julda | 18 | 0.041667 | Joypurhat | 37 | 18:00
| Tongi | 60 | 0.45833 | TK chemical | 19 | 0.75 | Sherpur(Bogura) | 32 | 18:30
| Kabirpur | 136 | 18:00 | Modern Steel | 12 | 0.041667 | Mohastangor | 32 | 18:30
| Basundhara | 92 | 18:00 | Shahmirpur | 14 | 0.083333 | Rangpur | 92 | 18:00
| Manikganj | 52 | 19:30 | Khagrachhari | 18 | 0.77083 | Lalmonirhat | 48 | 18:00
| Joydevpur | 88 | 18:30 | Matarbari | 27 | 0.79167 | Saidpur | 70 | 19:00
| New Tongi | 58 | 1:00 | Baroiar Hat | 24 | 0.75 | Purbasadipur | 70 | 18:30
| Kodda | 130 | 19:00 | Rangamati | 10 | 0.75 | Thakurgaon | 54 | 18:30
| Dhamrai | 50 | 19:30 | Abul Khair 230 | 139 | 0.375 | Palashbari | 75 | 18:30
| Rajendrapur | 64 | 18:30 | BSRM | 107 | 0.29167 | Barapukuria | 32 | 19:00
| Valuka | 60 | 1:00 | GPH Ispat | 60 | 0.58333 | Panchagar | 41 | 18:00
| Tangail | 127 | 18:30 | Goalpara | 17 | 0.041667 | Joldhaka | 17 | 19:00
| Mymensing | 143 | 18:00 | Central s/s | 54 | 18:00 | Kurigram | 39 | 18:00
| Kishorganj | 78 | 18:00 | Noapara | 33 | 18:30
| Netrokona | 75 | 18:00 | Jessore | 78 | 18:30
| Jamalpur | 86 | 18:00 | Benapol | 28 | 18:30
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-11-06 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 413 | 18:00 | 406 | 2:00 | Kaliakoir | 409 | 0.625 | 396 | 0.041667
| Bheramara | 406 | 18:00 | 391 | 18:00 | Bhulta | 385 | 0.75 | 369 | 0.95833
| Ashuganj(N) | 393 | 18:00 | 375 | 24:00 | Gopalganj | 426 | 0.29167 | 409 | 0.83333
| Payra | 420 | 18:00 | 408 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 230 | 1:00 | Comilla (N) | 237 | 18:00 | 230 | 1:00
| Ishurdi | 237 | 6:00 | 228 | 12:00 | Hathazari | 230 | 18:00 | 220 | 12:00
| Ashuganj | 240 | 18:00 | 230 | 11:00 | Megnaghat | 228 | 20:00 | 224 | 8:00
| Serajganj | 231 | 2:00 | 228 | 12:00 | Fenchuganj | 245 | 18:00 | 240 | 4:00
| Baghabari | 240 | 5:00 | 238 | 1:00 | Siddhirganj | 232 | 18:00 | 224 | 11:00
| Barapukuria | 231 | 6:00 | 226 | 19:00 | Maniknagar | 231 | 18:00 | 222 | 12:00
| Bogra | 231 | 5:00 | 222 | 20:00 | Agargaon | 228 | 18:00 | 218 | 12:00
| Rajshahi | 229 | 6:00 | 219 | 20:00 | Barisal | 248 | 20:00 | 236 | 12:00
| Khulna South | 230 | 17:00 | 222 | 23:00 | AKSML | 225 | 18:00 | 215 | 16:00
| Rampura | 228 | 8:00 | 222 | 1:00 | BSRM | 229 | 17:00 | 216 | 16:00
| Haripur | 229 | 18:30 | 222 | 12:00 | Bibiyana | 245 | 18:00 | 238 | 2:00
| Hasnabad | 227 | 18:00 | 215 | 10:00 | Bhulta | 232 | 19:00 | 224 | 17:00
| Shyampur | 230 | 18:00 | 220 | 11:00 | Ashuganj (S) | 236 | 19:00 | 227 | 12:00
| Aminbazar | 224 | 5:00 | 214 | 11:00 | Kaliakoir | 229 | 18:00 | 222 | 12:00
| Tongi | 223 | 18:00 | 214 | 11:00 | GPH | 219 | 18:00 | 217 | 1:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 139 | 18:00 | 133 | 11:00 | Hathazari | 137 | 0.75 | 130 | 0.5
| Munsiganj | 139 | 18:00 | 130 | 11:00 | Khulshi | 135 | 0.8125 | 127 | 0.5
| Sonargaon | 136 | 21:00 | 132 | 3:00 | Halishahar | 137 | 0.75 | 127 | 0.5
| Shyampur | 135 | 18:00 | 130 | 2:00 | Baraulia | 136 | 0.75 | 128 | 0.58333
| Bhulta | 132 | 18:00 | 128 | 1:00 | Sikalbaha | 137 | 0.75 | 129 | 0.45833
| Madanganj | 133 | 21:00 | 128 | 11:00 | Dohazari | 135 | 0.75 | 125 | 0.95833
| Shitalakhya | 142 | 18:00 | 128 | 13:00 | Cox'sbazar | 129 | 0.375 | 119 | 0.5
| Rahim steal | 138 | 18:30 | 133 | 1:00 | Chandraghona | 137 | 0.75 | 130 | 0.5
| Matuail | 139 | 18:00 | 133 | 11:00 | Kaptai | 137 | 0.75 | 132 | 0.16667
| Ghorasal | 138 | 8:00 | 136 | 11:00 | A. Khaer Stl. | 135 | 0.75 | 127 | 0.5
| Narsinghdi | 135 | 18:00 | 127 | 4:00 | Bakulia | 136 | 0.75 | 127 | 0.45833
| Haripur (SBU) | 137 | 21:00 | 133 | 11:00 | Julda | 137 | 0.75 | 129 | 0.375
| Ullon | 135 | 18:00 | 130 | 12:00 | TK Chemical | 137 | 0.75 | 129 | 0.625
| Hasnabad | 138 | 18:00 | 127 | 12:00 | Modern Steel | 136 | 0.75 | 128 | 0.45833
| Magbazar | 135 | 5:00 | 130 | 12:00 | Shahmirpur | 137 | 0.75 | 127 | 0.5
| Maniknagar | 138 | 18:00 | 134 | 11:00 | Khagrachhari | 136 | 0.77083 | 130 | 0.54167
| Bangabhaban | 138 | 18:00 | 134 | 11:00 | Matarbari | 130 | 0.75 | 121 | 0.91667
| Narinda | 138 | 18:00 | 134 | 11:00 | Baroiar Hat | 133 | 0.75 | 128 | 0.45833
| Dhanmondi | 135 | 18:00 | 130 | 12:00 | Rangamati | 136 | 0.75 | 130 | 0.625
| Lalbag | 139 | 18:00 | 133 | 12:00 | Goalpara S/S | 138 | 6:00 | 132 | 12:00
| Madartek | 135 | 18:00 | 130 | 12:00 | Khulna Central S/S | 139 | 6:00 | 130 | 0.5
| Dhaka University |  |  |  |  | Noapara | 137 | 5:00 | 129 | 0.54167
| Fatuiiah | 137 | 18:00 | 131 | 1:00 | Jessore | 136 | 6:00 | 126 | 0.54167
| Mirpur | 139 | 18:00 | 133 | 12:00 | Benapol | 135 | 0.25 | 127 | 0.83333
| Kalyanpur | 140 | 18:00 | 134 | 12:00 | Jhenida | 134 | 5:00 | 126 | 0.79167
| Gulshan | 135 | 18:00 | 130 | 12:00 | Bottail | 137 | 0.125 | 132 | 0.8125
| Uttara | 138 | 18:00 | 131 | 11:00 | G.K Project | 141 | 0.29167 | 138 | 0.79167
| Uttara New | 138 | 18:30 | 133 | 12:00 | Faridpur | 138 | 0.41667 | 134 | 0.83333
| Kamrangirchar | 137 | 18:00 | 126 | 12:00 | Madaripur | 139 | 0.125 | 134 | 0.54167
| Savar | 139 | 18:00 | 132 | 12:00 | Shariyatpur S/S | 139 | 4:00 | 135 | 0.5
| Bhasantec | 139 | 18:00 | 132 | 12:00 | Gopalganj | 142 | 0.25 | 137 | 0.041667
| Agargaon | 140 | 18:00 | 133 | 12:00 | Bagerhat | 139 | 6:00 | 122 | 0.54167
| Satmosjid | 139 | 18:00 | 133 | 12:00 | Mongla | 136 | 6:00 | 121 | 0.70833
| Tongi | 139 | 18:00 | 135 | 11:00 | Satkhira | 138 | 1:00 | 130 | 13:00
| Kabirpur | 139 | 7:00 | 131 | 14:00 | Gallamari | 139 | 0.25 | 131 | 0.5
| Basundhara | 135 | 18:00 | 130 | 12:00 | Magura | 135 | 6:00 | 125 | 0.54167
| Manikganj | 141 | 18:00 | 134 | 11:00 | Norail | 133 | 0.25 | 126 | 0.77083
| Joydevpur | 140 | 18:00 | 136 | 13:00 | Chuadanga | 132 | 6:00 | 122 | 0.83333
| New Tongi | 140 | 18:00 | 133 | 11:00 | Barisal(N) | 138 | 3:00 | 133 | 12:00
| Kodda | 139 | 18:00 | 129 | 12:00 | Barisal (S) | 138 | 0.75 | 132 | 0.66667
| Dhamrai | 137 | 21:00 | 133 | 1:00 | Patuakhali(S) | 136 | 0.16667 | 129 | 0.70833
| Rajendrapur | 135 | 18:30 | 126 | 13:00 | Bhandaria | 137 | 0.20833 | 125 | 0.54167
| Valuka | 131 | 18:00 | 116 | 13:00 | Ishurdi | 138 | 1:00 | 135 | 12:00
| Tangail | 136 | 22:00 | 107 | 13:00 | Ruppur Paromanobik | 137 | 6:00 | 134 | 1:00
| Mymensing | 133 | 18:30 | 116 | 13:00 | Natore | 138 | 1:00 | 134 | 19:00
| Kishorganj | 132 | 18:00 | 121 | 13:00 | Bogra | 138 | 4:00 | 132 | 20:00
| Netrokona | 131 | 18:00 | 117 | 17:00 | Noagaon | 134 | 5:00 | 130 | 12:00
| Jamalpur | 139 | 18:30 | 117 | 13:00 | Rajshahi | 138 | 1:00 | 133 | 12:00
| Sherpur | 138 | 18:00 | 119 | 13:00 | Rajshahi New | 139 | 2:00 | 133 | 12:00
| Srimongal | 140 | 18:00 | 135 | 1:00 | C.Nawabganj | 138 | 18:00 | 132 | 12:00
| Shahjibazar | 137 | 18:00 | 131 | 13:00 | Amnura | 138 | 18:30 | 131 | 12:00
| Fenchuganj | 139 | 22:00 | 134 | 2:00 | Pabna | 137 | 4:00 | 134 | 1:00
| Khulawara | 138 | 18:00 | 134 | 13:00 | Shahjadpur | 142 | 4:00 | 140 | 1:00
| Sylhet | 136 | 13:00 | 134 | 1:00 | Serajganj | 135 | 1:00 | 134 | 12:00
| Chatak | 135 | 18:00 | 132 | 13:00 | Niyamatpur | 134 | 4:00 | 127 | 20:00
| Sunamganj | 134 | 18:00 | 132 | 1:00 | Joypurhat | 136 | 4:00 | 131 | 12:00
| Biani Bazar | 135 | 10:00 | 132 | 13:00 | Sherpur(Bogura) | 138 | 6:00 | 133 | 19:30
| Comilla(s) | 128 | 1:00 | 126 | 12:00 | Mohastangor | 137 | 3:00 | 131 | 20:00
| Comilla(n) | 140 | 18:00 | 134 | 13:00 | Rangpur | 129 | 5:00 | 121 | 19:00
| Chandpur | 135 | 7:00 | 130 | 18:00 | Lalmonirhat | 130 | 2:00 | 120 | 18:00
| Feni | 136 | 18:00 | 130 | 0:00 | Saidpur | 132 | 4:00 | 122 | 18:00
| Chowmuhani | 130 | 19:00 | 126 | 13:00 | Purbasadipur | 129 | 6:00 | 119 | 20:00
| Ashuganj | 136 | 18:00 | 132 | 17:00 | Thakurgaon | 129 | 3:00 | 118 | 18:00
| Daudkandi | 136 | 18:00 | 132 | 12:00 | Palashbari | 133 | 6:00 | 125 | 20:00
| B.Baria | 133 | 7:00 | 129 | 17:00 | Barapukuria | 131 | 6:00 | 126 | 19:00
| Ramganj | 129 | 19:30 | 121 | 16:00 | Panchagar | 128 | 3:00 | 115 | 18:00
| Chaddagram | 137 | 18:30 | 128 | 12:00 | Joldhaka | 130 | 5:00 | 119 | 20:00
| PHP | 135 | 18:30 | 128 | 12:00 | Kurigram | 129 | 5:00 | 120 | 18:00
| Madanhat | 139 | 18:00 | 131 | 12:00

## L-Curve
Date | 2020-11-06
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 558 | 4187 | 2466 | 6653 |  |  |  | QF-LDC-11
0:30 | 453.5 | 4476 | 2373.5 | 6849.5 | Date: | 2020-11-06
1:00 | 349 | 4765 | 2281 | 7046
1:30 | 378 | 4599.5 | 2245 | 6844.5
2:00 | 407 | 4434 | 2209 | 6643
2:30 | 394.5 | 4417 | 2165.5 | 6582.5 | [5 empty] | Gen. at Eve. Peak | 7975 | 7975 MW (20:00 )
3:00 | 382 | 4400 | 2122 | 6522 | [6 empty] | 20:00
3:30 | 380 | 4331.5 | 2074 | 6405.5 | [5 empty] | Gen. at Day Peak | 6269 | 6269 MW (12:00 )
4:00 | 378 | 4263 | 2026 | 6289 | [6 empty] | 12:00
4:30 | 354 | 4214 | 1986 | 6200 | [5 empty] | Highest Generation | 7975
5:00 | 330 | 4165 | 1946 | 6111 | [6 empty] | 20:00
5:30 | 313 | 4137 | 1910.5 | 6047.5
6:00 | 296 | 4109 | 1875 | 5984
6:30 | 214.5 | 4066.5 | 1828.5 | 5895
7:00 | 133 | 4024 | 1782 | 5806
7:30 | 124.5 | 4044.5 | 1846.5 | 5891
8:00 | 116 | 4065 | 1911 | 5976
8:30 | 208 | 4032 | 1895.5 | 5927.5
9:00 | 300 | 3999 | 1880 | 5879
9:30 | 360 | 3922.5 | 1889.5 | 5812
10:00 | 420 | 3846 | 1899 | 5745
10:30 | 433.5 | 3865 | 1958 | 5823
11:00 | 447 | 3884 | 2017 | 5901
11:30 | 462.5 | 3991 | 2094 | 6085
12:00 | 478 | 4098 | 2171 | 6269
12:30 | 439 | 4244.5 | 2207 | 6451.5
13:00 | 400 | 4391 | 2243 | 6634
13:30 | 448 | 4234 | 2221.5 | 6455.5
14:00 | 496 | 4077 | 2200 | 6277
14:30 | 518 | 4029 | 2181.5 | 6210.5
15:00 | 540 | 3981 | 2163 | 6144
15:30 | 526.5 | 3950 | 2093 | 6043
16:00 | 513 | 3919 | 2023 | 5942
16:30 | 467.5 | 3959 | 2044.5 | 6003.5
17:00 | 422 | 3999 | 2066 | 6065
17:30 | 229 | 4584.5 | 2286 | 6870.5
18:00 | 36 | 5170 | 2506 | 7676
18:30 | 25.5 | 5228 | 2510.5 | 7738.5
19:00 | 15 | 5286 | 2515 | 7801
19:30 | 13 | 5309 | 2589 | 7898
20:00 | 70 | 5332 | 2643 | 7975 |  |  |  | Executive Engineer
20:30 | 125 | 5272.5 | 2650.5 | 7923 |  |  |  | Network Operation Division
21:00 | 180 | 5213 | 2658 | 7871
21:30 | 250 | 5040 | 2617.5 | 7657.5
22:00 | 320 | 4867 | 2577 | 7444 |  |  |  |  | Page 6 of 7
22:30 | 405 | 4710 | 2562.5 | 7272.5
23:00 | 490 | 4553 | 2548 | 7101
23:30 | 524 | 4370 | 2507 | 6877
24:00 | 558 | 4187 | 2466 | 6653
7975 MW (20:00 )
6269 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-11-06 |  | Energy | 161106432
[10 empty] | 2020-11-06 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3440 | 909 | 1346 | 243 | 529 | 162 | 0 | 0 | 80
0:30 | 3554 | 813 | 1290.5 | 411.5 | 564.5 | 161 | 0 | 0 | 83 | Date: | 2020-11-06
1:00 | 3668 | 717 | 1235 | 580 | 600 | 160 | 0 | 0 | 86
1:30 | 3598.5 | 717 | 1227.5 | 458.5 | 599 | 160 | 0 | 0 | 84 | [7 empty] | Total Energy | 161.1064 | Total Energy Gen 161.106 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 161.106 MKWHr
2:00 | 3529 | 717 | 1220 | 337 | 598 | 160 | 0 | 0 | 82 | [7 empty] | Energy not Served | 0
2:30 | 3508 | 717 | 1213.5 | 329.5 | 573.5 | 160 | 0 | 0 | 81 | [7 empty] | Energy Requirement | 161.1064
3:00 | 3487 | 717 | 1207 | 322 | 549 | 160 | 0 | 0 | 80
3:30 | 3383.5 | 717 | 1203.5 | 317 | 549 | 157.5 | 0 | 0 | 78 | [6 empty] | Shortage
4:00 | 3280 | 717 | 1200 | 312 | 549 | 155 | 0 | 0 | 76
4:30 | 3265.5 | 716.5 | 1162 | 302 | 524 | 155 | 0 | 0 | 75
5:00 | 3251 | 716 | 1124 | 292 | 499 | 155 | 0 | 0 | 74
5:30 | 3222 | 716.5 | 1128.5 | 284.5 | 469 | 155 | 0 | 0 | 72
6:00 | 3193 | 717 | 1133 | 277 | 439 | 155 | 0 | 0 | 70
6:30 | 3134.5 | 717 | 1114 | 285 | 419 | 154.5 | 0 | 0 | 67 |  |  |  |  | Coal
7:00 | 3076 | 717 | 1095 | 293 | 399 | 154 | 0 | 0 | 64
7:30 | 3140 | 717 | 1098 | 301 | 399.5 | 155.5 | 0 | 0 | 64 |  |  |  | Oil |  |  |  | ,
8:00 | 3204 | 717 | 1101 | 309 | 400 | 157 | 0 | 0 | 64
8:30 | 3136.5 | 717 | 1090 | 332 | 400 | 157.5 | 0 | 0 | 63
9:00 | 3069 | 717 | 1079 | 355 | 400 | 158 | 0 | 0 | 62
9:30 | 3023 | 763 | 1034 | 317 | 400 | 159 | 0 | 0 | 62
10:00 | 2977 | 809 | 989 | 279 | 400 | 160 | 0 | 0 | 62
10:30 | 2972.5 | 858.5 | 1054 | 261 | 400 | 137.5 | 0 | 0 | 65
11:00 | 2968 | 908 | 1119 | 243 | 400 | 115 | 0 | 0 | 68
11:30 | 3075 | 908 | 1184.5 | 250.5 | 400 | 115 | 0 | 0 | 71
12:00 | 3182 | 908 | 1250 | 258 | 400 | 115 | 0 | 0 | 74
12:30 | 3324 | 908 | 1293.5 | 254.5 | 400 | 115.5 | 0 | 0 | 77
13:00 | 3466 | 908 | 1337 | 251 | 400 | 116 | 0 | 0 | 80
13:30 | 3466 | 908 | 1337 | 251 | 400 | 116 | 0 | 0 | 80
14:00 | 3466 | 908 | 1337 | 251 | 400 | 116 | 0 | 0 | 80
14:30 | 3352.5 | 908 | 1212 | 267 | 400 | 115.5 | 0 | 0 | 75
15:00 | 3239 | 908 | 1087 | 283 | 400 | 115 | 0 | 0 | 70
15:30 | 3180.5 | 908 | 1054 | 285 | 400 | 115 | 0 | 0 | 71
16:00 | 3122 | 908 | 1021 | 287 | 400 | 115 | 0 | 0 | 72
16:30 | 3123.5 | 908 | 1035.5 | 327 | 400 | 120 | 8.5 | 0 | 72
17:00 | 3125 | 908 | 1050 | 367 | 400 | 125 | 17 | 0 | 72
17:30 | 3250.5 | 908 | 1213.5 | 808 | 425 | 125.5 | 56.5 | 0 | 83
18:00 | 3376 | 908 | 1377 | 1249 | 450 | 126 | 96 | 0 | 94
18:30 | 3484.5 | 908 | 1427.5 | 1168.5 | 465 | 143 | 48 | 0 | 94
19:00 | 3593 | 908 | 1478 | 1088 | 480 | 160 | 0 | 0 | 94
19:30 | 3652 | 908 | 1541 | 1021 | 520 | 160 | 0 | 0 | 96
20:00 | 3800 | 908 | 1630 | 833 | 550 | 160 | 0 | 0 | 94
20:30 | 3825 | 907.5 | 1630 | 749.5 | 555 | 161 | 0 | 0 | 95
21:00 | 3850 | 907 | 1630 | 666 | 560 | 162 | 0 | 0 | 96
21:30 | 3849 | 908 | 1607.5 | 493 | 545 | 162 | 0 | 0 | 93
22:00 | 3848 | 909 | 1585 | 320 | 530 | 162 | 0 | 0 | 90
22:30 | 3737.5 | 909 | 1565 | 281.5 | 529.5 | 162 | 0 | 0 | 88
23:00 | 3627 | 909 | 1545 | 243 | 529 | 162 | 0 | 0 | 86
23:30 | 3533.5 | 909 | 1445.5 | 243 | 529 | 162 | 0 | 0 | 83 | Max Temp. in Dhaka |  | 31° C
24:00 | 3440 | 909 | 1346 | 243 | 529 | 162 | 0 | 0 | 80
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 161.106 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 161.106 MKWHr
Note on W13: Author:

## Generation
g | 2020-11-06
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 90 | 90 | 90 | 85 | 85 | 85 | 84 | 87 | 88 | 90 | 80 | 80 | 81 | 81 | 80 | 80 | 90 | 91 |  | 90 | 90 | 90 | 92 | 92 | 92 | 92 | 2016524
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1416000
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 2 |  |  | 16 | 19 | 20 | 19 | 16 | 12 | 6 | 0 | [9 empty] | 108540
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 145 | 142 | 140 | 139 | 139 | 140 | 120 | 120 | 100 | 70 | 70 | 70 | 140 | 107 | 70 | 70 | 70 | 104 |  | 106 | 104 | 125 | 139 | 139 | 144 | 143 | 2746638
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 51 | [7 empty] | 0 | 60983
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 93 | 91 | 85 | 83 | 69 | 40 | 69 | 65 | 67 | 37 | 38 | 82 | 82 | 37 | 37 | 37 | 38 | 70 |  | 120 | 120 | 150 | 145 | 145 | 145 | 70 | 2107000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [17 empty] | 31 | [7 empty] | 0 | 55200
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 0 |  | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 150 | 98 | 107 | 98 | 99 | 100 | 100 | 100 | 100 | 120 | 100 | 100 | 120 | 117 | 120 | 130 | 113 | 116 |  | 120 | 120 | 120 | 120 | 120 | 112 | 120 | 2694000
23 | Ghorasal TPP Unit-5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2772000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4794573
26
28 | Ashuganj TPP Unit- 3 | [19 empty] | 10 | 15 | 30 | 50 | 55 | 60 | 65 | 227378
29 | Ashuganj TPP Unit- 4 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 65 | [5 empty] | 1365510
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 274392
33 | Ashuganj 225 MW CCPP | 165 | 163 | 162 | 162 | 162 | 162 | 143 | 141 | 141 | 141 | 142 | 142 | 141 | 141 | 142 | 141 | 141 | 179 |  | 155 | 129 | 163 | 175 | 180 | 218 | 179 | 3821000
34 | Ashuganj 450 MW CCPP(South) | 250 | 250 | 250 | 250 | 250 | 250 | 230 | 230 | 230 | 230 | 230 | 230 | 270 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 6233000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 250 | 250 | 265 | 265 | 285 | 295 | 270 | 260 | 275 | 280 | 295 | 265 |  | 310 | 290 | 275 | 275 | 270 | 0 | 0 | 6428000
35 | Ashuganj 55 MW PP (Precision) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 61920
36 | Chandpur 150 MW CCPP | 50 | 50 | 51 | 50 | 50 | 50 | 50 | 50 | 50 | 70 | 50 | 50 | 50 | 50 | 50 | 50 | 51 | 70 |  | 73 | 73 | 73 | 74 | 70 | 70 | 70 | 1341020
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 340 | 350 | 350 | 370 | 350 | 330 | 300 | 300 | 320 | 280 | 300 | 360 | 380 | 300 | 280 | 280 | 280 | 350 |  | 350 | 350 | 400 | 400 | 400 | 400 | 400 | 8223750
41 | Haripur 360MW CCPP(HPL) | 293 | 321 | 293 | 258 | 259 | 253 | 253 | 254 | 260 | 226 | 309 | 327 | 348 | 227 | 227 | 227 | 227 | 257 |  | 288 | 287 | 317 | 318 | 319 | 319 | 318 | 6633000
42 | RPCL 210MW CCPP | 108 | 129 | 130 | 129 | 129 | 148 | 147 | 149 | 128 | 127 | 125 | 122 | 124 | 124 | 154 | 154 | 155 | 161 |  | 158 | 160 | 159 | 161 | 163 | 162 | 162 | 3279000
43 | Mymensingh PV 50 MW Solar PP | [6 empty] | 5 | 20 | 33 | 44 | 49 | 50 | 46 | 37 | 24 | 9 | 1 | [9 empty] | 319280
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 579000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 588120
46 | Shajibazar 330 MW CCPP | 156 | 160 | 159 | 157 | 157 | 158 | 133 | 134 | 132 | 135 | 135 | 133 | 159 | 159 | 158 | 157 | 157 | 158 |  | 158 | 157 | 159 | 158 | 159 | 158 | 158 | 3370000
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 40 | 53 | 40 | 40 | 40 | 40 | 65 | 65 | 63 | 51 | 40 | 40 | 40 | 40 |  | 40 | 40 | 69 | 69 | 69 | 70 | 69 | 1183680
48 | Shahjibazar 86MW PP (Shahjibazar) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 87 |  | 87 | 87 | 87 | 87 | 50 | 20 | 5 | 586560
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 204 | 160 | 158 | 158 | 158 | 152 | 138 | 164 | 130 | 131 | 131 | 131 | 145 | 145 | 120 | 120 | 122 | 130 |  | 149 | 157 | 157 | 158 | 158 | 158 | 158 | 3525480
51 | Sylhet 20 MW GTPP | [16 empty] | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 0 | 113000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [17 empty] | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 0 | 50940
54 | Hobiganj 11MW PP Cofidence-E | [17 empty] | 5 |  | 8 | 11 | 11 | 11 | 11 | 11 | 0 | 57000
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 5 | 5 | 5 | 5 | 8 | 8 | 5 | 5 | 8 | 8 | 45 |  | 47 | 47 | 47 | 47 | 47 | 47 | 5 | 379200
56 | Shahjahanulla 25 MW PP | [14 empty] | 16 | 16 |  | 24 |  | 24 | 24 | 24 | 16 | 16 | 16 | 0 | 105466
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 265 | 280 | 290 | 255 | 290 | 280 | 290 | 250 | 230 | 260 | 310 | 320 | 270 | 280 | 270 | 290 | 260 |  | 260 | 315 | 315 | 280 | 270 | 270 | 290 | 7035450
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 4 | 35 | [7 empty] | 0 | 64391
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 472944
61 | Narshingdi 22 MW PP (Doreen) | [19 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 89316
62 | Tangail 22 MW PP (Doreen) | [6 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  |  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 309636
63 | Impoprt (Tripura) | 86 | 82 | 80 | 76 | 74 | 70 | 64 | 64 | 62 | 62 | 68 | 74 | 80 | 76 | 70 | 72 | 72 | 94 |  | 94 | 96 | 94 | 96 | 90 | 86 | 80 | 1902720
64 | Malancha, Ctg. EPZ (United) | 41 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 33 | 37 | 37 | 34 | 42 | 42 | 40 | 35 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 1032480
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 21 | 21 | 21 |  |  | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 430308
66 | Feni 11 MW PP (Doreen) | [11 empty] | 11 | 8 | 11 | 11 | 11 | 8 | 11 |  | 5 | 5 | 5 | 5 | 5 | 5 | 0 | 88200
67 | Jangalia 33MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [7 empty] | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 330700
68 | Cumilla 25 MW PP (Summit) | 15 | 15 | 12 | 12 | 12 |  | 8 | 8 | 8 | 8 | 10 | 10 | 10 | 10 | 12 | 12 | 12 | 12 |  | 19 | 19 | 20 | 21 | 18 | 15 | 15 | 339250
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 28 | 24 | 25 | 13 | 13 | 13 | 5 | 10 | 10 | 11 | 11 |  | 24 | 24 | 24 | 28 | 28 | 32 | 32 | 565020
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 |  | 20 |  | 16 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 601100
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 8 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 695200
73 | Ghorashal 108MW PP (Regent) | 51 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 40 | 51 | 12 | 12 | 12 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 673272
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | [17 empty] | 29 |  | 76 | 85 | 45 | 8 |  |  | 0 | 185640
| Manikgonj 162MW PP | [11 empty] | 5 | 9 | 11 | 13 | 33 | 33 | 17 | [8 empty] | 110880
77 | Siddhirganj 100 PP(Dutch Bangla) | [17 empty] | 14 | [7 empty] | 0 | 24000
78 | Gazipur 52 MW PP | [17 empty] | 12 |  | 16 | [6 empty] | 32220
79 | Kodda 150MW PP | [17 empty] | 16 | [7 empty] | 0 | 20160
80 | Jamalpur 95 MW PP(Powerpac) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 589440
81 | Jangalia 52 MW PP (Lakdanavi) | [17 empty] | 12 | [8 empty] | 18115
| Gazipur 100 MW PP | 52 | 17 | 17 | 17 | 17 | 17 | 42 | 52 | 52 | 35 | 35 | 35 | 35 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 17 | 869304
| Kaptai 7 MW Solar PP | [6 empty] | 1 | 2 | 3 | 4 | 5 | 5 | 4 | 3 | 2 | 1 | [10 empty] | 29880
| Jodiac Power | 54 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 38 |  | 54 | 54 | 54 | 54 |  |  | 0 | 586650
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | [17 empty] | 10 |  | 10 | [5 empty] | 0 | 27840
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP(Summit) | 145 | 140 | 130 | 140 | 140 | 145 | 140 | 125 | 133 | 140 | 140 | 150 | 130 | 132 | 130 | 122 | 140 | 110 |  | 145 | 145 | 132 | 132 | 120 | 120 | 120 | 3269178
87 | Meghnaghat 100 MW(IEL) | [17 empty] | 7 | [7 empty] | 0 | 14400
| Meghnaghat 104 MW PP (OPCL) | 17 | [18 empty] | 38 | 53 | 53 | 53 | 42 |  | 0 | 239040
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 23 |  | 47 | 47 | 47 | 47 | 47 | 47 | 5 | 451080
93 | Ashuganj 51 MW PP (Midland) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 32 | 15 | 15 | 15 | 25 |  | 51 | 51 | 51 | 51 | 51 | 51 | 5 | 690695
94 | Gagnagar 102 MW PP (Digital Power) | 7 | [15 empty] | 5 | 58 |  | 32 | 32 | 7 | 7 |  |  | 0 | 128592
95 | Patenga 50MW PP (Baraka) | 6 | 5 | [14 empty] | 0 | 14 |  | 40 | 50 | 50 | 45 |  |  | 0 | 164640
96 | Chattogram 108 MW PP (ECPV) | [17 empty] | 10 | [7 empty] | 0 | 18240
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | [16 empty] | 1 | 18 | [7 empty] | 0 | 39200
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 17 | [7 empty] | 0 | 20288
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2751218
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [10 empty] | 12850
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  | 5 | 17 | 17 | 17 | 17 | 54 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 439560
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [16 empty] | 2 | 62 |  | 40 | 40 | 7 | 7 |  |  | 0 | 192000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [17 empty] | 25 | [7 empty] | 0 | 45792
115 | Juldah 100 MW PP Unit-3 (Acorn) | 80 | 30 | 30 | 30 | 10 | 10 | 10 | 10 | 10 | [7 empty] | 10 | 60 |  | 60 | 60 | 60 | 30 |  |  | 0 | 508800
116 | Chandpur 200MW (Desh energy)
117 | Ashuganj 150MW PP (Midland) | [16 empty] | 2 | 38 |  | 30 | 30 |  |  |  |  | 0 | 132145
118 | Bibiyana-III 400 MW CCPP | 401 | 400 | 400 | 303 | 304 | 305 | 305 | 305 | 251 | 240 | 232 | 252 | 304 | 304 | 304 | 304 | 304 | 305 |  | 304 | 304 | 338 | 340 | 340 | 340 | 340 | 7202000
| Jamalpur 115 MW PP (United) | 8 | [5 empty] | 16 | 37 | 75 | 35 | 16 | 16 | 20 | 35 | 35 | 27 | 27 | 73 |  | 115 | 115 | 115 | 75 | 35 | 35 | 8 | 943200
| Anwara 300 MW PP (United) | 51 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | [7 empty] | 13 | 83 |  | 50 | 50 | 51 | 51 |  |  | 0 | 391418
| Juldah unit-2 (Acorn) | 100 | 70 | 70 | 50 | 50 | 30 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 60 |  | 60 | 60 | 60 | 40 | 10 | 10 | 0 | 823680
120 | Eastern Zone Total | 4765 | 4434 | 4400 | 4263 | 4165 | 4109 | 4024 | 4065 | 3999 | 3846 | 3884 | 4098 | 4391 | 4077 | 3981 | 3919 | 3999 | 5170 |  | 5286 | 5309 | 5332 | 5213 | 4867 | 4553 | 4187 | 106720013
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [16 empty] | 12 | 66 |  | 32 | 32 | [5 empty] | 119040
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [17 empty] | 105 |  | 105 | 105 | 105 | 70 | 35 |  | 0 | 441120
130
131
132
133 | Bhola Nutan Biddut BD LTD (GAS) | 36 | 35 | 37 | 35 | 36 | 35 | 36 | 36 | 38 | 42 | 35 | 36 | 35 | 35 | 36 | [7 empty] | 35 | 35 | 34 | 36 | 752730
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [16 empty] | 10 | 60 |  | 32 | 32 | 16 | 16 |  |  | 0 | 134400
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 22 | 23 | 22 | 22 | 0 | 0 | 0 | [5 empty] | 1 | 34 | 35 | 24 | 24 | 55 |  | 70 | 78 | 88 | 87 | 88 | 89 | 43 | 768476
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 23 | 22 | 21 | 21 | 20 | 21 | 19 | 17 | 16 | 12 | 16 | 18 | 18 | 19 | 19 | 17 | 19 | 24 |  | 25 | 26 | 25 | 25 | 25 | 24 | 23 | 480900
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 5 | [9 empty] | 1280
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 717 | 717 | 717 | 717 | 716 | 717 | 717 | 717 | 717 | 809 | 908 | 908 | 908 | 908 | 908 | 908 | 908 | 908 |  | 908 | 908 | 908 | 907 | 909 | 909 | 909 | 20049455
147 | Bheramara 410 MW CCPP | 345 | 360 | 345 | 275 | 275 | 275 | 220 | 260 | 270 | 240 | 260 | 380 | 345 | 345 | 340 | 285 | 285 | 285 |  | 290 | 290 | 345 | 340 | 340 | 345 | 340 | 7575840
148 | Payra 1320 MW | 450 | 450 | 400 | 400 | 350 | 290 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 300 |  | 330 | 370 | 400 | 410 | 380 | 380 | 380 | 7914500
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 148 | 149 | 149 | 149 | 149 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 149 | 149 | 3679500
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP | 60 | 60 | 60 | 60 | 50 | 50 | 50 | 70 | 70 | 50 | 50 | 50 | 70 | 50 | 50 | 50 | 50 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 50 | 1449000
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 153 | 100 | 77 | 73 | 73 | 73 | 70 | 90 | 90 | 75 | 75 | 75 | 100 | 100 | 100 | 70 | 70 | 70 |  | 70 | 70 | 90 | 135 | 150 | 150 | 150 | 2466700
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 158 | 159 | 159 | 139 | 142 | 130 | 136 | 152 | 139 | 130 | 130 | 153 | 171 | 146 | 134 | 130 | 130 | 137 |  | 157 | 211 | 200 | 178 | 177 | 182 | 183 | 3899864
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 153 | 130 | 130 | 130 | 130 | 130 | 130 | 163 | 130 | 130 | 130 | 138 | 182 | 151 | 130 | 130 | 130 | 137 |  | 159 | 205 | 204 | 193 | 179 | 181 | 187 | 3960182
Sirajgonj 225MW CCPP Unit-3 (Oil)
Sirajgonj 400 MW CCPP Unit-4
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | [13 empty] | 0 | 3 | 3 | 3 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 3 | 141120
163 | Bogura 20 MW PP (Energyprima) | 9 | [16 empty] | 7 |  | 9 | 9 | 9 | 9 | 9 | 8 | 8 | 58068
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 11 |  | 11 | 11 | 11 | 11 | 8 | 5 | 5 | 171073
165 | Amnura 50 MW PP(Sinha) | [16 empty] | 3 | 20 |  |  | 0 | [5 empty] | 34640
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [16 empty] | 8 | 29 | [7 empty] | 0 | 24029
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP | [16 empty] | 4 | [8 empty] | 0 | 65456
171 | Baghabari 200 MW PP (Paramount)
Bagura 113 MW PP (Confidence)-2
172 | Confidence Power Bogura Unit-1 113 MW | [17 empty] | 30 |  | 35 | [5 empty] | 0 | 106752
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | [17 empty] | 20 |  | 40 | [5 empty] | 0 | 61440
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 3 | 5 | 5 | 5 | 4 | 3 | 1 | 0 | [9 empty] | 30854
178
178