## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-11-13 | Friday
|  |  | Date (day): | 2020-11-13 |  | Friday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13029.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14216 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-11-12 | 2020-11-13 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 150 | 150 | 150 | 150
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 115 | 115 | 115 | 75 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 200 | 200 | 165 |  | Gas shortage
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 12 | 12 | 12 |  | 57 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under S/D for dust in gas.
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 283 | 267 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 320 | 300 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 94 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 150 | 150 | 150 | 150 |  | 150 | GT-1 Under maint.
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 40 | 80 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 30 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 50 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19 |  | 3 | Engine problem
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 85 | 32 | 100 | 100 | 110 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 50 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 94 | 94 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 100 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 56 | 56 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 17 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 33 | 51 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 15 | 296 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 15 | 138 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 101 | 101 | 100 | 100
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 90 | 90 | 90 | 90 |  | 14 | Engine problem
|  | Manikgonj 162MW PP |  | HFO | IPP | 9*18 | 0 | 0 | 77 | 0 | 0 | 0
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 2031 | 2686 | 3400 | 3740 | 692 | 1383
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 115 | 120 | 120 | 60 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 46 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 158 | 161 | 163 | 163 | 67 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 217 | 204 | 215 | 225
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 102 | 102
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 100 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 9 | 40 | 40
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 100 | 100 |  | 8 | Engine problem
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 82 | 160 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 915 | 1024 | 1724 | 1709 | 457 | 106
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 130 | 135 | 100 | 100 | 35 |  | Gas Shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 201 | 170 | 225 | 225 |  |  | FGMO
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 345 | 370 | 360 | 360 |  |  | FGMO
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 29 | 30 | 30 | 15 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 30 | 10 | 30 | 30 | 25 |  | Gas shortage
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 40 | 108 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 70 | 80 |  | 57 | ST Under maint.
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 165 | 180
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 88 | 118 | 156 | 172
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 25 | 33 | 33
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 52 | 52 | 52
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 20 | 20 | 21
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 17 | 114 | 114
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 55 | 113 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1100 | 1306 | 1710 | 2002 | 525 | 417
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 87 | 88 | 100 | 100 | 102 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 20 | 22 | 22
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 33 | 33 | 33 | 33 |  | 62 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 70 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 45 | 115 | 115 | 115
|  | Mymensingh PV 50 MW Solar PP |  | Solar | IPP | 50 | 0 | 0 | 54 | 0 | 50 | 0
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 221 | 326 | 521.6 | 470 | 102 | 62
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 44 | 41 | 44 | 44
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Unit-4 under shut down
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 107 | 107 | 110 | 110 |  | 54 | STG under maint.
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 160 | 159 | 160 | 160 |  | 170 | GT-2 S/D due to gas shortage.
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 50 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 46 | 49 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 11 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 40 | 66 | 66 |  |  | FGMO
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 84 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 218 | 217 | 220 | 220
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 280 | 341 | 341 |  |  | FGMO
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 404 | 402 | 400 | 400
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 50 | 40 | 40 | 40
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1535 | 1532 | 1626 | 1626 | 0 | 314
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 750 | 897 | 507 | 507
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 66 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 370 | 300 | 410 | 410
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 24 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 53 | 90 | 105 | 105
| 108 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1173 | 1377 | 1277 | 1703 | 0 | 0
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 32 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 22 | 28 | 22 | 22
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 23 | 88 | 95 | 95
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 400 | 660 | 600 | 660
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 35 | 35 | 35 | 35
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 480 | 843 | 862 | 922 | 0 | 194
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 40 | 50 | 70
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 75 | Gas shortage & ST Under maint
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 180 | 154 | 220 | 220 |  |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 165 | 167 | 220 | 220 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 418 | 296 | 413 | 413 |  | 414 | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 33
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 21 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 10 | 10 | 10 | 10
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 8 | 52 | 52
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 8 | 0 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 35 | 113 | 113
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 20 | 109 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 834 | 851 | 1574 | 1717 | 200 | 489
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 64 | 64 | 21 |  | Coal Shortage.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 39 | 98 | 113 | 113
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 195 | 248 | 335 | 327 | 230 | 40
|  | Total |  |  |  |  | 20383 | 19892 | 8484 | 10193 | 13029.6 | 14216 | 2206 | 3005
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7916.3469 | 9511 | 12157.8069 | 13264.8264
| A. |  | 2020-11-12 | (Yesterday) |  |  |  |  | Thursday
| 1 | Highest Generation : |  |  | 10193 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 6630 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10193 | MW
| 3 | Day peak Generation : |  |  | 8484 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9511 | MW
| 4 | Evening peak Generation : |  |  | 10193 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 196.782 | MKWHr | By Solar | 0.58458 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 126.5989 | MKWHr |  | By Oil: | 31.9 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 14.8746 | MKWHr |  | By Hydro: | 3.8109 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2206 | MW | Dhaka | 3693 | 3693 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3005 | MW | Chittagong | 991 | 991 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5211 | MW | Khulna | 1131 | 1131 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1051.54 | MMCFD |  |  | Rajshahi | 873 | 873 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 146133985.436 | ii) Oil : | Taka | 220215787.42 | Comilla | 901 | 901 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 69352654.46 | Total | Taka | 435702427.316 | Mymensingh | 686 | 686 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 386 | 386 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 212 | MW (E to W) at | 19:00 | hrs | Barisal | 267 | 267 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 138 | MW at | 8:00 | hrs | Rangpur | 583 | 583 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 33.5° C |  |  | Total | 9511 | 9511 |  | 0
| B. |  | 2020-11-13 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 31.5° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 10000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14216 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 7500 | MW
| 4 | Reserve(Generation end) |  |  |  | 4216 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 193.0561 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6280 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 16.6822 | MKWHr. | ii) HVDC Flow at Peak Time |  | 897 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.3309 | MKWHr. | iii) Maximum HVDC Flow : |  | 899 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 103.73 |  | (b) Today: | 103.58 |  | (c) Rule Curve: |  | 107.8
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-11-12
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Mymensingh PV 50 MW Solar PP | Manikgonj 162MW PP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 122 | 115 | 200 | 12 | 0 | 0 | 306 |  | 0 | 380 | 150 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 32 | 28 | 25 | 0 | 0 | 86 | 70 | 120 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 24 | 20 | 40 | 125 | 0 | 0 | 310 | 0 | 181 | 26 | 50 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 102 | 105 | 33 | 20 | 0 | 43 | 0 | 50 | 50 | 107 | 158 | 67 | 84 | 0 | 217 | 18 | 0 | 10 | 285 | 24 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 401 | 35 | 35 | 0 | 0 | 16 | 54 | 0 | 0 | 0 | 100 | 60 | 34 | 0 | 0 |  | 612 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 82 | 0 | 163 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 35 | 0 |  | 5141 | 2468 | 7609 | 3550 | 612 | 1933 | 616 | 640 | 156 | 0 | 102 | 0 | 0 | 103.78
2:00 | 0 | 0 | 100 | 115 | 200 | 12 | 0 | 0 | 331 |  | 0 | 390 | 150 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 32 | 28 | 25 | 0 | 0 | 86 | 70 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 125 | 0 | 0 | 310 | 0 | 185 | 26 | 50 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 8 | 21 | 100 | 104 | 33 | 20 | 0 | 43 | 0 | 50 | 50 | 107 | 157 | 67 | 70 | 0 | 217 | 18 | 0 | 0 | 280 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 100 | 60 | 0 | 0 | 0 |  | 612 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 37 | 0 | 158 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 35 | 0 |  | 4825 | 2335 | 7160 | 3471 | 612 | 1867 | 374 | 580 | 156 | 0 | 100 | 0 | 0 | 103.77
3:00 | 0 | 0 | 100 | 115 | 200 | 12 | 0 | 0 | 333 |  | 0 | 400 | 150 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 32 | 28 | 25 | 0 | 0 | 88 | 70 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 80 | 0 | 0 | 275 | 0 | 181 | 8 | 50 | 29 | 5 | 0 | 5 | 0 | 0 | 0 | 19 | 11 | 8 | 21 | 96 | 105 | 33 | 20 | 0 | 43 | 0 | 50 | 50 | 107 | 158 | 68 | 30 | 0 | 217 | 18 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 100 | 60 | 0 | 0 | 0 |  | 613 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 154 | 0 | 24 | 0 | 159 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 35 | 0 |  | 4619 | 2270 | 6889 | 3386 | 613 | 1791 | 345 | 500 | 158 | 0 | 96 | 0 | 0 | 103.76
4:00 | 0 | 0 | 100 | 115 | 200 | 12 | 0 | 0 | 335 |  | 0 | 400 | 150 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 32 | 28 | 25 | 0 | 0 | 89 | 70 | 120 | 0 | 0 | 205 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 80 | 0 | 0 | 275 | 0 | 181 | 8 | 50 | 29 | 5 | 0 | 5 | 0 | 0 | 0 | 19 | 11 | 8 | 21 | 94 | 106 | 33 | 20 | 0 | 43 | 0 | 11 | 50 | 107 | 159 | 67 | 30 | 0 | 217 | 18 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 100 | 60 | 0 | 0 | 0 |  | 516 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 153 | 0 | 24 | 0 | 166 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 36 | 0 |  | 4574 | 2169 | 6743 | 3408 | 516 | 1739 | 327 | 500 | 159 | 0 | 94 | 0 | 0 | 103.75
5:00 | 0 | 0 | 100 | 115 | 200 | 12 | 0 | 0 | 354 |  | 0 | 400 | 150 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 28 | 28 | 25 | 0 | 0 | 91 | 70 | 120 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 80 | 0 | 0 | 275 | 0 | 181 | 8 | 50 | 29 | 5 | 0 | 5 | 0 | 0 | 0 | 19 | 11 | 8 | 21 | 92 | 106 | 33 | 20 | 0 | 44 | 0 | 11 | 10 | 107 | 158 | 69 | 10 | 0 | 217 | 18 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 100 | 60 | 0 | 0 | 0 |  | 517 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 148 | 0 | 24 | 0 | 161 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 35 | 0 |  | 4522 | 2108 | 6630 | 3342 | 517 | 1691 | 327 | 500 | 161 | 0 | 92 | 0 | 0 | 103.74
6:00 | 0 | 0 | 100 | 115 | 200 | 12 | 0 | 0 | 352 |  | 0 | 400 | 150 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 28 | 28 | 0 | 0 | 0 | 92 | 70 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 38 | 80 | 0 | 0 | 275 | 0 | 182 | 8 | 50 | 29 | 5 | 0 | 5 | 0 | 0 | 0 | 19 | 11 | 8 | 21 | 88 | 106 | 33 | 20 | 0 | 44 | 0 | 11 | 10 | 107 | 158 | 67 | 10 | 0 | 217 | 18 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 100 | 60 | 0 | 0 | 0 |  | 517 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 151 | 0 | 24 | 0 | 163 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 35 | 0 |  | 4501 | 2173 | 6674 | 3323 | 517 | 1757 | 327 | 500 | 162 | 0 | 88 | 0 | 0 | 103.73
7:00 | 0 | 0 | 100 | 115 | 200 | 12 | 0 | 0 | 334 |  | 0 | 400 | 150 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 25 | 28 | 25 | 0 | 0 | 91 | 70 | 120 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 38 | 80 | 0 | 0 | 345 | 0 | 202 | 8 | 50 | 25 | 5 | 0 | 5 | 0 | 0 | 0 | 19 | 11 | 8 | 15 | 78 | 106 | 33 | 20 | 0 | 43 | 0 | 11 | 10 | 107 | 158 | 67 | 10 | 0 | 217 | 18 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 10 | 0 | 0 | 401 | 0 | 0 | 0 | 1 | 0 | 17 | 0 | 0 | 0 | 100 | 60 | 0 | 7 | 0 |  | 516 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 159 | 0 | 24 | 0 | 165 | 0 | 415 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 350 | 35 | 0 |  | 4603 | 2194 | 6797 | 3457 | 516 | 1745 | 327 | 500 | 161 | 0 | 78 | 13 | 0 | 103.72
8:00 | 0 | 0 | 120 | 115 | 200 | 12 | 0 | 0 | 314 |  | 0 | 390 | 150 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 32 | 28 | 25 | 0 | 0 | 92 | 70 | 120 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 5 | 20 | 5 | 80 | 0 | 0 | 315 | 0 | 188 | 8 | 71 | 25 | 5 | 0 | 25 | 0 | 0 | 0 | 19 | 11 | 33 | 15 | 80 | 105 | 33 | 20 | 1 | 44 | 0 | 50 | 40 | 107 | 158 | 67 | 84 | 0 | 217 | 18 | 0 | 10 | 295 | 24 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 10 | 0 | 0 | 401 | 24 | 50 | 0 | 2 | 0 | 36 | 0 | 0 | 0 | 100 | 60 | 23 | 25 | 0 |  | 516 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 164 | 0 | 24 | 0 | 170 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 350 | 35 | 0 |  | 4953 | 2218 | 7171 | 3548 | 516 | 1858 | 466 | 500 | 162 | 0 | 80 | 41 | 0 | 103.71
9:00 | 0 | 0 | 150 | 115 | 200 | 12 | 0 | 0 | 304 |  | 0 | 360 | 150 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 32 | 28 | 25 | 9 | 0 | 92 | 70 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 20 | 3 | 80 | 0 | 0 | 305 | 0 | 184 | 8 | 72 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 15 | 76 | 103 | 33 | 20 | 2 | 44 | 0 | 50 | 49 | 107 | 159 | 67 | 82 | 0 | 217 | 18 | 0 | 10 | 280 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 80 | 0 | 1 | 401 | 31 | 63 | 0 | 3 | 16 | 54 | 0 | 0 | 10 | 100 | 60 | 56 | 39 | 0 |  | 516 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 157 | 0 | 23 | 0 | 167 | 0 | 363 | 37 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 400 | 35 | 0 |  | 5146 | 2256 | 7402 | 3549 | 516 | 1786 | 693 | 550 | 162 | 8 | 76 | 62 | 0 | 103.7
10:00 | 0 | 0 | 150 | 115 | 200 | 12 | 0 | 0 | 298 |  | 0 | 350 | 150 | 0 | 0 | 8 | 0 | 0 | 60 | 27 | 72 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 31 | 17 | 25 | 33 | 0 | 92 | 70 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 5 | 80 | 0 | 0 | 305 | 0 | 183 | 8 | 70 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 15 | 78 | 102 | 33 | 0 | 2 | 44 | 0 | 50 | 46 | 107 | 158 | 65 | 82 | 0 | 218 | 18 | 0 | 10 | 280 | 24 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 18 | 90 | 0 | 38 | 404 | 45 | 102 | 0 | 4 | 16 | 54 | 0 | 0 | 55 | 100 | 60 | 89 | 49 | 0 |  | 516 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 151 | 0 | 23 | 0 | 158 | 0 | 382 | 53 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 400 | 37 | 0 |  | 5400 | 2279 | 7679 | 3469 | 516 | 1789 | 1029 | 550 | 162 | 8 | 78 | 78 | 0 | 103.69
11:00 | 0 | 0 | 150 | 115 | 200 | 12 | 0 | 0 | 294 |  | 0 | 340 | 150 | 0 | 10 | 30 | 0 | 0 | 60 | 50 | 84 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 31 | 17 | 25 | 33 | 0 | 90 | 70 | 120 | 0 | 0 | 205 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 36 | 20 | 4 | 80 | 0 | 0 | 305 | 0 | 181 | 8 | 71 | 29 | 30 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 82 | 86 | 33 | 0 | 2 | 44 | 0 | 47 | 46 | 107 | 157 | 40 | 84 | 0 | 218 | 18 | 0 | 10 | 270 | 24 | 2 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 19 | 90 | 0 | 40 | 403 | 45 | 102 | 0 | 4 | 66 | 54 | 0 | 0 | 55 | 100 | 60 | 90 | 54 | 36 |  | 751 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 154 | 0 | 23 | 0 | 158 | 0 | 359 | 53 | 0 | 0 | 0 | 5 | 0 | 6 | 0 | 400 | 35 | 0 |  | 5587 | 2507 | 8094 | 3448 | 751 | 1765 | 1246 | 549 | 160 | 8 | 82 | 85 | 0 | 103.67
12:00 | 0 | 0 | 150 | 115 | 200 | 12 | 0 | 0 | 283 |  | 0 | 320 | 150 | 0 | 40 | 30 | 0 | 0 | 85 | 50 | 94 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 31 | 17 | 25 | 33 | 0 | 88 | 70 | 120 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 46 | 20 | 5 | 130 | 0 | 0 | 345 | 0 | 201 | 8 | 50 | 29 | 30 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 88 | 87 | 33 | 0 | 2 | 44 | 0 | 50 | 46 | 107 | 160 | 40 | 82 | 0 | 218 | 18 | 0 | 10 | 280 | 24 | 2 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 19 | 90 | 0 | 40 | 404 | 45 | 101 | 0 | 4 | 82 | 54 | 0 | 0 | 55 | 100 | 50 | 90 | 54 | 77 |  | 750 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 180 | 0 | 23 | 0 | 165 | 0 | 418 | 53 | 0 | 0 | 0 | 39 | 0 | 6 | 20 | 400 | 35 | 0 |  | 5802 | 2682 | 8484 | 3633 | 750 | 1806 | 1406 | 550 | 158 | 8 | 88 | 85 | 0 | #REF!
13:00 | 0 | 0 | 150 | 115 | 200 | 12 | 0 | 0 | 284 |  | 0 | 320 | 150 | 10 | 48 | 35 | 0 | 0 | 85 | 50 | 94 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 31 | 17 | 25 | 33 | 0 | 88 | 70 | 120 | 0 | 0 | 205 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 45 | 20 | 10 | 135 | 0 | 0 | 325 | 0 | 189 | 8 | 50 | 29 | 30 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 25 | 18 | 88 | 70 | 24 | 0 | 2 | 44 | 0 | 50 | 46 | 107 | 157 | 63 | 84 | 0 | 218 | 18 | 0 | 10 | 310 | 24 | 2 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 18 | 90 | 0 | 50 | 404 | 75 | 101 | 0 | 4 | 137 | 54 | 0 | 0 | 55 | 100 | 40 | 90 | 50 | 71 |  | 750 | 0 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 179 | 0 | 62 | 0 | 201 | 0 | 423 | 90 | 0 | 0 | 0 | 40 | 0 | 5 | 40 | 420 | 35 | 0 |  | 5900 | 2823 | 8723 | 3600 | 750 | 1887 | 1583 | 570 | 158 | 8 | 88 | 79 | 8723 | 103.66
14:00 | 0 | 0 | 150 | 115 | 200 | 12 | 0 | 0 | 273 |  | 0 | 320 | 150 | 16 | 48 | 55 | 0 | 0 | 64 | 50 | 94 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 31 | 17 | 25 | 33 | 0 | 86 | 70 | 110 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 45 | 20 | 6 | 135 | 0 | 0 | 310 | 0 | 181 | 8 | 51 | 29 | 30 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 25 | 18 | 96 | 70 | 33 | 0 | 2 | 44 | 0 | 50 | 46 | 107 | 157 | 63 | 84 | 0 | 218 | 18 | 0 | 10 | 305 | 24 | 8 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 16 | 90 | 0 | 56 | 404 | 86 | 101 | 0 | 3 | 157 | 54 | 0 | 0 | 69 | 100 | 40 | 90 | 42 | 44 |  | 750 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 168 | 0 | 62 | 0 | 183 | 0 | 338 | 90 | 0 | 0 | 0 | 40 | 0 | 5 | 50 | 420 | 36 | 0 |  | 5894 | 2749 | 8643 | 3552 | 750 | 1791 | 1652 | 570 | 156 | 8 | 96 | 68 | 0 | 103.65
15:00 | 0 | 0 | 150 | 115 | 200 | 12 | 0 | 0 | 278 |  | 0 | 320 | 150 | 16 | 48 | 55 | 0 | 0 | 35 | 50 | 94 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 31 | 17 | 25 | 33 | 0 | 87 | 70 | 110 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 44 | 20 | 4 | 135 | 0 | 0 | 330 | 0 | 198 | 8 | 50 | 29 | 30 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 25 | 20 | 98 | 71 | 33 | 0 | 1 | 43 | 0 | 50 | 46 | 107 | 158 | 40 | 40 | 0 | 218 | 18 | 0 | 10 | 270 | 24 | 8 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 11 | 100 | 0 | 90 | 404 | 115 | 90 | 0 | 2 | 123 | 54 | 0 | 0 | 103 | 100 | 40 | 90 | 31 | 64 |  | 751 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 153 | 0 | 62 | 0 | 171 | 0 | 349 | 90 | 0 | 0 | 0 | 37 | 0 | 3 | 50 | 420 | 35 | 0 |  | 5884 | 2750 | 8634 | 3565 | 751 | 1715 | 1730 | 570 | 157 | 0 | 98 | 48 | 0 | 103.64
16:00 | 0 | 0 | 150 | 115 | 200 | 12 | 0 | 0 | 278 |  | 0 | 320 | 150 | 16 | 48 | 55 | 0 | 0 | 32 | 50 | 94 | 6 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 31 | 17 | 25 | 8 | 0 | 88 | 70 | 110 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 45 | 20 | 5 | 135 | 0 | 0 | 310 | 0 | 178 | 8 | 50 | 29 | 30 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 25 | 20 | 102 | 87 | 33 | 0 | 0 | 41 | 0 | 50 | 46 | 107 | 160 | 40 | 40 | 0 | 218 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 6 | 100 | 0 | 108 | 403 | 115 | 85 | 0 | 1 | 123 | 54 | 0 | 0 | 106 | 100 | 40 | 90 | 12 | 55 |  | 750 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 157 | 0 | 63 | 0 | 165 | 0 | 320 | 53 | 0 | 0 | 0 | 39 | 0 | 2 | 50 | 400 | 35 | 0 |  | 5842 | 2653 | 8495 | 3507 | 750 | 1723 | 1678 | 550 | 158 | 6 | 102 | 21 | 0 | 103.64
17:00 | 0 | 0 | 120 | 115 | 200 | 12 | 0 | 0 | 278 |  | 0 | 320 | 150 | 21 | 48 | 55 | 0 | 0 | 32 | 50 | 94 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 30 | 19 | 25 | 31 | 17 | 8 | 0 | 0 | 91 | 70 | 110 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 11 | 0 | 0 | 47 | 20 | 8 | 135 | 0 | 0 | 290 | 0 | 167 | 8 | 50 | 29 | 30 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 25 | 20 | 96 | 88 | 33 | 0 | 0 | 41 | 0 | 50 | 46 | 107 | 160 | 40 | 10 | 0 | 182 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 30 | 0 | 0 | 10 | 0 | 16 | 0 | 100 | 0 | 108 | 379 | 115 | 52 | 0 | 0 | 86 | 54 | 0 | 0 | 105 | 100 | 40 | 90 | 1 | 32 |  | 750 | 0 | 350 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 20 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 65 | 0 | 159 | 0 | 255 | 53 | 0 | 0 | 0 | 34 | 0 | 1 | 50 | 420 | 34 | 0 |  | 5618 | 2597 | 8215 | 3336 | 750 | 1615 | 1658 | 570 | 161 | 27 | 96 | 2 | 0 | 103.63
18:00 | 0 | 0 | 150 | 115 | 200 | 12 | 0 | 0 | 268 |  | 0 | 310 | 150 | 74 | 64 | 55 | 0 | 0 | 97 | 100 | 94 | 55 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 18 | 17 | 25 | 51 | 0 | 91 | 70 | 110 | 0 | 0 | 212 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 0 | 49 | 20 | 0 | 135 | 0 | 0 | 365 | 0 | 153 | 8 | 50 | 29 | 10 | 0 | 51 | 0 | 0 | 33 | 19 | 11 | 25 | 20 | 114 | 87 | 33 | 0 | 0 | 41 | 0 | 50 | 49 | 107 | 158 | 65 | 84 | 0 | 217 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 218 | 0 | 0 | 84 | 0 | 95 | 0 | 100 | 0 | 108 | 402 | 115 | 82 | 0 | 0 | 160 | 54 | 0 | 0 | 105 | 100 | 40 | 90 | 0 | 0 |  | 899 | 0 | 415 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 28 | 48 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 139 | 0 | 75 | 0 | 182 | 0 | 421 | 90 | 0 | 0 | 0 | 72 | 0 | 0 | 90 | 560 | 35 | 0 |  | 6673 | 3419 | 10092 | 3672 | 899 | 1849 | 2581 | 710 | 161 | 106 | 114 | 0 | 0 | 103.63
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 150 | 115 | 200 | 12 | 0 | 0 | 267 |  | 0 | 300 | 150 | 94 | 80 | 55 | 0 | 0 | 32 | 100 | 94 | 100 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 31 | 17 | 25 | 51 | 0 | 91 | 70 | 115 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 0 | 50 | 20 | 9 | 135 | 0 | 0 | 370 | 0 | 170 | 8 | 50 | 29 | 10 | 0 | 51 | 0 | 0 | 52 | 19 | 11 | 25 | 20 | 118 | 88 | 33 | 20 | 0 | 41 | 0 | 50 | 49 | 107 | 159 | 40 | 84 | 0 | 217 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 296 | 0 | 0 | 70 | 0 | 138 | 0 | 100 | 0 | 108 | 402 | 115 | 101 | 0 | 0 | 160 | 54 | 0 | 17 | 113 | 100 | 40 | 90 | 0 | 0 |  | 897 | 0 | 300 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 28 | 32 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 154 | 0 | 88 | 0 | 167 | 0 | 296 | 90 | 0 | 35 | 0 | 98 | 0 | 0 | 109 | 660 | 35 | 0 |  | 6874 | 3319 | 10193 | 3514 | 897 | 1715 | 2827 | 810 | 161 | 151 | 118 | 0 | 0 | 103.61
19:30 | 0 | 0 | 150 | 115 | 200 | 12 | 0 | 0 | 267 |  | 0 | 300 | 150 | 100 | 99 | 55 | 0 | 0 | 32 | 100 | 94 | 100 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 31 | 17 | 25 | 51 | 0 | 91 | 70 | 115 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 0 | 50 | 20 | 12 | 135 | 0 | 0 | 370 | 0 | 162 | 8 | 50 | 29 | 10 | 0 | 51 | 0 | 0 | 52 | 19 | 11 | 25 | 21 | 122 | 83 | 33 | 20 | 0 | 41 | 0 | 50 | 49 | 107 | 159 | 40 | 84 | 0 | 217 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 300 | 0 | 0 | 70 | 0 | 80 | 0 | 100 | 0 | 108 | 401 | 115 | 101 | 0 | 0 | 160 | 54 | 0 | 0 | 113 | 100 | 40 | 90 | 0 | 0 |  | 898 | 0 | 270 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 28 | 16 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 144 | 0 | 88 | 0 | 158 | 0 | 314 | 90 | 0 | 0 | 0 | 113 | 0 | 0 | 109 | 660 | 35 | 0 |  | 6805 | 3207 | 10012 | 3452 | 898 | 1736 | 2699 | 810 | 161 | 134 | 122 | 0 | 0 | 0
20:00 | 0 | 0 | 150 | 115 | 200 | 12 | 0 | 0 | 271 |  | 0 | 300 | 150 | 100 | 97 | 55 | 0 | 0 | 35 | 100 | 94 | 84 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 31 | 17 | 16 | 51 | 0 | 92 | 70 | 115 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 0 | 50 | 20 | 16 | 135 | 0 | 0 | 360 | 0 | 160 | 8 | 50 | 29 | 10 | 0 | 51 | 0 | 0 | 25 | 19 | 11 | 0 | 21 | 120 | 83 | 33 | 20 | 0 | 41 | 0 | 50 | 50 | 107 | 160 | 40 | 84 | 0 | 217 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 278 | 0 | 0 | 70 | 0 | 83 | 0 | 100 | 0 | 108 | 402 | 115 | 101 | 0 | 0 | 160 | 54 | 0 | 0 | 113 | 100 | 40 | 90 | 0 | 0 |  | 898 | 0 | 270 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 16 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 146 | 0 | 88 | 0 | 160 | 0 | 346 | 90 | 0 | 0 | 0 | 111 | 0 | 0 | 109 | 660 | 35 | 0 |  | 6690 | 3205 | 9895 | 3415 | 898 | 1777 | 2595 | 810 | 162 | 118 | 120 | 0 | 0 | 103.62
21:00 | 0 | 0 | 150 | 115 | 200 | 12 | 0 | 0 | 270 |  | 0 | 310 | 150 | 75 | 97 | 55 | 0 | 0 | 60 | 90 | 94 | 84 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 31 | 17 | 17 | 51 | 0 | 92 | 70 | 115 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 50 | 20 | 21 | 135 | 0 | 0 | 260 | 0 | 190 | 8 | 50 | 29 | 10 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 25 | 21 | 96 | 84 | 33 | 20 | 0 | 41 | 0 | 50 | 50 | 107 | 159 | 52 | 84 | 0 | 217 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 100 | 0 | 0 | 60 | 0 | 0 | 0 | 100 | 0 | 108 | 402 | 115 | 70 | 0 | 0 | 160 | 54 | 0 | 0 | 113 | 100 | 40 | 90 | 0 | 0 |  | 897 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 16 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 150 | 0 | 88 | 0 | 164 | 0 | 399 | 90 | 0 | 0 | 0 | 113 | 0 | 0 | 111 | 630 | 36 | 0 |  | 6314 | 3221 | 9535 | 3411 | 897 | 1867 | 2221 | 780 | 162 | 101 | 96 | 0 | 0 | #REF!
22:00 | 0 | 0 | 150 | 115 | 200 | 12 | 0 | 0 | 271 |  | 0 | 320 | 150 | 46 | 97 | 55 | 0 | 0 | 60 | 50 | 94 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 31 | 25 | 17 | 34 | 0 | 92 | 70 | 115 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 31 | 135 | 0 | 0 | 260 | 0 | 181 | 8 | 50 | 29 | 10 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 25 | 21 | 116 | 85 | 33 | 20 | 0 | 41 | 0 | 50 | 50 | 107 | 159 | 52 | 84 | 0 | 217 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 60 | 0 | 0 | 24 | 0 | 0 | 0 | 100 | 0 | 108 | 402 | 115 | 52 | 0 | 0 | 160 | 54 | 0 | 0 | 113 | 100 | 40 | 90 | 0 | 0 |  | 848 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 144 | 0 | 88 | 0 | 158 | 0 | 406 | 17 | 0 | 0 | 0 | 113 | 0 | 0 | 111 | 600 | 35 | 0 |  | 5999 | 3027 | 9026 | 3364 | 848 | 1873 | 1913 | 750 | 162 | 0 | 116 | 0 | 0 | 103.61
23:00 | 0 | 0 | 150 | 115 | 200 | 12 | 0 | 0 | 270 |  | 0 | 340 | 150 | 0 | 30 | 15 | 0 | 0 | 60 | 30 | 48 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 31 | 25 | 25 | 8 | 0 | 92 | 70 | 115 | 0 | 0 | 216 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 31 | 135 | 0 | 0 | 260 | 0 | 186 | 8 | 50 | 29 | 10 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 25 | 21 | 108 | 89 | 33 | 20 | 0 | 41 | 0 | 50 | 50 | 107 | 158 | 52 | 84 | 0 | 218 | 18 | 0 | 10 | 270 | 24 | 11 | 0 | 15 | 0 | 0 | 24 | 0 | 0 | 0 | 100 | 0 | 50 | 402 | 115 | 52 | 0 | 0 | 142 | 54 | 0 | 0 | 113 | 100 | 40 | 90 | 0 | 0 |  | 849 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 11 | 0 | 47 | 150 | 0 | 0 | 0 | 0 | 145 | 0 | 87 | 0 | 159 | 0 | 423 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 570 | 37 | 0 |  | 5646 | 2866 | 8512 | 3395 | 849 | 1898 | 1333 | 767 | 162 | 0 | 108 | 0 | 0 | 103.6
24:00 | 0 | 0 | 150 | 115 | 200 | 12 | 0 | 0 | 295 |  | 0 | 360 | 150 | 0 | 15 | 0 | 0 | 0 | 52 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 31 | 25 | 25 | 8 | 0 | 90 | 70 | 115 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 30 | 135 | 0 | 0 | 260 | 0 | 181 | 8 | 50 | 29 | 10 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 25 | 21 | 104 | 89 | 33 | 20 | 0 | 41 | 0 | 50 | 50 | 107 | 158 | 53 | 84 | 0 | 218 | 18 | 0 | 10 | 270 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 400 | 95 | 52 | 0 | 0 | 125 | 54 | 0 | 0 | 55 | 100 | 40 | 90 | 0 | 0 |  | 849 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 11 | 0 | 64 | 150 | 0 | 0 | 0 | 0 | 148 | 0 | 87 | 0 | 162 | 0 | 387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 570 | 36 | 0 |  | 5377 | 2791 | 8168 | 3375 | 849 | 1904 | 992 | 784 | 160 | 0 | 104 | 0 | 0 | 103.6
KWH | 0 | 0 | 3224000 | 2740500 | 4735927 | 291681 | 0 | 0 | 7089000 |  | 0 | 7478000 | 3495331 | 500160 | 860712 | 670310 | 0 | 0 | 1596000 | 894720 | 1270800 | 349440 | 0 | 0 | 0 | 0 | 1004760 | 342415 | 135256 | 267732 | 600000 | 682020 | 561700 | 559800 | 500136 | 0 | 2114945 | 1696000 | 2700000 | 0 | 0 | 4888916 | 0 | 0 | 0 |  | 0 | 0 | 170878 | 0 | 0 | 738240 | 477456 | 515040 | 2807624 | 0 | 0 | 7678700 | 0 | 4484000 | 250909 | 1270690 | 655776 | 387360 | 0 | 960146 | 0 | 0 | 132296 | 445140 | 246240 | 551800 | 489480 | 2330880 | 2122000 | 770880 | 275364 | 15100 | 1012000 | 0 | 1026600 | 1058688 | 2532927 | 3612000 | 1377312 | 1585920 | 0 | 5263220 | 419000 | 0 | 183060 | 7167200 | 420120 | 128500 | 0 | 1149163 | 0 | 0 | 422400 | 0 | 465264 | 137160 | 1731840 | 0 | 1246181 | 9618000 | 1580400 | 1444872 | 0 | 29160 | 1911927 | 1139481 | 0 | 26220 | 1406160 | 2451840 | 604900 | 1480320 | 364000 | 391680 |  | 16682181 | 0 | 8422848 | 0 | 221760 | 0 | 0 | 0 | 0 | 0 | 55125 | 0 | 504700 | 132480 | 0 | 0 | 340000 | 0 | 0 | 5072 | 0 | 0 | 0 | 14400 | 0 | 388560 | 230760 | 230688 | 0 | 160582 | 3679500 | 0 | 0 | 0 | 0 | 3930373 | 0 | 1300947 | 0 | 4221373 | 0 | 9082909 | 981120 | 0 | 47616 | 0 | 864960 | 0 | 39160 | 893376 | 11034500 | 903270 | 0 |  | 132413775 | 64368260 | 196782035 | 83661199 | 16682181 | 42937677 | 31374601 | 14874582 | 3810945 | 525390 | 2330880 | 584580 | 0
Fuel Cost | 0 | 0 | 4707040 | 4028535 | 5256878.97 | 385018.92 | 0 | 0 | 7301670 |  | 0 | 8151020 | 3879817.41 | 3796214.4 | 5930305.68 | 5670822.6 | 0 | 0 | 2761080 | 6737241.6 | 11589696 | 3438489.6 | 0 | 0 | 0 | 0 | 7334748 | 2646867.95 | 1333624.16 | 200799 | 450000 | 0 | 0 | 0 | 4836315.12 | 0 | 571035.15 | 457920 | 4887000 | 0 | 0 | 5328918.44 | 0 | 0 | 0 |  | 0 | 0 | 1657516.6 | 0 | 0 | 5846860.8 | 601594.56 | 1529668.8 | 4155283.52 | 0 | 0 | 5682238 | 0 | 4125280 | 323672.61 | 1461293.5 | 741026.88 | 542304 | 0 | 1641849.66 | 0 | 0 | 1263426.8 | 565327.8 | 184680 | 965650 | 367110 | 17481600 | 2249320 | 6999590.4 | 349712.28 | 240694 | 1659680 | 0 | 1827348 | 1651553.28 | 2887536.78 | 3756480 | 2713304.64 | 3029107.2 | 0 | 9105370.6 | 917610 | 0 | 373442.4 | 7238872 | 315090 | 97660 | 0 | 8687672.28 | 0 | 0 | 2196480 | 0 | 4578197.76 | 1603400.4 | 14114496 | 0 | 8785576.05 | 8944740 | 14413248 | 13654040.4 | 0 | 0 | 14454168.12 | 9924879.51 | 0 | 261675.6 | 12050791.2 | 16329254.4 | 0 | 0 | 0 | 0 |  | 96089362.56 | 0 | 8843990.4 | 0 | 1743033.6 | 0 | 0 | 0 | 0 | 0 | 574402.5 | 0 | 782285 | 1293004.8 | 0 | 0 | 697000 | 0 | 0 | 44887.2 | 0 | 0 | 0 | 139536 | 0 | 746035.2 | 357678 | 174630.816 | 0 | 968309.46 | 19942890 | 0 | 0 | 0 | 0 | 5188092.36 | 0 | 1951420.5 | 0 | 4939006.41 | 0 | 8992079.91 | 10242892.8 | 0 | 451875.84 | 0 | 6712089.6 | 0 | 432718 | 6602048.64 | 48441455 | 0 | 0 |  | 326228432.83 | 226350724.596 | 552579157.426 | 96421423.176 | 96089362.56 | 49712562.26 | 215074894.02 | 69352654.46 | 1028955.15 | 5140893.4 | 17481600 | 2276812.4 | 0
Yesterday Day Peak | 0 | 0 | 150 | 115 | 200 | 12 | 0 | 0 | 283 |  | 0 | 320 | 150 | 0 | 40 | 30 | 0 | 0 | 85 | 50 | 94 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 31 | 17 | 25 | 33 | 0 | 88 | 70 | 120 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 46 | 20 | 5 | 130 | 0 | 0 | 345 | 0 | 201 | 8 | 50 | 29 | 30 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 88 | 87 | 33 | 0 | 2 | 44 | 0 | 50 | 46 | 107 | 160 | 40 | 82 | 0 | 218 | 18 | 0 | 10 | 280 | 24 | 2 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 19 | 90 | 0 | 40 | 404 | 45 | 101 | 0 | 4 | 82 | 54 | 0 | 0 | 55 | 100 | 50 | 90 | 54 | 77 |  | 750 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 180 | 0 | 23 | 0 | 165 | 0 | 418 | 53 | 0 | 0 | 0 | 39 | 0 | 6 | 20 | 400 | 35 | 0 |  | 8484 | DayPeak
Yesterday Evening Peak | 0 | 0 | 150 | 115 | 200 | 12 | 0 | 0 | 267 | 0 | 0 | 300 | 150 | 94 | 80 | 55 | 0 | 0 | 32 | 100 | 94 | 100 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 31 | 17 | 25 | 51 | 0 | 91 | 70 | 115 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 50 | 20 | 9 | 135 | 0 | 0 | 370 | 0 | 170 | 8 | 50 | 29 | 10 | 0 | 51 | 0 | 0 | 52 | 19 | 11 | 25 | 20 | 118 | 88 | 33 | 20 | 0 | 41 | 0 | 50 | 49 | 107 | 159 | 40 | 84 | 0 | 217 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 296 | 0 | 0 | 70 | 0 | 138 | 0 | 100 | 0 | 108 | 402 | 115 | 101 | 0 | 0 | 160 | 54 | 0 | 17 | 113 | 100 | 40 | 90 | 0 | 0 |  | 897 | 0 | 300 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 28 | 32 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 154 | 0 | 88 | 0 | 167 | 0 | 296 | 90 | 0 | 35 | 0 | 98 | 0 | 0 | 109 | 660 | 35 | 0 |  | 10193 | EvPeak
Forecast for Evening | 0 | 0 | 150 | 115 | 200 | 12 | 0 | 0 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 0 | 0 | 100 | 100 | 100 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 33 | 33 | 33 | 52 | 0 | 93 | 70 | 120 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 0 |  | 102 | 100 | 100 | 50 | 20 | 40 | 100 | 0 | 0 | 360 | 0 | 225 | 8 | 80 | 30 | 30 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 172 | 100 | 33 | 22 | 0 | 44 | 0 | 51 | 44 | 110 | 160 | 66 | 86 | 0 | 220 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 180 | 150 | 400 | 115 | 100 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 40 | 90 | 0 |  |  | 507 | 16 | 410 | 0 | 115 | 220 | 0 | 0 | 30 | 60 | 40 | 0 | 22 | 110 | 0 | 0 | 70 | 50 | 40 | 100 | 0 | 0 | 50 | 52 | 33 | 22 | 10 | 11 | 0 | 64 | 150 | 0 | 0 | 0 | 0 | 220 | 0 | 95 | 100 | 220 | 0 | 413 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 660 | 35
Forecast for Day | 0 | 0 | 150 | 115 | 200 | 12 | 0 | 0 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 0 | 0 | 100 | 100 | 100 | 150 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 33 | 33 | 33 | 52 | 0 | 93 | 70 | 120 | 0 | 25 | 215 | 0 | 0 | 0 | 0 | 0 |  | 102 | 100 | 100 | 50 | 20 | 40 | 100 | 0 | 0 | 360 | 0 | 225 | 8 | 70 | 30 | 30 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 156 | 100 | 33 | 22 | 1.6 | 44 | 0 | 51 | 44 | 110 | 160 | 66 | 86 | 0 | 220 | 18 | 0 | 10 | 341 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 165 | 150 | 400 | 115 | 100 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 40 | 90 | 50 |  |  | 507 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 22 | 110 | 0 | 0 | 50 | 0 | 0 | 100 | 0 | 0 | 50 | 52 | 0 | 22 | 10 | 11 | 0 | 64 | 150 | 0 | 0 | 0 | 0 | 220 |  | 95 | 0 | 220 | 0 | 413 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 600 | 35
Generation at 08:00(Today) | 0 | 0 | 100 | 115 | 200 | 12 | 0 | 0 | 288 | 0 | 0 | 330 | 150 |  | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 28 | 25 | 25 | 0 | 0 | 91 | 70 | 115 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 39 | 100 | 0 | 0 | 285 | 0 | 197 | 8 | 50 | 29 | 10 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 12 | 15 | 60 | 105 | 33 | 0 | 1 | 41 | 0 | 11 | 10 | 107 | 157 | 40 | 10 | 0 | 165 | 18 | 0 | 8 | 310 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 10 | 0 | 0 | 351 | 8 | 17 | 0 | 2 | 0 | 35 | 0 | 0 | 0 | 40 | 40 | 17 | 25 | 0 | 0 | 407 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 64 | 150 | 0 | 0 | 0 | 0 | 169 | 0 | 23 | 0 | 173 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 350 | 37 | 0 | 0
199
| Minimum Generation |  | 6630 | 5:00
| Highest Generation |  | 10193 | 19:00
| Day Peak Generation |  | 8484 | 12:00
| Evening Peak Generation |  | 10193 | 19:00
| HVDC Max Flow |  | 899 | 18:00
| HVDC EvPeak Flow |  | 897 | 19:00
| Load factor L.F |  | 80.44%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-11-13
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-11-12 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8484 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 6280 | MW
Evening Peak Generation : |  | 10193 | MW Hour : | 19:00 | Available Max Generation : |  | 14216 | MW
E.P. Demand (at gen end) : |  | 10193 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 10000 | MW
Maximum Generation : |  | 10193 | MW Hour : | 19:00 | Reserve(Generation end) |  | 4216 | MW
Total Gen. (MKWH) : |  | 196.782 | System Load Factor : | 80.44% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 138 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-11-13
Actual : | 103.58 | Ft.(MSL) , | Rule curve : | 107.8 | Ft.( MSL )
Gas Consumed : | Total = | 1051.54 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 146133985.436
: |  | Coal : | 69352654.46 | Oil : | 220215787.42 | Total : | 435702427.316
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3482.4731 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1180.8589 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1057.4091 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 955.2449 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 863.3587 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 696.6914 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 393.8982 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 179.4942 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 537.3022 |  |  | 0 | 0%
Total | 0 |  | 9346.7308 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1 | 10) Sirajganj #1 CCPP STG
|  |  |  | 2) Baghabari-100 MW | 11) Summit Meghnaghat GT-1
|  |  |  | 3) Ghorasal Unit-1,2,3 | 13) Ashuganj(S)-360 MW
4) Ashuganj unit-4
5) Kaptai-2
6) Raozan #2,5
7) Siddirganj-335 MW
8) Haripur 412 MW
9) Chandpur-163 MW STG
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Sirajganj 230 kV Ckt-2 was under shut down from 07:37 to 17:38 for A/M.
b) Niamatpur 132/33 kV T2 transformer was under shut down from 08:21 to 17:31 for A/M.
c) Chapainawabganj 132/33 kV T-2 transformer was under shut down from 08:29 to 16:17 for A/M.
d) Rangpur confidence-Palashbari 132 kV Ckt-1 was under shut down from 08:27 to 15:27 for A/M.
e) Goalpara 132/33 kV T-5 transformer was under shut down from 08:24 to 16:23 for A/M.
f) Bagerhat 132/33 kV T-2 transformer was under shut down from 09:01 to 16:52 for A/M.
g) Patuakhali 132 kV main bus was under shut down from 08:13 to 14:13 for A/M.
h) Sikalbaha-Dohazari 132 kV Ckt-1 was under shut down from 09:06 to 16:22 for A/M.
i) Hathazari-Baroirhat 132 kV Ckt-1 was under shut down from 08:56 to 16:41 for A/M.
j) Joydevpur-Kodda 132 kV Ckt-1 was under shut down from 08:41 to 17:21 for A/M.
k) Meghnaghat-Cumilla(N) 230 kV Ckt-2 was under shut down from 09:01 to 15:03 for A/M.
l) Mymensing-Netrokona 132 kV Ckt-2 was under shut down from 08:38 to 16:51 for A/M.
m) Tongi 132/33 kV T-1 transformer was under shut down from 08:50 to 15:20 for A/M.
n) Kaliakoir 400 kV bus-2 was under shut down from 08:26 to 09:45 for A/M.
o) Barisal(N) 132/33 kV T-4 transformer was under shut down from 09:07 to 15:24 for A/M.
p) Mongla 132 kV bus coupler was under shut down from 09:10 to 12:30 for A/M.
q) Kaliakoir 230 kV bus-1 was under shut down from 09:57 to 11:19 for A/M.
r) Kaliakoir 230 kV bus-2 was under shut down from 11:52 to 13:34 for A/M.
s) GPH 230/33/11 kV transformer was shut down from 12:36 to 13:40 for primary bushing checking.
t) Modern Still Mill 132/11 kV transformer was shut down at 16:10 as per direction of high court.
u) Halishahar 132/33 kV T-3 transformer was under shut down at 21:21 for oil centrifuging.
v) Sikalbaha-Modunaghat 132 kV Ckt was under shut down from 07:25 to 10:57(13-11-2020) for D/W.
w) Madunaghat-TK 132 kV Ckt was under shut down from 07:25 to 11:01(13-11-2020) for D/W.
x) Tangail 132 kV main bus was under shut down since 06:05(13-11-2020) for D/W. |  |  |  |  | About 82 MW power interruption occurred under Tangail S/S areas
since 06:05 to till now
y) Kaliakoir 400/132kV T-2 transformer was under shut down from 06:16 to 10:35(13-11-2020) for C/M.
z) Gulshan 132/33 kV T-2 transformer was under shut down at 07:42 to 11:13(13-11-2020) for C/M.
aa) Dhamrai 132/33 kV T-2 transformer was under shut down at 07:54 to 11:54(13-11-2020) for D/W.
m) Joypurhat 132/33 kV T-1 transformer was under shut down from 08:52 to 14:16 for A/M.
n) Barishal 230/132 kV T-1 transformer was under shut down from 08:32 to 17:00 for A/M.
o) Benapole 132/33 kV T-1 transformer was under shut down from 07:47 to 15:30 for A/M.
p) Khulna(S) 230/132 kV T-1 transformer was under shut down from 08:27 to 14:07 for A/M.
q) Satkhira 132/33 kV T-1 transformer was under shut down from 08:55 to 16:21 for A/M.\r)
r) Ishurdi-Pabna 132 kV Ckt was under shut down from 08:21 to 16:44 for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-11-12 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 150 | 3224000 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 115 | 2740500 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 4735927 | Machin problem.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 12 | 291681 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 267 | 7089000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7478000 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 94 | 500160
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 150 | 3495331 | GT-2 under shut down
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 80 | 860712 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 670310
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 267732
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 32 | 1596000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 894720
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under Maintenance
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 94 | 1270800
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1004760
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 100 | 349440 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 342415
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 135256 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 56 | 1282020 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 17 | 561700 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 559800 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 500136
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 296 | 1149163
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 138 | 465264 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 101 | 1444872
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 1480320 | Unit Transformer problem
| Manikgonj 162MW PP |  | IPP | 9*18 | 0 | 0 | 391680
| Dhaka area Total |  |  |  | 5895 | 2686 | 44781699
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 115 | 2700000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve.
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 137160
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 738240
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 161 | 3810945 | Unit-2 under maint
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4888916
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 170878 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1731840
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 477456
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 9 | 515040
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve.
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 29160
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 160 | 1911927 | Transformer O/L
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1139481
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2451840
| Chattogram area Total |  |  |  | 2266 | 1024 | 20702883
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 135 | 2807624 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas Shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 170 | 4484000 | Gas shortage.
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 370 | 7678700
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 655776 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 10 | 387360 | Gas shortage
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 250909 | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 960146
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 108 | 1246181 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1270690 | ST Under maint
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve.
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 445140
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 246240
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 118 | 2330880 | Low demand
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 551800
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 132296
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 489480
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 26220 | Low demand
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 1406160
| Cumilla Area Total |  |  |  | 2980 | 1306 | 25369602
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 88 | 2122000 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 275364
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 33 | 770880 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 15100
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 70 | 422400
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1580400 | #REF!
| Mymensingh PV 50 MW Solar PP |  | IPP | 50 | 0 | 0 | 364000
| Mymensingh Area Total |  |  |  | 637 | 326 | 5550144
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 41 | 1012000 | GT-2 under maint.
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 107 | 2532927 | ST Under maint
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 159 | 3612000 | FGMO & GT-2 under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1026600
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 49 | 1058688
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 128500
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 40 | 1377312 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1585920
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 217 | 5263220
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 419000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 420120
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7167200 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 402 | 9618000
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 183060
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 40 | 604900 | On test
| Sylhet Area Total |  |  |  | 1988 | 1532 | 36009447
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 897 | 16682181
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 66 | 221760 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 300 | 8422848 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 24 | 55125 | Low demand
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 90 | 981120 | Engine problem
107 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1377 | 26363034
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 132480 | Low demand
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 28 | 504700 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 88 | 1300947 | Engine problem
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 660 | 11034500
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 35 | 903270
| Barisal Area Total |  |  |  | 1054 | 843 | 13875897
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 40 | 340000 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel Shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel Shortage
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | under rmaint.
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 154 | 3930373 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 167 | 4221373 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 296 | 9082909 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 388560
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 10 | 230760
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 230688
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 14400 | Low demand
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 5072 | Reserve.
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 35 | 47616 | Low demand
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 893376
| Rajshahi Area Total |  |  |  | 2183 | 851 | 19385127
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 160582 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3679500 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 98 | 864960
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 39160
| Rangpur Area Total |  |  |  | 605 | 248 | 4744202
| Total |  |  |  | 19892 | 10193 | 196782035
| Eastern Grid Total |  |  |  | 13766 | 6874 | 132413775
| Western Grid Total |  |  |  | 6126 | 3319 | 64368260
| National Grid Total |  |  |  | 19892 | 10193 | 196782035
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-11-12
| (a) ENTIRE EASTERN GRID : |  | 6657 | MW | (b) ENTIRE WESTERN GRID : |  | 2854 | MW
| i) Dhaka area |  | 3693 | MW | i) Khulna area |  | 1131 | MW
| ii) Chittagong area |  | 991 | MW | ii) Rajshahi area |  | 873 | MW
| iii) Comilla area |  | 901 | MW | iii) Barisal area |  | 267 | MW
| iv) Mymensingh area |  | 686 | MW | iv) Rangpur area |  | 583 | MW
| v) Sylhet area |  | 386 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 9511 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 122 | 15:00 | Sherpur | 82 | 18:00 | Jhenida | 81 | 18:00
| Munsiganj | 98 | 19:00 | Srimongal | 30 | 18:00 | Bottail | 100 | 18:00
| Sonargaon | 62 | 12:00 | Shahjibazar | 96 | 18:00 | G.K Project | 36 | 18:00
| Shyampur | 176 | 12:00 | Fenchuganj | 33 | 18:00 | Faridpur | 143 | 0.79167
| Bhulta | 166 | 19:00 | Kulawara | 35 | 19:00 | Madaripur | 67 | 0.8125
| Madanganj | 50 | 10:00 | Sylhet | 106 | 18:00 | Sariatpur | 46 | 19:30
| Shitalakhya | 114 | 16:00 | Chatak | 20 | 18:30 | Gopalganj | 69 | 18:00
| Rahim steel | 18 | 9:00 | Sunamganj | 33 | 18:30 | Bagerhat | 82 | 18:00
| Matuail | 78 | 10:00 | Biani Bazar | 42 | 18:00 | Mongla | 40 | 12:00
| Ghorasal | 108 | 18:00 | Comilla (S) | 122 | 19:30 | Satkhira | 78 | 0.77083
| Narsingdi | 135 | 19:00 | Comilla(N) | 101 | 19:30 | Gallamari | 40 | 13:00
| Haripur (SBU) | 96 | 16:00 | Chandpur | 74 | 18:00 | Magura | 40 | 0.75
| Ullon | 62 | 13:00 | Feni | 97 | 18:00 | Norail | 32 | 18:00
| Hasnabad | 173 | 19:30 | Chowmuhani | 142 | 18:00 | Chuadanga | 68 | 18:00
| Magbazar | 85 | 12:00 | Ashuganj | 46 | 21:00 | Barisal(N) | 31 | 0.77083
| Maniknagar | 86 | 16:00 | Daudkandi | 110 | 18:00 | Barisal (S) | 82 | 0.79167
| Bangabhaban | 30 | 10:00 | B.Baria | 115 | 18:00 | Patuakhali | 88 | 0.83333
| Narinda | 80 | 14:00 | Ramganj | 78 | 19:00 | Bhandaria | 42 | 0.83333
| Dhanmondi | 141 | 12:00 | Chaddagram | 31 | 18:00 | Borhan Uddin | 31 | 23:00
| Lalbag | 85 | 13:00 | PHP | 7 | 18:30 | Ishurdi | 45 | 19:00
| Madartek | 60 | 18:30 | Madunaghat | 53 | 19:30 | Ruppur Paromanobik | 2 | 20:00
| Dhaka University |  |  | Hathazari | 89 | 0.75 | Natore | 83 | 18:00
| Fatullah | 40 | 0.625 | Khulshi | 192 | 0.54167 | Bogra | 127 | 18:00
| Mirpur | 88 | 18:00 | Halishahar | 129 | 0.625 | Noagaon | 89 | 18:30
| Kalyanpur | 84 | 18:00 | Baraulia | 139 | 0 | Rajshahi | 98 | 20:00
| Gulshan | 112 | 14:00 | Sikalbaha | 25 | 0.75 | Rajshahi New | 9 | 20:00
| Uttara | 75 | 18:00 | Dohazari | 76 | 0.8125 | C.Nawabganj | 51 | 19:30
| Uttara New | 22 | 18:00 | Cox'sbazar | 91 | 0.77083 | Amnura | 30 | 18:30
| Kamrangirchar | 87 | 18:00 | Chandraghona | 24 | 0.75 | Pabna | 88 | 18:00
| Savar | 112 | 15:00 | Kaptai | 4.2 | 0.75 | Shahjadpur | 78 | 19:00
| Bhasantec | 136 | 14:00 | A. Khaer Stl. | 0 | 0.041667 | Serajganj | 58 | 19:30
| Agargaon | 63 | 14:00 | Bakulia | 93 | 0.625 | Niyamatpur | 37 | 18:00
| Satmosjid | 85 | 18:00 | Julda | 21 | 0.625 | Joypurhat | 37 | 19:00
| Tongi | 85 | 0.66667 | TK chemical | 23.8 | 0.79167 | Sherpur(Bogura) | 38 | 18:00
| Kabirpur | 209 | 16:00 | Modern Steel | 14 | 0.45833 | Mohastangor | 32 | 19:30
| Basundhara | 111 | 18:00 | Shahmirpur | 19.3 | 0.625 | Rangpur | 108 | 19:00
| Manikganj | 60 | 18:00 | Khagrachhari | 22 | 0.91667 | Lalmonirhat | 43 | 18:00
| Joydevpur | 128 | 18:00 | Matarbari | 31.5 | 0.875 | Saidpur | 84 | 18:00
| New Tongi | 90 | 14:00 | Baroiar Hat | 24 | 0.75 | Purbasadipur | 83 | 19:00
| Kodda | 229 | 15:00 | Rangamati | 10 | 0.75 | Thakurgaon | 58 | 18:00
| Dhamrai | 80 | 18:00 | Abul Khair 230 | 143 | 0.41667 | Palashbari | 92 | 18:00
| Rajendrapur | 92 | 18:30 | BSRM | 106 | 0.083333 | Barapukuria | 38 | 20:00
| Valuka | 84 | 18:30 | GPH Ispat | 74 | 0.083333 | Panchagar | 40 | 19:00
| Tangail | 156 | 18:00 | Goalpara | 18 | 0.54167 | Joldhaka | 19 | 18:30
| Mymensing | 156 | 18:30 | Central s/s | 87 | 18:00 | Kurigram | 42 | 18:30
| Kishorganj | 89 | 20:00 | Noapara | 48 | 18:00
| Netrokona | 78 | 18:30 | Jessore | 90 | 18:00
| Jamalpur | 95 | 18:00 | Benapol | 30 | 18:00
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-11-12 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 405 | 18:30 | 398 | 12:00 | Kaliakoir | 397 | 0.5 | 378 | 0.5
| Bheramara | 410 | 20:00 | 392 | 18:00 | Bhulta | 376 | 0.79167 | 360 | 0.45833
| Ashuganj(N) | 383 | 19:30 | 272 | 2:00 | Gopalganj | 418 | 0.125 | 393 | 0.75
| Payra | 420 | 19:30 | 406 | 18:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 18:00 | 226 | 1:00 | Comilla (N) | 232 | 19:30 | 226 | 7:00
| Ishurdi | 236 | 2:00 | 223 | 12:00 | Hathazari | 225 | 23:00 | 220 | 10:00
| Ashuganj | 232 | 18:30 | 225 | 12:00 | Megnaghat | 227 | 19:00 | 218 | 12:00
| Serajganj | 232 | 10:00 | 225 | 12:00 | Fenchuganj | 242 | 20:00 | 238 | 9:00
| Baghabari | 240 | 5:00 | 234 | 11:00 | Siddhirganj | 225 | 5:00 | 214 | 12:00
| Barapukuria | 231 | 22:00 | 226 | 8:00 | Maniknagar | 223 | 19:00 | 213 | 12:00
| Bogra | 229 | 3:00 | 222 | 12:00 | Agargaon | 219 | 14:00 | 207 | 12:00
| Rajshahi | 227 | 2:00 | 216 | 12:00 | Barisal | 249 | 19:00 | 238 | 18:00
| Khulna South | 234 | 14:00 | 213 | 12:00 | AKSML | 223 | 18:30 | 214 | 2:00
| Rampura | 222 | 8:00 | 216 | 11:00 | BSRM | 224 | 17:00 | 216 | 2:00
| Haripur | 223 | 18:30 | 213 | 12:00 | Bibiyana | 240 | 6:00 | 235 | 19:00
| Hasnabad | 216 | 2:00 | 205 | 11:00 | Bhulta | 224 | 19:00 | 216 | 17:00
| Shyampur | 223 | 19:30 | 220 | 12:00 | Ashuganj (S) | 230 | 18:30 | 222 | 11:00
| Aminbazar | 219 | 4:00 | 209 | 15:00 | Kaliakoir | 224 | 19:00 | 211 | 12:00
| Tongi | 225 | 18:00 | 210 | 11:00 | GPH | 221 | 19:00 | 217 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 135 | 19:00 | 128 | 11:00 | Hathazari | 135 | 0.95833 | 131 | 0.29167
| Munsiganj | 137 | 19:30 | 128 | 9:00 | Khulshi | 133 | 0.91667 | 128 | 0.20833
| Sonargaon | 135 | 20:00 | 127 | 11:00 | Halishahar | 134 | 0.79167 | 129 | 0.41667
| Shyampur | 132 | 19:00 | 125 | 12:00 | Baraulia | 133 | 0.125 | 131 | 0.45833
| Bhulta | 128 | 20:00 | 120 | 12:00 | Sikalbaha | 135 | 0.79167 | 129 | 0.083333
| Madanganj | 133 | 23:00 | 126 | 1:00 | Dohazari | 131 | 0.77083 | 124 | 0.54167
| Shitalakhya | 139 | 19:30 | 124 | 9:00 | Cox'sbazar | 126 | 0.33333 | 118 | 0.54167
| Rahim steal | 135 | 19:30 | 127 | 12:00 | Chandraghona | 134 | 0.70833 | 131 | 0.125
| Matuail | 135 | 19:00 | 128 | 11:00 | Kaptai | 134 | 0.70833 | 132 | 0.54167
| Ghorasal | 136 | 18:00 | 130 | 15:00 | A. Khaer Stl. | 132 | 0.041667 | 130 | 0.16667
| Narsinghdi | 130 | 19:30 | 123 | 12:00 | Bakulia | 133 | 0.77083 | 129 | 0.125
| Haripur (SBU) | 138 | 3:00 | 128 | 11:00 | Julda | 134 | 0.70833 | 130 | 0.16667
| Ullon | 132 | 1:00 | 124 | 12:00 | TK Chemical | 134 | 0.75 | 131 | 0.29167
| Hasnabad | 135 | 19:00 | 125 | 12:00 | Modern Steel | 133 | 0.75 | 129 | 0.625
| Magbazar | 131 | 4:00 | 125 | 11:00 | Shahmirpur | 134 | 0.77083 | 129 | 0.16667
| Maniknagar | 134 | 21:00 | 126 | 12:00 | Khagrachhari | 134 | 0.91667 | 130 | 0.54167
| Bangabhaban | 134 | 21:00 | 126 | 12:00 | Matarbari | 129 | 0.79167 | 120 | 0.54167
| Narinda | 134 | 21:00 | 126 | 12:00 | Baroiar Hat | 133 | 0.375 | 128 | 0.5
| Dhanmondi | 132 | 1:00 | 124 | 12:00 | Rangamati | 133 | 0.375 | 131 | 0.125
| Lalbag | 132 | 5:00 | 123 | 11:00 | Goalpara S/S | 138 | 17:00 | 125 | 8:00
| Madartek | 131 | 5:00 | 124 | 14:00 | Khulna Central S/S | 137 | 18:30 | 125 | 0.33333
| Dhaka University |  |  |  |  | Noapara | 137 | 17:00 | 124 | 0.29167
| Fatuiiah | 133 | 19:00 | 125 | 12:00 | Jessore | 133 | 14:00 | 121 | 0.5
| Mirpur | 132 | 20:00 | 126 | 12:00 | Benapol | 134 | 0.70833 | 121 | 0.5
| Kalyanpur | 133 | 20:00 | 126 | 11:00 | Jhenida | 132 | 3:00 | 122 | 0.5
| Gulshan | 130 | 20:00 | 125 | 12:00 | Bottail | 135 | 0.20833 | 128 | 0.5
| Uttara | 133 | 19:30 | 125 | 12:00 | G.K Project | 140 | 0.70833 | 135 | 0.5
| Uttara New | 132 | 19:00 | 124 | 10:00 | Faridpur | 136 | 0.16667 | 128 | 0.75
| Kamrangirchar | 132 | 20:00 | 122 | 12:00 | Madaripur | 137 | 0.70833 | 131 | 0.75
| Savar | 132 | 20:00 | 124 | 11:00 | Shariyatpur S/S | 139 | 4:00 | 129 | 0.75
| Bhasantec | 132 | 6:00 | 123 | 12:00 | Gopalganj | 141 | 0.25 | 128 | 0.75
| Agargaon | 133 | 20:00 | 125 | 12:00 | Bagerhat | 138 | 17:00 | 120 | 0.41667
| Satmosjid | 132 | 20:00 | 125 | 12:00 | Mongla | 134 | 17:00 | 120 | 0.33333
| Tongi | 140 | 18:00 | 130 | 11:00 | Satkhira | 138 | 13:00 | 125 | 8:00
| Kabirpur | 133 | 4:00 | 125 | 13:00 | Gallamari | 139 | 0.58333 | 127 | 0.33333
| Basundhara | 131 | 3:00 | 124 | 13:00 | Magura | 131 | 2:00 | 122 | 0.5
| Manikganj | 141 | 18:30 | 131 | 15:00 | Norail | 131 | 0.25 | 123 | 0.75
| Joydevpur | 140 | 19:00 | 128 | 15:00 | Chuadanga | 129 | 3:00 | 119 | 0.83333
| New Tongi | 139 | 19:00 | 129 | 15:00 | Barisal(N) | 140 | 8:00 | 133 | 18:00
| Kodda | 137 | 18:00 | 124 | 15:00 | Barisal (S) | 140 | 0.16667 | 131 | 0.75
| Dhamrai | 133 | 4:00 | 125 | 15:00 | Patuakhali(S) | 137 | 0.33333 | 126 | 0.75
| Rajendrapur | 137 | 19:00 | 122 | 16:00 | Bhandaria | 137 | 0.33333 | 128 | 0.75
| Valuka | 129 | 17:00 | 119 | 2:00 | Ishurdi | 137 | 1:00 | 131 | 12:00
| Tangail | 134 | 4:00 | 124 | 13:00 | Ruppur Paromanobik | 138 | 6:00 | 132 | 12:00
| Mymensing | 130 | 17:00 | 116 | 7:00 | Natore | 137 | 1:00 | 132 | 18:00
| Kishorganj | 128 | 9:00 | 123 | 20:00 | Bogra | 137 | 17:00 | 133 | 8:00
| Netrokona | 129 | 17:00 | 119 | 12:00 | Noagaon | 134 | 6:00 | 128 | 18:00
| Jamalpur | 139 | 17:00 | 121 | 3:00 | Rajshahi | 137 | 2:00 | 132 | 18:00
| Sherpur | 138 | 17:00 | 120 | 3:00 | Rajshahi New | 139 | 2:00 | 132 | 18:00
| Srimongal | 136 | 8:00 | 134 | 7:00 | C.Nawabganj | 136 | 3:00 | 130 | 12:00
| Shahjibazar | 135 | 8:00 | 131 | 5:00 | Amnura | 137 | 1:00 | 131 | 18:00
| Fenchuganj | 137 | 8:00 | 135 | 4:00 | Pabna | 138 | 4:00 | 130 | 12:00
| Khulawara | 136 | 1:00 | 134 | 5:00 | Shahjadpur | 139 | 18:30 | 135 | 12:00
| Sylhet | 134 | 1:00 | 133 | 4:00 | Serajganj | 135 | 1:00 | 130 | 12:00
| Chatak | 134 | 7:00 | 131 | 18:00 | Niyamatpur | 134 | 3:00 | 126 | 18:00
| Sunamganj | 134 | 7:00 | 131 | 18:00 | Joypurhat | 135 | 1:00 | 130 | 18:00
| Biani Bazar | 134 | 7:00 | 131 | 18:00 | Sherpur(Bogura) | 138 | 4:00 | 132 | 12:00
| Comilla(s) | 129 | 1:00 | 125 | 14:00 | Mohastangor | 136 | 6:00 | 132 | 8:00
| Comilla(n) | 137 | 18:30 | 132 | 11:00 | Rangpur | 128 | 3:00 | 122 | 8:00
| Chandpur | 135 | 7:00 | 130 | 13:00 | Lalmonirhat | 130 | 6:00 | 122 | 8:00
| Feni | 136 | 18:30 | 130 | 14:00 | Saidpur | 130 | 6:00 | 120 | 18:00
| Chowmuhani | 135 | 19:00 | 129 | 7:00 | Purbasadipur | 127 | 4:00 | 117 | 18:00
| Ashuganj | 133 | 18:30 | 130 | 7:00 | Thakurgaon | 126 | 4:00 | 116 | 18:00
| Daudkandi | 134 | 19:30 | 128 | 13:00 | Palashbari | 132 | 16:00 | 126 | 7:00
| B.Baria | 129 | 8:00 | 127 | 15:00 | Barapukuria | 130 | 20:00 | 126 | 18:00
| Ramganj | 130 | 20:00 | 126 | 18:00 | Panchagar | 126 | 6:00 | 114 | 18:00
| Chaddagram | 135 | 19:00 | 130 | 12:00 | Joldhaka | 127 | 3:00 | 120 | 18:00
| PHP | 134 | 18:30 | 128 | 12:00 | Kurigram | 128 | 6:00 | 120 | 18:00
| Madanhat | 135 | 18:00 | 131 | 4:00

## L-Curve
Date | 2020-11-12
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 535 | 5377 | 2791 | 8168 |  |  |  | QF-LDC-11
0:30 | 502.5 | 5259 | 2629.5 | 7888.5 | Date: | 2020-11-12
1:00 | 470 | 5141 | 2468 | 7609
1:30 | 470 | 4983 | 2401.5 | 7384.5
2:00 | 470 | 4825 | 2335 | 7160
2:30 | 463 | 4722 | 2302.5 | 7024.5 | [5 empty] | Gen. at Eve. Peak | 10193 | 10193 MW (19:00 )
3:00 | 456 | 4619 | 2270 | 6889 | [6 empty] | 19:00
3:30 | 428 | 4596.5 | 2219.5 | 6816 | [5 empty] | Gen. at Day Peak | 8484 | 8484 MW (12:00 )
4:00 | 400 | 4574 | 2169 | 6743 | [6 empty] | 12:00
4:30 | 393 | 4548 | 2138.5 | 6686.5 | [5 empty] | Highest Generation | 10193
5:00 | 386 | 4522 | 2108 | 6630 | [6 empty] | 19:00
5:30 | 362.5 | 4511.5 | 2140.5 | 6652
6:00 | 339 | 4501 | 2173 | 6674
6:30 | 263 | 4552 | 2183.5 | 6735.5
7:00 | 187 | 4603 | 2194 | 6797
7:30 | 162.5 | 4778 | 2206 | 6984
8:00 | 138 | 4953 | 2218 | 7171
8:30 | 238.5 | 5049.5 | 2237 | 7286.5
9:00 | 339 | 5146 | 2256 | 7402
9:30 | 401 | 5273 | 2267.5 | 7540.5
10:00 | 463 | 5400 | 2279 | 7679
10:30 | 515.5 | 5493.5 | 2393 | 7886.5
11:00 | 568 | 5587 | 2507 | 8094
11:30 | 605 | 5694.5 | 2594.5 | 8289
12:00 | 642 | 5802 | 2682 | 8484
12:30 | 602.5 | 5851 | 2752.5 | 8603.5
13:00 | 563 | 5900 | 2823 | 8723
13:30 | 576.5 | 5897 | 2786 | 8683
14:00 | 590 | 5894 | 2749 | 8643
14:30 | 627 | 5889 | 2749.5 | 8638.5
15:00 | 664 | 5884 | 2750 | 8634
15:30 | 635.5 | 5863 | 2701.5 | 8564.5
16:00 | 607 | 5842 | 2653 | 8495
16:30 | 546.5 | 5730 | 2625 | 8355
17:00 | 486 | 5618 | 2597 | 8215
17:30 | 444 | 6145.5 | 3008 | 9153.5
18:00 | 402 | 6673 | 3419 | 10092
18:30 | 307 | 6773.5 | 3369 | 10142.5
19:00 | 212 | 6874 | 3319 | 10193
19:30 | 175 | 6805 | 3207 | 10012
20:00 | 238 | 6690 | 3205 | 9895 |  |  |  | Executive Engineer
20:30 | 308.5 | 6502 | 3213 | 9715 |  |  |  | Network Operation Division
21:00 | 379 | 6314 | 3221 | 9535
21:30 | 386.5 | 6156.5 | 3124 | 9280.5
22:00 | 394 | 5999 | 3027 | 9026 |  |  |  |  | Page 6 of 7
22:30 | 443 | 5822.5 | 2946.5 | 8769
23:00 | 492 | 5646 | 2866 | 8512
23:30 | 513.5 | 5511.5 | 2828.5 | 8340
24:00 | 535 | 5377 | 2791 | 8168
10193 MW (19:00 )
8484 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-11-12 |  | Energy | 196782035
[10 empty] | 2020-11-12 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3375 | 849 | 1904 | 1333 | 784 | 160 | 0 | 0 | 104
0:30 | 3462.5 | 730.5 | 1918.5 | 974.5 | 712 | 158 | 0 | 0 | 103 | Date: | 2020-11-12
1:00 | 3550 | 612 | 1933 | 616 | 640 | 156 | 0 | 0 | 102
1:30 | 3510.5 | 612 | 1900 | 495 | 610 | 156 | 0 | 0 | 101 | [7 empty] | Total Energy | 196.782 | Total Energy Gen 196.782 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 196.782 MKWHr
2:00 | 3471 | 612 | 1867 | 374 | 580 | 156 | 0 | 0 | 100 | [7 empty] | Energy not Served | 0
2:30 | 3428.5 | 612.5 | 1829 | 359.5 | 540 | 157 | 0 | 0 | 98 | [7 empty] | Energy Requirement | 196.782
3:00 | 3386 | 613 | 1791 | 345 | 500 | 158 | 0 | 0 | 96
3:30 | 3397 | 564.5 | 1765 | 336 | 500 | 158.5 | 0 | 0 | 95 | [6 empty] | Shortage
4:00 | 3408 | 516 | 1739 | 327 | 500 | 159 | 0 | 0 | 94
4:30 | 3375 | 516.5 | 1715 | 327 | 500 | 160 | 0 | 0 | 93
5:00 | 3342 | 517 | 1691 | 327 | 500 | 161 | 0 | 0 | 92
5:30 | 3332.5 | 517 | 1724 | 327 | 500 | 161.5 | 0 | 0 | 90
6:00 | 3323 | 517 | 1757 | 327 | 500 | 162 | 0 | 0 | 88
6:30 | 3390 | 516.5 | 1751 | 327 | 500 | 161.5 | 0 | 0 | 83 |  |  |  |  | Coal
7:00 | 3457 | 516 | 1745 | 327 | 500 | 161 | 0 | 0 | 78
7:30 | 3502.5 | 516 | 1801.5 | 396.5 | 500 | 161.5 | 0 | 0 | 79 |  |  |  | Oil |  |  |  | ,
8:00 | 3548 | 516 | 1858 | 466 | 500 | 162 | 0 | 0 | 80
8:30 | 3548.5 | 516 | 1822 | 579.5 | 525 | 162 | 4 | 0 | 78
9:00 | 3549 | 516 | 1786 | 693 | 550 | 162 | 8 | 0 | 76
9:30 | 3509 | 516 | 1787.5 | 861 | 550 | 162 | 8 | 0 | 77
10:00 | 3469 | 516 | 1789 | 1029 | 550 | 162 | 8 | 0 | 78
10:30 | 3458.5 | 633.5 | 1777 | 1137.5 | 549.5 | 161 | 8 | 0 | 80
11:00 | 3448 | 751 | 1765 | 1246 | 549 | 160 | 8 | 0 | 82
11:30 | 3540.5 | 750.5 | 1785.5 | 1326 | 549.5 | 159 | 8 | 0 | 85
12:00 | 3633 | 750 | 1806 | 1406 | 550 | 158 | 8 | 0 | 88
12:30 | 3616.5 | 750 | 1846.5 | 1494.5 | 560 | 158 | 8 | 0 | 88
13:00 | 3600 | 750 | 1887 | 1583 | 570 | 158 | 8 | 0 | 88
13:30 | 3600 | 750 | 1887 | 1583 | 570 | 158 | 8 | 0 | 88
14:00 | 3600 | 750 | 1887 | 1583 | 570 | 158 | 8 | 0 | 88
14:30 | 3582.5 | 750.5 | 1801 | 1656.5 | 570 | 157.5 | 4 | 0 | 93
15:00 | 3565 | 751 | 1715 | 1730 | 570 | 157 | 0 | 0 | 98
15:30 | 3536 | 750.5 | 1719 | 1704 | 560 | 157.5 | 3 | 0 | 100
16:00 | 3507 | 750 | 1723 | 1678 | 550 | 158 | 6 | 0 | 102
16:30 | 3421.5 | 750 | 1669 | 1668 | 560 | 159.5 | 16.5 | 0 | 99
17:00 | 3336 | 750 | 1615 | 1658 | 570 | 161 | 27 | 0 | 96
17:30 | 3504 | 824.5 | 1732 | 2119.5 | 640 | 161 | 66.5 | 0 | 105
18:00 | 3672 | 899 | 1849 | 2581 | 710 | 161 | 106 | 0 | 114
18:30 | 3593 | 898 | 1782 | 2704 | 760 | 161 | 128.5 | 0 | 116
19:00 | 3514 | 897 | 1715 | 2827 | 810 | 161 | 151 | 0 | 118
19:30 | 3452 | 898 | 1736 | 2699 | 810 | 161 | 134 | 0 | 122
20:00 | 3415 | 898 | 1777 | 2595 | 810 | 162 | 118 | 0 | 120
20:30 | 3413 | 897.5 | 1822 | 2408 | 795 | 162 | 109.5 | 0 | 108
21:00 | 3411 | 897 | 1867 | 2221 | 780 | 162 | 101 | 0 | 96
21:30 | 3387.5 | 872.5 | 1870 | 2067 | 765 | 162 | 50.5 | 0 | 106
22:00 | 3364 | 848 | 1873 | 1913 | 750 | 162 | 0 | 0 | 116
22:30 | 3379.5 | 848.5 | 1885.5 | 1623 | 758.5 | 162 | 0 | 0 | 112
23:00 | 3395 | 849 | 1898 | 1333 | 767 | 162 | 0 | 0 | 108
23:30 | 3385 | 849 | 1901 | 1333 | 775.5 | 161 | 0 | 0 | 106 | Max Temp. in Dhaka |  | 33.5° C
24:00 | 3375 | 849 | 1904 | 1333 | 784 | 160 | 0 | 0 | 104
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 196.782 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 196.782 MKWHr
Note on W13: Author:

## Generation
g | 2020-11-12
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 86 | 86 | 88 | 89 | 91 | 92 | 91 | 92 | 92 | 92 | 90 | 88 | 88 | 86 | 87 | 88 | 91 | 91 |  | 91 | 91 | 92 | 92 | 92 | 92 | 90 | 2114945
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1696000
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 110 | 110 | 110 | 110 | 110 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2700000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 4 | 11 | 15 | 18 | 19 | 19 | 18 | 16 | 11 | 6 | 0 | [9 empty] | 137160
6 | Sikalbaha 225MW CCPP (Gas) | 202 | 204 | 204 | 205 | 203 | 204 | 217 | 203 | 204 | 204 | 205 | 217 | 205 | 204 | 217 | 204 | 203 | 212 |  | 204 | 204 | 204 | 204 | 204 | 216 | 204 | 4888916
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 11 | 51 |  | 51 | 34 | 34 | 17 |  |  | 0 | 170878
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 56 | 58 | 58 | 62 | 60 | 60 | 65 | 97 | 95 | 60 | 60 | 85 | 85 | 64 | 35 | 32 | 32 | 97 |  | 32 | 32 | 35 | 60 | 60 | 60 | 52 | 1596000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [10 empty] | 15 | 15 | 15 | 15 | 15 | 15 | 30 | 218 |  | 296 | 300 | 278 | 100 | 60 | 15 | 0 | 1149163
19 | Ashuganj 195MW PP (APSCL-United) | 26 | 26 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 250909
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 122 | 100 | 100 | 100 | 100 | 100 | 100 | 120 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 120 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3224000
23 | Ghorasal TPP Unit-5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2740500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4735927
26
28 | Ashuganj TPP Unit- 3 | 125 | 125 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 130 | 135 | 135 | 135 | 135 | 135 | 135 |  | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 2807624
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 29 | 29 | 29 | 29 | 29 | 29 | 25 | 25 | 26 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 655776
33 | Ashuganj 225 MW CCPP | 181 | 185 | 181 | 181 | 181 | 182 | 202 | 188 | 184 | 183 | 181 | 201 | 189 | 181 | 198 | 178 | 167 | 153 |  | 170 | 162 | 160 | 190 | 181 | 186 | 181 | 4484000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 275 | 275 | 275 | 275 | 345 | 315 | 305 | 305 | 305 | 345 | 325 | 310 | 330 | 310 | 290 | 365 |  | 370 | 370 | 360 | 260 | 260 | 260 | 260 | 7678700
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 387360
36 | Chandpur 150 MW CCPP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 71 | 72 | 70 | 71 | 50 | 50 | 51 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1270690
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 380 | 390 | 400 | 400 | 400 | 400 | 400 | 390 | 360 | 350 | 340 | 320 | 320 | 320 | 320 | 320 | 320 | 310 |  | 300 | 300 | 300 | 310 | 320 | 340 | 360 | 7478000
41 | Haripur 360MW CCPP(HPL) | 306 | 331 | 333 | 335 | 354 | 352 | 334 | 314 | 304 | 298 | 294 | 283 | 284 | 273 | 278 | 278 | 278 | 268 |  | 267 | 267 | 271 | 270 | 271 | 270 | 295 | 7089000
42 | RPCL 210MW CCPP | 105 | 104 | 105 | 106 | 106 | 106 | 106 | 105 | 103 | 102 | 86 | 87 | 70 | 70 | 71 | 87 | 88 | 87 |  | 88 | 83 | 83 | 84 | 85 | 89 | 89 | 2122000
43 | Mymensingh PV 50 MW Solar PP | [6 empty] | 7 | 25 | 39 | 49 | 54 | 54 | 50 | 42 | 31 | 12 | 1 | [9 empty] | 364000
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 44 | 44 | 43 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 1012000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP | 158 | 157 | 158 | 159 | 158 | 158 | 158 | 158 | 159 | 158 | 157 | 160 | 157 | 157 | 158 | 160 | 160 | 158 |  | 159 | 159 | 160 | 159 | 159 | 158 | 158 | 3612000
47 | Shahjibazar GTPP Unit- 8 & 9 | 67 | 67 | 68 | 67 | 69 | 67 | 67 | 67 | 67 | 65 | 40 | 40 | 63 | 63 | 40 | 40 | 40 | 65 |  | 40 | 40 | 40 | 52 | 52 | 52 | 53 | 1377312
48 | Shahjibazar 86MW PP (Shahjibazar) | 84 | 70 | 30 | 30 | 10 | 10 | 10 | 84 | 82 | 82 | 84 | 82 | 84 | 84 | 40 | 40 | 10 | 84 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 1585920
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 217 | 217 | 217 | 217 | 217 | 217 | 217 | 217 | 217 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 182 | 217 |  | 217 | 217 | 217 | 217 | 217 | 218 | 218 | 5263220
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 419000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | [6 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 183060
54 | Hobiganj 11MW PP Cofidence-E | 5 | 5 | [5 empty] | 5 |  | 2 | 2 | 2 | 2 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 128500
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 11 | 11 | 11 | 11 | 50 | 50 | 50 | 47 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1026600
56 | Shahjahanulla 25 MW PP | 24 | 6 | [5 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 420120
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 280 | 290 | 295 | 290 | 300 | 300 | 295 | 280 | 280 | 270 | 280 | 310 | 305 | 270 | 300 | 280 | 300 |  | 280 | 280 | 280 | 300 | 280 | 270 | 270 | 7167200
| Bibiyana South 400 MW | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 50 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 604900
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 30 | 35 |  | 35 | 35 | 17 | 17 |  |  | 0 | 135256
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 477456
61 | Narshingdi 22 MW PP (Doreen) | 19 | [9 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 267732
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | [10 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 275364
63 | Impoprt (Tripura) | 102 | 100 | 96 | 94 | 92 | 88 | 78 | 80 | 76 | 78 | 82 | 88 | 88 | 96 | 98 | 102 | 96 | 114 |  | 118 | 122 | 120 | 96 | 116 | 108 | 104 | 2330880
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 40 | 40 | 40 | 38 | 38 | 5 | 3 | 5 | 4 | 5 | 10 | 6 | 4 | 5 | 8 | 0 |  | 9 | 12 | 16 | 21 | 31 | 31 | 30 | 515040
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 445140
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 246240
67 | Jangalia 33MW PP (Summit) | 33 | 8 | 8 | 8 | 8 | 8 | 8 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 |  | 25 | 25 | 25 | 25 | 551800
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 15 | 15 | 15 | 15 | 18 | 18 | 18 | 18 | 20 | 20 | 20 | 20 |  | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 489480
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 32 | 28 | 28 | 25 | 32 | 32 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 18 |  | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 682020
71 | Maona 33 MW PP(Summit) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 25 | 25 | 25 | 561700
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 0 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 25 |  | 25 | 25 | 16 | 17 | 17 | 25 | 25 | 559800
73 | Ghorashal 108MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 291681
| Feni Lanka Power | [19 empty] | 17 | [5 empty] | 0 | 26220
| Chowmuhani 113 MW | [8 empty] | 10 | 55 | 55 | 55 | 55 | 69 | 103 | 106 | 105 | 105 |  | 113 | 113 | 113 | 113 | 113 | 113 | 55 | 1406160
| Manikgonj 162MW PP | [10 empty] | 36 | 77 | 71 | 44 | 64 | 55 | 32 | [9 empty] | 391680
77 | Siddhirganj 100 PP(Dutch Bangla) | [9 empty] | 27 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 100 |  | 100 | 100 | 100 | 90 | 50 | 30 | 0 | 894720
78 | Gazipur 52 MW PP | [8 empty] | 9 | 33 | 33 | 33 | 33 | 33 | 33 | 8 |  | 51 |  | 51 | 51 | 51 | 51 | 34 | 8 | 8 | 500136
79 | Kodda 150MW PP | [15 empty] | 6 | 16 | 55 |  | 100 | 100 | 84 | 84 |  |  | 0 | 349440
80 | Jamalpur 95 MW PP(Powerpac) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 24 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 770880
81 | Jangalia 52 MW PP (Lakdanavi) | [17 empty] | 33 |  | 52 | 52 | 25 |  |  |  |  | 132296
| Gazipur 100 MW PP | 35 | [6 empty] | 50 | 63 | 102 | 102 | 101 | 101 | 101 | 90 | 85 | 52 | 82 |  | 101 | 101 | 101 | 70 | 52 | 52 | 52 | 1444872
| Kaptai 7 MW Solar PP | [6 empty] | 1 | 2 | 3 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 29160
| Jodiac Power | 54 | 54 | 35 | 17 | 17 | 17 | 17 | 36 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1139481
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | [10 empty] | 10 | 40 | 48 | 48 | 48 | 48 | 48 | 64 |  | 80 | 99 | 97 | 97 | 97 | 30 | 15 | 860712
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP(Summit) | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3495331
87 | Meghnaghat 100 MW(IEL) | [12 empty] | 10 | 16 | 16 | 16 | 21 | 74 |  | 94 | 100 | 100 | 75 | 46 |  | 0 | 500160
| Meghnaghat 104 MW PP (OPCL) | 34 | [6 empty] | 23 | 56 | 89 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1480320
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 50 | 50 | 10 | 10 | 10 | 40 | 49 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 49 |  | 49 | 49 | 50 | 50 | 50 | 50 | 50 | 1058688
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 5 | 5 | 5 | 5 | 5 | 25 | 51 | 51 | 43 | 43 | 43 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 960146
94 | Gagnagar 102 MW PP (Digital Power) | [9 empty] | 72 | 84 | 94 | 94 | 94 | 94 | 94 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 48 | 48 | 1270800
95 | Patenga 50MW PP (Baraka) | 24 | 0 | [5 empty] | 5 | 18 | 19 | 36 | 46 | 45 | 45 | 44 | 45 | 47 | 49 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 738240
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | [9 empty] | 8 | 30 | 30 | 35 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 15 | 0 | 670310
100 | Manikganj 55 MW PP (Northern) | [12 empty] | 17 | 17 | 17 | 17 | 17 | 55 |  | 55 | 55 | 55 | 55 | 17 |  | 0 | 342415
101 | Kushiara 163 MW CCPP (KP) | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 |  | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 2532927
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | [9 empty] | 15100
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 17 | 1004760
104 | Keranigonj 300 MW PP (APR) | [25 empty] | 0 | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [16 empty] | 10 | 84 |  | 70 | 70 | 70 | 60 | 24 | 24 | 0 | 422400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [9 empty] | 10 | 15 | 15 | 15 | 15 | 15 | 15 | 16 | 95 |  | 138 | 80 | 83 |  |  |  | 0 | 465264
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 20 | 10 | 10 | 10 | 10 | 10 | 10 | 80 | 90 | 90 | 90 | 90 | 90 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1731840
116 | Chandpur 200MW (Desh energy) | [25 empty] | 0 | 0
117 | Ashuganj 150MW PP (Midland) | [8 empty] | 1 | 38 | 40 | 40 | 50 | 56 | 90 | 108 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 50 | 0 | 1246181
118 | Bibiyana-III 400 MW CCPP | 401 | 401 | 400 | 400 | 400 | 401 | 401 | 401 | 401 | 404 | 403 | 404 | 404 | 404 | 404 | 403 | 379 | 402 |  | 402 | 401 | 402 | 402 | 402 | 402 | 400 | 9618000
| Jamalpur 115 MW PP (United) | 35 | [6 empty] | 24 | 31 | 45 | 45 | 45 | 75 | 86 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 95 | 1580400
| Anwara 300 MW PP (United) | 16 | [7 empty] | 16 | 16 | 66 | 82 | 137 | 157 | 123 | 123 | 86 | 160 |  | 160 | 160 | 160 | 160 | 160 | 142 | 125 | 1911927
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2451840
120 | Eastern Zone Total | 5141 | 4825 | 4619 | 4574 | 4522 | 4501 | 4603 | 4953 | 5146 | 5400 | 5587 | 5802 | 5900 | 5894 | 5884 | 5842 | 5618 | 6673 |  | 6874 | 6805 | 6690 | 6314 | 5999 | 5646 | 5377 | 132413775
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [16 empty] | 4 | 99 |  | 66 | 42 | 16 |  |  |  |  | 221760
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [8 empty] | 37 | 53 | 53 | 53 | 90 | 90 | 90 | 53 | 53 | 90 |  | 90 | 90 | 90 | 90 | 17 |  | 0 | 981120
130
131
132
133 | Bhola Nutan Biddut BD LTD (GAS) | 35 | 35 | 35 | 36 | 35 | 35 | 35 | 35 | 35 | 37 | 35 | 35 | 35 | 36 | 35 | 35 | 34 | 35 |  | 35 | 35 | 35 | 36 | 35 | 37 | 36 | 903270
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [16 empty] | 20 | 48 |  | 32 | 16 | 16 | 16 | 16 |  | 0 | 132480
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 82 | 37 | 24 | 24 | 24 | 24 | 24 | 24 | 23 | 23 | 23 | 23 | 62 | 62 | 62 | 63 | 65 | 75 |  | 88 | 88 | 88 | 88 | 88 | 87 | 87 | 1300947
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 18 | 20 | 19 | 23 | 22 | 17 | 18 | 12 | 12 | 11 | 21 | 22 | 22 | 22 | 15 | 20 | 23 | 28 |  | 28 | 28 | 28 | 29 | 29 | 27 | 26 | 504700
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 24 |  | 24 | 10 | [5 empty] | 55125
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 612 | 612 | 613 | 516 | 517 | 517 | 516 | 516 | 516 | 516 | 751 | 750 | 750 | 750 | 751 | 750 | 750 | 899 |  | 897 | 898 | 898 | 897 | 848 | 849 | 849 | 16682181
147 | Bheramara 410 MW CCPP | 360 | 370 | 375 | 385 | 335 | 335 | 340 | 345 | 345 | 345 | 345 | 370 | 356 | 345 | 375 | 360 | 350 | 415 |  | 300 | 270 | 270 | 270 | 270 | 270 | 270 | 8422848
148 | Payra 1320 MW | 490 | 430 | 350 | 350 | 350 | 350 | 350 | 350 | 400 | 400 | 400 | 400 | 420 | 420 | 420 | 400 | 420 | 560 |  | 660 | 660 | 660 | 630 | 600 | 570 | 570 | 11034500
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2 | [24 empty] | 47 | 64 | 160582
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3679500
153 | Baghabari 71 MW GTPP | [13 empty] | 40 | 50 | 50 | 50 | 50 |  | 40 | 40 | 40 | 35 |  |  |  | 340000
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 158 | 152 | 154 | 153 | 148 | 151 | 159 | 164 | 157 | 151 | 154 | 180 | 179 | 168 | 153 | 157 | 140 | 139 |  | 154 | 144 | 146 | 150 | 144 | 145 | 148 | 3930373
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 163 | 158 | 159 | 166 | 161 | 163 | 165 | 170 | 167 | 158 | 158 | 165 | 201 | 183 | 171 | 165 | 159 | 182 |  | 167 | 158 | 160 | 164 | 158 | 159 | 162 | 4221373
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 360 | 350 | 370 | 345 | 345 | 410 | 415 | 414 | 363 | 382 | 359 | 418 | 423 | 338 | 349 | 320 | 255 | 421 |  | 296 | 314 | 346 | 399 | 406 | 423 | 387 | 9082909
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 3 | 3 | 3 | 3 | 3 | 3 | 18 | 22 | 22 | 22 | 22 | 21 | 21 | 18 | 18 | 18 | 21 |  | 21 | 21 | 21 | 22 | 21 | 21 | 21 | 388560
163 | Bogura 20 MW PP (Energyprima) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 230760
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 230688
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [19 empty] | 8 | [5 empty] | 0 | 14400
170 | Chapainawabganj 100 MW Peaking PP | [8 empty] | 8 | 8 | 8 | 8 | 8 | 8 | [11 empty] | 0 | 5072
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [19 empty] | 35 | [5 empty] | 0 | 47616
172 | Confidence Power Bogura Unit-1 113 MW | [11 empty] | 20 | 40 | 50 | 50 | 50 | 50 | 90 |  | 109 | 109 | 109 | 111 | 111 |  | 0 | 893376
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [10 empty] | 5 | 39 | 40 | 40 | 37 | 39 | 34 | 72 |  | 98 | 113 | 111 | 113 | 113 | 60 | 0 | 864960
177 | Sympa Solar Power 8MW | [6 empty] | 1 | 2 | 3 | 5 | 6 | 6 | 5 | 5 | 3 | 2 | 1 | [9 empty] | 39160
178
178