## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-11-14 | Saturday
|  |  | Date (day): | 2020-11-14 |  | Saturday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13177.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14511 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-11-13 | 2020-11-14 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 120 | 150 | 150
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 115 | 115 | 115 | 75 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 200 | 200 | 165 |  | Gas shortage
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 12 | 12 | 12 |  | 96 | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under S/D for dust in gas.
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 319 | 334 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 330 | 400 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 150 | 150 | 150 | 150 |  | 150 | GT-1 Under maint.
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 50 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 16 | 19 | 19 |  | 3 | Engine problem
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 95 | 82 | 100 | 100 | 110 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 64 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 38 | 50 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 16 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 22 | 53 | 100 | 100
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 90 | 90 | 90 |  | 14 | Engine problem
|  | Manikgonj 162MW PP |  | HFO | IPP | 9*18 | 0 | 0 | 18 | 0 | 0 | 0
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 1499 | 1781 | 3400 | 3740 | 692 | 1422
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 115 | 115 | 120 | 120 | 60 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 8 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 157 | 158 | 160 | 160 | 70 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 207 | 208 | 215 | 225
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 102 | 102
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 10 | 100 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 42 | 42 | 10 | 10
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 100 | 100 |  | 8 | Engine problem
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 16 | 144 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 54 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 30 | 100 | 100 | 100
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 645 | 991 | 1691 | 1676 | 460 | 106
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 135 | 80 | 100 | 100 | 35 |  | Gas Shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 192 | 196 | 225 | 225 |  |  | FGMO
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 340 | 315 | 360 | 360 |  |  | FGMO
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 29 | 30 | 30 | 15 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 30 | 20 | 20 | 20 | 35 |  | Gas shortage
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 45 | 26 | 26 | 26 | 169 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 10 | 51 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 50 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 74 | 75 | 90 | 90 |  | 57 | ST Under maint.
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 165 | 180
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 90 | 112 | 156 | 172
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 8 | 33 | 33 | 33
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 21 | 20 | 21
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 65 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 998 | 1103 | 1738 | 2020 | 517 | 417
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 100 | 122 | 163 | 163 | 39 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 17 | 22 | 22
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 33 | 33 | 33 | 33 |  | 62 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 16 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 8 | 115 | 115 | 115
|  | Mymensingh PV 50 MW Solar PP |  | Solar | IPP | 50 | 0 | 0 | 53 | 0 | 50 | 0
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 196 | 303 | 584.6 | 533 | 39 | 62
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 41 | 44 | 44 | 44
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 22 | 22 |  | 68 | Unit-4 under shut down
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 107 | 107 | 110 | 110 |  | 54 | STG under maint.
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 158 | 157 | 160 | 160 |  | 170 | GT-2 S/D due to gas shortage.
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 11 | 50 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 30 | 50 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 3 | 11 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 67 | 66 | 66 |  |  | FGMO
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 30 | 84 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 165 | 217 | 220 | 220
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 25 | 25
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 315 | 341 | 341 |  |  | FGMO
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 353 | 402 | 400 | 400
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 35 | 30 | 40 | 40
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1317 | 1578 | 1648 | 1648 | 0 | 292
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 408 | 688 | 555 | 796
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 335 | 360 | 410 | 410
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 105 | 105 | 105
| 108 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 760 | 1153 | 1325 | 1992 | 0 | 0
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 20 | 28 | 22 | 22
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 23 | 91 | 95 | 95
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 350 | 570 | 600 | 660
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 35 | 10 | 35 | 35
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 428 | 715 | 862 | 922 | 0 | 194
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 |  |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 60 | 70 | 70 | 70 | 30 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | Gas shortage & ST Under maint
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 188 | 186 | 220 | 220 |  |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 201 | 195 | 220 | 220 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 347 | 416 | 413 | 413 |  | 414 | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 33
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 10 | 10
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 113 | 113
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 109 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 829 | 1009 | 1594 | 1717 | 130 | 624
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 63 | 61 | 64 | 0 | 85 |  | Coal Shortage.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 71 | 113 | 113
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 219 | 282 | 335 | 263 | 294 | 40
|  | Total |  |  |  |  | 20383 | 19892 | 6891 | 8915 | 13177.6 | 14511 | 2132 | 3157
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6436.4955 | 8327 | 12308.4549 | 13553.9088
| A. |  | 2020-11-13 | (Yesterday) |  |  |  |  | Friday
| 1 | Highest Generation : |  |  | 8915 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
| 2 | Minimum Generation : |  |  | 6243 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8915 | MW
| 3 | Day peak Generation : |  |  | 6891 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8327 | MW
| 4 | Evening peak Generation : |  |  | 8915 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 176.8964 | MKWHr | By Solar | 0.57468 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 125.1815 | MKWHr |  | By Oil: | 17.5937 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 15.5573 | MKWHr |  | By Hydro: | 3.7364 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2132 | MW | Dhaka | 2970 | 2970 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3157 | MW | Chittagong | 941 | 941 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5289 | MW | Khulna | 1014 | 1014 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1036.17 | MMCFD |  |  | Rajshahi | 803 | 803 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 144640434.304 | ii) Oil : | Taka | 109285206.99 | Comilla | 837 | 837 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 74425699.89 | Total | Taka | 328351341.184 | Mymensingh | 651 | 651 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 365 | 365 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 392 | MW (E to W) at | 19:30 | hrs | Barisal | 237 | 237 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 115 | MW at | 18:00 | hrs | Rangpur | 509 | 509 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 33.8° C |  |  | Total | 8327 | 8327 |  | 0
| B. |  | 2020-11-14 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 30.6° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14511 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 7500 | MW
| 4 | Reserve(Generation end) |  |  |  | 4711 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 194.4571 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6298 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 12.0545 | MKWHr. | ii) HVDC Flow at Peak Time |  | 688 | MW at | 19:30 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.1984 | MKWHr. | iii) Maximum HVDC Flow : |  | 689 | MW at | 19:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 103.58 |  | (b) Today: | 103.49 |  | (c) Rule Curve: |  | 107.7
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-11-13
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Mymensingh PV 50 MW Solar PP | Manikgonj 162MW PP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 153 | 115 | 200 | 12 | 0 | 0 | 294 |  | 0 | 380 | 150 | 0 | 15 | 0 | 0 | 0 | 55 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 25 | 25 | 0 | 0 | 86 | 70 | 115 | 0 | 0 | 206 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 31 | 135 | 0 | 0 | 260 | 0 | 180 | 8 | 50 | 29 | 10 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 25 | 21 | 100 | 89 | 33 | 20 | 0 | 41 | 0 | 50 | 50 | 107 | 157 | 52 | 84 | 0 | 217 | 18 | 0 | 10 | 270 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 400 | 65 | 52 | 0 | 0 | 87 | 54 | 0 | 0 | 8 | 100 | 40 | 90 | 0 | 0 |  | 605 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 62 | 151 | 0 | 0 | 0 | 0 | 145 | 0 | 89 | 0 | 159 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 36 | 0 |  | 5240 | 2498 | 7738 | 3394 | 605 | 1925 | 845 | 713 | 156 | 0 | 100 | 0 | 0 | 103.59
2:00 | 0 | 0 | 150 | 115 | 200 | 12 | 0 | 0 | 294 |  | 0 | 390 | 150 | 0 | 15 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 25 | 25 | 0 | 0 | 86 | 70 | 115 | 0 | 0 | 205 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 20 | 31 | 135 | 0 | 0 | 260 | 0 | 190 | 8 | 50 | 29 | 10 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 25 | 21 | 44 | 89 | 33 | 20 | 0 | 41 | 0 | 50 | 50 | 107 | 157 | 52 | 84 | 0 | 217 | 18 | 0 | 10 | 295 | 24 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 400 | 24 | 52 | 0 | 0 | 16 | 54 | 0 | 0 | 0 | 100 | 40 | 58 | 0 | 0 |  | 414 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 59 | 150 | 0 | 0 | 0 | 0 | 147 | 0 | 88 | 0 | 161 | 0 | 419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 35 | 0 |  | 5021 | 2328 | 7349 | 3401 | 414 | 1981 | 644 | 709 | 156 | 0 | 44 | 0 | 0 | 103.59
3:00 | 0 | 0 | 100 | 115 | 200 | 12 | 0 | 0 | 320 |  | 0 | 400 | 150 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 25 | 25 | 0 | 0 | 86 | 70 | 115 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 33 | 135 | 0 | 0 | 270 | 0 | 189 | 8 | 50 | 29 | 10 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 25 | 21 | 92 | 89 | 33 | 20 | 0 | 41 | 0 | 50 | 50 | 107 | 157 | 40 | 40 | 0 | 217 | 18 | 0 | 10 | 280 | 24 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 401 | 8 | 35 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 100 | 40 | 17 | 0 | 0 |  | 414 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 60 | 150 | 0 | 0 | 0 | 0 | 145 | 0 | 87 | 0 | 160 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 35 | 0 |  | 4833 | 2255 | 7088 | 3344 | 414 | 1909 | 483 | 690 | 156 | 0 | 92 | 0 | 0 | 103.59
4:00 | 0 | 0 | 100 | 115 | 200 | 12 | 0 | 0 | 320 |  | 0 | 400 | 150 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 25 | 25 | 0 | 0 | 88 | 70 | 115 | 0 | 0 | 205 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 33 | 135 | 0 | 0 | 260 | 0 | 181 | 8 | 50 | 29 | 10 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 25 | 21 | 90 | 90 | 33 | 20 | 0 | 41 | 0 | 50 | 50 | 107 | 156 | 40 | 10 | 0 | 217 | 18 | 0 | 10 | 275 | 24 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 400 | 8 | 17 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 100 | 39 | 17 | 0 | 0 |  | 414 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 59 | 150 | 0 | 0 | 0 | 0 | 145 | 0 | 87 | 0 | 159 | 0 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 34 | 0 |  | 4723 | 2215 | 6938 | 3325 | 414 | 1836 | 426 | 689 | 158 | 0 | 90 | 0 | 0 | 103.58
5:00 | 0 | 0 | 100 | 115 | 200 | 12 | 0 | 0 | 320 |  | 0 | 360 | 150 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 25 | 25 | 0 | 0 | 88 | 70 | 115 | 0 | 0 | 207 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 33 | 135 | 0 | 0 | 265 | 0 | 181 | 8 | 50 | 29 | 10 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 25 | 21 | 86 | 90 | 33 | 20 | 0 | 41 | 0 | 11 | 10 | 107 | 157 | 40 | 10 | 0 | 217 | 18 | 0 | 10 | 280 | 24 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 400 | 8 | 17 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 100 | 40 | 17 | 0 | 0 |  | 414 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 62 | 150 | 0 | 0 | 0 | 0 | 144 | 0 | 25 | 0 | 158 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 36 | 0 |  | 4575 | 2152 | 6727 | 3332 | 414 | 1658 | 387 | 692 | 158 | 0 | 86 | 0 | 0 | 103.58
6:00 | 0 | 0 | 100 | 115 | 200 | 12 | 0 | 0 | 327 |  | 0 | 330 | 150 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 0 | 25 | 0 | 0 | 88 | 70 | 115 | 0 | 0 | 207 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 37 | 120 | 0 | 0 | 265 | 0 | 160 | 8 | 50 | 29 | 10 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 25 | 21 | 80 | 106 | 33 | 0 | 0 | 41 | 0 | 11 | 10 | 107 | 160 | 40 | 10 | 0 | 217 | 18 | 0 | 10 | 270 | 24 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 399 | 8 | 17 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 100 | 40 | 17 | 0 | 0 |  | 414 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 61 | 150 | 0 | 0 | 0 | 0 | 145 | 0 | 24 | 0 | 160 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 36 | 0 |  | 4454 | 2082 | 6536 | 3219 | 414 | 1597 | 387 | 681 | 158 | 0 | 80 | 0 | 0 | 103.58
7:00 | 0 | 0 | 100 | 115 | 200 | 12 | 0 | 0 | 298 |  | 0 | 330 | 150 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 0 | 25 | 0 | 0 | 90 | 70 | 115 | 0 | 0 | 216 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 100 | 0 | 0 | 300 | 0 | 201 | 8 | 51 | 10 | 10 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 25 | 15 | 72 | 106 | 33 | 0 | 0 | 41 | 0 | 11 | 10 | 107 | 158 | 40 | 10 | 0 | 185 | 18 | 0 | 10 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 0 | 351 | 8 | 17 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 40 | 40 | 17 | 5 | 0 |  | 414 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 63 | 150 | 0 | 0 | 0 | 0 | 138 | 0 | 23 | 0 | 139 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 350 | 35 | 0 |  | 4377 | 1903 | 6280 | 3145 | 414 | 1559 | 357 | 563 | 160 | 0 | 72 | 10 | 0 | 103.57
8:00 | 0 | 0 | 100 | 115 | 200 | 12 | 0 | 0 | 288 |  | 0 | 330 | 150 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 28 | 25 | 25 | 0 | 0 | 91 | 70 | 115 | 0 | 0 | 205 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 39 | 100 | 0 | 0 | 285 | 0 | 197 | 8 | 50 | 29 | 10 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 12 | 15 | 60 | 105 | 33 | 0 | 1 | 41 | 0 | 11 | 10 | 107 | 157 | 40 | 10 | 0 | 165 | 18 | 0 | 8 | 310 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 10 | 0 | 0 | 351 | 8 | 17 | 0 | 2 | 0 | 35 | 0 | 0 | 0 | 40 | 40 | 17 | 25 | 0 |  | 407 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 64 | 150 | 0 | 0 | 0 | 0 | 169 | 0 | 23 | 0 | 173 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 350 | 37 | 0 |  | 4338 | 2057 | 6395 | 3248 | 407 | 1587 | 327 | 564 | 161 | 0 | 60 | 41 | 0 | 103.57
9:00 | 0 | 0 | 100 | 115 | 200 | 12 | 0 | 0 | 288 |  | 0 | 330 | 150 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 6 | 25 | 25 | 0 | 0 | 93 | 70 | 115 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 41 | 100 | 0 | 0 | 260 | 0 | 180 | 8 | 73 | 29 | 10 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 8 | 15 | 60 | 105 | 33 | 0 | 2 | 41 | 0 | 11 | 10 | 107 | 157 | 40 | 10 | 0 | 164 | 18 | 0 | 9 | 280 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 10 | 0 | 0 | 351 | 8 | 17 | 0 | 3 | 0 | 17 | 0 | 0 | 0 | 40 | 40 | 17 | 39 | 18 |  | 408 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 47 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 23 | 0 | 156 | 0 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 330 | 36 | 0 |  | 4286 | 1957 | 6243 | 3137 | 408 | 1559 | 327 | 527 | 163 | 0 | 60 | 62 | 0 | 103.57
10:00 | 0 | 0 | 100 | 115 | 200 | 12 | 0 | 0 | 288 |  | 0 | 330 | 150 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 22 | 25 | 25 | 0 | 0 | 92 | 70 | 115 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 41 | 100 | 0 | 0 | 265 | 0 | 193 | 8 | 74 | 29 | 10 | 0 | 10 | 0 | 0 | 0 | 19 | 11 | 8 | 15 | 78 | 101 | 33 | 0 | 2 | 41 | 0 | 11 | 10 | 107 | 159 | 40 | 5 | 0 | 164 | 18 | 0 | 10 | 270 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 0 | 0 | 354 | 8 | 17 | 0 | 4 | 0 | 17 | 0 | 0 | 0 | 10 | 40 | 17 | 47 | 18 |  | 408 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 63 | 150 | 0 | 0 | 0 | 0 | 153 | 0 | 23 | 0 | 157 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 300 | 35 | 0 |  | 4274 | 1889 | 6163 | 3155 | 408 | 1474 | 297 | 513 | 162 | 0 | 78 | 76 | 0 | 103.57
11:00 | 0 | 0 | 100 | 115 | 200 | 12 | 0 | 0 | 296 |  | 0 | 330 | 150 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 22 | 25 | 25 | 0 | 0 | 90 | 70 | 115 | 0 | 0 | 229 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 41 | 100 | 0 | 0 | 355 | 0 | 208 | 8 | 73 | 29 | 10 | 0 | 10 | 0 | 0 | 0 | 19 | 11 | 8 | 15 | 80 | 99 | 33 | 0 | 2 | 41 | 0 | 11 | 10 | 107 | 158 | 40 | 5 | 0 | 164 | 18 | 0 | 10 | 310 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 0 | 0 | 354 | 8 | 17 | 0 | 4 | 0 | 17 | 0 | 0 | 0 | 10 | 45 | 17 | 52 | 0 |  | 408 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 63 | 150 | 0 | 0 | 0 | 0 | 186 | 0 | 23 | 0 | 169 | 0 | 276 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 320 | 34 | 0 |  | 4463 | 2007 | 6470 | 3393 | 408 | 1534 | 279 | 533 | 160 | 0 | 80 | 83 | 0 | 103.56
12:00 | 0 | 0 | 100 | 115 | 200 | 12 | 0 | 0 | 319 |  | 0 | 330 | 150 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 13 | 25 | 25 | 0 | 0 | 87 | 70 | 115 | 0 | 0 | 207 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 8 | 20 | 42 | 135 | 0 | 0 | 340 | 0 | 192 | 45 | 74 | 29 | 30 | 0 | 10 | 0 | 0 | 0 | 19 | 11 | 8 | 15 | 90 | 100 | 33 | 0 | 2 | 41 | 0 | 11 | 30 | 107 | 158 | 40 | 30 | 0 | 165 | 18 | 0 | 10 | 300 | 16 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 0 | 0 | 353 | 8 | 22 | 0 | 4 | 16 | 17 | 0 | 0 | 0 | 30 | 35 | 17 | 53 | 18 |  | 408 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 63 | 150 | 0 | 0 | 0 | 0 | 188 | 0 | 23 | 0 | 201 | 0 | 347 | 17 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 350 | 35 | 0 |  | 4655 | 2236 | 6891 | 3503 | 408 | 1723 | 363 | 563 | 157 | 0 | 90 | 84 | 0 | #REF!
13:00 | 0 | 0 | 170 | 115 | 200 | 12 | 0 | 0 | 343 |  | 0 | 330 | 150 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 16 | 25 | 13 | 25 | 25 | 0 | 0 | 85 | 70 | 115 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 20 | 42 | 135 | 0 | 0 | 330 | 0 | 181 | 45 | 70 | 29 | 30 | 0 | 10 | 0 | 0 | 0 | 19 | 11 | 33 | 15 | 94 | 99 | 33 | 0 | 2 | 41 | 0 | 50 | 35 | 107 | 159 | 65 | 82 | 0 | 192 | 18 | 0 | 10 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 48 | 0 | 0 | 402 | 16 | 34 | 0 | 4 | 33 | 17 | 0 | 0 | 0 | 58 | 30 | 18 | 49 | 18 |  | 501 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 62 | 150 | 0 | 0 | 0 | 0 | 183 | 0 | 39 | 0 | 197 | 0 | 379 | 17 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 400 | 0 | 0 |  | 5090 | 2402 | 7492 | 3676 | 501 | 1857 | 519 | 612 | 155 | 0 | 94 | 78 | 7492 | 103.55
14:00 | 0 | 0 | 120 | 115 | 200 | 12 | 0 | 0 | 288 |  | 0 | 330 | 150 | 0 | 0 | 7 | 0 | 0 | 32 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 25 | 10 | 25 | 25 | 0 | 0 | 85 | 70 | 115 | 0 | 0 | 206 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 36 | 20 | 42 | 100 | 0 | 0 | 260 | 0 | 181 | 45 | 73 | 29 | 40 | 0 | 35 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 94 | 98 | 33 | 0 | 2 | 41 | 0 | 22 | 20 | 107 | 158 | 40 | 40 | 0 | 185 | 18 | 0 | 10 | 260 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 50 | 0 | 13 | 353 | 35 | 34 | 0 | 4 | 33 | 47 | 0 | 0 | 36 | 77 | 30 | 71 | 42 | 18 |  | 502 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 60 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 40 | 0 | 130 | 0 | 270 | 35 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 350 | 0 | 0 |  | 4864 | 2076 | 6940 | 3187 | 502 | 1604 | 769 | 560 | 155 | 0 | 94 | 69 | 0 | 103.55
15:00 | 0 | 0 | 120 | 115 | 200 | 12 | 0 | 0 | 287 |  | 0 | 350 | 150 | 0 | 0 | 15 | 0 | 0 | 35 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 25 | 10 | 25 | 25 | 0 | 0 | 85 | 70 | 110 | 0 | 0 | 205 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 43 | 20 | 39 | 100 | 0 | 0 | 290 | 0 | 185 | 26 | 75 | 29 | 20 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 94 | 98 | 33 | 0 | 1 | 43 | 0 | 22 | 20 | 107 | 160 | 50 | 40 | 0 | 185 | 18 | 0 | 10 | 300 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 50 | 0 | 10 | 354 | 35 | 35 | 0 | 2 | 33 | 54 | 0 | 0 | 8 | 77 | 30 | 90 | 29 | 44 |  | 497 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 60 | 150 | 0 | 0 | 0 | 0 | 143 | 0 | 35 | 0 | 142 | 0 | 339 | 17 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 350 | 0 | 0 |  | 4921 | 2177 | 7098 | 3300 | 497 | 1690 | 755 | 560 | 155 | 0 | 94 | 47 | 0 | 103.54
16:00 | 0 | 0 | 120 | 115 | 200 | 12 | 0 | 0 | 287 |  | 0 | 350 | 150 | 0 | 0 | 15 | 0 | 0 | 32 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 10 | 25 | 16 | 0 | 0 | 86 | 70 | 110 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 20 | 40 | 100 | 0 | 0 | 275 | 0 | 179 | 26 | 72 | 29 | 20 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 98 | 98 | 33 | 0 | 0 | 43 | 0 | 22 | 20 | 107 | 159 | 51 | 20 | 0 | 185 | 18 | 0 | 10 | 270 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 20 | 0 | 10 | 353 | 8 | 35 | 0 | 1 | 16 | 54 | 0 | 0 | 8 | 77 | 30 | 70 | 11 | 23 |  | 497 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 62 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 35 | 0 | 161 | 0 | 303 | 17 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 350 | 0 | 0 |  | 4661 | 2172 | 6833 | 3290 | 497 | 1607 | 603 | 562 | 156 | 0 | 98 | 20 | 0 | 103.53
17:00 | 0 | 0 | 120 | 115 | 200 | 12 | 0 | 0 | 259 |  | 0 | 350 | 150 | 1 | 2 | 15 | 0 | 0 | 32 | 3 | 7 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 16 | 25 | 10 | 25 | 16 | 0 | 0 | 87 | 70 | 110 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 41 | 80 | 0 | 0 | 275 | 0 | 178 | 26 | 70 | 29 | 20 | 0 | 43 | 0 | 0 | 1 | 19 | 11 | 33 | 21 | 100 | 103 | 33 | 0 | 0 | 44 | 0 | 22 | 20 | 107 | 160 | 52 | 20 | 0 | 152 | 18 | 0 | 10 | 280 | 16 | 8 | 0 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 20 | 0 | 15 | 304 | 9 | 35 | 0 | 0 | 16 | 54 | 0 | 0 | 8 | 90 | 30 | 53 | 1 | 28 |  | 498 | 0 | 280 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 16 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 62 | 150 | 0 | 0 | 0 | 0 | 153 | 0 | 35 | 0 | 158 | 0 | 298 | 17 | 0 | 0 | 0 | 12 | 0 | 0 | 20 | 350 | 0 | 0 |  | 4587 | 2178 | 6765 | 3168 | 498 | 1585 | 694 | 562 | 157 | 0 | 100 | 1 | 0 | 103.53
18:00 | 0 | 0 | 120 | 115 | 200 | 12 | 0 | 0 | 305 |  | 0 | 400 | 150 | 20 | 30 | 30 | 0 | 0 | 82 | 30 | 94 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 0 | 16 | 25 | 15 | 25 | 16 | 0 | 0 | 88 | 70 | 110 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 41 | 20 | 41 | 80 | 0 | 0 | 295 | 0 | 178 | 26 | 70 | 26 | 20 | 0 | 43 | 0 | 0 | 16 | 19 | 11 | 33 | 21 | 118 | 155 | 33 | 0 | 0 | 44 | 0 | 50 | 40 | 107 | 159 | 67 | 84 | 0 | 202 | 18 | 0 | 10 | 270 | 16 | 8 | 0 | 35 | 0 | 0 | 40 | 0 | 0 | 0 | 100 | 0 | 61 | 399 | 92 | 36 | 0 | 0 | 132 | 54 | 0 | 0 | 94 | 100 | 30 | 76 | 0 | 29 |  | 683 | 0 | 345 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 32 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 63 | 150 | 0 | 0 | 0 | 0 | 151 | 0 | 78 | 0 | 156 | 0 | 367 | 105 | 0 | 0 | 0 | 76 | 0 | 0 | 90 | 460 | 0 | 0 |  | 5862 | 2902 | 8764 | 3512 | 683 | 1902 | 1701 | 673 | 158 | 17 | 118 | 0 | 0 | 103.53
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 120 | 115 | 200 | 12 | 0 | 0 | 334 |  | 0 | 400 | 150 | 24 | 0 | 0 | 0 | 0 | 82 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 16 | 25 | 25 | 25 | 16 | 0 | 0 | 88 | 70 | 110 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 41 | 80 | 0 | 0 | 305 | 0 | 192 | 26 | 75 | 29 | 20 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 116 | 123 | 33 | 17 | 0 | 44 | 0 | 50 | 50 | 107 | 158 | 65 | 84 | 0 | 217 | 18 | 0 | 10 | 280 | 16 | 11 | 0 | 15 | 0 | 0 | 16 | 0 | 0 | 0 | 100 | 0 | 50 | 402 | 115 | 52 | 0 | 0 | 132 | 54 | 0 | 0 | 65 | 100 | 30 | 90 | 0 | 0 |  | 689 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 32 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 62 | 150 | 0 | 0 | 0 | 0 | 166 | 0 | 90 | 0 | 173 | 0 | 416 | 105 | 0 | 0 | 0 | 98 | 0 | 0 | 109 | 570 | 17 | 0 |  | 5725 | 3158 | 8883 | 3592 | 689 | 2038 | 1508 | 782 | 158 | 0 | 116 | 0 | 0 | 103.51
19:30 | 0 | 0 | 120 | 115 | 200 | 12 | 0 | 0 | 334 |  | 0 | 400 | 150 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 16 | 25 | 25 | 25 | 16 | 0 | 0 | 88 | 70 | 115 | 0 | 0 | 208 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 42 | 80 | 0 | 0 | 315 | 0 | 196 | 26 | 75 | 29 | 20 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 112 | 122 | 33 | 17 | 0 | 44 | 0 | 50 | 50 | 107 | 157 | 67 | 84 | 0 | 217 | 18 | 0 | 10 | 315 | 16 | 11 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 100 | 0 | 50 | 402 | 115 | 53 | 0 | 0 | 144 | 54 | 0 | 0 | 65 | 100 | 30 | 90 | 0 | 0 |  | 688 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 16 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 61 | 150 | 0 | 0 | 0 | 0 | 186 | 0 | 91 | 0 | 195 | 0 | 416 | 105 | 0 | 0 | 0 | 71 | 0 | 0 | 109 | 570 | 10 | 0 |  | 5756 | 3159 | 8915 | 3669 | 688 | 2068 | 1439 | 781 | 158 | 0 | 112 | 0 | 0 | 0
20:00 | 0 | 0 | 120 | 115 | 200 | 12 | 0 | 0 | 334 |  | 0 | 400 | 150 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 30 | 25 | 16 | 0 | 0 | 89 | 70 | 115 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 40 | 80 | 0 | 0 | 300 | 0 | 189 | 26 | 75 | 29 | 20 | 0 | 51 | 0 | 0 | 0 | 16 | 11 | 33 | 21 | 102 | 123 | 33 | 17 | 0 | 44 | 22 | 50 | 50 | 107 | 158 | 67 | 84 | 0 | 217 | 18 | 0 | 10 | 310 | 16 | 11 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 100 | 0 | 50 | 402 | 115 | 53 | 0 | 0 | 142 | 54 | 0 | 0 | 65 | 100 | 30 | 90 | 0 | 0 |  | 689 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 16 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 60 | 150 | 0 | 0 | 0 | 0 | 185 | 0 | 92 | 0 | 193 | 0 | 417 | 105 | 0 | 0 | 0 | 72 | 0 | 0 | 109 | 570 | 4 | 0 |  | 5739 | 3143 | 8882 | 3657 | 689 | 2057 | 1438 | 780 | 159 | 0 | 102 | 0 | 0 | 103.52
21:00 | 0 | 0 | 120 | 115 | 200 | 12 | 0 | 0 | 334 |  | 0 | 400 | 150 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 30 | 25 | 16 | 0 | 0 | 89 | 70 | 115 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 40 | 100 | 0 | 0 | 295 | 0 | 184 | 26 | 75 | 26 | 20 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 100 | 126 | 33 | 17 | 0 | 44 | 22 | 50 | 50 | 107 | 158 | 67 | 84 | 0 | 217 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 50 | 402 | 115 | 53 | 0 | 0 | 142 | 54 | 0 | 0 | 65 | 100 | 30 | 90 | 0 | 0 |  | 689 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 16 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 60 | 150 | 0 | 0 | 0 | 0 | 179 | 0 | 90 | 0 | 187 | 0 | 408 | 105 | 0 | 0 | 0 | 52 | 0 | 0 | 50 | 570 | 36 | 0 |  | 5700 | 3063 | 8763 | 3656 | 689 | 2068 | 1311 | 780 | 159 | 0 | 100 | 0 | 0 | #REF!
22:00 | 0 | 0 | 120 | 115 | 200 | 12 | 0 | 0 | 334 |  | 0 | 400 | 150 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 30 | 25 | 16 | 0 | 0 | 90 | 70 | 115 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 40 | 100 | 0 | 0 | 300 | 0 | 180 | 26 | 72 | 29 | 20 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 96 | 124 | 33 | 17 | 0 | 44 | 22 | 50 | 50 | 107 | 159 | 68 | 84 | 0 | 217 | 18 | 0 | 10 | 295 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 10 | 402 | 115 | 53 | 0 | 0 | 142 | 54 | 0 | 0 | 9 | 100 | 30 | 90 | 0 | 0 |  | 689 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 60 | 150 | 0 | 0 | 0 | 0 | 176 | 0 | 91 | 0 | 184 | 0 | 377 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 570 | 36 | 0 |  | 5532 | 2820 | 8352 | 3652 | 689 | 2032 | 943 | 780 | 160 | 0 | 96 | 0 | 0 | 103.51
23:00 | 0 | 0 | 120 | 115 | 200 | 12 | 0 | 0 | 334 |  | 0 | 400 | 150 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 31 | 25 | 16 | 0 | 0 | 90 | 70 | 115 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 42 | 100 | 0 | 0 | 295 | 0 | 182 | 26 | 74 | 29 | 20 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 94 | 159 | 33 | 20 | 0 | 44 | 22 | 50 | 50 | 107 | 159 | 67 | 84 | 0 | 217 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 10 | 400 | 95 | 53 | 0 | 0 | 53 | 54 | 0 | 0 | 9 | 100 | 30 | 90 | 0 | 0 |  | 498 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 57 | 150 | 0 | 0 | 0 | 0 | 176 | 0 | 91 | 0 | 186 | 0 | 408 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 36 | 0 |  | 5425 | 2594 | 8019 | 3673 | 498 | 2050 | 837 | 707 | 160 | 0 | 94 | 0 | 0 | 103.5
24:00 | 0 | 0 | 120 | 115 | 200 | 12 | 0 | 0 | 304 |  | 0 | 400 | 150 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 31 | 25 | 16 | 0 | 0 | 90 | 70 | 115 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 42 | 100 | 0 | 0 | 295 | 0 | 180 | 26 | 70 | 29 | 20 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 92 | 161 | 33 | 20 | 0 | 44 | 22 | 50 | 50 | 107 | 160 | 67 | 40 | 0 | 217 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 0 | 401 | 40 | 35 | 0 | 0 | 16 | 54 | 0 | 0 | 0 | 100 | 30 | 90 | 0 | 0 |  | 498 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 57 | 150 | 0 | 0 | 0 | 0 | 165 | 0 | 91 | 0 | 174 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 36 | 0 |  | 5219 | 2475 | 7694 | 3625 | 498 | 1947 | 715 | 657 | 160 | 0 | 92 | 0 | 0 | 103.5
KWH | 0 | 0 | 2808000 | 2835000 | 4785200 | 295863 | 0 | 0 | 7342000 |  | 0 | 8503750 | 3415709 | 47040 | 93600 | 118896 | 0 | 0 | 1478000 | 58560 | 412272 | 0 | 0 | 0 | 0 | 0 | 765720 | 58582 | 0 | 362952 | 600000 | 545400 | 592600 | 512600 | 0 | 0 | 2044363 | 1692000 | 2800000 | 0 | 0 | 4896684 | 0 | 0 | 0 |  | 0 | 0 | 27512 | 0 | 0 | 627840 | 475728 | 569280 | 2728536 | 0 | 0 | 7130400 | 0 | 4476000 | 501818 | 1550510 | 635544 | 441600 | 0 | 1047112 | 0 | 0 | 25728 | 434520 | 250920 | 627000 | 494070 | 2198400 | 2537960 | 792960 | 192888 | 15200 | 998000 | 84480 | 762000 | 837360 | 2529163 | 3611000 | 1225728 | 1143360 | 0 | 4675330 | 421000 | 0 | 239400 | 7120950 | 457296 | 164000 | 0 | 60218 | 0 | 0 | 108000 | 0 | 0 | 138645 | 1308480 | 0 | 369672 | 9055000 | 1124400 | 853656 | 0 | 29641 | 1114036 | 1055222 | 0 | 0 | 495600 | 1862400 | 873600 | 1255640 | 352760 | 0 |  | 12054545 | 0 | 7748640 | 0 | 27840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530600 | 111360 | 0 | 850000 | 0 | 0 | 0 | 35512 | 0 | 0 | 0 | 0 | 0 | 508560 | 0 | 242982 | 0 | 1425163 | 3681600 | 0 | 0 | 0 | 0 | 4026227 | 0 | 1337212 | 0 | 4261000 | 0 | 8397509 | 601440 | 0 | 0 | 0 | 341760 | 0 | 38431 | 424032 | 10450500 | 629150 | 0 |  | 119172354 | 57724063 | 176896417 | 82444795 | 12054545 | 42736687 | 17530663 | 15557263 | 3736363 | 63024 | 2198400 | 574677 | 0
Fuel Cost | 0 | 0 | 4099680 | 4167450 | 5311572 | 390539.16 | 0 | 0 | 7562260 |  | 0 | 9269087.5 | 3791436.99 | 357033.6 | 644904 | 1005860.16 | 0 | 0 | 2556940 | 440956.8 | 3759920.64 | 0 | 0 | 0 | 0 | 0 | 5589756 | 452838.86 | 0 | 272214 | 450000 | 0 | 0 | 0 | 0 | 0 | 551978.01 | 456840 | 5068000 | 0 | 0 | 5337385.56 | 0 | 0 | 0 |  | 0 | 0 | 266866.4 | 0 | 0 | 4972492.8 | 599417.28 | 1690761.6 | 4038233.28 | 0 | 0 | 5276496 | 0 | 4117920 | 647345.22 | 1783086.5 | 718164.72 | 618240 | 0 | 1790561.52 | 0 | 0 | 245702.4 | 551840.4 | 188190 | 1097250 | 370552.5 | 16488000 | 2690237.6 | 7200076.8 | 244967.76 | 242288 | 1636720 | 135168 | 1356360 | 1306281.6 | 2883245.82 | 3755440 | 2414684.16 | 2183817.6 | 0 | 8088320.9 | 921990 | 0 | 488376 | 7192159.5 | 342972 | 124640 | 0 | 455248.08 | 0 | 0 | 561600 | 0 | 0 | 1620760.05 | 10664112 | 0 | 2606187.6 | 8421150 | 10254528 | 8067049.2 | 0 | 0 | 8422112.16 | 9190983.62 | 0 | 0 | 4247292 | 12403584 | 0 | 0 | 0 | 0 |  | 69434179.2 | 0 | 8136072 | 0 | 218822.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 822430 | 1086873.6 | 0 | 1742500 | 0 | 0 | 0 | 314281.2 | 0 | 0 | 0 | 0 | 0 | 976435.2 | 0 | 183937.374 | 0 | 8593732.89 | 19954272 | 0 | 0 | 0 | 0 | 5314619.64 | 0 | 2005818 | 0 | 4985370 | 0 | 8313533.91 | 6279033.6 | 0 | 0 | 0 | 2652057.6 | 0 | 424662.55 | 3133596.48 | 45877695 | 0 | 0 |  | 227120126.35 | 190449922.644 | 417570048.994 | 95143181.674 | 69434179.2 | 49497252.63 | 108704059.39 | 74425699.89 | 1008818.01 | 581147.6 | 16488000 | 2287710.6 | 0
Yesterday Day Peak | 0 | 0 | 100 | 115 | 200 | 12 | 0 | 0 | 319 |  | 0 | 330 | 150 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 13 | 25 | 25 | 0 | 0 | 87 | 70 | 115 | 0 | 0 | 207 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 8 | 20 | 42 | 135 | 0 | 0 | 340 | 0 | 192 | 45 | 74 | 29 | 30 | 0 | 10 | 0 | 0 | 0 | 19 | 11 | 8 | 15 | 90 | 100 | 33 | 0 | 2 | 41 | 0 | 11 | 30 | 107 | 158 | 40 | 30 | 0 | 165 | 18 | 0 | 10 | 300 | 16 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 0 | 0 | 353 | 8 | 22 | 0 | 4 | 16 | 17 | 0 | 0 | 0 | 30 | 35 | 17 | 53 | 18 |  | 408 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 63 | 150 | 0 | 0 | 0 | 0 | 188 | 0 | 23 | 0 | 201 | 0 | 347 | 17 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 350 | 35 | 0 |  | 6891 | DayPeak
Yesterday Evening Peak | 0 | 0 | 120 | 115 | 200 | 12 | 0 | 0 | 334 | 0 | 0 | 400 | 150 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 16 | 25 | 25 | 25 | 16 | 0 | 0 | 88 | 70 | 115 | 0 | 0 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 42 | 80 | 0 | 0 | 315 | 0 | 196 | 26 | 75 | 29 | 20 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 112 | 122 | 33 | 17 | 0 | 44 | 0 | 50 | 50 | 107 | 157 | 67 | 84 | 0 | 217 | 18 | 0 | 10 | 315 | 16 | 11 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 100 | 0 | 50 | 402 | 115 | 53 | 0 | 0 | 144 | 54 | 0 | 0 | 65 | 100 | 30 | 90 | 0 | 0 |  | 688 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 16 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 61 | 150 | 0 | 0 | 0 | 0 | 186 | 0 | 91 | 0 | 195 | 0 | 416 | 105 | 0 | 0 | 0 | 71 | 0 | 0 | 109 | 570 | 10 | 0 |  | 8915 | EvPeak
Forecast for Evening | 0 | 0 | 150 | 115 | 200 | 12 | 0 | 0 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 0 | 0 | 100 | 100 | 100 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 33 | 33 | 33 | 52 | 0 | 90 | 70 | 120 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 0 |  | 102 | 100 | 100 | 50 | 20 | 10 | 100 | 0 | 0 | 360 | 0 | 225 | 26 | 90 | 30 | 20 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 172 | 163 | 33 | 22 | 0 | 44 | 22 | 51 | 44 | 110 | 160 | 66 | 86 | 0 | 220 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 180 | 150 | 400 | 115 | 100 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 40 | 90 | 0 |  |  | 796 | 16 | 410 | 0 | 115 | 220 | 0 | 0 | 30 | 60 | 40 | 0 | 22 | 110 | 0 | 70 | 0 | 50 | 40 | 100 | 0 | 0 | 50 | 52 | 33 | 22 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 | 0 | 95 | 100 | 220 | 0 | 413 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 660 | 35
Forecast for Day | 0 | 0 | 150 | 115 | 200 | 12 | 0 | 0 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 0 | 0 | 100 | 100 | 100 | 150 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 33 | 33 | 33 | 52 | 0 | 90 | 70 | 120 | 0 | 25 | 215 | 0 | 0 | 0 | 0 | 0 |  | 102 | 100 | 100 | 50 | 20 | 10 | 100 | 0 | 0 | 360 | 0 | 225 | 26 | 90 | 30 | 20 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 156 | 163 | 33 | 22 | 1.6 | 44 | 22 | 51 | 44 | 110 | 160 | 66 | 86 | 0 | 220 | 18 | 0 | 10 | 341 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 165 | 150 | 400 | 115 | 100 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 40 | 90 | 50 |  |  | 555 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 22 | 110 | 0 | 70 | 0 | 0 | 0 | 100 | 0 | 0 | 50 | 52 | 0 | 22 | 10 | 11 | 0 | 64 | 150 | 0 | 0 | 0 | 0 | 220 |  | 95 | 0 | 220 | 0 | 413 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 600 | 35
Generation at 08:00(Today) | 0 | 0 | 100 | 115 | 200 | 12 | 0 | 0 | 361 | 0 | 0 | 370 | 150 |  | 0 | 0 | 0 | 0 | 62 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 22 | 25 | 16 | 0 | 0 | 89 | 70 | 115 | 0 | 0 | 207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 4 | 100 | 0 | 0 | 280 | 0 | 195 | 26 | 90 | 29 | 20 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 33 | 15 | 32 | 163 | 33 | 20 | 1 | 43 | 22 | 5 | 5 | 107 | 158 | 40 | 10 | 0 | 138 | 0 | 0 | 0 | 310 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 100 | 0 | 0 | 401 | 40 | 32 | 0 | 1 | 0 | 17 | 0 | 0 | 0 | 60 | 20 | 0 | 23 | 0 | 0 | 407 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 49 | 150 | 0 | 0 | 0 | 0 | 162 | 0 | 24 | 0 | 166 | 0 | 378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 36 | 0 | 0
199
| Minimum Generation |  | 6243 | 9:00
| Highest Generation |  | 8915 | 19:30
| Day Peak Generation |  | 6891 | 12:00
| Evening Peak Generation |  | 8915 | 19:30
| HVDC Max Flow |  | 689 | 19:00
| HVDC EvPeak Flow |  | 688 | 19:30
| Load factor L.F |  | 82.68%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-11-14
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-11-13 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6891 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6298 | MW
Evening Peak Generation : |  | 8915 | MW Hour : | 19:30 | Available Max Generation : |  | 14511 | MW
E.P. Demand (at gen end) : |  | 8915 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 9800 | MW
Maximum Generation : |  | 8915 | MW Hour : | 19:30 | Reserve(Generation end) |  | 4711 | MW
Total Gen. (MKWH) : |  | 176.8964 | System Load Factor : | 82.68% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 115 | MW at | 18:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-11-14
Actual : | 103.49 | Ft.(MSL) , | Rule curve : | 107.7 | Ft.( MSL )
Gas Consumed : | Total = | 1036.17 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 144640434.304
: |  | Coal : | 74425699.89 | Oil : | 109285206.99 | Total : | 328351341.184
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3417.2513 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1158.207 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1037.0295 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 936.8002 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 846.707 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 683.2529 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 386.9926 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 176.0503 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 526.9349 |  |  | 0 | 0%
Total | 0 |  | 9169.2258 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1 | 10) Sirajganj #1 CCPP STG
|  |  |  | 2) Baghabari-70 MW | 11) Summit Meghnaghat GT-1
|  |  |  | 3) Ghorasal Unit-1,2,3 | 13) Ashuganj(S)-360 MW
4) Ashuganj unit-4,5
5) Kaptai-2
6) Raozan #2,5
7) Siddirganj-335 MW
8) Haripur 412 MW
9) Chandpur-163 MW STG
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Meghnaghat-Comilla(N) 230 kV Ckt-2 was under shut down from 09:15 to 14:21 for A/M.
b) Kabirpur 132/33 kV T-3 transformer was under shut down from 08:11 to 10:31 for C/M.
c) Rangpur-Kurigram 132 kV Ckt was under shut down from 08:42 to 16:20 for A/M. |  |  |  |  | About 25 MW power interruption occurred under Kurigram S/S area
from 08:42 to 16:20.
d) Sirajganj 230 kV Bus-1 was under shut down from 09:35 to 16:09 for A/M.
e) Bagerhat-Goalpara 132 kV Ckt was under shut down from 08:24 to 12:54 for A/M.
f) Magura-Norail 132 kV Ckts 1 & 2 were under shut down from 08:09 to 13:00 for D/W. |  |  |  |  | About 10 MW power interruption occurred under Norail S/S area
from 08:09 to 13:00.
g) Bheramara-GK 132 kV Ckts 1 & 2 were under shut down from 08:00 to 13:27 for A/M. |  |  |  |  | About 22 MW power interruption occurred under Norail S/S area
from 08:00 to 13:27.
h) Dhamrai 132/33 kV T-1 transformer and Bus section-1 were under shut down from 14:15 to 17:15 for D/W.
i) Hasnabad 132/33 kV T-1 transformer was under shut down from 07:56 to 16:58 for A/M.
j) After maintenance Halishahar 132/33 kV T-3 transformer was switched on at 15:32.
k) After maintenance Kaliakoir-Tangail 132 kV Ckt-1 was switched on at 22:47.
l) Mymensingh-Netrokona 132 kV Ckt-2 tripped at 05:48(14/11/2020) from both ends showing Dist.Z1,
3-phase at Mymensingh end and E/F relay at Netrokona end and was switched on at 06:07.
m) Haripur-Ullon 132 kV Ckt-2 was shut down at 06:56(14/11/2020) for A/M.
n) Kishoreganj-Mymensingh 132 kV Ckt-1 was shut down at 07:17(14/11/2020) for A/M.
o) Comilla(S) 132/33 kV T-1 & T-2 transformers tripped at 07:38(14/11/2020) showing O/C relay at 132 kV
side and 132 kV protection trip at 33 kV side due to 33 kV Laksam feeder fault and were switched on at 08:16.
p) Sylhet 33 kV full Bus was shut down at 07:18(14/11/20200 for C/M. |  |  |  |  | About 80 MW power interruption occurred under Sylhet S/S area
from 07:18(14/11/2020) to till now.
q) Niamatpur 132/33 kV T-3 transformer was shut down at 07:37(14/11/2020) for A/M.
r) Magura-Norail 132 kV Ckts 1 & 2 were shut down at 07:52(14/11/2020) for D/W. |  |  |  |  | About 10 MW power interruption occurred under Norail S/S area
from 07:52(14/11/2020) to till now.
m) Joypurhat 132/33 kV T-1 transformer was under shut down from 08:52 to 14:16 for A/M.
n) Barishal 230/132 kV T-1 transformer was under shut down from 08:32 to 17:00 for A/M.
o) Benapole 132/33 kV T-1 transformer was under shut down from 07:47 to 15:30 for A/M.
p) Khulna(S) 230/132 kV T-1 transformer was under shut down from 08:27 to 14:07 for A/M.
q) Satkhira 132/33 kV T-1 transformer was under shut down from 08:55 to 16:21 for A/M.\r)
r) Ishurdi-Pabna 132 kV Ckt was under shut down from 08:21 to 16:44 for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-11-13 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 120 | 2808000 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 115 | 2835000 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 4785200 | Machin problem.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 12 | 295863 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 334 | 7342000 | Frequency control
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 8503750 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 47040 | Reserve.
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 150 | 3415709 | GT-2 under shut down
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 93600 | Reserve.
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 118896 | Reserve.
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 16 | 362952
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 82 | 1478000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 58560 | Reserve.
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under Maintenance
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 64 | 412272 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 765720
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 58582 | Reserve.
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve.
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Reserve.
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 50 | 1145400 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 592600 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 16 | 512600 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 60218 | Reserve.
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 0 | Reserve.
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 53 | 853656 | Low demand
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 1255640 | Unit Transformer problem
| Manikgonj 162MW PP |  | IPP | 9*18 | 0 | 0 | 0
| Dhaka area Total |  |  |  | 5895 | 1781 | 37801258
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 115 | 2800000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve.
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 138645
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 627840
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 158 | 3736363 | Unit-2 under maint
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 208 | 4896684
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 27512 | Reserve.
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1308480
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 475728
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 569280
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve.
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 29641
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 144 | 1114036 | Transformer O/L
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1055222
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1862400
| Chattogram area Total |  |  |  | 2266 | 991 | 18641831
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 2728536 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas Shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 196 | 4476000 | Gas shortage.
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 315 | 7130400
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 635544 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 20 | 441600 | Gas shortage
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 26 | 501818 | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1047112
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 50 | 369672 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 75 | 1550510 | ST Under maint
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve.
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 434520
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 250920
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 112 | 2198400 | Low demand
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 627000
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 25728
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 494070
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 65 | 495600 | Low demand
| Cumilla Area Total |  |  |  | 2980 | 1103 | 23407430
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 122 | 2537960 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 192888
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 33 | 792960 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 15200
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 16 | 108000
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1124400 | #REF!
| Mymensingh PV 50 MW Solar PP |  | IPP | 50 | 0 | 0 | 352760
| Mymensingh Area Total |  |  |  | 637 | 303 | 5124168
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 44 | 998000 | GT-2 under maint.
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 84480 | Under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 107 | 2529163 | ST Under maint
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 157 | 3611000 | FGMO & GT-2 under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 762000
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 837360
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 164000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 67 | 1225728 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1143360
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 217 | 4675330
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 421000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 457296
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7120950 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 402 | 9055000
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 239400
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 30 | 873600 | On test
| Sylhet Area Total |  |  |  | 1988 | 1578 | 34197667
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 688 | 12054545
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 27840 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 360 | 7748640 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Reserve.
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 601440
107 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1153 | 20432465
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 111360 | Low demand
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 28 | 530600 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 91 | 1337212 | Engine problem
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 570 | 10450500
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 10 | 629150
| Barisal Area Total |  |  |  | 1054 | 715 | 13058822
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 70 | 850000 | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel Shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel Shortage
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Under rmaint.
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 186 | 4026227 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 195 | 4261000 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 416 | 8397509 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 508560
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 242982
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve.
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 35512 | Reserve.
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 0 | Reserve.
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 424032
| Rajshahi Area Total |  |  |  | 2183 | 1009 | 18745822
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 61 | 1425163 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3681600 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 71 | 341760
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 38431
| Rangpur Area Total |  |  |  | 605 | 282 | 5486954
| Total |  |  |  | 19892 | 8915 | 176896417
| Eastern Grid Total |  |  |  | 13766 | 5756 | 119172354
| Western Grid Total |  |  |  | 6126 | 3159 | 57724063
| National Grid Total |  |  |  | 19892 | 8915 | 176896417
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-11-13
| (a) ENTIRE EASTERN GRID : |  | 5764 | MW | (b) ENTIRE WESTERN GRID : |  | 2563 | MW
| i) Dhaka area |  | 2970 | MW | i) Khulna area |  | 1014 | MW
| ii) Chittagong area |  | 941 | MW | ii) Rajshahi area |  | 803 | MW
| iii) Comilla area |  | 837 | MW | iii) Barisal area |  | 237 | MW
| iv) Mymensingh area |  | 651 | MW | iv) Rangpur area |  | 509 | MW
| v) Sylhet area |  | 365 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8327 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 100 | 23:00 | Sherpur | 80 | 18:00 | Jhenida | 78 | 18:00
| Munsiganj | 92 | 20:00 | Srimongal | 26 | 18:30 | Bottail | 78 | 19:00
| Sonargaon | 53 | 1:00 | Shahjibazar | 88 | 18:00 | G.K Project | 38 | 18:00
| Shyampur | 178 | 1:00 | Fenchuganj | 29 | 18:00 | Faridpur | 122 | 0.8125
| Bhulta | 146 | 1:00 | Kulawara | 36 | 18:00 | Madaripur | 64 | 0.83333
| Madanganj | 47 | 2:00 | Sylhet | 100 | 20:00 | Sariatpur | 42 | 18:00
| Shitalakhya | 80 | 1:00 | Chatak | 19 | 18:00 | Gopalganj | 64 | 18:00
| Rahim steel | 4 | 7:00 | Sunamganj | 31 | 19:00 | Bagerhat | 76 | 18:00
| Matuail | 60 | 1:00 | Biani Bazar | 41 | 18:00 | Mongla | 36 | 1:00
| Ghorasal | 58 | 19:00 | Comilla (S) | 118 | 18:00 | Satkhira | 76 | 0.79167
| Narsingdi | 127 | 20:00 | Comilla(N) | 87 | 18:00 | Gallamari | 20 | 1:00
| Haripur (SBU) | 88 | 1:00 | Chandpur | 72 | 18:30 | Magura | 36 | 0.75
| Ullon | 62 | 18:30 | Feni | 100 | 18:00 | Norail | 22 | 18:00
| Hasnabad | 138 | 18:00 | Chowmuhani | 125 | 18:30 | Chuadanga | 75 | 18:00
| Magbazar | 64 | 15:00 | Ashuganj | 41 | 19:30 | Barisal(N) | 30 | 0.75
| Maniknagar | 68 | 18:00 | Daudkandi | 108 | 19:30 | Barisal (S) | 72 | 0.79167
| Bangabhaban | 12 | 10:00 | B.Baria | 111 | 19:30 | Patuakhali | 82 | 0.8125
| Narinda | 66 | 20:00 | Ramganj | 76 | 18:30 | Bhandaria | 40 | 0.77083
| Dhanmondi | 97 | 18:00 | Chaddagram | 26 | 18:30 | Borhan Uddin | 27 | 20:00
| Lalbag | 63 | 1:00 | PHP | 6 | 8:00 | Ishurdi | 40 | 18:00
| Madartek | 60 | 21:00 | Madunaghat | 46 | 18:00 | Ruppur Paromanobik | 2 | 1:00
| Dhaka University |  |  | Hathazari | 80 | 0.77083 | Natore | 82 | 19:00
| Fatullah | 39 | 0.125 | Khulshi | 166 | 0.79167 | Bogra | 114 | 18:00
| Mirpur | 81 | 18:00 | Halishahar | 115 | 0.75 | Noagaon | 83 | 19:30
| Kalyanpur | 75 | 18:00 | Baraulia | 143 | 0.20833 | Rajshahi | 92 | 18:30
| Gulshan | 82 | 18:00 | Sikalbaha | 23 | 0.77083 | Rajshahi New | 9 | 18:00
| Uttara | 77 | 18:00 | Dohazari | 68 | 0.75 | C.Nawabganj | 48 | 18:00
| Uttara New | 26 | 18:00 | Cox'sbazar | 88 | 0.79167 | Amnura | 28 | 18:30
| Kamrangirchar | 62 | 18:30 | Chandraghona | 26 | 0.75 | Pabna | 76 | 18:30
| Savar | 96 | 18:00 | Kaptai | 3.8 | 0.75 | Shahjadpur | 74 | 18:30
| Bhasantec | 117 | 18:00 | A. Khaer Stl. | 0 | 0.041667 | Serajganj | 43 | 19:30
| Agargaon | 52 | 18:00 | Bakulia | 80 | 0.8125 | Niyamatpur | 37 | 18:00
| Satmosjid | 81 | 18:00 | Julda | 20 | 0.041667 | Joypurhat | 35 | 18:30
| Tongi | 73 | 0.45833 | TK chemical | 22.3 | 0.83333 | Sherpur(Bogura) | 32 | 18:00
| Kabirpur | 143 | 12:00 | Modern Steel | 0 | 0.041667 | Mohastangor | 33 | 19:00
| Basundhara | 101 | 18:00 | Shahmirpur | 14 | 0.041667 | Rangpur | 96 | 18:00
| Manikganj | 52 | 18:00 | Khagrachhari | 20 | 0.041667 | Lalmonirhat | 42 | 18:00
| Joydevpur | 99 | 15:00 | Matarbari | 31 | 0.83333 | Saidpur | 72 | 18:30
| New Tongi | 64 | 1:00 | Baroiar Hat | 24 | 0.75 | Purbasadipur | 75 | 18:00
| Kodda | 143 | 18:00 | Rangamati | 10 | 0.75 | Thakurgaon | 56 | 18:30
| Dhamrai | 52 | 18:30 | Abul Khair 230 | 125 | 0.16667 | Palashbari | 78 | 18:00
| Rajendrapur | 66 | 1:00 | BSRM | 108 | 0.125 | Barapukuria | 35 | 19:30
| Valuka | 66 | 19:00 | GPH Ispat | 7 | 0.041667 | Panchagar | 39 | 18:30
| Tangail | 129 | 20:00 | Goalpara | 15 | 0.54167 | Joldhaka | 18 | 18:00
| Mymensing | 154 | 18:00 | Central s/s | 75 | 18:00 | Kurigram | 44 | 8:00
| Kishorganj | 88 | 19:30 | Noapara | 44 | 19:00
| Netrokona | 78 | 18:00 | Jessore | 79 | 19:00
| Jamalpur | 89 | 18:00 | Benapol | 28 | 18:00
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-11-13 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 409 | 8:00 | 400 | 3:00 | Kaliakoir | 399 | 0.375 | 390 | 0.83333
| Bheramara | 414 | 9:00 | 396 | 18:00 | Bhulta | 374 | 0.75 | 367 | 0.25
| Ashuganj(N) | 384 | 8:00 | 373 | 11:00 | Gopalganj | 418 | 0.375 | 396 | 0.83333
| Payra | 422 | 18:00 | 409 | 21:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 228 | 24:00 | Comilla (N) | 232 | 18:00 | 225 | 10:00
| Ishurdi | 237 | 2:00 | 229 | 18:00 | Hathazari | 225 | 18:00 | 218 | 11:00
| Ashuganj | 232 | 18:00 | 228 | 2:00 | Megnaghat | 227 | 9:00 | 223 | 11:00
| Serajganj | 231 | 1:00 | 229 | 12:00 | Fenchuganj | 242 | 18:00 | 239 | 4:00
| Baghabari | 241 | 5:00 | 237 | 21:00 | Siddhirganj | 226 | 24:00 | 221 | 11:00
| Barapukuria | 231 | 5:00 | 228 | 12:00 | Maniknagar | 222 | 18:00 | 219 | 11:00
| Bogra | 230 | 5:00 | 225 | 1:00 | Agargaon | 221 | 4:00 | 212 | 11:00
| Rajshahi | 229 | 4:00 | 222 | 12:00 | Barisal | 250 | 18:00 | 235 | 14:00
| Khulna South | 234 | 6:00 | 223 | 22:00 | AKSML | 223 | 18:00 | 213 | 11:00
| Rampura | 222 | 9:00 | 220 | 12:00 | BSRM | 224 | 20:00 | 214 | 11:00
| Haripur | 223 | 13:00 | 219 | 11:00 | Bibiyana | 242 | 5:00 | 236 | 19:00
| Hasnabad | 216 | 1:00 | 208 | 12:00 | Bhulta | 224 | 19:00 | 221 | 17:00
| Shyampur | 224 | 18:00 | 220 | 15:00 | Ashuganj (S) | 231 | 18:00 | 225 | 11:00
| Aminbazar | 220 | 3:00 | 215 | 11:00 | Kaliakoir | 223 | 9:00 | 217 | 1:00
| Tongi | 219 | 18:00 | 213 | 11:00 | GPH | 221 | 9:00 | 215 | 13:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 136 | 18:00 | 131 | 1:00 | Hathazari | 135 | 0.91667 | 130 | 0.45833
| Munsiganj | 137 | 18:00 | 129 | 10:00 | Khulshi | 132 | 0.75 | 127 | 0.45833
| Sonargaon | 134 | 18:00 | 129 | 11:00 | Halishahar | 134 | 0.75 | 127 | 0.45833
| Shyampur | 133 | 18:00 | 129 | 1:00 | Baraulia | 134 | 0.70833 | 128 | 0.45833
| Bhulta | 129 | 14:00 | 125 | 1:00 | Sikalbaha | 135 | 0.75 | 130 | 0.45833
| Madanganj | 132 | 2:00 | 129 | 5:00 | Dohazari | 130 | 0.375 | 127 | 0.20833
| Shitalakhya | 140 | 18:00 | 126 | 12:00 | Cox'sbazar | 127 | 0.33333 | 119 | 0.8125
| Rahim steal | 134 | 13:00 | 131 | 11:00 | Chandraghona | 134 | 0.041667 | 131 | 0.45833
| Matuail | 136 | 18:00 | 131 | 1:00 | Kaptai | 134 | 0.041667 | 130 | 0.45833
| Ghorasal | 136 | 9:00 | 135 | 1:00 | A. Khaer Stl. | 132 | 0.75 | 129 | 0.5
| Narsinghdi | 132 | 9:00 | 127 | 1:00 | Bakulia | 132 | 0.041667 | 127 | 0.45833
| Haripur (SBU) | 134 | 6:00 | 131 | 3:00 | Julda | 134 | 0.75 | 129 | 0.29167
| Ullon | 132 | 9:00 | 128 | 12:00 | TK Chemical | 133 | 0.79167 | 128 | 0.45833
| Hasnabad | 130 | 4:00 | 126 | 12:00 | Modern Steel | 133 | 0.041667 | 129 | 0.41667
| Magbazar | 132 | 5:00 | 129 | 12:00 | Shahmirpur | 135 | 0.75 | 127 | 0.45833
| Maniknagar | 135 | 18:00 | 132 | 1:00 | Khagrachhari | 133 | 0.041667 | 130 | 0.45833
| Bangabhaban | 135 | 18:00 | 132 | 1:00 | Matarbari | 129 | 0.375 | 121 | 0.79167
| Narinda | 135 | 18:00 | 132 | 1:00 | Baroiar Hat | 132 | 0.041667 | 130 | 0.41667
| Dhanmondi | 132 | 9:00 | 128 | 12:00 | Rangamati | 133 | 0.041667 | 130 | 0.45833
| Lalbag | 135 | 18:00 | 129 | 11:00 | Goalpara S/S | 138 | 2:00 | 132 | 12:00
| Madartek | 132 | 6:00 | 128 | 11:00 | Khulna Central S/S | 137 | 3:00 | 130 | 0.91667
| Dhaka University |  |  |  |  | Noapara | 137 | 4:00 | 130 | 0.45833
| Fatuiiah | 134 | 18:00 | 129 | 3:00 | Jessore | 136 | 4:00 | 126 | 0.75
| Mirpur | 134 | 6:00 | 129 | 12:00 | Benapol | 136 | 0.125 | 126 | 0.79167
| Kalyanpur | 134 | 6:00 | 12130 | 12:00 | Jhenida | 135 | 4:00 | 124 | 0.75
| Gulshan | 131 | 6:00 | 128 | 12:00 | Bottail | 136 | 0.375 | 130 | 0.77083
| Uttara | 132 | 6:00 | 129 | 12:00 | G.K Project | 139 | 0.125 | 137 | 0.66667
| Uttara New | 133 | 6:00 | 129 | 12:00 | Faridpur | 138 | 0.375 | 130 | 0.79167
| Kamrangirchar | 129 | 6:00 | 125 | 12:00 | Madaripur | 139 | 0.375 | 131 | 0.8125
| Savar | 133 | 7:00 | 130 | 13:00 | Shariyatpur S/S | 139 | 9:00 | 132 | 0.83333
| Bhasantec | 132 | 6:00 | 128 | 12:00 | Gopalganj | 140 | 0.16667 | 132 | 0.83333
| Agargaon | 134 | 6:00 | 130 | 12:00 | Bagerhat | 137 | 7:00 | 129 | 0.45833
| Satmosjid | 134 | 6:00 | 130 | 12:00 | Mongla | 135 | 17:00 | 126 | 0.45833
| Tongi | 136 | 18:00 | 132 | 11:00 | Satkhira | 137 | 6:00 | 128 | 22:00
| Kabirpur | 135 | 8:00 | 131 | 19:00 | Gallamari | 139 | 0.25 | 131 | 0.91667
| Basundhara | 132 | 5:00 | 128 | 11:00 | Magura | 134 | 5:00 | 124 | 0.79167
| Manikganj | 137 | 8:00 | 132 | 11:00 | Norail | 132 | 0.125 | 122 | 0.75
| Joydevpur | 137 | 5:00 | 131 | 21:00 | Chuadanga | 130 | 1:00 | 120 | 0.79167
| New Tongi | 135 | 18:00 | 131 | 11:00 | Barisal(N) | 140 | 2:00 | 132 | 20:00
| Kodda | 131 | 18:00 | 125 | 11:00 | Barisal (S) | 138 | 0.25 | 132 | 0.83333
| Dhamrai | 136 | 6:00 | 130 | 19:30 | Patuakhali(S) | 135 | 0.16667 | 128 | 0.83333
| Rajendrapur | 129 | 14:00 | 124 | 13:00 | Bhandaria | 138 | 0.29167 | 129 | 0.83333
| Valuka | 126 | 23:00 | 118 | 12:00 | Ishurdi | 138 | 17:00 | 133 | 13:00
| Tangail | 134 | 3:00 | 122 | 17:00 | Ruppur Paromanobik | 138 | 4:00 | 135 | 19:30
| Mymensing | 128 | 23:00 | 119 | 16:00 | Natore | 139 | 1:00 | 135 | 12:00
| Kishorganj | 129 | 4:00 | 123 | 16:00 | Bogra | 138 | 2:00 | 136 | 7:00
| Netrokona | 127 | 25:00 | 120 | 12:00 | Noagaon | 135 | 6:00 | 131 | 12:00
| Jamalpur | 132 | 18:00 | 120 | 12:00 | Rajshahi | 139 | 16:00 | 131 | 12:00
| Sherpur | 131 | 18:30 | 118 | 16:00 | Rajshahi New | 140 | 2:00 | 135 | 11:00
| Srimongal | 136 | 1:00 | 135 | 7:00 | C.Nawabganj | 138 | 3:00 | 134 | 18:00
| Shahjibazar | 134 | 18:00 | 131 | 11:00 | Amnura | 138 | 1:00 | 135 | 9:00
| Fenchuganj | 138 | 13:00 | 135 | 4:00 | Pabna | 138 | 3:00 | 134 | 18:00
| Khulawara | 136 | 1:00 | 134 | 16:00 | Shahjadpur | 143 | 15:00 | 138 | 10:00
| Sylhet | 134 | 1:00 | 134 | 1:00 | Serajganj | 136 | 4:00 | 133 | 9:00
| Chatak | 133 | 1:00 | 132 | 15:00 | Niyamatpur | 135 | 6:00 | 129 | 19:00
| Sunamganj | 133 | 2:00 | 131 | 19:30 | Joypurhat | 136 | 1:00 | 132 | 18:00
| Biani Bazar | 134 | 1:00 | 132 | 11:00 | Sherpur(Bogura) | 138 | 4:00 | 135 | 8:00
| Comilla(s) | 130 | 2:00 | 125 | 7:00 | Mohastangor | 137 | 5:00 | 133 | 12:00
| Comilla(n) | 130 | 19:00 | 133 | 13:00 | Rangpur | 130 | 5:00 | 125 | 8:00
| Chandpur | 135 | 8:00 | 130 | 22:00 | Lalmonirhat | 130 | 5:00 | 125 | 19:00
| Feni | 133 | 18:00 | 130 | 15:00 | Saidpur | 129 | 4:00 | 122 | 19:00
| Chowmuhani | 130 | 18:00 | 128 | 15:00 | Purbasadipur | 128 | 6:00 | 121 | 18:00
| Ashuganj | 133 | 13:00 | 131 | 20:00 | Thakurgaon | 127 | 5:00 | 120 | 18:30
| Daudkandi | 134 | 18:00 | 130 | 11:00 | Palashbari | 133 | 5:00 | 129 | 12:00
| B.Baria | 130 | 7:00 | 128 | 15:00 | Barapukuria | 131 | 5:00 | 128 | 12:00
| Ramganj | 128 | 18:00 | 116 | 19:30 | Panchagar | 127 | 5:00 | 118 | 18:00
| Chaddagram | 135 | 17:00 | 131 | 15:00 | Joldhaka | 129 | 2:00 | 123 | 18:00
| PHP | 132 | 8:00 | 127 | 13:00 | Kurigram | 129 | 7:00 | 124 | 4:00
| Madanhat | 136 | 18:00 | 131 | 11:00

## L-Curve
Date | 2020-11-13
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 391 | 5219 | 2475 | 7694 |  |  |  | QF-LDC-11
0:30 | 378 | 5229.5 | 2486.5 | 7716 | Date: | 2020-11-13
1:00 | 365 | 5240 | 2498 | 7738
1:30 | 363.5 | 5130.5 | 2413 | 7543.5
2:00 | 362 | 5021 | 2328 | 7349
2:30 | 376 | 4927 | 2291.5 | 7218.5 | [5 empty] | Gen. at Eve. Peak | 8915 | 9500 MW (19:30 )
3:00 | 390 | 4833 | 2255 | 7088 | [6 empty] | 19:30
3:30 | 411 | 4778 | 2235 | 7013 | [5 empty] | Gen. at Day Peak | 6891 | 7952.5 MW (12:00 )
4:00 | 432 | 4723 | 2215 | 6938 | [6 empty] | 12:00
4:30 | 426.5 | 4649 | 2183.5 | 6832.5 | [5 empty] | Highest Generation | 8915
5:00 | 421 | 4575 | 2152 | 6727 | [6 empty] | 19:30
5:30 | 384 | 4514.5 | 2117 | 6631.5
6:00 | 347 | 4454 | 2082 | 6536
6:30 | 247.5 | 4415.5 | 1992.5 | 6408
7:00 | 148 | 4377 | 1903 | 6280
7:30 | 155 | 4357.5 | 1980 | 6337.5
8:00 | 162 | 4338 | 2057 | 6395
8:30 | 211 | 4312 | 2007 | 6319
9:00 | 260 | 4286 | 1957 | 6243
9:30 | 290 | 4280 | 1923 | 6203
10:00 | 320 | 4274 | 1889 | 6163
10:30 | 354 | 4368.5 | 1948 | 6316.5
11:00 | 388 | 4463 | 2007 | 6470
11:30 | 381.5 | 4559 | 2121.5 | 6680.5
12:00 | 375 | 4655 | 2236 | 6891
12:30 | 362.5 | 4872.5 | 2319 | 7191.5
13:00 | 350 | 5090 | 2402 | 7492
13:30 | 333.5 | 4977 | 2239 | 7216
14:00 | 317 | 4864 | 2076 | 6940
14:30 | 368.5 | 4892.5 | 2126.5 | 7019
15:00 | 420 | 4921 | 2177 | 7098
15:30 | 460 | 4791 | 2174.5 | 6965.5
16:00 | 500 | 4661 | 2172 | 6833
16:30 | 474 | 4624 | 2175 | 6799
17:00 | 448 | 4587 | 2178 | 6765
17:30 | 281.5 | 5224.5 | 2540 | 7764.5
18:00 | 115 | 5862 | 2902 | 8764
18:30 | 256 | 5793.5 | 3030 | 8823.5
19:00 | 397 | 5725 | 3158 | 8883
19:30 | 392 | 5756 | 3159 | 8915
20:00 | 393 | 5739 | 3143 | 8882 |  |  |  | Executive Engineer
20:30 | 396.5 | 5719.5 | 3103 | 8822.5 |  |  |  | Network Operation Division
21:00 | 400 | 5700 | 3063 | 8763
21:30 | 366.5 | 5616 | 2941.5 | 8557.5
22:00 | 333 | 5532 | 2820 | 8352 |  |  |  |  | Page 6 of 7
22:30 | 358.5 | 5478.5 | 2707 | 8185.5
23:00 | 384 | 5425 | 2594 | 8019
23:30 | 387.5 | 5322 | 2534.5 | 7856.5
24:00 | 391 | 5219 | 2475 | 7694
9500 MW (19:30 )
7952.5 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-11-13 |  | Energy | 176896417
[10 empty] | 2020-11-13 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3625 | 498 | 1947 | 837 | 657 | 160 | 0 | 0 | 92
0:30 | 3509.5 | 551.5 | 1936 | 841 | 685 | 158 | 0 | 0 | 96 | Date: | 2020-11-13
1:00 | 3394 | 605 | 1925 | 845 | 713 | 156 | 0 | 0 | 100
1:30 | 3397.5 | 509.5 | 1953 | 744.5 | 711 | 156 | 0 | 0 | 72 | [7 empty] | Total Energy | 176.8964 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 3401 | 414 | 1981 | 644 | 709 | 156 | 0 | 0 | 44 | [7 empty] | Energy not Served | 0
2:30 | 3372.5 | 414 | 1945 | 563.5 | 699.5 | 156 | 0 | 0 | 68 | [7 empty] | Energy Requirement | 176.8964
3:00 | 3344 | 414 | 1909 | 483 | 690 | 156 | 0 | 0 | 92
3:30 | 3334.5 | 414 | 1872.5 | 454.5 | 689.5 | 157 | 0 | 0 | 91 | [6 empty] | Shortage
4:00 | 3325 | 414 | 1836 | 426 | 689 | 158 | 0 | 0 | 90
4:30 | 3328.5 | 414 | 1747 | 406.5 | 690.5 | 158 | 0 | 0 | 88
5:00 | 3332 | 414 | 1658 | 387 | 692 | 158 | 0 | 0 | 86
5:30 | 3275.5 | 414 | 1627.5 | 387 | 686.5 | 158 | 0 | 0 | 83
6:00 | 3219 | 414 | 1597 | 387 | 681 | 158 | 0 | 0 | 80
6:30 | 3182 | 414 | 1578 | 372 | 622 | 159 | 0 | 0 | 76 |  |  |  |  | Coal
7:00 | 3145 | 414 | 1559 | 357 | 563 | 160 | 0 | 0 | 72
7:30 | 3196.5 | 410.5 | 1573 | 342 | 563.5 | 160.5 | 0 | 0 | 66 |  |  |  | Oil |  |  |  | ,
8:00 | 3248 | 407 | 1587 | 327 | 564 | 161 | 0 | 0 | 60
8:30 | 3192.5 | 407.5 | 1573 | 327 | 545.5 | 162 | 0 | 0 | 60
9:00 | 3137 | 408 | 1559 | 327 | 527 | 163 | 0 | 0 | 60
9:30 | 3146 | 408 | 1516.5 | 312 | 520 | 162.5 | 0 | 0 | 69
10:00 | 3155 | 408 | 1474 | 297 | 513 | 162 | 0 | 0 | 78
10:30 | 3274 | 408 | 1504 | 288 | 523 | 161 | 0 | 0 | 79
11:00 | 3393 | 408 | 1534 | 279 | 533 | 160 | 0 | 0 | 80
11:30 | 3448 | 408 | 1628.5 | 321 | 548 | 158.5 | 0 | 0 | 85
12:00 | 3503 | 408 | 1723 | 363 | 563 | 157 | 0 | 0 | 90
12:30 | 3589.5 | 454.5 | 1790 | 441 | 587.5 | 156 | 0 | 0 | 92
13:00 | 3676 | 501 | 1857 | 519 | 612 | 155 | 0 | 0 | 94
13:30 | 3676 | 501 | 1857 | 519 | 612 | 155 | 0 | 0 | 94
14:00 | 3676 | 501 | 1857 | 519 | 612 | 155 | 0 | 0 | 94
14:30 | 3488 | 499 | 1773.5 | 637 | 586 | 155 | 0 | 0 | 94
15:00 | 3300 | 497 | 1690 | 755 | 560 | 155 | 0 | 0 | 94
15:30 | 3295 | 497 | 1648.5 | 679 | 561 | 155.5 | 0 | 0 | 96
16:00 | 3290 | 497 | 1607 | 603 | 562 | 156 | 0 | 0 | 98
16:30 | 3229 | 497.5 | 1596 | 648.5 | 562 | 156.5 | 0 | 0 | 99
17:00 | 3168 | 498 | 1585 | 694 | 562 | 157 | 0 | 0 | 100
17:30 | 3340 | 590.5 | 1743.5 | 1197.5 | 617.5 | 157.5 | 8.5 | 0 | 109
18:00 | 3512 | 683 | 1902 | 1701 | 673 | 158 | 17 | 0 | 118
18:30 | 3552 | 686 | 1970 | 1604.5 | 727.5 | 158 | 8.5 | 0 | 117
19:00 | 3592 | 689 | 2038 | 1508 | 782 | 158 | 0 | 0 | 116
19:30 | 3669 | 688 | 2068 | 1439 | 781 | 158 | 0 | 0 | 112
20:00 | 3657 | 689 | 2057 | 1438 | 780 | 159 | 0 | 0 | 102
20:30 | 3656.5 | 689 | 2062.5 | 1374.5 | 780 | 159 | 0 | 0 | 101
21:00 | 3656 | 689 | 2068 | 1311 | 780 | 159 | 0 | 0 | 100
21:30 | 3654 | 689 | 2050 | 1127 | 780 | 159.5 | 0 | 0 | 98
22:00 | 3652 | 689 | 2032 | 943 | 780 | 160 | 0 | 0 | 96
22:30 | 3662.5 | 593.5 | 2041 | 890 | 743.5 | 160 | 0 | 0 | 95
23:00 | 3673 | 498 | 2050 | 837 | 707 | 160 | 0 | 0 | 94
23:30 | 3649 | 498 | 1998.5 | 837 | 682 | 160 | 0 | 0 | 93 | Max Temp. in Dhaka |  | 33.8° C
24:00 | 3625 | 498 | 1947 | 837 | 657 | 160 | 0 | 0 | 92
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
Note on W13: Author:

## Generation
g | 2020-11-13
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 86 | 86 | 86 | 88 | 88 | 88 | 90 | 91 | 93 | 92 | 90 | 87 | 85 | 85 | 85 | 86 | 87 | 88 |  | 88 | 88 | 89 | 89 | 90 | 90 | 90 | 2044363
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1692000
3 | Chattogram TPP-1 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 110 | 110 | 110 | 110 |  | 110 | 115 | 115 | 115 | 115 | 115 | 115 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 4 | 11 | 15 | 18 | 19 | 19 | 18 | 16 | 12 | 6 | 0 | [9 empty] | 138645
6 | Sikalbaha 225MW CCPP (Gas) | 206 | 205 | 203 | 205 | 207 | 207 | 216 | 205 | 204 | 204 | 229 | 207 | 204 | 206 | 205 | 204 | 204 | 204 |  | 202 | 208 | 202 | 202 | 203 | 204 | 204 | 4896684
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 17 |  | 0 | [6 empty] | 27512
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 55 | 55 | 55 | 55 | 55 | 32 | 35 | 35 | 35 | 35 | 62 | 95 | 92 | 32 | 35 | 32 | 32 | 82 |  | 82 | 82 | 82 | 82 | 82 | 60 | 37 | 1478000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [16 empty] | 5 | 35 |  | 15 | 0 | [5 empty] | 60218
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 45 | 45 | 45 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 501818
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 153 | 150 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 170 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2808000
23 | Ghorasal TPP Unit-5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2835000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4785200
26
28 | Ashuganj TPP Unit- 3 | 135 | 135 | 135 | 135 | 135 | 120 | 100 | 100 | 100 | 100 | 100 | 135 | 135 | 100 | 100 | 100 | 80 | 80 |  | 80 | 80 | 80 | 100 | 100 | 100 | 100 | 2728536
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 29 | 29 | 29 | 29 | 29 | 29 | 10 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 26 |  | 29 | 29 | 29 | 26 | 29 | 29 | 29 | 635544
33 | Ashuganj 225 MW CCPP | 180 | 190 | 189 | 181 | 181 | 160 | 201 | 197 | 180 | 193 | 208 | 192 | 181 | 181 | 185 | 179 | 178 | 178 |  | 192 | 196 | 189 | 184 | 180 | 182 | 180 | 4476000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 270 | 260 | 265 | 265 | 300 | 285 | 260 | 265 | 355 | 340 | 330 | 260 | 290 | 275 | 275 | 295 |  | 305 | 315 | 300 | 295 | 300 | 295 | 295 | 7130400
35 | Ashuganj 55 MW PP (Precision) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 30 | 30 | 40 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 441600
36 | Chandpur 150 MW CCPP | 50 | 50 | 50 | 50 | 50 | 50 | 51 | 50 | 73 | 74 | 73 | 74 | 70 | 73 | 75 | 72 | 70 | 70 |  | 75 | 75 | 75 | 75 | 72 | 74 | 70 | 1550510
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 380 | 390 | 400 | 400 | 360 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 350 | 350 | 350 | 400 |  | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 8503750
41 | Haripur 360MW CCPP(HPL) | 294 | 294 | 320 | 320 | 320 | 327 | 298 | 288 | 288 | 288 | 296 | 319 | 343 | 288 | 287 | 287 | 259 | 305 |  | 334 | 334 | 334 | 334 | 334 | 334 | 304 | 7342000
42 | RPCL 210MW CCPP | 89 | 89 | 89 | 90 | 90 | 106 | 106 | 105 | 105 | 101 | 99 | 100 | 99 | 98 | 98 | 98 | 103 | 155 |  | 123 | 122 | 123 | 126 | 124 | 159 | 161 | 2537960
43 | Mymensingh PV 50 MW Solar PP | [6 empty] | 5 | 25 | 39 | 47 | 52 | 53 | 49 | 42 | 29 | 11 | 1 | [9 empty] | 352760
44 | Fenchugonj CCPP Phase-1 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 43 | 43 | 44 | 44 |  | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 998000
45 | Fenchugonj CCPP Phase-2 | [20 empty] | 0 | 22 | 22 | 22 | 22 | 22 | 84480
46 | Shajibazar 330 MW CCPP | 157 | 157 | 157 | 156 | 157 | 160 | 158 | 157 | 157 | 159 | 158 | 158 | 159 | 158 | 160 | 159 | 160 | 159 |  | 158 | 157 | 158 | 158 | 159 | 159 | 160 | 3611000
47 | Shahjibazar GTPP Unit- 8 & 9 | 52 | 52 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 65 | 40 | 50 | 51 | 52 | 67 |  | 65 | 67 | 67 | 67 | 68 | 67 | 67 | 1225728
48 | Shahjibazar 86MW PP (Shahjibazar) | 84 | 84 | 40 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 30 | 82 | 40 | 40 | 20 | 20 | 84 |  | 84 | 84 | 84 | 84 | 84 | 84 | 40 | 1143360
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 217 | 217 | 217 | 217 | 217 | 217 | 185 | 165 | 164 | 164 | 164 | 165 | 192 | 185 | 185 | 185 | 152 | 202 |  | 217 | 217 | 217 | 217 | 217 | 217 | 217 | 4675330
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 421000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 8 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 239400
54 | Hobiganj 11MW PP Cofidence-E | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 3 | 5 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 164000
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 50 | 22 | 22 | 22 | 22 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 762000
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 24 | 24 | 24 | 24 | 457296
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 295 | 280 | 275 | 280 | 270 | 300 | 310 | 280 | 270 | 310 | 300 | 300 | 260 | 300 | 270 | 280 | 270 |  | 280 | 315 | 310 | 300 | 295 | 280 | 280 | 7120950
| Bibiyana South 400 MW | 40 | 40 | 40 | 39 | 40 | 40 | 40 | 40 | 40 | 40 | 45 | 35 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 873600
58 | Nababganj 55 MW PP (Southern power ) | [26 empty] | 0
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 475728
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 16 | 16 | 16 |  |  |  | 16 | 16 |  | 16 | 16 | 19 | 19 | 19 | 19 | 19 | 362952
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | [14 empty] | 17 | 17 | 17 | 17 | 17 | 20 | 20 | 192888
63 | Impoprt (Tripura) | 100 | 44 | 92 | 90 | 86 | 80 | 72 | 60 | 60 | 78 | 80 | 90 | 94 | 94 | 94 | 98 | 100 | 118 |  | 116 | 112 | 102 | 100 | 96 | 94 | 92 | 2198400
64 | Malancha, Ctg. EPZ (United) | 31 | 31 | 33 | 33 | 33 | 37 | 40 | 39 | 41 | 41 | 41 | 42 | 42 | 42 | 39 | 40 | 41 | 41 |  | 41 | 42 | 40 | 40 | 40 | 42 | 42 | 569280
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 16 | 19 | 19 | 19 | 19 | 434520
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 250920
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 12 | 8 | 8 | 8 | 8 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 627000
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 20 | 20 | 20 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 494070
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 6 | 22 | 22 | 13 | 13 | 10 | 10 | 10 | 10 | 15 |  | 25 | 25 | 30 | 30 | 30 | 31 | 31 | 545400
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 0 | 0 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 592600
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 512600
73 | Ghorashal 108MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 295863
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | 8 | [12 empty] | 36 | 8 | 8 | 8 | 94 |  | 65 | 65 | 65 | 65 | 9 | 9 |  | 495600
| Manikgonj 162MW PP | [8 empty] | 18 | 18 |  | 18 | 18 | 18 | 44 | 23 | 28 | 29
77 | Siddhirganj 100 PP(Dutch Bangla) | [16 empty] | 3 | 30 | [8 empty] | 58560
78 | Gazipur 52 MW PP
79 | Kodda 150MW PP
80 | Jamalpur 95 MW PP(Powerpac) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 792960
81 | Jangalia 52 MW PP (Lakdanavi) | [16 empty] | 1 | 16 | [8 empty] | 25728
| Gazipur 100 MW PP | 52 | 52 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 22 | 34 | 34 | 35 | 35 | 35 | 36 |  | 52 | 53 | 53 | 53 | 53 | 53 | 35 | 853656
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 2 | 3 | 4 | 4 | 4 | 4 | 4 | 2 | 1 | [10 empty] | 29641
| Jodiac Power | 54 | 54 | 54 | 54 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 47 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1055222
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | 15 | 15 | [14 empty] | 2 | 30 | [8 empty] | 93600
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP(Summit) | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3415709
87 | Meghnaghat 100 MW(IEL) | [16 empty] | 1 | 20 |  | 24 | 0 | [5 empty] | 47040
| Meghnaghat 104 MW PP (OPCL) | 90 | 58 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 71 | 90 | 70 | 53 | 76 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1255640
88 | Ghorashal 78.5 MW PP(MAX) | [26 empty] | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [26 empty] | 0
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 50 | 50 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 30 | 35 | 20 | 20 | 20 | 20 | 40 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 837360
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 10 | 10 | 10 | 10 | 35 | 43 | 43 | 43 | 43 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1047112
94 | Gagnagar 102 MW PP (Digital Power) | 24 | [11 empty] | 24 | 40 | 7 | 7 | 7 | 94 |  | 64 | 64 | 64 | 32 |  |  | 24 | 412272
95 | Patenga 50MW PP (Baraka) | 50 | 25 | 19 | [8 empty] | 8 | 18 | 36 | 43 | 25 | 19 | 41 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 627840
96 | Chattogram 108 MW PP (ECPV) | [26 empty] | 0
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | [13 empty] | 7 | 15 | 15 | 15 | 30 | [8 empty] | 118896
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 17 | 35 | [8 empty] | 58582
101 | Kushiara 163 MW CCPP (KP) | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 |  | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 2529163
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [10 empty] | 15200
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 54 | 54 | 35 | 35 | 54 |  | 54 | 54 | 54 | 54 | 35 | 35 | 35 | 765720
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [16 empty] | 7 | 40 |  | 16 | 16 | 16 |  |  |  |  | 108000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [26 empty] | 0
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 50 | 30 | 10 | 10 | 40 | 10 | 10 | 10 | 10 | 10 | 48 | 50 | 50 | 20 | 20 | 100 |  | 100 | 100 | 100 | 100 | 85 | 88 | 88 | 1308480
116 | Chandpur 200MW (Desh energy) | [26 empty] | 0
117 | Ashuganj 150MW PP (Midland) | [13 empty] | 13 | 10 | 10 | 15 | 61 |  | 50 | 50 | 50 | 50 | 10 | 10 |  | 369672
118 | Bibiyana-III 400 MW CCPP | 400 | 400 | 401 | 400 | 400 | 399 | 351 | 351 | 351 | 354 | 354 | 353 | 402 | 353 | 354 | 353 | 304 | 399 |  | 402 | 402 | 402 | 402 | 402 | 400 | 401 | 9055000
| Jamalpur 115 MW PP (United) | 65 | 24 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 35 | 35 | 8 | 9 | 92 |  | 115 | 115 | 115 | 115 | 115 | 95 | 40 | 1124400
| Anwara 300 MW PP (United) | 87 | 16 | [9 empty] | 16 | 33 | 33 | 33 | 16 | 16 | 132 |  | 132 | 144 | 142 | 142 | 142 | 53 | 16 | 1114036
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 40 | 40 | 40 | 10 | 10 | 30 | 58 | 77 | 77 | 77 | 90 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1862400
120 | Eastern Zone Total | 5240 | 5021 | 4833 | 4723 | 4575 | 4454 | 4377 | 4338 | 4286 | 4274 | 4463 | 4655 | 5090 | 4864 | 4921 | 4661 | 4587 | 5862 |  | 5725 | 5756 | 5739 | 5700 | 5532 | 5425 | 5219 | 119172354
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [16 empty] | 6 | 16 | [8 empty] | 27840
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [11 empty] | 17 | 17 | 35 | 17 | 17 | 17 | 105 |  | 105 | 105 | 105 | 105 | 17 | 17 |  | 601440
130
131
132
133 | Bhola Nutan Biddut BD LTD (GAS) | 36 | 35 | 35 | 34 | 36 | 36 | 35 | 37 | 36 | 35 | 34 | 35 | [7 empty] | 17 | 10 | 4 | 36 | 36 | 36 | 36 | 629150
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [16 empty] | 16 | 32 |  | 32 | 16 | 16 | 16 |  |  |  | 111360
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 89 | 88 | 87 | 87 | 25 | 24 | 23 | 23 | 23 | 23 | 23 | 23 | 39 | 40 | 35 | 35 | 35 | 78 |  | 90 | 91 | 92 | 90 | 91 | 91 | 91 | 1337212
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 26 | 25 | 24 | 24 | 23 | 22 | 20 | 19 | 17 | 12 | 19 | 20 | 21 | 21 | 19 | 20 | 20 | 27 |  | 28 | 28 | 28 | 28 | 27 | 27 | 26 | 530600
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 605 | 414 | 414 | 414 | 414 | 414 | 414 | 407 | 408 | 408 | 408 | 408 | 501 | 502 | 497 | 497 | 498 | 683 |  | 689 | 688 | 689 | 689 | 689 | 498 | 498 | 12054545
147 | Bheramara 410 MW CCPP | 300 | 300 | 300 | 300 | 300 | 270 | 270 | 330 | 300 | 280 | 320 | 335 | 345 | 270 | 320 | 320 | 280 | 345 |  | 350 | 360 | 350 | 340 | 340 | 345 | 345 | 7748640
148 | Payra 1320 MW | 500 | 500 | 480 | 480 | 480 | 470 | 350 | 350 | 330 | 300 | 320 | 350 | 400 | 350 | 350 | 350 | 350 | 460 |  | 570 | 570 | 570 | 570 | 570 | 500 | 450 | 10450500
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2 | 62 | 59 | 60 | 59 | 62 | 61 | 63 | 64 | 47 | 63 | 63 | 63 | 62 | 60 | 60 | 62 | 62 | 63 |  | 62 | 61 | 60 | 60 | 60 | 57 | 57 | 1425163
152 | Barapukuria 275 MW TPP Unit-3 | 151 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3681600
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP | [11 empty] | 60 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 850000
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 145 | 147 | 145 | 145 | 144 | 145 | 138 | 169 | 152 | 153 | 186 | 188 | 183 | 140 | 143 | 152 | 153 | 151 |  | 166 | 186 | 185 | 179 | 176 | 176 | 165 | 4026227
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 159 | 161 | 160 | 159 | 158 | 160 | 139 | 173 | 156 | 157 | 169 | 201 | 197 | 130 | 142 | 161 | 158 | 156 |  | 173 | 195 | 193 | 187 | 184 | 186 | 174 | 4261000
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 395 | 419 | 370 | 333 | 330 | 300 | 270 | 300 | 302 | 270 | 276 | 347 | 379 | 270 | 339 | 303 | 298 | 367 |  | 416 | 416 | 417 | 408 | 377 | 408 | 380 | 8397509
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 508560
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 242982
165 | Amnura 50 MW PP(Sinha) | [20 empty] | 0 | [5 empty] | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
170 | Chapainawabganj 100 MW Peaking PP | [26 empty] | 35512
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [26 empty] | 0
172 | Confidence Power Bogura Unit-1 113 MW | [16 empty] | 20 | 90 |  | 109 | 109 | 109 | 50 |  |  |  | 424032
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 12 | 76 |  | 98 | 71 | 72 | 52 |  |  |  | 341760
177 | Sympa Solar Power 8MW | [6 empty] | 1 | 2 | 3 | 5 | 6 | 6 | 5 | 5 | 3 | 2 | 0 | [9 empty] | 38431
178
178