## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-11-19 | Thursday
|  |  | Date (day): | 2020-11-19 |  | Thursday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13110.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14422 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-11-18 | 2020-11-19 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 170 | 170 | 150 | 150
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 115 | 115 | 115 | 75 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 200 | 200 |  | 165 | Machine problem
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 12 | 50 | 50 | 58 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under S/D for dust in gas.
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 284 | 324 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 360 | 370 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 50 | 78 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 270 | 290 | 305 | 305
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 15 | 78 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 30 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 50 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19 |  | 3 | Engine problem
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 4 | 80 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 64 | 94 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 41 | 47 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 17 | 17 | 17 |  | 16 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 51 | 16 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 30 | 180 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 86 | 0 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 90 | 105 | 90 | 90 |  | 15 | Engine problem
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 90 | 90 | 90 | 90 |  | 14 | Engine problem
|  | Manikgonj 162MW PP |  | HFO | IPP | 9*18 | 0 | 0 | 55 | 0 | 0 | 0
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 2167 | 2474 | 3509 | 3849 | 634 | 1380
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 158 | 158 | 160 | 160 | 70 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 204 | 203 | 215 | 225
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 102 | 102
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 60 | 100 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 16 | 10 | 20
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 12 | 100 | 100
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 53 | 157 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 845 | 1041 | 1691 | 1686 | 460 | 98
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 135 | 135 | 100 | 100 | 35 |  | Gas Shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 191 | 181 | 225 | 225 |  |  | FGMO
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 345 | 290 | 360 | 360 |  |  | FGMO
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 27 | 29 | 30 | 30 | 15 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 26 | 26 | 8 | 8 | 187 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 10 | 113 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 75 | 70 | 90 | 90 |  | 57 | ST Under maint.
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 165 | 180
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 92 | 116 | 156 | 172
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 52 | 52
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 21 | 20 | 21
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 36 | 113 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1070 | 1220 | 1705 | 1987 | 550 | 417
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 107 | 110 | 160 | 160 | 42 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 16 | 25 | 25 | 25 |  | 70 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 50 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
|  | Mymensingh PV 50 MW Solar PP |  | Solar | IPP | 50 | 0 | 0 | 49 | 0 | 50 | 0
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 309 | 320 | 573.6 | 522 | 42 | 70
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 32 | GT-2 under shut down for maint.
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 50 | 65 | 60 | 60
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 107 | 107 | 110 | 110 |  | 54 | STG under maint.
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 159 | 159 | 160 | 160 |  | 170 | GT-2 S/D due to gas shortage.
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 53 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 46 | 49 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 67 | 66 | 66 |  |  | FGMO
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 86 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 |  |  | Substation maintenance.
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  |  | Substation maintenance.
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 0 | 25 | 25
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 320 | 320
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 252 | 401 | 400 | 400
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 0 | 0 |  |  | Substation maintenance.
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 45 | 45 | 45 | 45
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 866 | 1073 | 1408 | 1408 | 0 | 256
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 738 | 881 | 744 | 889
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 49 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 350 | 345 | 410 | 410
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 53 | 90 | 90 | 90
| 108 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1157 | 1365 | 1499 | 2070 | 0 | 0
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 21 | 27 | 30 | 30
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 23 | 95 | 95 | 95
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 460 | 520 | 600 | 660
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 22 | 36 | 35 | 35
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 526 | 694 | 870 | 930 | 0 | 194
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 70 | 70 | 70 | 70 | 30 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | Gas shortage & ST Under maint
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 157 | 193 | 220 | 220 |  |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 159 | 187 | 220 | 220 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 388 | 386 | 413 | 413 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 33
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 22 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 113 | 113
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 110 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 838 | 979 | 1584 | 1707 | 201 | 210
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 19 | 113 | 113 | 113
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 174 | 263 | 271 | 263 | 294 | 40
|  | Total |  |  |  |  | 20383 | 19892 | 7952 | 9429 | 13110.6 | 14422 | 2181 | 2665
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7423.216 | 8802 | 12238.7847 | 13462.9806
| A. |  | 2020-11-18 | (Yesterday) |  |  |  |  | Wednesday
| 1 | Highest Generation : |  |  | 9429 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 6346 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9429 | MW
| 3 | Day peak Generation : |  |  | 7952 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8802 | MW
| 4 | Evening peak Generation : |  |  | 9429 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 182.7343 | MKWHr | By Solar | 0.50565 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 112.9455 | MKWHr |  | By Oil: | 31.281 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 15.2851 | MKWHr |  | By Hydro: | 3.776 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2181 | MW | Dhaka | 3368 | 3368 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2665 | MW | Chittagong | 991 | 991 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4846 | MW | Khulna | 1056 | 1056 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1012.43 | MMCFD |  |  | Rajshahi | 850 | 850 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 128932840.928 | ii) Oil : | Taka | 195761434.76 | Comilla | 770 | 770 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 70893740 | Total | Taka | 395588015.688 | Mymensingh | 668 | 668 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 297 | 297 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 348 | MW (E to W) at | 19:00 | hrs | Barisal | 244 | 244 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 236 | MW at | 8:00 | hrs | Rangpur | 558 | 558 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 30.6° C |  |  | Total | 8802 | 8802 |  | 0
| B. |  | 2020-11-19 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 29.3° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14422 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 8100 | MW
| 4 | Reserve(Generation end) |  |  |  | 4622 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 189.9243 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6301 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 16.6793 | MKWHr. | ii) HVDC Flow at Peak Time |  | 881 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.2618 | MKWHr. | iii) Maximum HVDC Flow : |  | 882 | MW at | 20:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 102.74 |  | (b) Today: | 102.61 |  | (c) Rule Curve: |  | 107.2
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-11-18
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Anlima Energy Ltd. | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Mymensingh PV 50 MW Solar PP | Manikgonj 162MW PP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 171 | 115 | 200 | 12 | 0 | 0 | 300 |  | 0 | 380 | 150 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 31 | 17 | 25 | 0 | 0 | 92 | 70 | 120 | 0 | 0 | 215 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 32 | 20 | 35 | 80 | 0 | 0 | 325 | 0 | 199 | 8 | 52 | 27 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 96 | 113 | 25 | 20 | 0 | 30 | 30 | 50 | 50 | 107 | 159 | 67 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 399 | 85 | 52 | 0 | 0 | 88 | 54 | 0 | 0 | 26 | 100 | 45 | 90 | 0 | 0 |  | 610 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 76 | 0 | 166 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 36 | 0 |  | 4840 | 2390 | 7230 | 3263 | 610 | 1593 | 856 | 650 | 162 | 0 | 96 | 0 | 0 | 102.79
2:00 | 0 | 0 | 164 | 115 | 200 | 12 | 0 | 0 | 300 |  | 0 | 380 | 150 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 31 | 17 | 25 | 0 | 0 | 94 | 70 | 120 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 30 | 20 | 35 | 80 | 0 | 0 | 300 | 0 | 180 | 8 | 46 | 27 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 15 | 94 | 114 | 25 | 20 | 0 | 30 | 30 | 50 | 50 | 107 | 158 | 67 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 399 | 45 | 52 | 0 | 0 | 16 | 54 | 0 | 0 | 0 | 100 | 45 | 75 | 0 | 0 |  | 610 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 75 | 0 | 156 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 37 | 0 |  | 4607 | 2324 | 6931 | 3169 | 610 | 1573 | 701 | 620 | 164 | 0 | 94 | 0 | 0 | 102.78
3:00 | 0 | 0 | 168 | 115 | 200 | 12 | 0 | 0 | 300 |  | 0 | 380 | 155 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 31 | 17 | 25 | 0 | 0 | 87 | 70 | 120 | 0 | 0 | 209 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 36 | 80 | 0 | 0 | 320 | 0 | 190 | 8 | 51 | 27 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 15 | 94 | 113 | 25 | 20 | 0 | 30 | 30 | 50 | 50 | 107 | 160 | 67 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 399 | 8 | 17 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 70 | 45 | 53 | 0 | 0 |  | 610 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 154 | 0 | 43 | 0 | 158 | 0 | 361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 36 | 0 |  | 4318 | 2324 | 6642 | 3219 | 610 | 1570 | 372 | 620 | 157 | 0 | 94 | 0 | 0 | 102.77
4:00 | 0 | 0 | 171 | 115 | 200 | 12 | 0 | 0 | 300 |  | 0 | 380 | 150 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 31 | 17 | 25 | 0 | 0 | 85 | 70 | 120 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 37 | 80 | 0 | 0 | 300 | 0 | 180 | 8 | 51 | 27 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 15 | 90 | 112 | 25 | 20 | 0 | 30 | 30 | 50 | 50 | 107 | 160 | 67 | 87 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 350 | 8 | 17 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 50 | 45 | 53 | 0 | 0 |  | 516 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 159 | 0 | 42 | 0 | 163 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 37 | 0 |  | 4212 | 2219 | 6431 | 3143 | 516 | 1560 | 347 | 620 | 155 | 0 | 90 | 0 | 0 | 102.76
5:00 | 0 | 0 | 173 | 115 | 200 | 12 | 0 | 0 | 300 |  | 0 | 380 | 165 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 17 | 25 | 0 | 0 | 83 | 70 | 120 | 0 | 0 | 213 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 38 | 80 | 0 | 0 | 315 | 0 | 197 | 8 | 50 | 27 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 15 | 84 | 113 | 25 | 20 | 0 | 30 | 30 | 11 | 50 | 107 | 160 | 67 | 20 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 350 | 8 | 17 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 45 | 25 | 0 | 0 |  | 516 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 163 | 0 | 42 | 0 | 168 | 0 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 38 | 0 |  | 4103 | 2243 | 6346 | 3193 | 516 | 1476 | 304 | 620 | 153 | 0 | 84 | 0 | 0 | 102.75
6:00 | 0 | 0 | 171 | 115 | 200 | 12 | 0 | 0 | 330 |  | 0 | 400 | 280 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 17 | 25 | 0 | 0 | 83 | 70 | 120 | 0 | 0 | 206 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 38 | 80 | 0 | 0 | 310 | 0 | 194 | 8 | 51 | 27 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 15 | 80 | 113 | 25 | 20 | 0 | 30 | 30 | 11 | 50 | 107 | 161 | 67 | 20 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 328 | 8 | 17 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 45 | 17 | 0 | 0 |  | 516 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 180 | 0 | 42 | 0 | 181 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 35 | 0 |  | 4218 | 2302 | 6520 | 3186 | 516 | 1524 | 411 | 650 | 153 | 0 | 80 | 0 | 0 | 102.74
7:00 | 0 | 0 | 170 | 115 | 200 | 12 | 0 | 0 | 330 |  | 0 | 400 | 290 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 25 | 28 | 17 | 25 | 4 | 0 | 86 | 70 | 120 | 0 | 0 | 216 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 33 | 80 | 0 | 0 | 320 | 0 | 202 | 8 | 51 | 27 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 15 | 76 | 113 | 25 | 20 | 0 | 30 | 30 | 11 | 50 | 107 | 159 | 67 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 10 | 0 | 0 | 290 | 14 | 18 | 0 | 0 | 16 | 21 | 0 | 0 | 0 | 52 | 45 | 17 | 5 | 0 |  | 516 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 193 | 0 | 42 | 0 | 170 | 0 | 367 | 17 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 500 | 34 | 0 |  | 4285 | 2321 | 6606 | 3156 | 516 | 1526 | 517 | 650 | 156 | 0 | 76 | 9 | 0 | 102.73
8:00 | 0 | 0 | 170 | 115 | 200 | 12 | 0 | 0 | 345 |  | 0 | 360 | 290 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 25 | 21 | 17 | 25 | 22 | 0 | 86 | 70 | 120 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 6 | 80 | 0 | 0 | 280 | 0 | 186 | 8 | 51 | 27 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 21 | 15 | 82 | 113 | 25 | 20 | 1 | 30 | 30 | 47 | 50 | 107 | 159 | 67 | 84 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 5 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 9 | 10 | 0 | 0 | 232 | 93 | 64 | 0 | 1 | 16 | 53 | 0 | 0 | 0 | 100 | 45 | 34 | 21 | 36 |  | 515 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 166 | 0 | 42 | 0 | 163 | 0 | 363 | 35 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 500 | 36 | 0 |  | 4603 | 2366 | 6969 | 3085 | 515 | 1577 | 870 | 650 | 156 | 0 | 82 | 34 | 0 | 102.7
9:00 | 0 | 0 | 170 | 115 | 200 | 12 | 0 | 0 | 284 |  | 0 | 360 | 300 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 21 | 17 | 25 | 48 | 0 | 86 | 70 | 120 | 0 | 0 | 210 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 4 | 80 | 0 | 0 | 300 | 0 | 198 | 8 | 51 | 27 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 0 | 15 | 80 | 110 | 25 | 20 | 2 | 30 | 30 | 47 | 50 | 107 | 157 | 65 | 84 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 5 | 0 | 30 | 0 | 0 | 0 | 0 | 11 | 14 | 10 | 0 | 0 | 232 | 115 | 90 | 0 | 3 | 16 | 54 | 0 | 0 | 2 | 100 | 45 | 90 | 37 | 61 |  | 500 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 168 | 0 | 42 | 0 | 173 | 0 | 364 | 53 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 490 | 33 | 0 |  | 4777 | 2399 | 7176 | 3153 | 500 | 1513 | 1075 | 640 | 156 | 0 | 80 | 59 | 0 | 102.72
10:00 | 0 | 0 | 170 | 115 | 200 | 12 | 0 | 0 | 284 |  | 0 | 360 | 280 | 11 | 6 | 15 | 0 | 0 | 37 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 0 | 19 | 25 | 20 | 17 | 25 | 51 | 0 | 86 | 70 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 32 | 20 | 3 | 135 | 0 | 0 | 260 | 0 | 181 | 26 | 51 | 27 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 25 | 15 | 84 | 108 | 16 | 20 | 2 | 30 | 30 | 47 | 47 | 107 | 158 | 40 | 84 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 5 | 0 | 30 | 0 | 0 | 0 | 0 | 100 | 17 | 60 | 0 | 10 | 232 | 115 | 90 | 0 | 4 | 49 | 54 | 0 | 0 | 36 | 100 | 45 | 90 | 42 | 76 |  | 500 | 0 | 340 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 201 | 0 | 20 | 0 | 177 | 0 | 358 | 53 | 0 | 0 | 0 | 0 | 0 | 4 | 25 | 460 | 6 | 0 |  | 5064 | 2360 | 7424 | 3092 | 500 | 1469 | 1444 | 610 | 156 | 0 | 84 | 69 | 0 | 102.71
11:00 | 0 | 0 | 160 | 115 | 200 | 12 | 0 | 0 | 285 |  | 0 | 360 | 250 | 50 | 15 | 30 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 0 | 19 | 25 | 20 | 17 | 25 | 51 | 0 | 88 | 70 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 44 | 20 | 3 | 135 | 0 | 0 | 260 | 0 | 182 | 26 | 50 | 27 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 25 | 15 | 86 | 107 | 16 | 20 | 2 | 30 | 30 | 47 | 47 | 107 | 159 | 40 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 30 | 0 | 0 | 0 | 0 | 100 | 19 | 60 | 0 | 10 | 232 | 115 | 90 | 0 | 4 | 53 | 37 | 0 | 0 | 36 | 100 | 45 | 90 | 47 | 73 |  | 739 | 0 | 345 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 165 | 0 | 23 | 0 | 155 | 0 | 348 | 53 | 0 | 0 | 0 | 0 | 0 | 5 | 35 | 460 | 4 | 0 |  | 5063 | 2546 | 7609 | 2992 | 739 | 1440 | 1507 | 610 | 158 | 0 | 86 | 77 | 0 | 102.7
12:00 | 0 | 0 | 170 | 115 | 200 | 12 | 0 | 0 | 284 |  | 0 | 360 | 270 | 50 | 15 | 30 | 0 | 0 | 0 | 4 | 64 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 0 | 19 | 25 | 16 | 17 | 25 | 51 | 0 | 88 | 70 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 3 | 135 | 0 | 0 | 345 | 0 | 191 | 26 | 75 | 27 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 15 | 92 | 107 | 16 | 20 | 2 | 30 | 50 | 47 | 46 | 107 | 159 | 40 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 30 | 0 | 0 | 0 | 0 | 86 | 19 | 60 | 0 | 10 | 252 | 115 | 90 | 0 | 4 | 53 | 54 | 0 | 0 | 36 | 100 | 45 | 90 | 49 | 55 |  | 738 | 0 | 350 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 157 | 0 | 23 | 0 | 159 | 0 | 388 | 53 | 0 | 0 | 0 | 19 | 0 | 5 | 35 | 460 | 22 | 0 |  | 5257 | 2695 | 7952 | 3236 | 738 | 1498 | 1541 | 610 | 158 | 0 | 92 | 79 | 0 | #REF!
13:00 | 0 | 0 | 170 | 115 | 200 | 12 | 0 | 0 | 297 |  | 0 | 360 | 280 | 50 | 15 | 30 | 0 | 0 | 0 | 15 | 64 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 0 | 19 | 25 | 20 | 17 | 25 | 51 | 0 | 88 | 70 | 120 | 0 | 0 | 219 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 7 | 135 | 0 | 0 | 335 | 0 | 193 | 26 | 75 | 27 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 15 | 94 | 107 | 17 | 20 | 2 | 30 | 51 | 47 | 49 | 107 | 161 | 40 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 30 | 0 | 0 | 0 | 0 | 81 | 18 | 60 | 0 | 10 | 252 | 115 | 90 | 0 | 4 | 52 | 39 | 0 | 0 | 36 | 100 | 45 | 90 | 43 | 55 |  | 738 | 0 | 385 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 166 | 0 | 23 | 0 | 169 | 0 | 391 | 53 | 0 | 0 | 0 | 36 | 0 | 5 | 35 | 460 | 36 | 0 |  | 5286 | 2783 | 8069 | 3304 | 738 | 1534 | 1559 | 610 | 158 | 0 | 94 | 72 | 8069 | 102.7
14:00 | 0 | 0 | 170 | 115 | 200 | 12 | 0 | 0 | 275 |  | 0 | 360 | 280 | 40 | 15 | 30 | 0 | 0 | 0 | 20 | 64 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 0 | 19 | 25 | 14 | 17 | 25 | 51 | 0 | 89 | 70 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 4 | 135 | 0 | 0 | 275 | 0 | 181 | 26 | 70 | 27 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 15 | 102 | 107 | 17 | 20 | 2 | 30 | 65 | 52 | 49 | 107 | 161 | 40 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 30 | 0 | 0 | 0 | 0 | 80 | 15 | 60 | 0 | 10 | 252 | 115 | 90 | 0 | 3 | 52 | 36 | 0 | 0 | 36 | 100 | 45 | 90 | 36 | 55 |  | 739 | 0 | 345 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 146 | 0 | 23 | 0 | 197 | 0 | 349 | 53 | 0 | 0 | 0 | 39 | 0 | 4 | 35 | 420 | 36 | 0 |  | 5172 | 2650 | 7822 | 3168 | 739 | 1471 | 1553 | 570 | 159 | 0 | 102 | 60 | 0 | 102.69
15:00 | 0 | 0 | 170 | 115 | 200 | 12 | 0 | 0 | 306 |  | 0 | 360 | 335 | 25 | 15 | 15 | 0 | 0 | 0 | 36 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 18 | 17 | 25 | 42 | 0 | 91 | 70 | 120 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 2 | 135 | 0 | 0 | 295 | 0 | 190 | 26 | 70 | 27 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 15 | 102 | 108 | 17 | 20 | 1 | 30 | 65 | 50 | 46 | 107 | 160 | 40 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 15 | 0 | 0 | 0 | 0 | 80 | 10 | 60 | 0 | 10 | 305 | 115 | 94 | 0 | 2 | 16 | 53 | 0 | 0 | 18 | 100 | 45 | 90 | 24 | 68 |  | 739 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 148 | 0 | 23 | 0 | 164 | 0 | 355 | 17 | 0 | 0 | 0 | 35 | 0 | 2 | 35 | 410 | 35 | 0 |  | 5203 | 2551 | 7754 | 3222 | 739 | 1495 | 1436 | 560 | 161 | 0 | 102 | 39 | 0 | 102.69
16:00 | 0 | 0 | 170 | 115 | 200 | 12 | 0 | 0 | 314 |  | 0 | 360 | 275 | 11 | 15 | 15 | 0 | 0 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 18 | 17 | 25 | 32 | 0 | 89 | 70 | 120 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 4 | 135 | 0 | 0 | 295 | 0 | 190 | 26 | 70 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 15 | 90 | 109 | 25 | 20 | 0 | 30 | 65 | 50 | 46 | 107 | 159 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 15 | 0 | 0 | 0 | 0 | 69 | 4 | 60 | 0 | 10 | 304 | 115 | 90 | 0 | 1 | 16 | 54 | 0 | 0 | 18 | 100 | 87 | 90 | 9 | 46 |  | 739 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 145 | 0 | 23 | 0 | 158 | 0 | 396 | 17 | 0 | 0 | 0 | 35 | 0 | 1 | 35 | 410 | 36 | 0 |  | 5045 | 2587 | 7632 | 3259 | 739 | 1506 | 1304 | 560 | 159 | 0 | 90 | 15 | 0 | 102.69
17:00 | 0 | 0 | 170 | 115 | 200 | 12 | 0 | 0 | 314 |  | 0 | 370 | 290 | 7 | 15 | 15 | 0 | 0 | 0 | 7 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 5 | 19 | 25 | 18 | 17 | 8 | 32 | 0 | 87 | 70 | 120 | 0 | 0 | 216 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 5 | 50 | 20 | 8 | 135 | 0 | 0 | 315 | 0 | 200 | 26 | 70 | 29 | 5 | 0 | 51 | 0 | 0 | 1 | 21 | 8 | 33 | 15 | 104 | 106 | 25 | 20 | 0 | 30 | 65 | 50 | 46 | 107 | 159 | 67 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 15 | 0 | 0 | 7 | 0 | 34 | 0 | 90 | 0 | 13 | 304 | 115 | 90 | 0 | 0 | 16 | 54 | 0 | 0 | 18 | 100 | 45 | 90 | 1 | 13 |  | 738 | 0 | 375 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 16 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 11 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 155 | 0 | 23 | 0 | 171 | 0 | 406 | 35 | 0 | 9 | 0 | 34 | 0 | 0 | 35 | 410 | 36 | 0 |  | 5067 | 2720 | 7787 | 3320 | 738 | 1535 | 1371 | 561 | 157 | 0 | 104 | 1 | 0 | 102.68
18:00 | 0 | 0 | 170 | 115 | 200 | 12 | 0 | 0 | 324 |  | 0 | 370 | 260 | 56 | 32 | 45 | 0 | 0 | 0 | 70 | 64 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 22 | 17 | 25 | 32 | 0 | 87 | 70 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 49 | 0 | 34 | 50 | 20 | 16 | 135 | 0 | 0 | 290 | 0 | 181 | 26 | 70 | 29 | 5 | 0 | 51 | 0 | 0 | 20 | 21 | 8 | 33 | 15 | 120 | 110 | 25 | 20 | 0 | 30 | 65 | 50 | 49 | 107 | 159 | 67 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 170 | 0 | 0 | 50 | 0 | 30 | 0 | 100 | 0 | 75 | 400 | 115 | 100 | 0 | 0 | 153 | 54 | 0 | 0 | 89 | 100 | 13 | 90 | 0 | 0 |  | 881 | 0 | 345 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 48 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 161 | 0 | 82 | 0 | 168 | 0 | 376 | 90 | 0 | 52 | 0 | 113 | 0 | 0 | 109 | 500 | 35 | 0 |  | 5969 | 3322 | 9291 | 3346 | 881 | 1637 | 2435 | 650 | 157 | 65 | 120 | 0 | 0 | 102.67
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 170 | 115 | 200 | 12 | 0 | 0 | 324 |  | 0 | 370 | 290 | 78 | 78 | 55 | 0 | 0 | 0 | 80 | 94 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 22 | 17 | 25 | 16 | 0 | 88 | 70 | 120 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 12 | 50 | 20 | 16 | 135 | 0 | 0 | 290 | 0 | 181 | 26 | 70 | 29 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 8 | 33 | 21 | 116 | 110 | 25 | 20 | 0 | 30 | 65 | 53 | 49 | 107 | 159 | 67 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 180 | 0 | 0 | 50 | 0 | 0 | 0 | 100 | 0 | 113 | 401 | 115 | 105 | 0 | 0 | 157 | 54 | 0 | 0 | 113 | 100 | 45 | 90 | 0 | 0 |  | 881 | 0 | 345 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 16 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 193 | 0 | 95 | 0 | 187 | 0 | 386 | 90 | 0 | 0 | 0 | 113 | 0 | 0 | 110 | 520 | 36 | 0 |  | 6128 | 3301 | 9429 | 3438 | 881 | 1665 | 2450 | 670 | 158 | 51 | 116 | 0 | 0 | 102.66
19:30 | 0 | 0 | 170 | 115 | 200 | 12 | 0 | 0 | 325 |  | 0 | 370 | 285 | 50 | 65 | 30 | 0 | 0 | 0 | 55 | 94 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 22 | 17 | 25 | 0 | 0 | 88 | 70 | 120 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 12 | 50 | 20 | 17 | 135 | 0 | 0 | 290 | 0 | 184 | 26 | 70 | 29 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 8 | 33 | 21 | 114 | 110 | 25 | 20 | 0 | 30 | 65 | 53 | 49 | 107 | 159 | 67 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 180 | 0 | 0 | 50 | 0 | 0 | 0 | 100 | 0 | 115 | 401 | 115 | 105 | 0 | 0 | 159 | 54 | 0 | 0 | 113 | 100 | 45 | 90 | 0 | 0 |  | 881 | 0 | 345 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 16 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 173 | 0 | 96 | 0 | 188 | 0 | 403 | 90 | 0 | 0 | 0 | 113 | 0 | 0 | 110 | 520 | 36 | 0 |  | 6022 | 3267 | 9289 | 3421 | 881 | 1685 | 2309 | 670 | 158 | 51 | 114 | 0 | 0 | 0
20:00 | 0 | 0 | 170 | 115 | 200 | 12 | 0 | 0 | 324 |  | 0 | 370 | 250 | 50 | 64 | 30 | 0 | 0 | 0 | 50 | 94 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 22 | 17 | 25 | 0 | 0 | 88 | 70 | 120 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 10 | 50 | 20 | 20 | 135 | 0 | 0 | 290 | 0 | 181 | 26 | 70 | 29 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 8 | 33 | 21 | 114 | 112 | 25 | 20 | 0 | 30 | 65 | 53 | 49 | 107 | 160 | 67 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 180 | 0 | 0 | 50 | 0 | 0 | 0 | 100 | 0 | 115 | 400 | 115 | 105 | 0 | 0 | 159 | 54 | 0 | 0 | 113 | 100 | 45 | 90 | 0 | 0 |  | 882 | 0 | 345 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 16 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 171 | 0 | 95 | 0 | 188 | 0 | 354 | 90 | 0 | 0 | 0 | 113 | 0 | 0 | 110 | 550 | 36 | 0 |  | 5981 | 3246 | 9227 | 3419 | 882 | 1637 | 2266 | 700 | 158 | 51 | 114 | 0 | 0 | 102.66
21:00 | 0 | 0 | 170 | 115 | 200 | 12 | 0 | 0 | 330 |  | 0 | 370 | 270 | 25 | 40 | 15 | 0 | 0 | 0 | 20 | 64 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 22 | 17 | 25 | 0 | 0 | 89 | 70 | 120 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 0 | 50 | 20 | 21 | 135 | 0 | 0 | 290 | 0 | 181 | 26 | 70 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 112 | 110 | 25 | 20 | 0 | 30 | 65 | 53 | 49 | 107 | 158 | 68 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 120 | 0 | 0 | 24 | 0 | 0 | 0 | 100 | 0 | 113 | 400 | 115 | 72 | 0 | 0 | 160 | 54 | 0 | 0 | 113 | 100 | 45 | 90 | 0 | 0 |  | 881 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 173 | 0 | 97 | 0 | 189 | 0 | 377 | 90 | 0 | 0 | 0 | 113 | 0 | 0 | 110 | 550 | 36 | 0 |  | 5704 | 3242 | 8946 | 3419 | 881 | 1669 | 1954 | 701 | 159 | 51 | 112 | 0 | 0 | #REF!
22:00 | 0 | 0 | 170 | 115 | 200 | 12 | 0 | 0 | 330 |  | 0 | 370 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 22 | 17 | 25 | 0 | 0 | 91 | 70 | 120 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 0 | 50 | 20 | 32 | 135 | 0 | 0 | 290 | 0 | 176 | 8 | 49 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 106 | 111 | 25 | 20 | 0 | 30 | 65 | 53 | 50 | 107 | 158 | 67 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 70 | 400 | 85 | 72 | 0 | 0 | 160 | 54 | 0 | 0 | 75 | 98 | 45 | 90 | 0 | 0 |  | 882 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 161 | 0 | 96 | 0 | 169 | 0 | 370 | 90 | 0 | 0 | 0 | 70 | 0 | 0 | 50 | 550 | 36 | 0 |  | 5343 | 3099 | 8442 | 3361 | 882 | 1655 | 1526 | 700 | 161 | 51 | 106 | 0 | 0 | 102.65
23:00 | 0 | 0 | 170 | 115 | 200 | 12 | 0 | 0 | 339 |  | 0 | 370 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 22 | 17 | 25 | 0 | 0 | 90 | 70 | 120 | 0 | 0 | 206 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 32 | 100 | 0 | 0 | 290 | 0 | 178 | 8 | 52 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 18 | 100 | 112 | 25 | 20 | 0 | 30 | 60 | 53 | 50 | 107 | 159 | 67 | 86 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 11 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 399 | 55 | 72 | 0 | 0 | 53 | 54 | 0 | 0 | 0 | 96 | 45 | 90 | 0 | 0 |  | 882 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 159 | 0 | 96 | 0 | 159 | 0 | 403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 520 | 36 | 0 |  | 4919 | 2919 | 7838 | 3320 | 882 | 1706 | 1000 | 670 | 160 | 0 | 100 | 0 | 0 | 102.64
24:00 | 0 | 0 | 170 | 115 | 200 | 12 | 0 | 0 | 357 |  | 0 | 370 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 22 | 17 | 25 | 0 | 0 | 89 | 70 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 36 | 20 | 32 | 100 | 0 | 0 | 290 | 0 | 175 | 8 | 52 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 18 | 96 | 113 | 25 | 20 | 0 | 30 | 60 | 53 | 50 | 107 | 158 | 69 | 86 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 11 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 399 | 16 | 72 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 98 | 45 | 90 | 0 | 0 |  | 882 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 162 | 0 | 54 | 0 | 160 | 0 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 500 | 36 | 0 |  | 4721 | 2792 | 7513 | 3308 | 882 | 1626 | 792 | 650 | 159 | 0 | 96 | 0 | 0 | 102.63
KWH | 0 | 0 | 4082000 | 2772000 | 4736091 | 302136 | 0 | 0 | 7476000 |  | 0 | 8319000 | 5982342 | 485760 | 393960 | 353032 | 0 | 0 | 598000 | 357120 | 912816 | 12000 | 0 | 0 | 0 | 3648 | 1160640 | 409697 | 26750 | 372852 | 600000 | 538020 | 411900 | 591500 | 502536 | 0 | 2079976 | 1696000 | 2900000 | 0 | 0 | 4908131 | 0 | 0 | 0 |  | 0 | 0 | 254250 | 0 | 83520 | 788160 | 473664 | 438240 | 2758194 | 0 | 0 | 7505500 | 0 | 4558000 | 418181 | 1397090 | 622800 | 138240 | 0 | 1223863 | 0 | 0 | 56597 | 505440 | 199080 | 747400 | 433510 | 2261760 | 2576600 | 537600 | 446112 | 13150 | 718000 | 723360 | 1083600 | 1180872 | 250470 | 3650000 | 1399968 | 1809600 | 0 | 0 | 0 | 0 | 0 | 68500 | 0 | 207504 | 0 | 1098981 | 0 | 0 | 196800 | 0 | 694080 | 126630 | 1500480 | 0 | 732654 | 7901000 | 2089200 | 1718820 | 0 | 25439 | 1435200 | 1102456 | 0 | 0 | 900480 | 2139840 | 1090200 | 1838400 | 308130 | 551520 |  | 16679272 | 0 | 8301600 | 0 | 211200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 494900 | 96672 | 0 | 820000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42240 | 0 | 477360 | 0 | 225594 | 0 | 0 | 3681700 | 0 | 0 | 0 | 0 | 4178836 | 0 | 1247236 | 0 | 4321245 | 0 | 8943236 | 925440 | 0 | 134208 | 0 | 697920 | 0 | 32302 | 854016 | 11603400 | 802910 | 0 |  | 117963042 | 64771287 | 182734329 | 78271191 | 16679272 | 34674344 | 31014785 | 15285100 | 3775976 | 266250 | 2261760 | 505651 | 0
Fuel Cost | 0 | 0 | 5959720 | 4074840 | 5257061.01 | 398819.52 | 0 | 0 | 7700280 |  | 0 | 9067710 | 6640399.62 | 3686918.4 | 2714384.4 | 2986650.72 | 0 | 0 | 1034540 | 2689113.6 | 8324881.92 | 118080 | 0 | 0 | 0 | 33160.32 | 8472672 | 3166957.81 | 263755 | 279639 | 450000 | 0 | 0 | 0 | 4859523.12 | 0 | 561593.52 | 457920 | 5249000 | 0 | 0 | 5349862.79 | 0 | 0 | 0 |  | 0 | 0 | 2466225 | 0 | 726624 | 6242227.2 | 596816.64 | 1301572.8 | 4082127.12 | 0 | 0 | 5554070 | 0 | 4193360 | 539453.49 | 1606653.5 | 703764 | 193536 | 0 | 2092805.73 | 0 | 0 | 540501.35 | 641908.8 | 149310 | 1307950 | 325132.5 | 16963200 | 2731196 | 4881408 | 566562.24 | 209611 | 1177520 | 1157376 | 1928808 | 1842160.32 | 285535.8 | 3796000 | 2757936.96 | 3456336 | 0 | 0 | 0 | 0 | 0 | 69185 | 0 | 157703.04 | 0 | 8308296.36 | 0 | 0 | 1023360 | 0 | 6829747.2 | 1480304.7 | 12228912 | 0 | 5165210.7 | 7347930 | 19053504 | 16242849 | 0 | 0 | 10850112 | 9602391.76 | 0 | 0 | 7717113.6 | 14251334.4 | 0 | 0 | 0 | 0 |  | 96072606.72 | 0 | 8716680 | 0 | 1660032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 767095 | 943518.72 | 0 | 1681000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409305.6 | 0 | 916531.2 | 0 | 170774.658 | 0 | 0 | 19954814 | 0 | 0 | 0 | 0 | 5516063.52 | 0 | 1870854 | 0 | 5055856.65 | 0 | 8853803.64 | 9661593.6 | 0 | 1273633.92 | 0 | 5415859.2 | 0 | 356937.1 | 6311178.24 | 50938926 | 0 | 0 |  | 285143124.96 | 226547063.768 | 511690188.728 | 87648354.428 | 96072606.72 | 41284486.5 | 193177129.76 | 70893740 | 1019513.52 | 2584305 | 16963200 | 2046852.8 | 0
Yesterday Day Peak | 0 | 0 | 170 | 115 | 200 | 12 | 0 | 0 | 284 |  | 0 | 360 | 270 | 50 | 15 | 30 | 0 | 0 | 0 | 4 | 64 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 0 | 19 | 25 | 16 | 17 | 25 | 51 | 0 | 88 | 70 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 3 | 135 | 0 | 0 | 345 | 0 | 191 | 26 | 75 | 27 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 15 | 92 | 107 | 16 | 20 | 2 | 30 | 50 | 47 | 46 | 107 | 159 | 40 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 30 | 0 | 0 | 0 | 0 | 86 | 19 | 60 | 0 | 10 | 252 | 115 | 90 | 0 | 4 | 53 | 54 | 0 | 0 | 36 | 100 | 45 | 90 | 49 | 55 |  | 738 | 0 | 350 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 157 | 0 | 23 | 0 | 159 | 0 | 388 | 53 | 0 | 0 | 0 | 19 | 0 | 5 | 35 | 460 | 22 | 0 |  | 7952 | DayPeak
Yesterday Evening Peak | 0 | 0 | 170 | 115 | 200 | 12 | 0 | 0 | 324 | 0 | 0 | 370 | 290 | 78 | 78 | 55 | 0 | 0 | 0 | 80 | 94 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 22 | 17 | 25 | 16 | 0 | 88 | 70 | 120 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 12 | 50 | 20 | 16 | 135 | 0 | 0 | 290 | 0 | 181 | 26 | 70 | 29 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 8 | 33 | 21 | 116 | 110 | 25 | 20 | 0 | 30 | 65 | 53 | 49 | 107 | 159 | 67 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 180 | 0 | 0 | 50 | 0 | 0 | 0 | 100 | 0 | 113 | 401 | 115 | 105 | 0 | 0 | 157 | 54 | 0 | 0 | 113 | 100 | 45 | 90 | 0 | 0 |  | 881 | 0 | 345 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 16 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 193 | 0 | 95 | 0 | 187 | 0 | 386 | 90 | 0 | 0 | 0 | 113 | 0 | 0 | 110 | 520 | 36 | 0 |  | 9429 | EvPeak
Forecast for Evening | 0 | 0 | 150 | 115 | 200 | 50 | 0 | 0 | 360 | 0 | 0 | 450 | 305 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 100 | 0 | 0 | 50 | 54 | 55 | 55 | 19 | 25 | 33 | 17 | 25 | 52 | 0 | 90 | 70 | 120 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 0 |  | 102 | 100 | 100 | 50 | 20 | 20 | 100 | 0 | 0 | 360 | 0 | 225 | 8 | 90 | 30 | 5 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 172 | 160 | 25 | 22 | 0 | 30 | 60 | 51 | 44 | 110 | 160 | 66 | 86 | 0 | 0 | 0 | 0 | 0 | 320 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 180 | 150 | 400 | 115 | 90 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 45 | 90 | 0 |  |  | 889 | 16 | 410 | 0 | 115 | 220 | 0 | 0 | 30 | 60 | 40 | 0 | 30 | 110 | 0 | 70 | 0 | 50 | 40 | 100 | 0 | 0 | 50 | 52 | 33 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 | 0 | 95 | 100 | 220 | 0 | 413 | 90 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 660 | 35
Forecast for Day | 0 | 0 | 150 | 115 | 200 | 50 | 0 | 0 | 360 | 0 | 0 | 450 | 305 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 50 | 0 | 0 | 50 | 54 | 55 | 55 | 19 | 25 | 33 | 17 | 25 | 52 | 0 | 90 | 70 | 120 | 0 | 25 | 215 | 0 | 0 | 0 | 0 | 0 |  | 102 | 100 | 100 | 50 | 20 | 10 | 100 | 0 | 0 | 360 | 0 | 225 | 8 | 90 | 30 | 5 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 156 | 160 | 25 | 22 | 1.6 | 30 | 60 | 51 | 44 | 110 | 160 | 66 | 86 | 0 | 0 | 0 | 0 | 0 | 320 | 25 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 165 | 150 | 400 | 115 | 90 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 45 | 90 | 50 |  |  | 744 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 30 | 110 | 0 | 70 | 0 | 0 | 0 | 100 | 0 | 0 | 50 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 |  | 95 | 0 | 220 | 0 | 413 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 600 | 35
Generation at 08:00(Today) | 0 | 0 | 120 | 115 | 200 | 50 | 0 | 0 | 330 | 0 | 0 | 380 | 335 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 18 | 17 |  | 0 | 0 | 87 | 70 | 115 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 100 | 0 | 0 | 290 | 0 | 177 | 8 | 75 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 0 | 33 | 18 | 76 | 165 | 3 | 20 | 1 | 30 | 60 | 49 | 23 | 107 | 158 | 68 | 50 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 11 | 17 | 0 | 1 | 0 | 19 | 0 | 0 | 0 | 70 | 45 | 0 | 14 | 0 | 0 | 497 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 167 | 0 | 12 | 0 | 179 | 0 | 426 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 400 | 33 | 0 | 0
199
| Minimum Generation |  | 6346 | 5:00
| Highest Generation |  | 9429 | 19:00
| Day Peak Generation |  | 7952 | 12:00
| Evening Peak Generation |  | 9429 | 19:00
| HVDC Max Flow |  | 882 | 20:00
| HVDC EvPeak Flow |  | 881 | 19:00
| Load factor L.F |  | 80.75%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-11-19
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-11-18 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7952 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6301 | MW
Evening Peak Generation : |  | 9429 | MW Hour : | 19:00 | Available Max Generation : |  | 14422 | MW
E.P. Demand (at gen end) : |  | 9429 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9800 | MW
Maximum Generation : |  | 9429 | MW Hour : | 19:00 | Reserve(Generation end) |  | 4622 | MW
Total Gen. (MKWH) : |  | 182.7343 | System Load Factor : | 80.75% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 236 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-11-19
Actual : | 102.61 | Ft.(MSL) , | Rule curve : | 107.2 | Ft.( MSL )
Gas Consumed : | Total = | 1012.43 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 128932840.928
: |  | Coal : | 70893740 | Oil : | 195761434.76 | Total : | 395588015.688
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3415.3541 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1157.5481 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1036.4367 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 936.2637 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 846.2227 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 682.862 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 386.7917 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 175.9501 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 526.6333 |  |  | 0 | 0%
Total | 0 |  | 9164.0624 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 10) Sirajganj #1 CCPP STG
|  |  |  | 2) Baghabari-71 MW | 11)Ashuganj(S)-360 MW
3) Ghorasal Unit-1,2,3
4) Ashuganj unit-4,5
5) Kaptai-2
6) Raozan #2
7) Siddirganj-335 MW
8) Haripur 412 MW
9) Chandpur-163 MW STG
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Sikalbaha-Dohazari 132 kV Ckt-2 was under shut down from 09:24 to 14:46 for A/M.
b) Hathazari-Baroirhat 132 kV Ckt-2 was under shut down from 08:47 to 16:01 for A/M.
c) Tongi-Kabirpur 132 kV Ckt-1 was under shut down from 08:46 to 15:49 for A/M.
d) Savar 33 kV Bus-B was under shut down from 10:58 to 16:09 for DS maintenance work.
e) Daudkandi 132/33 kV T-2 transformer was under shut down from 08:05 to 17:23 for A/M.
f) Kodda-Joydebpur 132 kV Ckt-2 was under shut down from 10:01 to 17:11 for A/M.
g) Kodda 132/33 kV MTR1 transformer was under shut down from 10:15 to 12:24 for D/W.
h) Kodda-Rajendrapur 132 kV Ckt-1 was under shut down from 12:33 to 16:54 for D/W.
i) Kishoreganj-Mymensingh 132 kV Ckt-1 was under shut down from 08:24 to 16:23 for A/M.
j) Aminbazar-Hasnabad 230 kV Ckt-1 was under shut down from 10:56 to 16:50 for A/M.
k) Hasnabad-APR 230 kV Ckt was shut down at 11:35 for maintenance work at Hasnabad end.
l) Mirpur 132/33 kV T-1 transformer was under shut down from 08:40 to 13:10 for A/M.
m) Khulna(S)-HVDC 230 kV Ckt-2 and its Bay were under shut down from 08:15 to 16:30 for A/M.
n) B.Pukuria-Rangpur 132 kV Ckt-1 was under shut down from 08:18 to 16:26 for A/M.
o) Purbasadipur 132/33 kV T-1 transformer was under shut down from 08:29 to 16:30 for A/M.
p) Sirajganj-Bogura 230 kV Ckt-2 was shut down at 08:13 for A/M.
q) Gopalganj 132/33 kV T-6 transformer was under shut down from 08:01 to 09:42 for A/M.
r) Noapara 132/33 kV T-4 transformer was under shut down from 08:46 to 14:06 for A/M.
s) Shariatpur 132/33 kV Bus coupler was under shut down from 08:45 to 15:14:59 for A/M.
t) Bibiyana Summit-2 341 MW GT was force shut down at 09:47 due to problem at ST side and GT was again
synchronized at 22:39 and ST was synchronized at 00:41(19/11/2020).
u) Sylhet-Fenchuganj 90 MW P/S 132 kV Ckt was under shut down from 12:30 to 13:47 for D.C. supply
checking at Sylhet S/S end.
v) Sylhet-Fenchuganj S/S 132 kV Ckt tripped at 14:46 showing SOTF at Sylhet end and was switched on at 14:57.
w) Sylhet-Fenchuganj S/S 132 kV Ckt tripped again at 16:02 showing SOTF at Sylhet end and was switched
on at 16:59 and Again tripped at 18:28 showing SOTF at Sylhet end.
x) Madunaghat-TK Chemical 132 kV Ckt was under shut down from 16:26 to 17:11 for oil leakage of PT,
Y-phase at Madunaghat end.
y) Sylhet 132/33 kV T-1 transformer was switched on at 17:05 and loaded.
z) Rangpur-Kurigram 132 kV Ckt tripped at 04:42(19/11/2020) from Rangpur end showing Dist. R,Z1 and |  |  |  |  | About 10 MW power interruption occurred under Kurigram S/S area
switched on at 04:05 as trial basis. At the time PT got burst at R-phase,Rangpur end. |  |  |  |  | from 04:42(19/11/2020) to till now.
aa) Polashbari-Rangpur Confidence 132 kV Ckts 1 & 2 tripped at 04:05(19/11/2020) from Polashbari end
showing Dist.Z3, 3-phase and was switched on at 04:29.
ab) Rangpur-Saidpur 132 kV Ckt-2 tripped at 04:05(19/11/2020) from Saidpur end showing Z3,3-phase |  |  |  |  | About 70 MW power interruption occurred under Saidpur S/S area
and was switched on at 04:45. |  |  |  |  | from 04:05(19/11/2020) to 04:23.
ac) Rangpur-Saidpur 132 kV Ckt-1 tripped at 04:05(19/11/2020) from Rangpur end showing Dist. A-phase
and was switched on at 04:23.
ad) Rangpur-Barapukuria 132 kV Ckts 1 & 2 tripped at 04:05(19/11/2020) from Barapukuria end showing
Dist. Z1,Z2 at Ckt-1 and was switched on at 04:31.
ae) Kabirpur-Manikganj 132 kV Ckt-2 was shut down at 06:49(19/11/2020) for C/M.
af) Meghnaghat 230 kV Bus-1 was shut down at 07:31(19/11/2020) for A/M.
m) Joypurhat 132/33 kV T-1 transformer was under shut down from 08:52 to 14:16 for A/M.
n) Barishal 230/132 kV T-1 transformer was under shut down from 08:32 to 17:00 for A/M.
o) Benapole 132/33 kV T-1 transformer was under shut down from 07:47 to 15:30 for A/M.
p) Khulna(S) 230/132 kV T-1 transformer was under shut down from 08:27 to 14:07 for A/M.
q) Satkhira 132/33 kV T-1 transformer was under shut down from 08:55 to 16:21 for A/M.\r)
r) Ishurdi-Pabna 132 kV Ckt was under shut down from 08:21 to 16:44 for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-11-18 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 170 | 4082000 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 115 | 2772000 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 4736091 | Machin problem.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 12 | 302136 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 324 | 7476000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 370 | 8319000 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 78 | 485760 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 290 | 5982342 | Engine problem
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 78 | 393960 | High voltage
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 353032 | High voltage
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 372852 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 598000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 80 | 357120 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under Maintenance
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 94 | 912816 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 3648 | Reserve.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1160640
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 12000 | Reserve.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 409697
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 26750 | Reserve.
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 47 | 1138020 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 17 | 411900 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 591500 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 16 | 502536 | Low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 180 | 1098981 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 694080 | Reserve.
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 1718820
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 1838400 | Engine problem
| Manikgonj 162MW PP |  | IPP | 9*18 | 0 | 0 | 551520
| Dhaka area Total |  |  |  | 5895 | 2474 | 47301601
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2900000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve.
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 126630
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 788160
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 158 | 3775976 | Unit-2 under maint
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4908131
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 254250 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1500480
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 473664
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 16 | 438240
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 12 | 83520 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 25439
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 157 | 1435200 | Transformer O/L
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1102456
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2139840
| Chattogram area Total |  |  |  | 2266 | 1041 | 19951986
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 135 | 2758194
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas Shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 181 | 4558000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 290 | 7505500 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 622800 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 138240 | Gas shortage
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 26 | 418181 | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1223863
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 113 | 732654 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1397090 | ST Under maint
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve.
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 505440
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 199080 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 116 | 2261760
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 747400
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 56597 | Low demand
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 433510
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 900480
| Cumilla Area Total |  |  |  | 2980 | 1220 | 24458789
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 110 | 2576600 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 446112
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 25 | 537600 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13150
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 50 | 196800
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2089200 | #REF!
| Mymensingh PV 50 MW Solar PP |  | IPP | 50 | 0 | 0 | 308130
| Mymensingh Area Total |  |  |  | 637 | 320 | 6167592
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 718000 | GT-2 under maint.
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 65 | 723360 | Engine problem
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 107 | 250470 | ST Under maint
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 159 | 3650000 | GT-2 under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1083600
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 49 | 1180872
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 207504
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 67 | 1399968 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1809600
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 0 | 0 | Engine problem
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 68500 | Under maint.
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 401 | 7901000
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 0
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 45 | 1090200 | On test
| Sylhet Area Total |  |  |  | 1988 | 1073 | 20083074
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 881 | 16679272
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 49 | 211200 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 345 | 8301600 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Reserve.
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 90 | 925440 | Engine problem
107 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1365 | 26117512
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 96672 | Low demand
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 27 | 494900 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 95 | 1247236
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 520 | 11603400
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 36 | 802910
| Barisal Area Total |  |  |  | 1054 | 694 | 14245118
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 70 | 820000 | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel Shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel Shortage
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Under rmaint.
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 193 | 4178836 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 187 | 4321245 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 386 | 8943236 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 477360
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Engine problem
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 225594
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 42240 | Reserve.
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve.
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 134208 | Reserve.
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 110 | 854016
| Rajshahi Area Total |  |  |  | 2183 | 979 | 19996735
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3681700 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 697920
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 32302
| Rangpur Area Total |  |  |  | 605 | 263 | 4411922
| Total |  |  |  | 19892 | 9429 | 182734329
| Eastern Grid Total |  |  |  | 13766 | 6128 | 117963042
| Western Grid Total |  |  |  | 6126 | 3301 | 64771287
| National Grid Total |  |  |  | 19892 | 9429 | 182734329
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-11-18
| (a) ENTIRE EASTERN GRID : |  | 6094 | MW | (b) ENTIRE WESTERN GRID : |  | 2708 | MW
| i) Dhaka area |  | 3368 | MW | i) Khulna area |  | 1056 | MW
| ii) Chittagong area |  | 991 | MW | ii) Rajshahi area |  | 850 | MW
| iii) Comilla area |  | 770 | MW | iii) Barisal area |  | 244 | MW
| iv) Mymensingh area |  | 668 | MW | iv) Rangpur area |  | 558 | MW
| v) Sylhet area |  | 297 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8802 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 114 | 18:00 | Sherpur | 8 | 19:00 | Jhenida | 78 | 18:00
| Munsiganj | 86 | 20:00 | Srimongal | 27 | 18:00 | Bottail | 96 | 18:00
| Sonargaon | 48 | 18:30 | Shahjibazar | 80 | 20:00 | G.K Project | 35 | 18:00
| Shyampur | 174 | 1:00 | Fenchuganj | 38 | 18:00 | Faridpur | 134 | 0.75
| Bhulta | 152 | 2:00 | Kulawara | 30 | 18:00 | Madaripur | 60 | 0.83333
| Madanganj | 48 | 12:00 | Sylhet | 43 | 19:00 | Sariatpur | 42 | 20:00
| Shitalakhya | 100 | 16:00 | Chatak | 21 | 18:00 | Gopalganj | 61 | 18:00
| Rahim steel | 17 | 7:00 | Sunamganj | 29 | 18:30 | Bagerhat | 80 | 18:00
| Matuail | 66 | 15:00 | Biani Bazar | 50 | 18:00 | Mongla | 38 | 10:00
| Ghorasal | 62 | 18:00 | Comilla (S) | 120 | 18:00 | Satkhira | 74 | 0.83333
| Narsingdi | 120 | 21:00 | Comilla(N) | 75 | 18:00 | Gallamari | 23 | 18:00
| Haripur (SBU) | 100 | 18:30 | Chandpur | 71 | 18:30 | Magura | 38 | 0.75
| Ullon | 60 | 18:00 | Feni | 85 | 18:00 | Norail | 24 | 18:00
| Hasnabad | 156 | 18:30 | Chowmuhani | 124 | 18:30 | Chuadanga | 64 | 18:00
| Magbazar | 80 | 12:00 | Ashuganj | 37 | 18:00 | Barisal(N) | 28 | 0.79167
| Maniknagar | 82 | 18:00 | Daudkandi | 92 | 18:00 | Barisal (S) | 74 | 0.75
| Bangabhaban | 26 | 10:00 | B.Baria | 105 | 19:00 | Patuakhali | 81 | 0.875
| Narinda | 80 | 16:00 | Ramganj | 64 | 18:00 | Bhandaria | 40 | 0.75
| Dhanmondi | 125 | 13:00 | Chaddagram | 24 | 20:00 | Borhan Uddin | 28 | 21:00
| Lalbag | 79 | 13:00 | PHP | 4 | 13:00 | Ishurdi | 47 | 18:00
| Madartek | 56 | 18:00 | Madunaghat | 45 | 18:30 | Ruppur Paromanobik | 2 | 1:00
| Dhaka University |  |  | Hathazari | 81 | 0.77083 | Natore | 83 | 18:00
| Fatullah | 38 | 0.5 | Khulshi | 194 | 0.75 | Bogra | 116 | 18:30
| Mirpur | 91 | 18:00 | Halishahar | 128 | 0.625 | Noagaon | 87 | 18:30
| Kalyanpur | 72 | 18:00 | Baraulia | 136 | 0.375 | Rajshahi | 95 | 19:30
| Gulshan | 94 | 19:00 | Sikalbaha | 23 | 0.75 | Rajshahi New | 11 | 18:30
| Uttara | 76 | 18:00 | Dohazari | 58 | 0.75 | C.Nawabganj | 50 | 19:00
| Uttara New | 27 | 18:00 | Cox'sbazar | 78 | 0.77083 | Amnura | 28 | 18:00
| Kamrangirchar | 83 | 18:00 | Chandraghona | 20 | 0.75 | Pabna | 85 | 18:00
| Savar | 102 | 18:00 | Kaptai | 3.8 | 0.75 | Shahjadpur | 75 | 18:00
| Bhasantec | 128 | 18:00 | A. Khaer Stl. | 0 | 0.041667 | Serajganj | 66 | 19:30
| Agargaon | 57 | 13:00 | Bakulia | 89 | 0.75 | Niyamatpur | 45 | 18:00
| Satmosjid | 79 | 13:00 | Julda | 20 | 0.083333 | Joypurhat | 36 | 18:00
| Tongi | 89 | 0.54167 | TK chemical | 20.9 | 0.77083 | Sherpur(Bogura) | 38 | 18:00
| Kabirpur | 199 | 12:00 | Modern Steel | 15 | 0.083333 | Mohastangor | 32 | 18:30
| Basundhara | 97 | 18:00 | Shahmirpur | 18 | 0.75 | Rangpur | 103 | 18:00
| Manikganj | 52 | 21:00 | Khagrachhari | 22 | 0.83333 | Lalmonirhat | 41 | 18:30
| Joydevpur | 113 | 18:00 | Matarbari | 29.5 | 0.75 | Saidpur | 84 | 18:00
| New Tongi | 86 | 12:00 | Baroiar Hat | 20 | 0.75 | Purbasadipur | 83 | 18:00
| Kodda | 191 | 18:30 | Rangamati | 10 | 0.77083 | Thakurgaon | 58 | 18:00
| Dhamrai | 72 | 18:00 | Abul Khair 230 | 159 | 0.20833 | Palashbari | 88 | 18:00
| Rajendrapur | 78 | 18:00 | BSRM | 106 | 0.54167 | Barapukuria | 35 | 18:30
| Valuka | 80 | 18:00 | GPH Ispat | 79 | 0.375 | Panchagar | 42 | 18:00
| Tangail | 131 | 18:00 | Goalpara | 22 | 0.375 | Joldhaka | 20 | 18:00
| Mymensing | 151 | 18:30 | Central s/s | 81 | 18:00 | Kurigram | 39 | 18:30
| Kishorganj | 82 | 19:00 | Noapara | 50 | 18:30
| Netrokona | 78 | 19:00 | Jessore | 79 | 18:00
| Jamalpur | 88 | 19:30 | Benapol | 36 | 18:00
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-11-18 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 401 | 20:00 | 394 | 16:00 | Kaliakoir | 384 | 0.20833 | 375 | 0.66667
| Bheramara | 407 | 8:00 | 395 | 21:00 | Bhulta | 385 | 0.8125 | 371 | 0.66667
| Ashuganj(N) | 389 | 7:00 | 378 | 16:00 | Gopalganj | 411 | 0.083333 | 400 | 0.875
| Payra | 417 | 20:00 | 410 | 20:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 230 | 1:00 | Comilla (N) | 236 | 20:00 | 230 | 4:00
| Ishurdi | 235 | 1:00 | 227 | 12:00 | Hathazari | 228 | 20:00 | 221 | 13:00
| Ashuganj | 236 | 18:00 | 230 | 16:00 | Megnaghat | 231 | 6:00 | 220 | 14:00
| Serajganj | 231 | 1:00 | 228 | 9:00 | Fenchuganj | 241 | 18:00 | 237 | 17:00
| Baghabari | 243 | 2:00 | 237 | 12:00 | Siddhirganj | 229 | 20:00 | 223 | 16:00
| Barapukuria | 231 | 3:00 | 226 | 12:00 | Maniknagar | 228 | 20:00 | 222 | 12:00
| Bogra | 229 | 1:00 | 219 | 9:00 | Agargaon | 226 | 2:00 | 217 | 16:00
| Rajshahi | 226 | 3:00 | 218 | 12:00 | Barisal | 249 | 20:00 | 241 | 12:00
| Khulna South | 245 | 1:00 | 203 | 4:00 | AKSML | 226 | 18:30 | 216 | 5:00
| Rampura | 228 | 5:00 | 221 | 16:00 | BSRM | 226 | 19:00 | 218 | 3:00
| Haripur | 227 | 20:00 | 222 | 17:00 | Bibiyana | 240 | 18:30 | 235 | 16:00
| Hasnabad | 224 | 10:00 | 215 | 16:00 | Bhulta | 230 | 19:00 | 224 | 17:00
| Shyampur | 227 | 20:00 | 220 | 16:00 | Ashuganj (S) | 234 | 20:00 | 227 | 12:00
| Aminbazar | 226 | 8:00 | 220 | 12:00 | Kaliakoir | 230 | 18:00 | 222 | 16:00
| Tongi | 227 | 7:00 | 220 | 15:00 | GPH | 224 | 18:00 | 219 | 2:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 137 | 18:00 | 133 | 13:00 | Hathazari | 136 | 0.83333 | 131 | 0.125
| Munsiganj | 139 | 23:00 | 133 | 3:00 | Khulshi | 134 | 0.77083 | 128 | 0.5
| Sonargaon | 135 | 19:30 | 131 | 13:00 | Halishahar | 136 | 0.91667 | 130 | 0.16667
| Shyampur | 137 | 18:00 | 133 | 12:00 | Baraulia | 134 | 0.77083 | 129 | 0.20833
| Bhulta | 130 | 5:00 | 127 | 10:00 | Sikalbaha | 136 | 0.75 | 129 | 0.20833
| Madanganj | 137 | 21:00 | 129 | 5:00 | Dohazari | 134 | 0.77083 | 126 | 0.5
| Shitalakhya | 142 | 18:00 | 132 | 15:00 | Cox'sbazar | 128 | 0.91667 | 121 | 0.41667
| Rahim steal | 137 | 19:00 | 133 | 12:00 | Chandraghona | 136 | 0.83333 | 131 | 0.20833
| Matuail | 137 | 18:00 | 133 | 13:00 | Kaptai | 135 | 0.875 | 132 | 0.45833
| Ghorasal | 137 | 1:00 | 135 | 13:00 | A. Khaer Stl. | 135 | 0.8125 | 129 | 0.125
| Narsinghdi | 134 | 18:00 | 130 | 12:00 | Bakulia | 135 | 0.83333 | 130 | 0.375
| Haripur (SBU) | 138 | 18:00 | 132 | 16:00 | Julda | 136 | 0.77083 | 132 | 0.66667
| Ullon | 134 | 7:00 | 130 | 11:00 | TK Chemical | 136 | 0.875 | 130 | 0.20833
| Hasnabad | 137 | 19:30 | 132 | 1:00 | Modern Steel | 135 | 0.79167 | 129 | 0.083333
| Magbazar | 134 | 3:00 | 130 | 11:00 | Shahmirpur | 136 | 0.8125 | 129 | 0.16667
| Maniknagar | 135 | 2:00 | 132 | 12:00 | Khagrachhari | 135 | 0.83333 | 131 | 0.20833
| Bangabhaban | 135 | 2:00 | 132 | 12:00 | Matarbari | 131 | 0.91667 | 123 | 0.5
| Narinda | 135 | 2:00 | 132 | 12:00 | Baroiar Hat | 136 | 0.83333 | 130 | 0.66667
| Dhanmondi | 134 | 7:00 | 130 | 11:00 | Rangamati | 136 | 0.91667 | 132 | 0.16667
| Lalbag | 134 | 24:00 | 130 | 16:00 | Goalpara S/S | 135 | 3:00 | 125 | 16:00
| Madartek | 134 | 6:00 | 129 | 12:00 | Khulna Central S/S | 135 | 4:00 | 125 | 0.54167
| Dhaka University |  |  |  |  | Noapara | 134 | 4:00 | 125 | 0.625
| Fatuiiah | 138 | 20:00 | 133 | 17:00 | Jessore | 130 | 1:00 | 125 | 0.66667
| Mirpur | 137 | 19:30 | 132 | 16:00 | Benapol | 133 | 0.083333 | 124 | 0.66667
| Kalyanpur | 138 | 10:00 | 133 | 17:00 | Jhenida | 133 | 3:00 | 124 | 0.75
| Gulshan | 133 | 6:00 | 129 | 16:00 | Bottail | 136 | 0.20833 | 130 | 0.54167
| Uttara | 136 | 8:00 | 130 | 17:00 | G.K Project | 139 | 0.125 | 135 | 0.54167
| Uttara New | 136 | 20:00 | 130 | 16:00 | Faridpur | 136 | 0.16667 | 132 | 0.33333
| Kamrangirchar | 134 | 18:00 | 126 | 16:00 | Madaripur | 138 | 0.41667 | 132 | 0.875
| Savar | 138 | 10:00 | 131 | 17:00 | Shariyatpur S/S | 138 | 2:00 | 133 | 0.83333
| Bhasantec | 137 | 8:00 | 131 | 16:00 | Gopalganj | 140 | 0.25 | 133 | 0.875
| Agargaon | 138 | 8:00 | 132 | 16:00 | Bagerhat | 135 | 9:00 | 121 | 0.66667
| Satmosjid | 137 | 6:00 | 132 | 16:00 | Mongla | 131 | 2:00 | 121 | 0.66667
| Tongi | 138 | 9:00 | 134 | 15:00 | Satkhira | 135 | 6:00 | 125 | 15:00
| Kabirpur | 131 | 1:00 | 125 | 15:00 | Gallamari | 136 | 0.375 | 125 | 0.66667
| Basundhara | 134 | 6:00 | 129 | 11:00 | Magura | 132 | 4:00 | 122 | 0.54167
| Manikganj | 141 | 9:00 | 133 | 23:00 | Norail | 133 | 0.083333 | 122 | 0.54167
| Joydevpur | 139 | 19:00 | 134 | 15:00 | Chuadanga | 131 | 2:00 | 120 | 0.54167
| New Tongi | 137 | 18:00 | 132 | 16:00 | Barisal(N) | 141 | 1:00 | 136 | 11:00
| Kodda | 140 | 10:00 | 128 | 1:00 | Barisal (S) | 140 | 0.20833 | 133 | 0.83333
| Dhamrai | 129 | 24:00 | 125 | 15:00 | Patuakhali(S) | 137 | 0.16667 | 130 | 0.875
| Rajendrapur | 138 | 10:00 | 126 | 22:00 | Bhandaria | 139 | 0.083333 | 130 | 0.875
| Valuka | 127 | 1:00 | 125 | 18:30 | Ishurdi | 138 | 2:00 | 132 | 18:30
| Tangail | 132 | 4:00 | 127 | 17:00 | Ruppur Paromanobik | 136 | 1:00 | 134 | 12:00
| Mymensing | 130 | 8:00 | 121 | 13:00 | Natore | 137 | 1:00 | 132 | 8:00
| Kishorganj | 131 | 8:00 | 126 | 21:00 | Bogra | 138 | 3:00 | 131 | 9:00
| Netrokona | 129 | 9:00 | 122 | 22:00 | Noagaon | 134 | 5:00 | 126 | 13:00
| Jamalpur | 135 | 9:00 | 124 | 6:00 | Rajshahi | 138 | 1:00 | 132 | 13:00
| Sherpur | 134 | 20:00 | 123 | 4:00 | Rajshahi New | 139 | 2:00 | 133 | 13:00
| Srimongal | 140 | 9:00 | 137 | 1:00 | C.Nawabganj | 139 | 4:00 | 132 | 9:00
| Shahjibazar | 139 | 8:00 | 134 | 17:00 | Amnura | 136 | 1:00 | 132 | 12:00
| Fenchuganj | 138 | 1:00 | 136 | 7:00 | Pabna | 138 | 4:00 | 132 | 12:00
| Khulawara | 137 | 7:00 | 135 | 4:00 | Shahjadpur | 140 | 1:00 | 135 | 8:00
| Sylhet | 133 | 18:30 | 133 | 19:00 | Serajganj | 135 | 1:00 | 130 | 9:00
| Chatak | 135 | 8:00 | 129 | 19:00 | Niyamatpur | 133 | 5:00 | 125 | 12:00
| Sunamganj | 135 | 3:00 | 129 | 19:00 | Joypurhat | 136 | 3:00 | 127 | 13:00
| Biani Bazar | 135 | 7:00 | 132 | 12:00 | Sherpur(Bogura) | 138 | 5:00 | 131 | 9:00
| Comilla(s) | 130 | 7:00 | 123 | 18:00 | Mohastangor | 136 | 3:00 | 129 | 9:00
| Comilla(n) | 140 | 20:00 | 135 | 16:00 | Rangpur | 128 | 4:00 | 121 | 9:00
| Chandpur | 136 | 19:00 | 132 | 11:00 | Lalmonirhat | 129 | 4:00 | 122 | 8:00
| Feni | 137 | 20:00 | 132 | 15:00 | Saidpur | 128 | 3:00 | 121 | 8:00
| Chowmuhani | 134 | 18:00 | 127 | 23:00 | Purbasadipur | 127 | 3:00 | 119 | 12:00
| Ashuganj | 135 | 19:00 | 134 | 23:00 | Thakurgaon | 126 | 4:00 | 118 | 18:00
| Daudkandi | 137 | 18:00 | 132 | 13:00 | Palashbari | 132 | 4:00 | 125 | 9:00
| B.Baria | 133 | 7:00 | 130 | 21:00 | Barapukuria | 131 | 3:00 | 126 | 12:00
| Ramganj | 131 | 18:30 | 128 | 21:00 | Panchagar | 126 | 4:00 | 115 | 18:00
| Chaddagram | 137 | 19:30 | 132 | 23:00 | Joldhaka | 127 | 5:00 | 120 | 9:00
| PHP | 135 | 20:00 | 130 | 15:00 | Kurigram | 128 | 5:00 | 121 | 8:00
| Madanhat | 138 | 20:00 | 132 | 5:00

## L-Curve
Date | 2020-11-18
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 650 | 4721 | 2792 | 7513 |  |  |  | QF-LDC-11
0:30 | 515 | 4780.5 | 2591 | 7371.5 | Date: | 2020-11-18
1:00 | 380 | 4840 | 2390 | 7230
1:30 | 392.5 | 4723.5 | 2357 | 7080.5
2:00 | 405 | 4607 | 2324 | 6931
2:30 | 440.5 | 4462.5 | 2324 | 6786.5 | [5 empty] | Gen. at Eve. Peak | 9429 | 9500 MW (19:30 )
3:00 | 476 | 4318 | 2324 | 6642 | [6 empty] | 19:00
3:30 | 504 | 4265 | 2271.5 | 6536.5 | [5 empty] | Gen. at Day Peak | 7952 | 7952.5 MW (12:00 )
4:00 | 532 | 4212 | 2219 | 6431 | [6 empty] | 12:00
4:30 | 530 | 4157.5 | 2231 | 6388.5 | [5 empty] | Highest Generation | 9429
5:00 | 528 | 4103 | 2243 | 6346 | [6 empty] | 19:00
5:30 | 519 | 4160.5 | 2272.5 | 6433
6:00 | 510 | 4218 | 2302 | 6520
6:30 | 449 | 4251.5 | 2311.5 | 6563
7:00 | 388 | 4285 | 2321 | 6606
7:30 | 312 | 4444 | 2343.5 | 6787.5
8:00 | 236 | 4603 | 2366 | 6969
8:30 | 345.5 | 4690 | 2382.5 | 7072.5
9:00 | 455 | 4777 | 2399 | 7176
9:30 | 457 | 4920.5 | 2379.5 | 7300
10:00 | 459 | 5064 | 2360 | 7424
10:30 | 458.5 | 5063.5 | 2453 | 7516.5
11:00 | 458 | 5063 | 2546 | 7609
11:30 | 534 | 5160 | 2620.5 | 7780.5
12:00 | 610 | 5257 | 2695 | 7952
12:30 | 607 | 5271.5 | 2739 | 8010.5
13:00 | 604 | 5286 | 2783 | 8069
13:30 | 614 | 5229 | 2716.5 | 7945.5
14:00 | 624 | 5172 | 2650 | 7822
14:30 | 637.5 | 5187.5 | 2600.5 | 7788
15:00 | 651 | 5203 | 2551 | 7754
15:30 | 667.5 | 5124 | 2569 | 7693
16:00 | 684 | 5045 | 2587 | 7632
16:30 | 687.5 | 5056 | 2653.5 | 7709.5
17:00 | 691 | 5067 | 2720 | 7787
17:30 | 541 | 5518 | 3021 | 8539
18:00 | 391 | 5969 | 3322 | 9291
18:30 | 369.5 | 6048.5 | 3311.5 | 9360
19:00 | 348 | 6128 | 3301 | 9429
19:30 | 356 | 6022 | 3267 | 9289
20:00 | 336 | 5981 | 3246 | 9227 |  |  |  | Executive Engineer
20:30 | 401 | 5842.5 | 3244 | 9086.5 |  |  |  | Network Operation Division
21:00 | 466 | 5704 | 3242 | 8946
21:30 | 488 | 5523.5 | 3170.5 | 8694
22:00 | 510 | 5343 | 3099 | 8442 |  |  |  |  | Page 6 of 7
22:30 | 589 | 5131 | 3009 | 8140
23:00 | 668 | 4919 | 2919 | 7838
23:30 | 659 | 4820 | 2855.5 | 7675.5
24:00 | 650 | 4721 | 2792 | 7513
9500 MW (19:30 )
7952.5 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-11-18 |  | Energy | 182734329
[10 empty] | 2020-11-18 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3308 | 882 | 1626 | 1000 | 650 | 159 | 0 | 0 | 96
0:30 | 3285.5 | 746 | 1609.5 | 928 | 650 | 160.5 | 0 | 0 | 96 | Date: | 2020-11-18
1:00 | 3263 | 610 | 1593 | 856 | 650 | 162 | 0 | 0 | 96
1:30 | 3216 | 610 | 1583 | 778.5 | 635 | 163 | 0 | 0 | 95 | [7 empty] | Total Energy | 182.7343 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 3169 | 610 | 1573 | 701 | 620 | 164 | 0 | 0 | 94 | [7 empty] | Energy not Served | 0
2:30 | 3194 | 610 | 1571.5 | 536.5 | 620 | 160.5 | 0 | 0 | 94 | [7 empty] | Energy Requirement | 182.7343
3:00 | 3219 | 610 | 1570 | 372 | 620 | 157 | 0 | 0 | 94
3:30 | 3181 | 563 | 1565 | 359.5 | 620 | 156 | 0 | 0 | 92 | [6 empty] | Shortage
4:00 | 3143 | 516 | 1560 | 347 | 620 | 155 | 0 | 0 | 90
4:30 | 3168 | 516 | 1518 | 325.5 | 620 | 154 | 0 | 0 | 87
5:00 | 3193 | 516 | 1476 | 304 | 620 | 153 | 0 | 0 | 84
5:30 | 3189.5 | 516 | 1500 | 357.5 | 635 | 153 | 0 | 0 | 82
6:00 | 3186 | 516 | 1524 | 411 | 650 | 153 | 0 | 0 | 80
6:30 | 3171 | 516 | 1525 | 464 | 650 | 154.5 | 0 | 0 | 78 |  |  |  |  | Coal
7:00 | 3156 | 516 | 1526 | 517 | 650 | 156 | 0 | 0 | 76
7:30 | 3120.5 | 515.5 | 1551.5 | 693.5 | 650 | 156 | 0 | 0 | 79 |  |  |  | Oil |  |  |  | ,
8:00 | 3085 | 515 | 1577 | 870 | 650 | 156 | 0 | 0 | 82
8:30 | 3119 | 507.5 | 1545 | 972.5 | 645 | 156 | 0 | 0 | 81
9:00 | 3153 | 500 | 1513 | 1075 | 640 | 156 | 0 | 0 | 80
9:30 | 3122.5 | 500 | 1491 | 1259.5 | 625 | 156 | 0 | 0 | 82
10:00 | 3092 | 500 | 1469 | 1444 | 610 | 156 | 0 | 0 | 84
10:30 | 3042 | 619.5 | 1454.5 | 1475.5 | 610 | 157 | 0 | 0 | 85
11:00 | 2992 | 739 | 1440 | 1507 | 610 | 158 | 0 | 0 | 86
11:30 | 3114 | 738.5 | 1469 | 1524 | 610 | 158 | 0 | 0 | 89
12:00 | 3236 | 738 | 1498 | 1541 | 610 | 158 | 0 | 0 | 92
12:30 | 3270 | 738 | 1516 | 1550 | 610 | 158 | 0 | 0 | 93
13:00 | 3304 | 738 | 1534 | 1559 | 610 | 158 | 0 | 0 | 94
13:30 | 3304 | 738 | 1534 | 1559 | 610 | 158 | 0 | 0 | 94
14:00 | 3304 | 738 | 1534 | 1559 | 610 | 158 | 0 | 0 | 94
14:30 | 3263 | 738.5 | 1514.5 | 1497.5 | 585 | 159.5 | 0 | 0 | 98
15:00 | 3222 | 739 | 1495 | 1436 | 560 | 161 | 0 | 0 | 102
15:30 | 3240.5 | 739 | 1500.5 | 1370 | 560 | 160 | 0 | 0 | 96
16:00 | 3259 | 739 | 1506 | 1304 | 560 | 159 | 0 | 0 | 90
16:30 | 3289.5 | 738.5 | 1520.5 | 1337.5 | 560.5 | 158 | 0 | 0 | 97
17:00 | 3320 | 738 | 1535 | 1371 | 561 | 157 | 0 | 0 | 104
17:30 | 3333 | 809.5 | 1586 | 1903 | 605.5 | 157 | 32.5 | 0 | 112
18:00 | 3346 | 881 | 1637 | 2435 | 650 | 157 | 65 | 0 | 120
18:30 | 3392 | 881 | 1651 | 2442.5 | 660 | 157.5 | 58 | 0 | 118
19:00 | 3438 | 881 | 1665 | 2450 | 670 | 158 | 51 | 0 | 116
19:30 | 3421 | 881 | 1685 | 2309 | 670 | 158 | 51 | 0 | 114
20:00 | 3419 | 882 | 1637 | 2266 | 700 | 158 | 51 | 0 | 114
20:30 | 3419 | 881.5 | 1653 | 2110 | 700.5 | 158.5 | 51 | 0 | 113
21:00 | 3419 | 881 | 1669 | 1954 | 701 | 159 | 51 | 0 | 112
21:30 | 3390 | 881.5 | 1662 | 1740 | 700.5 | 160 | 51 | 0 | 109
22:00 | 3361 | 882 | 1655 | 1526 | 700 | 161 | 51 | 0 | 106
22:30 | 3340.5 | 882 | 1680.5 | 1263 | 685 | 160.5 | 25.5 | 0 | 103
23:00 | 3320 | 882 | 1706 | 1000 | 670 | 160 | 0 | 0 | 100
23:30 | 3314 | 882 | 1666 | 1000 | 660 | 159.5 | 0 | 0 | 98 | Max Temp. in Dhaka |  | 30.6° C
24:00 | 3308 | 882 | 1626 | 1000 | 650 | 159 | 0 | 0 | 96
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
Note on W13: Author:

## Generation
g | 2020-11-18
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 92 | 94 | 87 | 85 | 83 | 83 | 86 | 86 | 86 | 86 | 88 | 88 | 88 | 89 | 91 | 89 | 87 | 87 |  | 88 | 88 | 88 | 89 | 91 | 90 | 89 | 2079976
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1696000
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2900000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 3 | 9 | 14 | 17 | 19 | 19 | 18 | 15 | 10 | 4 | 0 | [9 empty] | 126630
6 | Sikalbaha 225MW CCPP (Gas) | 215 | 203 | 209 | 203 | 213 | 206 | 216 | 203 | 210 | 204 | 204 | 204 | 219 | 204 | 203 | 203 | 216 | 204 |  | 203 | 202 | 203 | 203 | 203 | 206 | 204 | 4908131
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 49 |  | 51 | 51 | 51 | 51 | 51 |  |  | 254250
12 | Hathazari 100 MW peaking PP
Sikalbaha 105 MW PP (Baraka Sikalbaha)
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 97 | 97 | 37 | [16 empty] | 598000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [7 empty] | 22 | 30 | 30 | 30 | 30 | 30 | 30 | 15 | 15 | 15 | 170 |  | 180 | 180 | 180 | 120 | 65 | 15 | 15 | 1098981
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 8 | 8 | 8 | 418181
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 171 | 164 | 168 | 171 | 173 | 171 | 170 | 170 | 170 | 170 | 160 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4082000
23 | Ghorasal TPP Unit-5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2772000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4736091
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 |  | 135 | 135 | 135 | 135 | 135 | 100 | 100 | 2758194
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 29 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 622800
33 | Ashuganj 225 MW CCPP | 199 | 180 | 190 | 180 | 197 | 194 | 202 | 186 | 198 | 181 | 182 | 191 | 193 | 181 | 190 | 190 | 200 | 181 |  | 181 | 184 | 181 | 181 | 176 | 178 | 175 | 4558000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 325 | 300 | 320 | 300 | 315 | 310 | 320 | 280 | 300 | 260 | 260 | 345 | 335 | 275 | 295 | 295 | 315 | 290 |  | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 7505500
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 138240
36 | Chandpur 150 MW CCPP | 52 | 46 | 51 | 51 | 50 | 51 | 51 | 51 | 51 | 51 | 50 | 75 | 75 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 49 | 52 | 52 | 1397090
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 380 | 380 | 380 | 380 | 380 | 400 | 400 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 370 | 370 |  | 370 | 370 | 370 | 370 | 370 | 370 | 370 | 8319000
41 | Haripur 360MW CCPP(HPL) | 300 | 300 | 300 | 300 | 300 | 330 | 330 | 345 | 284 | 284 | 285 | 284 | 297 | 275 | 306 | 314 | 314 | 324 |  | 324 | 325 | 324 | 330 | 330 | 339 | 357 | 7476000
42 | RPCL 210MW CCPP | 113 | 114 | 113 | 112 | 113 | 113 | 113 | 113 | 110 | 108 | 107 | 107 | 107 | 107 | 108 | 109 | 106 | 110 |  | 110 | 110 | 112 | 110 | 111 | 112 | 113 | 2576600
43 | Mymensingh PV 50 MW Solar PP | [6 empty] | 5 | 21 | 37 | 42 | 47 | 49 | 43 | 36 | 24 | 9 | 1 | [9 empty] | 308130
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 718000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 50 | 51 | 65 | 65 | 65 | 65 | 65 |  | 65 | 65 | 65 | 65 | 65 | 60 | 60 | 723360
46 | Shajibazar 330 MW CCPP | 159 | 158 | 160 | 160 | 160 | 161 | 159 | 159 | 157 | 158 | 159 | 159 | 161 | 161 | 160 | 159 | 159 | 159 |  | 159 | 159 | 160 | 158 | 158 | 159 | 158 | 3650000
47 | Shahjibazar GTPP Unit- 8 & 9 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 65 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 67 | 67 |  | 67 | 67 | 67 | 68 | 67 | 67 | 69 | 1399968
48 | Shahjibazar 86MW PP (Shahjibazar) | 87 | 87 | 87 | 87 | 20 | 20 | 20 | 84 | 84 | 84 | 85 | 85 | 84 | 85 | 85 | 40 | 40 | 86 |  | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 1809600
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [26 empty] | 0
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 207504
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 11 | 11 | 11 | 47 | 47 | 47 | 47 | 47 | 47 | 52 | 50 | 50 | 50 | 50 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1083600
56 | Shahjahanulla 25 MW PP
57 | Bibiana-II 341 MW CCPP (Summit) |  |  |  | 7 | 13 | 12 | 20 | 20 | 20 | 20 | [14 empty] | 10 | 10 | 68500
| Bibiyana South 400 MW | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 87 | 45 | 13 |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 1090200
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 5 | 17 | [8 empty] | 26750
59 | Anlima Energy Ltd.
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 18 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 473664
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 372852
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 446112
63 | Impoprt (Tripura) | 96 | 94 | 94 | 90 | 84 | 80 | 76 | 82 | 80 | 84 | 86 | 92 | 94 | 102 | 102 | 90 | 104 | 120 |  | 116 | 114 | 114 | 112 | 106 | 100 | 96 | 2261760
64 | Malancha, Ctg. EPZ (United) | 35 | 35 | 36 | 37 | 38 | 38 | 33 | 6 | 4 | 3 | 3 | 3 | 7 | 4 | 2 | 4 | 8 | 16 |  | 16 | 17 | 20 | 21 | 32 | 32 | 32 | 438240
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 505440
66 | Feni 11 MW PP (Doreen) | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 199080
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 21 |  | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 747400
68 | Cumilla 25 MW PP (Summit) | 21 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 21 | 21 | 21 | 21 | 21 | 18 | 18 | 433510
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 31 | 31 | 28 | 28 | 28 | 21 | 21 | 20 | 20 | 16 | 20 | 14 | 18 | 18 | 18 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 538020
71 | Maona 33 MW PP(Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 411900
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 591500
73 | Ghorashal 108MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 302136
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | 26 | [7 empty] | 2 | 36 | 36 | 36 | 36 | 36 | 18 | 18 | 18 | 89 |  | 113 | 113 | 113 | 113 | 75 |  |  | 900480
| Manikgonj 162MW PP | [7 empty] | 36 | 61 | 76 | 73 | 55 | 55 | 55 | 68 | 46 | 13 | [9 empty] | 551520
77 | Siddhirganj 100 PP(Dutch Bangla) | [11 empty] | 4 | 15 | 20 | 36 | 8 | 7 | 70 |  | 80 | 55 | 50 | 20 |  |  |  | 357120
78 | Gazipur 52 MW PP | [6 empty] | 4 | 22 | 48 | 51 | 51 | 51 | 51 | 51 | 42 | 32 | 32 | 32 |  | 16 | [6 empty] | 502536
79 | Kodda 150MW PP | [17 empty] | 16 | [8 empty] | 12000
80 | Jamalpur 95 MW PP(Powerpac) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 16 | 16 | 16 | 17 | 17 | 17 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 537600
81 | Jangalia 52 MW PP (Lakdanavi) | [16 empty] | 1 | 20 |  | 8 | 8 | 8 |  |  |  |  | 56597
| Gazipur 100 MW PP | 52 | 52 | 17 | 17 | 17 | 17 | 18 | 64 | 90 | 90 | 90 | 90 | 90 | 90 | 94 | 90 | 90 | 100 |  | 105 | 105 | 105 | 72 | 72 | 72 | 72 | 1718820
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 3 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 25439
| Jodiac Power | 54 | 54 | 17 | 17 | 17 | 17 | 21 | 53 | 54 | 54 | 37 | 54 | 39 | 36 | 53 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1102456
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | [9 empty] | 6 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 32 |  | 78 | 65 | 64 | 40 |  |  |  | 393960
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP(Summit) | 150 | 150 | 155 | 150 | 165 | 280 | 290 | 290 | 300 | 280 | 250 | 270 | 280 | 280 | 335 | 275 | 290 | 260 |  | 290 | 285 | 250 | 270 | 270 | 285 | 250 | 5982342
87 | Meghnaghat 100 MW(IEL) | [9 empty] | 11 | 50 | 50 | 50 | 40 | 25 | 11 | 7 | 56 |  | 78 | 50 | 50 | 25 |  |  |  | 485760
| Meghnaghat 104 MW PP (OPCL) | 90 | 75 | 53 | 53 | 25 | 17 | 17 | 34 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1838400
88 | Ghorashal 78.5 MW PP(MAX) | [26 empty] | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [26 empty] | 0
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 47 | 46 | 49 | 49 | 46 | 46 | 46 | 49 |  | 49 | 49 | 49 | 49 | 50 | 50 | 50 | 1180872
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1223863
94 | Gagnagar 102 MW PP (Digital Power) | [6 empty] | 3 | 16 | 16 | 40 | 64 | 64 | 64 | 64 | 24 | 32 | 40 | 64 |  | 94 | 94 | 94 | 64 | 48 | 16 | 16 | 912816
95 | Patenga 50MW PP (Baraka) | 32 | 30 | [7 empty] | 32 | 44 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 36 | 788160
96 | Chattogram 108 MW PP (ECPV) | [10 empty] | 0 | [5 empty] | 5 | 34 |  | 12 | 12 | 10 |  |  |  |  | 83520
97 | katpotti 52 MW | [26 empty] | 3648
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [9 empty] | 15 | 30 | 30 | 30 | 30 | 15 | 15 | 15 | 45 |  | 55 | 30 | 30 | 15 |  |  |  | 353032
100 | Manikganj 55 MW PP (Northern) | [9 empty] | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 55 |  | 55 | 55 | 55 | 17 |  |  |  | 409697
101 | Kushiara 163 MW CCPP (KP) | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 |  | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 250470
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [10 empty] | 13150
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 17 | 17 | 17 | 17 | 30 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 1160640
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [16 empty] | 7 | 50 |  | 50 | 50 | 50 | 24 |  |  |  | 196800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [8 empty] | 11 | 100 | 100 | 86 | 81 | 80 | 80 | 69 | 34 | 30 | [8 empty] | 694080
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 90 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 1500480
116 | Chandpur 200MW (Desh energy)
117 | Ashuganj 150MW PP (Midland) | [8 empty] | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 13 | 75 |  | 113 | 115 | 115 | 113 | 70 |  |  | 732654
118 | Bibiyana-III 400 MW CCPP | 399 | 399 | 399 | 350 | 350 | 328 | 290 | 232 | 232 | 232 | 232 | 252 | 252 | 252 | 305 | 304 | 304 | 400 |  | 401 | 401 | 400 | 400 | 400 | 399 | 399 | 7901000
| Jamalpur 115 MW PP (United) | 85 | 45 | 8 | 8 | 8 | 8 | 14 | 93 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 85 | 55 | 16 | 2089200
| Anwara 300 MW PP (United) | 88 | 16 |  |  |  |  | 16 | 16 | 16 | 49 | 53 | 53 | 52 | 52 | 16 | 16 | 16 | 153 |  | 157 | 159 | 159 | 160 | 160 | 53 |  | 1435200
| Juldah unit-2 (Acorn) | 100 | 100 | 70 | 50 | 20 | 20 | 52 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 98 | 96 | 98 | 2139840
120 | Eastern Zone Total | 4840 | 4607 | 4318 | 4212 | 4103 | 4218 | 4285 | 4603 | 4777 | 5064 | 5063 | 5257 | 5286 | 5172 | 5203 | 5045 | 5067 | 5969 |  | 6128 | 6022 | 5981 | 5704 | 5343 | 4919 | 4721 | 117963042
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [9 empty] | 16 | 16 | 16 | 16 | 16 |  |  | 16 | 49 |  | 49 | 16 | 16 |  |  |  |  | 211200
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [6 empty] | 17 | 35 | 53 | 53 | 53 | 53 | 53 | 53 | 17 | 17 | 35 | 90 |  | 90 | 90 | 90 | 90 | 90 |  |  | 925440
130
131
132
133 | Bhola Nutan Biddut BD LTD (GAS) | 36 | 37 | 36 | 37 | 38 | 35 | 34 | 36 | 33 | 6 | 4 | 22 | 36 | 36 | 35 | 36 | 36 | 35 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 802910
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [16 empty] | 16 | 48 |  | 16 | 16 | 16 |  |  |  |  | 96672
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 76 | 75 | 43 | 42 | 42 | 42 | 42 | 42 | 42 | 20 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 82 |  | 95 | 96 | 95 | 97 | 96 | 96 | 54 | 1247236
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 23 | 23 | 22 | 15 | 15 | 16 | 14 | 19 | 20 | 18 | 19 | 21 | 22 | 20 | 15 | 19 | 20 | 27 |  | 27 | 27 | 27 | 27 | 27 | 26 | 24 | 494900
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 610 | 610 | 610 | 516 | 516 | 516 | 516 | 515 | 500 | 500 | 739 | 738 | 738 | 739 | 739 | 739 | 738 | 881 |  | 881 | 881 | 882 | 881 | 882 | 882 | 882 | 16679272
147 | Bheramara 410 MW CCPP | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 345 | 370 | 340 | 345 | 350 | 385 | 345 | 345 | 345 | 375 | 345 |  | 345 | 345 | 345 | 345 | 345 | 350 | 340 | 8301600
148 | Payra 1320 MW | 500 | 470 | 470 | 470 | 470 | 500 | 500 | 500 | 490 | 460 | 460 | 460 | 460 | 420 | 410 | 410 | 410 | 500 |  | 520 | 520 | 550 | 550 | 550 | 520 | 500 | 11603400
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 151 | 150 |  | 150 | 150 | 150 | 151 | 150 | 150 | 150 | 3681700
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP | [11 empty] | 70 | 70 | 50 | 50 | 50 | 50 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 820000
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 158 | 152 | 154 | 159 | 163 | 180 | 193 | 166 | 168 | 201 | 165 | 157 | 166 | 146 | 148 | 145 | 155 | 161 |  | 193 | 173 | 171 | 173 | 161 | 159 | 162 | 4178836
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 166 | 156 | 158 | 163 | 168 | 181 | 170 | 163 | 173 | 177 | 155 | 159 | 169 | 197 | 164 | 158 | 171 | 168 |  | 187 | 188 | 188 | 189 | 169 | 159 | 160 | 4321245
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 351 | 331 | 361 | 350 | 364 | 365 | 367 | 363 | 364 | 358 | 348 | 388 | 391 | 349 | 355 | 396 | 406 | 376 |  | 386 | 403 | 354 | 377 | 370 | 403 | 349 | 8943236
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 18 | 18 | 17 | 17 | 17 | 17 | 21 | 21 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 477360
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 225594
165 | Amnura 50 MW PP(Sinha) | [20 empty] | 0 | [5 empty] | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [26 empty] | 0
169 | Natore 52 MW PP (Rajlanka) | [16 empty] | 8 | 34 | [8 empty] | 42240
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [16 empty] | 9 | 52 | [8 empty] | 134208
172 | Confidence Power Bogura Unit-1 113 MW | [9 empty] | 25 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 109 |  | 110 | 110 | 110 | 110 | 50 | 35 | 35 | 854016
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [11 empty] | 19 | 36 | 39 | 35 | 35 | 34 | 113 |  | 113 | 113 | 113 | 113 | 70 |  |  | 697920
177 | Sympa Solar Power 8MW | [6 empty] | 1 | 2 | 3 | 4 | 5 | 5 | 5 | 4 | 2 | 1 | 0 | [9 empty] | 32302
178
178