## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-11-22 | Sunday
|  |  | Date (day): | 2020-11-22 |  | Sunday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12983.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14314 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-11-21 | 2020-11-22 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 115 | 115 | 115 | 75 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 200 | 200 |  | 165 | Machine problem
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 71 | 71 | 78 | 78
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 52 | 51 | 51 | 52 | 56
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under S/D for dust in gas.
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 53 | 304 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 |  |  | GT-1 under maint.
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 100 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 7 | 110 | 150 | 150 |  |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 64 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 30 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 50 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19 |  | 3
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 99 | 97 | 70 | 100 | 110 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 2 | 95 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 32 | 66 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 32 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 35 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 50 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 24 | 24 | 24 | 24 |  | 9 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 8 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 24 | 52 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 145 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 15 | 31 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 91 | 54 | 90 | 90 |  | 15 | Engine problem
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 53 | 53 | 90 | 90 |  | 14 | Engine problem
|  | Manikgonj 162MW PP |  | HFO | IPP | 9*18 | 0 | 0 | 116 | 0 | 0 | 0
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 1430 | 2227 | 3243 | 3614 | 454 | 1365
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 26 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 80 | 114 | 160 | 160 | 70 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 218 | 204 | 215 | 225
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 17 | 102 | 102
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 16 | 15 | 20
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 64 | 100 | 100
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 49 | 140 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 793 | 999 | 1696 | 1686 | 460 | 98
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 100 | 100 | 135 | 135 | 0 |  | Gas Shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 171 | 223 | 225 | 225 |  |  | FGMO
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 340 | 310 | 360 | 360 |  |  | FGMO
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 26 | 30 | 30 | 15 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 25 | 25 | 30 |  | Gas shortage
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 45 | 45 | 45 | 45 | 150 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 105 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 76 | 75 | 90 | 90 |  | 57 | ST Under maint.
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 165 | 200
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 21 | 22 | 22
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 84 | 108 | 156 | 172
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 24 | 33 | 33 | 33
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 52 | 52 | 52
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 21 | 20 | 21
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 17 | 114 | 114
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 41 | 106 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 989 | 1306 | 1797 | 2099 | 458 | 417
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 156 | 163 | 165 | 165 | 37 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 25 | 25 | 25 | 25 |  | 70 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 40 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 70 | 115 | 115 | 115
|  | Mymensingh PV 50 MW Solar PP |  | Solar | IPP | 50 | 0 | 0 | 43 | 0 | 50 | 0
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 315 | 363 | 578.6 | 527 | 37 | 70
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 60 | 60 | 60 |  | 32 | GT-2 under shut down for maint.
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 60 | 60 | 60
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 110 | 163 | 163
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 223 | 215 | 255 | 255 |  | 75 | Machine problem
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 11 | 50 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 30 | 50 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 64 | 67 | 66 | 66 |  |  | FGMO
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 50 | 82 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 120 | 90 | 145 | 145
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  |  | 33 kV S/S maint.
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 20 | 25
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 280 | 320 | 320
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 401 | 404 | 400 | 400
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 0 | 0 |  |  | 33 kV line maint.
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 45 | 45
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1468 | 1484 | 1726 | 1731 | 0 | 107
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 552 | 560 | 518 | 631
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 49 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 330 | 370 | 410 | 410
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 70 | 105 | 105
| 108 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 882 | 1049 | 1288 | 1827 | 0 | 0
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 48 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 0 | 0 | 30 | 30
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 23 | 92 | 95 | 95
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 400 | 550 | 600 | 660
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 35 | 36 | 35 | 35
|  | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 0 | 0 | 53 | 0 | 0 | 0
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 511 | 726 | 870 | 930 | 0 | 194
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | Gas shortage & ST Under maint
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 186 | 171 | 220 | 220 |  |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 200 | 182 | 220 | 220 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 429 | 409 | 413 | 413 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 33
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 22 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 8 | 52 | 52
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 113 | 113
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 111 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 841 | 914 | 1514 | 1637 | 271 | 210
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 140 | 140 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 2 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 142 | 253 | 271 | 263 | 294 | 40
|  | Total |  |  |  |  | 20383 | 19892 | 7371 | 9321 | 12983.6 | 14314 | 1974 | 2501
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6880.7071 | 8701 | 12119.9768 | 13361.8833
| A. |  | 2020-11-21 | (Yesterday) |  |  |  |  | Saturday
| 1 | Highest Generation : |  |  | 9321 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 5883 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9321 | MW
| 3 | Day peak Generation : |  |  | 7373 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8701 | MW
| 4 | Evening peak Generation : |  |  | 9321 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 177.1459 | MKWHr | By Solar | 0.40921 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 122.0451 | MKWHr |  | By Oil: | 23.1946 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 14.3765 | MKWHr |  | By Hydro: | 3.1289 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1974 | MW | Dhaka | 3294 | 3294 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2501 | MW | Chittagong | 1000 | 1000 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4475 | MW | Khulna | 1032 | 1032 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1018.56 | MMCFD |  |  | Rajshahi | 830 | 830 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 140481271.64 | ii) Oil : | Taka | 159610241.06 | Comilla | 746 | 746 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 66639555 | Total | Taka | 366731067.7 | Mymensingh | 688 | 688 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 323 | 323 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 55 | MW (E to W) at | 19:00 | hrs | Barisal | 230 | 230 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 45 | MW at | 20:00 | hrs | Rangpur | 558 | 558 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 27.2° C |  |  | Total | 8701 | 8701 |  | 0
| B. |  | 2020-11-22 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 28.2° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9600 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14314 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 7600 | MW
| 4 | Reserve(Generation end) |  |  |  | 4714 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 182.4483 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6066 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.8902 | MKWHr. | ii) HVDC Flow at Peak Time |  | 560 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.1014 | MKWHr. | iii) Maximum HVDC Flow : |  | 724 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 102.2 |  | (b) Today: | 101.96 |  | (c) Rule Curve: |  | 106.9
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-11-21
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Anlima Energy Ltd. | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Mymensingh PV 50 MW Solar PP | Manikgonj 162MW PP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 102 | 115 | 200 | 51 | 74 | 0 | 0 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 32 | 24 | 0 | 0 | 0 | 90 | 70 | 120 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 30 | 100 | 0 | 0 | 310 | 0 | 180 | 26 | 85 | 29 | 15 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 21 | 21 | 88 | 165 | 25 | 20 | 0 | 30 | 60 | 14 | 10 | 163 | 220 | 40 | 10 | 0 | 145 | 0 | 0 | 0 | 285 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 398 | 16 | 0 | 0 | 0 | 53 | 54 | 0 | 0 | 0 | 100 | 0 | 90 | 0 | 0 |  | 410 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 172 | 0 | 93 | 0 | 145 | 0 | 337 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 36 | 0 | 0 |  | 4548 | 2145 | 6693 | 3377 | 410 | 1451 | 577 | 630 | 160 | 0 | 88 | 0 | 0 | 102.25
2:00 | 0 | 0 | 100 | 115 | 200 | 51 | 74 | 0 | 0 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 32 | 24 | 33 | 0 | 0 | 90 | 70 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 30 | 100 | 0 | 0 | 325 | 0 | 193 | 26 | 85 | 29 | 15 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 20 | 21 | 86 | 164 | 25 | 20 | 0 | 30 | 60 | 14 | 10 | 163 | 215 | 40 | 10 | 0 | 145 | 0 | 0 | 0 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 400 | 16 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 |  | 410 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 172 | 0 | 58 | 0 | 146 | 0 | 387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 36 | 0 | 0 |  | 4319 | 2128 | 6447 | 3455 | 410 | 1461 | 265 | 610 | 160 | 0 | 86 | 0 | 0 | 102.24
3:00 | 0 | 0 | 100 | 115 | 200 | 51 | 73 | 0 | 0 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 32 | 24 | 33 | 0 | 0 | 90 | 70 | 120 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 30 | 100 | 0 | 0 | 310 | 0 | 180 | 26 | 80 | 29 | 15 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 8 | 21 | 84 | 163 | 25 | 20 | 0 | 30 | 60 | 14 | 10 | 163 | 219 | 40 | 10 | 0 | 145 | 0 | 0 | 0 | 275 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 |  | 410 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 172 | 0 | 55 | 0 | 149 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 36 | 0 | 0 |  | 4152 | 2096 | 6248 | 3417 | 410 | 1405 | 162 | 610 | 160 | 0 | 84 | 0 | 0 | 102.23
4:00 | 0 | 0 | 100 | 115 | 200 | 51 | 20 | 0 | 0 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 32 | 24 | 33 | 0 | 0 | 90 | 70 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 100 | 0 | 0 | 265 | 0 | 186 | 26 | 85 | 29 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 8 | 21 | 82 | 164 | 25 | 0 | 0 | 30 | 60 | 14 | 10 | 163 | 217 | 40 | 10 | 0 | 144 | 0 | 0 | 0 | 270 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 13 |  | 410 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 172 | 0 | 25 | 0 | 149 | 0 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 36 | 0 | 0 |  | 3885 | 2114 | 5999 | 3313 | 410 | 1286 | 138 | 610 | 160 | 0 | 82 | 0 | 0 | 102.22
5:00 | 0 | 0 | 100 | 115 | 200 | 12 | 20 | 0 | 0 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 24 | 20 | 33 | 0 | 0 | 90 | 70 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 100 | 0 | 0 | 290 | 0 | 195 | 8 | 82 | 29 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 8 | 13 | 80 | 163 | 25 | 0 | 0 | 30 | 60 | 14 | 10 | 163 | 217 | 40 | 10 | 0 | 100 | 0 | 0 | 0 | 280 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 31 |  | 410 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 172 | 0 | 26 | 0 | 154 | 0 | 386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 35 | 0 | 0 |  | 3759 | 2124 | 5883 | 3304 | 410 | 1253 | 86 | 590 | 160 | 0 | 80 | 0 | 0 | 102.21
6:00 | 0 | 0 | 100 | 115 | 200 | 12 | 30 | 0 | 0 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 24 | 20 | 33 | 0 | 0 | 88 | 70 | 120 | 0 | 0 | 206 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 39 | 135 | 0 | 0 | 305 | 0 | 196 | 8 | 85 | 26 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 8 | 10 | 76 | 163 | 25 | 0 | 0 | 30 | 60 | 14 | 10 | 163 | 221 | 67 | 44 | 0 | 101 | 0 | 0 | 0 | 300 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 99 |  | 410 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 168 | 0 | 25 | 0 | 160 | 0 | 387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 36 | 0 | 0 |  | 4027 | 2167 | 6194 | 3468 | 410 | 1318 | 154 | 610 | 158 | 0 | 76 | 0 | 0 | 102.2
7:00 | 0 | 0 | 100 | 115 | 200 | 51 | 30 | 0 | 0 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 24 | 20 | 25 | 0 | 0 | 88 | 70 | 120 | 0 | 0 | 205 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 20 | 39 | 135 | 0 | 0 | 300 | 0 | 182 | 45 | 85 | 26 | 25 | 0 | 11 | 0 | 0 | 0 | 15 | 0 | 20 | 15 | 72 | 163 | 25 | 20 | 0 | 30 | 60 | 14 | 30 | 130 | 216 | 67 | 44 | 0 | 90 | 0 | 0 | 0 | 270 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 10 | 0 | 3 | 400 | 8 | 6 | 0 | 0 | 16 | 23 | 0 | 0 | 0 | 30 | 0 | 9 | 3 | 96 |  | 410 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 148 | 0 | 21 | 0 | 144 | 0 | 387 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440 | 36 | 0 | 0 |  | 4160 | 2150 | 6310 | 3404 | 410 | 1387 | 294 | 580 | 158 | 0 | 72 | 5 | 0 | 102.19
8:00 | 0 | 0 | 100 | 115 | 200 | 51 | 60 | 0 | 0 |  | 0 | 225 | 0 | 0 | 0 | 2 | 0 | 0 | 40 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 25 | 28 | 20 | 8 | 0 | 0 | 88 | 70 | 120 | 0 | 0 | 207 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 47 | 20 | 14 | 135 | 0 | 0 | 315 | 0 | 195 | 45 | 84 | 26 | 25 | 0 | 37 | 0 | 0 | 0 | 21 | 0 | 20 | 18 | 78 | 165 | 25 | 20 | 0 | 30 | 60 | 11 | 30 | 130 | 217 | 67 | 44 | 0 | 90 | 0 | 0 | 0 | 300 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 15 | 0 | 20 | 400 | 10 | 27 | 0 | 1 | 16 | 34 | 0 | 0 | 5 | 60 | 0 | 38 | 9 | 92 |  | 410 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 138 | 0 | 0 | 0 | 0 | 151 | 0 | 21 | 0 | 138 | 0 | 385 | 17 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 440 | 36 | 0 | 0 |  | 4483 | 2153 | 6636 | 3439 | 410 | 1442 | 512 | 578 | 158 | 0 | 78 | 19 | 0 | 102.18
9:00 | 0 | 0 | 100 | 115 | 200 | 51 | 73 | 0 | 0 |  | 0 | 225 | 0 | 0 | 14 | 15 | 0 | 0 | 90 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 25 | 28 | 20 | 8 | 0 | 0 | 88 | 70 | 120 | 0 | 0 | 206 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 45 | 20 | 8 | 135 | 0 | 0 | 270 | 0 | 181 | 45 | 85 | 26 | 25 | 0 | 43 | 0 | 0 | 0 | 21 | 0 | 20 | 18 | 80 | 164 | 25 | 20 | 1 | 30 | 60 | 11 | 30 | 100 | 216 | 67 | 82 | 0 | 90 | 0 | 0 | 0 | 290 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 50 | 0 | 40 | 350 | 58 | 80 | 0 | 3 | 50 | 49 | 0 | 0 | 26 | 100 | 0 | 54 | 21 | 93 |  | 411 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 151 | 0 | 21 | 0 | 141 | 0 | 362 | 17 | 0 | 0 | 0 | 0 | 0 | 2 | 35 | 440 | 6 | 0 | 0 |  | 4737 | 2085 | 6822 | 3331 | 411 | 1394 | 829 | 579 | 158 | 0 | 80 | 40 | 0 | 102.17
10:00 | 0 | 0 | 100 | 115 | 200 | 51 | 73 | 0 | 52 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 0 | 28 | 24 | 8 | 24 | 0 | 88 | 70 | 120 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 20 | 4 | 115 | 0 | 0 | 305 | 0 | 170 | 45 | 85 | 26 | 20 | 0 | 43 | 0 | 0 | 0 | 21 | 0 | 24 | 15 | 82 | 160 | 17 | 20 | 1 | 30 | 60 | 11 | 30 | 100 | 230 | 67 | 82 | 0 | 90 | 0 | 0 | 0 | 300 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15 | 50 | 0 | 0 | 352 | 65 | 91 | 0 | 4 | 16 | 54 | 0 | 0 | 26 | 100 | 0 | 54 | 39 | 110 |  | 410 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 157 | 0 | 21 | 0 | 166 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 440 | 7 | 0 | 42 |  | 4695 | 2042 | 6737 | 3338 | 410 | 1382 | 725 | 580 | 158 | 0 | 82 | 62 | 0 | 102.16
11:00 | 0 | 0 | 100 | 115 | 200 | 52 | 72 | 0 | 52 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 24 | 8 | 24 | 0 | 10 | 70 | 120 | 0 | 0 | 210 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 20 | 6 | 100 | 0 | 0 | 270 | 0 | 172 | 45 | 85 | 23 | 20 | 0 | 43 | 0 | 0 | 0 | 21 | 0 | 24 | 15 | 88 | 159 | 25 | 20 | 1 | 30 | 60 | 11 | 30 | 130 | 220 | 66 | 82 | 0 | 90 | 0 | 0 | 0 | 310 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 17 | 50 | 0 | 0 | 396 | 65 | 91 | 0 | 4 | 16 | 54 | 0 | 0 | 26 | 100 | 0 | 53 | 44 | 110 |  | 552 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 138 | 0 | 0 | 0 | 0 | 165 | 0 | 20 | 0 | 177 | 0 | 392 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 400 | 34 | 0 | 55 |  | 4740 | 2293 | 7033 | 3413 | 552 | 1542 | 750 | 538 | 80 | 0 | 88 | 70 | 0 | 102.14
12:00 | 0 | 0 | 100 | 115 | 200 | 52 | 71 | 0 | 53 |  | 0 | 225 | 7 | 0 | 0 | 0 | 0 | 0 | 99 | 2 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 28 | 24 | 8 | 24 | 0 | 10 | 70 | 120 | 0 | 0 | 218 | 0 | 0 | 0 |  | 2 | 0 | 0 | 0 | 0 | 26 | 20 | 4 | 100 | 0 | 0 | 340 | 0 | 171 | 45 | 76 | 26 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 0 | 24 | 15 | 84 | 156 | 25 | 20 | 1 | 30 | 60 | 11 | 30 | 163 | 223 | 64 | 50 | 0 | 120 | 0 | 0 | 0 | 300 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 18 | 100 | 0 | 0 | 401 | 70 | 91 | 0 | 4 | 49 | 54 | 0 | 0 | 41 | 100 | 0 | 53 | 43 | 116 |  | 552 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 186 | 0 | 23 | 0 | 200 | 0 | 429 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 400 | 35 | 0 | 53 |  | 4997 | 2376 | 7373 | 3561 | 552 | 1557 | 931 | 540 | 80 | 0 | 84 | 68 | 0 | #REF!
13:00 | 0 | 0 | 88 | 115 | 200 | 52 | 70 | 0 | 176 |  | 0 | 225 | 8 | 11 | 14 | 15 | 0 | 0 | 97 | 24 | 66 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 28 | 24 | 8 | 24 | 0 | 10 | 70 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 9 | 0 | 0 | 0 | 0 | 39 | 20 | 14 | 100 | 0 | 0 | 310 | 0 | 171 | 45 | 76 | 26 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 0 | 0 | 18 | 82 | 159 | 25 | 20 | 2 | 45 | 60 | 11 | 30 | 163 | 225 | 64 | 50 | 0 | 120 | 0 | 0 | 0 | 305 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 17 | 100 | 0 | 0 | 401 | 85 | 91 | 0 | 3 | 49 | 54 | 0 | 0 | 97 | 100 | 0 | 53 | 39 | 147 |  | 552 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 185 | 0 | 12 | 0 | 195 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 400 | 34 | 0 | 49 |  | 5287 | 2306 | 7593 | 3496 | 552 | 1633 | 1146 | 540 | 80 | 0 | 82 | 64 | 7593 | 102.13
14:00 | 0 | 0 | 100 | 115 | 200 | 51 | 71 | 0 | 304 |  | 0 | 225 | 10 | 16 | 15 | 15 | 0 | 0 | 39 | 32 | 66 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 26 | 24 | 8 | 8 | 0 | 10 | 70 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 8 | 100 | 0 | 0 | 275 | 0 | 170 | 45 | 84 | 26 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 0 | 0 | 18 | 80 | 125 | 25 | 20 | 1 | 50 | 60 | 11 | 30 | 110 | 224 | 64 | 50 | 0 | 90 | 0 | 0 | 0 | 285 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 100 | 0 | 0 | 351 | 55 | 72 | 0 | 1 | 51 | 54 | 0 | 0 | 105 | 100 | 0 | 53 | 33 | 147 |  | 552 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 153 | 0 | 12 | 0 | 161 | 0 | 373 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 400 | 38 | 0 | 59 |  | 5058 | 2246 | 7304 | 3219 | 552 | 1683 | 1098 | 540 | 80 | 0 | 80 | 52 | 0 | 102.12
15:00 | 0 | 0 | 101 | 115 | 200 | 52 | 70 | 0 | 332 |  | 0 | 225 | 20 | 16 | 15 | 15 | 0 | 0 | 40 | 16 | 66 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 26 | 24 | 8 | 20 | 0 | 10 | 70 | 120 | 0 | 0 | 206 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 44 | 20 | 6 | 100 | 0 | 0 | 275 | 0 | 171 | 45 | 75 | 26 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 0 | 0 | 18 | 84 | 95 | 25 | 20 | 1 | 50 | 60 | 11 | 30 | 110 | 223 | 65 | 50 | 0 | 90 | 0 | 0 | 0 | 300 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 100 | 0 | 0 | 352 | 55 | 91 | 0 | 0 | 53 | 54 | 0 | 0 | 113 | 100 | 0 | 53 | 14 | 128 |  | 553 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 153 | 0 | 12 | 0 | 167 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 400 | 36 | 0 | 64 |  | 5081 | 2305 | 7386 | 3282 | 553 | 1702 | 1119 | 540 | 80 | 0 | 84 | 26 | 0 | 102.11
16:00 | 0 | 0 | 100 | 115 | 200 | 52 | 40 | 0 | 359 |  | 0 | 225 | 50 | 0 | 15 | 15 | 0 | 0 | 40 | 16 | 24 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 19 | 25 | 26 | 24 | 8 | 33 | 0 | 44 | 70 | 120 | 0 | 0 | 216 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 8 | 100 | 0 | 0 | 300 | 0 | 171 | 45 | 86 | 26 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 0 | 0 | 18 | 84 | 95 | 25 | 20 | 0 | 50 | 60 | 11 | 30 | 110 | 220 | 64 | 20 | 0 | 90 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 50 | 0 | 0 | 352 | 55 | 91 | 0 | 0 | 35 | 34 | 0 | 0 | 26 | 100 | 0 | 53 | 10 | 110 |  | 552 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 149 | 0 | 12 | 0 | 163 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 400 | 35 | 0 | 72 |  | 4826 | 2324 | 7150 | 3299 | 552 | 1672 | 875 | 540 | 114 | 0 | 84 | 14 | 0 | 102.1
17:00 | 0 | 0 | 100 | 115 | 200 | 52 | 40 | 0 | 304 |  | 0 | 225 | 70 | 6 | 15 | 16 | 0 | 0 | 100 | 30 | 24 | 10 | 0 | 0 | 0 | 0 | 54 | 17 | 10 | 19 | 0 | 28 | 24 | 17 | 33 | 0 | 44 | 70 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 5 | 19 | 20 | 10 | 100 | 0 | 0 | 320 | 0 | 171 | 45 | 80 | 26 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 0 | 33 | 18 | 98 | 95 | 25 | 20 | 0 | 45 | 60 | 11 | 30 | 110 | 210 | 67 | 20 | 0 | 90 | 0 | 0 | 0 | 300 | 8 | 0 | 0 | 4 | 0 | 0 | 5 | 0 | 0 | 0 | 50 | 0 | 13 | 400 | 67 | 91 | 0 | 0 | 34 | 34 | 0 | 0 | 28 | 100 | 0 | 53 | 1 | 46 |  | 552 | 0 | 390 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 172 | 0 | 12 | 0 | 186 | 0 | 400 | 17 | 0 | 0 | 0 | 35 | 0 | 0 | 20 | 430 | 36 | 0 | 58 |  | 4976 | 2508 | 7484 | 3465 | 552 | 1665 | 1009 | 570 | 114 | 10 | 98 | 1 | 0 | 102.09
18:00 | 0 | 0 | 99 | 115 | 200 | 51 | 60 | 0 | 304 |  | 0 | 225 | 90 | 50 | 42 | 30 | 0 | 0 | 94 | 70 | 50 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 18 | 24 | 33 | 43 | 0 | 44 | 70 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 46 | 41 | 20 | 12 | 100 | 0 | 0 | 315 | 0 | 171 | 45 | 76 | 26 | 5 | 0 | 43 | 0 | 0 | 25 | 21 | 0 | 33 | 21 | 108 | 123 | 25 | 20 | 0 | 55 | 60 | 44 | 43 | 110 | 215 | 67 | 79 | 0 | 90 | 0 | 0 | 0 | 290 | 16 | 0 | 0 | 110 | 0 | 0 | 46 | 0 | 28 | 0 | 100 | 0 | 78 | 400 | 115 | 91 | 0 | 0 | 135 | 46 | 0 | 66 | 87 | 100 | 0 | 53 | 0 | 0 |  | 724 | 0 | 385 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 185 | 0 | 84 | 0 | 193 | 0 | 380 | 70 | 0 | 15 | 0 | 108 | 0 | 0 | 100 | 500 | 36 | 0 | 30 |  | 6110 | 3102 | 9212 | 3554 | 724 | 1833 | 2173 | 640 | 114 | 66 | 108 | 0 | 0 | 102.08
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 100 | 115 | 200 | 51 | 71 | 0 | 304 |  | 0 | 225 | 110 | 100 | 64 | 30 | 0 | 0 | 97 | 95 | 66 | 32 | 0 | 0 | 0 | 0 | 54 | 35 | 17 | 19 | 25 | 25 | 24 | 33 | 52 | 0 | 44 | 70 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 64 | 50 | 20 | 16 | 100 | 0 | 0 | 310 | 0 | 223 | 45 | 75 | 26 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 33 | 21 | 108 | 163 | 25 | 20 | 0 | 60 | 60 | 50 | 50 | 110 | 215 | 67 | 82 | 0 | 90 | 0 | 0 | 0 | 280 | 16 | 0 | 0 | 145 | 0 | 0 | 40 | 0 | 31 | 0 | 100 | 0 | 105 | 404 | 115 | 54 | 0 | 0 | 140 | 54 | 0 | 17 | 106 | 100 | 0 | 53 | 0 | 0 |  | 560 | 0 | 370 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 171 | 0 | 92 | 0 | 182 | 0 | 409 | 70 | 0 | 0 | 0 | 113 | 0 | 0 | 111 | 550 | 36 | 0 | 0 |  | 6379 | 2942 | 9321 | 3628 | 560 | 1899 | 2273 | 690 | 114 | 49 | 108 | 0 | 0 | 102.05
19:30 | 0 | 0 | 100 | 115 | 200 | 52 | 72 | 0 | 304 |  | 0 | 225 | 120 | 100 | 64 | 30 | 0 | 0 | 100 | 98 | 66 | 32 | 0 | 0 | 0 | 0 | 54 | 35 | 0 | 19 | 25 | 32 | 24 | 26 | 52 | 0 | 44 | 70 | 120 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 25 | 50 | 20 | 23 | 100 | 0 | 0 | 320 | 0 | 194 | 45 | 85 | 26 | 5 | 0 | 51 | 0 | 0 | 16 | 21 | 8 | 33 | 21 | 104 | 147 | 25 | 20 | 0 | 60 | 60 | 50 | 50 | 110 | 210 | 67 | 82 | 0 | 90 | 0 | 0 | 0 | 310 | 16 | 0 | 0 | 145 | 0 | 0 | 24 | 0 | 0 | 0 | 100 | 0 | 108 | 400 | 115 | 54 | 0 | 0 | 140 | 54 | 0 | 0 | 113 | 100 | 0 | 53 | 0 | 0 |  | 560 | 0 | 365 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 171 | 0 | 92 | 0 | 188 | 0 | 426 | 70 | 0 | 0 | 0 | 113 | 0 | 0 | 111 | 550 | 36 | 0 | 0 |  | 6232 | 2928 | 9160 | 3597 | 560 | 1955 | 2108 | 690 | 114 | 32 | 104 | 0 | 0 | 0
20:00 | 0 | 0 | 100 | 115 | 200 | 52 | 72 | 0 | 304 |  | 0 | 225 | 125 | 100 | 64 | 30 | 0 | 0 | 99 | 97 | 66 | 32 | 0 | 0 | 0 | 0 | 54 | 35 | 0 | 19 | 25 | 32 | 24 | 31 | 52 | 0 | 44 | 70 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 25 | 50 | 20 | 27 | 100 | 0 | 0 | 310 | 0 | 182 | 45 | 75 | 26 | 5 | 0 | 51 | 0 | 0 | 16 | 21 | 8 | 33 | 21 | 104 | 147 | 25 | 20 | 0 | 59 | 60 | 53 | 50 | 110 | 210 | 67 | 81 | 0 | 90 | 0 | 0 | 0 | 280 | 16 | 0 | 0 | 145 | 0 | 0 | 24 | 0 | 0 | 0 | 100 | 0 | 108 | 400 | 115 | 54 | 0 | 0 | 140 | 54 | 0 | 0 | 113 | 100 | 0 | 53 | 0 | 0 |  | 560 | 0 | 365 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 173 | 0 | 93 | 0 | 184 | 0 | 399 | 70 | 0 | 0 | 0 | 113 | 0 | 0 | 112 | 550 | 36 | 0 | 0 |  | 6184 | 2912 | 9096 | 3567 | 560 | 1919 | 2110 | 690 | 114 | 32 | 104 | 0 | 0 | 102.06
21:00 | 0 | 0 | 100 | 115 | 200 | 52 | 72 | 0 | 307 |  | 0 | 225 | 128 | 55 | 32 | 30 | 0 | 0 | 100 | 50 | 32 | 32 | 0 | 0 | 0 | 0 | 54 | 35 | 0 | 19 | 25 | 32 | 24 | 31 | 0 | 0 | 44 | 70 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 32 | 100 | 0 | 0 | 310 | 0 | 182 | 45 | 75 | 29 | 5 | 0 | 51 | 0 | 0 | 16 | 21 | 8 | 33 | 21 | 102 | 146 | 25 | 20 | 0 | 60 | 60 | 53 | 50 | 110 | 210 | 67 | 81 | 0 | 90 | 0 | 0 | 0 | 270 | 20 | 0 | 0 | 60 | 0 | 0 | 24 | 0 | 0 | 0 | 100 | 0 | 108 | 400 | 115 | 54 | 0 | 0 | 141 | 54 | 0 | 0 | 113 | 100 | 0 | 53 | 0 | 0 |  | 555 | 0 | 360 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 175 | 0 | 93 | 0 | 181 | 0 | 405 | 70 | 0 | 0 | 0 | 113 | 0 | 0 | 113 | 550 | 36 | 0 | 0 |  | 5872 | 2928 | 8800 | 3569 | 555 | 1933 | 1805 | 690 | 114 | 32 | 102 | 0 | 0 | #REF!
22:00 | 0 | 0 | 100 | 115 | 200 | 52 | 72 | 0 | 306 |  | 0 | 225 | 128 | 0 | 15 | 0 | 0 | 0 | 97 | 0 | 32 | 10 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 32 | 24 | 33 | 0 | 0 | 43 | 70 | 120 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 37 | 100 | 0 | 0 | 310 | 0 | 182 | 45 | 75 | 29 | 5 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 96 | 148 | 25 | 20 | 0 | 57 | 60 | 53 | 47 | 110 | 200 | 67 | 82 | 0 | 90 | 0 | 0 | 0 | 270 | 20 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 100 | 0 | 108 | 400 | 115 | 54 | 0 | 0 | 141 | 54 | 0 | 0 | 113 | 100 | 0 | 53 | 0 | 0 |  | 555 | 0 | 350 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 168 | 0 | 95 | 0 | 179 | 0 | 303 | 70 | 0 | 0 | 0 | 60 | 0 | 0 | 50 | 520 | 36 | 0 | 0 |  | 5578 | 2654 | 8232 | 3537 | 555 | 1826 | 1435 | 660 | 113 | 10 | 96 | 0 | 0 | 102.04
23:00 | 0 | 0 | 100 | 115 | 200 | 52 | 72 | 0 | 306 |  | 0 | 225 | 135 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 32 | 24 | 33 | 0 | 0 | 43 | 70 | 120 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 39 | 100 | 0 | 0 | 310 | 0 | 184 | 45 | 83 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 90 | 148 | 25 | 20 | 0 | 60 | 60 | 50 | 50 | 110 | 203 | 67 | 82 | 0 | 90 | 0 | 0 | 0 | 285 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 10 | 400 | 75 | 17 | 0 | 0 | 31 | 54 | 0 | 0 | 8 | 100 | 0 | 53 | 0 | 0 |  | 506 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 154 | 0 | 95 | 0 | 183 | 0 | 396 | 35 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 520 | 35 | 0 | 0 |  | 5139 | 2477 | 7616 | 3543 | 506 | 1942 | 762 | 660 | 113 | 0 | 90 | 0 | 0 | 102.03
24:00 | 0 | 0 | 100 | 115 | 200 | 51 | 72 | 0 | 306 |  | 0 | 225 | 135 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 32 | 24 | 33 | 0 | 0 | 43 | 70 | 120 | 0 | 0 | 205 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 40 | 100 | 0 | 0 | 310 | 0 | 182 | 45 | 88 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 33 | 21 | 86 | 148 | 25 | 20 | 0 | 60 | 60 | 50 | 50 | 130 | 208 | 67 | 82 | 0 | 90 | 0 | 0 | 0 | 290 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 400 | 45 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 100 | 0 | 17 | 0 | 0 |  | 505 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 168 | 0 | 93 | 0 | 194 | 0 | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 36 | 0 | 0 |  | 4901 | 2386 | 7287 | 3571 | 505 | 1925 | 457 | 630 | 113 | 0 | 86 | 0 | 0 | 102.02
KWH | 0 | 0 | 2398000 | 2835000 | 4829636 | 1136409 | 1469216 | 0 | 3607000 |  | 0 | 4659100 | 945425 | 383040 | 374640 | 254250 | 0 | 0 | 1856000 | 491520 | 727920 | 157920 | 0 | 0 | 0 | 6816 | 924840 | 290614 | 80938 | 376560 | 600000 | 670140 | 584400 | 512400 | 366804 | 0 | 1436902 | 1692000 | 2800000 | 0 | 0 | 4949256 | 0 | 0 | 0 |  | 12545 | 0 | 48906 | 0 | 150720 | 754080 | 400896 | 523200 | 2649448 | 0 | 0 | 7689000 | 0 | 4426000 | 953454 | 1946940 | 617256 | 321600 | 0 | 969068 | 0 | 0 | 132096 | 414360 | 78120 | 480000 | 473170 | 2101440 | 3404840 | 583680 | 384912 | 8150 | 989000 | 1424280 | 532200 | 815400 | 3343990 | 4857000 | 1447776 | 1244160 | 0 | 2527750 | 0 | 0 | 0 | 7258000 | 335880 | 24000 | 0 | 582109 | 0 | 0 | 194400 | 0 | 132480 | 119610 | 1604160 | 0 | 712581 | 9380000 | 1437600 | 1207512 | 0 | 20880 | 1236982 | 1046500 | 0 | 47880 | 1141560 | 2197440 | 0 | 1019520 | 238300 | 1343520 |  | 11890182 | 0 | 8425152 | 0 | 143040 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159825 | 283392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41760 | 0 | 465600 | 0 | 218970 | 0 | 0 | 3424000 | 0 | 0 | 0 | 0 | 4212100 | 0 | 1124090 | 0 | 4268382 | 0 | 9149400 | 524160 | 0 | 20256 | 0 | 556800 | 0 | 22267 | 585408 | 10952500 | 826750 | 0 | 448800 |  | 119403097 | 57742834 | 177145931 | 83486624 | 11890182 | 38558462 | 22987788 | 14376500 | 3128902 | 206826 | 2101440 | 409207 | 0
Fuel Cost | 0 | 0 | 3501080 | 4167450 | 5360895.96 | 1500059.88 | 2497667.2 | 0 | 3715210 |  | 0 | 5078419 | 1049421.75 | 2907273.6 | 2581269.6 | 2150955 | 0 | 0 | 3210880 | 3701145.6 | 6638630.4 | 1553932.8 | 0 | 0 | 0 | 61957.44 | 6751332 | 2246446.22 | 798048.68 | 282420 | 450000 | 0 | 0 | 0 | 3546994.68 | 0 | 387963.54 | 456840 | 5068000 | 0 | 0 | 5394689.04 | 0 | 0 | 0 |  | 0 | 0 | 474388.2 | 0 | 1311264 | 5972313.6 | 505128.96 | 1553904 | 3921183.04 | 0 | 0 | 5689860 | 0 | 4071920 | 1229955.66 | 2238981 | 697499.28 | 450240 | 0 | 1657106.28 | 0 | 0 | 1261516.8 | 526237.2 | 58590 | 840000 | 354877.5 | 15760800 | 3609130.4 | 5299814.4 | 488838.24 | 129911 | 1621960 | 2278848 | 947316 | 1272024 | 3812148.6 | 5051280 | 2852118.72 | 2376345.6 | 0 | 4373007.5 | 0 | 0 | 0 | 7330580 | 251910 | 18240 | 0 | 4400744.04 | 0 | 0 | 1010880 | 0 | 1303603.2 | 1398240.9 | 13073904 | 0 | 5023696.05 | 8723400 | 13110912 | 11410988.4 | 0 | 0 | 9351583.92 | 9115015 | 0 | 477842.4 | 9783169.2 | 14634950.4 | 0 | 0 | 0 | 0 |  | 68487448.32 | 0 | 8846409.6 | 0 | 1124294.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 247728.75 | 2765905.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404654.4 | 0 | 893952 | 0 | 165760.29 | 0 | 0 | 18558080 | 0 | 0 | 0 | 0 | 5559972 | 0 | 1686135 | 0 | 4994006.94 | 0 | 9057906 | 5472230.4 | 0 | 192229.44 | 0 | 4320768 | 0 | 246050.35 | 4326165.12 | 48081475 | 0 | 0 | 0 |  | 268167149.88 | 185431171.93 | 453598321.81 | 95174573.67 | 68487448.32 | 45306697.97 | 157581920.06 | 66639555 | 844803.54 | 2028321 | 15760800 | 1774202.25 | 0
Yesterday Day Peak | 0 | 0 | 100 | 115 | 200 | 52 | 71 | 0 | 53 |  | 0 | 225 | 7 | 0 | 0 | 0 | 0 | 0 | 99 | 2 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 28 | 24 | 8 | 24 | 0 | 10 | 70 | 120 | 0 | 0 | 218 | 0 | 0 | 0 |  | 2 | 0 | 0 | 0 | 0 | 26 | 20 | 4 | 100 | 0 | 0 | 340 | 0 | 171 | 45 | 76 | 26 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 0 | 24 | 15 | 84 | 156 | 25 | 20 | 1 | 30 | 60 | 11 | 30 | 163 | 223 | 64 | 50 | 0 | 120 | 0 | 0 | 0 | 300 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 18 | 100 | 0 | 0 | 401 | 70 | 91 | 0 | 4 | 49 | 54 | 0 | 0 | 41 | 100 | 0 | 53 | 43 | 116 |  | 552 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 186 | 0 | 23 | 0 | 200 | 0 | 429 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 400 | 35 | 0 | 53 |  | 7373 | DayPeak
Yesterday Evening Peak | 0 | 0 | 100 | 115 | 200 | 51 | 71 | 0 | 304 | 0 | 0 | 225 | 110 | 100 | 64 | 30 | 0 | 0 | 97 | 95 | 66 | 32 | 0 | 0 | 0 | 0 | 54 | 35 | 17 | 19 | 25 | 25 | 24 | 33 | 52 | 0 | 44 | 70 | 120 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 64 | 50 | 20 | 16 | 100 | 0 | 0 | 310 | 0 | 223 | 45 | 75 | 26 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 33 | 21 | 108 | 163 | 25 | 20 | 0 | 60 | 60 | 50 | 50 | 110 | 215 | 67 | 82 | 0 | 90 | 0 | 0 | 0 | 280 | 16 | 0 | 0 | 145 | 0 | 0 | 40 | 0 | 31 | 0 | 100 | 0 | 105 | 404 | 115 | 54 | 0 | 0 | 140 | 54 | 0 | 17 | 106 | 100 | 0 | 53 | 0 | 0 |  | 560 | 0 | 370 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 171 | 0 | 92 | 0 | 182 | 0 | 409 | 70 | 0 | 0 | 0 | 113 | 0 | 0 | 111 | 550 | 36 | 0 | 0 |  | 9321 | EvPeak
Forecast for Evening | 0 | 0 | 100 | 115 | 200 | 52 | 78 | 0 | 360 | 0 | 0 | 225 | 150 | 100 | 100 | 55 | 0 | 0 | 100 | 100 | 100 | 150 | 100 | 0 | 0 | 50 | 54 | 55 | 55 | 19 | 25 | 33 | 24 | 33 | 52 | 0 | 90 | 70 | 120 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 0 |  | 102 | 100 | 100 | 50 | 20 | 20 | 135 | 0 | 0 | 360 | 0 | 225 | 45 | 90 | 30 | 25 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 172 | 165 | 25 | 22 | 0 | 60 | 60 | 51 | 44 | 163 | 255 | 66 | 86 | 0 | 145 | 0 | 0 | 0 | 320 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 90 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 45 | 90 | 0 |  |  | 631 | 16 | 410 | 0 | 115 | 220 | 0 | 0 | 30 | 60 | 40 | 0 | 30 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 0 | 0 | 50 | 52 | 33 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 | 0 | 95 | 100 | 220 | 0 | 413 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 660 | 35
Forecast for Day | 0 | 0 | 100 | 115 | 200 | 51 | 78 | 0 | 360 | 0 | 0 | 225 | 150 | 100 | 100 | 55 | 0 | 0 | 70 | 100 | 100 | 150 | 50 | 0 | 0 | 50 | 54 | 55 | 55 | 19 | 25 | 33 | 24 | 33 | 52 | 0 | 90 | 70 | 120 | 0 | 25 | 215 | 0 | 0 | 0 | 0 | 0 |  | 102 | 100 | 100 | 50 | 20 | 15 | 135 | 0 | 0 | 360 | 0 | 225 | 45 | 90 | 30 | 25 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 156 | 165 | 25 | 22 | 1.6 | 60 | 60 | 51 | 44 | 163 | 255 | 66 | 86 | 0 | 145 | 0 | 0 | 0 | 320 | 20 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 165 | 150 | 400 | 115 | 90 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 45 | 90 | 50 |  |  | 518 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 30 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 50 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 |  | 95 | 0 | 220 | 0 | 413 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 600 | 35
Generation at 08:00(Today) | 0 | 0 | 100 | 115 | 200 | 51 | 35 | 0 | 337 | 0 | 0 | 225 | 145 |  | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 16 | 25 | 32 | 24 |  | 4 | 0 | 28 | 70 | 120 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 20 | 10 | 100 | 0 | 0 | 315 | 0 | 193 | 26 | 90 | 14 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 5 | 33 | 15 | 70 | 164 | 25 | 17 | 1 | 60 | 60 | 22 | 20 | 163 | 205 | 67 | 30 | 0 | 140 | 0 | 0 | 0 | 310 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 336 | 5 | 11 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 9 | 10 | 0 | 0 | 410 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 164 | 0 | 12 | 0 | 190 | 0 | 396 | 17 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 400 | 37 | 0 | 0 | 0
199
| Minimum Generation |  | 5883 | 5:00
| Highest Generation |  | 9321 | 19:00
| Day Peak Generation |  | 7373 | 12:00
| Evening Peak Generation |  | 9321 | 19:00
| HVDC Max Flow |  | 724 | 18:00
| HVDC EvPeak Flow |  | 560 | 19:00
| Load factor L.F |  | 79.19%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-11-22
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-11-21 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7373 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6066 | MW
Evening Peak Generation : |  | 9321 | MW Hour : | 19:00 | Available Max Generation : |  | 14314 | MW
E.P. Demand (at gen end) : |  | 9321 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9600 | MW
Maximum Generation : |  | 9321 | MW Hour : | 19:00 | Reserve(Generation end) |  | 4714 | MW
Total Gen. (MKWH) : |  | 177.1459 | System Load Factor : | 79.19% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 45 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-11-22
Actual : | 101.96 | Ft.(MSL) , | Rule curve : | 106.9 | Ft.( MSL )
Gas Consumed : | Total = | 1018.56 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 140481271.64
: |  | Coal : | 66639555 | Oil : | 159610241.06 | Total : | 366731067.7
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3346.6933 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1133.7019 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1014.9826 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 916.8466 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 828.6931 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 668.715 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 379.522 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 172.3246 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 515.7193 |  |  | 0 | 0%
Total | 0 |  | 8977.1982 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 10) Sirajganj #1 CCPP STG
|  |  |  | 2) Baghabari-71,100 MW | 11)Ashuganj(S)-360 MW
|  |  |  | 3) Ghorasal Unit-1,2,3 | 12) Meghnaghat 450 MW GT-1
4) Ashuganj unit-4,5
5) Kaptai-2
6) Raozan #2
7) Siddirganj-335 MW
8) Haripur 412 MW
9) Chandpur-163 MW STG
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Khagrachari 132/33 kV T-2 transformer was under shut down from 09:57 to 12:04 for C/M.
b) Sylhet 33 kV Bus of 132/33 kV T2 transformer was under shut down from 08:16 to 15:48 due to |  |  |  |  | About 19 MW power interruption occurred under Sylhet S/S area
maintenance work by PBS |  |  |  |  | from08:16 to 15:48.
c) Shikolbaha-Dohajari 132KV Ckt-2 was under shut down from 12:25 to 16:18 for A/M.
d) Hathazari-Baroierhat 132KV Ckt-2 was shut down from 09:05 to 15:50 for A/M.
e) Bakulia 132/33 kV T-3 transformer was under shut down from 08:23 to 14:22 for A/M.
f) Tongi-Kabirpur 132 KV Ckt-2 was under shut down from 08:43 to 15:26 for A/M.
g) Valuka 132/33 kV T-1 transformer was under shut down from 08:48 to 17:13 for A/M.
h) B.Baria 132/33 kV T-1 transformer was under shut down from 09:02 to 15:48 for A/M.
i) Kulaura 132/33 kV T-1 transformer was under shut down from 08:54 to 16:39 for A/M.
j) Bibiyana 400/230 kV T01 transformer was under shut down from 08:56 to 16:07 for A/M.
k) Chandpur 132/33 kV T-2 transformer was under shut down from 08:39 to 18:00 for A/M.
l) Haripur-Meghnaghat 230 KV Ckt-2 was under shut down from 11:01 to 17:35 for A/M.
m) Rampura 132 kV Bus-1 was under shut down from 08:30 to 17:49 for A/M.
n) Kishorganj-Ashuganj 132 KV Ckt-2 was under shut down from 11:05 to 14:37 for A/M.
o) Jamalpur 132/33 kV T-4 transformer was under shut down from 09:28 to 13:55 for A/M.
p) Sherpur 132 kV Bus-coupler was under shut down from 09:10 to 16:55 for A/M.
q) Kishorganj-Mymensing 132 KV Ckt-2 was under shut down from 09:59 to 17:31 for A/M.
r) Ghorasal-Ashuganj 132KV Ckt-1 was under shut down from 10:09 to 18:11 for A/M.
s) Agrabad 132/33 kV T-1 transformer was under shut down from 09:18 to 10:51 for D/W.
t) Agrabad 132/33 kV T-2 transformer was under shut down from 10:59 to for D/W.
u) Hathazari-Madunaghat 132KV Ckt was under shut down from 10:13 to 13:55 for D/W.
v) Bheramara HVDC- Bheramara 230 kV S/S 230 KV Ckt-1 was under shut down from 08:25 to 15:03
A/M.
w) Rangpur-Barapukuria 132 KV Ckt-2 was under shut down from 09:00 to 16:58 for A/M.
x) Purbasadipur 132/33 kV T-2 transformer was under shut down from 08:18 to 16:02 for A/M.
y) Natore 132/33 kV T-4 transformer was under shut down from 08:37 to 15:33 for A/M.
z) Amnura 132/33 kV T-1 transformer was under shut down from 08:16 to 16:10 for A/M.
aa) Sirajgonj-Ashugonj 230 KV Ckt1 was under shut down from 09:14 to 16:52 for A/M.
ab) Goalpara 132 kV Bus-A was under shut down from 10:15 to 15:50 for A/M.
ac) Noapara 132 kV Bus-A was under shut down from 11:07 to 14:27 for A/M.
ad) Gollamari 132/33 kV T1 transformer was under shut down from 09:23 to for A/M.
ae) AES Haripur GT was synchronized at 09:03.
af) AES Haripur ST was synchronized at 12:26.
ag) Meghnaghat Summit GT-1 was synchronized at 11:28.
ah) Hathazari-Khulshi 132KV Ckt was under shut down from 14:30 to 16:30 for D/W.
ai) Cumilla(N) 132/33 kV T-4 transformer was under shut down from 14:44 to 15:44 due to red hot
maintenance at 33 kv Jangalia P/S feeder.
aj) Ashuganj-Shahjibazar 132 kV Ckt-3 tripped at 01:45(22/11/2020) from both end showing Dist.Z1,
L1L2L3 relay at Ashuganj end & Dist. Z2 relay at Shahjibazar.
ak) Manikganj-Kabirpur 132 kV Ckt-1 was shut down at 07:35(22/11/2020) for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-11-21 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 100 | 2398000 | Machin problem.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 115 | 2835000 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 4829636 | Machin problem.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 71 | 1469216
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 51 | 1136409 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 304 | 3607000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4659100 | GT-1 S/D due to Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 383040
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 110 | 945425 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 64 | 374640 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 30 | 254250 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 376560
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 97 | 1856000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 95 | 491520
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under Maintenance
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 66 | 727920 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 6816 | Reserve.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 924840
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 32 | 157920 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 290614 | Low demand
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 80938 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 50 | 1270140 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 24 | 584400 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 512400
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 52 | 366804
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 145 | 582109 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 31 | 132480 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 54 | 1207512 | Low demand
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 53 | 1019520 | Engine problem
| Manikgonj 162MW PP |  | IPP | 9*18 | 0 | 0 | 1343520
| Dhaka area Total |  |  |  | 5895 | 2227 | 34823729
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2800000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve.
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 119610
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 754080
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 114 | 3128902 | Unit-2 under maint
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4949256
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 48906 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1604160
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 400896
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 16 | 523200
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 64 | 150720 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 20880
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 140 | 1236982 | Transformer O/L
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1046500
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2197440
| Chattogram area Total |  |  |  | 2266 | 999 | 18981532
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 100 | 2649448
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas Shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 223 | 4426000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7689000 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 617256 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 321600 | Gas shortage
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 45 | 953454 | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 969068
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 105 | 712581 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 75 | 1946940 | ST Under maint
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve.
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 414360
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 78120
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 108 | 2101440 | Low demand
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 480000
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 132096 | Low demand
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 473170
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 47880 | Low demand
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 106 | 1141560
| Cumilla Area Total |  |  |  | 2980 | 1306 | 25153973
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 163 | 3404840 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 384912
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 25 | 583680 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 8150
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 40 | 194400
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1437600 | #REF!
| Mymensingh PV 50 MW Solar PP |  | IPP | 50 | 0 | 0 | 238300
| Mymensingh Area Total |  |  |  | 637 | 363 | 6251882
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 989000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1424280
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 3343990 | Frequency control
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 215 | 4857000 | Gas shortage
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 532200
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 815400
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 24000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 67 | 1447776 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1244160
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 90 | 2527750
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 335880
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7258000
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 404 | 9380000
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 0
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1484 | 34179436
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 560 | 11890182
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 49 | 143040 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 370 | 8425152 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Reserve.
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 70 | 524160 | Low demand
107 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1049 | 20982534
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 283392 | High Voltage
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 0 | 159825 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 92 | 1124090
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 550 | 10952500 | High Voltage
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 36 | 826750
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 0 | 0 | 448800 | Ontest.
| Barisal Area Total |  |  |  | 1054 | 726 | 13795357
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel Shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel Shortage
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Under maint.
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 171 | 4212100 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 182 | 4268382 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 409 | 9149400 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 465600
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Engine problem
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 218970
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 41760 | Low demand
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve.
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 20256 | Reserve.
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 111 | 585408
| Rajshahi Area Total |  |  |  | 2183 | 914 | 18961876
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 140 | 3424000 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 556800
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 22267
| Rangpur Area Total |  |  |  | 605 | 253 | 4003067
| Total |  |  |  | 19892 | 9321 | 177133386
| Eastern Grid Total |  |  |  | 13766 | 6379 | 119390552
| Western Grid Total |  |  |  | 6126 | 2942 | 57742834
| National Grid Total |  |  |  | 19892 | 9321 | 177133386
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-11-21
| (a) ENTIRE EASTERN GRID : |  | 6051 | MW | (b) ENTIRE WESTERN GRID : |  | 2650 | MW
| i) Dhaka area |  | 3294 | MW | i) Khulna area |  | 1032 | MW
| ii) Chittagong area |  | 1000 | MW | ii) Rajshahi area |  | 830 | MW
| iii) Comilla area |  | 746 | MW | iii) Barisal area |  | 230 | MW
| iv) Mymensingh area |  | 688 | MW | iv) Rangpur area |  | 558 | MW
| v) Sylhet area |  | 323 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8701 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 112 | 18:00 | Sherpur | 76 | 18:00 | Jhenida | 80 | 18:00
| Munsiganj | 88 | 20:00 | Srimongal | 27 | 18:00 | Bottail | 94 | 18:00
| Sonargaon | 53 | 0:00 | Shahjibazar | 86 | 18:30 | G.K Project | 36 | 18:00
| Shyampur | 172 | 13:00 | Fenchuganj | 34 | 19:30 | Faridpur | 134 | 0.75
| Bhulta | 149 | 22:00 | Kulawara | 32 | 19:30 | Madaripur | 67 | 0.8125
| Madanganj | 52 | 11:00 | Sylhet | 74 | 18:30 | Sariatpur | 42 | 19:30
| Shitalakhya | 102 | 11:00 | Chatak | 18 | 19:00 | Gopalganj | 59 | 18:00
| Rahim steel | 18 | 10:00 | Sunamganj | 29 | 21:00 | Bagerhat | 70 | 19:30
| Matuail | 69 | 12:00 | Biani Bazar | 40 | 18:30 | Mongla | 36 | 14:00
| Ghorasal | 61 | 18:30 | Comilla (S) | 108 | 18:00 | Satkhira | 71 | 0.75
| Narsingdi | 128 | 20:00 | Comilla(N) | 65 | 19:30 | Gallamari | 22 | 13:00
| Haripur (SBU) | 96 | 15:00 | Chandpur | 64 | 19:30 | Magura | 38 | 0.75
| Ullon | 57 | 18:00 | Feni | 77 | 20:00 | Norail | 30 | 18:00
| Hasnabad | 141 | 21:00 | Chowmuhani | 128 | 18:00 | Chuadanga | 62 | 18:00
| Magbazar | 71 | 18:00 | Ashuganj | 40 | 21:00 | Barisal(N) | 28 | 0.79167
| Maniknagar | 72 | 19:00 | Daudkandi | 90 | 20:00 | Barisal (S) | 72 | 0.75
| Bangabhaban | 16 | 11:00 | B.Baria | 102 | 19:00 | Patuakhali | 82 | 0.875
| Narinda | 76 | 14:00 | Ramganj | 66 | 20:00 | Bhandaria | 44 | 0.83333
| Dhanmondi | 107 | 13:00 | Chaddagram | 23 | 20:00 | Borhan Uddin | 34 | 18:00
| Lalbag | 77 | 13:00 | PHP | 8 | 15:00 | Ishurdi | 48 | 18:00
| Madartek | 53 | 18:00 | Madunaghat | 43 | 12:00 | Ruppur Paromanobik | 2 | 1:00
| Dhaka University |  |  | Hathazari | 76 | 0.75 | Natore | 81 | 18:00
| Fatullah | 34 | 0.5 | Khulshi | 168 | 0.79167 | Bogra | 115 | 18:30
| Mirpur | 87 | 18:00 | Halishahar | 115 | 0.5 | Noagaon | 86 | 20:00
| Kalyanpur | 72 | 18:00 | Baraulia | 143 | 0.58333 | Rajshahi | 96 | 19:00
| Gulshan | 76 | 13:00 | Sikalbaha | 22 | 0.75 | Rajshahi New | 9 | 18:00
| Uttara | 70 | 18:00 | Dohazari | 56 | 0.75 | C.Nawabganj | 50 | 20:00
| Uttara New | 25 | 18:00 | Cox'sbazar | 88 | 0.75 | Amnura | 28 | 18:00
| Kamrangirchar | 72 | 18:00 | Chandraghona | 22 | 0.75 | Pabna | 83 | 18:00
| Savar | 122 | 12:00 | Kaptai | 3.8 | 0.75 | Shahjadpur | 72 | 19:00
| Bhasantec | 112 | 18:00 | A. Khaer Stl. | 0 | 0.041667 | Serajganj | 54 | 18:30
| Agargaon | 51 | 13:00 | Bakulia | 93 | 0.75 | Niyamatpur | 38 | 19:00
| Satmosjid | 85 | 18:00 | Julda | 18 | 0.70833 | Joypurhat | 36 | 18:00
| Tongi | 86 | 0.77083 | TK chemical | 21 | 0.75 | Sherpur(Bogura) | 34 | 20:00
| Kabirpur | 200 | 18:00 | Modern Steel | 16 | 0.66667 | Mohastangor | 34 | 19:30
| Basundhara | 103 | 18:00 | Shahmirpur | 17 | 0.625 | Rangpur | 106 | 18:00
| Manikganj | 56 | 18:30 | Khagrachhari | 20 | 0.041667 | Lalmonirhat | 41 | 18:00
| Joydevpur | 113 | 18:00 | Matarbari | 30.5 | 0.75 | Saidpur | 86 | 18:30
| New Tongi | 82 | 12:00 | Baroiar Hat | 26 | 0.75 | Purbasadipur | 83 | 18:00
| Kodda | 196 | 15:00 | Rangamati | 8 | 0.5 | Thakurgaon | 60 | 18:00
| Dhamrai | 66 | 18:00 | Abul Khair 230 | 139 | 0.083333 | Palashbari | 79 | 18:30
| Rajendrapur | 78 | 18:00 | BSRM | 101 | 0.45833 | Barapukuria | 36 | 18:00
| Valuka | 82 | 18:00 | GPH Ispat | 78 | 0.77083 | Panchagar | 46 | 19:30
| Tangail | 136 | 18:00 | Goalpara | 18 | 0.33333 | Joldhaka | 24 | 18:30
| Mymensing | 156 | 19:00 | Central s/s | 84 | 18:00 | Kurigram | 38 | 18:00
| Kishorganj | 80 | 19:00 | Noapara | 46 | 18:00
| Netrokona | 77 | 18:00 | Jessore | 75 | 18:30
| Jamalpur | 93 | 18:00 | Benapol | 34 | 18:00
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-11-21 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 406 | 20:00 | 396 | 10:00 | Kaliakoir | 387 | 0.45833 | 372 | 0.45833
| Bheramara | 412 | 20:00 | 395 | 18:00 | Bhulta | 391 | 0.83333 | 366 | 0.45833
| Ashuganj(N) | 393 | 20:00 | 372 | 12:00 | Gopalganj | 412 | 0.45833 | 400 | 0.77083
| Payra | 417 | 20:00 | 409 | 18:30
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 232 | 23:00 | 230 | 1:00 | Comilla (N) | 240 | 20:00 | 226 | 11:00
| Ishurdi | 238 | 1:00 | 228 | 12:00 | Hathazari | 224 | 21:00 | 218 | 11:00
| Ashuganj | 331 | 5:00 | 226 | 11:00 | Megnaghat | 233 | 19:00 | 218 | 1:00
| Serajganj | 232 | 1:00 | 227 | 12:00 | Fenchuganj | 242 | 20:00 | 231 | 7:00
| Baghabari | 241 | 23:00 | 237 | 13:00 | Siddhirganj | 225 | 5:00 | 219 | 12:00
| Barapukuria | 231 | 22:00 | 226 | 12:00 | Maniknagar | 231 | 20:00 | 216 | 12:00
| Bogra | 230 | 22:00 | 222 | 13:00 | Agargaon | 228 | 18:00 | 214 | 12:00
| Rajshahi | 229 | 5:00 | 219 | 13:00 | Barisal | 250 | 18:00 | 243 | 6:00
| Khulna South | 234 | 22:00 | 217 | 12:00 | AKSML | 226 | 19:00 | 217 | 11:00
| Rampura | 230 | 19:00 | 221 | 10:00 | BSRM | 227 | 22:00 | 218 | 12:00
| Haripur | 230 | 19:30 | 219 | 12:00 | Bibiyana | 241 | 20:00 | 234 | 17:00
| Hasnabad | 226 | 20:00 | 214 | 15:00 | Bhulta | 234 | 19:00 | 220 | 17:00
| Shyampur | 230 | 20:00 | 220 | 12:00 | Ashuganj (S) | 236 | 19:30 | 224 | 11:00
| Aminbazar | 225 | 24:00 | 217 | 11:00 | Kaliakoir | 231 | 20:00 | 219 | 12:00
| Tongi | 228 | 18:00 | 215 | 12:00 | GPH | 225 | 20:00 | 217 | 5:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 140 | 20:00 | 130 | 11:00 | Hathazari | 137 | 0.8125 | 133 | 0.083333
| Munsiganj | 141 | 18:00 | 128 | 11:00 | Khulshi | 134 | 0.75 | 129 | 0.25
| Sonargaon | 137 | 20:00 | 127 | 11:00 | Halishahar | 136 | 0.75 | 130 | 0.25
| Shyampur | 137 | 18:00 | 129 | 12:00 | Baraulia | 136 | 0.75 | 131 | 0.20833
| Bhulta | 132 | 20:00 | 124 | 12:00 | Sikalbaha | 137 | 0.77083 | 129 | 0.16667
| Madanganj | 134 | 4:00 | 130 | 10:00 | Dohazari | 135 | 0.375 | 127 | 0.625
| Shitalakhya | 142 | 18:00 | 129 | 12:00 | Cox'sbazar | 129 | 0.375 | 120 | 0.8125
| Rahim steal | 138 | 18:30 | 130 | 10:00 | Chandraghona | 136 | 0.75 | 132 | 0.20833
| Matuail | 140 | 20:00 | 130 | 11:00 | Kaptai | 135 | 0.041667 | 132 | 0.70833
| Ghorasal | 137 | 1:00 | 135 | 11:00 | A. Khaer Stl. | 135 | 0.041667 | 129 | 0.70833
| Narsinghdi | 135 | 18:00 | 126 | 11:00 | Bakulia | 135 | 0.77083 | 129 | 0.20833
| Haripur (SBU) | 140 | 19:00 | 129 | 12:00 | Julda | 136 | 0.041667 | 130 | 0.25
| Ullon | 136 | 19:00 | 126 | 11:00 | TK Chemical | 136 | 0.75 | 131 | 0.70833
| Hasnabad | 137 | 6:00 | 127 | 11:00 | Modern Steel | 135 | 0.041667 | 130 | 0.45833
| Magbazar | 136 | 20:00 | 126 | 12:00 | Shahmirpur | 136 | 0.75 | 129 | 0.25
| Maniknagar | 136 | 19:30 | 130 | 11:00 | Khagrachhari | 135 | 0.041667 | 132 | 0.20833
| Bangabhaban | 136 | 19:30 | 130 | 11:00 | Matarbari | 131 | 0.375 | 124 | 0.66667
| Narinda | 136 | 19:30 | 130 | 11:00 | Baroiar Hat | 136 | 0.75 | 130 | 0.041667
| Dhanmondi | 136 | 19:00 | 126 | 11:00 | Rangamati | 135 | 0.29167 | 132 | 0.45833
| Lalbag | 138 | 6:00 | 130 | 12:00 | Goalpara S/S | 138 | 19:00 | 127 | 12:00
| Madartek | 135 | 19:00 | 126 | 12:00 | Khulna Central S/S | 137 | 18:30 | 125 | 0.5
| Dhaka University |  |  |  |  | Noapara | 134 | 19:00 | 123 | 0.5
| Fatuiiah | 138 | 20:00 | 130 | 11:00 | Jessore | 131 | 1:00 | 121 | 0.5
| Mirpur | 138 | 6:00 | 131 | 12:00 | Benapol | 132 | 0.95833 | 122 | 0.5
| Kalyanpur | 138 | 6:00 | 134 | 12:00 | Jhenida | 131 | 1:00 | 123 | 0.5
| Gulshan | 134 | 19:00 | 126 | 11:00 | Bottail | 135 | 0.125 | 130 | 0.5
| Uttara | 137 | 6:00 | 131 | 12:00 | G.K Project | 140 | 0.95833 | 136 | 0.5
| Uttara New | 137 | 6:00 | 131 | 11:00 | Faridpur | 135 | 0.125 | 130 | 0.77083
| Kamrangirchar | 137 | 6:00 | 126 | 12:00 | Madaripur | 140 | 0.16667 | 133 | 0.8125
| Savar | 140 | 6:00 | 132 | 12:00 | Shariyatpur S/S | 139 | 2:00 | 132 | 0.8125
| Bhasantec | 136 | 6:00 | 129 | 12:00 | Gopalganj | 139 | 0.125 | 133 | 0.77083
| Agargaon | 137 | 6:00 | 131 | 12:00 | Bagerhat | 137 | 22:00 | 124 | 0.5
| Satmosjid | 137 | 6:00 | 130 | 12:00 | Mongla | 136 | 22:00 | 122 | 0.5
| Tongi | 140 | 18:00 | 132 | 15:00 | Satkhira | 135 | 22:00 | 125 | 12:00
| Kabirpur | 131 | 1:00 | 124 | 16:00 | Gallamari | 139 | 0.91667 | 126 | 0.5
| Basundhara | 136 | 21:00 | 126 | 11:00 | Magura | 132 | 3:00 | 125 | 0.54167
| Manikganj | 140 | 20:00 | 133 | 14:00 | Norail | 131 | 0.16667 | 122 | 0.5
| Joydevpur | 139 | 18:00 | 133 | 16:00 | Chuadanga | 128 | 7:00 | 119 | 0.5
| New Tongi | 139 | 20:00 | 131 | 12:00 | Barisal(N) | 141 | 22:00 | 137 | 8:00
| Kodda | 140 | 18:00 | 126 | 14:00 | Barisal (S) | 139 | 0.041667 | 136 | 0.29167
| Dhamrai | 130 | 1:00 | 124 | 12:00 | Patuakhali(S) | 140 | 0.45833 | 133 | 0.77083
| Rajendrapur | 136 | 21:00 | 127 | 12:00 | Bhandaria | 139 | 0.45833 | 125 | 0.58333
| Valuka | 130 | 9:00 | 118 | 15:00 | Ishurdi | 138 | 1:00 | 133 | 12:00
| Tangail | 132 | 5:00 | 126 | 12:00 | Ruppur Paromanobik | 138 | 1:00 | 134 | 12:00
| Mymensing | 132 | 22:00 | 120 | 17:00 | Natore | 138 | 1:00 | 133 | 13:00
| Kishorganj | 132 | 9:00 | 123 | 3:00 | Bogra | 138 | 19:30 | 133 | 12:00
| Netrokona | 130 | 8:00 | 119 | 15:00 | Noagaon | 134 | 4:00 | 128 | 12:00
| Jamalpur | 136 | 22:00 | 124 | 16:00 | Rajshahi | 138 | 1:00 | 134 | 12:00
| Sherpur | 135 | 18:00 | 123 | 15:00 | Rajshahi New | 140 | 2:00 | 134 | 13:00
| Srimongal | 138 | 9:00 | 134 | 17:00 | C.Nawabganj | 138 | 1:00 | 133 | 13:00
| Shahjibazar | 137 | 9:00 | 133 | 1:00 | Amnura | 137 | 1:00 | 133 | 13:00
| Fenchuganj | 138 | 7:00 | 134 | 16:00 | Pabna | 138 | 1:00 | 133 | 10:00
| Khulawara | 137 | 19:00 | 134 | 17:00 | Shahjadpur | 143 | 4:00 | 138 | 10:00
| Sylhet | 136 | 7:00 | 131 | 16:00 | Serajganj | 135 | 1:00 | 131 | 12:00
| Chatak | 135 | 4:00 | 130 | 16:00 | Niyamatpur | 134 | 1:00 | 126 | 12:00
| Sunamganj | 135 | 6:00 | 130 | 17:00 | Joypurhat | 137 | 3:00 | 129 | 12:00
| Biani Bazar | 135 | 1:00 | 130 | 17:00 | Sherpur(Bogura) | 138 | 1:00 | 132 | 13:00
| Comilla(s) | 129 | 5:00 | 125 | 17:00 | Mohastangor | 137 | 20:00 | 131 | 12:00
| Comilla(n) | 141 | 19:00 | 135 | 11:00 | Rangpur | 129 | 4:00 | 121 | 13:00
| Chandpur | 136 | 21:00 | 132 | 15:00 | Lalmonirhat | 128 | 3:00 | 123 | 12:00
| Feni | 140 | 18:00 | 132 | 11:00 | Saidpur | 128 | 2:00 | 121 | 13:00
| Chowmuhani | 136 | 18:00 | 130 | 23:00 | Purbasadipur | 126 | 3:00 | 118 | 18:00
| Ashuganj | 136 | 9:00 | 131 | 16:00 | Thakurgaon | 128 | 5:00 | 117 | 18:00
| Daudkandi | 138 | 19:30 | 130 | 11:00 | Palashbari | 132 | 2:00 | 125 | 13:00
| B.Baria | 132 | 22:00 | 129 | 16:00 | Barapukuria | 130 | 3:00 | 126 | 12:00
| Ramganj | 132 | 18:00 | 126 | 17:00 | Panchagar | 126 | 3:00 | 115 | 18:00
| Chaddagram | 139 | 18:00 | 132 | 3:00 | Joldhaka | 129 | 2:00 | 119 | 18:00
| PHP | 138 | 18:00 | 131 | 16:00 | Kurigram | 128 | 2:00 | 121 | 13:00
| Madanhat | 139 | 19:00 | 132 | 5:00

## L-Curve
Date | 2020-11-21
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 285 | 4901 | 2386 | 7287 |  |  |  | QF-LDC-11
0:30 | 290 | 4724.5 | 2265.5 | 6990 | Date: | 2020-11-21
1:00 | 295 | 4548 | 2145 | 6693
1:30 | 303 | 4433.5 | 2136.5 | 6570
2:00 | 311 | 4319 | 2128 | 6447
2:30 | 356.5 | 4235.5 | 2112 | 6347.5 | [5 empty] | Gen. at Eve. Peak | 9321 | 9321 MW (19:00 )
3:00 | 402 | 4152 | 2096 | 6248 | [6 empty] | 19:00
3:30 | 413.5 | 4018.5 | 2105 | 6123.5 | [5 empty] | Gen. at Day Peak | 7373 | 7373 MW (12:00 )
4:00 | 425 | 3885 | 2114 | 5999 | [6 empty] | 12:00
4:30 | 422.5 | 3822 | 2119 | 5941 | [5 empty] | Highest Generation | 9321
5:00 | 420 | 3759 | 2124 | 5883 | [6 empty] | 19:00
5:30 | 407 | 3893 | 2145.5 | 6038.5
6:00 | 394 | 4027 | 2167 | 6194
6:30 | 322.5 | 4093.5 | 2158.5 | 6252
7:00 | 251 | 4160 | 2150 | 6310
7:30 | 219 | 4321.5 | 2151.5 | 6473
8:00 | 187 | 4483 | 2153 | 6636
8:30 | 213.5 | 4610 | 2119 | 6729
9:00 | 240 | 4737 | 2085 | 6822
9:30 | 297 | 4716 | 2063.5 | 6779.5
10:00 | 354 | 4695 | 2042 | 6737
10:30 | 433 | 4717.5 | 2167.5 | 6885
11:00 | 512 | 4740 | 2293 | 7033
11:30 | 493.5 | 4868.5 | 2334.5 | 7203
12:00 | 475 | 4997 | 2376 | 7373
12:30 | 385 | 5142 | 2341 | 7483
13:00 | 295 | 5287 | 2306 | 7593
13:30 | 285 | 5172.5 | 2276 | 7448.5
14:00 | 275 | 5058 | 2246 | 7304
14:30 | 359.5 | 5069.5 | 2275.5 | 7345
15:00 | 444 | 5081 | 2305 | 7386
15:30 | 486 | 4953.5 | 2314.5 | 7268
16:00 | 528 | 4826 | 2324 | 7150
16:30 | 515.5 | 4901 | 2416 | 7317
17:00 | 503 | 4976 | 2508 | 7484
17:30 | 340.5 | 5543 | 2805 | 8348
18:00 | 178 | 6110 | 3102 | 9212
18:30 | 116.5 | 6244.5 | 3022 | 9266.5
19:00 | 55 | 6379 | 2942 | 9321
19:30 | 47 | 6232 | 2928 | 9160
20:00 | 45 | 6184 | 2912 | 9096 |  |  |  | Executive Engineer
20:30 | 105.5 | 6028 | 2920 | 8948 |  |  |  | Network Operation Division
21:00 | 166 | 5872 | 2928 | 8800
21:30 | 149 | 5725 | 2791 | 8516
22:00 | 132 | 5578 | 2654 | 8232 |  |  |  |  | Page 6 of 7
22:30 | 191 | 5358.5 | 2565.5 | 7924
23:00 | 250 | 5139 | 2477 | 7616
23:30 | 267.5 | 5020 | 2431.5 | 7451.5
24:00 | 285 | 4901 | 2386 | 7287
9321 MW (19:00 )
7373 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-11-21 |  | Energy | 177145931
[10 empty] | 2020-11-21 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3571 | 505 | 1925 | 762 | 630 | 113 | 0 | 0 | 86
0:30 | 3474 | 457.5 | 1688 | 669.5 | 630 | 136.5 | 0 | 0 | 87 | Date: | 2020-11-21
1:00 | 3377 | 410 | 1451 | 577 | 630 | 160 | 0 | 0 | 88
1:30 | 3416 | 410 | 1456 | 421 | 620 | 160 | 0 | 0 | 87 | [7 empty] | Total Energy | 177.1459 | Total Energy Gen 177.146 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 177.146 MKWHr
2:00 | 3455 | 410 | 1461 | 265 | 610 | 160 | 0 | 0 | 86 | [7 empty] | Energy not Served | 0
2:30 | 3436 | 410 | 1433 | 213.5 | 610 | 160 | 0 | 0 | 85 | [7 empty] | Energy Requirement | 177.1459
3:00 | 3417 | 410 | 1405 | 162 | 610 | 160 | 0 | 0 | 84
3:30 | 3365 | 410 | 1345.5 | 150 | 610 | 160 | 0 | 0 | 83 | [6 empty] | Shortage
4:00 | 3313 | 410 | 1286 | 138 | 610 | 160 | 0 | 0 | 82
4:30 | 3308.5 | 410 | 1269.5 | 112 | 600 | 160 | 0 | 0 | 81
5:00 | 3304 | 410 | 1253 | 86 | 590 | 160 | 0 | 0 | 80
5:30 | 3386 | 410 | 1285.5 | 120 | 600 | 159 | 0 | 0 | 78
6:00 | 3468 | 410 | 1318 | 154 | 610 | 158 | 0 | 0 | 76
6:30 | 3436 | 410 | 1352.5 | 224 | 595 | 158 | 0 | 0 | 74 |  |  |  |  | Coal
7:00 | 3404 | 410 | 1387 | 294 | 580 | 158 | 0 | 0 | 72
7:30 | 3421.5 | 410 | 1414.5 | 403 | 579 | 158 | 0 | 0 | 75 |  |  |  | Oil |  |  |  | ,
8:00 | 3439 | 410 | 1442 | 512 | 578 | 158 | 0 | 0 | 78
8:30 | 3385 | 410.5 | 1418 | 670.5 | 578.5 | 158 | 0 | 0 | 79
9:00 | 3331 | 411 | 1394 | 829 | 579 | 158 | 0 | 0 | 80
9:30 | 3334.5 | 410.5 | 1388 | 777 | 579.5 | 158 | 0 | 0 | 81
10:00 | 3338 | 410 | 1382 | 725 | 580 | 158 | 0 | 0 | 82
10:30 | 3375.5 | 481 | 1462 | 737.5 | 559 | 119 | 0 | 0 | 85
11:00 | 3413 | 552 | 1542 | 750 | 538 | 80 | 0 | 0 | 88
11:30 | 3487 | 552 | 1549.5 | 840.5 | 539 | 80 | 0 | 0 | 86
12:00 | 3561 | 552 | 1557 | 931 | 540 | 80 | 0 | 0 | 84
12:30 | 3528.5 | 552 | 1595 | 1038.5 | 540 | 80 | 0 | 0 | 83
13:00 | 3496 | 552 | 1633 | 1146 | 540 | 80 | 0 | 0 | 82
13:30 | 3496 | 552 | 1633 | 1146 | 540 | 80 | 0 | 0 | 82
14:00 | 3496 | 552 | 1633 | 1146 | 540 | 80 | 0 | 0 | 82
14:30 | 3389 | 552.5 | 1667.5 | 1132.5 | 540 | 80 | 0 | 0 | 83
15:00 | 3282 | 553 | 1702 | 1119 | 540 | 80 | 0 | 0 | 84
15:30 | 3290.5 | 552.5 | 1687 | 997 | 540 | 97 | 0 | 0 | 84
16:00 | 3299 | 552 | 1672 | 875 | 540 | 114 | 0 | 0 | 84
16:30 | 3382 | 552 | 1668.5 | 942 | 555 | 114 | 5 | 0 | 91
17:00 | 3465 | 552 | 1665 | 1009 | 570 | 114 | 10 | 0 | 98
17:30 | 3509.5 | 638 | 1749 | 1591 | 605 | 114 | 38 | 0 | 103
18:00 | 3554 | 724 | 1833 | 2173 | 640 | 114 | 66 | 0 | 108
18:30 | 3591 | 642 | 1866 | 2223 | 665 | 114 | 57.5 | 0 | 108
19:00 | 3628 | 560 | 1899 | 2273 | 690 | 114 | 49 | 0 | 108
19:30 | 3597 | 560 | 1955 | 2108 | 690 | 114 | 32 | 0 | 104
20:00 | 3567 | 560 | 1919 | 2110 | 690 | 114 | 32 | 0 | 104
20:30 | 3568 | 557.5 | 1926 | 1957.5 | 690 | 114 | 32 | 0 | 103
21:00 | 3569 | 555 | 1933 | 1805 | 690 | 114 | 32 | 0 | 102
21:30 | 3553 | 555 | 1879.5 | 1620 | 675 | 113.5 | 21 | 0 | 99
22:00 | 3537 | 555 | 1826 | 1435 | 660 | 113 | 10 | 0 | 96
22:30 | 3540 | 530.5 | 1884 | 1098.5 | 660 | 113 | 5 | 0 | 93
23:00 | 3543 | 506 | 1942 | 762 | 660 | 113 | 0 | 0 | 90
23:30 | 3557 | 505.5 | 1933.5 | 762 | 645 | 113 | 0 | 0 | 88 | Max Temp. in Dhaka |  | 27.2° C
24:00 | 3571 | 505 | 1925 | 762 | 630 | 113 | 0 | 0 | 86
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 177.146 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 177.146 MKWHr
Note on W13: Author:

## Generation
g | 2020-11-21
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 90 | 90 | 90 | 90 | 90 | 88 | 88 | 88 | 88 | 88 | 10 | 10 | 10 | 10 | 10 | 44 | 44 | 44 |  | 44 | 44 | 44 | 44 | 43 | 43 | 43 | 1436902
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1692000
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 2 | 8 | 13 | 15 | 17 | 18 | 17 | 14 | 9 | 3 | 0 | [9 empty] | 119610
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 204 | 203 | 204 | 204 | 206 | 205 | 207 | 206 | 217 | 210 | 218 | 204 | 204 | 206 | 216 | 204 | 204 |  | 204 | 203 | 204 | 204 | 203 | 203 | 205 | 4949256
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 34 |  | 17 | [6 empty] | 48906
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 61 | 61 | 62 | 37 | 37 | 77 | 40 | 40 | 90 | 40 | 97 | 99 | 97 | 39 | 40 | 40 | 100 | 94 |  | 97 | 100 | 99 | 100 | 97 | 97 | 97 | 1856000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [16 empty] | 4 | 110 |  | 145 | 145 | 145 | 60 |  |  |  | 582109
19 | Ashuganj 195MW PP (APSCL-United) | 26 | 26 | 26 | 26 | 8 | 8 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 953454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 102 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 88 | 100 | 101 | 100 | 100 | 99 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2398000
23 | Ghorasal TPP Unit-5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2835000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4829636
26
28 | Ashuganj TPP Unit- 3 | 100 | 100 | 100 | 100 | 100 | 135 | 135 | 135 | 135 | 115 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2649448
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 29 | 29 | 29 | 29 | 29 | 26 | 26 | 26 | 26 | 26 | 23 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 29 | 29 | 29 | 29 | 617256
33 | Ashuganj 225 MW CCPP | 180 | 193 | 180 | 186 | 195 | 196 | 182 | 195 | 181 | 170 | 172 | 171 | 171 | 170 | 171 | 171 | 171 | 171 |  | 223 | 194 | 182 | 182 | 182 | 184 | 182 | 4426000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 310 | 325 | 310 | 265 | 290 | 305 | 300 | 315 | 270 | 305 | 270 | 340 | 310 | 275 | 275 | 300 | 320 | 315 |  | 310 | 320 | 310 | 310 | 310 | 310 | 310 | 7689000
35 | Ashuganj 55 MW PP (Precision) | 15 | 15 | 15 | 5 | 5 | 5 | 25 | 25 | 25 | 20 | 20 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 321600
36 | Chandpur 150 MW CCPP | 85 | 85 | 80 | 85 | 82 | 85 | 85 | 84 | 85 | 85 | 85 | 76 | 76 | 84 | 75 | 86 | 80 | 76 |  | 75 | 85 | 75 | 75 | 75 | 83 | 88 | 1946940
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 4659100
41 | Haripur 360MW CCPP(HPL) | [9 empty] | 52 | 52 | 53 | 176 | 304 | 332 | 359 | 304 | 304 |  | 304 | 304 | 304 | 307 | 306 | 306 | 306 | 3607000
42 | RPCL 210MW CCPP | 165 | 164 | 163 | 164 | 163 | 163 | 163 | 165 | 164 | 160 | 159 | 156 | 159 | 125 | 95 | 95 | 95 | 123 |  | 163 | 147 | 147 | 146 | 148 | 148 | 148 | 3404840
43 | Mymensingh PV 50 MW Solar PP | [6 empty] | 3 | 9 | 21 | 39 | 44 | 43 | 39 | 33 | 14 | 10 | 1 | [9 empty] | 238300
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 45 | 50 | 50 | 50 | 45 | 55 |  | 60 | 60 | 59 | 60 | 57 | 60 | 60 | 989000
45 | Fenchugonj CCPP Phase-2 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1424280
46 | Shajibazar 330 MW CCPP | 220 | 215 | 219 | 217 | 217 | 221 | 216 | 217 | 216 | 230 | 220 | 223 | 225 | 224 | 223 | 220 | 210 | 215 |  | 215 | 210 | 210 | 210 | 200 | 203 | 208 | 4857000
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 40 | 67 | 67 | 67 | 67 | 67 | 66 | 64 | 64 | 64 | 65 | 64 | 67 | 67 |  | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 1447776
48 | Shahjibazar 86MW PP (Shahjibazar) | 10 | 10 | 10 | 10 | 10 | 44 | 44 | 44 | 82 | 82 | 82 | 50 | 50 | 50 | 50 | 20 | 20 | 79 |  | 82 | 82 | 81 | 81 | 82 | 82 | 82 | 1244160
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 145 | 145 | 145 | 144 | 100 | 101 | 90 | 90 | 90 | 90 | 90 | 120 | 120 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2527750
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [26 empty] | 0
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 0 | 0 | 0 | 0 | 0 | [19 empty] | 24000
55 | Fenchugonj 51 MW PP (Barakatullah) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 44 |  | 50 | 50 | 53 | 53 | 53 | 50 | 50 | 532200
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 8 | 16 |  | 16 | 16 | 16 | 20 | 20 | 20 | 16 | 335880
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 280 | 275 | 270 | 280 | 300 | 270 | 300 | 290 | 300 | 310 | 300 | 305 | 285 | 300 | 280 | 300 | 290 |  | 280 | 310 | 280 | 270 | 270 | 285 | 290 | 7258000
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 10 | 55 |  | 17 | [6 empty] | 80938
59 | Anlima Energy Ltd. | [11 empty] | 2 | 9 | [13 empty] | 12545
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 400896
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 |  |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 376560
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 0 |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 384912
63 | Impoprt (Tripura) | 88 | 86 | 84 | 82 | 80 | 76 | 72 | 78 | 80 | 82 | 88 | 84 | 82 | 80 | 84 | 84 | 98 | 108 |  | 108 | 104 | 104 | 102 | 96 | 90 | 86 | 2101440
64 | Malancha, Ctg. EPZ (United) | 30 | 30 | 30 | 30 | 39 | 39 | 39 | 14 | 8 | 4 | 6 | 4 | 14 | 8 | 6 | 8 | 10 | 12 |  | 16 | 23 | 27 | 32 | 37 | 39 | 40 | 523200
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 0 |  |  | 15 | 21 | 21 | 21 | 21 | 19 | 19 | 19 | 19 | 19 | 19 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 414360
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 8 | 0 | [15 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 78120
67 | Jangalia 33MW PP (Summit) | 21 | 20 | 8 | 8 | 8 | 8 | 20 | 20 | 20 | 24 | 24 | 24 |  |  |  |  | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 480000
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 13 | 10 | 15 | 18 | 18 | 15 | 15 | 15 | 18 | 18 | 18 | 18 | 18 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 473170
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 32 | 24 | 24 | 24 | 28 | 28 | 28 | 28 | 28 | 28 | 26 | 26 | 26 | 28 | 18 |  | 25 | 32 | 32 | 32 | 32 | 32 | 32 | 670140
71 | Maona 33 MW PP(Summit) | 24 | 24 | 24 | 24 | 20 | 20 | 20 | 20 | 20 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 584400
72 | Rupganj 33 MW PP(Summit) | 0 | 33 | 33 | 33 | 33 | 33 | 25 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 17 | 33 |  | 33 | 26 | 31 | 31 | 33 | 33 | 33 | 512400
73 | Ghorashal 108MW PP (Regent) | 51 | 51 | 51 | 51 | 12 | 12 | 51 | 51 | 51 | 51 | 52 | 52 | 52 | 51 | 52 | 52 | 52 | 51 |  | 51 | 52 | 52 | 52 | 52 | 52 | 51 | 1136409
| Feni Lanka Power | [17 empty] | 66 |  | 17 | [6 empty] | 47880
| Chowmuhani 113 MW | [7 empty] | 5 | 26 | 26 | 26 | 41 | 97 | 105 | 113 | 26 | 28 | 87 |  | 106 | 113 | 113 | 113 | 113 | 8 |  | 1141560
| Manikgonj 162MW PP |  |  | 0 | 13 | 31 | 99 | 96 | 92 | 93 | 110 | 110 | 116 | 147 | 147 | 128 | 110 | 46 | [9 empty] | 1343520
77 | Siddhirganj 100 PP(Dutch Bangla) | [11 empty] | 2 | 24 | 32 | 16 | 16 | 30 | 70 |  | 95 | 98 | 97 | 50 |  |  |  | 491520
78 | Gazipur 52 MW PP | [9 empty] | 24 | 24 | 24 | 24 | 8 | 20 | 33 | 33 | 43 |  | 52 | 52 | 52 |  |  |  |  | 366804
79 | Kodda 150MW PP | [16 empty] | 10 | 32 |  | 32 | 32 | 32 | 32 | 10 |  |  | 157920
80 | Jamalpur 95 MW PP(Powerpac) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 17 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 583680
81 | Jangalia 52 MW PP (Lakdanavi) | [17 empty] | 25 |  | 52 | 16 | 16 | 16 |  |  |  | 132096
| Gazipur 100 MW PP | [6 empty] | 6 | 27 | 80 | 91 | 91 | 91 | 91 | 72 | 91 | 91 | 91 | 91 |  | 54 | 54 | 54 | 54 | 54 | 17 | 0 | 1207512
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 3 | 4 | 4 | 4 | 3 | 1 | 0 | 0 | [10 empty] | 20880
| Jodiac Power | 54 | 54 | 17 | 0 |  |  | 23 | 34 | 49 | 54 | 54 | 54 | 54 | 54 | 54 | 34 | 34 | 46 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1046500
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | [8 empty] | 14 |  |  |  | 14 | 15 | 15 | 15 | 15 | 42 |  | 64 | 64 | 64 | 32 | 15 |  |  | 374640
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP(Summit) | [11 empty] | 7 | 8 | 10 | 20 | 50 | 70 | 90 |  | 110 | 120 | 125 | 128 | 128 | 135 | 135 | 945425
87 | Meghnaghat 100 MW(IEL) | [12 empty] | 11 | 16 | 16 |  | 6 | 50 |  | 100 | 100 | 100 | 55 |  |  |  | 383040
| Meghnaghat 104 MW PP (OPCL) | 90 | 0 |  |  |  |  | 9 | 38 | 54 | 54 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 17 | 1019520
88 | Ghorashal 78.5 MW PP(MAX) | 74 | 74 | 73 | 20 | 20 | 30 | 30 | 60 | 73 | 73 | 72 | 71 | 70 | 71 | 70 | 40 | 40 | 60 |  | 71 | 72 | 72 | 72 | 72 | 72 | 72 | 1469216
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [26 empty] | 0
92 | Fenchuganj 44MW (Energyprima) | 10 | 10 | 10 | 10 | 10 | 10 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 43 |  | 50 | 50 | 50 | 50 | 47 | 50 | 50 | 815400
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 7 | 7 | 7 | 11 | 37 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 51 | 51 | 51 | 51 | 43 | 51 | 51 | 969068
94 | Gagnagar 102 MW PP (Digital Power) | [6 empty] | 10 | 50 | 24 | 24 | 24 | 32 | 66 | 66 | 66 | 24 | 24 | 50 |  | 66 | 66 | 66 | 32 | 32 | 7 |  | 727920
95 | Patenga 50MW PP (Baraka) | 50 | 0 |  |  |  |  | 6 | 47 | 45 | 25 | 25 | 26 | 39 | 44 | 44 | 19 | 19 | 41 |  | 50 | 50 | 50 | 50 | 50 | 50 | 19 | 754080
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 5 | 46 |  | 64 | 25 | 25 |  |  |  |  | 150720
97 | katpotti 52 MW | [26 empty] | 6816
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | [7 empty] | 2 | 15 |  |  |  | 15 | 15 | 15 | 15 | 16 | 30 |  | 30 | 30 | 30 | 30 |  |  |  | 254250
100 | Manikganj 55 MW PP (Northern) | [11 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 55 |  | 35 | 35 | 35 | 35 | 17 |  |  | 290614
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 163 | 130 | 130 | 100 | 100 | 130 | 163 | 163 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 130 | 3343990
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 0 | [10 empty] | 8150
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 0 |  |  |  |  | 35 | 54 | 54 | 17 | 17 | 54 | 54 | 54 | 54 | 35 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 17 | 924840
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [16 empty] | 5 | 46 |  | 40 | 24 | 24 | 24 | 24 |  |  | 194400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [9 empty] | 10 | 15 | 15 | 15 | 0 |  |  |  | 28 |  | 31 | [6 empty] | 132480
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 70 | 20 | 0 |  |  | 10 | 15 | 50 | 50 | 50 | 100 | 100 | 100 | 100 | 50 | 50 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 45 | 1604160
116 | Chandpur 200MW (Desh energy) | [26 empty] | 0
117 | Ashuganj 150MW PP (Midland) | [6 empty] | 3 | 20 | 40 | [7 empty] | 13 | 78 |  | 105 | 108 | 108 | 108 | 108 | 10 |  | 712581
118 | Bibiyana-III 400 MW CCPP | 398 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 350 | 352 | 396 | 401 | 401 | 351 | 352 | 352 | 400 | 400 |  | 404 | 400 | 400 | 400 | 400 | 400 | 400 | 9380000
| Jamalpur 115 MW PP (United) | 16 | 16 | 0 |  |  |  | 8 | 10 | 58 | 65 | 65 | 70 | 85 | 55 | 55 | 55 | 67 | 115 |  | 115 | 115 | 115 | 115 | 115 | 75 | 45 | 1437600
| Anwara 300 MW PP (United) | 53 | 0 |  |  |  |  | 16 | 16 | 50 | 16 | 16 | 49 | 49 | 51 | 53 | 35 | 34 | 135 |  | 140 | 140 | 140 | 141 | 141 | 31 |  | 1236982
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 30 | 30 | 30 | 60 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2197440
120 | Eastern Zone Total | 4548 | 4319 | 4152 | 3885 | 3759 | 4027 | 4160 | 4483 | 4737 | 4695 | 4740 | 4997 | 5287 | 5058 | 5081 | 4826 | 4976 | 6110 |  | 6379 | 6232 | 6184 | 5872 | 5578 | 5139 | 4901 | 119403097
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [16 empty] | 16 | 49 |  | 49 | 25 | 16 | 16 | 8 |  |  | 143040
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | 0 |  |  |  |  | 17 | 17 | 17 | [7 empty] | 17 | 70 |  | 70 | 70 | 70 | 70 | 70 | 35 |  | 524160
130
131
132 | United Payra Power Ltd. | [9 empty] | 42 | 55 | 53 | 49 | 59 | 64 | 72 | 58 | 30 | [8 empty] | 448800
133 | Bhola Nutan Biddut BD LTD (GAS) | 36 | 36 | 36 | 36 | 35 | 36 | 36 | 36 | 6 | 7 | 34 | 35 | 34 | 38 | 36 | 35 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 35 | 36 | 826750
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [16 empty] | 6 | 36 |  | 48 | 48 | 54 | 64 | 64 | 2 |  | 283392
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 93 | 58 | 55 | 25 | 26 | 25 | 21 | 21 | 21 | 21 | 20 | 23 | 12 | 12 | 12 | 12 | 12 | 84 |  | 92 | 92 | 93 | 93 | 95 | 95 | 93 | 1124090
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 9 | 9 | 9 | 8 | 8 | 8 | 7 | 6 | 0 | 0 | 0 | [10 empty] | 14 | 24 | 23 | 22 | 20 | 159825
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 411 | 410 | 552 | 552 | 552 | 552 | 553 | 552 | 552 | 724 |  | 560 | 560 | 560 | 555 | 555 | 506 | 505 | 11890182
147 | Bheramara 410 MW CCPP | 245 | 270 | 285 | 310 | 330 | 350 | 370 | 380 | 330 | 330 | 330 | 330 | 330 | 325 | 395 | 395 | 390 | 385 |  | 370 | 365 | 365 | 360 | 350 | 350 | 350 | 8425152
148 | Payra 1320 MW | 490 | 470 | 470 | 470 | 450 | 470 | 440 | 440 | 440 | 440 | 400 | 400 | 400 | 400 | 400 | 400 | 430 | 500 |  | 550 | 550 | 550 | 550 | 520 | 520 | 490 | 10952500
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 138 | 139 | 140 | 138 | 140 | 140 | 140 | 140 | 140 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3424000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 172 | 172 | 172 | 172 | 172 | 168 | 148 | 151 | 151 | 157 | 165 | 186 | 185 | 153 | 153 | 149 | 172 | 185 |  | 171 | 171 | 173 | 175 | 168 | 154 | 168 | 4212100
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 145 | 146 | 149 | 149 | 154 | 160 | 144 | 138 | 141 | 166 | 177 | 200 | 195 | 161 | 167 | 163 | 186 | 193 |  | 182 | 188 | 184 | 181 | 179 | 183 | 194 | 4268382
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 337 | 387 | 340 | 364 | 386 | 387 | 387 | 385 | 362 | 300 | 392 | 429 | 380 | 373 | 353 | 375 | 400 | 380 |  | 409 | 426 | 399 | 405 | 303 | 396 | 357 | 9149400
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 5 | 5 | 22 | 22 | 22 | 18 | 18 | 18 | 18 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 465600
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 218970
165 | Amnura 50 MW PP(Sinha) | [20 empty] | 0 | [5 empty] | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [26 empty] | 0
169 | Natore 52 MW PP (Rajlanka) | [16 empty] | 8 | 34 |  | 8 | [6 empty] | 41760
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [17 empty] | 15 | [8 empty] | 20256
172 | Confidence Power Bogura Unit-1 113 MW | [8 empty] | 35 | [7 empty] | 20 | 100 |  | 111 | 111 | 112 | 113 | 50 |  |  | 585408
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 35 | 108 |  | 113 | 113 | 113 | 113 | 60 | 6 |  | 556800
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 3 | 4 | 2 | 3 | 3 | 2 | 1 | 0 | [9 empty] | 22267
178
178