## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:October 2020
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | October 2020 |  | September 2020 |  | October 2019
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 12759 | 11/10/20 | 12892 | 05/09/20 | 11952 | 17/10/19 | 12893 | 29/05/19
|  |  | 19:00 |  | 19:30 |  | 19:00 |  | 21:00
2 | Minimum Generation (MW) | 6045 | 23/10/20 | 7634 | 25/09/20 | 5208 | 26/10/19 | - | -
|  |  | 9:00 |  | 9:00 |  | 5:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 12759 | 11-10-2020 | 12892 | 05/09/20 | 11952 | 17/10/19 | 12893 | 29/05/19
|  |  | 19:00 |  | 19:30 |  | 19:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 10723 | 13-10-2020 | 10888 | 05/09/20 | 9531.4 | 07/10/19 | 10888 | 05/09/20
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 12759 | 11/10/20 | 12892 | 05/09/20 | 11952 | 17/10/19 | 12893 | 29/05/19
|  |  | 19:00 |  | 19:30 |  | 19:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 11755.2903 |  | 11890.0667 |  | 10692.2903 |  | 11890.0667 | Sept'20
7 | Average Generation (MW) at Day Peak | 9551.7742 |  | 9851.3753 |  | 8531.2581 |  | 9378.1933 | 2019-09-19
8 | Maximum Power Import from India, BIPTC (MW) | 933 | 28/10/2020 | 937 | 23/09/2020 | 942 | 20/10/19 | 956 | 27/3/2019
|  |  | 15:00 |  | 1:30 |  | 12:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 178 | 14/10/2020 | 184 | 07/09/2020 | 184 | 21/10/19 | 194 | 12/06/19
|  |  | 18:00 |  | 18:30 |  | 19:30 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 2010-05-04
20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 3707.5 | 05/04/10
20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 3604.3882 |  | 3387.808 |  | 3525.1883 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 123.1125 |  | 137.7396 |  | 133.5169
22 | Net Generation of BPDB (MKWH) | 3481.2758 |  | 3250.0684 |  | 3391.6713
23 | Net Generation of IPP & RPCL (MKWH) | 2428.8487 |  | 2551.8684 |  | 1792.18
24 | Net Generation of REB (MKWH) | 145.8563 |  | 139.565 |  | 144.8634
24 | Net Generation of Rental Power Plant (MKWH) | 540.7093 |  | 614.8876 |  | 371.5133
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 6596.69 |  | 6556.3894 |  | 5700.2281 |  | 6596.69 | Oct'20
26 | Energy Generation by Gas (MKWH) | 4215.0603 |  | 4127.7738 |  | 4520.3065 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 467.3091 |  | 388.8315 |  | 141.1366 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1436.1631 |  | 1679.4648 |  | 848.4787 |  | 1679.4648 | Sep-20
29 | Energy Generation by Hydro (MKWH) | 85.0566 |  | 42.0017 |  | 84.059 |  | 151.4 | August-19
30 | Energy Generation by Solar (MKWH) | 6.3227 |  | 4.8414 |  | 6.7654 |  | 22.56 | 2019-09-16
31 | Energy Generation by Coal (MKWH) | 509.8908 |  | 451.2158 |  | 235.097 |  | 509.8908 | Oct'20
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 765.2903 |  | 764.6635 |  | 711.459 |  | 775.9511 | August-20
33 | Monthly Load Factor (%) | 78.8511 |  | 80.3555 |  | 73.629 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:October' 2020
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 12759 | 11/10/20 | 19:00
Generation Period
| Dhaka | MW | 4332
| Chattogram | MW | 1216
| Cumilla | MW | 1203
| Mymensingh | MW | 988
| Sylhet | MW | 546
a) | Total supply in East zone | MW | 8285
| Khulna | MW | 1518
| Barisal | MW | 362
| Rajshahi | MW | 1270
| Rangpur | MW | 763
b) | Total supply in West zone | MW | 3913
c) | Total supply in both zone ( a+b) | MW | 12198
Ref: | 27.21.0000.603.16.087.20.336 | Date: 15/11/2020
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:October' 2020
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 150 | 04/10/20 | 21:00
| b) Ishurdi end | MW | 220 | 07/10/20 | 17:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 485 | 07/10/20 | 17:00
| b) Ishurdi end | MW | 50 | 04/10/20 | 21:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 1.7264
| b) Ishurdi end | MKWH | 67.0111
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 65.0008
| b) Ishurdi end | MKWH | 1.6761
23 | Transmission loss of EWI/ NO-1 | % | 2.955
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 230 | 05/10/20 | 21:00
| b)Serajganj end | MW | 470 | 02/10/20 | 16:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 460 | 02/10/20 | 16:00
| b)Sirajganj end | MW | 200 | 05/10/20 | 21:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 1.954 | 06/10/20
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 1.944 | 06/10/20
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 10.924
| b)Sirajganj end | MKWH | 112.594
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 110.83
| b)Sirajganj end | MKWH | 10.902
30 | Transmission loss of EWI /NO-2 | % | 1.446
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishwardi.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: October 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tongi | 132/33 kV Transformer-T3 & 33 kV Bus | 2020-10-01 21:30 | 2020-10-01 22:45 | 1:15 | E/O | Due to red-hot maintenance | 20 | 25 | Power interruption
Savar | 132/33 kV Transformer-T3 | 2020-10-07 12:25 | 2020-10-07 17:21 | 4:56 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
| 132/33 kV Transformers-T-1 & T2 | 2020-10-07 09:07 | 2020-10-07 09:13 | 0:06 | T | Tripped showing E/F relay | 25 | 2.5 | Power interruption
Jamalpur | 132/33 kV Transformer-T1 & 33 kV Bus | 2020-10-09 09:25 | 2020-10-09 11:13 | 1:48 | E/O | Due to red-hot maintenance at 33 kV | 18 | 32.4 | Power interruption
| 132/33 kV Transformers-T-1 & T2 | 2020-10-12 05:45 | 2020-10-12 06:11 | 0:26 | T | Tripped showing 33 kVside IDMT | 62 | 26.8667 | Power interruption
Mymensingh | 132/33 kV Transformer-T2 with 33 kV Bus | 2020-10-13 06:04 | 2020-10-13 10:05 | 4:01 | E/O | Due to Oil leakage | 30 | 120.5 | Power interruption
Kabirpur | 132/33 kV Transformer-T3 with 33 kV bus | 2020-10-13 08:29 | 2020-10-13 09:42 | 1:13 | E/O | Due to red-hot maintenance with 33 kV side | 50 | 60.8333 | Power interruption
Agargaon | 230/132 kV Transformer-T-2 | 2020-10-14 12:45 | 2020-10-14 13:05 | 0:20 | T | Tripped showing Bas bar Diff. relay | 0 | 0 | No interruption
Dhamrai | 132/33 kV Transformer-T1 | 2020-10-19 12:23 | 2020-10-19 12:25 | 0:02 | T | Tripped showing Buchholz relay | 80 | 2.6667 | Power interruption
Kishoreganj | 132/33 kV Transformer-T1 | 2020-10-20 22:45 | 2020-10-20 23:27 | 0:42 | E/O | Due to red-hot maintenance | 50 | 35 | Power interruption
Agargaon | 230/132 kV Transformer-T-1 | 2020-10-24 03:55 | 2020-10-24 03:55 | 0:00 | T | Tripped showing gen.trip | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T3 | 2020-10-29 22:58 | 2020-10-29 23:30 | 0:32 | T | Tripped showing O/C relay at 33 kV feeder fault | 35 | 18.6667 | Power interruption
Aminbazar | 230/132 kV Transformer-T-3 | 2020-10-30 13:25 | 2020-10-30 17:54 | 4:29 | E/O | Due to bursting of L/A | 0 | 0 | No interruption
|  |  | Total : | 19:50 |  | Unserved Energy: |  | 324.4333
Dhaka (South) Grid Circle :
Haripur | 132 kV reserve Bus | 2020-10-09 09:55 | 2020-10-09 12:50 | 2:55 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Bhulta | 132/33 kV Transformer-T2 | 2020-10-10 21:10 | 2020-10-10 21:53 | 0:43 | E/O | Due to red-hot maintenance | 20 | 14.3333 | Power interruption
| 132/33 kV Transformer-T2 | 2020-10-19 12:54 | 2020-10-19 14:37 | 1:43 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
| 400/230 kV Transformer-T1 | 2020-10-19 14:56 | 2020-10-19 16:33 | 1:37 | E/O | Due to red-hot maintenance at 230 kV DS | 0 | 0 | No interruption
Shyampur | 132/33 kV Transformer-GT1 | 2020-10-23 08:33 | 2020-10-23 08:58 | 0:25 | T | Tripped showing differential relay
| 132/33 kV Transformer-GT2 | 2020-10-23 08:33 | 2020-10-23 09:25 | 0:52 | T |  | 140 | 121.3333 | Power interruption
| 132/33 kV Transformer-GT3 | 2020-10-23 08:33 | 2020-10-23 09:45 | 1:12 | T
Hasnabad | 132/33 kV Transformers-T1,T2 & T3 | 2020-10-26 02:45 | 2020-10-26 03:22 | 0:37 | T | Tripped showing O/C relay | 150 | 92.5 | Power interruption
|  |  | Total : | 10:04 |  | Unserved Energy: |  | 228.1667
Chattogram Grid Circle :
Bakulia | 132/33 kV Transformer-T3 | 2020-10-04 09:52 | 2020-10-04 17:10 | 7:18 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Juldah | 132/33 kV Transformer-T2 | 2020-10-09 15:55 | 2020-10-09 19:52 | 3:57 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Halishahar | 132/33 kV Transformer-T2 | 2020-10-10 02:42 | 2020-10-10 02:56 | 0:14 | T | Tripped showing O/C & E/F relay at 33 kV side | 0 | 0 | No interruption
Bakulia | 132/33 kV Transformer-T2 | 2020-10-21 06:43 | 2020-10-21 10:41 | 3:58 | T | Tripped showing Diff. relay | 0 | 0 | No interruption
Halishahar | 132/33 kV Transformers-T1 & T2 | 2020-10-23 14:07 | 2020-10-23 14:42 | 0:35 | T | Tripped showing O/C & E/F relay at 33 kV side | 32 | 18.6667 | Power interruption
| 132/33 kV Transformer-T2 | 2020-10-24 00:35 | 2020-10-24 01:03 | 0:28 | T | Tripped showing O/C relay | 20 | 9.3333 | Power interruption
|  |  | Total : | 16:30 |  | Unserved Energy: |  | 28
Cumilla Grid Circle :
Bibiyana | 230 kV dia Bus-2 | 2020-10-01 11:31 | 2020-10-01 12:25 | 0:54 | E/O | Due to SF6 gas leakage | 0 | 0 | No interruption
Chowmuhani | 132/33 kV Transformer-T2 & 33 kV Bus | 2020-10-01 21:27 | 2020-10-01 23:30 | 2:03 | E/O | Due to red-hot maintenance | 86 | 176.3 | Power interruption
| 132/33 kV Transformer-T2 | 2020-10-02 08:20 | 2020-10-02 10:00 | 1:40 | E/O | Due to Oil leakage | 10 | 16.6667 | Power interruption
Cumilla (N) | 132/33 kV Transformer-T3 | 2020-10-05 11:13 | 2020-10-05 11:32 | 0:19 | T | Due to 33 kV feeder fault | 10 | 3.1667 | Power interruption
| 132/33 kV Transformer-T3 | 2020-10-06 10:04 | 2020-10-06 10:18 | 0:14 | T | Tripped showing O/C & E/F. relay | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2020-10-06 10:04 | 2020-10-06 10:24 | 0:20 | T |  | 0 | 0 | No interruption
Fenchuganj | 230/132 kV Transformer-T1 | 2020-10-06 15:55 |  |  | T | Tripped showing Bhuchaltz. relay | 0 | 0 | No interruption
Shahjibazar | 132/33 kV Transformer-T2 | 2020-10-10 22:08 | 2020-10-10 22:23 | 0:15 | T | Tripped showing Lockout relay at 33 kV side | 20 | 5 | Power interruption
Cumilla (N) | 132/33 kV Transformer-T3 | 2020-10-14 02:09 | 2020-10-14 02:48 | 0:39 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2020-10-14 12:15 | 2020-10-14 14:12 | 1:57 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
B.Baria | 132/33 kV Transformer-T1 | 2020-10-19 10:38 | 2020-10-19 14:45 | 4:07 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Cumilla (N) | 132/33 kV Transformer-T3 | 2020-10-22 19:22 | 2020-10-22 19:36 | 0:14 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
| 132/33 kV Transformers-T3 & T4 | 2020-10-23 14:39 | 2020-10-23 14:56 | 0:17 | T | Tripped showing O/C .relay at 33 kV side | 40 | 11.3333 | Power interruption
|  |  | Total : | 12:59 |  |  |  | 212.4667
Page: 2/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: October 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Bagerhat | 132/33 kV Transformers-T1 | 2020-10-02 23:06 | 2020-10-03 01:58 | 2:52 | T | Due to 33 kV feeder fault
| 132/33 kV Transformers-T2 | 2020-10-02 23:06 | 2020-10-02 23:37 | 0:31 | T |  | 10 | 5.1667 | Power interruption
Madaripur | 132/33 kV Transformer-T-3 | 2020-10-04 09:45 | 2020-10-04 12:00 | 2:15 | T | Due to 33 kV feeder fault | 10 | 22.5 | Power interruption
Noapara | 132/33 kV Transformers-T1 | 2020-10-08 19:38 | 2020-10-08 23:49 | 4:11 | T | Tripped showing differential & O/C relay | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 | 2020-10-08 19:38 | 2020-10-08 20:24 | 0:46 | T
| 132/33 kV Transformers-T4 | 2020-10-08 19:38 | 2020-10-08 20:03 | 0:25 | T |  | 45 | 18.75 | Power interruption
Bagerhat | 132/33 kV Transformers-T1 & T2 | 2020-10-11 08:42 | 2020-10-11 08:47 | 0:05 | T | Due to 33 kV feeder fault | 24 | 2 | Power interruption
Khulna© | 132/33 kV Transformers-T3 | 2020-10-15 09:26 | 2020-10-15 11:31 | 2:05 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Gopalganj(O) | 132/33 kV Transformer-T1 | 2020-10-17 07:22 | 2020-10-17 08:13 | 0:51 | E/O | Due to red-hot maintenance at 33 kV side | 20 | 17 | Power interruption
Mongla | 132/33 kV Transformer-T2 | 2020-10-23 12:07 | 2020-10-23 12:59 | 0:52 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Narail | 132/33 kV Transformer-T1 | 2020-10-25 09:11 | 2020-10-25 09:48 | 2:52 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Mongla | 132/33 kV Transformers-T1 & T2 | 2020-10-27 17:27 | 2020-10-27 17:39 | 0:12 | T | Tripped showing E/F as bird made short circuited | 26 | 5.2 | Power interruption
Magura | 132/33 kV Transformers-T1 & T2 | 2020-10-30 06:57 | 2020-10-30 07:22 | 0:25 | T | Due to 33 kV feeder fault | 20 | 8.3333 | Power interruption
|  |  | Total : | 18:22 |  | Unserved Energy: |  | 78.95
HVDC Grid Circle :
Baghabari | 230/132 kV Transformer-T01 | 2020-10-01 15:51 | 2020-10-01 19:32 | 3:41 | T | Tripped showing Gen.trip,mechanical protection operated | 0 | 0 | No interruption
HVDC Bheramara | Auxiliary transformer | 2020-10-04 17:16 | 2020-10-04 19:07 | 1:51 | T | Tripped showing PRD relay | 0 | 0 | No interruption
GK.project | 132/33 kV Transformer-T1 | 2020-10-04 16:27 | 2020-10-04 17:54 | 1:27 | T | Due to 33 kV feeder fault
| 132/33 kV Transformer-T2 | 2020-10-04 16:27 | 2020-10-04 17:53 | 1:26 | T |  | 36 | 51.6 | Power interruption
Bottail | 132/33 kV Transformer-T2 | 2020-10-05 12:24 | 2020-10-05 14:37 | 2:13 | T | Tripped showing dist. relay | 20 | 44.3333 | Power interruption
Jessore | 132/33 kV Transformers-T1 & T2 | 2020-10-10 16:57 | 2020-10-10 17:26 | 0:29 | T | Due to 33 kV feeder fault | 50 | 24.1667 | Power interruption
Bheramara | 230/132 kV Transformer-GT-2 | 2020-10-10 19:48 | 2020-10-10 20:59 | 1:11 | T | Tripped showing differenetial relay | 50 | 59.1667 | Power interruption
| 132/33 kV Transformer-T-1 & 33 kV Bus | 2020-10-13 07:30 | 2020-10-13 09:23 | 1:53 | E/O | Due to red-hot maintenance at 33 kV side | 12 | 22.6 | Power interruption
|  |  | Total : | 14:11 |  |  |  | 201.8667
Bogura Grid Circle:
Bogura | 132/33 kV Transformer-T3 | 2020-10-01 10:08 | 2020-10-01 11:40 | 1:32 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2020-10-01 11:43 | 2020-10-01 12:55 | 1:12 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Barapukuria | 132/33 kV Transformer-T3 | 2020-10-03 16:26 | 2020-10-03 16:41 | 0:15 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformer-T-1 | 2020-10-04 09:10 | 2020-10-04 10:30 | 1:20 | E/O | Due to red-hot maintenance | 22 | 29.3333 | Power interruption
Barapukuria | 132/33 kV Transformer-T3 | 2020-10-05 01:32 | 2020-10-05 01:42 | 0:10 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformer-T3 | 2020-10-05 09:45 | 2020-10-05 11:15 | 1:30 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Niyamatpur | 132/33 kV Transformer-T-1 & 33 kV Bus | 2020-10-05 08:58 | 2020-10-05 09:45 | 0:47 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer-TR-1 | 2020-10-08 18:51 | 2020-10-08 19:14 | 0:23 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Noapara | 132/33 kV Transformer-T-3 | 2020-10-09 16:19 | 2020-10-09 16:30 | 0:11 | T | Tripped showing lockout relay & 33 kV side | 27 | 4.95 | Power interruption
Rajshahi | 230/132 kV Transformer-TR-2 | 2020-10-13 09:01 | 2020-10-13 10:40 | 1:39 | T | Tripped showing differential relay | 0 | 0 | No interruption
| 132/33 kV Transformers-T-2 & T3 | 2020-10-13 10:58 | 2020-10-13 11:05 | 0:07 | T | Due to Katakhali -1 feeder bus DS short circuit | 74 | 8.6333 | Power interruption
Naogaon | 132/33 kV Transformer-T3 | 2020-10-15 05:54 | 2020-10-15 06:05 | 0:11 | T | Tripped showing lockout & E/F relay | 32 | 5.8667 | Power interruption
Barapukuria | 132/33 kV Transformer-T-5 | 2020-10-19 20:14 | 2020-10-19 21:43 | 1:29 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Purbasadipur | 132/33 kV Transformer-T-2 | 2020-10-24 16:20 | 2020-10-24 16:40 | 0:20 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Juldhaka | 132/33 kV Transformer-T-2 | 2020-10-26 11:00 | 2020-10-26 14:35 | 3:35 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Bogura | 132/33 kV Transformers-T-3 | 2020-10-26 06:16 | 2020-10-26 06:17 | 0:01 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
| 132/33 kV Transformers-T-4 | 2020-10-26 06:16 | 2020-10-26 07:01 | 0:45 | T |  | 0 | 0 | No interruption
Barapukuria | 132 kV Bus-2 | 2020-10-28 15:20 | 2020-10-28 15:30 | 0:10 | T | Due to bus bar protection relay
Noapara | 132/33 kV Transformers-T-1 & T2 | 2020-10-29 21:51 | 2020-10-29 22:53 | 1:02 | E/O | Due to red-hot maintenance at Y-phase REB feeder fault | 34 | 35.1333 | Power interruption
|  |  | Total : | 16:39 |  |  |  | 83.9167
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 108:35 | Hours
T = Tripping | [7 empty] | Executive Engineer
E/O = Emergency Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: October 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kaliakoir | Kaliakoir-Tangail 132 kV line-2 | 2020-10-02 02:16 | 2020-10-02 04:04 | 1:48 | T | Tripped showing dist.relay | 0 | 0 | No interruption
Tangail | Tangail-RPcL 132 kV line-2 | 2020-10-06 22:39 | 2020-10-06 23:42 | 1:03 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kabirpur | Kabirpur-Tongi 132 kV line | 2020-10-11 11:18 | 2020-10-11 11:50 | 0:32 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-2 | 2020-10-12 11:24 | 2020-10-12 13:25 | 2:01 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Mymensingh RPCL | Mymensingh RPCL-Mymensingh S/S 132 kV line-1 | 2020-10-15 11:22 | 2020-10-15 11:30 | 0:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV line | 2020-10-17 10:36 | 2020-10-17 10:40 | 0:04 | T | Tripped showing dist. relay | 80 | 5.3333 | Power interruption
Kaliakoir | Kaliakoir-Tangail 132 kV line-2 | 2020-10-18 14:01 | 2020-10-18 14:39 | 0:38 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV line | 2020-10-24 10:45 | 2020-11-02 16:45 | 222:00 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV line-2 | 2020-10-24 21:16 | 2020-10-24 22:22 | 1:06 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
| Kabirpur-Kaliakoir 132 kV line-2 | 2020-10-25 22:35 | 2020-10-25 23:22 | 0:47 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-1 | 2020-10-26 12:51 | 2020-10-26 12:56 | 0:05 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Mymensingh RPCL-Mymensingh Solar 132 kV line | 2020-10-26 22:33 | 2020-10-26 22:33 | 0:00 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghnaghat 230 kV line-2 | 2020-10-27 09:12 | 2020-10-27 09:47 | 0:35 | T | Tripped showing gen. trip relay | 0 | 0 | No interruption
|  |  | Total : | 230:47 |  | Unserved Energy: |  | 5.3333
Dhaka (South) Grid Circle :
Siddhirganj | Siddhirganj-Haripur 230 kV line-2 | 2020-10-04 14:52 | 2020-10-04 16:47 | 1:55 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj 132 kV line-1 | 2020-10-06 16:07 | 2020-10-06 16:27 | 0:20 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV line-1 | 2020-10-07 14:29 | 2020-10-07 14:48 | 0:19 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Lalbagh | Lalbagh-Kallyanpur 132 kV line- 1 & 2 | 2020-10-08 05:59 | 2020-10-08 05:59 | 0:00 | T | Tripped showing Dir.& E/F. relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj 132 kV line-1 | 2020-10-08 09:51 | 2020-10-08 10:59 | 1:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ghorashal-Ashuganj 132 kV line-2 | 2020-10-08 09:51 | 2020-10-08 11:07 | 1:16 | T |  | 0 | 0 | No interruption
Hasnabad | Hasnabad-Aurahati 132 kV line | 2020-10-11 11:19 | 2020-10-11 11:30 | 0:11 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kamrangirchar | Kamrangirchar-Aurahati 132 kV line | 2020-10-11 11:19 | 2020-10-11 11:30 | 0:11 | T | Tripped showing O/C & E/F. relay
| Kamrangirchar-Aurahati 132 kV line | 2020-10-11 11:30 | 2020-10-11 18:03 | 6:33 | T |  | 94 | 615.7 | Power interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-1 | 2020-10-17 09:58 | 2020-10-17 11:42 | 1:44 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sonargaon | Sonargaon-Meghnaghat IEL 132 kV line | 2020-10-21 15:02 | 2020-10-21 15:15 | 0:13 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-1 | 2020-10-22 12:50 | 2020-10-22 13:27 | 0:37 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Ullon 132 kV line | 2020-10-22 19:58 | 2020-10-22 20:42 | 0:44 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-2 | 2020-10-30 07:57 | 2020-10-30 08:35 | 0:38 | T | Tripped showing DT & PD3. relay | 0 | 0 | No interruption
|  |  | Total : | 15:49 |  | Unserved Energy: |  | 615.7
Chittagong Grid Circle :
Chandraghona | Chandraghona-Rangamati 132 kV line-1 | 2020-10-03 17:31 | 2020-10-03 17:40 | 0:09 | T | Tripped showing gen.trip relay | 25 | 3.75 | Power interruption
Hathazari | Hathazari-Baroierhat 132 kV line-1 | 2020-10-10 11:26 | 2020-10-10 11:36 | 0:10 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'xbazar 132 kV line-1 | 2020-10-11 12:08 | 2020-10-11 12:15 | 0:07 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV line-1 | 2020-10-15 08:14 | 2020-10-15 17:17 | 9:03 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Halishahar | Halishahar-Khulshi 132 kV line-1 | 2020-10-23 14:07 | 2020-10-23 14:24 | 0:17 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 9:46 |  | Unserved Energy: |  | 3.75
Cumilla Grid Circle :
Fenchuganj | Fenchuganj S/S- Sylhet 132 kV line | 2020-10-05 03:05 | 2020-10-05 03:34 | 0:29 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Fenchuganj-Kulaura 132 kV line-2 | 2020-10-05 08:55 | 2020-10-05 21:28 | 12:33 | T | Tripped showing MCB trip | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2020-10-05 23:12 | 2020-10-05 23:52 | 0:40 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-B.Baria 132 kV line-1 | 2020-10-08 09:31 | 2020-10-08 10:11 | 0:40 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Shahjibazar-B.Baria 132 kV line-2 | 2020-10-08 09:31 | 2020-10-08 10:10 | 0:39 | T |  | 0 | 0 | No interruption
| Shahjibazar-Ashuganj 132 kV line | 2020-10-08 09:51 | 2020-10-08 12:07 | 2:16 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2020-10-08 09:51 | 2020-10-08 11:24 | 1:33 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 kV line-2 | 2020-10-08 09:51 | 2020-10-08 17:23 | 7:32 | T |  | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Bibiyana 230 kV line-1 | 2020-10-08 12:54 | 2020-10-08 14:06 | 1:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Page: 2/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: October 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Bibiyana | Bibiyana-Kaliakoir 400 kV line-1 | 2020-10-10 09:57 | 2020-10-10 12:06 | 2:09 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Bibiyana 230 kV line-1 | 2020-10-11 16:32 | 2020-10-11 17:19 | 0:47 | T | Tripped showing differential & E/F. relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Meghnaghat 230 kV line-1 | 2020-10-13 11:48 | 2020-10-13 12:45 | 0:57 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sylhet | Sylhet-Sylhet Energy Prima 132 kV line | 2020-10-14 15:12 | 2020-10-14 15:12 | 0:00 | E/O | Due to bursting of L/A | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Kulaura 132 kV line-1 & 2 | 2020-10-14 21:55 | 2020-10-14 22:07 | 0:12 | E/O | Due to Oil leakage | 45 | 9 | Power interruption
Cumilla(N) | Cumilla(N)-Chuddagram 132 kV line-1 | 2020-10-18 05:41 | 2020-10-18 06:22 | 0:41 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Cumilla(N)-Chuddagram 132 kV line-2 | 2020-10-18 05:41 | 2020-10-18 06:35 | 0:54 | T |  | 0 | 0 | No interruption
Feni | Feni-Chauddagram 132 kV line-2 | 2020-10-18 02:55 | 2020-10-18 03:35 | 0:40 | T | Tripped showing SOTF ,AR fail & Lockout relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2020-10-20 14:18 | 2020-10-21 05:18 | 15:00 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Daudkandi 132 kV line-2 | 2020-10-31 04:00 | 2020-10-31 12:48 | 8:48 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kV line-2 | 2020-10-31 16:52 | 2020-10-31 17:28 | 0:36 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 58:18 |  | Unserved Energy: |  | 9
Khulna Grid Circle :
Gopalganj(N) | Gopalganj(N)-Gopalganj (O) 132 kV line | 2020-10-02 12:35 | 2020-10-02 12:42 | 0:07 | T | Tripped showing dist. relay | 50 | 5.8333 | Power interruption
Bagerhat | Bagerhat-Bhandaria 132 kV line | 2020-10-04 06:23 | 2020-10-04 08:38 | 2:15 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Barishal(N) | Barishal(N)-Bhola 230 kV line-1 | 2020-10-04 12:43 | 2020-10-04 13:29 | 0:46 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Magura | Magura-Norail 132 kV line-2 | 2020-10-05 10:47 | 2020-10-05 10:47 | 0:00 | E/O | Due to sparking at Norail at B-phase DS | 0 | 0 | No interruption
Madaripur | Madaripur-Gopalganj 132 kV line-1 | 2020-10-11 08:06 | 2020-10-11 09:42 | 1:36 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Barishal(N) | Barishal(N)-Bhola 230 kV line | 2020-10-12 11:13 | 2020-10-12 11:58 | 0:45 | T | Tripped showing dist. relay | 30 | 22.5 | Power interruption
Faridpur | Faridpur-Gopalganj 132 kV line-1 | 2020-10-12 12:20 | 2020-10-12 12:30 | 0:10 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Barishal(N) | Barishal(N)-Bhola P/S 230 kV line-1 | 2020-10-18 05:55 | 2020-10-18 06:32 | 0:37 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Faridpur | Faridpur-Gopalganj 132 kV line-1 | 2020-10-26 21:34 | 2020-10-26 21:51 | 0:17 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 6:33 |  | Unserved Energy: |  | 28.3333
HVDC Grid Circle :
Bheramara | Bheramara-Bottail 132 kV line-1 | 2020-10-01 14:34 | 2020-10-01 16:03 | 1:29 | E/O | Due to bursting of L/A | 0 | 0 | No interruption
Bheramara | Bheramara-Ishurdi 132 kV line-1 | 2020-10-01 14:34 | 2020-10-01 19:12 | 4:38 | E/O |  | 0 | 0 | No interruption
Ishurdi | Ishurdi-Natore 132 kV line-1 | 2020-10-01 14:35 | 2020-10-01 14:46 | 0:11 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bheramara | Bheramara-Ishurdi 132 kV line-2 | 2020-10-01 14:34 | 2020-10-01 16:12 | 1:38 | T | Tripped showing CAT,CD & CSN signal | 0 | 0 | No interruption
Ishurdi | Ishurdi-Bheramara 132 kV line-2 | 2020-10-13 07:35 | 2020-10-13 07:35 | 0:00 | T | Tripped showing backup protection relay | 0 | 0 | No interruption
Bheramara | Bheramara-Ishurdi 132 kV line-2 | 2020-10-13 08:40 | 2020-10-13 09:09 | 0:29 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ishurdi | Ishurdi-Bheramara 132 kV line-2 | 2020-10-20 15:45 | 2020-10-20 16:48 | 1:03 | E/O | Due to Oil leakage | 0 | 0 | No interruption
|  |  | Total : | 9:28 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Bogura | Bogura-Mohasthangarth 132 kV line-1 & 2 | 2020-10-05 12:40 | 2020-10-05 13:04 | 0:24 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Saidpur | Saidpur-Jaldhaka 132 kV line -2 | 2020-10-06 11:35 | 2020-10-06 11:47 | 0:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bogura | Bogura-Mohasthangarth 132 kV line-1 & 2 | 2020-10-08 18:51 | 2020-10-08 19:16 | 0:25 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Barapukuria | Barapukuria-Saidpur 132 kV line-1 & 2 | 2020-10-08 18:51 | 2020-10-08 19:12 | 0:21 | T | Tripped showing O/C. relay | 730 | 255.5 | Power interruption
Jaldhaka | Jaldhaka-Bottail 132 kV line-2 | 2020-10-23 05:30 | 2020-10-23 05:50 | 0:20 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV line-1 | 2020-10-23 08:25 | 2020-10-23 10:09 | 1:44 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Rajshahi | Rajshahi-Rajshahi new 132 kV line-2 | 2020-10-26 17:25 | 2020-10-26 18:31 | 1:06 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 4:32 |  | Unserved Energy: |  | 255.5
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 344:41 | Hours
T = Tripping | [7 empty] | Executive Engineer
E/O = Emergency Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/5 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:October 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Dhamrai | 132/33 kV Transformer-T1 | 2020-10-01 07:11 | 2020-10-01 09:06 | 1:55 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-10-02 09:14 | 2020-10-02 11:33 | 2:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132 kV Bus | 2020-10-03 09:48 | 2020-10-03 17:05 | 7:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T2 | 2020-10-03 08:02 | 2020-10-03 12:32 | 4:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV Transformer-GT2 | 2020-10-04 09:32 | 2020-10-04 09:32 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T2 | 2020-10-05 12:10 | 2020-10-05 13:31 | 1:21 | S/O | Due to C/M work | 70 | 94.5 | Power interruption
Kishoreganj | 132/33 kV Transformer-T1 | 2020-10-06 09:15 | 2020-10-06 17:16 | 8:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T2 | 2020-10-06 06:31 | 2020-10-06 08:51 | 2:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhaluka | 132/33 kV Transformer-T2 | 2020-10-06 06:29 | 2020-10-06 08:10 | 1:41 | S/O | Due to D/W work | 35 | 58.9167 | Power interruption
Kabirpur | 132/33 kV Transformer-T1 | 2020-10-08 06:37 | 2020-10-08 09:21 | 2:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Agargaon | 132/33 kV Transformer-T1 | 2020-10-08 09:53 | 2020-10-08 15:29 | 5:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T2 & 33 kV bus | 2020-10-10 06:24 | 2020-10-10 11:02 | 4:38 | S/O | Due to C/M work | 8 | 37.0667 | Power interruption
Kallyanpur | 132/33 kV Transformer-GT2 |  | 2020-10-10 22:35 |  | S/O | After maintenance work | 0 | 0 | No interruption
Agargaon | 132/33 kV Transformer-T2 | 2020-10-11 08:40 | 2020-10-11 12:55 | 4:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | 400/230 kV Transformer-T2 | 2020-10-12 06:16 | 2020-10-12 09:31 | 3:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T2 | 2020-10-12 07:16 | 2020-10-12 10:39 | 3:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Uttara | 132/33 kV Transformer-T3 | 2020-10-12 09:42 | 2020-10-12 09:42 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T2 with 33 kV Bus | 2020-10-13 06:04 | 2020-10-13 10:05 | 4:01 | S/O | Due to C/M work | 30 | 120.5 | Power interruption
Kishoreganj | 132/33 kV Transformer-T3 | 2020-10-13 09:16 | 2020-10-13 13:28 | 4:12 | S/O | Due to C/M work | 5 | 21 | Power interruption
Kabirpur | 132/33 kV Transformer-T1 | 2020-10-15 06:31 | 2020-10-15 08:29 | 1:58 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV reserve Bus | 2020-10-16 06:58 | 2020-10-16 07:08 | 0:10 | S/O | Due to D/W work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T2 with 33 kV Bus | 2020-10-16 04:40 | 2020-10-16 10:45 | 6:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T4 | 2020-10-16 09:02 | 2020-10-16 13:10 | 4:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajendrapur | 132/33 kV Transformer-T1 with33 kV Bus | 2020-10-16 08:13 | 2020-10-16 09:44 | 1:31 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 with33 kV Bus | 2020-10-16 08:14 | 2020-10-16 09:45 | 1:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T3 | 2020-10-17 07:13 | 2020-10-18 15:55 | 32:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Agargaon | 230/132 kV Transformer-T2 | 2020-10-17 08:09 | 2020-10-17 11:30 | 3:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T4 | 2020-10-17 14:34 | 2020-10-17 16:48 | 2:14 | S/O | Due to 33 kV Bus maintenance work | 0 | 0 | No interruption
Tongi | 132/33 kV Transformer-T1 | 2020-10-18 06:12 | 2020-10-18 07:14 | 1:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T1 | 2020-10-18 09:20 | 2020-10-18 11:42 | 2:22 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-10-18 11:50 | 2020-10-18 12:40 | 0:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T2 | 2020-10-18 08:01 | 2020-10-18 10:39 | 2:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | 132 kV main Bus | 2020-10-19 06:26 | 2020-10-19 06:39 | 0:13 | S/O | Due to D/W work | 0 | 0 | No interruption
Kaliakoir | 400/230 kV Transformer-T1 | 2020-10-20 05:58 | 2020-10-20 07:17 | 1:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132 kV main Bus | 2020-10-20 07:35 | 2020-10-20 08:05 | 0:30 | S/O | Due to D/W work | 60 | 30 | Power interruption
Saver | 33 kV Bus-A | 2020-10-20 08:17 | 2020-10-20 10:49 | 2:32 | S/O | Due to PBS work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T3 | 2020-10-21 06:36 | 2020-10-21 08:58 | 2:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132 kV main Bus-1 | 2020-10-21 07:10 | 2020-10-21 07:54 | 0:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Dhamrai | 132/33 kV Transformer-T1 |  | 2020-10-21 09:09 |  | S/O | After maintenance work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV Transformer-T1 | 2020-10-21 10:07 | 2020-10-21 12:12 | 2:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Saver | 33 kV Bus |  | 2020-10-22 07:29 |  | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T2 | 2020-10-22 06:20 | 2020-10-22 08:09 | 1:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV Transformer-T3 | 2020-10-22 09:23 | 2020-10-22 16:37 | 7:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaliakoir | 400/132 kV Transformer-T1 | 2020-10-24 06:19 | 2020-10-24 07:11 | 0:52 | S/O | Due to maintenance work | 0 | 0 | No interruption
Agargaon | 230/132 kV Transformer-T1 |  | 2020-10-24 15:15 |  | S/O | After maintenance work | 0 | 0 | No interruption
Kaliakoir | 400/132 kV Transformer-T02 | 2020-10-25 06:03 | 2020-10-25 06:33 | 0:30 | S/O | Due to C/M work | 0 | 0 | No interruption
| 400/132 kV Transformer-T01 | 2020-10-25 07:27 | 2020-10-25 07:30 | 0:03 | S/O | Due to Bus change | 0 | 0 | No interruption
New Tongi | 132/33 kV Transformer-T1 | 2020-10-27 06:10 | 2020-10-27 06:38 | 0:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Saver | 132/33 kV Transformer-T3 | 2020-10-27 07:29 | 2020-10-27 12:10 | 4:41 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaliakoir | 400 kV Bus-1 | 2020-10-28 06:18 | 2020-10-28 07:42 | 1:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T3 | 2020-10-28 06:09 | 2020-10-28 07:38 | 1:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Saver | 132/33 kV Transformer-T2 | 2020-10-28 06:39 | 2020-10-28 08:18 | 1:39 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | 132/33 kV Transformer-T1 | 2020-10-28 09:15 | 2020-10-28 09:15 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 33 kV Bus-3 | 2020-10-29 07:18 | 2020-10-29 09:25 | 2:07 | S/O | Due to C/M work | 30 | 63.5 | Power interruption
Tongi | 132/33 kV Transformer-T1 |  | 2020-10-29 17:20 |  | S/O | After maintenance work | 0 | 0 | No interruption
Page: 2/5 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:October 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kaliakoir | 400/132 kV Transformer-T02 | 2020-10-30 06:29 | 2020-10-30 08:53 | 2:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaliakoir | 400 kV Bus-1 |  | 2020-10-30 11:52 |  | S/O | After maintenance work | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T3 | 2020-10-30 17:30 | 2020-10-30 19:20 | 1:50 | S/O | Due to problem at 33 kV Bus | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T2 | 2020-10-31 07:01 | 2020-10-31 12:36 | 5:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaliakoir | 400/132 kV Transformer-T01 | 2020-10-31 09:15 | 2020-10-31 15:35 | 6:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T2 with 33 kV Bus | 2020-10-31 09:10 | 2020-10-31 16:43 | 7:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T1 | 2020-10-31 12:53 | 2020-10-31 16:34 | 3:41 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 181:24 |  | Unserved Energy: |  | 425.4833
Dhaka (South) Grid Circle :
Rampura | 230/132 kV Transformer-T01 | 2020-10-02 06:20 | 2020-10-02 06:20 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | 132 kV Bus section -1 | 2020-10-08 15:10 | 2020-10-08 17:37 | 2:27 | S/O | Due to protection work | 0 | 0 | No interruption
Siddhirganj | 132/33 kV Transformer-T-1 | 2020-10-12 07:08 | 2020-10-12 08:48 | 1:40 | S/O | Due to C/M work | 26 | 43.3333 | Power interruption
Haripur | 230/132 kV Transformer-T2 |  | 2020-10-15 16:14 |  | S/O | After maintenance work | 0 | 0 | No interruption
Hasnabad | 230/132 kV Transformer-T2 | 2020-10-18 09:40 | 2020-10-18 16:46 | 7:06 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-T2 | 2020-10-19 10:08 | 2020-10-19 17:05 | 6:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 230/132 kV Transformer-T2 | 2020-10-20 10:21 | 2020-10-20 17:24 | 7:03 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-T01 | 2020-10-21 09:36 | 2020-10-21 15:59 | 6:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | 230/132 kV Transformer-T01 | 2020-10-24 10:57 | 2020-10-24 13:15 | 2:18 | S/O | Due to replacemnet work | 0 | 0 | No interruption
Siddhirganj | 132/33 kV Transformer-GT-1 & GT-2 | 2020-10-28 15:09 | 2020-10-28 15:13 | 0:04 | S/O | Due to compressor problem | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-10-30 07:13 | 2020-10-30 08:58 | 1:45 | S/O | Due to C/M work | 5 | 8.75 | Power interruption
|  |  | Total : | 35:43 |  | Unserved Energy: |  | 52.0833
Chattogram Grid Circle :
Khulshi | 132/33 kV Transformer-T2 | 2020-10-02 01:20 | 2020-10-02 01:20 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Kagrachari | 132/33 kV Transformer-T1 | 2020-10-02 10:02 | 2020-10-02 12:07 | 2:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Bakulia | 132/33 kV Transformer-T3 | 2020-10-03 06:17 | 2020-10-03 12:49 | 6:32 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikalbaha | 132 kV Bus-A | 2020-10-07 09:28 | 2020-10-07 11:40 | 2:12 | S/O | Due to installation work | 0 | 0 | No interruption
Halishahar | 132/33 kV Transformer-T3 | 2020-10-09 07:03 | 2020-10-09 09:34 | 2:31 | S/O | Due to maintenance work | 0 | 0 | No interruption
Hathazari | 230/132 kV Transformer-MT3 | 2020-10-11 10:30 | 2020-10-11 16:09 | 5:39 | S/O | Due to D/W work | 0 | 0 | No interruption
Sikalbaha | 132 kV Bus-B | 2020-10-12 08:39 | 2020-10-12 12:05 | 3:26 | S/O | Due to installation work | 0 | 0 | No interruption
Juldah | 132 kV main Bus | 2020-10-17 07:16 | 2020-10-17 12:59 | 5:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Baroierhat | 132/33 kV Transformer-T1 | 2020-10-19 10:02 | 2020-10-19 12:09 | 2:07 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-10-19 12:29 | 2020-10-19 14:11 | 1:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | 230/132 kV Transformer-T01 | 2020-10-20 17:40 | 2020-10-20 19:37 | 1:57 | S/O | Due to 230 kV PT R-phase vibration | 0 | 0 | No interruption
| 230/132 kV Transformer-T02 | 2020-10-20 19:55 | 2020-10-20 20:32 | 0:37 | S/O |  | 0 | 0 | No interruption
| 230/132 kV Transformer-MT01 | 2020-10-21 12:08 | 2020-10-21 12:45 | 0:37 | S/O | Due to PT connection | 0 | 0 | No interruption
| 132 kV Bus section-1 | 2020-10-30 06:29 | 2020-10-30 09:44 | 3:15 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 38:23 |  | Unserved Energy : |  | 0
Cumilla Grid Circle :
Shahjibazar | 132/33 kV Transformer-Tr6 | 2020-10-01 10:01 | 2020-10-02 09:53 | 23:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Daudkandi | 132/33 kV Transformer-T1 | 2020-10-02 07:04 | 2020-10-02 07:04 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahjibazar | 132/33 kV Transformer-T4 | 2020-10-02 09:38 | 2020-10-02 17:20 | 7:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Daudkandi | 132/33 kV Transformer-T2 | 2020-10-02 11:40 | 2020-10-02 16:12 | 4:32 | S/O | Due to C/M work | 0 | 0 | No interruption
Chowmuhani | 132/33 kV Transformer-T1 | 2020-10-04 06:32 | 2020-10-04 11:26 | 4:54 | S/O | Due to C/M work | 20 | 98 | Power interruption
Shahjibazar | 132/33 kV Transformer-T2 | 2020-10-06 08:16 | 2020-10-06 12:16 | 4:00 | S/O | Due to C/M work | 0 | 0 | No interruption
APSCL | 132 kV Bus Voltage Zero | 2020-10-08 09:51 | 2020-10-08 11:00 | 1:09 | S/O | Due to malfunction of kishoreganj 132 kV line-2 DS | 218 | 69.0333 | Power interruption 09:51 to 10:10
Ashuganj | 132 kV Bus coupler | 2020-10-11 14:19 | 2020-10-12 09:40 | 19:21 | S/O | Due to high temperature | 0 | 0 | No interruption
Cumilla (N) | 230/132 kV Transformer-T2 | 2020-10-14 06:53 | 2020-10-14 09:33 | 2:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | 230 kV Bus-2 | 2020-10-16 07:05 | 2020-10-16 07:05 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230 kV Bus-2 | 2020-10-16 07:03 | 2020-10-16 12:50 | 5:47 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230 kV Bus-1 | 2020-10-17 07:00 | 2020-10-17 07:00 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
B.Baria | 132/33 kV Transformer-T2 | 2020-10-17 09:52 | 2020-10-17 11:30 | 1:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Sunamganj | 132/33 kV Transformer-T1 | 2020-10-18 08:50 | 2020-10-18 16:22 | 7:32 | S/O | Due to DS alignment | 0 | 0 | No interruption
Sreemongal | 132/33 kV Transformer-T1 | 2020-10-19 07:30 | 2020-10-19 09:15 | 1:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Sylhet | 132/33 kV Transformer-T2 | 2020-10-22 09:50 | 2020-10-22 12:30 | 2:40 | S/O | Due to replacement work | 0 | 0 | No interruption
Feni | 132/33 kV Transformer-T1 | 2020-10-25 07:38 | 2020-10-25 08:36 | 0:58 | S/O | Due to maintenance work | 21 | 20.3 | Power interruption
Page: 3/5 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:October 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Fenchuganj | 132/33 kV Transformer-T1 | 2020-10-27 08:06 | 2020-10-27 16:50 | 8:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjibazar | 132/33 kV Transformer-T2 | 2020-10-27 09:04 | 2020-10-27 16:54 | 7:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Chowmuhani | 132/33 kV Transformer-T2 | 2020-10-28 06:42 | 2020-10-28 10:10 | 3:28 | S/O | Due to C/M work | 12 | 41.6 | Power interruption
Shahjibazar | 132/33 kV Transformer-T2 | 2020-10-28 08:18 | 2020-10-28 16:58 | 8:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | 230/132 kV Transformer-T2 | 2020-10-28 08:53 | 2020-10-28 16:26 | 7:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Chatak | 132/33 kV Transformer-T2 | 2020-10-29 06:26 | 2020-10-29 12:50 | 6:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | 132/33 kV Transformer-T2 | 2020-10-29 09:08 | 2020-10-29 12:16 | 3:08 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 134:17 |  | Unserved Energy : |  | 228.9333
Khulna Grid Circle :
Satkhira | 132/33 kV Transformer-T2 with 33 kV Bus | 2020-10-09 06:44 | 2020-10-09 09:44 | 3:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Patuakhali | 132/33 kV Transformer-T1 | 2020-10-10 07:01 | 2020-10-10 17:22 | 10:21 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-10-11 07:03 | 2020-10-11 17:12 | 10:09 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-10-12 07:07 | 2020-10-12 17:13 | 10:06 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-10-13 07:03 | 2020-10-13 17:34 | 10:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T2 | 2020-10-13 17:30 | 2020-10-13 23:38 | 6:08 | S/O | Due to 33 kV feeder maintenance | 70 | 429.3333 | Power interruption
Patuakhali | 132/33 kV Transformer-T3 | 2020-10-14 07:10 | 2020-10-14 07:10 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T1 & T3 | 2020-10-15 15:17 | 2020-10-15 18:23 | 3:06 | S/O | Due to A/M work at 33 kV side | 48 | 148.8 | Power interruption
Goalpara | 132/33 kV Transformer-T5 | 2020-10-17 14:06 | 2020-10-17 16:47 | 2:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Patuakhali | 132/33 kV Transformer-T1 | 2020-10-22 13:38 | 2020-10-22 16:57 | 3:19 | S/O | Due to sparking was found from control panel | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T2 | 2020-10-28 07:57 | 2020-10-28 14:26 | 6:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | 132 kV Bus-& Magura 132 kV Bus | 2020-10-30 06:39 | 2020-10-30 10:35 | 3:56 | S/O | Due to D/W work | 65 | 255.6667 | Power interruption
Madaripur | 132/33 kV Transformer-T2 | 2020-10-30 09:14 | 2020-10-30 13:33 | 4:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Magura | 132/33 kV Transformer-T2 | 2020-10-30 08:45 | 2020-10-30 10:46 | 2:01 | S/O | Due to C/M work | 22 | 44.3667 | No interruption
Madaripur | 132/33 kV Transformer-T3 | 2020-10-31 08:50 | 2020-10-31 14:07 | 5:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | 230/132 kV Transformer-T-1 | 2020-10-31 08:40 | 2020-10-31 17:30 | 8:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Satkhira | 132/33 kV Transformer-T1 | 2020-10-31 09:16 | 2020-10-31 17:20 | 8:04 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 98:17 |  | Unserved Energy : |  | 878.1667
HVDC Grid Circle :
Ishurdi | 132 kV Bus-2 | 2020-10-01 16:00 | 2020-10-01 19:01 | 3:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Jhenidah | 132/33 kV Transformer-T2 | 2020-10-02 08:15 | 2020-10-02 11:52 | 3:37 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-10-02 11:56 | 2020-10-02 12:59 | 1:03 | S/O | Due to C/M work | 0 | 0 | No interruption
HVDC Bheramara | HVDC Bheramara station 10CF-14 | 2020-10-03 09:14 | 2020-10-03 16:05 | 6:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Baghabari | 230/132 kV Transformer-T2 | 2020-10-04 08:05 | 2020-10-04 13:32 | 5:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Bottail | 132/33 kV Transformer-T2 | 2020-10-06 07:04 | 2020-10-06 08:45 | 1:41 | S/O | Due to C/M work | 28 | 47.1333 | Power interruption
HVDC Bheramara | HVDC Bheramara station 10CF-14 | 2020-10-06 08:32 | 2020-10-06 15:53 | 7:21 | S/O | Due to C/M work | 0 | 0 | No interruption
| HVDC Bheramara station 10CF-14 | 2020-10-10 08:38 | 2020-10-10 08:38 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| HVDC Bheramara 230 kV reactor 20DF44 | 2020-10-10 09:37 | 2020-10-10 09:37 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| HVDC Bheramara station 10CF-26 | 2020-10-11 08:39 | 2020-10-11 14:53 | 6:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Jessore | 132/33 kV Transformer-T2 | 2020-10-12 09:01 | 2020-10-12 11:40 | 2:39 | S/O | Due to replacement work | 0 | 0 | No interruption
HVDC Bheramara | HVDC filter20DF31 | 2020-10-13 08:45 | 2020-10-13 15:23 | 6:38 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bheramara station HVDC filter20DF12 | 2020-10-14 08:32 | 2020-10-14 14:56 | 6:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjadpur | 132/33 kV Transformer-T4 | 2020-10-15 08:03 | 2020-10-15 09:23 | 1:20 | S/O | Due to C/M work | 0 | 0 | No interruption
HVDC Bheramara | HVDC filter20DF41 at 230 kV side | 2020-10-15 10:29 | 2020-10-15 16:34 | 6:05 | S/O | Due to A/M work | 0 | 0 | No interruption
| HVDC filter20DF24 | 2020-10-18 08:23 | 2020-10-18 15:31 | 7:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara | 230/132 kV Transformer-T1 | 2020-10-18 08:44 | 2020-10-18 15:42 | 6:58 | S/O | Due to C/M work | 0 | 0 | No interruption
HVDC Bheramara | capacitor at 230 kV | 2020-10-21 09:21 | 2020-10-21 16:18 | 6:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | 132/33 kV Transformer-T2 | 2020-10-24 10:50 | 2020-10-24 12:45 | 1:55 | S/O | Due ti maintenance work | 0 | 0 | No interruption
HVDC Bheramara | HVDC Bheramara shunt reactor 10CF-15 | 2020-10-24 09:01 | 2020-10-24 13:50 | 4:49 | S/O | Due to C/M work | 0 | 0 | No interruption
| HVDC Bheramara 230 kV 10CF-11 | 2020-10-25 08:52 | 2020-10-25 14:56 | 6:04 | S/O | Due to C/M work | 0 | 0 | No interruption
| HVDC Bheramara shunt reactor 10CF-12 | 2020-10-27 09:24 | 2020-10-27 15:25 | 6:01 | S/O | Due to A/M work | 0 | 0 | No interruption
| HVDC Bheramara 10CF-22 | 2020-10-28 09:25 | 2020-10-28 14:38 | 5:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Bottail | 132/33 kV Transformer-T1 | 2020-10-30 08:07 | 2020-10-30 10:03 | 1:56 | S/O | Due to C/M work | 60 | 116 | Power interruption
|  |  | Total : | 105:22 |  | Unserved Energy : |  | 163.1333
Page: 4/5 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:October 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle:
Rangpur | 132/33 kV Transformer-T-1 | 2020-10-03 08:10 | 2020-10-03 16:20 | 8:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | 230/132 kV Transformer-T-01 | 2020-10-03 08:11 | 2020-10-03 17:44 | 9:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T-1 | 2020-10-03 13:11 | 2020-10-03 16:33 | 3:22 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T-2 | 2020-10-03 14:15 | 2020-10-03 14:44 | 0:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformer-T-1 | 2020-10-04 08:04 | 2020-10-04 17:10 | 9:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | 230/132 kV Transformer-T-2 | 2020-10-05 08:12 | 2020-10-05 17:20 | 9:08 | S/O | Due to A/M work | 0 | 0 | No interruption
C.nawabganj | 132 kV main Bus | 2020-10-06 06:16 | 2020-10-06 10:03 | 3:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | 230/132 kV Transformer-T-2 | 2020-10-06 10:37 | 2020-10-06 16:22 | 5:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformer-T-2 | 2020-10-06 08:16 | 2020-10-06 16:55 | 8:39 | S/O | Due to A/M work | 15 | 129.75 | Power interruption
| 230/132 kV Transformer-T-3 | 2020-10-07 09:20 | 2020-10-07 18:40 | 9:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | 230/132 kV Transformer-T-03 | 2020-10-07 11:34 | 2020-10-07 20:09 | 8:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Panchagar | 132/33 kV Transformer-T-3 with 33 kV Bus | 2020-10-09 09:05 | 2020-10-09 17:33 | 8:28 | S/O | Due to D/W work | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformer-T-1 | 2020-10-09 20:50 | 2020-10-09 21:00 | 0:10 | S/O | Due to bus DS alignment | 18 | 3 | Power interruption
Saidpur | 132/33 kV Transformer-T-1 | 2020-10-10 08:20 | 2020-10-10 16:45 | 8:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Panchagar | 132/33 kV Transformer-T-3 | 2020-10-10 08:20 | 2020-10-10 17:25 | 9:05 | S/O | Due to D/W work | 20 | 181.6667 | Power interruption
Saidpur | 132/33 kV Transformer-T-2 | 2020-10-11 08:20 | 2020-10-11 15:10 | 6:50 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T-3 | 2020-10-12 08:45 | 2020-10-12 15:56 | 7:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | 132/33 kV Transformer-T-1 | 2020-10-12 08:39 | 2020-10-12 16:42 | 8:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Niyamatpur | 132/33 kV Transformer-T-3 | 2020-10-12 10:08 | 2020-10-12 13:12 | 3:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Saidpur | 132/33 kV Transformer-T-3 | 2020-10-13 08:35 | 2020-10-13 16:20 | 7:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Lalmonirhat | 132/33 kV Transformer-T-1 | 2020-10-13 08:10 | 2020-10-13 17:45 | 9:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | 230/132 kV Transformer-T-03 | 2020-10-13 08:23 | 2020-10-13 17:55 | 9:32 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformer-T-3 | 2020-10-13 12:19 | 2020-10-13 15:22 | 3:03 | S/O | Due to replacement work | 22 | 67.1 | Power interruption
Natore | 132/33 kV Transformer-T-3 | 2020-10-13 21:31 | 2020-10-13 22:43 | 1:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Lalmonirhat | 132/33 kV Transformer-T-2 | 2020-10-14 08:20 | 2020-10-14 16:47 | 8:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | 132/33 kV Transformer-T-2 | 2020-10-14 08:45 | 2020-10-14 16:30 | 7:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T-3 | 2020-10-14 10:19 | 2020-10-14 13:22 | 3:03 | S/O | Due to bushing problem at y-phase 33 kV side | 0 | 0 | No interruption
Saidpur | 132/33 kV Transformer-T-4 | 2020-10-14 08:38 | 2020-10-14 14:45 | 6:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T-2 | 2020-10-14 16:17 | 2020-10-14 18:34 | 2:17 | S/O | Due to modification work at 33 kV side | 20 | 45.6667 | Power interruption
| 132/33 kV Transformer-T-3 | 2020-10-14 17:44 | 2020-10-14 17:44 | 0:00 | S/O | Due to high temperature at 33 kv side | 0 | 0 | No interruption
Saidpur | 132/33 kV Transformer-T-4 | 2020-10-15 08:20 | 2020-10-15 13:15 | 4:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | 132/33 kV Transformer-T-1 | 2020-10-15 10:12 | 2020-10-15 11:27 | 1:15 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T-2 | 2020-10-15 12:13 | 2020-10-15 12:53 | 0:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | 132/33 kV Transformer-T-5 | 2020-10-17 08:30 | 2020-10-17 16:01 | 7:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Lalmonirhat | 132/33 kV Transformer-T-3 | 2020-10-17 08:20 | 2020-10-17 17:05 | 8:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformer-T-1 | 2020-10-17 08:05 | 2020-10-17 15:21 | 7:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Juldhaka | 132/33 kV Transformer-T-1 | 2020-10-17 08:45 | 2020-10-17 16:18 | 7:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | 132/33 kV Transformer-T-3 | 2020-10-17 09:24 | 2020-10-17 17:35 | 8:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T-3 |  | 2020-10-17 13:34 |  | S/O | After maintenance work | 0 | 0 | No interruption
Saidpur | 132/33 kV Transformer-T-5 | 2020-10-18 08:45 | 2020-10-18 15:10 | 6:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformer-T-1 | 2020-10-18 08:05 | 2020-10-18 15:14 | 7:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Juldhaka | 132/33 kV Transformer-T-1 | 2020-10-18 08:25 | 2020-10-18 16:50 | 8:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Kurigram | 132/33 kV Transformer-T-1 | 2020-10-18 09:30 | 2020-10-18 18:30 | 9:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Thakurgaon | 132/33 kV Transformer-T-1 | 2020-10-18 08:40 | 2020-10-18 16:25 | 7:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | 132/33 kV Transformer-T-3 | 2020-10-18 09:35 | 2020-10-18 17:46 | 8:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | 132/33 kV Transformer-T-3 | 2020-10-18 08:24 | 2020-10-18 21:05 | 12:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura(O) | 132/33 kV Transformer-T-4 | 2020-10-19 08:22 | 2020-10-19 16:18 | 7:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformer-T-2 | 2020-10-19 08:06 | 2020-10-19 19:08 | 11:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Juldhaka | 132/33 kV Transformer-T-2 | 2020-10-19 08:45 | 2020-10-19 16:35 | 7:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Thakurgaon | 132/33 kV Transformer-T-1 | 2020-10-19 08:35 | 2020-10-19 15:50 | 7:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | 132/33 kV Transformer-T-4 | 2020-10-19 08:40 | 2020-10-19 16:00 | 7:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Lalmonirhat | 132/33 kV Transformer-T-4 | 2020-10-19 08:15 | 2020-10-19 08:15 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura(O) | 132/33 kV Transformer-T-4 | 2020-10-20 08:32 | 2020-10-20 18:06 | 9:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformer-T-2 | 2020-10-20 08:10 | 2020-10-20 14:56 | 6:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Juldhaka | 132/33 kV Transformer-T-2 | 2020-10-20 08:45 | 2020-10-20 16:45 | 8:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 5/5 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:October 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle:
Thakurgaon | 132/33 kV Transformer-T-1 | 2020-10-20 08:38 | 2020-10-20 15:28 | 6:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | 132/33 kV Transformer-T-4 | 2020-10-20 10:46 | 2020-10-20 17:28 | 6:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Kurigram | 132/33 kV Transformer-T-2 | 2020-10-20 08:26 | 2020-10-20 15:35 | 7:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Thakurgaon | 132/33 kV Transformer-T-2 | 2020-10-21 08:01 | 2020-10-21 16:30 | 8:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformer-T-1 | 2020-10-21 08:50 | 2020-10-21 14:30 | 5:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformer-T-3 | 2020-10-21 08:08 | 2020-10-21 14:10 | 6:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Juldhaka | 132 kV bus coupler | 2020-10-21 09:00 | 2020-10-21 15:46 | 6:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Mohastangor | 132/33 kV Transformer-T-1 | 2020-10-21 08:44 | 2020-10-21 17:04 | 8:20 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T-1 | 2020-10-22 09:04 | 2020-10-22 15:47 | 6:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | 230/132 kV Transformer-T-03 | 2020-10-22 08:33 | 2020-10-22 12:31 | 3:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformer-T-3 | 2020-10-22 08:05 | 2020-10-22 14:18 | 6:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | 230/132 kV Transformer-T-01 |  | 2020-10-22 15:53 |  | S/O | After maintenance work | 0 | 0 | No interruption
| 230 kV Bus-1 |  | 2020-10-24 12:16 |  |  | New charged | 0 | 0 | No interruption
| 230 kV Bus-2 | 2020-10-24 13:02 | 2020-10-24 14:07 | 1:05 | S/O | Due to maintenance work | 0 | 0 | No interruption
Thakurgaon | 132/33 kV Transformer-T-3 |  | 2020-10-24 15:25 |  | S/O | After maintenance work | 0 | 0 | No interruption
| 132/33 kV Transformer-T-3 | 2020-10-25 08:45 | 2020-10-25 15:30 | 6:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | 132 kV Bus coupler | 2020-10-27 10:25 | 2020-10-27 12:20 | 1:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Mohastangor | 132/33 kV Transformer-T-2 | 2020-10-27 09:01 | 2020-10-27 16:43 | 7:42 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T-2 | 2020-10-28 09:21 | 2020-10-28 13:19 | 3:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | 132 kV Bus-A | 2020-10-28 08:35 | 2020-10-28 11:44 | 3:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Panchugar | 132/33 kV Transformer-T-1 | 2020-10-28 08:03 | 2020-10-28 16:58 | 8:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | 132/33 kV Transformer-T-2 | 2020-10-28 13:15 | 2020-10-28 14:45 | 1:30 | S/O | Due to D/W work | 0 | 0 | No interruption
Palashbari | 132 kV Bus-B | 2020-10-29 08:10 | 2020-10-29 12:20 | 4:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | 132/33 kV Transformer-T-4 | 2020-10-29 09:40 | 2020-10-29 13:05 | 3:25 | S/O | Due to replacement work | 0 | 0 | No interruption
Niyamatpur | 132/33 kV Transformer-T-3 |  | 2020-10-30 10:50 |  | S/O | After maintenance work | 0 | 0 | No interruption
Bogura | 132/33 kV Transformer-T-1 | 2020-10-31 10:30 | 2020-10-31 12:05 | 1:35 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 474:22 |  | Unserved Energy : |  | 427.1833
Others :
Ashuganj | 230/132 kV Transformer-OAT12 |  | 2020-10-09 11:35 |  | S/O | After maintenance work | 0 | 0 | No interruption
| 132 kV reactor -01 |  | 2020-10-09 12:07 |  | S/O |  | 0 | 0 | No interruption
| 132 kV reactor -03 |  | 2020-10-09 12:30 |  | S/O |  | 0 | 0 | No interruption
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1067:48 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/4 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:October 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar | Aminbazar-Mirpur 132 kV line-1 | 2020-10-01 07:48 | 2020-10-01 16:45 | 8:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh S/S | Mymensingh S/S-RPCL 132 kV line-1 | 2020-10-01 08:41 | 2020-10-01 13:48 | 5:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-2 | 2020-10-01 13:33 | 2020-10-01 16:59 | 3:26 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | Tangail-Kaliakoir 132 kV line-1 | 2020-10-02 08:24 | 2020-10-02 15:01 | 6:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-1 | 2020-10-03 09:14 | 2020-10-03 13:35 | 4:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV line-1 | 2020-10-03 09:42 | 2020-10-03 16:59 | 7:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara (3rd) 132 kV line | 2020-10-03 08:20 | 2020-10-03 17:50 | 9:30 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mirpur-Uttara (3rd) 132 kV line | 2020-10-04 07:48 | 2020-10-04 07:48 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV line-1 | 2020-10-05 09:42 | 2020-10-05 15:55 | 6:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara (3rd) 132 kV line | 2020-10-05 08:33 | 2020-10-05 19:40 | 11:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV line-1 | 2020-10-06 11:33 | 2020-10-06 17:40 | 6:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh S/S | Mymensingh S/S-RPCL 132 kV line-1 | 2020-10-06 11:54 | 2020-10-06 18:27 | 6:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara (3rd) 132 kV line | 2020-10-07 08:41 | 2020-10-07 17:02 | 8:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Mymensingh RPCL 132 kV line-2 | 2020-10-07 09:37 | 2020-10-07 11:21 | 1:44 | S/O | Due to C/M work | 0 | 0 | No interruption
| Mymensingh-Kishoreganj 132 kV line-2 | 2020-10-07 11:28 | 2020-10-07 13:22 | 1:54 | S/O | Due to C/M work | 0 | 0 | No interruption
| Mymensingh-Kishoreganj 132 kV line-1 | 2020-10-07 13:26 | 2020-10-07 14:35 | 1:09 | S/O | Due to C/M work | 0 | 0 | No interruption
| Mymensingh-Jamalpur 132 kV line-1 | 2020-10-08 08:27 | 2020-10-08 10:08 | 1:41 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Bibiyana 400 kV CKt-2 | 2020-10-10 05:44 | 2020-10-10 12:07 | 6:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Joydevpur | Joydevpur-Kadda 132 kV line-1 & 2 | 2020-10-10 06:53 | 2020-10-10 18:24 | 11:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | Tangail-RPCL 132 kV line-2 | 2020-10-10 20:09 | 2020-10-10 20:09 | 0:00 | S/O | Due to Overload Ckt. | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghnaghat 230 kV line-2 | 2020-10-11 07:42 | 2020-10-11 07:42 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-1 | 2020-10-12 09:35 | 2020-10-12 14:10 | 4:35 | S/O | Due to C/M work | 0 | 0 | No interruption
| Mymensingh-Jamalpur 132 kV line-2 | 2020-10-12 14:25 | 2020-10-12 17:42 | 3:17 | S/O | Due to C/M work | 0 | 0 | No interruption
| Mymensingh-Jamalpur 132 kV line-2 | 2020-10-13 10:51 | 2020-10-13 14:58 | 4:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Kaliakoir 230 kV line | 2020-10-14 08:45 | 2020-10-14 16:16 | 7:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Bibiyana 400 kV CKt-1 | 2020-10-15 06:06 | 2020-10-15 08:33 | 2:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kadda 132 kV line-1 | 2020-10-16 06:42 | 2020-10-21 09:05 | 122:23 | S/O | Due to D/W work | 0 | 0 | No interruption
| Kabirpur-Kadda 132 kV line-2 | 2020-10-16 06:42 | 2020-10-21 09:07 | 122:25 | S/O | Due to C/M work | 0 | 0 | No interruption
| Kabirpur-Kaliakoir 132 kV line-1 | 2020-10-16 07:12 | 2020-10-18 17:12 | 58:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Savar | Savar-Manikganj P/P 132 kv line-2 | 2020-10-16 07:10 | 2020-10-16 08:50 | 1:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Basila 132 kV line | 2020-10-16 13:58 | 2020-10-16 23:10 | 9:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Mymensingh solar 50 MW 132 kV CKt |  | 2020-10-17 10:50 |  |  | for test | 0 | 0 | No interruption
Agargaon | Agargaon-Cantonment 132 kV line-1 | 2020-10-18 08:49 | 2020-10-18 12:33 | 3:44 | S/O | Due to A/M work | 0 | 0 | No interruption
| Agargaon-Cantonment 132 kV line-2 | 2020-10-18 12:39 | 2020-10-18 15:00 | 2:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV line-2 | 2020-10-19 08:39 | 2020-10-19 08:39 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Kabirpur 132 kV line-1 | 2020-10-20 15:53 | 2020-10-20 16:47 | 0:54 | S/O | Due to D/W work | 0 | 0 | No interruption
| Kaliakoir-Kabirpur 132 kV line-2 |  | 2020-10-20 16:48 |  | S/O | After maintenance work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV line-1 | 2020-10-21 08:26 | 2020-10-21 16:25 | 7:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj P/P132 kV line-2 | 2020-10-21 09:31 | 2020-10-21 17:46 | 8:15 | S/O | Due to D/W work | 0 | 0 | No interruption
Kadda | Kadda-Kabirpur 132 kV both Ckt |  | 2020-10-21 09:06 |  | S/O | After maintenance work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV line-1 | 2020-10-21 08:18 | 2020-10-22 16:35 | 32:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Agargaon | Agargaon-Satmosjid 132 kV line-1 | 2020-10-22 08:47 | 2020-10-22 13:47 | 5:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Kabirpur 132 kV line- 1 & 2 | 2020-10-25 06:48 | 2020-10-25 06:51 | 0:03 | S/O | Due to Bus change over | 0 | 0 | No interruption
| Kaliakoir-Tangail 132 kV line-1 & 2 | 2020-10-25 07:20 | 2020-10-25 07:23 | 0:03 | S/O |  | 0 | 0 | No interruption
| Kaliakoir-Dhamrai 132 kV line-1 & 2 | 2020-10-25 06:38 | 2020-10-25 06:40 | 0:02 | S/O | Due to Bus change over | 46 | 1.5333 | Power interruption
Agargaon | Agargaon-Satmosjid 132 kV line-2 | 2020-10-25 14:34 | 2020-10-25 16:20 | 1:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV line-2 | 2020-10-27 09:00 | 2020-10-27 15:58 | 6:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 2/3 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:October 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
kabirpur | kabirpur-Kaliakoir 132 kV line-2 | 2020-10-28 06:25 | 2020-10-28 08:02 | 1:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV line-2 | 2020-10-28 08:28 | 2020-10-28 16:50 | 8:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Kabirpur 132 kV line-1 | 2020-10-29 06:33 | 2020-10-29 08:35 | 2:02 | S/O | Due to D/W work | 0 | 0 | No interruption
Savar | Savar-Manikganj P/S 132 kV line-1 | 2020-10-29 06:16 | 2020-10-29 07:17 | 1:01 | S/O | Due to A/M work | 0 | 0
| Savar-Manikganj P/S 132 kV line-2 | 2020-10-29 07:45 | 2020-10-29 09:28 | 1:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV line-2 | 2020-10-29 07:56 | 2020-10-29 16:35 | 8:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-1 | 2020-10-31 07:07 | 2020-10-31 07:07 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 536:21 |  | Unserved Energy: |  | 1.5333
Dhaka (South) Grid Circle :
Haripur | Haripur-Meghnaghat 230 kV line-1 | 2020-10-01 08:30 | 2020-10-02 21:22 | 36:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | Bhulta-Haripur 132 kV line-1 | 2020-10-02 10:53 | 2020-10-02 12:55 | 2:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Sitalkyha 132 kV line | 2020-10-03 07:32 | 2020-10-03 13:17 | 5:45 | S/O | Due to D/W work | 0 | 0 | No interruption
| Hasnabad-Bramongaon 132 kV line | 2020-10-03 07:45 | 2020-10-03 13:17 | 5:32 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | Haripur-Meghnaghat 230 kV line-1 | 2020-10-03 08:15 | 2020-10-03 21:10 | 12:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Manikganj 230 kV line-1 | 2020-10-04 07:17 | 2020-10-04 07:17 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| Siddhirganj-Manikganj 230 kV line-1 | 2020-10-05 08:27 | 2020-10-05 12:46 | 4:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Meghnaghat 230 kV line-2 | 2020-10-07 08:35 | 2020-10-07 17:17 | 8:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj S/S | Siddhirganj S/S-SidB 230 kV linedhirganj EGCB | 2020-10-07 17:08 | 2020-10-07 17:08 | 0:00 | S/O | Due to maintenance work | 0 | 0 | No interruption
Haripur | Haripur-Meghnaghat 230 kV line-2 | 2020-10-08 08:18 | 2020-10-08 17:57 | 9:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Ullon 132 kV line-1 | 2020-10-08 14:55 | 2020-10-08 17:06 | 2:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Aminbazar 230 kV line-2 | 2020-10-11 07:42 | 2020-10-24 21:07 |  | S/O | Due to A/M work | 0 | 0 | No interruption
| Meghnaghat-Cumilla(N) 230 kV line-2 | 2020-10-11 08:41 | 2020-10-11 15:24 | 6:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Lalbagh | Lalbagh-Kamrangirchar 132 kV line |  | 2020-10-11 11:52 |  | S/O | After maintenance work | 0 | 0 | No interruption
Rampura | Rampura-Gulshan 132 kV line-1 | 2020-10-13 05:27 | 2020-10-13 07:59 | 2:32 | S/O | Due to C/M work | 0 | 0 | No interruption
Madanganj | Madanganj-Munshiganj 132 kV line-1 | 2020-10-14 08:24 | 2020-10-14 14:12 | 5:48 | S/O | Due to A/M work | 0 | 0 | No interruption
| Madanganj-Basundhara cement 132 kV line | 2020-10-16 09:30 | 2020-10-16 15:32 | 6:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Sitalakhya | Sitalakhya-Bramangaon Agreeko 132 kV line | 2020-10-16 09:08 | 2020-10-16 14:58 | 5:50 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | Haripur-HPL 230 kV line | 2020-10-19 08:56 | 2020-10-19 17:28 | 8:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghnaghat 230 kV line-2 |  | 2020-10-19 15:18 |  | S/O | After maintenance work | 0 | 0 | No interruption
Madanganj | Madanganj-Munshiganj 132 kV line-2 | 2020-10-20 09:02 | 2020-10-20 14:45 | 5:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur- HPL 230 kV line-2 | 2020-10-20 08:15 | 2020-10-20 16:20 | 8:05 | S/O | Due to A/M work | 0 | 0 | No interruption
| Haripur- HPL 230 kV line-2 | 2020-10-21 11:18 | 2020-10-21 15:49 | 4:31 | S/O | Due to A/M work | 0 | 0 | No interruption
| Haripur-Siddhirganj 230 kV line-1 | 2020-10-25 08:18 | 2020-10-25 16:56 | 8:38 | S/O | Due to A/M work | 0 | 0 | No interruption
| Haripur-Siddhirganj 230 kV line-1 | 2020-10-26 08:20 | 2020-10-26 17:30 | 9:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Aminbazar 230 kV line-2 | 2020-10-26 08:54 | 2020-10-26 16:04 | 7:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 230 kV line-1 | 2020-10-27 07:10 | 2020-10-27 16:18 | 9:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Madanganj | Madanganj-Madanganj P/S 132 kV line | 2020-10-27 08:27 | 2020-10-27 17:22 | 8:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Aminbazar 230 kV line-1 | 2020-10-27 09:05 | 2020-10-27 16:27 | 7:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Shyampur | Shyampur-Hasnabad 230 kV line | 2020-10-30 09:22 | 2020-10-30 09:22 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| Shyampur-APR 230 kV line | 2020-10-30 09:25 | 2020-10-30 09:25 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 132 kV line | 2020-10-31 14:57 | 2020-10-31 16:45 | 1:48 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 193:54 |  | Unserved Energy: |  | 0
Page: 3/4 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:October 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Chattogram Grid Circle :
Chandraghona | Chandraghona-Rangamati 132 kV line-1 | 2020-10-03 10:35 | 2020-10-03 17:10 | 6:35 | S/O | Due to D/W work | 0 | 0 | No interruption
| Chandraghona-Rangamati 132 kV line-2 | 2020-10-03 17:17 | 2020-10-03 21:06 | 3:49 | S/O | Due to D/W work | 0 | 0 | No interruption
Rangamati | Rangamati-Kaghrachari 132 kV line-1 | 2020-10-05 08:32 | 2020-10-05 14:20 | 5:48 | S/O | Due to C/M work | 0 | 0 | No interruption
| Rangamati-Kaghrachari 132 kV line-2 | 2020-10-05 14:28 | 2020-10-05 17:05 | 2:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-T.K chemical 132 kV line | 2020-10-06 06:10 | 2020-10-06 07:41 | 1:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Madunaghat 132 kV line-1 | 2020-10-06 07:46 | 2020-10-06 10:23 | 2:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangamati | Rangamati-Kaghrachari 132 kV line-1 | 2020-10-06 08:17 | 2020-10-06 13:14 | 4:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Kaptai 132 kV line-1 | 2020-10-09 07:09 | 2020-10-09 08:17 | 1:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Cox'sbazar | Cox'sbazar-Dohazari 132 kV line-2 | 2020-10-10 07:10 | 2020-10-10 17:01 | 9:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-2 | 2020-10-11 08:08 | 2020-10-11 16:45 | 8:37 | S/O | Due to D/W work | 0 | 0 | No interruption
| Dohazari-Cox'sbazar 132 kV line-2 | 2020-10-12 06:14 | 2020-10-12 17:30 | 11:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangamati | Rangamati-Kaghrachari 132 kV line-2 | 2020-10-12 08:36 | 2020-10-12 13:24 | 4:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-T.K chemical 132 kV line | 2020-10-13 05:51 | 2020-10-13 08:42 | 2:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-2 | 2020-10-13 06:08 | 2020-10-13 17:22 | 11:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaptai | Kaptai-Chandraghona 132 kV line-1 | 2020-10-13 08:48 | 2020-10-13 17:21 | 8:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangamati | Rangamati-Kaghrachari 132 kV line-2 | 2020-10-13 08:40 | 2020-10-13 16:38 | 7:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-2 | 2020-10-14 06:18 | 2020-10-14 17:23 | 11:05 | S/O | Due to D/W work | 0 | 0 | No interruption
Kaptai | Kaptai-Chandraghona 132 kV line-1 | 2020-10-14 08:35 | 2020-10-14 16:05 | 7:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangamati | Rangamati-Kaghrachari 132 kV line-2 | 2020-10-14 08:57 | 2020-10-14 15:17 | 6:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-2 | 2020-10-15 06:24 | 2020-10-15 17:16 | 10:52 | S/O | Due to D/W work | 0 | 0 | No interruption
Kaptai | Kaptai-Chandraghona 132 kV line-1 | 2020-10-15 08:04 | 2020-10-15 16:10 | 8:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangamati | Rangamati-Kaghrachari 132 kV line-2 | 2020-10-15 08:28 | 2020-10-15 14:07 | 5:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV line-1 | 2020-10-15 08:14 | 2020-10-15 17:17 | 9:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaptai | Kaptai-Chandraghona 132 kV line-2 | 2020-10-17 09:52 | 2020-10-17 16:03 | 6:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangamati | Rangamati-Kaghrachari 132 kV line-2 | 2020-10-17 08:30 | 2020-10-17 14:23 | 5:53 | S/O | Due to C/M work | 0 | 0 | No interruption
Baraulia | Baraulia-Hathazari 132 kV line-1 & 2 | 2020-10-18 06:12 | 2020-10-18 07:14 | 1:02 | S/O | Due to C/M work | 0 | 0 | No interruption
| Baraulia-Hathazari 132 kV line-1 & 2 | 2020-10-19 06:00 | 2020-10-19 06:00 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 1132 kV line-1 | 2020-10-20 07:48 | 2020-10-20 16:15 | 8:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangamati | Rangamati-Kaghrachari 132 kV line-2 | 2020-10-20 08:42 | 2020-10-20 14:45 | 6:03 | S/O | Due to A/M work | 0 | 0 | No interruption
| Rangamati-Kaghrachari 132 kV line-1 | 2020-10-21 08:27 | 2020-10-21 15:43 | 7:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kv line-1 | 2020-10-22 07:32 | 2020-10-22 12:24 | 4:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangamati | Rangamati-Chandraghona 132 kV line-1 | 2020-10-22 09:04 | 2020-10-22 15:27 | 6:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Rangamati 132 kV line-1 | 2020-10-25 08:24 | 2020-10-25 14:43 | 6:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangamati | Rangamati-Chandraghona 132 kV line-2 | 2020-10-27 08:41 | 2020-10-27 14:17 | 5:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kv line-2 | 2020-10-28 07:39 | 2020-10-28 17:04 | 9:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangamati | Rangamati-Chandraghona 132 kV line-2 | 2020-10-28 08:44 | 2020-10-28 14:16 | 5:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kv line-2 | 2020-10-29 07:29 | 2020-10-29 16:59 | 9:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangamati | Rangamati-Chandraghona 132 kV line-2 | 2020-10-29 09:00 | 2020-10-29 14:44 | 5:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Madunaghat 132 kV line-2 | 2020-10-31 07:42 | 2020-10-31 13:33 | 5:51 | S/O | Due to D/W work | 0 | 0 | No interruption
| Hathazari-Khulshi 132 kV line-1 | 2020-10-31 07:45 | 2020-10-31 16:11 | 8:26 | S/O | Due to D/W work | 0 | 0 | No interruption
Rangamati | Rangamati-Chandraghona 132 kV line-2 | 2020-10-31 08:39 | 2020-10-31 16:11 | 7:32 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 262:47 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Ashuganj | Ashuganj-Ashuganj(S) 230 kV line-2 | 2020-09-02 09:27 | 2020-09-02 11:00 | 1:33 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ashuganj S/S-Ashuganj precision |  | 2020-10-09 22:34 |  | S/O | After maintenance work | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-2 | 2020-10-14 09:08 | 2020-10-14 10:44 | 1:36 | S/O | Due to DC fail problem at CB | 0 | 0 | No interruption
Ashuganj | Ashuganj-Cumilla(N) 230 kV line-1 | 2020-10-16 06:55 | 2020-10-16 06:55 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV line-2 | 2020-10-16 10:18 | 2020-10-16 12:50 | 2:32 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ashuganj-Ashuganj (S) 230 kV line-2 | 2020-10-16 11:18 | 2020-10-16 13:30 | 2:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Chaddagram | Chaddagram-Cumilla(N) -Lakdhan 132 kV line | 2020-10-21 10:13 | 2020-10-21 14:57 | 4:44 | S/O | Due to maintenance work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2020-10-28 09:53 | 2020-10-28 13:27 | 3:34 | S/O | Due to D/W work | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 kV line-2 | 2020-10-28 13:28 | 2020-10-28 14:49 | 1:21 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 17:32 |  | Unserved Energy: |  | 0
Page: 4/4 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:October 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Madaripur | Madaripur-Gopalganj 132 kV line-2 | 2020-10-09 07:24 | 2020-10-09 08:57 | 1:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Magura | Magura-Norail 132 kV line-1 |  | 2020-10-10 10:10 |  | S/O | Due to maintenance work | 0 | 0 | No interruption
Barishal | Barishal-Bhola 230 kV line-1 | 2020-10-13 08:53 | 2020-10-13 10:46 | 1:53 | S/O | Due to C/M work | 0 | 0 | No interruption
| Barishal(N)-Barishal (S) 132 kV line-2 | 2020-10-14 11:49 | 2020-10-14 13:16 | 1:27 | S/O | Due to protection work | 0 | 0 | No interruption
Norail | Norail-Magura 132 kV line-1 | 2020-10-14 14:40 | 2020-10-14 21:30 | 6:50 | S/O | Due to abnormal sound | 0 | 0 | No interruption
Barishal(N) | Barishal(N)-Madaripur 132 kV line-1 | 2020-10-14 14:03 | 2020-10-14 17:31 | 3:28 | S/O | Due to protection work | 0 | 0 | No interruption
Khulna © | Khulna ©-Khulna-225 MW 132 kV line-1 | 2020-10-18 12:42 | 2020-10-18 13:35 | 0:53 | S/O | Due to high temperature | 0 | 0 | No interruption
Khulna© | Khulna©-Khulna 225 MW 132 kV line-2 | 2020-10-18 11:28 | 2020-10-18 12:41 | 1:13 | S/O |  | 0 | 0 | No interruption
Barishal | Barishal-Madaripur 132 kV line-2 | 2020-10-23 09:44 | 2020-10-23 17:27 | 7:43 | S/O | Due to D/W work | 0 | 0 | No interruption
Barishal(N) | Barishal(N)-Madaripur 132 kV line-2 | 2020-10-24 07:48 | 2020-10-24 14:05 | 6:17 | S/O | Due to C/M work | 0 | 0 | No interruption
| Barishal(N)-Madaripur 132 kV line-1 | 2020-10-24 14:09 | 2020-10-24 17:34 | 3:25 | S/O | Due to D/W work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Goalpara 132 kV line & Bageraht-Orion P.P 132 kV line |  | 2020-10-30 11:53 |  |  | New connection
|  |  | Total : | 34:42 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Bheramara | Bheramara-Faridpur 132 kV line-2 | 2020-10-02 07:05 | 2020-10-02 10:20 | 3:15 | S/O | Due to C/M work | 0 | 0 | No interruption
HVDC Bheramara | HVDC Bheramara station filter 10CF-14 | 2020-10-05 08:54 | 2020-10-05 13:29 | 4:35 | S/O | Due to A/M work | 0 | 0 | No interruption
| HVDC Bheramara station filter 10CF-14 | 2020-10-07 08:40 | 2020-10-07 16:08 | 7:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara | Bheramara-Kustia 132 kV line-2 | 2020-10-09 06:34 | 2020-10-09 09:53 | 3:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Bheramara 132 kV line-2 | 2020-10-12 05:54 | 2020-10-12 15:54 | 10:00 | S/O | Due to replacement work | 0 | 0 | No interruption
| Ishurdi-Bheramara 132 kV line-2 | 2020-10-14 08:55 | 2020-10-14 20:14 | 11:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Bheramara 132 kV line-2 | 2020-10-21 11:12 | 2020-10-21 16:16 | 5:04 | S/O | Due to replacement work | 0 | 0 | No interruption
| HVDC Bheramara station filter 10CO4A -1 | 2020-10-29 09:05 | 2020-10-29 16:18 | 7:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Bottail | Bottail-Jhenidah 132 kV line | 2020-10-30 07:08 | 2020-10-30 09:31 | 2:23 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 54:36 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Barapukuria | Barapukuria-Saidpur 132 kV line-1 | 2020-10-03 10:08 | 2020-10-03 23:13 | 13:05 | S/O | Due to CT problem | 0 | 0 | No interruption
Rajshahi | Rajshahi-Bheramara 230 kV line-2 |  | 2020-10-22 16:08 |  | S/O | After maintenance work | 0 | 0 | No interruption
| Rajshahi-Bheramara 230 kV line-1 | 2020-10-22 17:13 | 2020-10-22 17:13 | 0:00 | S/O | Due to project work | 0 | 0 | No interruption
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1099:52 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:October' 2020
| Area | Previous Month (September) 2020) |  |  |  | Current Month (October 2020)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 24 | 14 | 88 | 126 | 16 | 10 | 114 | 140
2 | Dhaka (South) Grid Circle. | 19 | 7 | 27 | 53 | 17 | 5 | 43 | 65
3 | Chattogram Grid Circle. | 13 | 6 | 20 | 39 | 10 | 1 | 56 | 67
4 | Cumilla Grid Circle. | 20 | 8 | 51 | 79 | 26 | 7 | 33 | 66
5 | Khulna Grid Circle. | 7 | 8 | 23 | 38 | 15 | 7 | 28 | 50
6 | HVDC Grid Circle | 10 | 4 | 18 | 32 | 9 | 4 | 32 | 45
7 | Bogura Grid Circle. | 34 | 17 | 48 | 99 | 15 | 11 | 80 | 106
8 | Others | 3 |  | 2 | 5 | 2 |  | 3 | 5
9 | Total | 130 | 64 | 277 | 471 | 110 | 45 | 389 | 544
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:October' 2020
| Area | Previous Month (September 2020) |  |  |  | Current Month (October 2020)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 545.89 | 1562.7 | 1667.57 | 3776.16 | 56.04 | 273.73 | 427.01 | 756.78
2 | Dhaka (South) Grid Circle. | 4186.55 |  | 161.42 | 4347.97 | 829.53 | 14.33 | 52.08 | 895.94
3 | Chattogram Grid Circle. | 159.08 | 25 | 51.2 | 235.28 | 31.75 |  |  | 31.75
4 | Cumilla Grid Circle. | 132.41 | 130.8 | 70.08 | 333.29 | 19.5 | 201.97 | 228.93 | 450.4
5 | Khulna Grid Circle. | 53.33 | 39.67 | 90.55 | 183.55 | 90.28 | 17 | 878.17 | 985.45
6 | HVDC Grid Circle | 30 | 99.33 | 173.25 | 302.58 | 179.27 | 22.6 | 163.13 | 365
7 | Bogura Grid Circle. | 311.75 | 293.75 | 1865.58 | 2471.08 | 274.95 | 64.46 | 427.18 | 766.59
8 | Others
9 | Total | 5419.01 | 2151.25 | 4079.65 | 11649.91 | 1481.32 | 594.09 | 2176.5 | 4251.91
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:October' 2020
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 9 | 6 | 15 | 4 | 2 | 10 | 749.91
2 | Dhaka (South) | 5031.6 | 3 | 2 | 5 | 3 |  | 2 | 280.25
3 | Chattogram | 2042 | 2 |  | 2 | 1 | 1 |  | 28
4 | Khulna | 2434 | 7 | 4 | 11 | 4 | 2 | 5 | 957.12
5 | HVDC | 5954.3 | 4 | 2 | 6 | 1 |  | 5 | 365
6 | Bogura | 3145.6 | 5 | 5 | 10 | 4 | 4 | 6 | 511.1
7 | Cumilla | 2981 | 5 | 4 | 9 | 3 |  | 6 | 441.4
8 | Others | -
| Total | 30390.1 | [6 empty] | 3332.78
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.962
2 | Dhaka (South) | 99.9598
3 | Chattogram | 99.9289
4 | Khulna | 99.9448
5 | HVDC | 99.967 | [6 empty] | Executive Engineer
6 | Bogura | 99.9509 | [6 empty] | Information Management Division
7 | Cumilla | 99.9568 | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:October' 2020
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 1 | 1 | 2 | 2 | - | - | 6.86
2 | Dhaka (South) | 990.29 |  | 1 | - | 1 |  |  | 1 | 615.7
3 | Chattogram | 917 | - | 1 | - | 1 | 1 | - |  | 3.75
4 | Khulna | 1238.4 | - | 2 | - | 2 | - | 1 | 1 | 28.33
5 | HVDC | 1325 | 501 | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | - | 1 | - | 1 | 1 | - | - | 255.5
7 | Cumilla | 1648.16 | - | 1 | - | 1 | 1 | - | - | 9
8 | Others | - |  | - | - | - | - | - | - | -
| Total | 10176.6215 | 501 | [6 empty] | 919.14
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.9808
2 | Dhaka (South) | 99.9424
3 | Chattogram | 99.8502
4 | Khulna | 99.9819
5 | Bheramara (HVDC) | 99.9973 | [7 empty] | Executive Engineer
6 | Bogura | 99.9953 | [7 empty] | Information Management Division
7 | Cumilla | 99.8058 | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:October' 2020
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2020-10-18 | 12 | - | 4 | 7hour 21 min | 1 | 12 min | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/2 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:October' 2020
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Tongi | 1 | 1:15 | 20 | 25 | Due to red-hot maintenance of 132/33 kV Transformer T3 & 33 kV Bus
Savar | 1 | 0:06 | 25 | 2.5 | Due to tripping of 132/33 kV Transformers-T1 & T2
Jamalpur | 2 | 1:48 | 18 | 32.4 | Due to red-hot maintenance of 132/33 kV Transformer T1 & 33 kV Bus
|  | 0:26 | 62 | 26.8667 | Due to tripping of 33 kV feeder fault
Mymensingh | 1 | 4:01 | 30 | 120.5 | Due to Oil leakage of 132/33 kV Transformer T2
Kabirpur | 1 | 1:13 | 50 | 60.8333 | Due to red-hot maintenance of 132/33 kV Transformer T3 & 33 kV Bus
Dhamrai | 1 | 0:02 | 80 | 2.6667 | Due to tripping of 132/33 kV Transformer-T1
Kishoreganj | 1 | 0:42 | 50 | 35 | Due to red-hot maintenance of 132/33 kV Transformer T1
Sherpur | 1 | 0:32 | 35 | 18.6667 | Due to tripping of 132/33 kV Transformer-T3
Mirpur | 1 | 0:44 | 80 | 5.3333 | Due to tripping of Mirpur-Uttara 132 kV line
Tangail | 1 | 1:21 | 70 | 94.5 | Due to S/D of132/33 kV Transformer-T2
Bhaluka | 1 | 1:41 | 35 | 58.9167 | Due to S/D of132/33 kV Transformer-T2
Netrakona |  | 4:38 | 8 | 37.0667
Mymensingh | 1 | 4:01 | 30 | 120.5
Kishoreganj | 1 | 4:12 | 5 | 21 | Due to S/D of132/33 kV Transformer-T3
Kabirpur |  | 0:30 | 60 | 30 | Due to S/D of 132 kV main Bus
Mymensingh | 1 | 2:07 | 30 | 63.5 | Due to S/D of 33 kV Bus-3
Kaliakoir | 1 | 0:02 | 46 | 1.5333 | Due to S/D of Kaliakoir-Dhamrai 132 kV line-1 & 2
Bhulta | 1 | 0:43 | 20 | 14.3333 | Due to red-hot maintenance of 132/33 kV Transformer T2
Shyampur | 1 | 0:52 | 140 | 121.3333 | Due to tripping of 132/33 kV Transformer-GT2
Hasnabad | 1 | 0:37 | 150 | 92.5 | Due to tripping of 132/33 kV Transformers-T1, T2 & T3
Kamrangirchar | 1 | 6:33 | 94 | 615.7 | Due to triiping of Kamrangirchar-Aurahati 132 kV line
Siddhirganj | 2 | 1:40 | 26 | 43.3333 | Due to S/D of132/33 kV Transformer-T1
|  | 1:45 | 5 | 8.75 | Due to S/D of132/33 kV Transformer-T2
Halishahar |  | 0:35 | 32 | 18.6667 | Due to tripping of 132/33 kV Transformers-T1, & T2
| 2 | 0:28 | 20 | 9.3333 | Due to tripping of 132/33 kV Transformer-T3
Chandraghona | 1 | 0:09 | 25 | 3.75 | Due to tripping of Chandraghona-Rangamati 132 kV line-1
Chowmuhani | 2 | 2:03 | 86 | 176.3 | Due to red-hot maintenance of 132/33 kV Transformer T1
|  | 1:40 | 10 | 16.6667 | Due to Oil leakage of tripping of 132/33 kV Transformer-T2
Cumilla (N) | 1 | 0:19 | 10 | 3.1667 | Due to 33 feeder fault of 132/33 kV Transformer T3
Shahjibazar | 1 | 0:15 | 20 | 5 | Due to tripping of 132/33 kV Transformer-T3
Cumilla (N) | 1 | 0:17 | 40 | 11.3333 | Due to tripping of 132/33 kV Transformers-T3 & T4
Fenchuganj | 1 | 0:12 | 45 | 9 | Due to tripping of Fenchuganj-Kulaura 132 kV line-1 & 2
Chowmuhani | 1 | 4:54 | 20 | 98 | Due to S/D of132/33 kV Transformer-T1
APSCL |  | 0:19 | 218 | 69.0333 | Due to S/D of132 kV reserve Bus
Feni | 1 | 0:58 | 21 | 20.3 | Due to S/D of 132/33 kV Transformer T1
Chowmuhani | 1 | 3:28 | 12 | 41.6 | Due to S/D of 230/132 kV Transformer T2
Page: 2/2 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:October' 2020
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Bagerhat | 1 | 0:31 | 10 | 5.1667 | Due to tripping of 132/33 kV Transformer-T2
Madaripur | 1 | 2:15 | 10 | 22.5 | Due to tripping of 132/33 kV Transformer-T3
Noapara | 1 | 0:25 | 45 | 18.75 | Due to tripping of 132/33 kV Transformer-T4
Bagerhat | 1 | 0:05 | 24 | 2 | Due to tripping of 132/33 kV Transformers-T1 ,& T2
Gopalganj(O) | 1 | 0:51 | 20 | 17 | Due to red-hot maintenance of 132/33 kV Transformer T1
Mongla | 1 | 0:12 | 26 | 5.2 | Due to tripping of 132/33 kV Transformer-T1
Magura | 1 | 0:25 | 20 | 8.3333 | Due to tripping of 132/33 kV Transformers-T1 ,& T2
Gopalganj(N) | 1 | 0:07 | 50 | 5.8333 | Due to tripping of Gopalganj(N)-Gopalganj (O) 132 kV line
Barishal(N) | 1 | 0:45 | 30 | 22.5 | Due to tripping of Barisal(N)-Bhola 230 kV lie
Faridpur | 1 | 6:08 | 70 | 429.3333 | Due to S/D of132/33 kV Transformer-T2
Bagerhat | 2 | 3:06 | 48 | 148.8 | Due to S/D of132/33 kV Transformer-T1 & T3
|  | 3:56 | 65 | 255.6667 | Due to S/D of 132 kV Bus
Magura | 1 | 2:01 | 22 | 44.3667 | Due to S/D of132/33 kV Transformer-T2
Jessore | 1 | 0:29 | 50 | 24.1667 | Due to tripping of 132/33 kV Transformers-T1 ,& T2
Bheramara | 2 | 1:11 | 50 | 59.1667 | Due to tripping of 230/132 kV Transformer-GT2
|  | 1:53 | 12 | 22.6 | Due to red-hot maintenance of 132/33 kV Transformer T1
Bottail |  | 2:13 | 20 | 44.3333 | Due to tripping of 132/33 kV Transformer-T2
Bottail | 2 | 1:41 | 28 | 47.1333 | Due to S/D of 132/33 kV Transformer T2
|  | 1:56 | 60 | 116 | Due to S/D of 132/33 kV Transformer T1
Palashbari |  | 1:20 | 22 | 29.3333 | Due to S/D of 132/33 kV Transformer T1
Noapara |  | 0:11 | 27 | 4.95 | Due to tripping of 132/33 kV Transformer-T3
Rajshahi |  | 0:07 | 74 | 8.6333 | Due to tripping of 132/33 kV Transformers-T2 ,& T3
Naogaon |  | 0:11 | 32 | 5.8667 | Due to tripping of 132/33 kV Transformer-T3
Noapara |  | 1:02 | 34 | 35.1333 | Due to tripping of 132/33 kV Transformers-T1 ,& T2
Barapukuria |  | 0:21 | 730 | 255.5 | Due to tripping of Barapukuria 132 kv line- 1 & 2
Rangpur |  | 8:39 | 15 | 129.75 | Due to S/D of 132/33 kV Transformer T2
Rajshahi |  | 0:10 | 18 | 3 | Due to S/D of 132/33 kV Transformer T1
Panchagar |  | 9:05 | 20 | 181.6667 | Due to S/D of 132/33 kV Transformer T3
Rajshahi |  | 3:03 | 22 | 67.1
Natore |  | 2:17 | 20 | 45.6667 | Due to S/D of 132/33 kV Transformer T2
GK.project |  | 1:26 | 36 | 51.6 | Due to tripping of 132/33 kV Transformer-T2
| Total Unserved energy : |  |  | 4251.9333 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:October'2020
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 134 | 12 | 2020-10-01 | 15:00
2 | Munsiganj | 130 | 8 | 2020-10-01 | 0:00
3 | Sonargaon | 88 | 14 | 2020-10-01 | 18:30
4 | Shyampur | 210 | 21 | 2020-10-01 | 10:00
5 | Bhulta | 207 | 4 | 2020-10-01 | 22:00
6 | Madanganj | 65 | 31 | 2020-10-01 | 20:00
7 | Shitalakhya | 128 | 12 | 2020-10-01 | 12:00
8 | Rahim steel | 25 | 10 | 2020-10-01 | 12:00
9 | Matuail | 87 | 5 | 2020-10-01 | 9:00
10 | Ghorasal | 90 | 6 | 2020-10-01 | 7:00
11 | Narsingdi | 179 | 13 | 2020-10-01 | 20:00
12 | Haripur (SBU) | 118 | 13 | 2020-10-01 | 11:00
13 | Ullon | 65 | 12 | 2020-10-01 | 13:00
14 | Hasnabad | 220 | 18 | 2020-10-01 | 20:00
15 | Magbazar | 113 | 1 | 2020-10-01 | 11:00
16 | Maniknagar | 106 | 18 | 2020-10-01 | 16:00
17 | Bangabhaban | 40 | 11 | 2020-10-01 | 10:00
18 | Narinda | 94 | 8 | 2020-10-01 | 13:00
19 | Dhanmondi | 212 | 11 | 2020-10-01 | 12:00
20 | Lalbag | 101 | 11 | 2020-10-01 | 16:00
21 | Madartek | 76 | 1 | 2020-10-01 | 20:00
22 | Dhaka University | - | - | - | -
23 | Fatullah | 48 | 5 | 2020-10-01 | 20:00
24 | Mirpur | 120 | 12 | 2020-10-01 | 18:00
25 | Kalyanpur | 111 | 17 | 2020-10-01 | 18:00
26 | Gulshan | 144 | 13 | 2020-10-01 | 13:00
27 | Uttara | 104 | 20 | 2020-10-01 | 13:00
28 | Uttara(new) | 41 | 17 | 2020-10-01 | 18:00
29 | Kamrangirchar | 101 | 17 | 2020-10-01 | 18:00
30 | Savar | 155 | 19 | 2020-10-01 | 18:30
31 | Bhasantec | 164 | 13 | 2020-10-01 | 13:00
32 | Agargaon | 80 | 13 | 2020-10-01 | 13:00
33 | Satmosjid | 123 | 11 | 2020-10-01 | 18:00
34 | Tongi | 120 | 18 | 2020-10-01 | 15:00
35 | Kabirpur | 253 | 21 | 2020-10-01 | 14:00
36 | Basundhara | 157 | 18 | 2020-10-01 | 13:00
37 | Manikganj | 80 | 9 | 2020-10-01 | 21:00
38 | Joydevpur | 170 | 17 | 2020-10-01 | 18:30
39 | New Tongi | 112 | 14 | 2020-10-01 | 12:00
40 | Kodda | 248 | 6 | 2020-10-01 | 18:30
41 | Dhamrai | 100 | 11 | 2020-10-01 | 18:30
42 | Rajendrapur | 112 | 13 | 2020-10-01 | 21:00
43 | Valuka | 138 | 4 | 2020-10-01 | 18:30
44 | Tangail | 208 | 11 | 2020-10-01 | 20:00
45 | Mymensing | 226 | 18 | 2020-10-01 | 19:30
46 | Kishorganj | 156 | 18 | 2020-10-01 | 20:00
47 | Netrokona | 117 | 12 | 2020-10-01 | 19:00
48 | Jamalpur | 151 | 13 | 2020-10-01 | 20:00
49 | Sherpur | 114 | 11 | 2020-10-01 | 19:00
50 | Srimongal | 63 | 10 | 2020-10-01 | 14:00
Page: 2/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:October'2020
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
51 | Shahjibazar | 129 | 14 | 2020-10-01 | 21:00
52 | Fenchuganj | 53 | 1 | 2020-10-01 | 18:00
53 | Kulawara | 50 | 12 | 2020-10-01 | 18:30
54 | Sylhet | 152 | 10 | 2020-10-01 | 18:00
55 | Chatak | 34 | 11 | 2020-10-01 | 19:30
56 | Sunamganj | 51 | 12 | 2020-10-01 | 19:30
57 | Bianibazar | 71 | 21 | 2020-10-01 | 19:00
58 | Cumilla (S) | 180 | 13 | 2020-10-01 | 18:00
59 | Cumilla(N) | 147 | 11 | 2020-10-01 | 20:00
60 | Chandpur | 111 | 9 | 2020-10-01 | 22:00
61 | Feni | 139 | 10 | 2020-10-01 | 19:30
62 | Chowmuhani | 194 | 15 | 2020-10-01 | 19:30
63 | Ashuganj | 64 | 1 | 2020-10-01 | 20:00
64 | Daudkandi | 155 | 10 | 2020-10-01 | 19:30
65 | B.Baria | 168 | 17 | 2020-10-01 | 20:00
66 | Ramganj | 126 | 10 | 2020-10-01 | 22:00
67 | Chaddagram | 51 | 20 | 2020-10-01 | 20:00
68 | PHP | 11 | 3 | 2020-10-01 | 19:00
69 | Madanhat | 65 | 31 | 2020-10-01 | 18:00
70 | Hathazari | 107 | 12 | 2020-10-01 | 19:00
71 | Khulshi | 222 | 28 | 2020-10-01 | 13:00
72 | Halishahar | 166 | 11 | 2020-10-01 | 15:00
73 | Baraulia | 169 | 11 | 2020-10-01 | 0:00
74 | Sikalbaha | 29 | 10 | 2020-10-01 | 19:30
75 | Dohazari | 96 | 19 | 2020-10-01 | 22:00
76 | Cox'sbazar | 120 | 25 | 2020-10-01 | 15:00
77 | Chandraghona | 42 | 18 | 2020-10-01 | 4:00
78 | Kaptai | 4.8 | 3 | 2020-10-01 | 18:00
79 | A. Khaer Stl. | 20 | 16 | 2020-10-01 | 19:00
80 | Bakulia | 125 | 17 | 2020-10-01 | 15:00
81 | Julda | 26 | 4 | 2020-10-01 | 11:00
82 | TK chemical | 32.4 | 10 | 2020-10-01 | 21:00
83 | Modern Steel | 16 | 4 | 2020-10-01 | 2:00
84 | Shahmirpur | 30 | 3 | 2020-10-01 | 21:00
85 | Khagrachhari | 28 | 9 | 2020-10-01 | 4:00
86 | Matarbari | 40.5 | 3 | 2020-10-01 | 19:30
87 | Baroiar Hat | 60 | 2 | 2020-10-01 | 18:30
88 | Rangamati | 13 | 10 | 2020-10-01 | 18:00
89 | Abul Khair 230 | 67 | 10 | 2020-10-01 | 4:00
90 | BSRM | 163 | 27 | 2020-10-01 | 9:00
91 | GPH Ispat | 90 | 8 | 2020-10-01 | 11:00
92 | Goalpara | 30 | 11 | 2020-10-01 | 23:00
93 | Central s/s | 93 | 17 | 2020-10-01 | 20:00
94 | Noapara | 65 | 10 | 2020-10-01 | 18:00
95 | Jashore | 121 | 8 | 2020-10-01 | 20:00
96 | Benapol | 54 | 10 | 2020-10-01 | 21:00
97 | Jhenidah | 115 | 8 | 2020-10-01 | 18:30
98 | Bottail | 140 | 15 | 2020-10-01 | 18:30
Page: 3/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:October'2020
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
99 | G.K Project | 67 | 5 | 2020-10-01 | 20:00
100 | Faridpur | 208 | 11 | 2020-10-01 | 21:00
101 | Madaripur | 107 | 15 | 2020-10-01 | 22:00
102 | Sariatpur | 70 | 8 | 2020-10-01 | 22:00
103 | Gopalganj | 99 | 17 | 2020-10-01 | 19:30
104 | Bagerhat | 106 | 17 | 2020-10-01 | 22:00
105 | Mongla | 40 | 1 | 2020-10-01 | 12:00
106 | Satkhira | 116 | 19 | 2020-10-01 | 21:00
107 | Gallamari | 52 | 12 | 2020-10-01 | 13:00
108 | Magura | 55 | 3 | 2020-10-01 | 19:00
109 | Norail | 52 | 9 | 2020-10-01 | 21:00
110 | Chuadanga | 95 | 18 | 2020-10-01 | 19:30
111 | Barsal(N) | 54 | 17 | 2020-10-01 | 22:00
112 | Barsal(S) | 112 | 10 | 2020-10-01 | 20:00
113 | Patuakhali | 129 | 12 | 2020-10-01 | 22:00
114 | Bhandaria | 60 | 17 | 2020-10-01 | 20:00
115 | Borhan Uddin | 46 | 12 | 2020-10-01 | 1:00
116 | Ishurdi | 70 | 10 | 2020-10-01 | 21:00
117 | Ruppur Paromanobik | 3 | 4 | 2020-10-01 | 16:00
118 | Natore | 136 | 11 | 2020-10-01 | 20:00
119 | Bogura | 176 | 12 | 2020-10-01 | 18:30
120 | Naogaon | 120 | 14 | 2020-10-01 | 21:00
121 | Rajshahi | 158 | 14 | 2020-10-01 | 22:00
122 | Rajshahi New | 18 | 13 | 2020-10-01 | 21:00
123 | C.Nawabganj | 78 | 20 | 2020-10-01 | 20:00
124 | Amnura | 48 | 21 | 2020-10-01 | 19:30
125 | Pabna | 136 | 17 | 2020-10-01 | 19:00
126 | Shahjadpur | 112 | 12 | 2020-10-01 | 18:30
127 | Serajganj | 122 | 13 | 2020-10-01 | 19:30
128 | Niyamatpur | 67 | 13 | 2020-10-01 | 21:00
129 | Joypurhat | 62 | 8 | 2020-10-01 | 19:00
130 | Sherpur(Bogura) | 51 | 13 | 2020-10-01 | 18:30
131 | Mohastangar | 62 | 18 | 2020-10-01 | 19:30
132 | Rangpur | 158 | 14 | 2020-10-01 | 20:00
133 | Lalmonirhat | 60 | 9 | 2020-10-01 | 19:00
134 | Saidpur | 118 | 13 | 2020-10-01 | 18:30
135 | Purbasadipur | 104 | 14 | 2020-10-01 | 18:30
136 | Thakurgaon | 84 | 8 | 2020-10-01 | 21:00
137 | Palshbari | 127 | 10 | 2020-10-01 | 20:00
138 | Barapukuria | 55 | 10 | 2020-10-01 | 21:00
139 | Panchugar | 53 | 9 | 2020-10-01 | 18:30
140 | Joldhaka | 36 | 12 | 2020-10-01 | 19:00
141 | Kurigram | 59 | 9 | 2020-10-01 | 18:30
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:October' 2020
Area | MW | Date | Hour | Remarks
Dhaka | 4394 | 18.10.2020 | 18:30
Chattogram | 1317 | 08.10.2020 | 23:00
Khulna | 1550 | 17.10.2020 | 20:00
Rajshahi | 1322 | 14.10.2020 | 21:00
Cumilla | 1278 | 10.10.2020 | 20:00
Mymensingh | 1008 | 15.10.2020 | 22:00
Sylhet | 561 | 17.10.2020 | 20:00
Barisal | 385 | 17.10.2020 | 22:00
Rangpur | 785 | 17.10.2020 | 18:30
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: October'2020
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 418 | 23 | 2020-10-01 | 6:00 | 385 | 4 | 2020-10-01 | 12:00
2 | Bheramara | 400 | 414 | 10 | 2020-10-01 | 1:00 | 382 | 16 | 2020-10-01 | 18:30
3 | Ashuganj(N) | 400 | 395 | 2 | 2020-10-01 | 13:00 | 359 | 25 | 2020-10-01 | 10:00
4 | Payra | 400 | 422 | 23 | 2020-10-01 | 18:00 | 391 | 9 | 2020-10-01 | 19:00
5 | Kaliakoir | 400 | 412 | 23 | 2020-10-01 | 7:00 | 328 | 10 | 2020-10-01 | 10:00
6 | Bhulta | 400 | 392 | 2 | 2020-10-01 | 6:00 | 355 | 25 | 2020-10-01 | 10:00
7 | Gopalganj | 400 | 426 | 23 | 2020-10-01 | 9:00 | 380 | 12 | 2020-10-01 | 18:30
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 238 | 4 | 2020-10-01 | 1:00 | 220 | 13 | 2020-10-01 | 10:00
2 | Ishurdi | 230 | 238 | 23 | 2020-10-01 | 5:00 | 223 | 10 | 2020-10-01 | 18:30
3 | Ashuganj | 230 | 238 | 2 | 2020-10-01 | 18:30 | 224 | 17 | 2020-10-01 | 10:00
4 | Serajganj | 230 | 232 | 1 | 2020-10-01 | 5:00 | 221 | 14 | 2020-10-01 | 20:00
5 | Baghabari | 230 | 244 | 11 | 2020-10-01 | 17:00 | 230 | 6 | 2020-10-01 | 13:00
6 | Barapukuria | 230 | 240 | 8 | 2020-10-01 | 19:00 | 224 | 8 | 2020-10-01 | 19:30
7 | Bogura | 230 | 229 | 8 | 2020-10-01 | 19:00 | 212 | 4 | 2020-10-01 | 20:00
8 | Rajshahi | 230 | 231 | 1 | 2020-10-01 | 17:00 | 213 | 6 | 2020-10-01 | 13:00
9 | Khulna South | 230 | 238 | 7 | 2020-10-01 | 17:00 | 206 | 26 | 2020-10-01 | 13:00
10 | Rampura | 230 | 230 | 2 | 2020-10-01 | 15:00 | 211 | 13 | 2020-10-01 | 10:00
11 | Haripur | 230 | 232 | 2 | 2020-10-01 | 19:00 | 209 | 13 | 2020-10-01 | 11:00
12 | Hasnabad | 230 | 230 | 1 | 2020-10-01 | 19:30 | 208 | 13 | 2020-10-01 | 11:00
13 | Shyampur | 230 | 229 | 2 | 2020-10-01 | 19:00 | 206 | 13 | 2020-10-01 | 11:00
14 | Aminbazar | 230 | 231 | 2 | 2020-10-01 | 18:00 | 205 | 13 | 2020-10-01 | 11:00
15 | Tongi | 230 | 231 | 2 | 2020-10-01 | 23:00 | 204 | 22 | 2020-10-01 | 12:00
16 | Comilla (N) | 230 | 239 | 3 | 2020-10-01 | 18:30 | 219 | 10 | 2020-10-01 | 11:00
17 | Hathazari | 230 | 229 | 2 | 2020-10-01 | 14:00 | 217 | 15 | 2020-10-01 | 10:00
18 | Megnaghat | 230 | 234 | 2 | 2020-10-01 | 17:00 | 213 | 19 | 2020-10-01 | 13:00
19 | Fenchuganj | 230 | 246 | 23 | 2020-10-01 | 18:00 | 230 | 4 | 2020-10-01 | 13:00
20 | Siddhirganj | 230 | 234 | 3 | 2020-10-01 | 1:00 | 210 | 12 | 2020-10-01 | 7:00
21 | Maniknagar | 230 | 232 | 2 | 2020-10-01 | 18:30 | 209 | 13 | 2020-10-01 | 11:00
22 | Old Airport | 230 | 230 | 2 | 2020-10-01 | 6:00 | 204 | 10 | 2020-10-01 | 10:00
23 | Barisal | 230 | 252 | 31 | 2020-10-01 | 19:00 | 214 | 4 | 2020-10-01 | 13:00
24 | AKSML | 230 | 226 | 2 | 2020-10-01 | 14:00 | 214 | 13 | 2020-10-01 | 13:00
25 | BSRM | 230 | 229 | 2 | 2020-10-01 | 15:00 | 214 | 10 | 2020-10-01 | 11:00
26 | Bibiyana | 230 | 244 | 23 | 2020-10-01 | 18:00 | 228 | 3 | 2020-10-01 | 20:00
27 | Bhulta | 230 | 234 | 2 | 2020-10-01 | 19:00 | 212 | 13 | 2020-10-01 | 17:00
28 | Ashuganj (S) | 230 | 235 | 2 | 2020-10-01 | 14:00 | 221 | 17 | 2020-10-01 | 17:00
29 | Kaliakoir | 230 | 235 | 5 | 2020-10-01 | 4:00 | 204 | 14 | 2020-10-01 | 11:00
30 | GPH | 230 | 224 | 2 | 2020-10-01 | 18:00 | 212 | 17 | 2020-10-01 | 10:00
132 kV Substation
1 | Siddhirganj | 132 | 137 | 22 | 2020-10-01 | 0.91667 | 120 | 10 | 2020-10-01 | 0.41667
2 | Munsiganj | 132 | 138 | 24 | 2020-10-01 | 0.75 | 119 | 10 | 2020-10-01 | 0.41667
3 | Sonargaon | 132 | 138 | 23 | 2020-10-01 | 0.77083 | 120 | 8 | 2020-10-01 | 0.625
4 | Shyampur | 132 | 139 | 23 | 2020-10-01 | 0.375 | 121 | 10 | 2020-10-01 | 0.41667
5 | Bhulta | 132 | 130 | 23 | 2020-10-01 | 0.125 | 114 | 11 | 2020-10-01 | 0.5
6 | Madanganj | 132 | 136 | 17 | 2020-10-01 | 0.20833 | 118 | 10 | 2020-10-01 | 0.41667
7 | Shitalakhya | 132 | 143 | 3 | 2020-10-01 | 0.041667 | 118 | 10 | 2020-10-01 | 0.41667
8 | Rahim Steal | 132 | 137 | 23 | 2020-10-01 | 0.75 | 120 | 10 | 2020-10-01 | 0.41667
9 | Matuail | 132 | 137 | 22 | 2020-10-01 | 0.91667 | 121 | 8 | 2020-10-01 | 0.54167
10 | Ghorasal | 132 | 140 | 3 | 2020-10-01 | 0.041667 | 132 | 10 | 2020-10-01 | 0.45833
11 | Narsinghdi | 132 | 134 | 23 | 2020-10-01 | 0.58333 | 113 | 10 | 2020-10-01 | 0.45833
12 | Haripur (SBU) | 132 | 138 | 23 | 2020-10-01 | 0.77083 | 120 | 10 | 2020-10-01 | 0.41667
13 | Ullon | 132 | 139 | 22 | 2020-10-01 | 0.91667 | 122 | 12 | 2020-10-01 | 0.41667
14 | Hasnabad | 132 | 140 | 3 | 2020-10-01 | 0.083333 | 123 | 12 | 2020-10-01 | 0.41667
15 | Magbazar | 132 | 138 | 20 | 2020-10-01 | 0.25 | 118 | 29 | 2020-10-01 | 0.79167
16 | Maniknagar | 132 | 137 | 23 | 2020-10-01 | 0.77083 | 118 | 4 | 2020-10-01 | 0.5
17 | Bangabhaban | 132 | 137 | 23 | 2020-10-01 | 0.77083 | 118 | 4 | 2020-10-01 | 0.5
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: October'2020
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
18 | Narinda | 132 | 137 | 23 | 2020-10-01 | 0.77083 | 118 | 4 | 2020-10-01 | 0.5
19 | Dhanmondi | 132 | 139 | 22 | 2020-10-01 | 0.91667 | 122 | 12 | 2020-10-01 | 0.41667
20 | Lalbag | 132 | 140 | 3 | 2020-10-01 | 0.041667 | 118 | 12 | 2020-10-01 | 0.45833
21 | Madartek | 132 | 138 | 22 | 2020-10-01 | 0.91667 | 122 | 11 | 2020-10-01 | 0.45833
22 | Dhaka University | 132 | - | - | - | - | - | - | - | -
23 | Fatullah | 132 | 139 | 23 | 2020-10-01 | 0.375 | 122 | 10 | 2020-10-01 | 0.41667
24 | Mirpur | 132 | 138 | 3 | 2020-10-01 | 0.25 | 120 | 10 | 2020-10-01 | 0.5
25 | Kalyanpur | 132 | 138 | 3 | 2020-10-01 | 0.25 | 122 | 10 | 2020-10-01 | 0.41667
26 | Gulshan | 132 | 138 | 22 | 2020-10-01 | 0.91667 | 121 | 12 | 2020-10-01 | 0.45833
27 | Uttara | 132 | 138 | 23 | 2020-10-01 | 0.75 | 119 | 13 | 2020-10-01 | 0.45833
28 | Uttara(New) | 132 | 137 | 3 | 2020-10-01 | 0.20833 | 118 | 10 | 2020-10-01 | 0.41667
29 | Kamrangirchar | 132 | 139 | 1 | 2020-10-01 | 0.75 | 118 | 13 | 2020-10-01 | 0.45833
30 | Savar | 132 | 137 | 3 | 2020-10-01 | 0.25 | 120 | 10 | 2020-10-01 | 0.41667
31 | Bhasantec | 132 | 139 | 3 | 2020-10-01 | 0.25 | 117 | 14 | 2020-10-01 | 0.54167
32 | Agargaon | 132 | 140 | 3 | 2020-10-01 | 0.25 | 120 | 14 | 2020-10-01 | 0.54167
33 | Satmosjid | 132 | 140 | 3 | 2020-10-01 | 0.25 | 119 | 14 | 2020-10-01 | 0.54167
34 | Tongi | 132 | 141 | 0 | 2020-10-01 | 0.41667 | 124 | 13 | 2020-10-01 | 0.45833
35 | Kabirpur | 132 | 138 | 11 | 2020-10-01 | 0.54167 | 115 | 10 | 2020-10-01 | 0.41667
36 | Basundhara | 132 | 139 | 22 | 2020-10-01 | 0.91667 | 121 | 13 | 2020-10-01 | 0.41667
37 | Manikganj | 132 | 141 | 23 | 2020-10-01 | 0.75 | 122 | 12 | 2020-10-01 | 0.33333
38 | Joydevpur | 132 | 142 | 3 | 2020-10-01 | 0.54167 | 128 | 12 | 2020-10-01 | 0.375
39 | New Tongi | 132 | 139 | 23 | 2020-10-01 | 0.75 | 118 | 10 | 2020-10-01 | 0.41667
40 | Kodda | 132 | 139 | 16 | 2020-10-01 | 0.79167 | 120 | 13 | 2020-10-01 | 0.45833
41 | Dhamrai | 132 | 139 | 23 | 2020-10-01 | 0.75 | 114 | 10 | 2020-10-01 | 0.41667
42 | Rajendrapur | 132 | 138 | 16 | 2020-10-01 | 0.41667 | 118 | 10 | 2020-10-01 | 0.41667
43 | Valuka | 132 | 134 | 23 | 2020-10-01 | 0.75 | 105 | 10 | 2020-10-01 | 0.79167
44 | Tangail | 132 | 138 | 25 | 2020-10-01 | 0.29167 | 115 | 17 | 2020-10-01 | 0.75
45 | Mymensing | 132 | 137 | 23 | 2020-10-01 | 0.77083 | 112 | 3 | 2020-10-01 | 0.875
46 | Kishorganj | 132 | 137 | 23 | 2020-10-01 | 0.75 | 114 | 8 | 2020-10-01 | 0.77083
47 | Netrokona | 132 | 135 | 23 | 2020-10-01 | 0.75 | 107 | 12 | 2020-10-01 | 0.875
48 | Jamalpur | 132 | 139 | 1 | 2020-10-01 | 0.54167 | 120 | 1 | 2020-10-01 | 0.875
49 | Sherpur | 132 | 139 | 1 | 2020-10-01 | 0.70833 | 119 | 31 | 2020-10-01 | 0.54167
50 | Srimongal | 132 | 141 | 23 | 2020-10-01 | 0.79167 | 126 | 15 | 2020-10-01 | 0.8125
51 | Shahjibazar | 132 | 139 | 23 | 2020-10-01 | 0.75 | 126 | 8 | 2020-10-01 | 0.8125
52 | Fenchuganj | 132 | 139 | 23 | 2020-10-01 | 0.83333 | 126 | 14 | 2020-10-01 | 0.77083
53 | Khulawara | 132 | 137 | 23 | 2020-10-01 | 0.77083 | 125 | 14 | 2020-10-01 | 0.79167
54 | Sylhet | 132 | 138 | 1 | 2020-10-01 | 0.75 | 119 | 15 | 2020-10-01 | 0.8125
55 | Chattak | 132 | 135 | 23 | 2020-10-01 | 0.83333 | 115 | 14 | 2020-10-01 | 0.77083
56 | Sunamganj | 132 | 135 | 23 | 2020-10-01 | 0.83333 | 112 | 14 | 2020-10-01 | 0.8125
57 | Biani Bazar | 132 | 135 | 21 | 2020-10-01 | 0.25 | 117 | 14 | 2020-10-01 | 0.77083
58 | Comilla(South) | 132 | 130 | 7 | 2020-10-01 | 0.25 | 116 | 15 | 2020-10-01 | 0.75
59 | Comilla (North) | 132 | 141 | 1 | 2020-10-01 | 0.77083 | 127 | 10 | 2020-10-01 | 0.45833
60 | Chandpur | 132 | 140 | 1 | 2020-10-01 | 0.041667 | 120 | 16 | 2020-10-01 | 0.75
61 | Feni | 132 | 137 | 1 | 2020-10-01 | 0.77083 | 123 | 15 | 2020-10-01 | 0.625
62 | Chowmuhani | 132 | 135 | 3 | 2020-10-01 | 0.29167 | 120 | 16 | 2020-10-01 | 0.75
63 | Ashuganj | 132 | 138 | 23 | 2020-10-01 | 0.79167 | 126 | 8 | 2020-10-01 | 0.79167
64 | Daudkandi | 132 | 138 | 3 | 2020-10-01 | 0.77083 | 120 | 10 | 2020-10-01 | 0.45833
65 | Brahminbaria | 132 | 136 | 23 | 2020-10-01 | 0.77083 | 121 | 8 | 2020-10-01 | 0.79167
66 | Ramganj | 132 | 132 | 5 | 2020-10-01 | 0.83333 | 118 | 15 | 2020-10-01 | 0.5
67 | Chaddagram | 132 | 138 | 1 | 2020-10-01 | 0.79167 | 125 | 10 | 2020-10-01 | 0.5
68 | PHP | 132 | 136 | 6 | 2020-10-01 | 0.75 | 121 | 30 | 2020-10-01 | 0.41667
69 | Madanhat | 132 | 137 | 1 | 2020-10-01 | 0.77083 | 130 | 6 | 2020-10-01 | 0.5
70 | Hathazari | 132 | 136 | 4 | 2020-10-01 | 0.875 | 130 | 5 | 2020-10-01 | 0.20833
71 | Khulshi | 132 | 134 | 4 | 2020-10-01 | 0.875 | 125 | 17 | 2020-10-01 | 0.375
72 | Halishahar | 132 | 136 | 3 | 2020-10-01 | 0.083333 | 124 | 17 | 2020-10-01 | 0.41667
73 | Baraulia | 132 | 135 | 1 | 2020-10-01 | 0.083333 | 126 | 19 | 2020-10-01 | 0.45833
74 | Sikalbaha | 132 | 137 | 1 | 2020-10-01 | 0.8125 | 127 | 17 | 2020-10-01 | 0.41667
75 | Dohazari | 132 | 135 | 10 | 2020-10-01 | 0.041667 | 123 | 4 | 2020-10-01 | 0.41667
76 | Cox'sbazar | 132 | 130 | 22 | 2020-10-01 | 0.77083 | 110 | 10 | 2020-10-01 | 0.70833
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: October'2020
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
77 | Chandraghona | 132 | 136 | 22 | 2020-10-01 | 0.75 | 129 | 15 | 2020-10-01 | 0.45833
78 | Kaptai | 132 | 135 | 1 | 2020-10-01 | 0.91667 | 130 | 5 | 2020-10-01 | 0.58333
79 | A. Khaer Stl. | 132 | 135 | 1 | 2020-10-01 | 0.41667 | 126 | 19 | 2020-10-01 | 0.45833
80 | Bakulia | 132 | 135 | 1 | 2020-10-01 | 0.77083 | 126 | 17 | 2020-10-01 | 0.41667
81 | Julda | 132 | 137 | 30 | 2020-10-01 | 0.75 | 128 | 25 | 2020-10-01 | 0.29167
82 | TK Chemical | 132 | 136 | 4 | 2020-10-01 | 0 | 128 | 25 | 2020-10-01 | 0.375
83 | Modern Steel | 132 | 135 | 1 | 2020-10-01 | 0.875 | 126 | 6 | 2020-10-01 | 0.54167
84 | Shahmirpur | 132 | 137 | 30 | 2020-10-01 | 0.75 | 127 | 17 | 2020-10-01 | 0.41667
85 | Khagrachhari | 132 | 135 | 22 | 2020-10-01 | 0.75 | 127 | 6 | 2020-10-01 | 0.5
86 | Matarbari | 132 | 133 | 24 | 2020-10-01 | 0.041667 | 115 | 11 | 2020-10-01 | 0.54167
87 | Baroiar Hat | 132 | 138 | 22 | 2020-10-01 | 0.54167 | 123 | 15 | 2020-10-01 | 0.5
88 | Rangamati | 132 | 139 | 25 | 2020-10-01 | 0.54167 | 128 | 15 | 2020-10-01 | 0.45833
89 | Goalpara | 132 | 141 | 30 | 2020-10-01 | 0.25 | 120 | 9 | 2020-10-01 | 0.95833
90 | Khulna Central | 132 | 141 | 30 | 2020-10-01 | 0.25 | 121 | 9 | 2020-10-01 | 0.95833
91 | Noapara | 132 | 139 | 30 | 2020-10-01 | 0.25 | 119 | 31 | 2020-10-01 | 0.54167
92 | Jessore | 132 | 137 | 30 | 2020-10-01 | 0.25 | 113 | 9 | 2020-10-01 | 0.95833
93 | Benapol | 132 | 137 | 30 | 2020-10-01 | 0.25 | 116 | 9 | 2020-10-01 | 0.91667
94 | Jhenida | 132 | 134 | 28 | 2020-10-01 | 0.25 | 107 | 10 | 2020-10-01 | 0.77083
95 | Bottail | 132 | 139 | 23 | 2020-10-01 | 0.25 | 120 | 10 | 2020-10-01 | 0.77083
96 | G.K Project | 132 | 143 | 21 | 2020-10-01 | 0.70833 | 132 | 10 | 2020-10-01 | 0.79167
97 | Faridpur | 132 | 140 | 23 | 2020-10-01 | 0.25 | 122 | 10 | 2020-10-01 | 0.77083
98 | Madaripur | 132 | 144 | 23 | 2020-10-01 | 0.41667 | 127 | 3 | 2020-10-01 | 0.77083
99 | Sariatpur | 132 | 143 | 23 | 2020-10-01 | 0.41667 | 124 | 15 | 2020-10-01 | 0.95833
100 | Gopalganj | 132 | 144 | 23 | 2020-10-01 | 0.25 | 122 | 9 | 2020-10-01 | 0.91667
101 | Bagerhat | 132 | 141 | 23 | 2020-10-01 | 0.375 | 113 | 9 | 2020-10-01 | 0.91667
102 | Mongla | 132 | 138 | 30 | 2020-10-01 | 0.25 | 110 | 9 | 2020-10-01 | 0.95833
103 | Satkhira | 132 | 140 | 28 | 2020-10-01 | 0.25 | 117 | 9 | 2020-10-01 | 0.91667
104 | Gallamari | 132 | 141 | 28 | 2020-10-01 | 0.25 | 122 | 9 | 2020-10-01 | 0.95833
105 | Magura | 132 | 135 | 28 | 2020-10-01 | 0.25 | 105 | 9 | 2020-10-01 | 0.91667
106 | Norail | 132 | 132 | 30 | 2020-10-01 | 0.25 | 104 | 9 | 2020-10-01 | 0.91667
107 | Chuadanga | 132 | 131 | 28 | 2020-10-01 | 0.25 | 97 | 10 | 2020-10-01 | 0.77083
108 | Barisal(N) | 132 | 145 | 23 | 2020-10-01 | 0.41667 | 122 | 4 | 2020-10-01 | 0.54167
109 | Barisal(S) | 132 | 145 | 23 | 2020-10-01 | 0.41667 | 119 | 18 | 2020-10-01 | 0.25
110 | Patuakhali | 132 | 143 | 23 | 2020-10-01 | 0.45833 | 118 | 4 | 2020-10-01 | 0.54167
111 | Bhandaria | 132 | 137 | 24 | 2020-10-01 | 0.33333 | 107 | 9 | 2020-10-01 | 0.95833
112 | Ishurdi | 132 | 140 | 23 | 2020-10-01 | 0.375 | 129 | 10 | 2020-10-01 | 0.77083
113 | Ruppur paromanobik | 132 | 140 | 23 | 2020-10-01 | 0.29167 | 130 | 15 | 2020-10-01 | 0.75
114 | Natore | 132 | 139 | 10 | 2020-10-01 | 0.70833 | 128 | 13 | 2020-10-01 | 0.375
115 | Bogra | 132 | 140 | 7 | 2020-10-01 | 0.70833 | 126 | 4 | 2020-10-01 | 0.83333
116 | Noagaon | 132 | 134 | 7 | 2020-10-01 | 0.25 | 118 | 4 | 2020-10-01 | 0.83333
117 | Rajshahi | 132 | 138 | 1 | 2020-10-01 | 0.54167 | 124 | 13 | 2020-10-01 | 0.375
118 | Rajshahi New | 132 | 140 | 1 | 2020-10-01 | 0.70833 | 121 | 5 | 2020-10-01 | 0.66667
119 | C.Nawabganj | 132 | 138 | 11 | 2020-10-01 | 0.70833 | 122 | 6 | 2020-10-01 | 0.33333
120 | Amnura | 132 | 140 | 11 | 2020-10-01 | 0.70833 | 123 | 13 | 2020-10-01 | 0.41667
121 | Pabna | 132 | 139 | 23 | 2020-10-01 | 0.375 | 127 | 10 | 2020-10-01 | 0.77083
122 | Shahjadpur | 132 | 141 | 23 | 2020-10-01 | 0.375 | 131 | 8 | 2020-10-01 | 0.041667
123 | Serajganj | 132 | 135 | 8 | 2020-10-01 | 0.75 | 126 | 8 | 2020-10-01 | 0.83333
124 | Niyamatpur | 132 | 134 | 7 | 2020-10-01 | 0.70833 | 115 | 4 | 2020-10-01 | 0.83333
125 | Joypurhat | 132 | 135 | 1 | 2020-10-01 | 0.66667 | 117 | 4 | 2020-10-01 | 0.83333
126 | Sherpur(Bogura) | 132 | 138 | 7 | 2020-10-01 | 0.70833 | 126 | 18 | 2020-10-01 | 0.83333
127 | Mohastangor | 132 | 138 | 11 | 2020-10-01 | 0.25 | 115 | 5 | 2020-10-01 | 0.54167
128 | Rangpur | 132 | 135 | 22 | 2020-10-01 | 0.25 | 113 | 15 | 2020-10-01 | 0.8125
129 | Lalmonirhat | 132 | 136 | 21 | 2020-10-01 | 0.25 | 115 | 13 | 2020-10-01 | 0.77083
130 | Saidpur | 132 | 135 | 13 | 2020-10-01 | 0.25 | 114 | 11 | 2020-10-01 | 0.77083
131 | Purbasadipur | 132 | 135 | 8 | 2020-10-01 | 0.25 | 107 | 10 | 2020-10-01 | 0.77083
132 | Thakurgaon | 132 | 132 | 28 | 2020-10-01 | 0.25 | 108 | 10 | 2020-10-01 | 0.77083
133 | Palashbari | 132 | 134 | 7 | 2020-10-01 | 0.70833 | 118 | 10 | 2020-10-01 | 0.79167
134 | Barapukuria | 132 | 144 | 8 | 2020-10-01 | 0.79167 | 124 | 8 | 2020-10-01 | 0.8125
135 | Panchagar | 132 | 132 | 31 | 2020-10-01 | 0.25 | 101 | 10 | 2020-10-01 | 0.77083
136 | Joldhaka | 132 | 134 | 24 | 2020-10-01 | 0.25 | 109 | 10 | 2020-10-01 | 0.77083
137 | Kurigram | 132 | 133 | 24 | 2020-10-01 | 0.25 | 109 | 15 | 2020-10-01 | 0.8125
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:October' 2020
Name of the | Auto transofrmer |  | Recorded maximum load
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kV side ) | Date | Time | Remarks
| TR1 | 225 | 130 | 420
Hasnabad | TR2 | 225 | 125 | 420 | 28.10.2020 | 10:00
| TR3 | 225 | 125 | 420
| TR1 | 225 | 192 | 550
Tongi | TR2 | 225 | 192 | 550 | 04.10.2020 | 15:00
| TR3 | 225 | 192 | 550
Haripur | TR1 | 225 | 115 | 330 | 28.10.2020 | 16:00
| TR2 | 225 | 115 | 330
| TR3 | 225 | 115 | 330
| TR1 | 225 | 178 | 510
Rampura | TR2 | 225 | 178 | 510
| TR3 | 225 | 178 | 510 | 08.10.2020 | 15:00
| TR1 | 225 | 145 | 420
Aminbazar | TR2 | 225 | 145 | 420
| TR3 | 225 | 151 | 420 | 17.10.2020 | 18:00
Maniknagar | TR1 | 300 | 151 | 435
| TR2 | 300 | 114 | 360 | 20.10.2020 | 13:00
Cumilla (N) | TR1 | 225 | 169 | 492
| TR2 | 225 | 167 | 484 | 21.10.2020 | 2:00
Fenchuganj | AT2 | 300 | 167 | 484
| MT1 | 150 | 68 | 200 | 07.10.2020 | 22:00
Hathazari | MT2 | 150 | 68 | 200
| MT3 | 150 | 68 | 200 |  | 07:00
| MT4 | 150 | 68 | 200
| TR1 | 225 | 140 | 400
Ishurdi | TR2 | 225 | 140 | 400
| TR3 | 225 | 140 | 400 | 10.10.2020 | 20:00
Khulna(S) | TR1 | 225 | 117 | 332
| TR2 | 225 | 117 | 332
| TR3 | 300 | 117 | 332 | 10.10.2020 | 18:30
Bogra | TR1 | 225 | 102 | 316
| TR2 | 225 | 102 | 316 | 03.10.2020 | 20:00
| TR3 | 225 | 139 | 416
Baghabari | TR1 | 300 | 138 | 375
| TR2 | 225 | 103 | 280 | 06.10.2020 | 21:00
Barapukuria | TR1 | 225 | 146 | 740 |  |  | Due to unavailability of 230 kV side meters
| TR2 | 225 | 154 | 760 | 15.10.2020 | 19:30 | 132 kV current is being provided
| TR6 | 300 | 197 | 992
Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:October' 2020
Name of the | Transofrmer |  | Recorded maximum load |  |  |  | Remarks
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 400 kV side ) | Date | Time
Kaliakoir | TR1(400/230 kV) | 520 | 206 | 353 | 07.10.2020 | 10:00
| TR2(400/230 kV) | 520 | 206 | 353
| TR1(400/132 kV) | 325 | 278 | 459 | 11.10.2020 | 18:15
| TR2(400/132 kV) | 325 | 278 | 459
Bibiyana | ICT1(400/230 kV) | 520 | 128 | 205 | 10.10.2020 | 9:54
| ICT2(400/230kV) | 520 | 127 | 205
Bhulta | ATR1(400/230 kV) | 520 | 203 | 385 | 28.10.2020 | 15:15
| ATR2(400/230kV) | 520 | 203 | 385
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:October' 2020 | [6 empty] | (For Evening Peak) | [7 empty] | Month:October' 2020 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-10-20 | 12065 | 12065 | - | - | - | - | - | - | - | - | - | - | - | - | 01-10-20 | 10286 | 10286 | - | - | - | - | - | - | - | - | - | - | - | -
02-10-20 | 11238 | 11238 | - | - | - | - | - | - | - | - | - | - | - | - | 02-10-20 | 8595 | 8595 | - | - | - | - | - | - | - | - | - | - | - | -
03-10-20 | 12091 | 12091 | - | - | - | - | - | - | - | - | - | - | - | - | 03-10-20 | 9624 | 9624 | - | - | - | - | - | - | - | - | - | - | - | -
04-10-20 | 12317 | 12317 | - | - | - | - | - | - | - | - | - | - | - | - | 04-10-20 | 10180 | 10180 | - | - | - | - | - | - | - | - | - | - | - | -
05-10-20 | 12054 | 12054 | - | - | - | - | - | - | - | - | - | - | - | - | 05-10-20 | 10276 | 10276 | - | - | - | - | - | - | - | - | - | - | - | -
06-10-20 | 11944 | 11944 | - | - | - | - | - | - | - | - | - | - | - | - | 06-10-20 | 9668 | 9668 | - | - | - | - | - | - | - | - | - | - | - | -
07-10-20 | 11899 | 11899 | - | - | - | - | - | - | - | - | - | - | - | - | 07-10-20 | 9787 | 9787 | - | - | - | - | - | - | - | - | - | - | - | -
08-10-20 | 12063 | 12063 | - | - | - | - | - | - | - | - | - | - | - | - | 08-10-20 | 10097 | 10097 | - | - | - | - | - | - | - | - | - | - | - | -
09-10-20 | 11909 | 11909 | - | - | - | - | - | - | - | - | - | - | - | - | 09-10-20 | 8938 | 8938 | - | - | - | - | - | - | - | - | - | - | - | -
10-10-20 | 12650 | 12650 | - | - | - | - | - | - | - | - | - | - | - | - | 10-10-20 | 9646 | 9646 | - | - | - | - | - | - | - | - | - | - | - | -
11-10-20 | 12759 | 12759 | - | - | - | - | - | - | - | - | - | - | - | - | 11-10-20 | 10648 | 10648 | - | - | - | - | - | - | - | - | - | - | - | -
12-10-20 | 12722 | 12722 | - | - | - | - | - | - | - | - | - | - | - | - | 12-10-20 | 10495 | 10495 | - | - | - | - | - | - | - | - | - | - | - | -
13-10-20 | 12727 | 12727 | - | - | - | - | - | - | - | - | - | - | - | - | 13-10-20 | 10723 | 10723 | - | - | - | - | - | - | - | - | - | - | - | -
14-10-20 | 12528 | 12528 | - | - | - | - | - | - | - | - | - | - | - | - | 14-10-20 | 10646 | 10646 | - | - | - | - | - | - | - | - | - | - | - | -
15-10-20 | 12684 | 12684 | - | - | - | - | - | - | - | - | - | - | - | - | 15-10-20 | 10583 | 10583 | - | - | - | - | - | - | - | - | - | - | - | -
16-1020 | 11984 | 11984 | - | - | - | - | - | - | - | - | - | - | - | - | 16-1020 | 9142 | 9142 | - | - | - | - | - | - | - | - | - | - | - | -
17-10-20 | 12637 | 12637 | - | - | - | - | - | - | - | - | - | - | - | - | 17-10-20 | 9771 | 9771 | - | - | - | - | - | - | - | - | - | - | - | -
18-10-20 | 12512 | 12512 | - | - | - | - | - | - | - | - | - | - | - | - | 18-10-20 | 10327 | 10327 | - | - | - | - | - | - | - | - | - | - | - | -
19-10-20 | 12659 | 12659 | - | - | - | - | - | - | - | - | - | - | - | - | 19-10-20 | 10188 | 10188 | - | - | - | - | - | - | - | - | - | - | - | -
20-10-20 | 12538 | 12538 | - | - | - | - | - | - | - | - | - | - | - | - | 20-10-20 | 10568 | 10568 | - | - | - | - | - | - | - | - | - | - | - | -
21-10-20 | 12026 | 12026 | - | - | - | - | - | - | - | - | - | - | - | - | 21-10-20 | 9957 | 9957 | - | - | - | - | - | - | - | - | - | - | - | -
22-10-20 | 9836 | 9836 | - | - | - | - | - | - | - | - | - | - | - | - | 22-10-20 | 9034 | 9034 | - | - | - | - | - | - | - | - | - | - | - | -
23-10-20 | 8212 | 8212 | - | - | - | - | - | - | - | - | - | - | - | - | 23-10-20 | 6310 | 6310 | - | - | - | - | - | - | - | - | - | - | - | -
24-10-20 | 9790 | 9790 | - | - | - | - | - | - | - | - | - | - | - | - | 24-10-20 | 8031 | 8031 | - | - | - | - | - | - | - | - | - | - | - | -
25-10-20 | 10732 | 10732 | - | - | - | - | - | - | - | - | - | - | - | - | 25-10-20 | 8818 | 8818 | - | - | - | - | - | - | - | - | - | - | - | -
26-10-20 | 10705 | 10705 | - | - | - | - | - | - | - | - | - | - | - | - | 26-10-20 | 8505 | 8505 | - | - | - | - | - | - | - | - | - | - | - | -
27-10-20 | 11294 | 11294 | - | - | - | - | - | - | - | - | - | - | - | - | 27-10-20 | 9190 | 9190 | - | - | - | - | - | - | - | - | - | - | - | -
28-10-20 | 11381 | 11381 | - | - | - | - | - | - | - | - | - | - | - | - | 28-10-20 | 10012.9 | 10012.9 | - | - | - | - | - | - | - | - | - | - | - | -
29-10-20 | 12085 | 12085 | - | - | - | - | - | - | - | - | - | - | - | - | 29-10-20 | 9689 | 9689 | - | - | - | - | - | - | - | - | - | - | - | -
30-10-20 | 11107 | 11107 | - | - | - | - | - | - | - | - | - | - | - | - | 30-10-20 | 8265 | 8265 | - | - | - | - | - | - | - | - | - | - | - | -
31-10-20 | 11266 | 11266 | [12 empty] | 31-10-20 | 8600 | 8600 | - | - | - | - | - | - | - | - | - | - | - | -

## QF-LDC-38
page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:October' 2020
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 12759 | 11/10/20 | 19:00
2 | Maximum Day Peak Genaration | MW | 10723 | 13-10-2020 | 12:00
3 | Maximum Evening Peak Demand | MW | 12759 | 11/10/20 | 19:00
4 | Minimum Generation | MW | 6045 | 23/10/20 | 9:00
5 | Average of the daily evening peak Genaration | MW | 11755.2903
6 | Average of the daily day peak Genaration | MW | 9551.7742
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW | -
11 | Total Generation | MKWH | 7485.0928
12 | Total Generation by BPDB | MKWH | 3604.3882 | % of total Gen. | 48.15%
13 | Total Generation by IPP | MKWH | 2287.2024 | '' | 30.56%
14 | A) Total Generation by RPCL | MKWH | 141.6463 | '' | 1.892%
| B) Total Generation by REB | MKWH | 145.8563 | " | 1.949%
| C) Total Generation by RENTAL | MKWH | 540.7093 | " | 7.224%
| D) Total Imported from India (BIPTC) | MKWH | 669.9738 | " | 8.951%
| E) Total Imported from Tripura, India (A.C) | MKWH | 95.3165 | " | 1.273%
15 | Fuel wise Generation.
| A) Gas | MKWH | 4215.0603 | % of total Gen. | 56.31%
| B) Oil | MKWH | 1903.4721 | '' | 25.43%
| C) Hydro | MKWH | 85.0566 | '' | 1.136%
| D) Solar | MKWH | 6.3227 | '' | 0.08447%
| E) Coal | MKWH | 509.8908 | '' | 6.812%
| F) BIPTC (Import from India) | MKWH | 669.9738 | '' | 8.951%
| G) A.C (Import from Tripura, India) | MKWH | 95.3165 | '' | 1.273%
16 | Maximun of the daily total Generation . | MKWH | 269.5796 | 11-10-2020
17 | Monthly Load factor | % | 78.8511
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 26768.2515
| A) Gas | M.Taka | 4920.1076
| B) Liquid fuel | M.Taka | 15377.0654
| C) Coal | M.Taka | 2339.3384
| D) BIPTC (Import from India) | M.Taka | 3416.8664
| E) Tripura(Import from India) | M.Taka | 714.8736
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 939.0016 | 11/10/2020
| A) Gas | M.Taka | 166.6327 | 30/10/2020
| B) Liquid fuel | M.Taka | 707.2206 | 01/10/2020
| C) Coal | M.Taka | 89.4519 | 31/10/2020
| D) BIPTC (Import from India) | M.Taka | 114.0286 | 29-10-2020
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 3.7457
| B) Excluding Hydro & Solar | Taka/KWHR | 3.791
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 108.9 | 31/10/2020 | 06:00
b) | Actual | FT (MSL) | 103.8 | 31/10/2020 | 06:00
22 | Peak Genaration of October 2019 | MW | 12717 | 01/09/19 | 21:00
23 | Peak Demand of Otober 2019 | MW | 12717 | 01/09/19 | 21:00
24 | Maximum peak Generation recorded upto 31/10/2020 | MW | 12893 | 29/05/19 | 21:00
25 | Maximum peak Demand recorded upto 31/10/2020 | MW | 12893 | 29/05/19 | 21:00
26 | Maximum load shed recorded upto 31/10/2020 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.