## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-11-27 | Friday
|  |  | Date (day): | 2020-11-27 |  | Friday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12806.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14211 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-11-26 | 2020-11-27 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 115 | 115 | 115 | 75 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 200 | 200 |  | 165 | Machine problem
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 30 | 72 | 78 | 78
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 96 | 96 | 100 | 100
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 286 | 249 | 300 | 300 |  | 139 | ST under maint.
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 312 | 308 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 |  | 225 | GT-1 under maint.
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 63 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 142 | 135 | 150 | 150 |  | 155 | FGMO, GT-1 under maint.
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 15 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 50 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 19 | 19 | 19
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 60 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 60 | 102 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 32 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 56 | 57 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 24 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 125 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 35 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 89 | 89 | 90 | 90 |  | 14 | Engine problem
|  | Manikgonj 162MW PP |  | HFO | IPP | 9*18 | 0 | 0 | 166 | 165 | 162 | 162
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 1957 | 2390 | 3600 | 3940 | 498 | 1633
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 12 | 50 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 125 | 126 | 127 | 127 | 103 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 217 | 204 | 215 | 225
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 139 | 140 | 140
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 102 | 102
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 30 | 100 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 23 | 20 | 20
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 100 | 100
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 16 | 123 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 18 | 54 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 72 | 100 | 100 | 100
|  | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 0 | 0 | 0 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 535 | 990 | 1688 | 1673 | 463 | 98
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 100 | 100 | 100 | 35 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 159 | 192 | 225 | 225 |  |  | FGMO
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 335 | 310 | 360 | 360 |  |  | FGMO
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 29 | 30 | 30 | 15 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 8 | 8 | 8 | 8 | 47 |  | Gas shortage
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 37 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 10 | 81 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 52 | 68 | 90 | 90 |  | 57 | ST Under maint.
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 165 | 200
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 84 | 104 | 133 | 145
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 21 | 20 | 21
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 113 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 891 | 1131 | 1685 | 1983 | 547 | 417
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 106 | 109 | 120 | 150 | 52 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 20 | 22 | 22
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 8 | 17 | 17 |  | 78 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 32 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 85 | 115 | 115 | 115
|  | Mymensingh PV 50 MW Solar PP |  | Solar | IPP | 50 | 0 | 0 | 46 | 0 | 50 | 0
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 264 | 284 | 525.6 | 504 | 52 | 78
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 60 | 60 | 60
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 52 | 60 | 60 | 60
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 257 | 260 | 260 | 260 |  | 70 | Machine problem
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 48 | 49 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 47 | 47 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 31 | 68 | 66 | 66 |  |  | FGMO
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 82 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 150 | 150 | 150 | 150
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 0 | 18 | 18
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 310 | 320 | 320 |  |  | FGMO
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 0 | 0 |  |  | 33 kV line maint.
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1237 | 1276 | 1305 | 1305 | 0 | 479
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 689 | 508 | 696 | 888
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 49 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 385 | 320 | 410 | 410
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 90 | 90 | 90 |  | 15 | Engine problem
| 108 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1091 | 967 | 1451 | 2069 | 0 | 15
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 14 | 20 | 20 | 20
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 35 | 91 | 95 | 95
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 400 | 480 | 600 | 660
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 36 | 1 | 35 | 35
|  | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | 65 | 0 | 0
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 485 | 673 | 860 | 920 | 0 | 194
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 40 | 0 | 0 | 0 |  |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 140 | 150 |  | 75 | ST Under maint
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 185 | 185 | 220 | 220 |  |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 186 | 199 | 0 | 0 |  | 220 | Under maint.
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 392 | 435 | 400 | 400 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 33
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 113 | 113
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 832 | 965 | 1421 | 1554 | 200 | 295
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 140 | 140 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 110 | 113 | 113
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 145 | 250 | 271 | 263 | 294 | 40
|  | Total |  |  |  |  | 20383 | 19892 | 7437 | 8926 | 12806.6 | 14211 | 2054 | 3249
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7031.2394 | 8439 | 12107.8756 | 13435.6519
| A. |  | 2020-11-26 | (Yesterday) |  |  |  |  | Thursday
| 1 | Highest Generation : |  |  | 8926 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 5537 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8926 | MW
| 3 | Day peak Generation : |  |  | 7437 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8439 | MW
| 4 | Evening peak Generation : |  |  | 8926 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 166.2397 | MKWHr | By Solar | 0.45048 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 113.3482 | MKWHr |  | By Oil: | 20.1058 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 13.2936 | MKWHr |  | By Hydro: | 2.9288 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2054 | MW | Dhaka | 3127 | 3127 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3249 | MW | Chittagong | 963 | 963 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5303 | MW | Khulna | 1031 | 1031 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 959.25 | MMCFD |  |  | Rajshahi | 825 | 825 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 130025973.41 | ii) Oil : | Taka | 111157363.1 | Comilla | 709 | 709 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 61900147 | Total | Taka | 303083483.51 | Mymensingh | 662 | 662 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.167 | MKWHr. | Sylhet | 321 | 321 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -28 | MW (E to W) at | 19:00 | hrs | Barisal | 234 | 234 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -28 | MW at | 19:00 | hrs | Rangpur | 567 | 567 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 27.4° C |  |  | Total | 8439 | 8439 |  | 0
| B. |  | 2020-11-27 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 27.3° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 8000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14211 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 6200 | MW
| 4 | Reserve(Generation end) |  |  |  | 6211 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 148.9937 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5587 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 14.0662 | MKWHr. | ii) HVDC Flow at Peak Time |  | 508 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.0467 | MKWHr. | iii) Maximum HVDC Flow : |  | 873 | MW at | 21:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 101.19 |  | (b) Today: | 101.04 |  | (c) Rule Curve: |  | 106.4
.

## YesterdayGen
2020-11-26
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha Energies 55 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Mymensingh PV 50 MW Solar PP | Manikgonj 162MW PP | Anlima Energy Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 115 | 200 | 98 | 73 | 303 | 299 |  | 0 | 225 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 32 | 22 | 33 | 0 | 0 | 86 | 35 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 80 | 0 | 0 | 260 | 0 | 182 | 8 | 52 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 33 | 21 | 78 | 133 | 17 | 17 | 0 | 60 | 52 | 47 | 47 | 130 | 255 | 69 | 10 | 0 | 150 | 18 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 12 | 0 |  | 498 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 5 | 27 | 0 | 140 | 0 | 0 | 0 | 0 | 157 | 0 | 53 | 0 | 160 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 0 | 0 |  | 4052 | 2267 | 6319 | 3101 | 498 | 1718 | 186 | 617 | 121 | 0 | 78 | 0 | 0 | 101.21
2:00 | 0 | 0 | 0 | 115 | 200 | 42 | 30 | 304 | 325 |  | 0 | 225 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 32 | 22 | 33 | 0 | 0 | 84 | 35 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 80 | 0 | 0 | 260 | 0 | 182 | 8 | 51 | 29 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 78 | 131 | 17 | 0 | 0 | 60 | 52 | 11 | 5 | 130 | 250 | 56 | 10 | 0 | 150 | 18 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 12 | 0 |  | 498 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 150 | 0 | 13 | 0 | 130 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440 | 0 | 0 | 0 |  | 3789 | 2135 | 5924 | 2968 | 498 | 1495 | 186 | 580 | 119 | 0 | 78 | 0 | 0 | 101.21
3:00 | 0 | 0 | 0 | 115 | 200 | 13 | 30 | 302 | 283 |  | 0 | 225 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 28 | 22 | 33 | 0 | 0 | 86 | 35 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 80 | 0 | 0 | 260 | 0 | 182 | 8 | 50 | 5 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 76 | 151 | 17 | 0 | 0 | 60 | 52 | 11 | 5 | 130 | 250 | 40 | 10 | 0 | 150 | 18 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 12 | 0 |  | 497 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 130 | 0 | 13 | 0 | 130 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 |  | 3716 | 2065 | 5781 | 2921 | 497 | 1435 | 191 | 540 | 121 | 0 | 76 | 0 | 0 | 101.2
4:00 | 0 | 0 | 0 | 115 | 200 | 13 | 30 | 304 | 283 |  | 0 | 225 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 22 | 33 | 0 | 0 | 87 | 35 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 35 | 80 | 0 | 0 | 260 | 0 | 182 | 8 | 50 | 5 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 74 | 152 | 17 | 0 | 0 | 60 | 52 | 11 | 5 | 110 | 253 | 40 | 10 | 0 | 150 | 18 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 |  | 404 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 130 | 0 | 13 | 0 | 130 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 |  | 3654 | 1946 | 5600 | 2927 | 404 | 1374 | 159 | 540 | 122 | 0 | 74 | 0 | 0 | 101.2
5:00 | 0 | 0 | 0 | 115 | 200 | 13 | 30 | 303 | 284 |  | 0 | 225 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 22 | 33 | 0 | 0 | 89 | 35 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 33 | 80 | 0 | 0 | 260 | 0 | 182 | 8 | 50 | 5 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 74 | 169 | 17 | 0 | 0 | 60 | 52 | 11 | 5 | 110 | 253 | 40 | 10 | 0 | 150 | 18 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 |  | 404 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 130 | 0 | 11 | 0 | 130 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 |  | 3675 | 1862 | 5537 | 2937 | 404 | 1334 | 164 | 500 | 124 | 0 | 74 | 0 | 0 | 101.19
6:00 | 0 | 0 | 0 | 115 | 200 | 13 | 30 | 301 | 283 |  | 0 | 225 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 25 | 20 | 22 | 33 | 0 | 0 | 91 | 35 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 80 | 0 | 0 | 290 | 0 | 200 | 36 | 50 | 5 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 70 | 167 | 17 | 0 | 0 | 60 | 52 | 11 | 5 | 163 | 258 | 40 | 10 | 0 | 150 | 18 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 404 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 130 | 0 | 11 | 0 | 154 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 |  | 3822 | 1929 | 5751 | 3038 | 404 | 1459 | 174 | 480 | 126 | 0 | 70 | 0 | 0 | 101.19
7:00 | 0 | 0 | 0 | 115 | 200 | 60 | 30 | 302 | 304 |  | 0 | 225 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 28 | 22 | 33 | 0 | 0 | 91 | 35 | 0 | 0 | 0 | 205 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 33 | 135 | 0 | 0 | 275 | 0 | 198 | 36 | 50 | 29 | 5 | 0 | 20 | 0 | 0 | 0 | 16 | 0 | 23 | 18 | 68 | 168 | 17 | 0 | 0 | 60 | 52 | 11 | 10 | 163 | 262 | 33 | 10 | 0 | 150 | 18 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 2 | 0 | 0 |  | 404 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 130 | 0 | 12 | 0 | 191 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 |  | 4043 | 2034 | 6077 | 3206 | 404 | 1598 | 192 | 480 | 126 | 0 | 68 | 3 | 0 | 101.18
8:00 | 0 | 0 | 0 | 115 | 200 | 96 | 30 | 299 | 304 |  | 0 | 225 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 28 | 22 | 33 | 0 | 0 | 92 | 35 | 0 | 0 | 0 | 214 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 4 | 20 | 9 | 135 | 0 | 0 | 315 | 0 | 197 | 55 | 50 | 29 | 20 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 23 | 15 | 74 | 167 | 17 | 17 | 1 | 60 | 52 | 42 | 43 | 120 | 263 | 32 | 50 | 0 | 150 | 18 | 0 | 0 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 10 | 0 | 3 | 0 | 24 | 0 | 0 | 1 | 16 | 12 | 0 | 0 | 6 | 30 | 0 | 14 | 18 | 0 | 0 |  | 404 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 152 | 0 | 12 | 0 | 191 | 0 | 375 | 17 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 340 | 0 | 0 | 0 |  | 4415 | 2113 | 6528 | 3305 | 404 | 1770 | 340 | 480 | 127 | 0 | 74 | 28 | 0 | 101.18
9:00 | 0 | 0 | 0 | 115 | 200 | 96 | 30 | 294 | 332 |  | 0 | 225 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 31 | 25 | 33 | 0 | 0 | 92 | 35 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 20 | 3 | 110 | 0 | 0 | 320 | 0 | 189 | 55 | 50 | 26 | 35 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 33 | 15 | 76 | 148 | 17 | 17 | 1 | 60 | 52 | 42 | 47 | 163 | 258 | 32 | 50 | 0 | 150 | 18 | 0 | 0 | 315 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 10 | 0 | 10 | 0 | 53 | 1 | 0 | 2 | 16 | 17 | 0 | 0 | 8 | 40 | 0 | 35 | 28 | 0 | 0 |  | 404 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 167 | 0 | 12 | 0 | 203 | 0 | 433 | 17 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 340 | 0 | 0 | 0 |  | 4565 | 2205 | 6770 | 3290 | 404 | 1927 | 418 | 480 | 127 | 0 | 76 | 48 | 0 | 101.17
10:00 | 0 | 0 | 0 | 115 | 200 | 96 | 30 | 293 | 328 |  | 0 | 225 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 10 | 0 | 0 | 25 | 31 | 25 | 33 | 0 | 0 | 92 | 35 | 0 | 0 | 0 | 213 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 20 | 2 | 80 | 0 | 0 | 325 | 0 | 149 | 36 | 37 | 26 | 35 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 33 | 15 | 76 | 127 | 17 | 17 | 2 | 60 | 52 | 42 | 47 | 163 | 261 | 32 | 79 | 0 | 150 | 18 | 0 | 0 | 310 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 0 | 10 | 0 | 85 | 50 | 0 | 4 | 16 | 17 | 0 | 0 | 8 | 70 | 0 | 86 | 47 | 4 | 0 |  | 404 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 161 | 0 | 34 | 0 | 201 | 0 | 435 | 17 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 370 | 0 | 0 | 0 |  | 4683 | 2246 | 6929 | 3174 | 404 | 1950 | 613 | 510 | 127 | 0 | 76 | 75 | 0 | 101.17
11:00 | 0 | 0 | 0 | 115 | 200 | 94 | 30 | 290 | 306 |  | 0 | 225 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 0 | 25 | 31 | 25 | 33 | 0 | 0 | 90 | 35 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 20 | 2 | 80 | 0 | 0 | 305 | 0 | 180 | 8 | 74 | 29 | 8 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 33 | 15 | 84 | 106 | 8 | 17 | 2 | 60 | 52 | 48 | 47 | 110 | 260 | 20 | 77 | 0 | 150 | 18 | 0 | 0 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 0 | 10 | 0 | 85 | 35 | 0 | 4 | 16 | 17 | 0 | 0 | 8 | 30 | 0 | 89 | 53 | 111 | 0 |  | 679 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 163 | 0 | 37 | 0 | 185 | 0 | 375 | 17 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 370 | 0 | 0 | 0 |  | 4671 | 2488 | 7159 | 3212 | 679 | 1753 | 714 | 510 | 125 | 0 | 84 | 82 | 0 | 101.16
12:00 | 0 | 0 | 0 | 115 | 200 | 96 | 30 | 286 | 312 |  | 0 | 225 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 16 | 25 | 31 | 25 | 33 | 0 | 0 | 90 | 35 | 0 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 20 | 2 | 80 | 0 | 0 | 335 | 0 | 159 | 8 | 52 | 29 | 8 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 33 | 15 | 84 | 106 | 8 | 17 | 2 | 60 | 52 | 48 | 47 | 163 | 257 | 31 | 80 | 0 | 150 | 18 | 0 | 0 | 310 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 30 | 0 | 10 | 0 | 85 | 35 | 0 | 4 | 16 | 18 | 0 | 0 | 8 | 72 | 0 | 89 | 46 | 166 | 0 |  | 689 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 185 | 0 | 35 | 0 | 186 | 0 | 392 | 17 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 400 | 36 | 0 | 0 |  | 4884 | 2553 | 7437 | 3206 | 689 | 1878 | 839 | 540 | 125 | 0 | 84 | 76 | 0 | #REF!
13:00 | 0 | 0 | 0 | 115 | 200 | 96 | 60 | 286 | 307 |  | 0 | 225 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 16 | 25 | 31 | 25 | 33 | 0 | 0 | 90 | 35 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 8 | 20 | 5 | 80 | 0 | 0 | 300 | 0 | 167 | 8 | 45 | 29 | 8 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 33 | 12 | 92 | 103 | 8 | 17 | 2 | 60 | 52 | 48 | 47 | 163 | 255 | 31 | 80 | 0 | 150 | 18 | 0 | 0 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 31 | 0 | 85 | 35 | 0 | 4 | 100 | 48 | 0 | 0 | 29 | 100 | 0 | 89 | 25 | 162 | 0 |  | 690 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 196 | 0 | 35 | 0 | 214 | 0 | 389 | 53 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 400 | 35 | 0 | 0 |  | 5082 | 2552 | 7634 | 3114 | 690 | 1895 | 1143 | 540 | 125 | 0 | 92 | 35 | 7634 | 101.15
14:00 | 0 | 0 | 0 | 115 | 200 | 95 | 72 | 287 | 270 |  | 0 | 225 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 16 | 25 | 18 | 25 | 33 | 0 | 0 | 86 | 35 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 24 | 20 | 5 | 80 | 0 | 0 | 310 | 0 | 174 | 8 | 76 | 29 | 8 | 0 | 33 | 0 | 0 | 0 | 19 | 0 | 33 | 12 | 88 | 100 | 8 | 17 | 1 | 60 | 52 | 48 | 47 | 110 | 263 | 31 | 20 | 0 | 150 | 18 | 0 | 0 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 50 | 0 | 10 | 0 | 85 | 35 | 0 | 3 | 16 | 54 | 0 | 0 | 18 | 100 | 0 | 89 | 35 | 166 | 0 |  | 690 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 164 | 0 | 36 | 0 | 195 | 0 | 376 | 35 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 350 | 36 | 0 | 0 |  | 4837 | 2370 | 7207 | 3055 | 690 | 1726 | 980 | 490 | 121 | 0 | 88 | 57 | 0 | 101.15
15:00 | 0 | 0 | 0 | 115 | 200 | 93 | 72 | 287 | 270 |  | 0 | 225 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 31 | 25 | 33 | 0 | 0 | 88 | 35 | 0 | 0 | 0 | 204 | 0 | 15 | 0 |  | 0 | 0 | 0 | 0 | 0 | 30 | 20 | 2 | 80 | 0 | 0 | 300 | 0 | 193 | 8 | 75 | 29 | 8 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 33 | 15 | 82 | 101 | 8 | 17 | 1 | 60 | 52 | 47 | 47 | 110 | 255 | 31 | 20 | 0 | 150 | 18 | 0 | 0 | 315 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 50 | 0 | 10 | 0 | 85 | 35 | 0 | 2 | 16 | 54 | 0 | 0 | 18 | 100 | 0 | 89 | 38 | 166 | 0 |  | 690 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 170 | 0 | 35 | 0 | 200 | 0 | 377 | 35 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 350 | 5 | 0 | 0 |  | 4833 | 2347 | 7180 | 3101 | 690 | 1668 | 971 | 490 | 123 | 0 | 82 | 55 | 0 | 101.14
16:00 | 0 | 0 | 0 | 115 | 200 | 43 | 40 | 286 | 270 |  | 0 | 225 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 0 | 25 | 23 | 25 | 33 | 0 | 0 | 88 | 35 | 0 | 0 | 0 | 209 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 30 | 20 | 2 | 80 | 0 | 0 | 315 | 0 | 195 | 8 | 75 | 26 | 8 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 33 | 15 | 88 | 108 | 8 | 0 | 0 | 60 | 60 | 11 | 10 | 110 | 262 | 51 | 20 | 0 | 151 | 18 | 0 | 0 | 290 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 50 | 0 | 10 | 0 | 85 | 35 | 0 | 1 | 16 | 54 | 0 | 0 | 18 | 100 | 0 | 89 | 7 | 166 | 0 |  | 690 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 159 | 0 | 34 | 0 | 188 | 0 | 376 | 17 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 350 | 11 | 0 | 0 |  | 4706 | 2306 | 7012 | 3150 | 690 | 1489 | 966 | 490 | 123 | 0 | 88 | 16 | 0 | 101.14
17:00 | 0 | 0 | 0 | 115 | 200 | 48 | 40 | 252 | 270 |  | 0 | 225 | 140 | 10 | 4 | 0 | 0 | 0 | 0 | 11 | 74 | 32 | 0 | 0 | 0 | 0 | 54 | 35 | 0 | 0 | 25 | 24 | 25 | 33 | 0 | 0 | 91 | 35 | 0 | 0 | 0 | 204 | 0 | 70 | 0 |  | 0 | 0 | 51 | 0 | 0 | 38 | 20 | 12 | 80 | 0 | 0 | 300 | 0 | 182 | 8 | 75 | 29 | 8 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 33 | 15 | 88 | 111 | 8 | 20 | 0 | 60 | 60 | 11 | 10 | 110 | 257 | 66 | 20 | 0 | 150 | 18 | 0 | 0 | 305 | 16 | 5 | 0 | 30 | 0 | 0 | 5 | 0 | 0 | 0 | 50 | 0 | 15 | 0 | 85 | 50 | 0 | 0 | 65 | 54 | 0 | 0 | 36 | 100 | 0 | 89 | 1 | 166 | 0 |  | 683 | 0 | 300 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 171 | 0 | 34 | 0 | 196 | 0 | 374 | 53 | 0 | 0 | 0 | 40 | 0 | 0 | 35 | 350 | 8 | 0 | 0 |  | 4948 | 2441 | 7389 | 3139 | 683 | 1524 | 1255 | 490 | 126 | 83 | 88 | 1 | 0 | 101.13
18:00 | 0 | 0 | 0 | 115 | 200 | 96 | 72 | 259 | 308 |  | 0 | 225 | 146 | 34 | 15 | 0 | 0 | 0 | 0 | 25 | 84 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 18 | 25 | 24 | 0 | 0 | 91 | 35 | 0 | 0 | 0 | 219 | 0 | 145 | 0 |  | 0 | 0 | 51 | 0 | 0 | 50 | 20 | 10 | 90 | 0 | 0 | 350 | 0 | 203 | 8 | 76 | 29 | 8 | 0 | 11 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 106 | 109 | 8 | 20 | 0 | 60 | 60 | 46 | 37 | 130 | 263 | 66 | 82 | 0 | 150 | 0 | 0 | 0 | 310 | 16 | 9 | 0 | 90 | 0 | 0 | 32 | 0 | 0 | 0 | 100 | 0 | 55 | 0 | 115 | 100 | 0 | 0 | 100 | 54 | 0 | 0 | 113 | 100 | 0 | 89 | 0 | 165 | 0 |  | 508 | 0 | 330 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 176 | 0 | 90 | 0 | 199 | 0 | 422 | 70 | 0 | 0 | 0 | 108 | 0 | 0 | 95 | 550 | 3 | 0 | 56 |  | 5893 | 2850 | 8743 | 3367 | 508 | 1900 | 1963 | 690 | 126 | 83 | 106 | 0 | 0 | 101.13
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 115 | 200 | 96 | 72 | 249 | 308 |  | 0 | 225 | 135 | 63 | 15 | 0 | 0 | 0 | 0 | 60 | 102 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 32 | 25 | 24 | 0 | 0 | 91 | 35 | 0 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 51 | 0 | 0 | 50 | 20 | 23 | 100 | 0 | 0 | 310 | 0 | 192 | 8 | 68 | 29 | 8 | 0 | 37 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 104 | 109 | 8 | 20 | 0 | 60 | 60 | 49 | 47 | 163 | 260 | 68 | 82 | 0 | 150 | 0 | 0 | 0 | 310 | 16 | 11 | 0 | 125 | 0 | 0 | 32 | 0 | 0 | 0 | 100 | 0 | 81 | 0 | 115 | 105 | 0 | 0 | 123 | 54 | 0 | 0 | 113 | 100 | 0 | 89 | 0 | 165 | 0 |  | 508 | 0 | 320 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 185 | 0 | 91 | 0 | 199 | 0 | 435 | 90 | 0 | 0 | 0 | 110 | 0 | 0 | 113 | 480 | 1 | 0 | 65 |  | 6071 | 2855 | 8926 | 3301 | 508 | 1997 | 2187 | 620 | 126 | 83 | 104 | 0 | 0 | 101.11
19:30 | 0 | 0 | 0 | 115 | 200 | 97 | 72 | 241 | 310 |  | 0 | 225 | 135 | 37 | 15 | 0 | 0 | 0 | 0 | 30 | 94 | 32 | 0 | 0 | 0 | 0 | 54 | 35 | 0 | 19 | 25 | 32 | 25 | 24 | 0 | 0 | 91 | 35 | 0 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 51 | 0 | 0 | 50 | 20 | 26 | 100 | 0 | 0 | 315 | 0 | 193 | 8 | 70 | 29 | 8 | 0 | 40 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 106 | 109 | 8 | 20 | 0 | 60 | 60 | 49 | 47 | 163 | 259 | 64 | 82 | 0 | 150 | 0 | 0 | 0 | 310 | 16 | 11 | 0 | 95 | 0 | 0 | 32 | 0 | 0 | 0 | 100 | 0 | 100 | 0 | 115 | 50 | 0 | 0 | 123 | 54 | 0 | 0 | 113 | 100 | 0 | 89 | 0 | 165 | 0 |  | 610 | 0 | 315 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 177 | 0 | 83 | 0 | 195 | 0 | 432 | 90 | 0 | 0 | 0 | 113 | 0 | 0 | 113 | 480 | 21 | 0 | 17 |  | 5927 | 2852 | 8779 | 3279 | 610 | 2005 | 1950 | 620 | 126 | 83 | 106 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 115 | 200 | 97 | 72 | 237 | 310 |  | 0 | 225 | 135 | 45 | 15 | 0 | 0 | 0 | 0 | 40 | 68 | 32 | 0 | 0 | 0 | 0 | 54 | 35 | 0 | 19 | 25 | 32 | 22 | 24 | 0 | 0 | 91 | 35 | 0 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 51 | 0 | 0 | 50 | 20 | 30 | 100 | 0 | 0 | 300 | 0 | 181 | 8 | 68 | 29 | 8 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 102 | 109 | 8 | 20 | 0 | 60 | 60 | 49 | 47 | 163 | 255 | 64 | 82 | 0 | 150 | 0 | 0 | 0 | 280 | 16 | 11 | 0 | 45 | 0 | 0 | 32 | 0 | 0 | 0 | 100 | 0 | 50 | 0 | 115 | 50 | 0 | 0 | 123 | 54 | 0 | 0 | 113 | 100 | 0 | 89 | 0 | 165 | 0 |  | 803 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 176 | 0 | 30 | 0 | 190 | 0 | 410 | 90 | 0 | 0 | 0 | 80 | 0 | 0 | 70 | 480 | 17 | 0 | 0 |  | 5759 | 2889 | 8648 | 3232 | 803 | 1908 | 1774 | 620 | 126 | 83 | 102 | 0 | 0 | 101.12
21:00 | 0 | 0 | 0 | 115 | 200 | 97 | 73 | 237 | 309 |  | 0 | 225 | 140 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 0 | 0 | 0 | 0 | 54 | 35 | 0 | 19 | 25 | 32 | 22 | 24 | 0 | 0 | 91 | 35 | 0 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 32 | 100 | 0 | 0 | 305 | 0 | 190 | 8 | 69 | 29 | 8 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 104 | 109 | 8 | 20 | 0 | 60 | 60 | 49 | 47 | 163 | 260 | 64 | 82 | 0 | 150 | 0 | 0 | 0 | 290 | 16 | 11 | 0 | 45 | 0 | 0 | 32 | 0 | 0 | 0 | 100 | 0 | 10 | 0 | 115 | 50 | 0 | 0 | 89 | 54 | 0 | 0 | 65 | 100 | 0 | 89 | 0 | 165 | 0 |  | 873 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 165 | 0 | 91 | 0 | 179 | 0 | 335 | 90 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 490 | 22 | 0 | 0 |  | 5511 | 2837 | 8348 | 3226 | 873 | 1912 | 1458 | 629 | 126 | 20 | 104 | 0 | 0 | #REF!
22:00 | 0 | 0 | 0 | 115 | 200 | 98 | 73 | 235 | 309 |  | 0 | 225 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 32 | 22 | 24 | 0 | 0 | 92 | 35 | 0 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 35 | 100 | 0 | 0 | 300 | 0 | 181 | 8 | 69 | 29 | 8 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 96 | 110 | 8 | 20 | 0 | 60 | 60 | 49 | 47 | 163 | 251 | 66 | 80 | 0 | 150 | 0 | 0 | 0 | 285 | 16 | 11 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 115 | 17 | 0 | 0 | 35 | 54 | 0 | 0 | 26 | 100 | 0 | 89 | 0 | 165 | 0 |  | 873 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 151 | 0 | 90 | 0 | 161 | 0 | 295 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 36 | 0 | 0 |  | 5162 | 2644 | 7806 | 3181 | 873 | 1884 | 1005 | 640 | 127 | 0 | 96 | 0 | 0 | 101.1
23:00 | 0 | 0 | 0 | 115 | 200 | 98 | 73 | 235 | 309 |  | 0 | 225 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 32 | 22 | 30 | 0 | 0 | 92 | 35 | 0 | 0 | 0 | 203 | 0 | 138 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 20 | 40 | 100 | 0 | 0 | 300 | 0 | 188 | 8 | 69 | 29 | 8 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 88 | 111 | 8 | 20 | 0 | 60 | 60 | 50 | 47 | 163 | 256 | 67 | 40 | 0 | 150 | 0 | 0 | 0 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 100 | 0 | 72 | 0 | 165 | 0 |  | 777 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 146 | 0 | 87 | 0 | 160 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 36 | 0 | 0 |  | 4740 | 2569 | 7309 | 3209 | 777 | 1884 | 584 | 640 | 127 | 0 | 88 | 0 | 0 | 101.1
24:00 | 0 | 0 | 0 | 115 | 200 | 98 | 73 | 235 | 329 |  | 0 | 225 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 32 | 22 | 32 | 0 | 0 | 89 | 35 | 0 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 38 | 100 | 0 | 0 | 300 | 0 | 187 | 8 | 68 | 29 | 8 | 0 | 43 | 0 | 0 | 0 | 19 | 0 | 33 | 21 | 82 | 111 | 8 | 20 | 0 | 60 | 60 | 50 | 47 | 130 | 254 | 68 | 5 | 0 | 150 | 0 | 0 | 0 | 295 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 26 | 0 | 165 | 0 |  | 592 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 145 | 0 | 86 | 0 | 159 | 0 | 387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 36 | 0 | 0 |  | 4441 | 2411 | 6852 | 3182 | 592 | 1906 | 356 | 610 | 124 | 0 | 82 | 0 | 0 | 101.1
KWH | 0 | 0 | 0 | 2835000 | 0 | 1762636 | 1255968 | 6821144 | 7152000 |  | 0 | 4785000 | 3291258 | 161280 | 78912 | 0 | 0 | 0 | 0 | 147840 | 849024 | 150240 | 0 | 0 | 0 | 0 | 923400 | 345329 | 0 | 209664 | 600000 | 678240 | 583700 | 770100 | 0 | 0 | 2080767 | 848000 | 0 | 0 | 0 | 4899811 | 0 | 1047017 | 0 |  | 0 | 0 | 185212 | 0 | 0 | 480960 | 472992 | 538080 | 2254008 | 0 | 0 | 7474100 | 0 | 4482000 | 368000 | 1417870 | 563184 | 268800 | 0 | 802797 | 0 | 0 | 0 | 337932 | 52740 | 633600 | 467240 | 2046720 | 2941560 | 279360 | 293616 | 12500 | 1434000 | 1282680 | 864000 | 856728 | 3515236 | 5863000 | 1130688 | 1180800 | 0 | 3606730 | 310000 | 0 | 0 | 7360250 | 358968 | 136100 | 0 | 426545 | 0 | 0 | 184800 | 0 | 0 | 102330 | 909120 | 0 | 485091 | 0 | 1450800 | 718620 | 0 | 27240 | 780327 | 704532 | 0 | 0 | 662760 | 1447680 | 0 | 1339200 | 281960 | 2234880 | 0 |  | 14066182 | 0 | 8308224 | 0 | 85440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397600 | 124896 | 0 | 0 | 720000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377040 | 0 | 180270 | 0 | 0 | 3438100 | 0 | 0 | 0 | 0 | 4037000 | 0 | 1010770 | 0 | 4521464 | 0 | 8788500 | 688800 | 0 | 0 | 0 | 426240 | 0 | 26452 | 414816 | 9855500 | 339350 | 0 | 128400 |  | 108304666 | 57935044 | 166239710 | 71724642 | 14066182 | 41623555 | 19770310 | 13293600 | 2928767 | 335452 | 2046720 | 450482 | 0
Fuel Cost | 0 | 0 | 0 | 4167450 | 0 | 2326679.52 | 2135145.6 | 6889355.44 | 7366560 |  | 0 | 5215650 | 3653296.38 | 1224115.2 | 543703.68 | 0 | 0 | 0 | 0 | 1113235.2 | 7743098.88 | 1478361.6 | 0 | 0 | 0 | 0 | 6740820 | 2669393.17 | 0 | 157248 | 450000 | 0 | 0 | 0 | 0 | 0 | 561807.09 | 228960 | 0 | 0 | 0 | 5340793.99 | 0 | 1779928.9 | 0 |  | 0 | 0 | 1796556.4 | 0 | 0 | 3809203.2 | 595969.92 | 1598097.6 | 3335931.84 | 0 | 0 | 5530834 | 0 | 4123440 | 474720 | 1630550.5 | 636397.92 | 376320 | 0 | 1372782.87 | 0 | 0 | 0 | 429173.64 | 39555 | 1108800 | 350430 | 15350400 | 3118053.6 | 2536588.8 | 372892.32 | 199250 | 2351760 | 2052288 | 1537920 | 1336495.68 | 4007369.04 | 6097520 | 2227455.36 | 2255328 | 0 | 6239642.9 | 678900 | 0 | 0 | 7433852.5 | 269226 | 103436 | 0 | 3224680.2 | 0 | 0 | 960960 | 0 | 0 | 1196237.7 | 7409328 | 0 | 3419891.55 | 0 | 13231296 | 6790959 | 0 | 0 | 5899272.12 | 6136473.72 | 0 | 0 | 5679853.2 | 9641548.8 | 0 | 0 | 0 | 0 | 0 |  | 81021208.32 | 0 | 8723635.2 | 0 | 671558.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 616280 | 1218984.96 | 0 | 0 | 1476000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 723916.8 | 0 | 136464.39 | 0 | 0 | 18634502 | 0 | 0 | 0 | 0 | 5328840 | 0 | 1516155 | 0 | 5290112.88 | 0 | 8700615 | 7191072 | 0 | 0 | 0 | 3307622.4 | 0 | 292294.6 | 3065490.24 | 43265645 | 0 | 0 | 0 |  | 210753244.03 | 191180397.19 | 401933641.22 | 81032085.8 | 81021208.32 | 48993887.61 | 107882445.1 | 61900147 | 790767.09 | 3274918 | 15350400 | 1687782.3 | 0
Yesterday Day Peak | 0 | 0 | 0 | 115 | 200 | 96 | 30 | 286 | 312 |  | 0 | 225 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 16 | 25 | 31 | 25 | 33 | 0 | 0 | 90 | 35 | 0 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 20 | 2 | 80 | 0 | 0 | 335 | 0 | 159 | 8 | 52 | 29 | 8 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 33 | 15 | 84 | 106 | 8 | 17 | 2 | 60 | 52 | 48 | 47 | 163 | 257 | 31 | 80 | 0 | 150 | 18 | 0 | 0 | 310 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 30 | 0 | 10 | 0 | 85 | 35 | 0 | 4 | 16 | 18 | 0 | 0 | 8 | 72 | 0 | 89 | 46 | 166 | 0 |  | 689 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 185 | 0 | 35 | 0 | 186 | 0 | 392 | 17 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 400 | 36 | 0 | 0 |  | 7437 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 115 | 200 | 96 | 72 | 249 | 308 | 0 | 0 | 225 | 135 | 63 | 15 | 0 | 0 | 0 | 0 | 60 | 102 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 32 | 25 | 24 | 0 | 0 | 91 | 35 | 0 | 0 | 0 | 204 | 0 | 139 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 50 | 20 | 23 | 100 | 0 | 0 | 310 | 0 | 192 | 8 | 68 | 29 | 8 | 0 | 37 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 104 | 109 | 8 | 20 | 0 | 60 | 60 | 49 | 47 | 163 | 260 | 68 | 82 | 0 | 150 | 0 | 0 | 0 | 310 | 16 | 11 | 0 | 125 | 0 | 0 | 32 | 0 | 0 | 0 | 100 | 0 | 81 | 0 | 115 | 105 | 0 | 0 | 123 | 54 | 0 | 0 | 113 | 100 | 0 | 89 | 0 | 165 | 0 |  | 508 | 0 | 320 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 185 | 0 | 91 | 0 | 199 | 0 | 435 | 90 | 0 | 0 | 0 | 110 | 0 | 0 | 113 | 480 | 1 | 0 | 65 |  | 8926 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 115 | 200 | 100 | 78 | 300 | 360 | 0 | 0 | 225 | 150 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 100 | 0 | 0 | 50 | 54 | 55 | 55 | 19 | 25 | 33 | 25 | 33 | 52 | 0 | 92 | 35 | 0 | 0 | 25 | 225 | 0 | 140 | 0 | 0 | 0 |  | 102 | 100 | 100 | 50 | 20 | 20 | 100 | 0 | 0 | 360 | 0 | 225 | 8 | 90 | 30 | 8 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 145 | 150 | 17 | 22 | 0 | 60 | 60 | 51 | 44 | 163 | 260 | 66 | 86 | 0 | 150 | 18 | 0 | 0 | 320 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 90 | 0 | 162 |  |  | 888 | 16 | 410 | 0 | 115 | 220 | 0 | 0 | 30 | 60 | 40 | 0 | 20 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 0 | 0 | 50 | 52 | 33 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 150 | 0 | 220 | 0 | 95 | 100 | 0 | 0 | 400 | 90 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 660 | 35
Forecast for Day | 0 | 0 | 0 | 115 | 200 | 100 | 78 | 300 | 360 | 0 | 0 | 225 | 150 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 50 | 0 | 0 | 50 | 54 | 55 | 55 | 19 | 25 | 33 | 25 | 33 | 52 | 0 | 92 | 35 | 0 | 0 | 25 | 215 | 0 | 140 | 0 | 0 | 0 |  | 102 | 100 | 100 | 50 | 20 | 20 | 100 | 0 | 0 | 360 | 0 | 225 | 8 | 90 | 30 | 8 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 133 | 120 | 17 | 22 | 1.6 | 60 | 60 | 51 | 44 | 163 | 260 | 66 | 86 | 0 | 150 | 18 | 0 | 0 | 320 | 16 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 165 | 150 | 0 | 115 | 105 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 90 | 50 | 162 |  |  | 696 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 20 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 50 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 220 |  | 95 | 0 | 0 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 600 | 35
Generation at 08:00(Today) | 0 | 0 | 0 | 115 | 200 | 13 | 20 | 209 | 289 | 0 | 0 | 225 | 140 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 22 |  | 0 | 0 | 91 | 35 | 0 | 0 | 0 | 211 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 13 | 100 | 0 | 0 | 315 | 0 | 196 | 8 | 75 | 10 | 8 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 8 | 15 | 64 | 164 | 0 | 0 | 0 | 60 | 60 | 5 | 5 | 130 | 260 | 20 | 5 | 0 | 120 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 110 | 0 | 0 | 407 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 110 | 0 | 163 | 0 | 12 | 0 | 0 | 0 | 397 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 350 | 36 | 0 | 0 | 0
199
| Minimum Generation |  | 5537 | 5:00
| Highest Generation |  | 8926 | 19:00
| Day Peak Generation |  | 7437 | 12:00
| Evening Peak Generation |  | 8926 | 19:00
| HVDC Max Flow |  | 873 | 21:00
| HVDC EvPeak Flow |  | 508 | 19:00
| Load factor L.F |  | 77.6%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-11-27
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-11-26 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7437 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5587 | MW
Evening Peak Generation : |  | 8926 | MW Hour : | 19:00 | Available Max Generation : |  | 14211 | MW
E.P. Demand (at gen end) : |  | 8926 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 8000 | MW
Maximum Generation : |  | 8926 | MW Hour : | 19:00 | Reserve(Generation end) |  | 6211 | MW
Total Gen. (MKWH) : |  | 166.2397 | System Load Factor : | 77.6% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -28 | MW at | 19:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-11-27
Actual : | 101.04 | Ft.(MSL) , | Rule curve : | 106.4 | Ft.( MSL )
Gas Consumed : | Total = | 959.25 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 130025973.41
: |  | Coal : | 61900147 | Oil : | 111157363.1 | Total : | 303083483.51
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 2831.9994 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 954.9459 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 854.1582 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 771.2922 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 697.2878 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 562.6662 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 325.0266 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 145.1469 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 433.9063 |  |  | 0 | 0%
Total | 0 |  | 7576.4295 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 10) Sirajganj #1 CCPP STG
|  |  |  | 2) Baghabari-100 MW | 11)Ashuganj(S)-360 MW
|  |  |  | 3) Ghorasal Unit-1,2,3,4 | 12) Meghnaghat 450 MW GT-1
|  |  |  | 4) Ashuganj unit-4,5 | 13) Sirajganj #3
5) Kaptai-2
6) Raozan #2
7) Siddirganj-335 MW
8) Bibiyana-3
9) Chandpur-163 MW STG
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Kaptai-Hathazari 132 kV Ckt-1 was under shut down from 08:35 to 16:24 for A/M.
b) Savar-Manikganj 162 MW P/S 132 kV Ckt-1 was under shut down from 09:47 to 16:28 for A/M.
c) Chandpur-Chandpur P/S 132 kV Ckt-2 was under shut down from 09:01 to 21:57 for A/M.
d) Haripur-Fatulla 132 kV Ckt was under shut down from 10:12 to 18:27 for painting work.
e) Hasnabad-Sitalakhya 132 kV Ckt was under shut down from 10:59 to 16:57 for tower painting.
f) Bheramara HVDC-Ishurdi 230 kV Ckt-4 was under shut down from 09:14 to 19:43 for A/M.
g) Rangpur-Saidpur 132 kV Ckt-1 was under shut down from 08:32 to 16:40 for A/M.
h) Jhenaidah-Magura 132 kV Ckt-1 was under shut down from 08:06 to 15:55 for C/M.
i) Srimongal 132/33 kV T-1 transformer was under shut down from 08:22 to 16:34 for A/M.
j) Kishorganj-Mymensing 132 kV Ckt-2 was under shut down from 08:49 to 17:30 for A/M.
k) Bhulta 400/230 kV T-2 transformer was under shut down from 08:19 to 20:27 for A/M.
l) Natore 132/33 kV T-2 transformer was under shut down from 08:56 to 12:57 for A/M.
m) Faridpur 132/33 kV T-3 transformer was under shut down from 10:25 to 16:35 for A/M.
n) HVDC Block-2 tripped at 17:37 due to filter trip and was deblock at 19:10.
o) After restoration of gas Sikalbaha-150 MW GT was synchronized at 14:45.
p) Sirajganj #3 GT & ST were shut down at 07:40(27/11/20) for air filter changing.
q) Sirajganj #1 GT was synchronized at 06:34(27/11/20).
r) Bheramara HVDC pole-2 is under shut down at 07:30(27/11/20) for maint.
s) Chandraghona 132/33 kV T-1 transformer is under shut down at 07:31(27/11/20) for A/M.
t) Aminbazar-Hasnabad 230 kV Ckt-1 & 2 are under shut down since 07:21(27/11/20) for D/W.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-11-26 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 115 | 2835000 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 0 | Machin problem.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 72 | 1255968
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 96 | 1762636 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 249 | 6821144 | ST Under maint
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 308 | 7152000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4785000 | GT-1 under maint.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 63 | 161280 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 135 | 3291258 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 15 | 78912 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 0 | Reserve.
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 209664 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 60 | 147840 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under Maintenance
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 849024
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 923400
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 32 | 150240 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 345329
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve.
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1278240 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 583700 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 24 | 770100 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 125 | 426545 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 0 | Reserve.
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 718620
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 89 | 1339200 | Engine problem
| Manikgonj 162MW PP |  | IPP | 9*18 | 0 | 165 | 2234880 | on test.
| Dhaka area Total |  |  |  | 5895 | 2390 | 38119980
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve.
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 102330
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 480960
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 126 | 2928767 | Unit-2 under maint
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4899811
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 139 | 1047017
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 185212 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 909120
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 472992
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 23 | 538080
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve.
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27240
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 123 | 780327 | Transformer O/L
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 704532
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1447680
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 0 | 0 | 0
| Chattogram area Total |  |  |  | 2266 | 990 | 14524068
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 100 | 2254008 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas Shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 192 | 4482000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7474100 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 563184 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 8 | 268800 | Gas shortage
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 368000 | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 37 | 802797
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 81 | 485091 | Engine problem
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 68 | 1417870 | ST Under maint
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve.
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 337932
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 52740 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 104 | 2046720 | Low demand
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 633600
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve.
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 467240
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 662760
| Cumilla Area Total |  |  |  | 2980 | 1131 | 22316842
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 109 | 2941560 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 293616
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 8 | 279360 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12500
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 32 | 184800
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1450800 | #REF!
| Mymensingh PV 50 MW Solar PP |  | IPP | 50 | 0 | 0 | 281960
| Mymensingh Area Total |  |  |  | 637 | 284 | 5444596
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1434000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1282680
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3515236
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 260 | 5863000 | Machin problem.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 49 | 864000
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 47 | 856728
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 136100
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 68 | 1130688 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1180800
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 150 | 3606730
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 310000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 358968 | Engine problem
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7360250 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 0 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1276 | 27899180
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 508 | 14066182
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 49 | 85440 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 320 | 8308224 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Reserve.
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 90 | 688800 | Engine problem
107 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 967 | 23148646
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 124896 | High voltage
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 20 | 397600 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 91 | 1010770
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 480 | 9855500
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 1 | 339350
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 0 | 65 | 128400 | Ontest.
| Barisal Area Total |  |  |  | 1054 | 673 | 11856516
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 720000 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machin problem.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel Shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel Shortage
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Under maint.
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 185 | 4037000 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 199 | 4521464 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 435 | 8788500 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 377040
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 180270
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve.
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve.
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 0 | Reserve.
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 414816
| Rajshahi Area Total |  |  |  | 2183 | 965 | 19039090
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 140 | 3438100 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 110 | 426240
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 26452
| Rangpur Area Total |  |  |  | 605 | 250 | 3890792
| Total |  |  |  | 19892 | 8926 | 166239710
| Eastern Grid Total |  |  |  | 13766 | 6071 | 108304666
| Western Grid Total |  |  |  | 6126 | 2855 | 57935044
| National Grid Total |  |  |  | 19892 | 8926 | 166239710
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-11-26
| (a) ENTIRE EASTERN GRID : |  | 5782 | MW | (b) ENTIRE WESTERN GRID : |  | 2657 | MW
| i) Dhaka area |  | 3127 | MW | i) Khulna area |  | 1031 | MW
| ii) Chittagong area |  | 963 | MW | ii) Rajshahi area |  | 825 | MW
| iii) Comilla area |  | 709 | MW | iii) Barisal area |  | 234 | MW
| iv) Mymensingh area |  | 662 | MW | iv) Rangpur area |  | 567 | MW
| v) Sylhet area |  | 321 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8439 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 106 | 12:00 | Jamalpur | 92 | 18:00 | Benapol | 34 | 18:00
| Munsiganj | 90 | 19:00 | Sherpur | 76 | 18:00 | Jhenida | 76 | 18:00
| Sonargaon | 62 | 12:00 | Srimongal | 27 | 18:00 | Bottail | 94 | 18:00
| Shyampur | 170 | 11:00 | Shahjibazar | 80 | 18:00 | G.K Project | 34 | 19:00
| Bhulta | 149 | 18:30 | Fenchuganj | 27 | 18:00 | Faridpur | 130 | 19:30
| Madanganj | 56 | 12:00 | Kulawara | 31 | 18:30 | Madaripur | 61 | 20:00
| Shitalakhya | 101 | 12:00 | Sylhet | 81 | 19:00 | Sariatpur | 40 | 19:30
| Rahim steel | 17 | 9:00 | Chatak | 20 | 18:00 | Gopalganj | 56 | 21:00
| Matuail | 70 | 12:00 | Sunamganj | 28 | 19:00 | Bagerhat | 75 | 19:00
| Ghorasal | 64 | 18:30 | Biani Bazar | 37 | 18:00 | Mongla | 37 | 18:00
| Narsingdi | 121 | 20:00 | Comilla (S) | 108 | 18:30 | Satkhira | 70 | 18:00
| Haripur (SBU) | 100 | 21:00 | Comilla(N) | 63 | 18:00 | Gallamari | 29 | 9:00
| Ullon | 43 | 18:00 | Chandpur | 59 | 19:00 | Magura | 36 | 18:00
| Hasnabad | 141 | 19:30 | Feni | 72 | 18:00 | Norail | 28 | 18:00
| Magbazar | 73 | 14:00 | Chowmuhani | 114 | 20:00 | Chuadanga | 62 | 18:00
| Maniknagar | 72 | 11:00 | Ashuganj | 35 | 19:00 | Barisal(N) | 27 | 19:00
| Bangabhaban | 22 | 10:00 | Daudkandi | 96 | 19:30 | Barisal (S) | 70 | 18:00
| Narinda | 68 | 13:00 | B.Baria | 95 | 19:30 | Patuakhali | 72 | 18:00
| Dhanmondi | 106 | 13:00 | Ramganj | 62 | 19:30 | Bhandaria | 40 | 19:00
| Lalbag | 75 | 12:00 | Chaddagram | 22 | 18:00 | Borhan Uddin | 25 | 19:30
| Madartek | 47 | 18:30 | PHP | 10 | 20:00 | Ishurdi | 47 | 18:00
| Dhaka University |  |  | Madunaghat | 39 | 17:00 | Ruppur Paromanobik | 2 | 2:00
| Aftabnagar | 6 | 0.5 | Hathazari | 72 | 0.75 | Natore | 82 | 0.75
| Fatullah | 32 | 17:00 | Khulshi | 169 | 14:00 | Bogra | 121 | 19:30
| Mirpur | 69 | 18:00 | Halishahar | 98 | 15:00 | Noagaon | 78 | 20:00
| Kalyanpur | 60 | 18:00 | Baraulia | 136 | 8:00 | Rajshahi | 92 | 19:30
| Gulshan | 78 | 18:00 | Sikalbaha | 21 | 18:30 | Rajshahi New | 8 | 18:00
| Uttara | 65 | 18:00 | Dohazari | 58 | 19:30 | C.Nawabganj | 50 | 12:00
| Uttara New | 23 | 18:00 | Cox'sbazar | 70 | 18:00 | Amnura | 28 | 18:00
| Kamrangirchar | 73 | 18:00 | Chandraghona | 20 | 18:00 | Pabna | 81 | 18:00
| Savar | 106 | 18:00 | Kaptai | 3.2 | 18:30 | Shahjadpur | 50 | 18:30
| Bhasantec | 105 | 18:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 68 | 12:00
| Agargaon | 48 | 18:00 | Bakulia | 81 | 18:30 | Niyamatpur | 37 | 18:00
| Satmosjid | 64 | 0.77083 | Julda | 21 | 0.625 | Joypurhat | 41 | 0.75
| Tongi | 87 | 11:00 | TK chemical | 19 | 18:00 | Sherpur(Bogura) | 36 | 18:00
| Kabirpur | 153 | 15:00 | Modern Steel | 16 | 13:00 | Mohastangor | 32 | 18:00
| Basundhara | 94 | 13:00 | Shahmirpur | 16 | 14:00 | Rangpur | 99 | 18:30
| Manikganj | 52 | 21:00 | Khagrachhari | 18 | 20:00 | Lalmonirhat | 41 | 18:30
| Joydevpur | 111 | 18:30 | Matarbari | 26.5 | 18:00 | Saidpur | 88 | 18:00
| New Tongi | 73 | 18:30 | Baroiar Hat | 32 | 13:00 | Purbasadipur | 81 | 18:30
| Kodda | 176 | 17:00 | Rangamati | 9 | 18:30 | Thakurgaon | 60 | 18:30
| Dhamrai | 66 | 18:30 | Abul Khair 230 | 9 | 1:00 | Palashbari | 86 | 18:30
| Rajendrapur | 80 | 18:30 | BSRM | 108 | 13:00 | Barapukuria | 34 | 18:30
| Valuka | 80 | 12:00 | GPH Ispat | 76 | 23:00 | Panchagar | 42 | 18:00
| Tangail | 135 | 18:00 | Goalpara | 18 | 13:00 | Joldhaka | 19 | 18:00
| Mymensing | 127 | 18:00 | Central s/s | 75 | 18:00 | Kurigram | 38 | 18:30
| Kishorganj | 84 | 20:00 | Noapara | 45 | 18:00
| Netrokona | 87 | 18:00 | Jessore | 76 | 18:30
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-11-26 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 417 | 19:00 | 400 | 9:00 | Kaliakoir | 394 | 0.25 | 377 | 0.66667
| Bheramara | 413 | 21:00 | 400 | 19:30 | Bhulta | 396 | 0.79167 | 383 | 0.5
| Ashuganj(N) | 401 | 4:00 | 388 | 12:00 | Gopalganj | 419 | 0.041667 | 400 | 0.75
| Payra | 420 | 19:00 | 410 | 18:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 238 | 1:00 | 232 | 11:00 | Comilla (N) | 238 | 19:00 | 231 | 12:00
| Ishurdi | 240 | 3:00 | 230 | 12:00 | Hathazari | 223 | 18:30 | 209 | 12:00
| Ashuganj | 241 | 19:00 | 232 | 11:00 | Megnaghat | 238 | 21:00 | 231 | 11:00
| Serajganj | 232 | 4:00 | 228 | 12:00 | Fenchuganj | 247 | 4:00 | 239 | 10:00
| Baghabari | 242 | 1:00 | 238 | 7:00 | Siddhirganj | 234 | 19:00 | 226 | 11:00
| Barapukuria | 231 | 4:00 | 225 | 12:00 | Maniknagar | 232 | 5:00 | 228 | 14:00
| Bogra | 231 | 3:00 | 223 | 12:00 | Agargaon | 233 | 1:00 | 225 | 10:00
| Rajshahi | 229 | 1:00 | 218 | 12:00 | Barisal | 253 | 22:00 | 244 | 8:00
| Khulna South | 233 | 2:00 | 214 | 12:00 | AKSML | 225 | 19:00 | 210 | 12:00
| Rampura | 231 | 18:00 | 227 | 11:00 | BSRM | 227 | 19:30 | 215 | 11:00
| Haripur | 231 | 19:30 | 224 | 12:00 | Bibiyana | 247 | 22:00 | 235 | 11:00
| Hasnabad | 233 | 23:00 | 225 | 9:00 | Bhulta | 235 | 19:00 | 226 | 17:00
| Shyampur | 231 | 19:00 | 220 | 12:00 | Ashuganj (S) | 239 | 19:00 | 230 | 12:00
| Aminbazar | 233 | 18:30 | 227 | 11:00 | Kaliakoir | 235 | 18:30 | 227 | 11:00
| Tongi | 233 | 19:00 | 221 | 11:00 | GPH | 224 | 18:30 | 209 | 11:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 139 | 18:30 | 134 | 12:00 | Madanhat | 136 | 0.77083 | 127 | 0.45833
| Munsiganj | 140 | 18:30 | 132 | 12:00 | Hathazari | 135 | 0.77083 | 127 | 0.5
| Sonargaon | 137 | 19:00 | 132 | 10:00 | Khulshi | 133 | 0.77083 | 122 | 0.5
| Shyampur | 137 | 18:30 | 130 | 12:00 | Halishahar | 135 | 0.79167 | 123 | 0.45833
| Bhulta | 133 | 6:00 | 128 | 11:00 | Baraulia | 134 | 0.5 | 126 | 0.41667
| Madanganj | 140 | 20:00 | 129 | 4:00 | Sikalbaha | 135 | 0.79167 | 125 | 0.45833
| Shitalakhya | 140 | 18:30 | 132 | 12:00 | Dohazari | 133 | 0.8125 | 126 | 0.33333
| Rahim steal | 139 | 18:00 | 134 | 11:00 | Cox'sbazar | 128 | 0.54167 | 118 | 0.45833
| Matuail | 139 | 18:30 | 134 | 12:00 | Chandraghona | 135 | 0.79167 | 127 | 0.45833
| Ghorasal | 140 | 1:00 | 136 | 9:00 | Kaptai | 135 | 0.75 | 130 | 0.375
| Narsinghdi | 136 | 3:00 | 131 | 10:00 | A. Khaer Stl. | 134 | 0.79167 | 124 | 0.5
| Haripur (SBU) | 139 | 18:00 | 135 | 9:00 | Bakulia | 134 | 0.79167 | 123 | 0.45833
| Ullon | 133 | 21:00 | 127 | 10:00 | Julda | 135 | 0.77083 | 123 | 0.45833
| Hasnabad | 140 | 21:00 | 134 | 9:00 | TK Chemical | 135 | 0.8125 | 125 | 0.45833
| Magbazar | 133 | 22:00 | 127 | 10:00 | Modern Steel | 134 | 0.79167 | 122 | 0.5
| Maniknagar | 138 | 4:00 | 133 | 12:00 | Shahmirpur | 135 | 0.79167 | 124 | 0.45833
| Bangabhaban | 138 | 4:00 | 133 | 12:00 | Khagrachhari | 134 | 0.83333 | 127 | 0.45833
| Narinda | 138 | 4:00 | 133 | 12:00 | Matarbari | 130 | 0.54167 | 120 | 0.45833
| Dhanmondi | 133 | 21:00 | 127 | 10:00 | Baroiar Hat | 136 | 0.77083 | 128 | 0.5
| Lalbag | 131 | 24:00 | 122 | 10:00 | Rangamati | 134 | 19:00 | 127 | 11:00
| Madartek | 132 | 4:00 | 127 | 10:00 | Goalpara S/S | 137 | 4:00 | 128 | 12:00
| Dhaka University |  |  |  |  | Khulna Central S/S | 137 | 2:00 | 131 | 0.33333
| Aftabnagar | 133 | 22:00 | 127 | 10:00 | Noapara | 136 | 2:00 | 129 | 0.33333
| Fatuiiah | 138 | 20:00 | 130 | 12:00 | Jessore | 134 | 2:00 | 126 | 0.5
| Mirpur | 131 | 20:00 | 124 | 10:00 | Benapol | 135 | 0.125 | 125 | 0.5
| Kalyanpur | 132 | 19:00 | 125 | 10:00 | Jhenida | 134 | 4:00 | 124 | 0.45833
| Gulshan | 131 | 6:00 | 126 | 10:00 | Bottail | 138 | 0.20833 | 130 | 0.75
| Uttara | 130 | 5:00 | 124 | 10:00 | G.K Project | 142 | 0.16667 | 136 | 0.5
| Uttara New | 130 | 19:00 | 124 | 10:00 | Faridpur | 138 | 0.16667 | 130 | 0.75
| Kamrangirchar | 137 | 5:00 | 131 | 10:00 | Madaripur | 141 | 0.16667 | 135 | 0.91667
| Savar | 133 | 19:00 | 123 | 10:00 | Shariyatpur S/S | 141 | 2:00 | 135 | 0.75
| Bhasantec | 136 | 5:00 | 130 | 12:00 | Gopalganj | 143 | 0.20833 | 135 | 0.75
| Agargaon | 137 | 5:00 | 131 | 10:00 | Bagerhat | 135 | 4:00 | 126 | 0.5
| Satmosjid | 137 | 5:00 | 131 | 10:00 | Mongla | 135 | 19:00 | 125 | 0.5
| Tongi | 141 | 19:00 | 134 | 11:00 | Satkhira | 137 | 2:00 | 127 | 12:00
| Kabirpur | 135 | 21:00 | 128 | 16:00 | Gallamari | 138 | 0.083333 | 128 | 0.5
| Basundhara | 133 | 22:00 | 127 | 10:00 | Magura | 135 | 1:00 | 124 | 0.75
| Manikganj | 141 | 19:00 | 132 | 12:00 | Norail | 134 | 0.16667 | 123 | 0.75
| Joydevpur | 141 | 7:00 | 135 | 15:00 | Chuadanga | 133 | 1:00 | 119 | 0.75
| New Tongi | 139 | 19:00 | 133 | 12:00 | Barisal(N) | 143 | 1:00 | 141 | 5:00
| Kodda | 136 | 19:00 | 130 | 16:00 | Barisal (S) | 141 | 0.041667 | 136 | 0.91667
| Dhamrai | 134 | 3:00 | 128 | 15:00 | Patuakhali(S) | 140 | 0.77083 | 132 | 0.5
| Rajendrapur | 138 | 21:00 | 131 | 12:00 | Bhandaria | 140 | 0.041667 | 134 | 0.8125
| Valuka | 132 | 23:00 | 126 | 17:00 | Ishurdi | 139 | 3:00 | 134 | 12:00
| Tangail | 135 | 4:00 | 130 | 15:00 | Ruppur Paromanobik | 139 | 4:00 | 134 | 11:00
| Mymensing | 133 | 11:00 | 126 | 23:00 | Natore | 139 | 5:00 | 133 | 12:00
| Kishorganj | 132 | 10:00 | 128 | 18:00 | Bogra | 139 | 3:00 | 134 | 9:00
| Netrokona | 132 | 11:00 | 126 | 16:00 | Noagaon | 135 | 3:00 | 127 | 12:00
| Jamalpur | 138 | 22:00 | 124 | 23:00 | Rajshahi | 140 | 4:00 | 133 | 12:00
| Sherpur | 136 | 22:00 | 123 | 23:00 | Rajshahi New | 141 | 3:00 | 134 | 12:00
| Srimongal | 138 | 18:30 | 136 | 11:00 | C.Nawabganj | 139 | 4:00 | 131 | 12:00
| Shahjibazar | 135 | 1:00 | 133 | 15:00 | Amnura | 139 | 3:00 | 131 | 12:00
| Fenchuganj | 139 | 22:00 | 135 | 12:00 | Pabna | 138 | 3:00 | 133 | 18:00
| Khulawara | 138 | 23:00 | 135 | 10:00 | Shahjadpur | 141 | 6:00 | 138 | 9:00
| Sylhet | 136 | 21:00 | 133 | 11:00 | Serajganj | 136 | 3:00 | 131 | 12:00
| Chatak | 135 | 21:00 | 132 | 10:00 | Niyamatpur | 135 | 4:00 | 126 | 12:00
| Sunamganj | 134 | 1:00 | 132 | 11:00 | Joypurhat | 136 | 4:00 | 127 | 12:00
| Biani Bazar | 136 | 24:00 | 132 | 11:00 | Sherpur(Bogura) | 139 | 3:00 | 132 | 12:00
| Comilla(s) | 132 | 1:00 | 125 | 18:00 | Mohastangor | 137 | 4:00 | 130 | 12:00
| Comilla(n) | 141 | 20:00 | 137 | 11:00 | Rangpur | 129 | 5:00 | 122 | 8:00
| Chandpur | 138 | 18:00 | 134 | 10:00 | Lalmonirhat | 130 | 4:00 | 122 | 13:00
| Feni | 138 | 20:00 | 132 | 11:00 | Saidpur | 127 | 3:00 | 121 | 12:00
| Chowmuhani | 136 | 18:30 | 130 | 23:00 | Purbasadipur | 127 | 3:00 | 119 | 12:00
| Ashuganj | 137 | 10:00 | 135 | 12:00 | Thakurgaon | 128 | 5:00 | 118 | 18:00
| Daudkandi | 139 | 18:30 | 133 | 12:00 | Palashbari | 133 | 3:00 | 127 | 12:00
| B.Baria | 133 | 21:00 | 130 | 16:00 | Barapukuria | 131 | 4:00 | 125 | 12:00
| Ramganj | 132 | 20:00 | 126 | 12:00 | Panchagar | 126 | 3:00 | 114 | 18:00
| Chaddagram | 137 | 17:00 | 133 | 9:00 | Joldhaka | 129 | 3:00 | 119 | 12:00
| PHP | 136 | 19:00 | 128 | 11:00 | Kurigram | 128 | 0.16667 | 121 | 0.54167

## L-Curve
Date | 2020-11-26
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 345 | 4441 | 2411 | 6852 |  |  |  | QF-LDC-11
0:30 | 344.5 | 4246.5 | 2339 | 6585.5 | Date: | 2020-11-26
1:00 | 344 | 4052 | 2267 | 6319
1:30 | 346 | 3920.5 | 2201 | 6121.5
2:00 | 348 | 3789 | 2135 | 5924
2:30 | 352 | 3752.5 | 2100 | 5852.5 | [5 empty] | Gen. at Eve. Peak | 8926 | 8926 MW (19:00 )
3:00 | 356 | 3716 | 2065 | 5781 | [6 empty] | 19:00
3:30 | 324 | 3685 | 2005.5 | 5690.5 | [5 empty] | Gen. at Day Peak | 7437 | 7437 MW (12:00 )
4:00 | 292 | 3654 | 1946 | 5600 | [6 empty] | 12:00
4:30 | 262.5 | 3664.5 | 1904 | 5568.5 | [5 empty] | Highest Generation | 8926
5:00 | 233 | 3675 | 1862 | 5537 | [6 empty] | 19:00
5:30 | 216 | 3748.5 | 1895.5 | 5644
6:00 | 199 | 3822 | 1929 | 5751
6:30 | 150.5 | 3932.5 | 1981.5 | 5914
7:00 | 102 | 4043 | 2034 | 6077
7:30 | 73 | 4229 | 2073.5 | 6302.5
8:00 | 44 | 4415 | 2113 | 6528
8:30 | 144 | 4490 | 2159 | 6649
9:00 | 244 | 4565 | 2205 | 6770
9:30 | 334 | 4624 | 2225.5 | 6849.5
10:00 | 424 | 4683 | 2246 | 6929
10:30 | 504.5 | 4677 | 2367 | 7044
11:00 | 585 | 4671 | 2488 | 7159
11:30 | 568 | 4777.5 | 2520.5 | 7298
12:00 | 551 | 4884 | 2553 | 7437
12:30 | 444 | 4983 | 2552.5 | 7535.5
13:00 | 337 | 5082 | 2552 | 7634
13:30 | 387.5 | 4959.5 | 2461 | 7420.5
14:00 | 438 | 4837 | 2370 | 7207
14:30 | 459 | 4835 | 2358.5 | 7193.5
15:00 | 480 | 4833 | 2347 | 7180
15:30 | 470 | 4769.5 | 2326.5 | 7096
16:00 | 460 | 4706 | 2306 | 7012
16:30 | 401 | 4827 | 2373.5 | 7200.5
17:00 | 342 | 4948 | 2441 | 7389
17:30 | 193.5 | 5420.5 | 2645.5 | 8066
18:00 | 45 | 5893 | 2850 | 8743
18:30 | 36.5 | 5982 | 2852.5 | 8834.5
19:00 | 28 | 6071 | 2855 | 8926
19:30 | 60 | 5927 | 2852 | 8779
20:00 | 160 | 5759 | 2889 | 8648 |  |  |  | Executive Engineer
20:30 | 170.5 | 5635 | 2863 | 8498 |  |  |  | Network Operation Division
21:00 | 181 | 5511 | 2837 | 8348
21:30 | 217 | 5336.5 | 2740.5 | 8077
22:00 | 253 | 5162 | 2644 | 7806 |  |  |  |  | Page 6 of 7
22:30 | 316.5 | 4951 | 2606.5 | 7557.5
23:00 | 380 | 4740 | 2569 | 7309
23:30 | 362.5 | 4590.5 | 2490 | 7080.5
24:00 | 345 | 4441 | 2411 | 6852
8926 MW (19:00 )
7437 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-11-26 |  | Energy | 166239710
[10 empty] | 2020-11-26 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3182 | 592 | 1906 | 584 | 610 | 124 | 0 | 0 | 82
0:30 | 3141.5 | 545 | 1812 | 385 | 613.5 | 122.5 | 0 | 0 | 80 | Date: | 2020-11-26
1:00 | 3101 | 498 | 1718 | 186 | 617 | 121 | 0 | 0 | 78
1:30 | 3034.5 | 498 | 1606.5 | 186 | 598.5 | 120 | 0 | 0 | 78 | [7 empty] | Total Energy | 166.2397 | Total Energy Gen 166.240 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 166.240 MKWHr
2:00 | 2968 | 498 | 1495 | 186 | 580 | 119 | 0 | 0 | 78 | [7 empty] | Energy not Served | 0
2:30 | 2944.5 | 497.5 | 1465 | 188.5 | 560 | 120 | 0 | 0 | 77 | [7 empty] | Energy Requirement | 166.2397
3:00 | 2921 | 497 | 1435 | 191 | 540 | 121 | 0 | 0 | 76
3:30 | 2924 | 450.5 | 1404.5 | 175 | 540 | 121.5 | 0 | 0 | 75 | [6 empty] | Shortage
4:00 | 2927 | 404 | 1374 | 159 | 540 | 122 | 0 | 0 | 74
4:30 | 2932 | 404 | 1354 | 161.5 | 520 | 123 | 0 | 0 | 74
5:00 | 2937 | 404 | 1334 | 164 | 500 | 124 | 0 | 0 | 74
5:30 | 2987.5 | 404 | 1396.5 | 169 | 490 | 125 | 0 | 0 | 72
6:00 | 3038 | 404 | 1459 | 174 | 480 | 126 | 0 | 0 | 70
6:30 | 3122 | 404 | 1528.5 | 183 | 480 | 126 | 0 | 0 | 69 |  |  |  |  | Coal
7:00 | 3206 | 404 | 1598 | 192 | 480 | 126 | 0 | 0 | 68
7:30 | 3255.5 | 404 | 1684 | 266 | 480 | 126.5 | 0 | 0 | 71 |  |  |  | Oil |  |  |  | ,
8:00 | 3305 | 404 | 1770 | 340 | 480 | 127 | 0 | 0 | 74
8:30 | 3297.5 | 404 | 1848.5 | 379 | 480 | 127 | 0 | 0 | 75
9:00 | 3290 | 404 | 1927 | 418 | 480 | 127 | 0 | 0 | 76
9:30 | 3232 | 404 | 1938.5 | 515.5 | 495 | 127 | 0 | 0 | 76
10:00 | 3174 | 404 | 1950 | 613 | 510 | 127 | 0 | 0 | 76
10:30 | 3193 | 541.5 | 1851.5 | 663.5 | 510 | 126 | 0 | 0 | 80
11:00 | 3212 | 679 | 1753 | 714 | 510 | 125 | 0 | 0 | 84
11:30 | 3209 | 684 | 1815.5 | 776.5 | 525 | 125 | 0 | 0 | 84
12:00 | 3206 | 689 | 1878 | 839 | 540 | 125 | 0 | 0 | 84
12:30 | 3160 | 689.5 | 1886.5 | 991 | 540 | 125 | 0 | 0 | 88
13:00 | 3114 | 690 | 1895 | 1143 | 540 | 125 | 0 | 0 | 92
13:30 | 3114 | 690 | 1895 | 1143 | 540 | 125 | 0 | 0 | 92
14:00 | 3114 | 690 | 1895 | 1143 | 540 | 125 | 0 | 0 | 92
14:30 | 3107.5 | 690 | 1781.5 | 1057 | 515 | 124 | 0 | 0 | 87
15:00 | 3101 | 690 | 1668 | 971 | 490 | 123 | 0 | 0 | 82
15:30 | 3125.5 | 690 | 1578.5 | 968.5 | 490 | 123 | 0 | 0 | 85
16:00 | 3150 | 690 | 1489 | 966 | 490 | 123 | 0 | 0 | 88
16:30 | 3144.5 | 686.5 | 1506.5 | 1110.5 | 490 | 124.5 | 41.5 | 0 | 88
17:00 | 3139 | 683 | 1524 | 1255 | 490 | 126 | 83 | 0 | 88
17:30 | 3253 | 595.5 | 1712 | 1609 | 590 | 126 | 83 | 0 | 97
18:00 | 3367 | 508 | 1900 | 1963 | 690 | 126 | 83 | 0 | 106
18:30 | 3334 | 508 | 1948.5 | 2075 | 655 | 126 | 83 | 0 | 105
19:00 | 3301 | 508 | 1997 | 2187 | 620 | 126 | 83 | 0 | 104
19:30 | 3279 | 610 | 2005 | 1950 | 620 | 126 | 83 | 0 | 106
20:00 | 3232 | 803 | 1908 | 1774 | 620 | 126 | 83 | 0 | 102
20:30 | 3229 | 838 | 1910 | 1616 | 624.5 | 126 | 51.5 | 0 | 103
21:00 | 3226 | 873 | 1912 | 1458 | 629 | 126 | 20 | 0 | 104
21:30 | 3203.5 | 873 | 1898 | 1231.5 | 634.5 | 126.5 | 10 | 0 | 100
22:00 | 3181 | 873 | 1884 | 1005 | 640 | 127 | 0 | 0 | 96
22:30 | 3195 | 825 | 1884 | 794.5 | 640 | 127 | 0 | 0 | 92
23:00 | 3209 | 777 | 1884 | 584 | 640 | 127 | 0 | 0 | 88
23:30 | 3195.5 | 684.5 | 1895 | 584 | 625 | 125.5 | 0 | 0 | 85 | Max Temp. in Dhaka |  | 27.4° C
24:00 | 3182 | 592 | 1906 | 584 | 610 | 124 | 0 | 0 | 82
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 166.240 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 166.240 MKWHr
Note on W13: Author:

## Generation
g | 2020-11-26
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 86 | 84 | 86 | 87 | 89 | 91 | 91 | 92 | 92 | 92 | 90 | 90 | 90 | 86 | 88 | 88 | 91 | 91 |  | 91 | 91 | 91 | 91 | 92 | 92 | 89 | 2080767
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 848000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [7 empty] | 7 | 14 | 18 | 19 | 19 |  | 15 | 11 | 6 | 0 | [9 empty] | 102330
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 203 | 203 | 203 | 202 | 203 | 205 | 214 | 211 | 213 | 203 | 217 | 203 | 204 | 204 | 209 | 204 | 219 |  | 204 | 204 | 203 | 204 | 203 | 203 | 203 | 4899811
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | [14 empty] | 15 | 70 | 70 | 145 |  | 139 | 139 | 139 | 139 | 139 | 138 | 139 | 1047017
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 51 | 51 |  | 51 | 51 | 51 |  |  |  |  | 185212
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [16 empty] | 30 | 90 |  | 125 | 95 | 45 | 45 |  |  |  | 426545
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 36 | 36 | 55 | 55 | 36 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 368000
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2835000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 0
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 135 | 135 | 110 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 90 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2254008
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 29 | 29 | 5 | 5 | 5 | 5 | 29 | 29 | 26 | 26 | 29 | 29 | 29 | 29 | 29 | 26 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 563184
33 | Ashuganj 225 MW CCPP | 182 | 182 | 182 | 182 | 182 | 200 | 198 | 197 | 189 | 149 | 180 | 159 | 167 | 174 | 193 | 195 | 182 | 203 |  | 192 | 193 | 181 | 190 | 181 | 188 | 187 | 4482000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 260 | 260 | 260 | 290 | 275 | 315 | 320 | 325 | 305 | 335 | 300 | 310 | 300 | 315 | 300 | 350 |  | 310 | 315 | 300 | 305 | 300 | 300 | 300 | 7474100
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 20 | 35 | 35 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 268800
36 | Chandpur 150 MW CCPP | 52 | 51 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 37 | 74 | 52 | 45 | 76 | 75 | 75 | 75 | 76 |  | 68 | 70 | 68 | 69 | 69 | 69 | 68 | 1417870
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 303 | 304 | 302 | 304 | 303 | 301 | 302 | 299 | 294 | 293 | 290 | 286 | 286 | 287 | 287 | 286 | 252 | 259 |  | 249 | 241 | 237 | 237 | 235 | 235 | 235 | 6821144
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 4785000
41 | Haripur 360MW CCPP(HPL) | 299 | 325 | 283 | 283 | 284 | 283 | 304 | 304 | 332 | 328 | 306 | 312 | 307 | 270 | 270 | 270 | 270 | 308 |  | 308 | 310 | 310 | 309 | 309 | 309 | 329 | 7152000
42 | RPCL 210MW CCPP | 133 | 131 | 151 | 152 | 169 | 167 | 168 | 167 | 148 | 127 | 106 | 106 | 103 | 100 | 101 | 108 | 111 | 109 |  | 109 | 109 | 109 | 109 | 110 | 111 | 111 | 2941560
43 | Mymensingh PV 50 MW Solar PP | [6 empty] | 2 | 18 | 28 | 47 | 53 | 46 | 25 | 35 | 38 | 7 | 1 | [9 empty] | 281960
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1434000
45 | Fenchugonj CCPP Phase-2 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1282680
46 | Shajibazar 330 MW CCPP | 255 | 250 | 250 | 253 | 253 | 258 | 262 | 263 | 258 | 261 | 260 | 257 | 255 | 263 | 255 | 262 | 257 | 263 |  | 260 | 259 | 255 | 260 | 251 | 256 | 254 | 5863000
47 | Shahjibazar GTPP Unit- 8 & 9 | 69 | 56 | 40 | 40 | 40 | 40 | 33 | 32 | 32 | 32 | 20 | 31 | 31 | 31 | 31 | 51 | 66 | 66 |  | 68 | 64 | 64 | 64 | 66 | 67 | 68 | 1130688
48 | Shahjibazar 86MW PP (Shahjibazar) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 50 | 50 | 79 | 77 | 80 | 80 | 20 | 20 | 20 | 20 | 82 |  | 82 | 82 | 82 | 82 | 80 | 40 | 5 | 1180800
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 151 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3606730
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | [9 empty] | 310000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [26 empty] | 0
54 | Hobiganj 11MW PP Cofidence-E | [7 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 9 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 136100
55 | Fenchugonj 51 MW PP (Barakatullah) | 47 | 11 | 11 | 11 | 11 | 11 | 11 | 42 | 42 | 42 | 48 | 48 | 48 | 48 | 47 | 11 | 11 | 46 |  | 49 | 49 | 49 | 49 | 49 | 50 | 50 | 864000
56 | Shahjahanulla 25 MW PP | [7 empty] | 16 | 16 | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 358968
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 280 | 300 | 290 | 290 | 300 | 310 | 300 | 315 | 310 | 300 | 310 | 300 | 300 | 315 | 290 | 305 | 310 |  | 310 | 310 | 280 | 290 | 285 | 280 | 295 | 7360250
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | [26 empty] | 0
59 | Sikalbaha Energies 55 MW
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 472992
61 | Narshingdi 22 MW PP (Doreen) | [11 empty] | 16 | 16 | 16 | 19 |  |  | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 |  | 209664
62 | Tangail 22 MW PP (Doreen) | 17 | [6 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 293616
63 | Impoprt (Tripura) | 78 | 78 | 76 | 74 | 74 | 70 | 68 | 74 | 76 | 76 | 84 | 84 | 92 | 88 | 82 | 88 | 88 | 106 |  | 104 | 106 | 102 | 104 | 96 | 88 | 82 | 2046720
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 40 | 35 | 33 | 40 | 33 | 9 | 3 | 2 | 2 | 2 | 5 | 5 | 2 | 2 | 12 | 10 |  | 23 | 26 | 30 | 32 | 35 | 40 | 38 | 538080
65 | Feni 22MW PP (Doreen) | [6 empty] | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 337932
66 | Feni 11 MW PP (Doreen) | [17 empty] | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 |  | 52740
67 | Jangalia 33MW PP (Summit) | 33 | [5 empty] | 23 | 23 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 633600
68 | Cumilla 25 MW PP (Summit) | 21 | 15 | 15 | 15 | 15 | 15 | 18 | 15 | 15 | 15 | 15 | 15 | 12 | 12 | 15 | 15 | 15 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 467240
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 28 | 28 | 28 | 20 | 28 | 28 | 31 | 31 | 31 | 31 | 31 | 18 | 31 | 23 | 24 | 18 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 678240
71 | Maona 33 MW PP(Summit) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 22 | 22 | 22 | 22 | 22 | 583700
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 24 |  | 24 | 24 | 24 | 24 | 24 | 30 | 32 | 770100
73 | Ghorashal 108MW PP (Regent) | 98 | 42 | 13 | 13 | 13 | 13 | 60 | 96 | 96 | 96 | 94 | 96 | 96 | 95 | 93 | 43 | 48 | 96 |  | 96 | 97 | 97 | 97 | 98 | 98 | 98 | 1762636
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | [7 empty] | 6 | 8 | 8 | 8 | 8 | 29 | 18 | 18 | 18 | 36 | 113 |  | 113 | 113 | 113 | 65 | 26 |  |  | 662760
| Manikgonj 162MW PP | 12 | 12 | 12 | 12 | 12 |  |  |  |  | 4 | 111 | 166 | 162 | 166 | 166 | 166 | 166 | 165 |  | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 2234880
77 | Siddhirganj 100 PP(Dutch Bangla) | [16 empty] | 11 | 25 |  | 60 | 30 | 40 |  |  |  |  | 147840
78 | Gazipur 52 MW PP
79 | Kodda 150MW PP | [16 empty] | 32 | 32 |  | 32 | 32 | 32 | 20 |  |  |  | 150240
80 | Jamalpur 95 MW PP(Powerpac) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 279360
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [8 empty] | 1 | 50 | 35 | 35 | 35 | 35 | 35 | 35 | 50 | 100 |  | 105 | 50 | 50 | 50 | 17 |  |  | 718620
| Kaptai 7 MW Solar PP | [6 empty] | 1 | 1 | 2 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 27240
| Jodiac Power | [7 empty] | 12 | 17 | 17 | 17 | 18 | 48 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 17 |  | 704532
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | [16 empty] | 4 | 15 |  | 15 | 15 | 15 | 15 |  |  |  | 78912
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP(Summit) | 130 | 130 | 135 | 130 | 135 | 145 | 140 | 145 | 140 | 140 | 145 | 142 | 140 | 145 | 130 | 143 | 140 | 146 |  | 135 | 135 | 135 | 140 | 125 | 135 | 130 | 3291258
87 | Meghnaghat 100 MW(IEL) | [16 empty] | 10 | 34 |  | 63 | 37 | 45 |  |  |  |  | 161280
| Meghnaghat 104 MW PP (OPCL) | [7 empty] | 14 | 35 | 86 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 |  | 89 | 89 | 89 | 89 | 89 | 72 | 26 | 1339200
88 | Ghorashal 78.5 MW PP(MAX) | 73 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 60 | 72 | 72 | 40 | 40 | 72 |  | 72 | 72 | 72 | 73 | 73 | 73 | 73 | 1255968
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [26 empty] | 0
92 | Fenchuganj 44MW (Energyprima) | 47 | 5 | 5 | 5 | 5 | 5 | 10 | 43 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 10 | 10 | 37 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 856728
93 | Ashuganj 51 MW PP (Midland) | 51 | 7 | 7 | 7 | 7 | 7 | 20 | 51 | 51 | 51 | 51 | 51 | 51 | 33 |  |  |  | 11 |  | 37 | 40 | 51 | 51 | 51 | 43 | 43 | 802797
94 | Gagnagar 102 MW PP (Digital Power) | [7 empty] | 7 | 7 | 7 | 50 | 60 | 84 | 74 | 74 | 74 | 74 | 84 |  | 102 | 94 | 68 | 50 |  |  |  | 849024
95 | Patenga 50MW PP (Baraka) | [7 empty] | 4 | 12 | 12 | 12 | 12 | 8 | 24 | 30 | 30 | 38 | 50 |  | 50 | 50 | 50 | 50 | 50 | 18 |  | 480960
96 | Chattogram 108 MW PP (ECPV) | [26 empty] | 0
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | [26 empty] | 0
100 | Manikganj 55 MW PP (Northern) | [9 empty] | 10 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 55 |  | 55 | 35 | 35 | 35 |  |  |  | 345329
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 110 | 110 | 163 | 163 | 120 | 163 | 163 | 110 | 163 | 163 | 110 | 110 | 110 | 110 | 130 |  | 163 | 163 | 163 | 163 | 163 | 163 | 130 | 3515236
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [10 empty] | 12500
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 |  |  | 10 | 17 | 35 | 35 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 35 | 17 | 923400
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [16 empty] | 5 | 32 |  | 32 | 32 | 32 | 32 | 32 |  |  | 184800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit)
115 | Juldah 100 MW PP Unit-3 (Acorn) | [7 empty] | 10 | 10 | 10 | 10 | 30 | 100 | 50 | 50 | 50 | 50 | 100 |  | 100 | 100 | 100 | 100 | 100 | 10 |  | 909120
116 | Chandpur 200MW (Desh energy) | [26 empty] | 0
117 | Ashuganj 150MW PP (Midland) | [7 empty] | 3 | 10 | 10 | 10 | 10 | 31 | 10 | 10 | 10 | 15 | 55 |  | 81 | 100 | 50 | 10 |  |  |  | 485091
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | [5 empty] | 2 | 8 | 24 | 53 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 115 |  | 115 | 115 | 115 | 115 | 115 | 24 |  | 1450800
| Anwara 300 MW PP (United) | [7 empty] | 16 | 16 | 16 | 16 | 16 | 100 | 16 | 16 | 16 | 65 | 100 |  | 123 | 123 | 123 | 89 | 35 |  |  | 780327
| Juldah unit-2 (Acorn) | 10 | 10 | 10 |  |  |  | 10 | 30 | 40 | 70 | 30 | 72 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 10 | 1447680
| Anlima Energy Ltd. | [26 empty] | 0
120 | Eastern Zone Total | 4052 | 3789 | 3716 | 3654 | 3675 | 3822 | 4043 | 4415 | 4565 | 4683 | 4671 | 4884 | 5082 | 4837 | 4833 | 4706 | 4948 | 5893 |  | 6071 | 5927 | 5759 | 5511 | 5162 | 4740 | 4441 | 108304666
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [16 empty] | 8 | 34 |  | 49 | 23 | [5 empty] | 85440
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [7 empty] | 17 | 17 | 17 | 17 | 17 | 53 | 35 | 35 | 17 | 53 | 70 |  | 90 | 90 | 90 | 90 | 35 |  |  | 688800
130
131
132 | United Payra Power Ltd. | [17 empty] | 56 |  | 65 | 17 | [5 empty] | 128400
133 | Bhola Nutan Biddut BD LTD (GAS) | [11 empty] | 36 | 35 | 36 | 5 | 11 | 8 | 3 |  | 1 | 21 | 17 | 22 | 36 | 36 | 36 | 339350
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [17 empty] | 16 |  | 16 |  | 48 | 32 |  |  |  | 124896
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 53 | 13 | 13 | 13 | 11 | 11 | 12 | 12 | 12 | 34 | 37 | 35 | 35 | 36 | 35 | 34 | 34 | 90 |  | 91 | 83 | 30 | 91 | 90 | 87 | 86 | 1010770
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 22 | 19 | 20 | 19 | 17 | 20 | 16 | 17 | 17 | 16 | 14 | 14 | 17 | 16 | 13 | 10 | 19 | 20 |  | 20 | 10 | 7 | 8 | 10 | 20 | 26 | 397600
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 498 | 498 | 497 | 404 | 404 | 404 | 404 | 404 | 404 | 404 | 679 | 689 | 690 | 690 | 690 | 690 | 683 | 508 |  | 508 | 610 | 803 | 873 | 873 | 777 | 592 | 14066182
147 | Bheramara 410 MW CCPP | 345 | 345 | 345 | 345 | 345 | 380 | 370 | 365 | 370 | 365 | 410 | 385 | 350 | 300 | 300 | 300 | 300 | 330 |  | 320 | 315 | 315 | 310 | 320 | 335 | 340 | 8308224
148 | Payra 1320 MW | 450 | 440 | 400 | 400 | 360 | 340 | 340 | 340 | 340 | 370 | 370 | 400 | 400 | 350 | 350 | 350 | 350 | 550 |  | 480 | 480 | 480 | 490 | 500 | 500 | 470 | 9855500
149
150 | Barapukuria TPP Unit-1 | 27
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 |  | 140 | 140 | 140 | 139 | 140 | 140 | 140 | 3438100
153 | Baghabari 71 MW GTPP | 70 | 50 | 50 | 50 | 50 | 50 | 70 | 70 | 70 | 70 | 65 | 40 | [14 empty] | 720000
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 157 | 150 | 130 | 130 | 130 | 130 | 130 | 152 | 167 | 161 | 163 | 185 | 196 | 164 | 170 | 159 | 171 | 176 |  | 185 | 177 | 176 | 165 | 151 | 146 | 145 | 4037000
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 160 | 130 | 130 | 130 | 130 | 154 | 191 | 191 | 203 | 201 | 185 | 186 | 214 | 195 | 200 | 188 | 196 | 199 |  | 199 | 195 | 190 | 179 | 161 | 160 | 159 | 4521464
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 330 | 345 | 335 | 310 | 275 | 300 | 343 | 375 | 433 | 435 | 375 | 392 | 389 | 376 | 377 | 376 | 374 | 422 |  | 435 | 432 | 410 | 335 | 295 | 335 | 387 | 8788500
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 10 | [5 empty] | 10 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 377040
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 180270
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [26 empty] | 0
172 | Confidence Power Bogura Unit-1 113 MW | [16 empty] | 35 | 95 |  | 113 | 113 | 70 | 35 |  |  |  | 414816
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 40 | 108 |  | 110 | 113 | 80 | 35 |  |  |  | 426240
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 3 | 4 | 4 | 5 | 4 | 3 | 3 | 2 | 0 | [9 empty] | 26452
178
178