## Forecast
q | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-11-29 | Sunday
|  |  | Date (day): | 2020-11-29 |  | Sunday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13120.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14246 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-11-28 | 2020-11-29 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1,2 Under maint
|  | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 115 | 115 | 115 | 75 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 200 | 200 |  | 165 | Machine problem
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 50 | 73 | 78 | 78
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 95 | 98 | 100 | 100
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 199 | 338 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 338 | 359 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 |  | 225 | GT-1 under maint.
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 45 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 150 | 140 | 150 | 150 |  | 155 | FGMO, GT-1 under maint.
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 15 | 40 | 100 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 50 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 19 | 19 | 19
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 50 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 58 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 32 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 37 | 57 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 21 | 21 | 21 |  | 12 | Engine problem
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 140 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 60 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 90 | 90 | 90 |  | 14 | Engine problem
|  | Manikgonj 162MW PP |  | HFO | IPP | 9*18 | 0 | 0 | 168 | 168 | 162 | 162
|  | Dhaka area Total |  |  |  |  | 6119 | 5895 | 1642 | 2487 | 3700 | 4040 | 498 | 1506
| 38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
| 40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
| 41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 45 | 50 | 50
| 42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 128 | 127 | 127 | 127 | 103 |  | Low water level
| 43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 219 | 203 | 215 | 225
| 44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 100 | 139 | 140 | 140
| 45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
| 46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
| 47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 34 | 102 | 102
| 48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 10 | 100 | 100 | 100
| 50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 20 | 20 | 20
| 51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 100 | 100
| 52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 141 | 300 | 300
| 54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 54 | 54 | 54
| 55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 10 | 100 | 100 | 100
|  | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 0 | 0 | 0 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2326 | 2266 | 548 | 983 | 1688 | 1673 | 463 | 98
| 57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 80 | 80 | 80 | 35 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 205 | 182 | 225 | 225 |  |  | FGMO
| 59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 370 | 280 | 360 | 360 |  |  | FGMO
| 60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
| 61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 29 | 30 | 30 | 15 |  | Gas shortage
| 62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 25 | 25 | 8 | 8 | 47 |  | Gas shortage
| 63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
| 65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 100 | 150 | 150
| 66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 48 | 80 | 90 | 90 |  | 57 | ST Under maint.
| 68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 200 | 0 | 200 | 200
| 69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 21 | 22 | 22
| 70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 68 | 90 | 125 | 145
| 71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
| 72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
| 73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 9 | 21 | 20 | 21
| 74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 113 | 113 | 113
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1085 | 1124 | 1692 | 1963 | 547 | 417
| 77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 142 | 125 | 120 | 150 | 52 |  | Gas shortage
| 78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 17 | 17 |  | 5 | Engine problem
| 79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 8 | 17 | 17 |  | 78 | Engine problem
| 80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 60 | 200 | 200
| 82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 70 | 115 | 115 | 115
|  | Mymensingh PV 50 MW Solar PP |  | Solar | IPP | 50 | 0 | 0 | 48 | 0 | 50 | 0
|  | Mymensingh Area Total |  |  |  |  | 645 | 637 | 287 | 325 | 520.6 | 499 | 52 | 83
| 83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 40 | 60 | 60 | 60
| 84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 60 | 60 | 60
| 85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
| 86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 267 | 254 | 260 | 260 |  | 70 | Machine problem
| 87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 45 | 53 | 51 | 51
| 88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 47 | 47 | 44 | 44
| 89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
| 90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 30 | 66 | 32 | 32 |  | 33 | GT-8 under maint.
| 91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 50 | 80 | 86 | 86
| 92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 90 | 130 | 150 | 150
| 93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 16 | 16 | 16 |  | 9 | Engine problem
| 96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 290 | 325 | 325 |  |  | FGMO
| 97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 143 | 398 | 400 | 400
| 98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 0 | 0 |  |  | 33 kV line maint.
|  | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
|  | Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1212 | 1628 | 1658 | 1658 | 0 | 112
| 99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 404 | 405 | 407 | 407
| 100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 115 | 115
| 101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30
| 102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
| 104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 410 | 245 | 410 | 410
| 105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
| 106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
| 107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 90 | 90 | 90 |  | 15 | Engine problem
| 108 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 814 | 740 | 1162 | 1588 | 0 | 15
| 109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 110 | 110
| 110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 14 | 27 | 27 | 27
| 111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maintenance
| 112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 14 | 94 | 95 | 95
| 113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 280 | 520 | 600 | 600
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 4 | 30 | 35 | 35
|  | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 0 | 0 | 0 | 0 | 0 | 0
|  | Barisal Area Total |  |  |  |  | 1054 | 1054 | 312 | 687 | 867 | 867 | 0 | 194
| 114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 50 | 0 | 0 | 0
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
| 116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
| 117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
| 119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
| 120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 120 | 150 | 140 | 150 |  | 75 | ST Under maint
| 121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 192 | 174 | 220 | 220 |  |  | FGMO
| 122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 141 | 141 |  |  | FGMO
| 123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 396 | 359 | 400 | 400 |  |  | FGMO
| 124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 33
| 125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
| 129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 8 | 0 | 100 | 100
| 130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 113 | 113
| 132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 796 | 829 | 1562 | 1695 | 200 | 75
| 133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint.
| 134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 140 | 140 | 150 | 150 | 124 |  | Coal Shortage.
| 135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
| 138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 145 | 253 | 271 | 263 | 294 | 40
|  | Total |  |  |  |  | 20383 | 19892 | 6841 | 9056 | 13120.6 | 14246 | 2054 | 2540
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6461.0284 | 8553 | 12391.8388 | 13454.7303
| A. |  | 2020-11-28 | (Yesterday) |  |  |  |  | Saturday
| 1 | Highest Generation : |  |  | 9056 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 5330 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9056 | MW
| 3 | Day peak Generation : |  |  | 6841 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8553 | MW
| 4 | Evening peak Generation : |  |  | 9056 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 160.2633 | MKWHr | By Solar | 0.4852 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 113.4592 | MKWHr |  | By Oil: | 20.2854 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 11.575 | MKWHr |  | By Hydro: | 2.9799 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2054 | MW | Dhaka | 3168 | 3168 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2540 | MW | Chittagong | 1008 | 1008 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4594 | MW | Khulna | 1036 | 1036 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 995.67 | MMCFD |  |  | Rajshahi | 835 | 835 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 129202719.51 | ii) Oil : | Taka | 105058576.34 | Comilla | 726 | 726 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : | Taka | 54367338 | Total | Taka | 288628633.85 | Mymensingh | 667 | 667 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 1.1 | MKWHr. | Sylhet | 322 | 322 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -330 | MW (E to W) at | 19:00 | hrs | Barisal | 236 | 236 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -360 | MW at | 20:00 | hrs | Rangpur | 555 | 555 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 29.8° C |  |  | Total | 8553 | 8553 |  | 0
| B. |  | 2020-11-29 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 30° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14246 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 7500 | MW
| 4 | Reserve(Generation end) |  |  |  | 5046 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 162.8117 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5683 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 9.6305 | MKWHr. | ii) HVDC Flow at Peak Time |  | 405 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.848 | MKWHr. | iii) Maximum HVDC Flow : |  | 405 | MW at | 13:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 100.91 |  | (b) Today: | 100.73 |  | (c) Rule Curve: |  | 106.3
.

## YesterdayGen
2020-11-28
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha Energies 55 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Mymensingh PV 50 MW Solar PP | Manikgonj 162MW PP | Anlima Energy Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 115 | 200 | 12 | 0 | 227 | 309 |  | 0 | 225 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 32 | 22 | 33 | 0 | 0 | 87 | 35 | 0 | 0 | 0 | 203 | 0 | 119 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 80 | 0 | 0 | 260 | 0 | 180 | 8 | 81 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 74 | 163 | 8 | 0 | 0 | 60 | 60 | 0 | 3 | 130 | 253 | 20 | 5 | 0 | 129 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 |  | 389 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 120 | 0 | 130 | 0 | 14 | 0 | 51 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 22 | 0 | 0 |  | 3886 | 2005 | 5891 | 3062 | 389 | 1420 | 334 | 490 | 122 | 0 | 74 | 0 | 0 | 100.93
2:00 | 0 | 0 | 0 | 115 | 200 | 12 | 0 | 227 | 258 |  | 0 | 225 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 32 | 22 | 33 | 0 | 0 | 87 | 35 | 0 | 0 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 80 | 0 | 0 | 260 | 0 | 181 | 8 | 82 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 72 | 110 | 8 | 0 | 0 | 60 | 60 | 0 | 3 | 110 | 258 | 20 | 5 | 0 | 120 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 |  | 399 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 110 | 0 | 130 | 0 | 12 | 0 | 20 | 0 | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 18 | 0 | 0 |  | 3744 | 1825 | 5569 | 2951 | 399 | 1299 | 336 | 390 | 122 | 0 | 72 | 0 | 0 | 100.93
3:00 | 0 | 0 | 0 | 115 | 200 | 12 | 0 | 227 | 258 |  | 0 | 225 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 24 | 22 | 33 | 0 | 0 | 86 | 35 | 0 | 0 | 0 | 203 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 80 | 0 | 0 | 260 | 0 | 181 | 8 | 81 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 70 | 110 | 0 | 0 | 0 | 60 | 60 | 0 | 3 | 110 | 257 | 20 | 5 | 0 | 80 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 |  | 399 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 75 | 0 | 130 | 0 | 12 | 0 | 20 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 23 | 0 | 0 |  | 3650 | 1826 | 5476 | 2828 | 399 | 1345 | 323 | 390 | 121 | 0 | 70 | 0 | 0 | 100.92
4:00 | 0 | 0 | 0 | 115 | 200 | 12 | 0 | 182 | 259 |  | 0 | 225 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 24 | 20 | 33 | 0 | 0 | 86 | 35 | 0 | 0 | 0 | 203 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 80 | 0 | 0 | 260 | 0 | 181 | 8 | 85 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 68 | 109 | 0 | 0 | 0 | 60 | 60 | 0 | 3 | 110 | 258 | 20 | 5 | 0 | 80 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 |  | 399 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 70 | 0 | 130 | 0 | 12 | 0 | 20 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 18 | 0 | 0 |  | 3599 | 1776 | 5375 | 2778 | 399 | 1296 | 323 | 390 | 121 | 0 | 68 | 0 | 0 | 100.92
5:00 | 0 | 0 | 0 | 115 | 200 | 12 | 0 | 148 | 260 |  | 0 | 225 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 22 | 33 | 0 | 0 | 86 | 35 | 0 | 0 | 0 | 208 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 80 | 0 | 0 | 270 | 0 | 192 | 8 | 85 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 68 | 109 | 0 | 0 | 0 | 30 | 60 | 0 | 3 | 110 | 259 | 20 | 5 | 0 | 80 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 |  | 399 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 70 | 0 | 130 | 0 | 12 | 0 | 20 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 22 | 0 | 0 |  | 3565 | 1765 | 5330 | 2686 | 399 | 1350 | 316 | 390 | 121 | 0 | 68 | 0 | 0 | 100.91
6:00 | 0 | 0 | 0 | 115 | 200 | 12 | 0 | 136 | 259 |  | 0 | 225 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 17 | 33 | 0 | 0 | 91 | 35 | 0 | 0 | 0 | 205 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 80 | 0 | 0 | 285 | 0 | 200 | 8 | 92 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 64 | 109 | 0 | 0 | 0 | 30 | 60 | 0 | 3 | 130 | 261 | 32 | 5 | 0 | 80 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 |  | 399 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 85 | 0 | 130 | 0 | 12 | 0 | 57 | 0 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 23 | 0 | 0 |  | 3627 | 1822 | 5449 | 2763 | 399 | 1401 | 306 | 390 | 126 | 0 | 64 | 0 | 0 | 100.91
7:00 | 0 | 0 | 0 | 115 | 200 | 28 | 0 | 136 | 259 |  | 0 | 225 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 25 | 19 | 17 | 33 | 0 | 0 | 91 | 35 | 0 | 0 | 0 | 213 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 0 | 0 | 320 | 0 | 197 | 8 | 84 | 23 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 70 | 109 | 2 | 0 | 0 | 30 | 60 | 0 | 3 | 163 | 257 | 32 | 5 | 0 | 80 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 40 | 0 | 79 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 2 | 166 | 0 |  | 399 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 144 | 0 | 190 | 0 | 12 | 0 | 70 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 23 | 0 | 0 |  | 3827 | 2017 | 5844 | 3001 | 399 | 1472 | 381 | 390 | 126 | 0 | 70 | 5 | 0 | 100.9
8:00 | 0 | 0 | 0 | 115 | 200 | 98 | 0 | 104 | 309 |  | 0 | 225 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 28 | 22 | 33 | 0 | 0 | 92 | 35 | 0 | 0 | 0 | 203 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 9 | 80 | 0 | 0 | 310 | 0 | 181 | 8 | 84 | 27 | 25 | 0 | 45 | 0 | 0 | 0 | 16 | 0 | 0 | 15 | 72 | 167 | 8 | 20 | 0 | 30 | 60 | 44 | 14 | 163 | 258 | 32 | 40 | 0 | 80 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 10 | 180 | 0 | 80 | 8 | 0 | 0 | 2 | 0 | 11 | 0 | 0 | 0 | 10 | 0 | 13 | 14 | 167 | 0 |  | 400 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 150 | 0 | 183 | 0 | 12 | 0 | 70 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 250 | 12 | 0 | 0 |  | 4325 | 1990 | 6315 | 3059 | 400 | 1668 | 574 | 390 | 127 | 0 | 72 | 25 | 0 | 100.9
9:00 | 0 | 0 | 0 | 115 | 200 | 95 | 30 | 22 | 309 |  | 0 | 225 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 18 | 17 | 17 | 0 | 0 | 92 | 35 | 0 | 0 | 0 | 216 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 4 | 18 | 3 | 80 | 0 | 0 | 330 | 0 | 201 | 8 | 50 | 22 | 25 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 62 | 164 | 8 | 20 | 1 | 30 | 60 | 48 | 47 | 110 | 260 | 32 | 40 | 0 | 80 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 10 | 200 | 8 | 90 | 8 | 0 | 0 | 2 | 0 | 17 | 0 | 0 | 0 | 10 | 0 | 40 | 17 | 166 | 0 |  | 404 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 150 | 0 | 189 | 0 | 12 | 0 | 70 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 250 | 7 | 0 | 0 |  | 4297 | 2030 | 6327 | 2983 | 404 | 1688 | 638 | 390 | 127 | 0 | 62 | 35 | 0 | 100.89
10:00 | 0 | 0 | 0 | 115 | 200 | 95 | 30 | 38 | 309 |  | 0 | 225 | 150 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 17 | 17 | 0 | 0 | 93 | 35 | 0 | 0 | 0 | 207 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 3 | 80 | 0 | 0 | 315 | 0 | 192 | 8 | 45 | 25 | 25 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 68 | 161 | 8 | 17 | 2 | 30 | 60 | 47 | 47 | 130 | 252 | 32 | 40 | 0 | 80 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 200 | 10 | 80 | 33 | 0 | 0 | 4 | 0 | 17 | 0 | 0 | 0 | 10 | 0 | 17 | 35 | 166 | 0 |  | 404 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 150 | 0 | 186 | 0 | 13 | 0 | 70 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 250 | 26 | 0 | 0 |  | 4290 | 2031 | 6321 | 2906 | 404 | 1740 | 623 | 390 | 128 | 0 | 68 | 62 | 0 | 100.89
11:00 | 0 | 0 | 0 | 115 | 200 | 95 | 30 | 121 | 309 |  | 0 | 225 | 150 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 25 | 17 | 0 | 0 | 93 | 35 | 0 | 0 | 0 | 204 | 0 | 70 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 3 | 80 | 0 | 0 | 325 | 0 | 194 | 8 | 44 | 28 | 25 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 74 | 144 | 8 | 17 | 2 | 30 | 60 | 47 | 47 | 130 | 258 | 31 | 40 | 0 | 80 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 200 | 0 | 80 | 55 | 0 | 0 | 4 | 0 | 17 | 0 | 0 | 0 | 10 | 0 | 17 | 54 | 169 | 0 |  | 404 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 50 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 120 | 0 | 179 | 0 | 13 | 0 | 70 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 250 | 21 | 0 | 0 |  | 4440 | 2005 | 6445 | 2971 | 404 | 1717 | 651 | 390 | 128 | 26 | 74 | 84 | 0 | 100.88
12:00 | 0 | 0 | 0 | 115 | 200 | 95 | 50 | 199 | 338 |  | 0 | 225 | 150 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 25 | 0 | 0 | 0 | 93 | 35 | 0 | 0 | 0 | 219 | 0 | 100 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 3 | 80 | 0 | 0 | 370 | 0 | 205 | 8 | 48 | 29 | 25 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 68 | 142 | 8 | 17 | 2 | 40 | 60 | 45 | 47 | 130 | 267 | 30 | 50 | 0 | 90 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 200 | 0 | 143 | 70 | 0 | 0 | 5 | 0 | 17 | 0 | 0 | 0 | 10 | 0 | 17 | 48 | 168 | 0 |  | 404 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 50 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 120 | 0 | 192 | 0 | 14 | 0 | 0 | 0 | 396 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 280 | 4 | 0 | 0 |  | 4774 | 2067 | 6841 | 3225 | 404 | 1819 | 673 | 420 | 128 | 25 | 68 | 79 | 0 | #REF!
13:00 | 0 | 0 | 0 | 115 | 200 | 95 | 70 | 265 | 339 |  | 0 | 225 | 130 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 10 | 25 | 0 | 0 | 0 | 92 | 35 | 0 | 0 | 0 | 204 | 0 | 100 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 4 | 80 | 0 | 0 | 310 | 0 | 183 | 8 | 45 | 29 | 25 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 68 | 117 | 8 | 17 | 2 | 60 | 60 | 50 | 47 | 163 | 250 | 31 | 80 | 0 | 120 | 0 | 0 | 0 | 305 | 15 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 10 | 200 | 1 | 312 | 85 | 0 | 0 | 4 | 0 | 17 | 0 | 0 | 0 | 10 | 0 | 45 | 46 | 165 | 15 |  | 405 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 40 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 120 | 0 | 194 | 0 | 34 | 0 | 0 | 0 | 354 | 17 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 300 | 4 | 0 | 0 |  | 5094 | 2038 | 7132 | 3366 | 405 | 1884 | 747 | 440 | 127 | 21 | 68 | 74 | 7132 | 100.87
14:00 | 0 | 0 | 0 | 115 | 200 | 99 | 40 | 337 | 288 |  | 0 | 225 | 145 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 7 | 25 | 0 | 0 | 0 | 90 | 35 | 0 | 0 | 0 | 203 | 0 | 100 | 0 |  | 0 | 0 | 15 | 0 | 0 | 0 | 20 | 3 | 80 | 0 | 0 | 260 | 0 | 182 | 8 | 44 | 29 | 25 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 80 | 103 | 8 | 17 | 2 | 60 | 60 | 50 | 47 | 110 | 260 | 20 | 80 | 0 | 120 | 0 | 0 | 0 | 270 | 15 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 200 | 10 | 351 | 85 | 0 | 0 | 3 | 0 | 17 | 0 | 0 | 0 | 10 | 0 | 54 | 36 | 166 | 12 |  | 404 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 139 | 0 | 0 | 80 | 0 | 160 | 0 | 34 | 0 | 0 | 0 | 337 | 17 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 300 | 1 | 0 | 0 |  | 5007 | 1871 | 6878 | 3257 | 404 | 1699 | 788 | 439 | 125 | 23 | 80 | 63 | 0 | 100.87
15:00 | 0 | 0 | 0 | 115 | 200 | 95 | 40 | 346 | 288 |  | 0 | 225 | 150 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 7 | 8 | 8 | 0 | 0 | 90 | 35 | 0 | 0 | 0 | 215 | 0 | 100 | 0 |  | 0 | 0 | 15 | 0 | 0 | 0 | 20 | 2 | 80 | 0 | 0 | 285 | 0 | 201 | 8 | 50 | 26 | 25 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 76 | 102 | 8 | 17 | 1 | 60 | 60 | 49 | 47 | 110 | 264 | 40 | 79 | 0 | 120 | 0 | 0 | 0 | 300 | 15 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 10 | 50 | 10 | 351 | 85 | 0 | 0 | 3 | 0 | 17 | 0 | 0 | 0 | 10 | 0 | 54 | 24 | 166 | 0 |  | 405 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 80 | 0 | 164 | 0 | 34 | 0 | 0 | 0 | 361 | 17 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 300 | 30 | 0 | 0 |  | 4949 | 1921 | 6870 | 3343 | 405 | 1784 | 631 | 440 | 125 | 24 | 76 | 42 | 0 | 100.86
16:00 | 0 | 0 | 0 | 115 | 200 | 43 | 40 | 367 | 288 |  | 0 | 225 | 150 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 12 | 16 | 11 | 0 | 0 | 90 | 35 | 0 | 0 | 0 | 216 | 0 | 100 | 0 |  | 0 | 0 | 15 | 0 | 0 | 0 | 20 | 4 | 80 | 0 | 0 | 295 | 0 | 204 | 8 | 50 | 26 | 25 | 0 | 51 | 0 | 0 | 0 | 5 | 0 | 20 | 19 | 74 | 122 | 8 | 17 | 0 | 60 | 60 | 52 | 47 | 110 | 265 | 40 | 20 | 0 | 120 | 0 | 0 | 0 | 315 | 15 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 10 | 0 | 13 | 352 | 85 | 0 | 0 | 1 | 16 | 17 | 0 | 0 | 0 | 25 | 0 | 53 | 9 | 168 | 0 |  | 404 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 80 | 0 | 174 | 0 | 34 | 0 | 0 | 0 | 360 | 17 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 300 | 14 | 0 | 0 |  | 4913 | 1888 | 6801 | 3433 | 404 | 1675 | 616 | 440 | 125 | 15 | 74 | 19 | 0 | 100.86
17:00 | 0 | 0 | 0 | 115 | 200 | 43 | 40 | 348 | 288 |  | 0 | 225 | 140 | 12 | 30 | 0 | 0 | 0 | 39 | 14 | 24 | 32 | 0 | 0 | 0 | 0 | 22 | 35 | 0 | 19 | 25 | 12 | 16 | 12 | 0 | 0 | 90 | 35 | 0 | 0 | 0 | 203 | 0 | 70 | 0 |  | 0 | 0 | 49 | 0 | 0 | 9 | 20 | 9 | 80 | 0 | 0 | 260 | 0 | 182 | 8 | 46 | 26 | 25 | 0 | 51 | 0 | 0 | 0 | 20 | 8 | 33 | 16 | 90 | 125 | 8 | 17 | 0 | 60 | 60 | 53 | 47 | 110 | 254 | 40 | 20 | 0 | 120 | 0 | 0 | 0 | 300 | 15 | 5 | 0 | 42 | 0 | 0 | 3 | 0 | 0 | 0 | 50 | 0 | 35 | 351 | 105 | 41 | 0 | 0 | 50 | 17 | 0 | 0 | 26 | 60 | 0 | 53 | 1 | 168 | 0 |  | 404 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 5 | 0 | 80 | 0 | 165 | 0 | 34 | 0 | 0 | 0 | 325 | 17 | 0 | 0 | 0 | 35 | 0 | 0 | 25 | 300 | 2 | 0 | 0 |  | 5257 | 1884 | 7141 | 3350 | 404 | 1617 | 1028 | 440 | 125 | 86 | 90 | 1 | 0 | 100.85
18:00 | 0 | 0 | 0 | 115 | 200 | 98 | 60 | 368 | 356 |  | 0 | 225 | 150 | 25 | 30 | 0 | 0 | 0 | 37 | 25 | 40 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 32 | 25 | 21 | 0 | 0 | 92 | 35 | 0 | 0 | 0 | 209 | 0 | 139 | 0 |  | 0 | 0 | 34 | 0 | 0 | 26 | 20 | 12 | 80 | 0 | 0 | 315 | 0 | 198 | 8 | 72 | 29 | 25 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 98 | 124 | 8 | 17 | 0 | 60 | 60 | 53 | 47 | 163 | 258 | 67 | 79 | 0 | 130 | 0 | 0 | 0 | 315 | 16 | 8 | 0 | 95 | 0 | 0 | 26 | 0 | 0 | 0 | 100 | 0 | 60 | 400 | 115 | 105 | 0 | 0 | 118 | 52 | 0 | 0 | 87 | 100 | 0 | 78 | 0 | 169 | 0 |  | 404 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 115 | 0 | 181 | 0 | 94 | 0 | 0 | 0 | 422 | 70 | 0 | 0 | 0 | 108 | 0 | 0 | 90 | 450 | 30 | 0 | 0 |  | 6431 | 2460 | 8891 | 3717 | 404 | 2087 | 1802 | 590 | 127 | 66 | 98 | 0 | 0 | 100.85
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 115 | 200 | 98 | 73 | 338 | 359 |  | 0 | 225 | 140 | 45 | 40 | 0 | 0 | 0 | 0 | 50 | 58 | 32 | 0 | 0 | 0 | 0 | 54 | 35 | 0 | 19 | 25 | 32 | 25 | 21 | 0 | 0 | 92 | 35 | 0 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 34 | 0 | 0 | 45 | 20 | 20 | 80 | 0 | 0 | 280 | 0 | 182 | 8 | 80 | 29 | 25 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 90 | 125 | 8 | 17 | 0 | 60 | 60 | 53 | 47 | 163 | 254 | 66 | 80 | 0 | 130 | 0 | 0 | 0 | 290 | 16 | 11 | 0 | 140 | 0 | 0 | 60 | 0 | 0 | 0 | 100 | 0 | 100 | 398 | 115 | 105 | 0 | 0 | 141 | 54 | 0 | 0 | 113 | 100 | 0 | 90 | 0 | 168 | 0 |  | 405 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 150 | 0 | 174 | 0 | 94 | 0 | 0 | 0 | 359 | 90 | 0 | 0 | 0 | 113 | 0 | 0 | 113 | 520 | 30 | 0 | 0 |  | 6547 | 2509 | 9056 | 3591 | 405 | 2024 | 2093 | 660 | 127 | 66 | 90 | 0 | 0 | 100.82
19:30 | 0 | 0 | 0 | 115 | 200 | 98 | 73 | 336 | 359 |  | 0 | 225 | 140 | 25 | 15 | 0 | 0 | 0 | 0 | 24 | 58 | 32 | 0 | 0 | 0 | 0 | 54 | 35 | 0 | 19 | 25 | 32 | 25 | 21 | 0 | 0 | 92 | 35 | 0 | 0 | 0 | 203 | 0 | 130 | 0 |  | 0 | 0 | 34 | 0 | 0 | 50 | 20 | 15 | 100 | 0 | 0 | 285 | 0 | 183 | 8 | 78 | 26 | 25 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 94 | 126 | 8 | 17 | 0 | 60 | 60 | 53 | 47 | 163 | 252 | 66 | 80 | 0 | 120 | 0 | 0 | 0 | 300 | 16 | 11 | 0 | 95 | 0 | 0 | 60 | 0 | 0 | 0 | 100 | 0 | 100 | 398 | 115 | 88 | 0 | 0 | 141 | 54 | 0 | 0 | 113 | 100 | 0 | 90 | 0 | 168 | 0 |  | 405 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 150 | 0 | 154 | 0 | 94 | 0 | 0 | 0 | 387 | 90 | 0 | 0 | 0 | 113 | 0 | 0 | 113 | 520 | 30 | 0 | 0 |  | 6427 | 2518 | 8945 | 3570 | 405 | 2058 | 1965 | 660 | 127 | 66 | 94 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 115 | 200 | 98 | 74 | 335 | 359 |  | 0 | 225 | 130 | 28 | 15 | 0 | 0 | 0 | 0 | 30 | 58 | 32 | 0 | 0 | 0 | 0 | 54 | 35 | 0 | 19 | 25 | 32 | 25 | 21 | 0 | 0 | 92 | 35 | 0 | 0 | 0 | 203 | 0 | 130 | 0 |  | 0 | 0 | 34 | 0 | 0 | 50 | 20 | 15 | 100 | 0 | 0 | 280 | 0 | 182 | 8 | 78 | 29 | 25 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 94 | 125 | 8 | 17 | 0 | 60 | 60 | 53 | 47 | 163 | 257 | 67 | 80 | 0 | 120 | 0 | 0 | 0 | 280 | 16 | 11 | 0 | 95 | 0 | 0 | 60 | 0 | 0 | 0 | 100 | 0 | 100 | 398 | 115 | 70 | 0 | 0 | 141 | 54 | 0 | 0 | 113 | 100 | 0 | 90 | 0 | 168 | 0 |  | 405 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 150 | 0 | 152 | 0 | 93 | 0 | 0 | 0 | 359 | 90 | 0 | 0 | 0 | 113 | 0 | 0 | 113 | 520 | 2 | 0 | 0 |  | 6390 | 2454 | 8844 | 3564 | 405 | 1982 | 1946 | 660 | 127 | 66 | 94 | 0 | 0 | 100.83
21:00 | 0 | 0 | 0 | 115 | 200 | 98 | 74 | 335 | 358 |  | 0 | 225 | 140 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 24 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 32 | 25 | 21 | 0 | 0 | 92 | 35 | 0 | 0 | 0 | 203 | 0 | 129 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 20 | 100 | 0 | 0 | 280 | 0 | 182 | 8 | 78 | 29 | 25 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 90 | 126 | 16 | 17 | 0 | 60 | 60 | 53 | 47 | 163 | 256 | 66 | 80 | 0 | 120 | 0 | 0 | 0 | 290 | 16 | 11 | 0 | 14 | 0 | 0 | 60 | 0 | 0 | 0 | 100 | 0 | 100 | 398 | 115 | 34 | 0 | 0 | 141 | 54 | 0 | 0 | 113 | 100 | 0 | 90 | 0 | 168 | 0 |  | 405 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 150 | 0 | 153 | 0 | 95 | 0 | 0 | 0 | 379 | 90 | 0 | 0 | 0 | 70 | 0 | 0 | 70 | 520 | 2 | 0 | 0 |  | 6139 | 2381 | 8520 | 3553 | 405 | 2018 | 1651 | 660 | 127 | 16 | 90 | 0 | 0 | #REF!
22:00 | 0 | 0 | 0 | 115 | 200 | 98 | 75 | 335 | 358 |  | 0 | 225 | 136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 32 | 25 | 21 | 0 | 0 | 92 | 35 | 0 | 0 | 0 | 203 | 0 | 129 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 30 | 80 | 0 | 0 | 280 | 0 | 156 | 8 | 78 | 29 | 25 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 82 | 121 | 8 | 17 | 0 | 60 | 60 | 53 | 47 | 163 | 256 | 67 | 77 | 0 | 120 | 0 | 0 | 0 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 10 | 400 | 115 | 17 | 0 | 0 | 107 | 54 | 0 | 0 | 26 | 100 | 0 | 90 | 0 | 168 | 0 |  | 405 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 150 | 0 | 157 | 0 | 95 | 0 | 0 | 0 | 351 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 29 | 0 | 0 |  | 5715 | 2207 | 7922 | 3509 | 405 | 2024 | 1105 | 660 | 127 | 10 | 82 | 0 | 0 | 100.82
23:00 | 0 | 0 | 0 | 115 | 200 | 98 | 75 | 335 | 303 |  | 0 | 225 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 32 | 25 | 21 | 0 | 0 | 93 | 35 | 0 | 0 | 0 | 203 | 0 | 129 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 20 | 32 | 80 | 0 | 0 | 280 | 0 | 152 | 8 | 78 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 76 | 123 | 8 | 17 | 0 | 60 | 60 | 53 | 47 | 130 | 255 | 66 | 79 | 0 | 120 | 0 | 0 | 0 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 398 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 100 | 0 | 90 | 0 | 168 | 0 |  | 405 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 150 | 0 | 157 | 0 | 95 | 0 | 0 | 0 | 369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 35 | 0 | 0 |  | 5183 | 2140 | 7323 | 3503 | 405 | 1933 | 638 | 640 | 128 | 0 | 76 | 0 | 0 | 100.8
24:00 | 0 | 0 | 0 | 115 | 200 | 98 | 75 | 337 | 292 |  | 0 | 225 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 32 | 17 | 21 | 0 | 0 | 91 | 35 | 0 | 0 | 0 | 203 | 0 | 129 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 35 | 80 | 0 | 0 | 280 | 0 | 175 | 8 | 78 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 74 | 129 | 8 | 17 | 0 | 60 | 60 | 53 | 47 | 130 | 250 | 40 | 79 | 0 | 120 | 0 | 0 | 0 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 50 | 0 | 168 | 0 |  | 405 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 150 | 0 | 159 | 0 | 13 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 35 | 0 | 0 |  | 4936 | 1968 | 6904 | 3474 | 405 | 1799 | 426 | 600 | 126 | 0 | 74 | 0 | 0 | 100.79
KWH | 0 | 0 | 0 | 2772000 | 4795773 | 1634045 | 932960 | 594951 | 7261000 |  | 0 | 4805500 | 3455185 | 121920 | 313656 | 0 | 0 | 0 | 64000 | 134400 | 324720 | 142560 | 0 | 0 | 0 | 0 | 483840 | 169495 | 0 | 208656 | 600000 | 507060 | 489600 | 508100 | 0 | 0 | 2131910 | 848000 | 0 | 0 | 0 | 4897122 | 0 | 2345602 | 0 |  | 0 | 0 | 215689 | 0 | 0 | 278880 | 349248 | 438240 | 2006858 | 0 | 0 | 7274100 | 0 | 4532000 | 217454 | 1619200 | 492480 | 458880 | 0 | 927779 | 0 | 0 | 0 | 182268 | 81900 | 272400 | 452810 | 1848000 | 2933400 | 172800 | 272340 | 12650 | 1201000 | 1434360 | 823800 | 799200 | 3391036 | 5873000 | 994832 | 1126080 | 0 | 2535440 | 0 | 0 | 0 | 7303000 | 27266 | 102000 | 0 | 396436 | 0 | 0 | 244800 | 0 | 0 | 131085 | 720000 | 1743840 | 575418 | 5368000 | 1288800 | 406680 | 0 | 27240 | 697527 | 521696 | 0 | 0 | 558600 | 818880 | 0 | 983040 | 282630 | 3964320 | 26345 |  | 9630545 | 0 | 7744896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451500 | 69888 | 0 | 0 | 585000 | 0 | 0 | 29136 | 0 | 0 | 0 | 0 | 0 | 514080 | 0 | 211770 | 0 | 0 | 3449600 | 3000 | 0 | 3057300 | 0 | 4115836 | 0 | 940307 | 0 | 775100 | 0 | 8610363 | 510720 | 0 | 0 | 0 | 463680 | 0 | 31600 | 447072 | 8125400 | 546350 | 0 | 2400 |  | 109947782 | 50315543 | 160263325 | 72277668 | 9630545 | 41181574 | 19895038 | 11575000 | 2979910 | 390385 | 1848000 | 485205 | 0
Fuel Cost | 0 | 0 | 0 | 4074840 | 5323308.03 | 2156939.4 | 1586032 | 600900.51 | 7478830 |  | 0 | 5237995 | 3835255.35 | 925372.8 | 2161089.84 | 0 | 0 | 0 | 110720 | 1012032 | 2961446.4 | 1402790.4 | 0 | 0 | 0 | 0 | 3532032 | 1310196.35 | 0 | 156492 | 450000 | 0 | 0 | 0 | 0 | 0 | 575615.7 | 228960 | 0 | 0 | 0 | 5337862.98 | 0 | 3987523.4 | 0 |  | 0 | 0 | 2092183.3 | 0 | 0 | 2208729.6 | 440052.48 | 1301572.8 | 2970149.84 | 0 | 0 | 5382834 | 0 | 4169440 | 280515.66 | 1862080 | 556502.4 | 642432 | 0 | 1586502.09 | 0 | 0 | 0 | 231480.36 | 61425 | 476700 | 339607.5 | 13860000 | 3109404 | 1569024 | 345871.8 | 201641 | 1969640 | 2294976 | 1466364 | 1246752 | 3865781.04 | 6107920 | 1959819.04 | 2150812.8 | 0 | 4386311.2 | 0 | 0 | 0 | 7376030 | 20449.5 | 77520 | 0 | 2997056.16 | 0 | 0 | 1272960 | 0 | 0 | 1532383.65 | 5868000 | 18920664 | 4056696.9 | 4992240 | 11753856 | 3843126 | 0 | 0 | 5273304.12 | 4543972.16 | 0 | 0 | 4787202 | 5453740.8 | 0 | 0 | 0 | 0 | 0 |  | 55471939.2 | 0 | 8132140.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 699825 | 682106.88 | 0 | 0 | 1199250 | 0 | 0 | 257853.6 | 0 | 0 | 0 | 0 | 0 | 987033.6 | 0 | 160309.89 | 0 | 0 | 18696832 | 103950 | 0 | 3577041 | 0 | 5432903.52 | 0 | 1410460.5 | 0 | 906867 | 0 | 8524259.37 | 5331916.8 | 0 | 0 | 0 | 3598156.8 | 0 | 349180 | 3303862.08 | 35670506 | 0 | 0 | 0 |  | 206351959.36 | 154496394.04 | 360848353.4 | 81204582.25 | 55471939.2 | 47998137.26 | 101201799.04 | 54367338 | 804575.7 | 3856777.3 | 13860000 | 2083204.65 | 0
Yesterday Day Peak | 0 | 0 | 0 | 115 | 200 | 95 | 50 | 199 | 338 |  | 0 | 225 | 150 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 25 | 0 | 0 | 0 | 93 | 35 | 0 | 0 | 0 | 219 | 0 | 100 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 3 | 80 | 0 | 0 | 370 | 0 | 205 | 8 | 48 | 29 | 25 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 68 | 142 | 8 | 17 | 2 | 40 | 60 | 45 | 47 | 130 | 267 | 30 | 50 | 0 | 90 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 200 | 0 | 143 | 70 | 0 | 0 | 5 | 0 | 17 | 0 | 0 | 0 | 10 | 0 | 17 | 48 | 168 | 0 |  | 404 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 50 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 120 | 0 | 192 | 0 | 14 | 0 | 0 | 0 | 396 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 280 | 4 | 0 | 0 |  | 6841 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 115 | 200 | 98 | 73 | 338 | 359 | 0 | 0 | 225 | 140 | 45 | 40 | 0 | 0 | 0 | 0 | 50 | 58 | 32 | 0 | 0 | 0 | 0 | 54 | 35 | 0 | 19 | 25 | 32 | 25 | 21 | 0 | 0 | 92 | 35 | 0 | 0 | 0 | 203 | 0 | 139 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 45 | 20 | 20 | 80 | 0 | 0 | 280 | 0 | 182 | 8 | 80 | 29 | 25 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 90 | 125 | 8 | 17 | 0 | 60 | 60 | 53 | 47 | 163 | 254 | 66 | 80 | 0 | 130 | 0 | 0 | 0 | 290 | 16 | 11 | 0 | 140 | 0 | 0 | 60 | 0 | 0 | 0 | 100 | 0 | 100 | 398 | 115 | 105 | 0 | 0 | 141 | 54 | 0 | 0 | 113 | 100 | 0 | 90 | 0 | 168 | 0 |  | 405 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 140 | 0 | 0 | 150 | 0 | 174 | 0 | 94 | 0 | 0 | 0 | 359 | 90 | 0 | 0 | 0 | 113 | 0 | 0 | 113 | 520 | 30 | 0 | 0 |  | 9056 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 115 | 200 | 100 | 78 | 412 | 360 | 0 | 0 | 225 | 150 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 100 | 0 | 0 | 50 | 54 | 55 | 55 | 19 | 25 | 33 | 25 | 21 | 52 | 0 | 92 | 35 | 0 | 0 | 25 | 225 | 0 | 140 | 0 | 0 | 0 |  | 102 | 100 | 100 | 50 | 20 | 20 | 80 | 0 | 0 | 360 | 0 | 225 | 8 | 90 | 30 | 8 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 145 | 150 | 17 | 17 | 0 | 60 | 60 | 51 | 44 | 163 | 260 | 32 | 86 | 0 | 150 | 0 | 0 | 0 | 325 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 90 | 0 | 162 |  |  | 407 | 16 | 410 | 0 | 115 | 220 | 0 | 0 | 30 | 60 | 40 | 0 | 27 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 0 | 0 | 50 | 52 | 33 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 150 | 0 | 220 | 0 | 95 | 100 | 141 | 0 | 400 | 90 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 600 | 35
Forecast for Day | 0 | 0 | 0 | 115 | 200 | 100 | 78 | 412 | 360 | 0 | 0 | 225 | 150 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 150 | 50 | 0 | 0 | 50 | 54 | 55 | 55 | 19 | 25 | 33 | 25 | 21 | 52 | 0 | 92 | 35 | 0 | 0 | 25 | 215 | 0 | 140 | 0 | 0 | 0 |  | 102 | 100 | 100 | 50 | 20 | 20 | 80 | 0 | 0 | 360 | 0 | 225 | 8 | 90 | 30 | 8 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 125 | 120 | 17 | 17 | 1.6 | 60 | 60 | 51 | 44 | 163 | 260 | 32 | 86 | 0 | 150 | 0 | 0 | 0 | 325 | 16 | 11 | 0 | 300 | 100 | 50 | 200 | 60 | 149 | 20 | 100 | 200 | 150 | 400 | 115 | 105 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 90 | 50 | 162 |  |  | 407 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 27 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 50 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 220 |  | 95 | 0 | 141 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 600 | 35
Generation at 08:00(Today) | 0 | 0 | 0 | 115 | 200 | 90 | 10 | 353 | 307 | 0 | 0 | 225 | 150 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 32 | 25 |  | 0 | 0 | 91 | 35 | 0 | 0 | 0 | 203 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 5 | 80 | 0 | 0 | 270 | 0 | 187 | 8 | 78 | 5 | 5 | 0 | 40 | 0 | 0 | 0 | 21 | 0 | 33 | 21 | 76 | 132 | 5 | 17 | 1 | 60 | 60 | 50 | 33 | 163 | 250 | 40 | 50 | 0 | 110 | 0 | 0 | 0 | 315 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 375 | 34 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 16 | 168 | 0 | 0 | 407 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 8 | 0 | 0 | 139 | 0 | 0 | 130 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 300 | 27 | 0 | 0 | 0
199
| Minimum Generation |  | 5330 | 5:00
| Highest Generation |  | 9056 | 19:00
| Day Peak Generation |  | 6841 | 12:00
| Evening Peak Generation |  | 9056 | 19:00
| HVDC Max Flow |  | 405 | 13:00
| HVDC EvPeak Flow |  | 405 | 19:00
| Load factor L.F |  | 73.74%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-11-29
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-11-28 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6841 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5683 | MW
Evening Peak Generation : |  | 9056 | MW Hour : | 19:00 | Available Max Generation : |  | 14246 | MW
E.P. Demand (at gen end) : |  | 9056 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9200 | MW
Maximum Generation : |  | 9056 | MW Hour : | 19:00 | Reserve(Generation end) |  | 5046 | MW
Total Gen. (MKWH) : |  | 160.2633 | System Load Factor : | 73.74% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -360 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-11-29
Actual : | 100.73 | Ft.(MSL) , | Rule curve : | 106.3 | Ft.( MSL )
Gas Consumed : | Total = | 995.67 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 129202719.51
: |  | Coal : | 54367338 | Oil : | 105058576.34 | Total : | 288628633.85
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3245.5909 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1098.5885 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 983.3915 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 888.255 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 802.8809 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 647.8836 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 368.8173 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 166.986 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 499.6486 |  |  | 0 | 0%
Total | 0 |  | 8702.0423 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 10)Ashuganj(S)-360 MW
|  |  |  | 2) Baghabari-100 MW | 11) Meghnaghat 450 MW GT-1
3) Ghorasal Unit-1,2,3,4
4) Ashuganj unit-4,5
5) Kaptai-2
6) Raozan #2
7) Siddirganj-335 MW
8) Chandpur-163 MW STG
9) Sirajganj #1 CCPP STG
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Kaptai-Hathazari 132 kV Ckt-1 was under shut down from 08:56 to 17:00 for A/M.
b) UMPL-Sherpur 132 kV Ckt-1 was under shut down from 09:07 to 16:48 for A/M.
c) Bahrampur-HVDC 230 kV Ckt-1 was under shut down from 09:38 to 17:14 for A/M.
d) Jamalpur-UMPL 132 kV Ckt-1 was under shut down from 09:54 to 16:41 for A/M.
e) Rangpur-Saidpur 132 kV Ckt-2 was under shut down from 08:45 to 16:23 for A/M.
f) Jhenaidah-Magura 132 kV Ckt-2 was under shut down from 08:05 to 15:14 for A/M.
g) HVDC-Rajshahi 230 kV Ckt-1 was under shut down from 09:27 to 21:20 for D/W.
h) Fenchuganj-Bibiyana 230 kV Ckt-1 was under shut down from 08:39 to 14:39 for A/M.
i) Savar-Manikganj power-Aminbazar 132 kV Ckt-1 was under shut down from 10:03 to 17:14 for A/M.
j) Maniknagar-Narinda 132 kV Ckt-1 was under shut down from 08:24 to 17:40 for A/M.
k) Tangail-RPCL132 kV Ckt-2 was under shut down from 08:32 to 15:37 for A/M.
l) Mymensing-RPCL 132 kV Ckt-2 was under shut down from 10:10 to 16:56 for A/M.
m) Ashuganj-Ghorasal 132 kV Ckt-2 was under shut down from 09:07 to 20:07 for A/M.
n) Kodda 132/33 kV T-5 was under shut down from 08:17 to 12:58 for A/M.
o) Netrokona 132/33 kV T-3 was under shut down from 08:31 to 13:52 for A/M.
p) Natore 132/33 kV T-1 was under shut down from 08:35 to 15:16 for A/M.
q) Bagerhat 33 kV Bus-section-1 & 2 were under shut down from 08:16 to 14:58 for C/M. |  |  |  |  | About 20 MW power interruption occurred under Bagerhat S/S
r) Sikalbaha 132/33 kV T-4 was under shut down from 09:42 to 16:43 for isolator work. |  |  |  |  | from 08:16 to 13:06.
s) Haripur-412 MW CCPP ST was synchronized at 10:04.
T) Bibiyana #3 CCPP ST was synchronized at 11:40.
u) Agargaon 230/132 kV T-1 transformer tripped at 12:08 showing master trip and was switched on at 14:19.
v) Khulsi 132/33 kV T-2 transformer tripped at 10:12 due to flashing in 33 kV isolator and was switched |  |  |  |  | About 60 MW power interruption occurred under Khulsi S/S
on at 10:28. |  |  |  |  | from 10:12 to 10:28.
w) Baghabari-71 MW was shut down at 13:13 due to gas shortage.
y) Maniknagar-Kabirpur 132 kV Ckt-2 & 132/33 kV GT-2 transformer are shut down since 07:40(29/11/20)
for A/M.
z) Mymensing-RPCL 132 kV Ckt-1 is under shut down since 07:52(29/11/20) for A/M.
aa) Cumilla(N)-Daudkandi 132 kV Ckt-1 tripped at 01:08(29/11/20) showing dist.A-phase and was
switched on at 01:28(28/11/20).
ab) Rampura 230 kV Bus-2 is under shut down since 07:46(29/11/20) for A/M.
ac) Rajshahi 132/33 kV T-3 transformer along with 33 kV Bus were shut down at 16:50 for emergency |  |  |  |  | About 20 MW power interruption occurred under Khulsi S/S
maintenance by NESCO and were switched on at 17:17. |  |  |  |  | from 16:50 to 17:17.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-11-28 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 115 | 2772000 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 4795773 | Machin problem.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 73 | 932960
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 98 | 1634045
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 338 | 594951
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 359 | 7261000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4805500 | GT-1 under maint.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 45 | 121920 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 140 | 3455185 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 40 | 313656 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 0 | Reserve.
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 208656
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 64000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 50 | 134400 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under Maintenance
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 58 | 324720 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 483840
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 32 | 142560 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 169495 | Low demand
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve.
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1107060 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 489600 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 21 | 508100 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 140 | 396436 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 0 | Reserve.
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 406680
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 983040 | Engine problem
| Manikgonj 162MW PP |  | IPP | 9*18 | 0 | 168 | 3964320 | on test.
| Dhaka area Total |  |  |  | 5895 | 2487 | 36069897
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve.
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 131085
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 45 | 278880
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 127 | 2979910 | Unit-2 under maint
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4897122
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 139 | 2345602
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 215689 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 720000
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 349248
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 20 | 438240
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve.
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27240
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 141 | 697527 | Transformer O/L
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 521696
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 818880
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 0 | 0 | 26345
| Chattogram area Total |  |  |  | 2266 | 983 | 14447464
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 2006858 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas Shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 182 | 4532000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7274100 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 492480 | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 25 | 458880 | Gas shortage
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 927779
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 100 | 575418 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 1619200 | ST Under maint
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 1743840 | Reserve.
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 182268
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 81900
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 90 | 1848000 | Low demand
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 272400
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve.
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 452810
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 558600
| Cumilla Area Total |  |  |  | 2980 | 1124 | 23243987
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 125 | 2933400 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 272340
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 8 | 172800 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12650
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 60 | 244800
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1288800 | #REF!
| Mymensingh PV 50 MW Solar PP |  | IPP | 50 | 0 | 0 | 282630
| Mymensingh Area Total |  |  |  | 637 | 325 | 5207420
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1201000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1434360
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3391036
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 254 | 5873000 | Machin problem.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 823800
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 47 | 799200
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 102000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 66 | 994832
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1126080
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 130 | 2535440
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | under maint.
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 27266 | Engine problem
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7303000 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 398 | 5368000
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 0 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1628 | 30979014
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 405 | 9630545 | Pole #02 under maint.
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 0 | Reserve.
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 245 | 7744896 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Reserve.
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 90 | 510720
107 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 740 | 17886161
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 69888 | Reserve.
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 27 | 451500 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 94 | 940307
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 520 | 8125400
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 30 | 546350
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 0 | 0 | 2400 | Ontest.
| Barisal Area Total |  |  |  | 1054 | 687 | 10135845
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 585000 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machin problem.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel Shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel Shortage
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 150 | 3057300
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 174 | 4115836 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 775100 | under maint.
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 359 | 8610363 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 514080
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 211770
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve.
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 29136 | Reserve.
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 0 | Reserve.
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 447072
| Rajshahi Area Total |  |  |  | 2183 | 829 | 18345657
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 140 | 3449600 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 3000 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 463680
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 31600
| Rangpur Area Total |  |  |  | 605 | 253 | 3947880
| Total |  |  |  | 19892 | 9056 | 160263325
| Eastern Grid Total |  |  |  | 13766 | 6547 | 109947782
| Western Grid Total |  |  |  | 6126 | 2509 | 50315543
| National Grid Total |  |  |  | 19892 | 9056 | 160263325
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
l
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2020-11-28
| (a) ENTIRE EASTERN GRID : |  | 5891 | MW | (b) ENTIRE WESTERN GRID : |  | 2662 | MW
| i) Dhaka area |  | 3168 | MW | i) Khulna area |  | 1036 | MW
| ii) Chittagong area |  | 1008 | MW | ii) Rajshahi area |  | 835 | MW
| iii) Comilla area |  | 726 | MW | iii) Barisal area |  | 236 | MW
| iv) Mymensingh area |  | 667 | MW | iv) Rangpur area |  | 555 | MW
| v) Sylhet area |  | 322 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8553 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
| Siddhirganj | 108 | 18:00 | Jamalpur | 88 | 18:00 | Benapol | 34 | 18:30
| Munsiganj | 84 | 20:00 | Sherpur | 82 | 18:00 | Jhenida | 78 | 18:00
| Sonargaon | 63 | 18:30 | Srimongal | 26 | 18:00 | Bottail | 95 | 18:00
| Shyampur | 164 | 0:00 | Shahjibazar | 79 | 19:00 | G.K Project | 29 | 19:00
| Bhulta | 140 | 3:00 | Fenchuganj | 27 | 18:00 | Faridpur | 126 | 18:30
| Madanganj | 54 | 0:00 | Kulawara | 35 | 18:00 | Madaripur | 62 | 19:30
| Shitalakhya | 107 | 12:00 | Sylhet | 72 | 19:00 | Sariatpur | 42 | 19:30
| Rahim steel | 12 | 19:00 | Chatak | 19 | 18:30 | Gopalganj | 58 | 18:00
| Matuail | 70 | 12:00 | Sunamganj | 28 | 18:30 | Bagerhat | 78 | 18:30
| Ghorasal | 58 | 21:00 | Biani Bazar | 42 | 18:00 | Mongla | 37 | 12:00
| Narsingdi | 132 | 18:30 | Comilla (S) | 102 | 18:30 | Satkhira | 72 | 18:30
| Haripur (SBU) | 114 | 18:30 | Comilla(N) | 73 | 19:30 | Gallamari | 28 | 9:00
| Ullon | 43 | 19:30 | Chandpur | 63 | 20:00 | Magura | 38 | 18:00
| Hasnabad | 141 | 19:00 | Feni | 86 | 18:00 | Norail | 28 | 18:00
| Magbazar | 71 | 13:00 | Chowmuhani | 120 | 18:00 | Chuadanga | 63 | 18:30
| Maniknagar | 68 | 18:00 | Ashuganj | 43 | 17:00 | Barisal(N) | 28 | 18:30
| Bangabhaban | 14 | 11:00 | Daudkandi | 96 | 20:00 | Barisal (S) | 70 | 18:00
| Narinda | 66 | 18:30 | B.Baria | 97 | 21:00 | Patuakhali | 84 | 20:00
| Dhanmondi | 100 | 12:00 | Ramganj | 66 | 20:00 | Bhandaria | 41 | 20:00
| Lalbag | 77 | 17:00 | Chaddagram | 23 | 19:30 | Borhan Uddin | 26 | 20:00
| Madartek | 49 | 19:00 | PHP | 5 | 9:00 | Ishurdi | 42 | 19:00
| Dhaka University | 0 | #NUM! | Madunaghat | 42 | 18:00 | Ruppur Paromanobik | 2 | 19:00
| Aftabnagar | 6 | 0.5 | Hathazari | 79 | 0.77083 | Natore | 81 | 0.77083
| Fatullah | 33 | 15:00 | Khulshi | 168 | 14:00 | Bogra | 120 | 18:00
| Mirpur | 77 | 18:00 | Halishahar | 111 | 19:00 | Noagaon | 82 | 19:00
| Kalyanpur | 63 | 18:00 | Baraulia | 156 | 9:00 | Rajshahi | 93 | 20:00
| Gulshan | 72 | 18:00 | Sikalbaha | 20 | 19:00 | Rajshahi New | 9 | 20:00
| Uttara | 67 | 18:00 | Dohazari | 56 | 18:00 | C.Nawabganj | 47 | 20:00
| Uttara New | 22 | 18:00 | Cox'sbazar | 76 | 18:00 | Amnura | 28 | 20:00
| Kamrangirchar | 70 | 19:00 | Chandraghona | 22 | 18:00 | Pabna | 77 | 19:00
| Savar | 103 | 18:00 | Kaptai | 3.5 | 18:00 | Shahjadpur | 68 | 19:00
| Bhasantec | 102 | 18:00 | A. Khaer Stl. | 9 | 13:00 | Serajganj | 55 | 18:00
| Agargaon | 45 | 18:30 | Bakulia | 77 | 18:00 | Niyamatpur | 37 | 19:00
| Satmosjid | 68 | 0.75 | Julda | 18 | 0.54167 | Joypurhat | 41 | 0.75
| Tongi | 83 | 16:00 | TK chemical | 20 | 18:00 | Sherpur(Bogura) | 38 | 18:00
| Kabirpur | 159 | 18:00 | Modern Steel | 17 | 18:30 | Mohastangor | 32 | 18:00
| Basundhara | 94 | 18:00 | Shahmirpur | 23 | 14:00 | Rangpur | 110 | 18:00
| Manikganj | 54 | 19:00 | Khagrachhari | 18 | 19:00 | Lalmonirhat | 40 | 18:00
| Joydevpur | 122 | 18:30 | Matarbari | 25 | 18:00 | Saidpur | 86 | 18:00
| New Tongi | 75 | 16:00 | Baroiar Hat | 20 | 19:00 | Purbasadipur | 83 | 18:00
| Kodda | 170 | 18:30 | Rangamati | 8 | 12:00 | Thakurgaon | 60 | 19:00
| Dhamrai | 62 | 18:00 | Abul Khair 230 | 6 | 13:00 | Palashbari | 88 | 18:00
| Rajendrapur | 82 | 16:00 | BSRM | 154 | 5:00 | Barapukuria | 34 | 19:00
| Valuka | 76 | 18:00 | GPH Ispat | 77 | 19:30 | Panchagar | 41 | 19:30
| Tangail | 133 | 18:30 | Goalpara | 15 | 19:30 | Joldhaka | 24 | 18:30
| Mymensing | 146 | 19:00 | Central s/s | 75 | 18:30 | Kurigram | 45 | 18:30
| Kishorganj | 79 | 19:30 | Noapara | 45 | 18:00
| Netrokona | 84 | 18:00 | Jessore | 76 | 18:00
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-11-28 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 419 | 19:00 | 406 | 16:00 | Kaliakoir | 395 | 0.20833 | 378 | 0.5
| Bheramara | 408 | 3:00 | 388 | 10:00 | Bhulta | 392 | 0.16667 | 380 | 0.5
| Ashuganj(N) | 396 | 18:30 | 386 | 12:00 | Gopalganj | 420 | 0.16667 | 404 | 0.8125
| Payra | 421 | 18:30 | 413 | 18:30
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 240 | 21:00 | 235 | 14:00 | Comilla (N) | 241 | 5:00 | 233 | 12:00
| Ishurdi | 239 | 2:00 | 226 | 18:00 | Hathazari | 221 | 20:00 | 211 | 15:00
| Ashuganj | 240 | 8:00 | 235 | 11:00 | Megnaghat | 240 | 1:00 | 232 | 11:00
| Serajganj | 235 | 6:00 | 228 | 18:00 | Fenchuganj | 246 | 2:00 | 240 | 16:00
| Baghabari | 243 | 5:00 | 236 | 18:00 | Siddhirganj | 236 | 3:00 | 228 | 11:00
| Barapukuria | 230 | 1:00 | 225 | 12:00 | Maniknagar | 234 | 4:00 | 226 | 12:00
| Bogra | 231 | 5:00 | 222 | 18:00 | Agargaon | 237 | 23:00 | 227 | 12:00
| Rajshahi | 226 | 1:00 | 219 | 18:00 | Barisal | 252 | 21:00 | 246 | 8:00
| Khulna South | 234 | 4:00 | 217 | 18:00 | AKSML | 225 | 20:00 | 214 | 14:00
| Rampura | 234 | 2:00 | 226 | 12:00 | BSRM | 228 | 20:00 | 215 | 15:00
| Haripur | 232 | 1:00 | 226 | 12:00 | Bibiyana | 248 | 20:00 | 240 | 24:00
| Hasnabad | 235 | 1:00 | 228 | 13:00 | Bhulta | 237 | 19:00 | 229 | 17:00
| Shyampur | 2311 | 18:30 | 220 | 12:00 | Ashuganj (S) | 238 | 18:30 | 232 | 12:00
| Aminbazar | 237 | 20:00 | 227 | 11:00 | Kaliakoir | 238 | 4:00 | 226 | 12:00
| Tongi | 233 | 23:00 | 225 | 15:00 | GPH | 225 | 4:00 | 212 | 14:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 139 | 19:00 | 134 | 12:00 | Madanhat | 137 | 0.91667 | 130 | 0.625
| Munsiganj | 140 | 19:00 | 132 | 12:00 | Hathazari | 135 | 0.8125 | 130 | 0.58333
| Sonargaon | 136 | 19:00 | 133 | 9:00 | Khulshi | 134 | 0.8125 | 126 | 0.625
| Shyampur | 136 | 3:00 | 129 | 12:00 | Halishahar | 134 | 0.8125 | 126 | 0.625
| Bhulta | 132 | 3:00 | 130 | 9:00 | Baraulia | 135 | 0.77083 | 128 | 0.5
| Madanganj | 140 | 19:00 | 132 | 11:00 | Sikalbaha | 135 | 0.83333 | 129 | 0.45833
| Shitalakhya | 142 | 1:00 | 132 | 12:00 | Dohazari | 132 | 0.79167 | 127 | 0.041667
| Rahim steal | 139 | 20:00 | 134 | 12:00 | Cox'sbazar | 128 | 0.83333 | 123 | 0.125
| Matuail | 139 | 19:00 | 134 | 12:00 | Chandraghona | 135 | 0.79167 | 129 | 0.66667
| Ghorasal | 140 | 1:00 | 136 | 11:00 | Kaptai | 135 | 0.75 | 130 | 0.5
| Narsinghdi | 136 | 3:00 | 131 | 12:00 | A. Khaer Stl. | 132 | 0.8125 | 128 | 0.45833
| Haripur (SBU) | 139 | 1:00 | 135 | 11:00 | Bakulia | 134 | 0.8125 | 127 | 0.625
| Ullon | 134 | 2:00 | 129 | 12:00 | Julda | 135 | 0.75 | 128 | 0.5
| Hasnabad | 140 | 1:00 | 134 | 11:00 | TK Chemical | 134 | 0.79167 | 128 | 0.5
| Magbazar | 134 | 1:00 | 128 | 12:00 | Modern Steel | 134 | 0.83333 | 127 | 0.5
| Maniknagar | 138 | 1:00 | 135 | 11:00 | Shahmirpur | 135 | 0.79167 | 127 | 0.625
| Bangabhaban | 138 | 1:00 | 135 | 11:00 | Khagrachhari | 134 | 0.79167 | 129 | 0.5
| Narinda | 138 | 1:00 | 135 | 11:00 | Matarbari | 130 | 0.70833 | 124 | 0.625
| Dhanmondi | 134 | 2:00 | 129 | 12:00 | Baroiar Hat | 136 | 0.8125 | 130 | 0.625
| Lalbag | 134 | 4:00 | 126 | 12:00 | Rangamati | 135 | 22:00 | 128 | 16:00
| Madartek | 134 | 2:00 | 128 | 12:00 | Goalpara S/S | 138 | 2:00 | 129 | 12:00
| Dhaka University | 0 |  | 0 |  | Khulna Central S/S | 138 | 4:00 | 124 | 0.75
| Aftabnagar | 134 | 1:00 | 129 | 11:00 | Noapara | 137 | 4:00 | 126 | 0.75
| Fatuiiah | 137 | 4:00 | 130 | 12:00 | Jessore | 134 | 6:00 | 123 | 0.75
| Mirpur | 133 | 6:00 | 127 | 12:00 | Benapol | 136 | 0.16667 | 124 | 0.75
| Kalyanpur | 134 | 19:30 | 130 | 12:00 | Jhenida | 134 | 1:00 | 122 | 0.75
| Gulshan | 133 | 5:00 | 127 | 12:00 | Bottail | 138 | 0.20833 | 129 | 0.75
| Uttara | 133 | 6:00 | 128 | 12:00 | G.K Project | 141 | 0.125 | 135 | 0.75
| Uttara New | 134 | 6:00 | 127 | 12:00 | Faridpur | 139 | 0.16667 | 131 | 0.77083
| Kamrangirchar | 140 | 6:00 | 131 | 12:00 | Madaripur | 140 | 0.20833 | 136 | 0.77083
| Savar | 136 | 6:00 | 131132 | 12:00 | Shariyatpur S/S | 141 | 4:00 | 135 | 0.77083
| Bhasantec | 139 | 5:00 | 133 | 12:00 | Gopalganj | 144 | 0.25 | 136 | 0.75
| Agargaon | 139 | 5:00 | 133 | 12:00 | Bagerhat | 138 | 2:00 | 122 | 0.75
| Satmosjid | 139 | 4:00 | 133 | 12:00 | Mongla | 135 | 1:00 | 124 | 0.75
| Tongi | 141 | 19:30 | 136 | 13:00 | Satkhira | 137 | 5:00 | 124 | 18:00
| Kabirpur | 134 | 22:00 | 128 | 14:00 | Gallamari | 139 | 0.20833 | 129 | 0.75
| Basundhara | 135 | 1:00 | 128 | 12:00 | Magura | 135 | 2:00 | 120 | 0.75
| Manikganj | 142 | 17:00 | 131 | 16:00 | Norail | 134 | 0.25 | 120 | 0.75
| Joydevpur | 141 | 20:00 | 134 | 15:00 | Chuadanga | 132 | 1:00 | 118 | 0.75
| New Tongi | 140 | 19:00 | 133 | 15:00 | Barisal(N) | 141 | 3:00 | 138 | 20:00
| Kodda | 138 | 19:00 | 130 | 15:00 | Barisal (S) | 140 | 0.083333 | 137 | 0.8125
| Dhamrai | 134 | 22:00 | 127 | 15:00 | Patuakhali(S) | 139 | 0.16667 | 135 | 0.5
| Rajendrapur | 138 | 4:00 | 130 | 12:00 | Bhandaria | 139 | 0.25 | 135 | 0.75
| Valuka | 132 | 19:00 | 126 | 9:00 | Ishurdi | 139 | 6:00 | 133 | 18:00
| Tangail | 135 | 3:00 | 128 | 12:00 | Ruppur Paromanobik | 139 | 6:00 | 133 | 18:00
| Mymensing | 133 | 20:00 | 127 | 24:00 | Natore | 139 | 6:00 | 131 | 18:00
| Kishorganj | 132 | 10:00 | 129 | 23:00 | Bogra | 140 | 6:00 | 134 | 18:00
| Netrokona | 131 | 20:00 | 127 | 1:00 | Noagaon | 136 | 6:00 | 128 | 18:00
| Jamalpur | 138 | 19:30 | 125 | 23:00 | Rajshahi | 140 | 5:00 | 132 | 18:00
| Sherpur | 137 | 19:30 | 123 | 24:00 | Rajshahi New | 140 | 2:00 | 132 | 18:00
| Srimongal | 139 | 9:00 | 136 | 16:00 | C.Nawabganj | 139 | 4:00 | 131 | 18:00
| Shahjibazar | 136 | 23:00 | 134 | 6:00 | Amnura | 136 | 6:00 | 133 | 18:00
| Fenchuganj | 138 | 1:00 | 136 | 15:00 | Pabna | 138 | 6:00 | 132 | 18:00
| Khulawara | 138 | 5:00 | 136 | 15:00 | Shahjadpur | 142 | 1:00 | 136 | 19:00
| Sylhet | 136 | 8:00 | 134 | 16:00 | Serajganj | 135 | 6:00 | 132 | 18:00
| Chatak | 135 | 4:00 | 133 | 15:00 | Niyamatpur | 136 | 5:00 | 127 | 18:00
| Sunamganj | 135 | 1:00 | 132 | 18:00 | Joypurhat | 138 | 4:00 | 130 | 18:00
| Biani Bazar | 136 | 9:00 | 132 | 18:00 | Sherpur(Bogura) | 140 | 5:00 | 132 | 18:00
| Comilla(s) | 130 | 1:00 | 127 | 11:00 | Mohastangor | 138 | 6:00 | 132 | 18:00
| Comilla(n) | 142 | 19:00 | 137 | 12:00 | Rangpur | 130 | 6:00 | 122 | 18:00
| Chandpur | 145 | 10:00 | 135 | 17:00 | Lalmonirhat | 130 | 6:00 | 122 | 18:00
| Feni | 138 | 8:00 | 132 | 16:00 | Saidpur | 130 | 6:00 | 119 | 18:00
| Chowmuhani | 136 | 8:00 | 132 | 22:00 | Purbasadipur | 129 | 4:00 | 117 | 18:00
| Ashuganj | 138 | 20:00 | 135 | 15:00 | Thakurgaon | 129 | 6:00 | 116 | 18:00
| Daudkandi | 138 | 19:00 | 133 | 12:00 | Palashbari | 133 | 6:00 | 127 | 18:00
| B.Baria | 133 | 13:00 | 132 | 14:00 | Barapukuria | 130 | 6:00 | 125 | 18:00
| Ramganj | 133 | 20:00 | 130 | 15:00 | Panchagar | 128 | 5:00 | 114 | 18:00
| Chaddagram | 139 | 21:00 | 133 | 15:00 | Joldhaka | 131 | 4:00 | 118 | 18:00
| PHP | 136 | 18:30 | 132 | 16:00 | Kurigram | 129 | 0.16667 | 119 | 0.75

## L-Curve
Date | 2020-11-28
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 21 | 4936 | 1968 | 6904 |  |  |  | QF-LDC-11
0:30 | 144 | 4411 | 1986.5 | 6397.5 | Date: | 2020-11-28
1:00 | 267 | 3886 | 2005 | 5891
1:30 | 268.5 | 3815 | 1915 | 5730
2:00 | 270 | 3744 | 1825 | 5569
2:30 | 271 | 3697 | 1825.5 | 5522.5 | [5 empty] | Gen. at Eve. Peak | 9056 | 9056 MW (19:00 )
3:00 | 272 | 3650 | 1826 | 5476 | [6 empty] | 19:00
3:30 | 279 | 3624.5 | 1801 | 5425.5 | [5 empty] | Gen. at Day Peak | 6841 | 6841 MW (12:00 )
4:00 | 286 | 3599 | 1776 | 5375 | [6 empty] | 12:00
4:30 | 342 | 3582 | 1770.5 | 5352.5 | [5 empty] | Highest Generation | 9056
5:00 | 398 | 3565 | 1765 | 5330 | [6 empty] | 19:00
5:30 | 458 | 3596 | 1793.5 | 5389.5
6:00 | 518 | 3627 | 1822 | 5449
6:30 | 359 | 3727 | 1919.5 | 5646.5
7:00 | 200 | 3827 | 2017 | 5844
7:30 | 117.5 | 4076 | 2003.5 | 6079.5
8:00 | 35 | 4325 | 1990 | 6315
8:30 | 172.5 | 4311 | 2010 | 6321
9:00 | 310 | 4297 | 2030 | 6327
9:30 | 338 | 4293.5 | 2030.5 | 6324
10:00 | 366 | 4290 | 2031 | 6321
10:30 | 356.5 | 4365 | 2018 | 6383
11:00 | 347 | 4440 | 2005 | 6445
11:30 | 284.5 | 4607 | 2036 | 6643
12:00 | 222 | 4774 | 2067 | 6841
12:30 | 128 | 4934 | 2052.5 | 6986.5
13:00 | 34 | 5094 | 2038 | 7132
13:30 | 60 | 5050.5 | 1954.5 | 7005
14:00 | 86 | 5007 | 1871 | 6878
14:30 | 141 | 4978 | 1896 | 6874
15:00 | 196 | 4949 | 1921 | 6870
15:30 | 176.5 | 4931 | 1904.5 | 6835.5
16:00 | 157 | 4913 | 1888 | 6801
16:30 | 79.5 | 5085 | 1886 | 6971
17:00 | 2 | 5257 | 1884 | 7141
17:30 | 177 | 5844 | 2172 | 8016
18:00 | 352 | 6431 | 2460 | 8891
18:30 | 341 | 6489 | 2484.5 | 8973.5
19:00 | 330 | 6547 | 2509 | 9056
19:30 | 310 | 6427 | 2518 | 8945
20:00 | 360 | 6390 | 2454 | 8844 |  |  |  | Executive Engineer
20:30 | 310 | 6264.5 | 2417.5 | 8682 |  |  |  | Network Operation Division
21:00 | 260 | 6139 | 2381 | 8520
21:30 | 229 | 5927 | 2294 | 8221
22:00 | 198 | 5715 | 2207 | 7922 |  |  |  |  | Page 6 of 7
22:30 | 102.5 | 5449 | 2173.5 | 7622.5
23:00 | 7 | 5183 | 2140 | 7323
23:30 | 14 | 5059.5 | 2054 | 7113.5
24:00 | 21 | 4936 | 1968 | 6904
9056 MW (19:00 )
6841 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-11-28 |  | Energy | 160263325
[10 empty] | 2020-11-28 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3474 | 405 | 1799 | 638 | 600 | 126 | 0 | 0 | 74
0:30 | 3268 | 397 | 1609.5 | 486 | 545 | 124 | 0 | 0 | 74 | Date: | 2020-11-28
1:00 | 3062 | 389 | 1420 | 334 | 490 | 122 | 0 | 0 | 74
1:30 | 3006.5 | 394 | 1359.5 | 335 | 440 | 122 | 0 | 0 | 73 | [7 empty] | Total Energy | 160.2633 | Total Energy Gen 160.263 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 160.263 MKWHr
2:00 | 2951 | 399 | 1299 | 336 | 390 | 122 | 0 | 0 | 72 | [7 empty] | Energy not Served | 0
2:30 | 2889.5 | 399 | 1322 | 329.5 | 390 | 121.5 | 0 | 0 | 71 | [7 empty] | Energy Requirement | 160.2633
3:00 | 2828 | 399 | 1345 | 323 | 390 | 121 | 0 | 0 | 70
3:30 | 2803 | 399 | 1320.5 | 323 | 390 | 121 | 0 | 0 | 69 | [6 empty] | Shortage
4:00 | 2778 | 399 | 1296 | 323 | 390 | 121 | 0 | 0 | 68
4:30 | 2732 | 399 | 1323 | 319.5 | 390 | 121 | 0 | 0 | 68
5:00 | 2686 | 399 | 1350 | 316 | 390 | 121 | 0 | 0 | 68
5:30 | 2724.5 | 399 | 1375.5 | 311 | 390 | 123.5 | 0 | 0 | 66
6:00 | 2763 | 399 | 1401 | 306 | 390 | 126 | 0 | 0 | 64
6:30 | 2882 | 399 | 1436.5 | 343.5 | 390 | 126 | 0 | 0 | 67 |  |  |  |  | Coal
7:00 | 3001 | 399 | 1472 | 381 | 390 | 126 | 0 | 0 | 70
7:30 | 3030 | 399.5 | 1570 | 477.5 | 390 | 126.5 | 0 | 0 | 71 |  |  |  | Oil |  |  |  | ,
8:00 | 3059 | 400 | 1668 | 574 | 390 | 127 | 0 | 0 | 72
8:30 | 3021 | 402 | 1678 | 606 | 390 | 127 | 0 | 0 | 67
9:00 | 2983 | 404 | 1688 | 638 | 390 | 127 | 0 | 0 | 62
9:30 | 2944.5 | 404 | 1714 | 630.5 | 390 | 127.5 | 0 | 0 | 65
10:00 | 2906 | 404 | 1740 | 623 | 390 | 128 | 0 | 0 | 68
10:30 | 2938.5 | 404 | 1728.5 | 637 | 390 | 128 | 13 | 0 | 71
11:00 | 2971 | 404 | 1717 | 651 | 390 | 128 | 26 | 0 | 74
11:30 | 3098 | 404 | 1768 | 662 | 405 | 128 | 25.5 | 0 | 71
12:00 | 3225 | 404 | 1819 | 673 | 420 | 128 | 25 | 0 | 68
12:30 | 3295.5 | 404.5 | 1851.5 | 710 | 430 | 127.5 | 23 | 0 | 68
13:00 | 3366 | 405 | 1884 | 747 | 440 | 127 | 21 | 0 | 68
13:30 | 3366 | 405 | 1884 | 747 | 440 | 127 | 21 | 0 | 68
14:00 | 3366 | 405 | 1884 | 747 | 440 | 127 | 21 | 0 | 68
14:30 | 3354.5 | 405 | 1834 | 689 | 440 | 126 | 22.5 | 0 | 72
15:00 | 3343 | 405 | 1784 | 631 | 440 | 125 | 24 | 0 | 76
15:30 | 3388 | 404.5 | 1729.5 | 623.5 | 440 | 125 | 19.5 | 0 | 75
16:00 | 3433 | 404 | 1675 | 616 | 440 | 125 | 15 | 0 | 74
16:30 | 3391.5 | 404 | 1646 | 822 | 440 | 125 | 50.5 | 0 | 82
17:00 | 3350 | 404 | 1617 | 1028 | 440 | 125 | 86 | 0 | 90
17:30 | 3533.5 | 404 | 1852 | 1415 | 515 | 126 | 76 | 0 | 94
18:00 | 3717 | 404 | 2087 | 1802 | 590 | 127 | 66 | 0 | 98
18:30 | 3654 | 404.5 | 2055.5 | 1947.5 | 625 | 127 | 66 | 0 | 94
19:00 | 3591 | 405 | 2024 | 2093 | 660 | 127 | 66 | 0 | 90
19:30 | 3570 | 405 | 2058 | 1965 | 660 | 127 | 66 | 0 | 94
20:00 | 3564 | 405 | 1982 | 1946 | 660 | 127 | 66 | 0 | 94
20:30 | 3558.5 | 405 | 2000 | 1798.5 | 660 | 127 | 41 | 0 | 92
21:00 | 3553 | 405 | 2018 | 1651 | 660 | 127 | 16 | 0 | 90
21:30 | 3531 | 405 | 2021 | 1378 | 660 | 127 | 13 | 0 | 86
22:00 | 3509 | 405 | 2024 | 1105 | 660 | 127 | 10 | 0 | 82
22:30 | 3506 | 405 | 1978.5 | 871.5 | 650 | 127.5 | 5 | 0 | 79
23:00 | 3503 | 405 | 1933 | 638 | 640 | 128 | 0 | 0 | 76
23:30 | 3488.5 | 405 | 1866 | 638 | 620 | 127 | 0 | 0 | 75 | Max Temp. in Dhaka |  | 29.8° C
24:00 | 3474 | 405 | 1799 | 638 | 600 | 126 | 0 | 0 | 74
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 160.263 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 160.263 MKWHr
Note on W13: Author:

## Generation
g | 2020-11-28
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 87 | 87 | 86 | 86 | 86 | 91 | 91 | 92 | 92 | 93 | 93 | 93 | 92 | 90 | 90 | 90 | 90 | 92 |  | 92 | 92 | 92 | 92 | 92 | 93 | 91 | 2131910
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 848000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 3 | 8 | 13 | 18 | 19 | 19 | 17 | 18 | 11 | 6 | 0 | [9 empty] | 131085
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 203 | 203 | 203 | 208 | 205 | 213 | 203 | 216 | 207 | 204 | 219 | 204 | 203 | 215 | 216 | 203 | 209 |  | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 4897122
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 119 | 104 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 100 | 100 | 100 | 100 | 100 | 70 | 139 |  | 139 | 130 | 130 | 129 | 129 | 129 | 129 | 2345602
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [10 empty] | 17 | 17 | 17 | 15 | 15 | 15 | 49 | 34 |  | 34 | 34 | 34 |  |  |  | 0 | 215689
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | [16 empty] | 39 | 37 | [7 empty] | 0 | 64000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [16 empty] | 42 | 95 |  | 140 | 95 | 95 | 14 |  |  | 0 | 396436
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2772000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4795773
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 100 | 100 | 100 | 80 | 80 | 80 | 2006858
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 23 | 27 | 22 | 25 | 28 | 29 | 29 | 29 | 26 | 26 | 26 | 29 |  | 29 | 26 | 29 | 29 | 29 | 29 | 5 | 492480
33 | Ashuganj 225 MW CCPP | 180 | 181 | 181 | 181 | 192 | 200 | 197 | 181 | 201 | 192 | 194 | 205 | 183 | 182 | 201 | 204 | 182 | 198 |  | 182 | 183 | 182 | 182 | 156 | 152 | 175 | 4532000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 260 | 260 | 270 | 285 | 320 | 310 | 330 | 315 | 325 | 370 | 310 | 260 | 285 | 295 | 260 | 315 |  | 280 | 285 | 280 | 280 | 280 | 280 | 280 | 7274100
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 5 | 5 | 458880
36 | Chandpur 150 MW CCPP | 81 | 82 | 81 | 85 | 85 | 92 | 84 | 84 | 50 | 45 | 44 | 48 | 45 | 44 | 50 | 50 | 46 | 72 |  | 80 | 78 | 78 | 78 | 78 | 78 | 78 | 1619200
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 227 | 227 | 227 | 182 | 148 | 136 | 136 | 104 | 22 | 38 | 121 | 199 | 265 | 337 | 346 | 367 | 348 | 368 |  | 338 | 336 | 335 | 335 | 335 | 335 | 337 | 594951
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 4805500
41 | Haripur 360MW CCPP(HPL) | 309 | 258 | 258 | 259 | 260 | 259 | 259 | 309 | 309 | 309 | 309 | 338 | 339 | 288 | 288 | 288 | 288 | 356 |  | 359 | 359 | 359 | 358 | 358 | 303 | 292 | 7261000
42 | RPCL 210MW CCPP | 163 | 110 | 110 | 109 | 109 | 109 | 109 | 167 | 164 | 161 | 144 | 142 | 117 | 103 | 102 | 122 | 125 | 124 |  | 125 | 126 | 125 | 126 | 121 | 123 | 129 | 2933400
43 | Mymensingh PV 50 MW Solar PP | [6 empty] | 2 | 14 | 17 | 35 | 54 | 48 | 46 | 36 | 24 | 9 | 1 | [9 empty] | 282630
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 40 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1201000
45 | Fenchugonj CCPP Phase-2 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1434360
46 | Shajibazar 330 MW CCPP | 253 | 258 | 257 | 258 | 259 | 261 | 257 | 258 | 260 | 252 | 258 | 267 | 250 | 260 | 264 | 265 | 254 | 258 |  | 254 | 252 | 257 | 256 | 256 | 255 | 250 | 5873000
47 | Shahjibazar GTPP Unit- 8 & 9 | 20 | 20 | 20 | 20 | 20 | 32 | 32 | 32 | 32 | 32 | 31 | 30 | 31 | 20 | 40 | 40 | 40 | 67 |  | 66 | 66 | 67 | 66 | 67 | 66 | 40 | 994832
48 | Shahjibazar 86MW PP (Shahjibazar) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 40 | 40 | 40 | 40 | 50 | 80 | 80 | 79 | 20 | 20 | 79 |  | 80 | 80 | 80 | 80 | 77 | 79 | 79 | 1126080
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 129 | 120 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 90 | 120 | 120 | 120 | 120 | 120 | 130 |  | 130 | 120 | 120 | 120 | 120 | 120 | 120 | 2535440
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [25 empty] | 0 | 0
54 | Hobiganj 11MW PP Cofidence-E | [12 empty] | 5 | 5 | 8 | 5 | 5 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 102000
55 | Fenchugonj 51 MW PP (Barakatullah) | [7 empty] | 44 | 48 | 47 | 47 | 45 | 50 | 50 | 49 | 52 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 823800
56 | Shahjahanulla 25 MW PP | [12 empty] | 15 | 15 | 15 | 15 | 15 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 27266
57 | Bibiana-II 341 MW CCPP (Summit) | 275 | 280 | 290 | 285 | 290 | 310 | 320 | 290 | 300 | 305 | 300 | 310 | 305 | 270 | 300 | 315 | 300 | 315 |  | 290 | 300 | 280 | 290 | 290 | 280 | 290 | 7303000
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | [25 empty] | 0 | 0
59 | Sikalbaha Energies 55 MW
60 | Barabkunda 22 MW PP (Regent) | [7 empty] | 18 | 18 | 18 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 349248
61 | Narshingdi 22 MW PP (Doreen) | [12 empty] | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 208656
62 | Tangail 22 MW PP (Doreen) | [7 empty] | 20 | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 272340
63 | Impoprt (Tripura) | 74 | 72 | 70 | 68 | 68 | 64 | 70 | 72 | 62 | 68 | 74 | 68 | 68 | 80 | 76 | 74 | 90 | 98 |  | 90 | 94 | 94 | 90 | 82 | 76 | 74 | 1848000
64 | Malancha, Ctg. EPZ (United) | 11 | 5 | 5 | 5 | 9 | 16 | 30 | 9 | 3 | 3 | 3 | 3 | 4 | 3 | 2 | 4 | 9 | 12 |  | 20 | 15 | 15 | 20 | 30 | 32 | 35 | 438240
65 | Feni 22MW PP (Doreen) | [7 empty] | 16 | [7 empty] | 5 | 20 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 182268
66 | Feni 11 MW PP (Doreen) | [16 empty] | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 81900
67 | Jangalia 33MW PP (Summit) | [15 empty] | 20 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 272400
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 18 | 15 | 15 | 15 | 15 | 15 | 9 | 9 | 9 | 9 | 12 | 12 | 19 | 19 | 16 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 452810
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 24 | 24 | 24 | 24 | 19 | 28 | 18 | 12 | 12 | 12 | 10 | 7 | 7 | 12 | 12 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 507060
71 | Maona 33 MW PP(Summit) | 22 | 22 | 22 | 20 | 22 | 17 | 17 | 22 | 17 | 17 | 25 | 25 | 25 | 25 | 8 | 16 | 16 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 17 | 489600
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 17 | 17 | 17 |  |  |  | 8 | 11 | 12 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 508100
73 | Ghorashal 108MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 28 | 98 | 95 | 95 | 95 | 95 | 95 | 99 | 95 | 43 | 43 | 98 |  | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 1634045
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | [16 empty] | 26 | 87 |  | 113 | 113 | 113 | 113 | 26 |  |  | 558600
| Manikgonj 162MW PP | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 167 | 166 | 166 | 169 | 168 | 165 | 166 | 166 | 168 | 168 | 169 |  | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 3964320
77 | Siddhirganj 100 PP(Dutch Bangla) | [16 empty] | 14 | 25 |  | 50 | 24 | 30 |  |  |  | 0 | 134400
78 | Gazipur 52 MW PP | [25 empty] | 0 | 0
79 | Kodda 150MW PP | [16 empty] | 32 | 32 |  | 32 | 32 | 32 | 16 | 10 |  |  | 142560
80 | Jamalpur 95 MW PP(Powerpac) | 8 | 8 |  |  |  |  | 2 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 16 | 8 | 8 | 8 | 172800
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [16 empty] | 41 | 105 |  | 105 | 88 | 70 | 34 | 17 |  | 0 | 406680
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 2 | 2 | 4 | 4 | 5 | 4 | 3 | 3 | 1 | [10 empty] | 27240
| Jodiac Power | [7 empty] | 11 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 52 |  | 54 | 54 | 54 | 54 | 54 | 17 | 0 | 521696
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | [9 empty] | 2 | 15 | 15 | 20 | 30 | 30 | 30 | 30 | 30 |  | 40 | 15 | 15 | 15 |  |  | 0 | 313656
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP(Summit) | 135 | 145 | 140 | 140 | 150 | 140 | 150 | 150 | 150 | 150 | 150 | 150 | 130 | 145 | 150 | 150 | 140 | 150 |  | 140 | 140 | 130 | 140 | 136 | 147 | 140 | 3455185
87 | Meghnaghat 100 MW(IEL) | [16 empty] | 12 | 25 |  | 45 | 25 | 28 |  |  |  | 0 | 121920
| Meghnaghat 104 MW PP (OPCL) | [7 empty] | 13 | 40 | 17 | 17 | 17 | 45 | 54 | 54 | 53 | 53 | 78 |  | 90 | 90 | 90 | 90 | 90 | 90 | 50 | 983040
88 | Ghorashal 78.5 MW PP(MAX) | [8 empty] | 30 | 30 | 30 | 50 | 70 | 40 | 40 | 40 | 40 | 60 |  | 73 | 73 | 74 | 74 | 75 | 75 | 75 | 932960
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44MW (Energyprima) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 14 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 799200
93 | Ashuganj 51 MW PP (Midland) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 45 | 51 | 51 | 43 | 43 | 43 | 43 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 927779
94 | Gagnagar 102 MW PP (Digital Power) | [11 empty] | 8 | 24 | 24 | 24 | 24 | 24 | 40 |  | 58 | 58 | 58 | 24 |  |  |  | 324720
95 | Patenga 50MW PP (Baraka) | [8 empty] | 4 | [7 empty] | 9 | 26 |  | 45 | 50 | 50 | 50 | 50 | 18 | 0 | 278880
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | [25 empty] | 0 | 0
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 35 | 55 |  | 35 | 35 | 35 | 17 |  |  | 0 | 169495
101 | Kushiara 163 MW CCPP (KP) | 130 | 110 | 110 | 110 | 110 | 130 | 163 | 163 | 110 | 130 | 130 | 130 | 163 | 110 | 110 | 110 | 110 | 163 |  | 163 | 163 | 163 | 163 | 163 | 130 | 130 | 3391036
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [10 empty] | 12650
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 |  |  | 9 | 17 | 17 | [7 empty] | 22 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 483840
104 | Keranigonj 300 MW PP (APR) | [25 empty] | 0 | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [16 empty] | 3 | 26 |  | 60 | 60 | 60 | 60 |  |  | 0 | 244800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [25 empty] | 0 | 0
115 | Juldah 100 MW PP Unit-3 (Acorn) | [7 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 50 | 100 |  | 100 | 100 | 100 | 100 | 100 | 20 | 0 | 720000
116 | Chandpur 200MW (Desh energy) | [6 empty] | 40 | 180 | 200 | 200 | 200 | 200 | 200 | 200 | 50 | [10 empty] | 0 | 1743840
117 | Ashuganj 150MW PP (Midland) | [8 empty] | 8 | 10 |  |  | 1 | 10 | 10 | 13 | 35 | 60 |  | 100 | 100 | 100 | 100 | 10 |  | 0 | 575418
118 | Bibiyana-III 400 MW CCPP | 80 | 80 | 79 | 80 | 78 | 79 | 79 | 80 | 90 | 80 | 80 | 143 | 312 | 351 | 351 | 352 | 351 | 400 |  | 398 | 398 | 398 | 398 | 400 | 398 | 397 | 5368000
| Jamalpur 115 MW PP (United) | 8 | [5 empty] | 4 | 8 | 8 | 33 | 55 | 70 | 85 | 85 | 85 | 85 | 105 | 115 |  | 115 | 115 | 115 | 115 | 115 | 16 | 0 | 1288800
| Anwara 300 MW PP (United) | [15 empty] | 16 | 50 | 118 |  | 141 | 141 | 141 | 141 | 107 |  | 0 | 697527
| Juldah unit-2 (Acorn) | [6 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 25 | 60 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 25 | 818880
| Anlima Energy Ltd. | [12 empty] | 15 | 12 | [11 empty] | 0 | 26345
120 | Eastern Zone Total | 3886 | 3744 | 3650 | 3599 | 3565 | 3627 | 3827 | 4325 | 4297 | 4290 | 4440 | 4774 | 5094 | 5007 | 4949 | 4913 | 5257 | 6431 |  | 6547 | 6427 | 6390 | 6139 | 5715 | 5183 | 4936 | 109947782
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [26 empty] | 0
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [12 empty] | 17 | 17 | 17 | 17 | 17 | 70 |  | 90 | 90 | 90 | 90 | 70 |  | 0 | 510720
130
131
132 | United Payra Power Ltd. | [25 empty] | 0 | 2400
133 | Bhola Nutan Biddut BD LTD (GAS) | 22 | 18 | 23 | 18 | 22 | 23 | 23 | 12 | 7 | 26 | 21 | 4 | 4 | 1 | 30 | 14 | 2 | 30 |  | 30 | 30 | 2 | 2 | 29 | 35 | 35 | 546350
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [16 empty] | 7 | 16 |  | 16 | 16 | 16 | 16 |  |  | 0 | 69888
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 14 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 13 | 13 | 14 | 34 | 34 | 34 | 34 | 34 | 94 |  | 94 | 94 | 93 | 95 | 95 | 95 | 13 | 940307
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 22 | 18 | 18 | 18 | 16 | 17 | 16 | 15 | 9 | 16 | 13 | 14 | 16 | 17 | 18 | 17 | 15 | 27 |  | 27 | 28 | 28 | 28 | 27 | 26 | 25 | 451500
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 389 | 399 | 399 | 399 | 399 | 399 | 399 | 400 | 404 | 404 | 404 | 404 | 405 | 404 | 405 | 404 | 404 | 404 |  | 405 | 405 | 405 | 405 | 405 | 405 | 405 | 9630545
147 | Bheramara 410 MW CCPP | 345 | 345 | 345 | 345 | 290 | 290 | 355 | 340 | 370 | 345 | 355 | 410 | 375 | 340 | 330 | 315 | 300 | 280 |  | 245 | 245 | 240 | 230 | 230 | 230 | 235 | 7744896
148 | Payra 1320 MW | 350 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 280 | 300 | 300 | 300 | 300 | 300 | 450 |  | 520 | 520 | 520 | 520 | 520 | 500 | 460 | 8125400
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 139 | 140 | 140 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3449600
153 | Baghabari 71 MW GTPP | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 50 | 50 | 50 | 50 | 50 | 40 | [13 empty] | 585000
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [26 empty] | 0
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 120 | 110 | 75 | 70 | 70 | 85 | 144 | 150 | 150 | 150 | 120 | 120 | 120 | 80 | 80 | 80 | 80 | 115 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3057300
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 130 | 130 | 130 | 130 | 130 | 130 | 190 | 183 | 189 | 186 | 179 | 192 | 194 | 160 | 164 | 174 | 165 | 181 |  | 174 | 154 | 152 | 153 | 157 | 157 | 159 | 4115836
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 51 | 20 | 20 | 20 | 20 | 57 | 70 | 70 | 70 | 70 | 70 | [14 empty] | 0 | 775100
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 352 | 313 | 344 | 304 | 346 | 349 | 348 | 337 | 347 | 348 | 346 | 396 | 354 | 337 | 361 | 360 | 325 | 422 |  | 359 | 387 | 359 | 379 | 351 | 369 | 316 | 8610363
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 514080
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 211770
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP | [10 empty] | 9 | 8 | 4 | 8 | 9 | [10 empty] | 0 | 29136
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [25 empty] | 0 | 0
172 | Confidence Power Bogura Unit-1 113 MW | [16 empty] | 25 | 90 |  | 113 | 113 | 113 | 70 |  |  | 0 | 447072
173 | Rangpur 20 MW GTPP | [16 empty] | 5 | [9 empty] | 3000
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 35 | 108 |  | 113 | 113 | 113 | 70 |  |  | 0 | 463680
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 3 | 5 | 5 | 5 | 4 | 3 | 3 | 0 | [9 empty] | 31600
178
178